## Test Conditions
DESIREE-FIRE Test Number 41 - Circuit Simulator Data Only
Test Date: | 2009-09-14
DCSim DAQ Start Time | 15:11
DCSim Time for Synchronization | 15:54
Heat Source Synchronization | 0:37 | minutes:seconds
Heat Source DAQ Start Time | 15:17
Fire Time | 15:57
Offset | 0:46 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2775 | seconds
Heat Source Offset | 0:40 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2412 | seconds
Heat Source Stop Time | 16:48
Test Duration | 0:51 | minutes:seconds
| 3060 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | PE/PVC, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
MOV 2 | PE/PVC, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-0.23438 | 122.6715 | -59.7885 | 62.7319 | -0.079269 | -0.00043792 | 0.06523 | 0.074245 | 0.00059812 | -0.0001496 | 0.00096124 | -0.027771 | 0.0014356 | 0.065033 | 0.060836 | -0.0062827 | 0.00098693 | 0.0018159 | -0.086975 | 62.6358 | -59.8526 | 62.6816 | -59.7427 | -60.141 | -0.11902 | -0.15564 | 62.6129 | -59.8114 | 62.6724 | -59.848 | -59.9899 | -59.7931 | -0.064087 | -0.096131 | -0.050354 | 0.045776 | 59.6695 | -0.35248 | 59.7336 | -0.28839 | -0.022888 | -0.11902 | -0.05951 | -0.059509 | -0.004578 | -0.20142 | 0.01831 | -0.17853 | 0.10986 | 122.5342 | -0.036621 | 122.4838 | 122.4884 | 122.4243 | 122.4243 | 122.4014 | -122.5845 | -122.5433 | 122.4701 | 122.4609 | 59.7015 | 59.6329
0.76562 | 122.7402 | -59.7702 | 62.709 | -0.06401 | -1.0718e-05 | 0.065016 | 0.075099 | -0.00089728 | -0.0005768 | -0.002243 | -0.012512 | -0.00091423 | 0.064179 | 0.063826 | -0.0047873 | -0.00029487 | 0.0020295 | -0.086975 | 62.6175 | -59.8572 | 62.7136 | -59.697 | -60.0906 | -0.10529 | -0.11902 | 62.5992 | -59.8068 | 62.7457 | -59.8297 | -59.9396 | -59.7931 | -0.086975 | -0.091552 | 0.004578 | 0.073243 | 59.6649 | -0.32043 | 59.7519 | -0.23346 | -0.036621 | -0.10986 | 0.036622 | -0.059509 | -0.022888 | -0.16937 | 0.013733 | -0.13275 | 0.16022 | 122.5708 | -0.022888 | 122.5525 | 122.4747 | 122.406 | 122.3877 | 122.3694 | -122.5662 | -122.5159 | 122.4838 | 122.5159 | 59.6832 | 59.6512
1.7656 | 122.7402 | -59.7519 | 62.7457 | -0.033493 | 0.00020288 | 0.064589 | 0.075099 | 0.0014527 | -0.0005768 | -0.002243 | -0.030823 | -0.0019824 | 0.063538 | 0.058913 | -0.0058553 | 0.0037641 | -0.00074771 | -0.10529 | 62.6221 | -59.8755 | 62.7182 | -59.7061 | -60.0998 | -0.091553 | -0.1236 | 62.5946 | -59.7839 | 62.764 | -59.816 | -59.9258 | -59.7839 | -0.1236 | -0.1236 | -0.027466 | 0.045776 | 59.6603 | -0.3479 | 59.7839 | -0.2243 | -0.032044 | -0.15106 | 0.01831 | -0.064087 | -0.032044 | -0.17395 | 0 | -0.14191 | 0.16937 | 122.5937 | -0.032043 | 122.5479 | 122.4976 | 122.3785 | 122.374 | 122.3465 | -122.6212 | -122.5296 | 122.4701 | 122.5159 | 59.6466 | 59.6283
2.7656 | 122.7585 | -59.7702 | 62.6999 | -0.033493 | 0.0014847 | 0.063948 | 0.072536 | 0.0016663 | -0.0024994 | 0.001175 | -0.021667 | 0.001222 | 0.063965 | 0.062545 | -0.0047873 | 0.0022687 | -0.00010671 | -0.091553 | 62.6129 | -59.8434 | 62.7319 | -59.6878 | -60.0952 | -0.082397 | -0.10529 | 62.5809 | -59.8068 | 62.7319 | -59.8526 | -59.9213 | -59.7565 | -0.073242 | -0.086975 | 0.032044 | 0.082398 | 59.6878 | -0.32501 | 59.761 | -0.25177 | -0.036621 | -0.11902 | 0.032044 | -0.082397 | 0.013733 | -0.15106 | 0.050354 | -0.11444 | 0.15564 | 122.5754 | -0.045776 | 122.5388 | 122.4564 | 122.3877 | 122.3831 | 122.3511 | -122.5433 | -122.5067 | 122.5021 | 122.5021 | 59.6787 | 59.6649
3.7656 | 122.7676 | -59.7519 | 62.7045 | 0.019913 | 0.00041648 | 0.065016 | 0.07339 | 0.0010253 | -0.0016448 | 0.001175 | 0.06073 | -0.002196 | 0.062683 | 0.066603 | -0.0054281 | 0.0037641 | -0.0033111 | -0.09613 | 62.6221 | -59.8572 | 62.7319 | -59.6878 | -60.0632 | -0.082397 | -0.16022 | 62.5946 | -59.7931 | 62.7731 | -59.8022 | -59.9213 | -59.7565 | -0.10529 | -0.082398 | 0.027466 | 0.064087 | 59.6695 | -0.31128 | 59.7748 | -0.20599 | -0.041199 | -0.10986 | 0.068664 | -0.050354 | -0.004578 | -0.16937 | 0.036621 | -0.12817 | 0.16937 | 122.5891 | -0.009155 | 122.5662 | 122.4792 | 122.3877 | 122.374 | 122.3465 | -122.5616 | -122.4976 | 122.4838 | 122.525 | 59.6558 | 59.5917
4.7656 | 122.7859 | -59.7427 | 62.6907 | -0.033493 | 0.0014847 | 0.064803 | 0.075954 | 0.00081172 | -0.0012176 | -0.0013886 | -0.0094604 | 0.00058097 | 0.065674 | 0.061904 | -0.0052145 | 0.0016277 | 0.0018159 | -0.027466 | 62.5946 | -59.8114 | 62.796 | -59.6008 | -59.9991 | -0.027466 | -0.018311 | 62.5351 | -59.7565 | 62.8052 | -59.761 | -59.8663 | -59.7153 | -0.068664 | -0.096131 | 0.10529 | 0.14191 | 59.7153 | -0.25635 | 59.7839 | -0.18768 | -0.013733 | -0.15564 | 0.11444 | -0.01831 | 0.027466 | -0.1236 | 0.041199 | -0.10986 | 0.21057 | 122.6074 | -0.004577 | 122.5616 | 122.406 | 122.2916 | 122.3373 | 122.2778 | -122.5021 | -122.4472 | 122.5388 | 122.5479 | 59.7153 | 59.7244
5.7656 | 122.7722 | -59.7336 | 62.6953 | -0.07164 | 0.0021255 | 0.064375 | 0.074886 | 0.0038025 | 0.0011322 | -0.00053396 | -0.046081 | 0.0010084 | 0.065888 | 0.071089 | -0.0071371 | 0.0026959 | 0.00032049 | -0.086975 | 62.6175 | -59.8389 | 62.6999 | -59.7198 | -60.0723 | -0.086975 | -0.07782 | 62.5717 | -59.8022 | 62.8006 | -59.7794 | -59.8709 | -59.7336 | -0.10529 | -0.077819 | 0.004578 | 0.013733 | 59.6466 | -0.33875 | 59.7519 | -0.23346 | -0.068664 | -0.1236 | 0.10529 | -0.045776 | 0 | -0.13733 | 0.068664 | -0.068665 | 0.11902 | 122.5388 | 0.022888 | 122.6028 | 122.4564 | 122.374 | 122.3511 | 122.3053 | -122.5342 | -122.4976 | 122.4335 | 122.5342 | 59.6466 | 59.6558
6.7656 | 122.7859 | -59.761 | 62.6816 | -0.07164 | -0.0012923 | 0.063307 | 0.074458 | 0.0023071 | 6.4004e-05 | -0.002884 | -0.024719 | 0.00079477 | 0.063751 | 0.065322 | -0.0073507 | 0.0024823 | -0.0011749 | -0.11444 | 62.6175 | -59.8526 | 62.7686 | -59.6786 | -60.0403 | -0.073242 | -0.07782 | 62.5809 | -59.8022 | 62.7823 | -59.7748 | -59.8846 | -59.729 | -0.091553 | -0.064087 | 0.086975 | 0.082397 | 59.6878 | -0.27924 | 59.7794 | -0.18768 | -0.041199 | -0.10071 | 0.10071 | -0.013733 | 0.032043 | -0.1236 | 0.073242 | -0.082398 | 0.17395 | 122.6212 | 0.027466 | 122.5845 | 122.4701 | 122.3831 | 122.3785 | 122.3419 | -122.5342 | -122.4838 | 122.5296 | 122.5433 | 59.6466 | 59.6832
7.7656 | 122.7859 | -59.729 | 62.6999 | -0.086899 | 0.00063028 | 0.06288 | 0.073604 | -0.0011109 | 0.0022004 | -0.00053396 | -0.0064086 | -5.9826e-05 | 0.06546 | 0.065535 | -0.0075643 | 0.00098693 | -0.0011749 | -0.032043 | 62.5717 | -59.8022 | 62.8372 | -59.6008 | -60.0037 | -0.004578 | -0.032043 | 62.5717 | -59.761 | 62.8098 | -59.7427 | -59.8572 | -59.7244 | -0.073242 | -0.12817 | 0.13733 | 0.12817 | 59.7244 | -0.27466 | 59.7977 | -0.20142 | -0.032043 | -0.12817 | 0.10986 | -0.013733 | 0.004578 | -0.12817 | 0.036621 | -0.096131 | 0.20142 | 122.6395 | 0.01831 | 122.5708 | 122.374 | 122.3328 | 122.3007 | 122.3007 | -122.5021 | -122.4609 | 122.5662 | 122.5388 | 59.697 | 59.697
8.7656 | 122.8226 | -59.7519 | 62.6862 | -0.079269 | 0.0010575 | 0.064375 | 0.075099 | 0.0016663 | -0.0020722 | 0.00010684 | -0.027771 | 0.00036737 | 0.064606 | 0.065535 | -0.0073507 | 0.00034613 | 0.0020295 | -0.022888 | 62.5809 | -59.7885 | 62.8143 | -59.5963 | -59.9899 | -0.032043 | -0.018311 | 62.5442 | -59.7794 | 62.8098 | -59.7427 | -59.8755 | -59.7198 | -0.036621 | -0.10529 | 0.12817 | 0.15564 | 59.7198 | -0.23804 | 59.7565 | -0.20142 | -0.027466 | -0.14191 | 0.1236 | 0.009155 | 0.032043 | -0.1236 | 0.059509 | -0.09613 | 0.19226 | 122.6028 | 0.036621 | 122.5891 | 122.3694 | 122.3236 | 122.3328 | 122.2961 | -122.4747 | -122.4655 | 122.5662 | 122.5616 | 59.729 | 59.7336
9.7656 | 122.7905 | -59.761 | 62.6862 | -0.10979 | -1.0718e-05 | 0.064162 | 0.075526 | 0.0012391 | -0.0018586 | -0.0013886 | 0.0027466 | -0.0013416 | 0.065888 | 0.061049 | -0.0064963 | 0.00013253 | 0.0033111 | -0.027466 | 62.5809 | -59.8206 | 62.8372 | -59.5917 | -60.0082 | -0.018311 | -0.009155 | 62.5397 | -59.7748 | 62.8189 | -59.7382 | -59.8663 | -59.7336 | -0.05951 | -0.10529 | 0.15106 | 0.16937 | 59.7427 | -0.24719 | 59.8022 | -0.18768 | -0.013733 | -0.14648 | 0.13275 | 0.022888 | 0.027465 | -0.10529 | 0.041198 | -0.091553 | 0.22888 | 122.6578 | 0.036621 | 122.5937 | 122.4014 | 122.3145 | 122.3419 | 122.3007 | -122.5067 | -122.4609 | 122.5983 | 122.58 | 59.7336 | 59.7519
10.7656 | 122.7768 | -59.7656 | 62.6633 | -0.07164 | 0.0029801 | 0.063307 | 0.072749 | 0.0012391 | -0.0016448 | -0.00032036 | 0.0057984 | -0.0017688 | 0.064392 | 0.056136 | -0.0071371 | 0.0033367 | 0.0024567 | -0.027466 | 62.5809 | -59.8068 | 62.8052 | -59.5734 | -60.0082 | -0.018311 | -0.027466 | 62.5671 | -59.761 | 62.8784 | -59.8114 | -59.9533 | -59.7839 | -0.041199 | -0.082397 | 0.14191 | 0.19226 | 59.7473 | -0.24262 | 59.7885 | -0.20142 | 0.004578 | -0.09613 | 0.21515 | -0.045776 | -0.018311 | -0.18768 | -0.022889 | -0.19226 | 0.23346 | 122.612 | -0.050354 | 122.6395 | 122.3877 | 122.3282 | 122.3465 | 122.3328 | -122.4701 | -122.4243 | 122.5708 | 122.644 | 59.7382 | 59.7382
11.7656 | 122.7448 | -59.761 | 62.6907 | -0.1403 | 0.00084388 | 0.063734 | 0.075313 | 0.00059812 | -0.0016448 | -0.00053396 | -0.0033568 | -0.00048703 | 0.063538 | 0.05464 | -0.0071371 | 0.00098693 | -0.0024567 | -0.054932 | 62.6038 | -59.8206 | 62.8235 | -59.5871 | -60.0082 | -0.013733 | 0 | 62.5809 | -59.7702 | 62.764 | -59.7931 | -59.8755 | -59.7427 | -0.05951 | -0.086975 | 0.13275 | 0.17395 | 59.7473 | -0.24719 | 59.8068 | -0.18768 | -0.009156 | -0.10986 | 0.073242 | -0.032044 | 0.01831 | -0.11444 | 0.027466 | -0.10528 | 0.23346 | 122.644 | -0.022888 | 122.5342 | 122.4243 | 122.3511 | 122.3648 | 122.3419 | -122.5113 | -122.4609 | 122.5845 | 122.525 | 59.7061 | 59.761
12.7656 | 122.7951 | -59.7519 | 62.6862 | -0.10216 | 0.0010575 | 0.065871 | 0.075099 | 0.0020935 | -0.0007904 | -0.0033112 | -0.0064086 | 0.00036737 | 0.062683 | 0.063399 | -0.0075643 | -0.0013629 | -0.0013885 | -0.041199 | 62.5946 | -59.816 | 62.8189 | -59.5963 | -60.0082 | -0.027466 | -0.018311 | 62.5671 | -59.7382 | 62.8052 | -59.7565 | -59.8755 | -59.7382 | -0.064087 | -0.091553 | 0.13275 | 0.15564 | 59.7244 | -0.25635 | 59.7885 | -0.19226 | 0.013733 | -0.11902 | 0.11902 | -0.004578 | 0.013733 | -0.1236 | 0 | -0.13733 | 0.21973 | 122.6349 | -0.018311 | 122.5433 | 122.4106 | 122.3053 | 122.3465 | 122.319 | -122.5021 | -122.4243 | 122.5708 | 122.5571 | 59.7107 | 59.7336
13.7656 | 122.8409 | -59.7427 | 62.6907 | -0.10216 | 0.0016983 | 0.063307 | 0.076381 | -0.0053833 | 0.000705 | 0.0013886 | -0.027771 | -0.00048703 | 0.064179 | 0.067244 | -0.0084189 | 0.00077333 | -0.0039521 | -0.022888 | 62.5854 | -59.8297 | 62.8052 | -59.6008 | -59.9945 | -0.013733 | -0.009155 | 62.59 | -59.7885 | 62.8235 | -59.7473 | -59.8572 | -59.7336 | -0.086975 | -0.10529 | 0.11444 | 0.14191 | 59.729 | -0.25177 | 59.816 | -0.16479 | -0.045776 | -0.10071 | 0.13275 | -0.004577 | 0.009155 | -0.11444 | 0.054931 | -0.068665 | 0.22888 | 122.6349 | 0.041199 | 122.612 | 122.4152 | 122.3785 | 122.3282 | 122.3328 | -122.5204 | -122.4792 | 122.5479 | 122.5662 | 59.7198 | 59.7336
14.7656 | 122.7997 | -59.7565 | 62.6953 | -0.12505 | 0.0025529 | 0.063094 | 0.07339 | -0.0023925 | 0.0013458 | -0.0024566 | -0.027771 | -0.0013416 | 0.065247 | 0.059767 | -0.0069235 | 0.0031231 | -0.0011749 | -0.036621 | 62.5854 | -59.8297 | 62.8189 | -59.5871 | -60.0037 | -0.022888 | 0 | 62.59 | -59.7656 | 62.7823 | -59.7885 | -59.9121 | -59.7473 | -0.073242 | -0.10986 | 0.1236 | 0.16937 | 59.7336 | -0.24719 | 59.8068 | -0.17395 | -0.009155 | -0.10529 | 0.086976 | -0.032043 | 0.009156 | -0.15564 | 0.018311 | -0.14648 | 0.24262 | 122.6486 | -0.022888 | 122.5479 | 122.4152 | 122.3557 | 122.3419 | 122.3465 | -122.525 | -122.4609 | 122.5754 | 122.5388 | 59.7198 | 59.7565
15.7656 | 122.7493 | -59.7336 | 62.7182 | -0.094528 | 0.0016983 | 0.063948 | 0.074458 | -0.00089728 | 0.000705 | -0.00053396 | -0.030823 | -0.00070063 | 0.064179 | 0.061049 | -0.0079917 | 0.0014141 | -0.0011749 | -0.036621 | 62.6083 | -59.816 | 62.8235 | -59.5825 | -59.9945 | -0.013733 | -0.022888 | 62.5534 | -59.7656 | 62.7777 | -59.7565 | -59.9075 | -59.7656 | -0.082397 | -0.10986 | 0.10529 | 0.15106 | 59.7198 | -0.26093 | 59.8022 | -0.17853 | -0.032043 | -0.16479 | 0.059509 | -0.022888 | -0.032043 | -0.17395 | 0 | -0.14191 | 0.23346 | 122.6395 | 0.009155 | 122.5433 | 122.4243 | 122.319 | 122.3419 | 122.287 | -122.5342 | -122.4838 | 122.5571 | 122.5113 | 59.697 | 59.7107
16.7656 | 122.7631 | -59.7427 | 62.7182 | -0.086899 | 0.0025529 | 0.063307 | 0.076167 | -0.0026063 | 0.0009186 | 0.0013886 | -0.015564 | -0.00048703 | 0.064392 | 0.052291 | -0.0064963 | 0.0035503 | 0.00010689 | -0.036621 | 62.5763 | -59.8114 | 62.8098 | -59.5825 | -60.0037 | -0.018311 | 0.018311 | 62.5671 | -59.7748 | 62.764 | -59.761 | -59.8892 | -59.761 | -0.068664 | -0.14191 | 0.091552 | 0.16022 | 59.7244 | -0.26093 | 59.7931 | -0.19226 | -0.032043 | -0.15106 | 0.045776 | -0.01831 | -0.01831 | -0.14648 | 0.013733 | -0.11444 | 0.22888 | 122.6212 | 0.013733 | 122.5388 | 122.3877 | 122.3419 | 122.319 | 122.3099 | -122.5296 | -122.493 | 122.5525 | 122.5067 | 59.7061 | 59.761
17.7656 | 122.7585 | -59.7473 | 62.6862 | -0.11742 | 0.0012711 | 0.063307 | 0.072322 | -0.0055969 | -0.0020722 | -0.0030976 | -0.039978 | -0.0026232 | 0.062897 | 0.065749 | -0.0054281 | 0.00098693 | -0.0022431 | -0.045776 | 62.5992 | -59.8068 | 62.8235 | -59.5825 | -60.0082 | -0.009155 | 0 | 62.5671 | -59.7794 | 62.8281 | -59.8251 | -59.9258 | -59.729 | -0.05951 | -0.086975 | 0.13733 | 0.16479 | 59.7382 | -0.26093 | 59.7977 | -0.20142 | -0.032044 | -0.11902 | 0.14191 | -0.07782 | 0.01831 | -0.17853 | 0.050354 | -0.14648 | 0.2243 | 122.6303 | -0.045776 | 122.6074 | 122.406 | 122.3465 | 122.3465 | 122.3145 | -122.493 | -122.4655 | 122.5708 | 122.5754 | 59.7015 | 59.7473
18.7656 | 122.7814 | -59.7473 | 62.7365 | -0.06401 | 0.00041648 | 0.063948 | 0.07574 | 0.00038452 | -0.002713 | -0.00074776 | -0.0094604 | -0.0017688 | 0.061402 | 0.059127 | -0.0050009 | 0.0029095 | -0.00053411 | -0.073242 | 62.6083 | -59.816 | 62.7823 | -59.6237 | -60.0311 | -0.022888 | -0.059509 | 62.5763 | -59.7839 | 62.7686 | -59.7702 | -59.8938 | -59.7427 | -0.068665 | -0.12817 | 0.045777 | 0.1236 | 59.7244 | -0.28381 | 59.7931 | -0.21515 | -0.036622 | -0.16022 | 0.032044 | -0.022889 | 0.004577 | -0.14648 | 0.041199 | -0.10986 | 0.19226 | 122.5983 | 0.013733 | 122.5525 | 122.4243 | 122.3602 | 122.3557 | 122.3236 | -122.5525 | -122.5204 | 122.5296 | 122.5159 | 59.6741 | 59.6878
19.7656 | 122.8226 | -59.7427 | 62.7045 | -0.11742 | 0.0029801 | 0.06523 | 0.074458 | -0.0017517 | -0.0024994 | -0.0024566 | -0.049133 | 0.00015377 | 0.061615 | 0.066817 | -0.0050009 | 0.0024823 | 0.00053409 | -0.027466 | 62.5946 | -59.816 | 62.8143 | -59.5734 | -59.9991 | -0.013733 | -0.004578 | 62.5854 | -59.7656 | 62.8143 | -59.7702 | -59.8938 | -59.6329 | -0.073242 | -0.10986 | 0.10986 | 0.16937 | 59.729 | -0.25635 | 59.8022 | -0.18311 | -0.022888 | -0.11902 | 0.10986 | -0.027466 | 0.10986 | -0.15106 | 0.13275 | -0.12817 | 0.24262 | 122.6303 | -0.004578 | 122.58 | 122.4106 | 122.3511 | 122.3373 | 122.3282 | -122.5204 | -122.4701 | 122.5571 | 122.5571 | 59.7153 | 59.7382
20.7656 | 122.7493 | -59.7519 | 62.7319 | -0.17082 | 0.0016983 | 0.064162 | 0.074245 | 0.0038025 | -0.0012176 | -0.00074776 | -0.021667 | -0.0019824 | 0.064392 | 0.058699 | -0.0054281 | 0.0026959 | -0.0054473 | -0.045776 | 62.59 | -59.8251 | 62.8281 | -59.5871 | -59.9945 | 0 | -0.004578 | 62.5717 | -59.7748 | 62.8098 | -59.7519 | -59.8801 | -59.7336 | -0.073242 | -0.14191 | 0.09613 | 0.16479 | 59.7519 | -0.24262 | 59.8251 | -0.16937 | -0.022888 | -0.16022 | 0.077819 | 0 | 0.01831 | -0.12817 | 0.041198 | -0.10529 | 0.23804 | 122.6532 | 0.022888 | 122.5845 | 122.4152 | 122.3465 | 122.3419 | 122.3236 | -122.5571 | -122.5067 | 122.58 | 122.5616 | 59.7061 | 59.7473
21.7656 | 122.7448 | -59.7519 | 62.7045 | -0.1403 | 0.0016983 | 0.063094 | 0.075313 | -0.0013245 | -0.0007904 | -0.00032036 | -0.0094604 | -0.0013416 | 0.061402 | 0.06169 | -0.0060691 | 0.00098693 | 0.00032049 | -0.050354 | 62.59 | -59.8251 | 62.7914 | -59.6191 | -60.0403 | -0.018311 | -0.041199 | 62.59 | -59.7794 | 62.7777 | -59.761 | -59.8801 | -59.7565 | -0.073242 | -0.11444 | 0.086975 | 0.13275 | 59.7336 | -0.28839 | 59.8068 | -0.21515 | -0.027466 | -0.11444 | 0.073242 | -0.009155 | -0.004578 | -0.12817 | 0.022888 | -0.10071 | 0.20599 | 122.6166 | 0.018311 | 122.5571 | 122.4152 | 122.3694 | 122.3419 | 122.3419 | -122.5296 | -122.4838 | 122.5433 | 122.5296 | 59.7015 | 59.7107
22.7656 | 122.7631 | -59.7382 | 62.7045 | -0.018234 | 0.0012711 | 0.064803 | 0.07339 | 0.00059812 | -0.0003632 | -0.0024566 | -0.021667 | 0.00079477 | 0.062897 | 0.063826 | -0.0056417 | 0.00013253 | 0.0033111 | -0.073242 | 62.6038 | -59.8343 | 62.7731 | -59.6283 | -60.0311 | -0.032043 | -0.050354 | 62.5946 | -59.7748 | 62.7731 | -59.7794 | -59.8846 | -59.7427 | -0.096131 | -0.10071 | 0.068664 | 0.10986 | 59.7061 | -0.29297 | 59.8022 | -0.19684 | -0.036621 | -0.10986 | 0.068664 | -0.041199 | -0.004578 | -0.14648 | 0.032043 | -0.10986 | 0.20599 | 122.6074 | -0.004578 | 122.5479 | 122.4381 | 122.3694 | 122.3419 | 122.3328 | -122.5388 | -122.4792 | 122.5113 | 122.5113 | 59.6649 | 59.6878
23.7656 | 122.7814 | -59.7244 | 62.6999 | -0.094528 | 0.0025529 | 0.065657 | 0.072749 | 0.0012391 | -0.0020722 | -0.0020294 | -0.036926 | -0.00070063 | 0.062897 | 0.063826 | -0.0043601 | -0.00029487 | 0.00010689 | -0.064087 | 62.6083 | -59.8206 | 62.7777 | -59.6558 | -60.0174 | -0.036621 | -0.032043 | 62.5809 | -59.7794 | 62.7777 | -59.7839 | -59.8801 | -59.7656 | -0.096131 | -0.091553 | 0.07782 | 0.068664 | 59.6878 | -0.29297 | 59.7839 | -0.19684 | -0.054932 | -0.11902 | 0.07782 | -0.05951 | -0.041199 | -0.15564 | 0.013733 | -0.10071 | 0.16479 | 122.5983 | -0.004578 | 122.5571 | 122.4289 | 122.3602 | 122.3328 | 122.3053 | -122.5204 | -122.4792 | 122.5021 | 122.5021 | 59.6603 | 59.6924
24.7656 | 122.7585 | -59.7244 | 62.7136 | -0.10216 | 0.00084388 | 0.06288 | 0.074031 | 0.0010253 | -0.0020722 | -0.0037384 | -0.015564 | -0.00091423 | 0.06247 | 0.06404 | -0.0092733 | 0.00077333 | -0.0024567 | -0.050354 | 62.645 | -59.7977 | 62.7823 | -59.6329 | -60.0174 | -0.027466 | -0.045776 | 62.59 | -59.7885 | 62.7777 | -59.7656 | -59.8846 | -59.7565 | -0.073242 | -0.068665 | 0.068665 | 0.091552 | 59.697 | -0.29297 | 59.7702 | -0.21973 | -0.064087 | -0.1236 | 0.064087 | -0.041199 | -0.032044 | -0.16022 | 0.032043 | -0.096131 | 0.16479 | 122.58 | 0.022888 | 122.5662 | 122.4426 | 122.3785 | 122.3694 | 122.3145 | -122.5113 | -122.5021 | 122.5067 | 122.5021 | 59.6741 | 59.6787
25.7656 | 122.7448 | -59.7519 | 62.7365 | -0.10216 | 0.0010575 | 0.061598 | 0.076381 | 0.0031617 | 0.000705 | -0.0030976 | -0.0094604 | -0.00048703 | 0.061829 | 0.06404 | -0.0052145 | 0.0018413 | -0.0011749 | -0.054932 | 62.6175 | -59.8114 | 62.7823 | -59.6283 | -60.022 | -0.009155 | -0.054932 | 62.59 | -59.7794 | 62.7731 | -59.7748 | -59.8801 | -59.7656 | -0.059509 | -0.11902 | 0.045777 | 0.1236 | 59.7427 | -0.27008 | 59.8022 | -0.21057 | -0.027466 | -0.14648 | 0.036621 | -0.022888 | -0.013733 | -0.12817 | 0.013733 | -0.10071 | 0.1831 | 122.5937 | 0.004578 | 122.5525 | 122.4289 | 122.3694 | 122.3694 | 122.3419 | -122.5479 | -122.5159 | 122.5342 | 122.525 | 59.697 | 59.697
26.7656 | 122.7905 | -59.7153 | 62.7365 | -0.056381 | -1.0718e-05 | 0.062666 | 0.075099 | 0.0025207 | -0.0020722 | 0.00096124 | -0.0033568 | -0.001128 | 0.063324 | 0.055709 | -0.0077779 | 0.0012005 | -0.00074771 | 0.064087 | 62.6175 | -59.7839 | 62.8876 | -59.5047 | -59.903 | 0.1236 | 0.15106 | 62.5946 | -59.7382 | 62.8601 | -59.6558 | -59.7748 | -59.6924 | -0.068665 | -0.11902 | 0.15106 | 0.21057 | 59.8389 | -0.18768 | 59.9075 | -0.11902 | -0.022888 | -0.14191 | 0.1236 | 0.059509 | 0.022888 | -0.059509 | 0.045776 | -0.036621 | 0.27924 | 122.6715 | 0.082397 | 122.5983 | 122.4014 | 122.3328 | 122.3328 | 122.3099 | -122.5204 | -122.4747 | 122.6028 | 122.5754 | 59.7794 | 59.8663
27.7656 | 122.7402 | -59.7382 | 62.7136 | -0.10216 | 0.0010575 | 0.063094 | 0.076167 | -0.0019653 | 0.0002778 | -0.0026704 | -0.024719 | 0.0010084 | 0.063324 | 0.064467 | -0.0062827 | 0.00055973 | 0.0013885 | -0.059509 | 62.5946 | -59.816 | 62.7914 | -59.6329 | -60.0311 | -0.022888 | -0.059509 | 62.5854 | -59.7794 | 62.7869 | -59.7794 | -59.8984 | -59.7519 | -0.07782 | -0.11902 | 0.07782 | 0.10529 | 59.7153 | -0.29297 | 59.7931 | -0.21515 | -0.041199 | -0.12817 | 0.073242 | -0.041199 | -0.013733 | -0.16022 | 0.027466 | -0.11902 | 0.1831 | 122.6074 | 0 | 122.5662 | 122.4106 | 122.3648 | 122.3328 | 122.3236 | -122.5296 | -122.493 | 122.5296 | 122.525 | 59.6787 | 59.6787
28.7656 | 122.7402 | -59.7382 | 62.709 | -0.10979 | 0.00020288 | 0.063948 | 0.073604 | 0.00059812 | 0.0013458 | 0.00032044 | -0.024719 | -0.00048703 | 0.062897 | 0.067031 | -0.0077779 | 0.0022687 | -0.0020295 | -0.068665 | 62.6129 | -59.8114 | 62.7823 | -59.6283 | -60.0266 | -0.018311 | -0.059509 | 62.5809 | -59.7839 | 62.7731 | -59.7702 | -59.8801 | -59.7382 | -0.073242 | -0.09613 | 0.073243 | 0.10986 | 59.7198 | -0.28839 | 59.7931 | -0.21515 | -0.045777 | -0.12817 | 0.064087 | -0.032044 | 0 | -0.14191 | 0.045777 | -0.09613 | 0.1831 | 122.5937 | 0.013733 | 122.5571 | 122.4243 | 122.3648 | 122.3511 | 122.319 | -122.5204 | -122.493 | 122.5204 | 122.5113 | 59.6695 | 59.6787
29.7656 | 122.7676 | -59.7519 | 62.7228 | -0.079269 | 0.0036209 | 0.063094 | 0.075099 | -0.0013245 | -0.0016448 | 0.001175 | -0.030823 | 0.00079477 | 0.063965 | 0.066176 | -0.0077779 | 0.0022687 | 0.00096129 | -0.064087 | 62.5992 | -59.816 | 62.7777 | -59.6146 | -60.0311 | -0.022888 | -0.054932 | 62.6038 | -59.7748 | 62.7823 | -59.7656 | -59.8801 | -59.7794 | -0.064087 | -0.1236 | 0.054932 | 0.13733 | 59.729 | -0.27924 | 59.7931 | -0.21515 | -0.022888 | -0.11902 | 0.05951 | -0.013733 | -0.027466 | -0.12817 | -0.004578 | -0.10529 | 0.20142 | 122.5937 | 0.009155 | 122.5571 | 122.4152 | 122.3785 | 122.3511 | 122.3557 | -122.5388 | -122.4976 | 122.5296 | 122.5342 | 59.6878 | 59.697
30.7656 | 122.7676 | -59.761 | 62.6907 | -0.010605 | -0.00086512 | 0.063948 | 0.074672 | -0.00046988 | 6.4004e-05 | 0.00096124 | -0.030823 | -0.0019824 | 0.064606 | 0.06938 | -0.0045737 | 0.0024823 | -0.0020295 | -0.09613 | 62.6038 | -59.8206 | 62.7731 | -59.6237 | -60.0357 | -0.045776 | -0.050354 | 62.5992 | -59.7702 | 62.7731 | -59.7794 | -59.8755 | -59.7519 | -0.05951 | -0.086975 | 0.082397 | 0.13733 | 59.7153 | -0.27466 | 59.7748 | -0.21515 | -0.009156 | -0.091553 | 0.082397 | -0.018311 | 0.009155 | -0.11444 | 0.018311 | -0.10528 | 0.19684 | 122.5937 | -0.009155 | 122.5433 | 122.4243 | 122.3694 | 122.3648 | 122.3602 | -122.5113 | -122.4609 | 122.5342 | 122.5342 | 59.6649 | 59.7107
31.7656 | 122.7036 | -59.7244 | 62.7777 | -0.06401 | -0.00043792 | 0.064375 | 0.07574 | 0.00017092 | -0.0018586 | -0.00053396 | -0.097961 | -5.9826e-05 | 0.063751 | 0.06874 | -0.0045737 | 0.0035503 | -0.0026703 | 0 | 62.645 | -59.8251 | 62.7457 | -59.6786 | -60.0174 | 0.018311 | -0.11902 | 62.6266 | -59.7794 | 62.7914 | -59.7794 | -59.9075 | -59.761 | -0.10071 | -0.13275 | -0.032043 | 0.045776 | 59.7427 | -0.29297 | 59.8434 | -0.19226 | -0.054932 | -0.15106 | 0.013733 | -0.054932 | -0.036621 | -0.18311 | 0.018311 | -0.12817 | 0.14648 | 122.5708 | 0 | 122.5708 | 122.4701 | 122.406 | 122.3694 | 122.3511 | -122.6028 | -122.5571 | 122.4701 | 122.5159 | 59.7244 | 59.6054
32.7656 | 122.7448 | -59.7519 | 62.7228 | -0.07164 | 0.00084388 | 0.06523 | 0.075954 | -0.0013245 | 0.000705 | -0.00096136 | -0.055237 | -0.00048703 | 0.063538 | 0.054854 | -0.0039327 | 0.00098693 | 0.0016021 | -0.032043 | 62.5946 | -59.8114 | 62.8006 | -59.5413 | -59.8801 | -0.032043 | -0.004578 | 62.5534 | -59.7885 | 62.7777 | -59.7794 | -59.8892 | -59.7473 | -0.059509 | -0.12817 | 0.07782 | 0.21057 | 59.7198 | -0.12817 | 59.7794 | -0.068665 | -0.036621 | -0.16937 | 0.054932 | -0.027466 | 0.004578 | -0.13733 | 0.041199 | -0.10071 | 0.27008 | 122.612 | 0.009155 | 122.5662 | 122.406 | 122.3419 | 122.3465 | 122.3053 | -122.5342 | -122.5113 | 122.5525 | 122.5296 | 59.7198 | 59.7473
33.7656 | 122.7585 | -59.7473 | 62.6999 | -0.10979 | -0.0012923 | 0.062239 | 0.074031 | 0.0023071 | -0.0001496 | -0.00010676 | -0.052185 | -0.0017688 | 0.063111 | 0.065322 | -0.0058553 | 0.00034613 | 0.0035247 | -0.032043 | 62.5946 | -59.816 | 62.8189 | -59.5825 | -60.0082 | -0.004578 | 0.064087 | 62.5992 | -59.7473 | 62.7777 | -59.7565 | -59.8343 | -59.7473 | -0.068665 | -0.10529 | 0.11902 | 0.16479 | 59.7427 | -0.26093 | 59.8114 | -0.19226 | 0 | -0.10071 | 0.07782 | -0.009156 | 0 | -0.086976 | 0 | -0.086976 | 0.23346 | 122.6349 | -0.009156 | 122.525 | 122.4106 | 122.3465 | 122.3419 | 122.3465 | -122.5159 | -122.4472 | 122.5662 | 122.525 | 59.7153 | 59.8114
34.7656 | 122.7448 | -59.729 | 62.709 | -0.12505 | 0.0010575 | 0.063521 | 0.072963 | -0.00025628 | -0.0018586 | -0.00010676 | -0.015564 | 0.00015377 | 0.065033 | 0.059554 | -0.0060691 | 0.0026959 | 0.0026703 | -0.041199 | 62.6266 | -59.8114 | 62.7869 | -59.6329 | -60.0174 | 0.013733 | -0.018311 | 62.6038 | -59.7565 | 62.7823 | -59.7473 | -59.8663 | -59.7382 | -0.082397 | -0.082397 | 0.07782 | 0.09613 | 59.7427 | -0.28839 | 59.8251 | -0.20599 | -0.027466 | -0.10529 | 0.073243 | -0.01831 | -0.009155 | -0.13733 | 0.018311 | -0.10986 | 0.17853 | 122.5983 | 0.009156 | 122.5388 | 122.438 | 122.3602 | 122.3557 | 122.3328 | -122.5204 | -122.4655 | 122.5159 | 122.5113 | 59.6878 | 59.7107
35.7656 | 122.7585 | -59.7473 | 62.7228 | -0.079269 | 0.0010575 | 0.065657 | 0.074245 | 0.00059812 | 0.0009186 | -0.00053396 | -0.052185 | -0.0013416 | 0.06482 | 0.058486 | -0.0054281 | 0.0029095 | -0.00010671 | -0.073242 | 62.6038 | -59.8251 | 62.7777 | -59.6283 | -60.0311 | -0.018311 | -0.059509 | 62.5946 | -59.7702 | 62.7731 | -59.7885 | -59.8755 | -59.7519 | -0.07782 | -0.11902 | 0.054932 | 0.11902 | 59.729 | -0.28381 | 59.8068 | -0.20599 | -0.022889 | -0.12817 | 0.050354 | -0.041199 | -0.004578 | -0.12817 | 0.018311 | -0.10528 | 0.19684 | 122.6028 | -0.01831 | 122.5433 | 122.4289 | 122.3648 | 122.3511 | 122.3419 | -122.5479 | -122.493 | 122.525 | 122.5204 | 59.6741 | 59.6878
36.7656 | 122.7264 | -59.7336 | 62.7731 | -0.033493 | 0.0040481 | 0.065443 | 0.075526 | -0.0030335 | -0.0018586 | -0.00053396 | -0.030823 | -0.001128 | 0.064392 | 0.068312 | -0.0067099 | 0.0035503 | -0.0030975 | 0.059509 | 62.6175 | -59.7839 | 62.8418 | -59.5551 | -59.9396 | 0.10986 | 0.10986 | 62.6358 | -59.7519 | 62.8326 | -59.6832 | -59.816 | -59.729 | -0.050354 | -0.15564 | 0.068665 | 0.17853 | 59.8434 | -0.20599 | 59.8938 | -0.15564 | -0.01831 | -0.13733 | 0.05951 | 0.050354 | 0.004578 | -0.082397 | 0.022888 | -0.064087 | 0.22888 | 122.6257 | 0.068664 | 122.5845 | 122.4014 | 122.3877 | 122.3511 | 122.3694 | -122.5571 | -122.525 | 122.5754 | 122.5662 | 59.7931 | 59.8434
37.7656 | 122.731 | -59.7336 | 62.7182 | -0.06401 | -0.00043792 | 0.066298 | 0.074886 | 0.00017092 | -0.0007904 | -0.001175 | -0.064392 | -0.0015552 | 0.06482 | 0.067885 | -0.0060691 | 0.0016277 | -0.00074771 | -0.054932 | 62.59 | -59.816 | 62.796 | -59.5596 | -59.8434 | -0.009155 | 0 | 62.558 | -59.7839 | 62.7914 | -59.7839 | -59.8892 | -59.761 | -0.082397 | -0.12817 | 0.07782 | 0.17395 | 59.7244 | -0.10986 | 59.8068 | -0.027466 | -0.050354 | -0.16022 | 0.073242 | -0.050354 | -0.027465 | -0.15564 | 0.022889 | -0.10529 | 0.25635 | 122.612 | 0 | 122.5754 | 122.406 | 122.3419 | 122.3236 | 122.2916 | -122.5342 | -122.5021 | 122.5296 | 122.525 | 59.6786 | 59.7336
38.7656 | 122.7493 | -59.7427 | 62.7182 | -0.048752 | 0.0021255 | 0.063307 | 0.074245 | -0.00089728 | -0.0005768 | 0.00074764 | -0.021667 | 0.00058097 | 0.064606 | 0.06404 | -0.0052145 | -0.00029487 | -0.0020295 | -0.068665 | 62.6312 | -59.8114 | 62.7823 | -59.6283 | -60.0174 | -0.013733 | -0.050354 | 62.5763 | -59.7748 | 62.7914 | -59.7839 | -59.8938 | -59.7519 | -0.068664 | -0.086975 | 0.064087 | 0.11444 | 59.729 | -0.27466 | 59.7977 | -0.20599 | -0.032043 | -0.14191 | 0.073242 | -0.041199 | -0.009155 | -0.15106 | 0.022888 | -0.11902 | 0.1831 | 122.5937 | -0.009156 | 122.5662 | 122.4426 | 122.3511 | 122.374 | 122.319 | -122.5296 | -122.493 | 122.525 | 122.5342 | 59.6741 | 59.6924
39.7656 | 122.7356 | -59.7198 | 62.7136 | -0.056381 | 0.00063028 | 0.064589 | 0.076167 | -0.00025628 | -0.0005768 | 0.00053404 | -0.052185 | -0.00070063 | 0.063538 | 0.061904 | -0.0047873 | 0.0031231 | -0.0024567 | -0.041199 | 62.59 | -59.8206 | 62.8235 | -59.5779 | -59.9945 | -0.009155 | 0 | 62.5626 | -59.7702 | 62.8098 | -59.7656 | -59.8618 | -59.7382 | -0.10071 | -0.1236 | 0.10986 | 0.14191 | 59.7107 | -0.27466 | 59.8114 | -0.17395 | -0.050354 | -0.15106 | 0.09613 | -0.045776 | -0.01831 | -0.14191 | 0.032044 | -0.091552 | 0.24262 | 122.644 | 0.004578 | 122.58 | 122.4106 | 122.3328 | 122.3099 | 122.2824 | -122.5342 | -122.4838 | 122.5433 | 122.5296 | 59.6787 | 59.7198
40.7656 | 122.7905 | -59.7382 | 62.6953 | -0.11742 | 0.00063028 | 0.064803 | 0.074672 | -0.0011109 | -0.0022858 | -0.0030976 | -0.046081 | 0.00036737 | 0.063538 | 0.068099 | -0.0054281 | 0.0031231 | 0.00096129 | -0.022888 | 62.6038 | -59.8206 | 62.8235 | -59.5825 | -60.0128 | 0 | -0.004578 | 62.5717 | -59.7748 | 62.8189 | -59.7382 | -59.8618 | -59.7244 | -0.082398 | -0.091552 | 0.12817 | 0.15564 | 59.7382 | -0.27466 | 59.8206 | -0.19226 | -0.036621 | -0.1236 | 0.1236 | 0 | 0.013733 | -0.1236 | 0.050354 | -0.086975 | 0.23804 | 122.644 | 0.036621 | 122.5937 | 122.4243 | 122.3465 | 122.3419 | 122.3099 | -122.5159 | -122.4701 | 122.5616 | 122.5571 | 59.7153 | 59.7336
41.7656 | 122.7585 | -59.7061 | 62.7319 | -0.041122 | 0.0029801 | 0.065016 | 0.075313 | -0.0021789 | 6.4004e-05 | 0.00053404 | -0.027771 | -0.001128 | 0.064606 | 0.062972 | -0.0064963 | 0.0022687 | -0.0011749 | 0.050354 | 62.6266 | -59.7977 | 62.8647 | -59.5413 | -59.9213 | 0.10529 | 0.14191 | 62.6129 | -59.729 | 62.8281 | -59.7061 | -59.816 | -59.7015 | -0.091552 | -0.10529 | 0.13275 | 0.16479 | 59.8114 | -0.21515 | 59.903 | -0.1236 | -0.022888 | -0.11902 | 0.09613 | 0 | 0.004578 | -0.10986 | 0.027466 | -0.086975 | 0.25635 | 122.6624 | 0.022888 | 122.5571 | 122.4243 | 122.3419 | 122.3328 | 122.319 | -122.5296 | -122.4609 | 122.5708 | 122.5342 | 59.7565 | 59.848
42.7656 | 122.8043 | -59.7198 | 62.7045 | -0.12505 | 0.00041648 | 0.062453 | 0.076594 | 0.0033753 | -0.0012176 | -0.0018158 | -0.058289 | 0.0016492 | 0.064392 | 0.06639 | -0.0054281 | 0.0029095 | -0.00074771 | -0.036621 | 62.5763 | -59.8251 | 62.8235 | -59.5734 | -60.0082 | -0.018311 | 0 | 62.5717 | -59.7702 | 62.7914 | -59.761 | -59.8526 | -59.7565 | -0.10528 | -0.12817 | 0.11902 | 0.14649 | 59.7015 | -0.28839 | 59.8068 | -0.18311 | -0.050354 | -0.13275 | 0.086975 | -0.041198 | -0.036621 | -0.13275 | 0.013733 | -0.082397 | 0.25177 | 122.6486 | 0.009156 | 122.5616 | 122.4014 | 122.3419 | 122.2961 | 122.2916 | -122.5296 | -122.4747 | 122.5433 | 122.5113 | 59.6832 | 59.7198
43.7656 | 122.7951 | -59.7382 | 62.7136 | -0.1403 | 0.0029801 | 0.062666 | 0.074458 | 0.0029479 | -0.0001496 | -0.002243 | -0.064392 | -0.00048703 | 0.065674 | 0.061049 | -0.0056417 | 0.0018413 | 0.00053409 | -0.036621 | 62.5763 | -59.7977 | 62.8189 | -59.5825 | -60.0128 | -0.022888 | -0.018311 | 62.5854 | -59.7794 | 62.8098 | -59.7336 | -59.8526 | -59.7107 | -0.059509 | -0.13733 | 0.10529 | 0.15564 | 59.7153 | -0.27466 | 59.7748 | -0.21515 | -0.041199 | -0.12817 | 0.09613 | 0.004577 | 0.027466 | -0.11444 | 0.068665 | -0.073242 | 0.21515 | 122.6166 | 0.045776 | 122.5891 | 122.374 | 122.3648 | 122.3145 | 122.3236 | -122.5113 | -122.493 | 122.5571 | 122.5479 | 59.7015 | 59.7198
44.7656 | 122.818 | -59.7336 | 62.6816 | -0.12505 | 0.0027665 | 0.065657 | 0.074672 | 0.0016663 | -0.0005768 | 0.00074764 | -0.049133 | 0.0016492 | 0.063111 | 0.065749 | -0.0069235 | 0.0014141 | 0.00074769 | -0.036621 | 62.5809 | -59.8251 | 62.8281 | -59.5871 | -59.9899 | -0.032043 | -0.013733 | 62.6083 | -59.7977 | 62.8326 | -59.7473 | -59.8434 | -59.7061 | -0.091552 | -0.10071 | 0.14648 | 0.14648 | 59.7015 | -0.25635 | 59.7931 | -0.16479 | -0.064086 | -0.073243 | 0.15106 | -0.013732 | 0.027466 | -0.10986 | 0.091552 | -0.045777 | 0.23804 | 122.6532 | 0.050354 | 122.6303 | 122.406 | 122.406 | 122.3145 | 122.3419 | -122.5067 | -122.4792 | 122.5616 | 122.5662 | 59.697 | 59.7198
45.7656 | 122.7814 | -59.7382 | 62.6907 | -0.041122 | 0.0021255 | 0.063094 | 0.077022 | 0.0016663 | -0.0031402 | 0.00053404 | -0.049133 | -0.00027343 | 0.06247 | 0.070449 | -0.0060691 | 0.0022687 | -0.00010671 | -0.045776 | 62.6038 | -59.8206 | 62.8235 | -59.5642 | -59.9854 | -0.004578 | -0.013733 | 62.5717 | -59.7794 | 62.8006 | -59.7519 | -59.8709 | -59.7336 | -0.082398 | -0.086975 | 0.13275 | 0.17395 | 59.7336 | -0.24719 | 59.816 | -0.16479 | -0.041199 | -0.11902 | 0.10986 | -0.013733 | 0.004577 | -0.13275 | 0.045776 | -0.091553 | 0.25635 | 122.644 | 0.027466 | 122.58 | 122.4243 | 122.3511 | 122.3419 | 122.3099 | -122.5113 | -122.4701 | 122.5616 | 122.5388 | 59.6924 | 59.7244
46.7656 | 122.7997 | -59.7244 | 62.6953 | -0.094528 | 0.0025529 | 0.064803 | 0.077235 | -0.00046988 | 6.4004e-05 | -0.00074776 | -0.058289 | 0.0016492 | 0.064606 | 0.063826 | -0.0050009 | 0.0039777 | -0.0020295 | -0.018311 | 62.5992 | -59.8434 | 62.8098 | -59.6008 | -59.9945 | -0.027466 | -0.013733 | 62.5763 | -59.7794 | 62.8189 | -59.7336 | -59.848 | -59.697 | -0.11902 | -0.09613 | 0.11444 | 0.1236 | 59.697 | -0.27008 | 59.816 | -0.15106 | -0.054932 | -0.11902 | 0.1236 | -0.009156 | 0.027466 | -0.1236 | 0.082398 | -0.068664 | 0.24262 | 122.6532 | 0.045776 | 122.5983 | 122.4426 | 122.3557 | 122.3236 | 122.3007 | -122.5388 | -122.4747 | 122.5342 | 122.5433 | 59.7061 | 59.7107
47.7656 | 122.7814 | -59.7336 | 62.6953 | -0.12505 | 0.0010575 | 0.064375 | 0.075313 | -0.0034607 | -0.0012176 | 0.00096124 | -0.079651 | 0.0018628 | 0.062256 | 0.059981 | -0.0060691 | 0.0018413 | -0.0011749 | -0.059509 | 62.5854 | -59.848 | 62.796 | -59.61 | -60.0174 | -0.050354 | -0.032043 | 62.5946 | -59.7702 | 62.8189 | -59.7473 | -59.8572 | -59.7107 | -0.11444 | -0.10986 | 0.10071 | 0.1236 | 59.6832 | -0.28381 | 59.7977 | -0.16937 | -0.036621 | -0.10071 | 0.1236 | -0.013732 | 0.022889 | -0.1236 | 0.05951 | -0.086975 | 0.23804 | 122.644 | 0.022889 | 122.5891 | 122.4335 | 122.3648 | 122.319 | 122.3282 | -122.5433 | -122.4655 | 122.5296 | 122.5525 | 59.6741 | 59.7015
48.7656 | 122.7951 | -59.7382 | 62.6816 | -0.06401 | 0.0014847 | 0.063948 | 0.077022 | 0.0050843 | 0.0015594 | -0.0020294 | -0.06134 | -5.9826e-05 | 0.063538 | 0.058272 | -0.0079917 | 0.0033367 | 0.00053409 | -0.032043 | 62.5854 | -59.816 | 62.8052 | -59.6054 | -59.9808 | -0.013733 | -0.004578 | 62.5671 | -59.7839 | 62.8326 | -59.7336 | -59.8572 | -59.7015 | -0.07782 | -0.096131 | 0.1236 | 0.13275 | 59.7244 | -0.24261 | 59.8022 | -0.16479 | -0.045777 | -0.11444 | 0.15106 | 0.004577 | 0.036621 | -0.11902 | 0.082398 | -0.073242 | 0.21057 | 122.6212 | 0.050354 | 122.6166 | 122.4014 | 122.3511 | 122.3236 | 122.3053 | -122.4976 | -122.4655 | 122.5433 | 122.5708 | 59.7061 | 59.7336
49.7656 | 122.7859 | -59.7336 | 62.6816 | -0.10979 | 0.0023391 | 0.064162 | 0.07574 | 0.00059812 | -0.0007904 | -0.001175 | -0.055237 | -5.9826e-05 | 0.063751 | 0.064681 | -0.0058553 | 0.0026959 | 0.0026703 | -0.041199 | 62.59 | -59.816 | 62.8235 | -59.5734 | -60.0082 | -0.027466 | -0.027466 | 62.5854 | -59.7748 | 62.8281 | -59.7336 | -59.8572 | -59.7107 | -0.082397 | -0.091553 | 0.14191 | 0.16022 | 59.7061 | -0.27466 | 59.7885 | -0.19226 | -0.041198 | -0.096131 | 0.14648 | 0 | 0.022889 | -0.1236 | 0.064087 | -0.082398 | 0.24262 | 122.6395 | 0.041198 | 122.6028 | 122.406 | 122.3602 | 122.3236 | 122.319 | -122.4976 | -122.4564 | 122.5571 | 122.5616 | 59.6924 | 59.7061
50.7656 | 122.7905 | -59.7473 | 62.7136 | -0.10216 | 0.0019119 | 0.063521 | 0.075099 | 0.0014527 | 0.0004914 | 0.0030976 | -0.04303 | -0.00091423 | 0.06247 | 0.063826 | -0.0071371 | 0.0018413 | -0.00032051 | -0.032043 | 62.5717 | -59.8297 | 62.8143 | -59.5825 | -59.9945 | -0.018311 | -0.018311 | 62.5488 | -59.761 | 62.8143 | -59.7336 | -59.848 | -59.7153 | -0.082398 | -0.14191 | 0.10071 | 0.16479 | 59.729 | -0.24719 | 59.8114 | -0.16479 | -0.013733 | -0.16479 | 0.10071 | 0.013732 | 0.032043 | -0.10071 | 0.045776 | -0.086975 | 0.24719 | 122.644 | 0.027465 | 122.5754 | 122.4014 | 122.3099 | 122.319 | 122.2961 | -122.5433 | -122.4747 | 122.5616 | 122.5616 | 59.7153 | 59.729
51.7656 | 122.8134 | -59.7473 | 62.709 | -0.1403 | -0.0010787 | 0.065657 | 0.07574 | 0.00081172 | -0.0018586 | 0.0016022 | -0.064392 | 0.00036737 | 0.062256 | 0.056136 | -0.0067099 | 0.0031231 | 0.0011749 | -0.07782 | 62.6266 | -59.8572 | 62.7777 | -59.6191 | -60.054 | -0.050354 | -0.050354 | 62.5809 | -59.7977 | 62.8098 | -59.7473 | -59.8755 | -59.7107 | -0.10986 | -0.082397 | 0.068665 | 0.12817 | 59.697 | -0.3067 | 59.8068 | -0.19684 | -0.050354 | -0.12817 | 0.10071 | 0 | 0.036621 | -0.12817 | 0.086975 | -0.07782 | 0.23804 | 122.6349 | 0.050354 | 122.6074 | 122.4838 | 122.3785 | 122.374 | 122.3282 | -122.5662 | -122.5067 | 122.525 | 122.5571 | 59.6695 | 59.697
52.7656 | 122.7951 | -59.7336 | 62.6862 | -0.079269 | 0.0014847 | 0.066298 | 0.075313 | 0.0012391 | 0.0004914 | -0.00053396 | -0.027771 | -0.00048703 | 0.06482 | 0.06169 | -0.0067099 | 0.0014141 | -0.00053411 | -0.032043 | 62.5854 | -59.8343 | 62.8189 | -59.5963 | -60.0037 | -0.036621 | -0.004578 | 62.5534 | -59.761 | 62.8281 | -59.7382 | -59.8389 | -59.7107 | -0.10071 | -0.10071 | 0.13275 | 0.13733 | 59.697 | -0.27008 | 59.7977 | -0.16937 | -0.027465 | -0.13275 | 0.14191 | -0.004577 | 0.022889 | -0.10529 | 0.050354 | -0.07782 | 0.23804 | 122.6532 | 0.022888 | 122.5891 | 122.4197 | 122.3145 | 122.319 | 122.287 | -122.5204 | -122.4472 | 122.5525 | 122.5616 | 59.7015 | 59.729
53.7656 | 122.7539 | -59.7382 | 62.7136 | -0.056381 | 0.00041648 | 0.063948 | 0.077449 | 0.0031617 | -0.0031402 | 0.0024566 | -0.088806 | 0.0010084 | 0.063965 | 0.065962 | -0.0071371 | 0.0016277 | -0.0026703 | -0.09613 | 62.6312 | -59.8389 | 62.7274 | -59.6924 | -60.0998 | -0.10071 | -0.036621 | 62.59 | -59.7794 | 62.7731 | -59.7885 | -59.8846 | -59.7565 | -0.10071 | -0.082397 | 0.013733 | 0.045776 | 59.6375 | -0.36163 | 59.7382 | -0.26093 | -0.041199 | -0.1236 | 0.059509 | -0.050354 | -0.018311 | -0.14648 | 0.022888 | -0.10529 | 0.14648 | 122.5662 | -0.009155 | 122.5525 | 122.4701 | 122.3694 | 122.3694 | 122.3282 | -122.5525 | -122.493 | 122.4655 | 122.5113 | 59.642 | 59.7015
54.7656 | 122.7127 | -59.7565 | 62.709 | -0.079269 | 0.0023391 | 0.061385 | 0.077022 | 0.0050843 | 0.000705 | -0.00096136 | -0.079651 | 0.002931 | 0.06546 | 0.065962 | -0.0058553 | 0.0029095 | 0.00032049 | -0.10986 | 62.6358 | -59.8709 | 62.7136 | -59.7107 | -60.0861 | -0.10986 | -0.1236 | 62.59 | -59.7885 | 62.6862 | -59.7107 | -59.903 | -59.816 | -0.11444 | -0.073242 | 0.004578 | 0.045777 | 59.6466 | -0.32959 | 59.761 | -0.21515 | -0.032043 | -0.11902 | -0.022888 | 0.045777 | -0.059509 | -0.14648 | -0.027466 | -0.11444 | 0.16022 | 122.5845 | 0.07782 | 122.4747 | 122.5067 | 122.3785 | 122.3923 | 122.3465 | -122.58 | -122.4976 | 122.4701 | 122.4426 | 59.6466 | 59.6329
55.7656 | 122.7814 | -59.7336 | 62.6907 | -0.025863 | 0.0012711 | 0.062453 | 0.074672 | 0.0016663 | -0.0024994 | 0.001175 | -0.06134 | -0.00091423 | 0.064179 | 0.062545 | -0.0062827 | 0.0024823 | -0.0013885 | -0.10529 | 62.645 | -59.8343 | 62.7731 | -59.6375 | -60.0449 | -0.059509 | -0.073242 | 62.5534 | -59.7885 | 62.8143 | -59.761 | -59.8709 | -59.7061 | -0.10071 | -0.045777 | 0.082397 | 0.096131 | 59.6741 | -0.31128 | 59.7748 | -0.21057 | -0.054931 | -0.13733 | 0.1236 | -0.027465 | 0.027466 | -0.13733 | 0.082397 | -0.082398 | 0.19684 | 122.6074 | 0.027466 | 122.6028 | 122.4792 | 122.3419 | 122.3785 | 122.287 | -122.525 | -122.4792 | 122.5067 | 122.5479 | 59.6283 | 59.6603
56.7656 | 122.7722 | -59.7519 | 62.7136 | -0.12505 | -0.00043792 | 0.063948 | 0.075313 | 0.0020935 | 0.005191 | -0.001175 | -0.067444 | 0.00058097 | 0.064606 | 0.065108 | -0.0064963 | 0.0024823 | -0.00074771 | -0.10071 | 62.6221 | -59.8526 | 62.6999 | -59.5459 | -60.0311 | -0.15106 | -0.07782 | 62.5717 | -59.7931 | 62.796 | -59.761 | -59.8892 | -59.7473 | -0.10071 | -0.091553 | -0.013733 | 0.20599 | 59.6008 | -0.27924 | 59.7015 | -0.17853 | -0.041199 | -0.14191 | 0.082398 | -0.009155 | 0.004578 | -0.13733 | 0.045777 | -0.09613 | 0.3067 | 122.5525 | 0.032044 | 122.5891 | 122.4747 | 122.3648 | 122.374 | 122.3236 | -122.5662 | -122.5067 | 122.4518 | 122.5479 | 59.6512 | 59.6741
57.7656 | 122.7539 | -59.7565 | 62.6999 | -0.025863 | -0.00065152 | 0.065443 | 0.076808 | 0.00081172 | -0.0018586 | -0.0016022 | -0.04303 | 0.00015377 | 0.063324 | 0.060836 | -0.0067099 | 0.0037641 | -0.00010671 | -0.09613 | 62.59 | -59.8618 | 62.6953 | -59.697 | -60.0861 | -0.09613 | -0.11444 | 62.5992 | -59.7931 | 62.7274 | -59.8572 | -59.9442 | -59.7794 | -0.10529 | -0.10986 | -0.004578 | 0.05951 | 59.6603 | -0.32959 | 59.7656 | -0.22431 | -0.036621 | -0.10071 | 0.027466 | -0.10071 | -0.022888 | -0.18768 | 0.013733 | -0.15106 | 0.1648 | 122.5571 | -0.064087 | 122.5204 | 122.4518 | 122.3923 | 122.3465 | 122.3557 | -122.5616 | -122.493 | 122.4518 | 122.4838 | 59.6603 | 59.642
58.7656 | 122.7127 | -59.761 | 62.7274 | -0.10216 | -1.0718e-05 | 0.06288 | 0.076808 | -0.0019653 | -0.0018586 | 0.0013886 | -0.082703 | 0.00015377 | 0.06482 | 0.064253 | -0.0069235 | 0.0041913 | 0.0016021 | -0.10529 | 62.6175 | -59.8572 | 62.6862 | -59.7107 | -60.0952 | -0.11444 | -0.13733 | 62.6083 | -59.7931 | 62.7411 | -59.8389 | -59.9579 | -59.7931 | -0.096131 | -0.10986 | -0.041199 | 0.050354 | 59.6466 | -0.33417 | 59.7427 | -0.23804 | -0.032044 | -0.11902 | 0.013733 | -0.07782 | -0.032044 | -0.19684 | 0 | -0.1648 | 0.14648 | 122.5433 | -0.045776 | 122.5342 | 122.4747 | 122.4014 | 122.3785 | 122.3694 | -122.5845 | -122.5204 | 122.4472 | 122.5021 | 59.6558 | 59.6237
59.7656 | 122.7493 | -59.7382 | 62.709 | -0.086899 | -0.00022432 | 0.062453 | 0.074672 | -0.0013245 | -0.0022858 | -0.00010676 | -0.064392 | 0.00079477 | 0.063324 | 0.069808 | -0.0060691 | 0.0039777 | -0.0024567 | -0.09613 | 62.6129 | -59.8434 | 62.7182 | -59.7198 | -59.9167 | -0.045776 | -0.10071 | 62.5763 | -59.7977 | 62.7777 | -59.7748 | -59.8892 | -59.7519 | -0.10529 | -0.09613 | 0.009156 | 0.01831 | 59.6924 | -0.17853 | 59.7977 | -0.073242 | -0.059509 | -0.13275 | 0.068665 | -0.036621 | -0.013733 | -0.15106 | 0.045776 | -0.091553 | 0.1236 | 122.5616 | 0.022888 | 122.5754 | 122.4564 | 122.374 | 122.3511 | 122.3145 | -122.5525 | -122.5067 | 122.4564 | 122.5159 | 59.642 | 59.6375
60.7656 | 122.6852 | -59.7794 | 62.7365 | -0.041122 | 0.0012711 | 0.065016 | 0.077235 | -0.00046988 | 0.0002778 | 0.00074764 | -0.070496 | 0.0033582 | 0.064606 | 0.060836 | -0.0064963 | 0.0026959 | -0.00053411 | -0.07782 | 62.6404 | -59.8434 | 62.6816 | -59.7244 | -60.1227 | -0.11444 | -0.16937 | 62.6038 | -59.7931 | 62.709 | -59.8846 | -59.9945 | -59.8114 | -0.064087 | -0.09613 | -0.054931 | 0.054932 | 59.6649 | -0.34332 | 59.729 | -0.27924 | -0.013733 | -0.13275 | -0.027466 | -0.10529 | -0.032043 | -0.21515 | -0.01831 | -0.20142 | 0.11902 | 122.525 | -0.091553 | 122.5021 | 122.4838 | 122.3969 | 122.4197 | 122.3831 | -122.58 | -122.5296 | 122.4609 | 122.4884 | 59.7015 | 59.61
61.7656 | 122.6761 | -59.7885 | 62.7274 | -0.10216 | 0.0012711 | 0.066084 | 0.076808 | 0.00038452 | 0.000705 | -0.001175 | -0.067444 | -0.00070063 | 0.061615 | 0.062972 | -0.0045737 | 0.0014141 | 0.0016021 | -0.082397 | 62.645 | -59.848 | 62.6587 | -59.761 | -60.1318 | -0.11902 | -0.15106 | 62.6175 | -59.8206 | 62.6953 | -59.8755 | -59.9808 | -59.816 | -0.059509 | -0.082398 | -0.068665 | 0.027466 | 59.6695 | -0.34332 | 59.729 | -0.28381 | -0.032044 | -0.10986 | -0.032044 | -0.086975 | -0.027466 | -0.19226 | 0.004578 | -0.16022 | 0.086975 | 122.5067 | -0.054931 | 122.5159 | 122.493 | 122.4381 | 122.4335 | 122.406 | -122.5754 | -122.5479 | 122.4472 | 122.4838 | 59.7061 | 59.6375
62.7656 | 122.6898 | -59.8068 | 62.7136 | -0.048752 | -0.0015061 | 0.064375 | 0.074458 | 0.00038452 | -0.0001496 | -0.00032036 | -0.04303 | -0.00027343 | 0.066529 | 0.061049 | -0.0052145 | 0.0022687 | -0.00010671 | -0.10071 | 62.6358 | -59.8572 | 62.677 | -59.7198 | -60.1227 | -0.11444 | -0.15564 | 62.6083 | -59.7977 | 62.709 | -59.8618 | -59.9808 | -59.8206 | -0.050354 | -0.07782 | -0.036621 | 0.086975 | 59.6924 | -0.31586 | 59.7427 | -0.2655 | 0.009156 | -0.10529 | -0.004578 | -0.054931 | -0.013733 | -0.17395 | -0.022889 | -0.18311 | 0.13733 | 122.5342 | -0.064087 | 122.5067 | 122.493 | 122.406 | 122.4426 | 122.4152 | -122.5708 | -122.5113 | 122.4838 | 122.5159 | 59.7061 | 59.6512
63.7656 | 122.6807 | -59.7656 | 62.7411 | -0.086899 | 0.0010575 | 0.063948 | 0.076808 | 0.00038452 | 0.0004914 | -0.001175 | -0.06134 | 0.0020764 | 0.065888 | 0.062758 | -0.0060691 | 0.0018413 | -0.0035247 | -0.086975 | 62.6221 | -59.8663 | 62.677 | -59.7382 | -60.1227 | -0.11444 | -0.16022 | 62.5992 | -59.816 | 62.709 | -59.8846 | -60.0037 | -59.816 | -0.10071 | -0.11902 | -0.064087 | 0.027466 | 59.6512 | -0.35706 | 59.7519 | -0.25635 | -0.050354 | -0.14191 | -0.032044 | -0.11902 | -0.050354 | -0.23804 | 0 | -0.18768 | 0.12817 | 122.5433 | -0.068665 | 122.525 | 122.4884 | 122.4152 | 122.3877 | 122.3648 | -122.6074 | -122.5571 | 122.4426 | 122.4747 | 59.6786 | 59.6054
64.7656 | 122.6669 | -59.7931 | 62.7182 | -0.079269 | 0.0025529 | 0.063307 | 0.076808 | 0.0040161 | 6.4004e-05 | 0.00010684 | -0.06134 | 0.00079477 | 0.064179 | 0.067458 | -0.0039327 | 0.0033367 | -0.00053411 | -0.091553 | 62.6312 | -59.8526 | 62.6816 | -59.7565 | -60.1318 | -0.12817 | -0.15106 | 62.6038 | -59.7977 | 62.6953 | -59.8846 | -59.9991 | -59.8068 | -0.059509 | -0.086975 | -0.036621 | 0.036621 | 59.6649 | -0.33875 | 59.7244 | -0.27924 | -0.004577 | -0.11444 | -0.022889 | -0.091553 | -0.013733 | -0.20599 | -0.009156 | -0.20142 | 0.09613 | 122.5342 | -0.086976 | 122.493 | 122.4838 | 122.4014 | 122.4243 | 122.3969 | -122.5708 | -122.5159 | 122.4747 | 122.4884 | 59.7015 | 59.642
65.7656 | 122.6303 | -59.7702 | 62.7502 | -0.10216 | -0.00022432 | 0.063734 | 0.075954 | 0.0040161 | -0.0014312 | 0.00010684 | -0.073547 | -0.00070063 | 0.065674 | 0.06169 | -0.0062827 | 0.0026959 | 0.0011749 | -0.064087 | 62.6312 | -59.8434 | 62.7045 | -59.7244 | -60.1089 | -0.10071 | -0.15564 | 62.6266 | -59.8022 | 62.6678 | -59.8892 | -60.0174 | -59.8434 | -0.073242 | -0.11902 | -0.045776 | 0.045777 | 59.6695 | -0.33874 | 59.7427 | -0.2655 | -0.032043 | -0.1236 | -0.082397 | -0.11902 | -0.073242 | -0.24719 | -0.041199 | -0.21515 | 0.11902 | 122.5479 | -0.086975 | 122.4701 | 122.4747 | 122.4289 | 122.4014 | 122.3969 | -122.5937 | -122.5525 | 122.4747 | 122.4381 | 59.7061 | 59.6146
66.7656 | 122.6669 | -59.7794 | 62.7502 | -0.079269 | 0.0021255 | 0.063948 | 0.077449 | 0.00059812 | 0.0009186 | -0.0018158 | -0.058289 | 0.001222 | 0.065888 | 0.06874 | -0.0062827 | 0.0024823 | 0.00074769 | -0.10986 | 62.6358 | -59.8663 | 62.6678 | -59.7382 | -60.1181 | -0.11902 | -0.16022 | 62.6358 | -59.8022 | 62.7045 | -59.8801 | -59.9808 | -59.816 | -0.086975 | -0.11444 | -0.082397 | 0.041199 | 59.6603 | -0.33874 | 59.7473 | -0.25177 | -0.022888 | -0.11444 | -0.045776 | -0.10071 | -0.036621 | -0.20142 | -0.013733 | -0.17853 | 0.12817 | 122.5342 | -0.07782 | 122.5067 | 122.5021 | 122.438 | 122.4152 | 122.4152 | -122.6166 | -122.5525 | 122.4472 | 122.4838 | 59.6695 | 59.6191
67.7656 | 122.6669 | -59.7702 | 62.7502 | -0.086899 | -0.00043792 | 0.064375 | 0.077235 | 0.00017092 | 0.0009186 | -0.00096136 | -0.036926 | 0.0010084 | 0.06482 | 0.071089 | -0.0056417 | 0.0026959 | 0.0035247 | -0.045776 | 62.645 | -59.8297 | 62.709 | -59.6649 | -60.0632 | -0.073242 | -0.07782 | 62.6312 | -59.7702 | 62.7045 | -59.8389 | -59.9716 | -59.8114 | -0.059509 | -0.10529 | -0.041199 | 0.10529 | 59.697 | -0.29297 | 59.7565 | -0.23346 | 0 | -0.11902 | -0.045776 | -0.068664 | -0.041198 | -0.20142 | -0.041198 | -0.20142 | 0.16479 | 122.5388 | -0.068664 | 122.4747 | 122.4747 | 122.4014 | 122.4152 | 122.4014 | -122.58 | -122.5204 | 122.4792 | 122.4747 | 59.7244 | 59.6924
68.7656 | 122.6761 | -59.761 | 62.7457 | -0.056381 | 0.0025529 | 0.063521 | 0.078517 | 0.0035889 | -0.0007904 | -0.00010676 | -0.04303 | -5.9826e-05 | 0.06482 | 0.061904 | -0.0064963 | 0.0035503 | 0.0043793 | -0.022888 | 62.6129 | -59.8343 | 62.7457 | -59.6512 | -60.0494 | -0.041199 | -0.054932 | 62.6038 | -59.7794 | 62.7228 | -59.8206 | -59.9579 | -59.8022 | -0.073243 | -0.13275 | 0 | 0.10986 | 59.7198 | -0.28839 | 59.7931 | -0.21515 | -0.018311 | -0.14191 | -0.022889 | -0.05951 | -0.041199 | -0.19684 | -0.022888 | -0.17853 | 0.18311 | 122.58 | -0.041199 | 122.5021 | 122.4472 | 122.3831 | 122.374 | 122.3648 | -122.58 | -122.525 | 122.5067 | 122.4838 | 59.7382 | 59.7061
69.7656 | 122.6715 | -59.7702 | 62.7457 | -0.041122 | 0.0019119 | 0.063521 | 0.07809 | 0.0014527 | 0.0002778 | -0.002243 | -0.024719 | 0.00036737 | 0.066101 | 0.064253 | -0.0039327 | 0.0016277 | -0.0039521 | -0.059509 | 62.6587 | -59.8251 | 62.6999 | -59.7061 | -60.0723 | -0.082397 | -0.1236 | 62.6129 | -59.8022 | 62.6907 | -59.8846 | -60.0037 | -59.816 | -0.054931 | -0.086976 | -0.045777 | 0.064087 | 59.6878 | -0.30212 | 59.7427 | -0.24719 | -0.032043 | -0.13275 | -0.054932 | -0.11444 | -0.045776 | -0.23346 | -0.013733 | -0.20142 | 0.11902 | 122.525 | -0.082398 | 122.493 | 122.4838 | 122.4152 | 122.4289 | 122.3831 | -122.5708 | -122.5479 | 122.4701 | 122.4609 | 59.7107 | 59.6466
70.7656 | 122.6761 | -59.7656 | 62.7548 | -0.048752 | 0.00084388 | 0.065016 | 0.076808 | -0.00025628 | 0.0011322 | 0.0020294 | -0.036926 | 0.0031446 | 0.062683 | 0.062545 | -0.0064963 | 0.0018413 | 0.0039521 | -0.036621 | 62.6495 | -59.8251 | 62.709 | -59.6741 | -60.0723 | -0.068665 | -0.09613 | 62.6129 | -59.7839 | 62.709 | -59.8572 | -59.9854 | -59.8022 | -0.059509 | -0.10529 | -0.045777 | 0.091553 | 59.697 | -0.3067 | 59.7565 | -0.24719 | -0.018311 | -0.14191 | -0.045777 | -0.091553 | -0.036621 | -0.21973 | -0.01831 | -0.20142 | 0.15106 | 122.5342 | -0.073242 | 122.493 | 122.4747 | 122.3969 | 122.4152 | 122.3785 | -122.58 | -122.5388 | 122.4747 | 122.4747 | 59.729 | 59.6695
71.7656 | 122.6532 | -59.7473 | 62.7365 | -0.086899 | 0.0038345 | 0.061812 | 0.076167 | 0.0018799 | -0.0012176 | 0.00096124 | -0.039978 | 0.0025036 | 0.065674 | 0.062545 | -0.0047873 | 0.00077333 | -0.0030975 | -0.027466 | 62.6633 | -59.8434 | 62.7274 | -59.6603 | -60.0677 | -0.059509 | -0.059509 | 62.5992 | -59.7794 | 62.7228 | -59.8343 | -59.9762 | -59.7977 | -0.096131 | -0.073242 | -0.009155 | 0.086975 | 59.6878 | -0.32043 | 59.7839 | -0.2243 | -0.032044 | -0.13733 | -0.013733 | -0.086976 | -0.050354 | -0.22888 | -0.01831 | -0.19684 | 0.18311 | 122.5708 | -0.054932 | 122.5021 | 122.5067 | 122.3785 | 122.4106 | 122.3465 | -122.58 | -122.5159 | 122.4747 | 122.4701 | 59.7198 | 59.6878
72.7656 | 122.6761 | -59.7427 | 62.7594 | -0.025863 | 0.0010575 | 0.063734 | 0.075099 | 0.0010253 | -0.0005768 | -0.003952 | -0.046081 | 0.00015377 | 0.065247 | 0.061049 | -0.0058553 | 0.00077333 | 0.0035247 | -0.022888 | 62.6633 | -59.8434 | 62.7319 | -59.6603 | -60.0586 | -0.059509 | -0.027466 | 62.6312 | -59.7885 | 62.7319 | -59.8251 | -59.9579 | -59.7748 | -0.10071 | -0.09613 | -0.027465 | 0.082398 | 59.6832 | -0.31586 | 59.7839 | -0.21515 | -0.045776 | -0.12817 | -0.027465 | -0.082397 | -0.032043 | -0.21515 | 0.013733 | -0.16937 | 0.18311 | 122.5754 | -0.036621 | 122.5204 | 122.5067 | 122.4197 | 122.406 | 122.374 | -122.6028 | -122.5479 | 122.4747 | 122.4747 | 59.7198 | 59.7153
73.7656 | 122.6761 | -59.7656 | 62.7548 | -0.086899 | 0.0029801 | 0.064375 | 0.079799 | 0.0010253 | -0.0012176 | 0.0018158 | -0.021667 | 0.00015377 | 0.06482 | 0.06639 | -0.0067099 | 0.0016277 | -0.00032051 | -0.041199 | 62.6724 | -59.8663 | 62.6907 | -59.7107 | -60.0769 | -0.091553 | -0.13275 | 62.6221 | -59.7977 | 62.6907 | -59.8938 | -59.9854 | -59.8114 | -0.10071 | -0.082398 | -0.064087 | 0.054932 | 59.6741 | -0.31128 | 59.7748 | -0.21057 | -0.032043 | -0.13275 | -0.064087 | -0.12817 | -0.045776 | -0.21973 | -0.013733 | -0.18768 | 0.15564 | 122.5571 | -0.096131 | 122.4884 | 122.5388 | 122.4197 | 122.438 | 122.3877 | -122.6212 | -122.5525 | 122.4564 | 122.4564 | 59.7244 | 59.6329
74.7656 | 122.6944 | -59.7656 | 62.7457 | -0.094528 | -0.00065152 | 0.063307 | 0.075954 | -0.0043151 | 0.000705 | 0.0018158 | -0.0064086 | 0.0018628 | 0.06482 | 0.063826 | -0.0071371 | 0.0016277 | -0.0011749 | 0 | 62.6495 | -59.8251 | 62.7502 | -59.6329 | -60.022 | -0.022888 | -0.009155 | 62.6083 | -59.7565 | 62.7365 | -59.816 | -59.935 | -59.7748 | -0.059509 | -0.096131 | 0.004577 | 0.13275 | 59.7427 | -0.25635 | 59.8022 | -0.19684 | 0.009155 | -0.13733 | -0.009156 | -0.050354 | -0.009155 | -0.16937 | -0.01831 | -0.17853 | 0.19226 | 122.5754 | -0.059509 | 122.493 | 122.4747 | 122.3648 | 122.4152 | 122.374 | -122.5708 | -122.5021 | 122.5159 | 122.5021 | 59.7656 | 59.7565
75.7656 | 122.7127 | -59.7519 | 62.7411 | -0.06401 | 0.0014847 | 0.063521 | 0.077022 | 0.0018799 | -0.002713 | -0.00032036 | -0.036926 | -0.00048703 | 0.06482 | 0.058913 | -0.0062827 | 0.0029095 | 0.0013885 | 0 | 62.6266 | -59.8114 | 62.7594 | -59.6466 | -60.0403 | -0.004578 | 0.004578 | 62.6266 | -59.8068 | 62.7457 | -59.7931 | -59.9167 | -59.7702 | -0.059509 | -0.11444 | 0.01831 | 0.10529 | 59.7473 | -0.28839 | 59.8068 | -0.22888 | -0.054932 | -0.11444 | 0.004578 | -0.041199 | -0.018311 | -0.1648 | 0.036621 | -0.10986 | 0.16479 | 122.5708 | 0.013733 | 122.5525 | 122.438 | 122.4335 | 122.3785 | 122.3785 | -122.5525 | -122.5479 | 122.5113 | 122.4976 | 59.7519 | 59.7565
76.7656 | 122.6715 | -59.7656 | 62.7548 | -0.086899 | -0.00086512 | 0.065657 | 0.076808 | 0.0040161 | 6.4004e-05 | -0.002884 | -0.036926 | 0.0010084 | 0.064606 | 0.062545 | -0.0062827 | 0.0026959 | 0.0016021 | -0.032043 | 62.6312 | -59.8389 | 62.7319 | -59.6695 | -60.0815 | -0.059509 | -0.073242 | 62.6175 | -59.7839 | 62.6999 | -59.8526 | -59.9579 | -59.7977 | -0.073242 | -0.1236 | -0.022888 | 0.09613 | 59.7061 | -0.31586 | 59.7794 | -0.24262 | -0.018311 | -0.13733 | -0.054932 | -0.086975 | -0.032043 | -0.19226 | -0.013732 | -0.17395 | 0.16937 | 122.5708 | -0.068664 | 122.4838 | 122.4701 | 122.4014 | 122.3969 | 122.3831 | -122.5937 | -122.5388 | 122.4976 | 122.4655 | 59.7336 | 59.6924
77.7656 | 122.6532 | -59.761 | 62.7457 | -0.048752 | 0.00041648 | 0.064375 | 0.076381 | 0.0010253 | -0.0020722 | -0.00053396 | -0.058289 | -0.0013416 | 0.06546 | 0.062545 | -0.0045737 | 0.0026959 | 0.00053409 | -0.027466 | 62.6358 | -59.8389 | 62.7182 | -59.6832 | -60.0494 | -0.064087 | -0.054932 | 62.6266 | -59.7702 | 62.709 | -59.8526 | -59.9762 | -59.8114 | -0.07782 | -0.10986 | -0.027466 | 0.077819 | 59.697 | -0.28839 | 59.7748 | -0.21057 | -0.009156 | -0.11902 | -0.036622 | -0.091553 | -0.050354 | -0.21515 | -0.041198 | -0.20599 | 0.15564 | 122.5571 | -0.082397 | 122.4792 | 122.4747 | 122.3969 | 122.3969 | 122.3877 | -122.5845 | -122.5159 | 122.4792 | 122.4701 | 59.7336 | 59.7061
78.7656 | 122.6715 | -59.7702 | 62.7457 | -0.13267 | 0.00084388 | 0.06288 | 0.07809 | 0.0010253 | -0.0005768 | 0.0018158 | -0.021667 | 0.0010084 | 0.066956 | 0.063399 | -0.0062827 | 0.0031231 | 0.00096129 | -0.022888 | 62.645 | -59.8297 | 62.7274 | -59.6695 | -60.0403 | -0.036621 | -0.054932 | 62.6083 | -59.7931 | 62.7136 | -59.8434 | -59.9533 | -59.8022 | -0.059509 | -0.10071 | -0.018311 | 0.10071 | 59.7336 | -0.27008 | 59.7931 | -0.21057 | -0.022888 | -0.13733 | -0.032044 | -0.073242 | -0.032043 | -0.1831 | -0.009155 | -0.16022 | 0.16022 | 122.5571 | -0.050354 | 122.5067 | 122.4747 | 122.4014 | 122.4152 | 122.3785 | -122.5754 | -122.5388 | 122.4976 | 122.4838 | 59.7473 | 59.7153
79.7656 | 122.6807 | -59.7473 | 62.7502 | -0.056381 | 0.0010575 | 0.064589 | 0.076594 | 0.0016663 | -0.0016448 | 0.0013886 | -0.024719 | 0.001222 | 0.064179 | 0.060622 | -0.0041465 | 0.0029095 | 0.00074769 | -0.032043 | 62.6312 | -59.8206 | 62.7411 | -59.6741 | -60.0586 | -0.022888 | -0.045776 | 62.6266 | -59.7885 | 62.7136 | -59.8389 | -59.9442 | -59.761 | -0.073243 | -0.11902 | -0.009155 | 0.073242 | 59.7244 | -0.31128 | 59.7977 | -0.23804 | -0.041199 | -0.1236 | -0.036621 | -0.091553 | -0.013733 | -0.19684 | 0.027466 | -0.15564 | 0.14648 | 122.5616 | -0.050354 | 122.5021 | 122.4518 | 122.4152 | 122.3785 | 122.374 | -122.5708 | -122.5388 | 122.4884 | 122.4609 | 59.7153 | 59.7015
80.7656 | 122.6395 | -59.7656 | 62.7502 | -0.056381 | 0.0012711 | 0.065871 | 0.078303 | 0.00081172 | -0.0016448 | 0.0026702 | -0.024719 | -0.0017688 | 0.064179 | 0.057204 | -0.0056417 | 0.0024823 | 0.0056611 | -0.064087 | 62.6312 | -59.8572 | 62.6862 | -59.729 | -60.0998 | -0.09613 | -0.16022 | 62.6129 | -59.7839 | 62.6633 | -59.9075 | -60.0128 | -59.8343 | -0.091553 | -0.11902 | -0.064087 | 0.036621 | 59.6695 | -0.33417 | 59.761 | -0.24261 | -0.018311 | -0.13733 | -0.086975 | -0.14191 | -0.068665 | -0.24719 | -0.050354 | -0.22888 | 0.12817 | 122.5433 | -0.1236 | 122.4472 | 122.4884 | 122.3969 | 122.3969 | 122.3785 | -122.6074 | -122.5342 | 122.4518 | 122.4289 | 59.7015 | 59.6054
81.7656 | 122.6715 | -59.7427 | 62.7274 | -0.086899 | -0.00022432 | 0.063307 | 0.076808 | 0.0027343 | -0.0022858 | 0.00053404 | -0.030823 | 0.0033582 | 0.067597 | 0.057418 | -0.0075643 | 0.0012005 | 0.00053409 | -0.013733 | 62.6358 | -59.8114 | 62.7228 | -59.6649 | -60.0403 | -0.045776 | -0.054932 | 62.6312 | -59.7931 | 62.7228 | -59.8434 | -59.9808 | -59.7931 | -0.068664 | -0.091553 | -0.004578 | 0.07782 | 59.697 | -0.29755 | 59.7656 | -0.22888 | -0.050354 | -0.09613 | -0.004578 | -0.10071 | -0.050354 | -0.23804 | 0 | -0.18768 | 0.14648 | 122.5342 | -0.050354 | 122.5159 | 122.4472 | 122.4243 | 122.3785 | 122.374 | -122.5388 | -122.5204 | 122.4655 | 122.4655 | 59.729 | 59.6878
82.7656 | 122.7219 | -59.7473 | 62.7365 | -0.06401 | 0.0034073 | 0.062666 | 0.077876 | -4.2682e-05 | -0.0018586 | -0.0013886 | -0.027771 | -0.00027343 | 0.064606 | 0.062331 | -0.0064963 | 0.0022687 | 0.0016021 | -0.018311 | 62.6541 | -59.8206 | 62.7274 | -59.6603 | -60.0632 | -0.041199 | -0.054932 | 62.6221 | -59.7931 | 62.7045 | -59.8114 | -59.9716 | -59.7931 | -0.073243 | -0.082397 | -0.009155 | 0.086975 | 59.7061 | -0.31586 | 59.7794 | -0.24261 | -0.045777 | -0.11444 | -0.032043 | -0.064087 | -0.045777 | -0.2243 | 0 | -0.17853 | 0.16022 | 122.5479 | -0.01831 | 122.4976 | 122.4747 | 122.4152 | 122.4014 | 122.3694 | -122.5571 | -122.5296 | 122.4747 | 122.4518 | 59.729 | 59.6924
83.7656 | 122.6532 | -59.7702 | 62.7411 | -0.06401 | 0.0012711 | 0.063734 | 0.076381 | 0.0014527 | -0.0022858 | 0.001175 | -0.024719 | -5.9826e-05 | 0.066315 | 0.061263 | -0.0062827 | 0.0026959 | -0.0060883 | -0.059509 | 62.6587 | -59.848 | 62.6816 | -59.7336 | -60.1089 | -0.10529 | -0.16022 | 62.6312 | -59.8022 | 62.6724 | -59.903 | -60.0311 | -59.8343 | -0.077819 | -0.082398 | -0.059509 | 0.036621 | 59.6649 | -0.33874 | 59.7427 | -0.26093 | -0.032043 | -0.10986 | -0.068665 | -0.13275 | -0.064087 | -0.26093 | -0.032044 | -0.22888 | 0.11444 | 122.5296 | -0.10071 | 122.4747 | 122.5067 | 122.4335 | 122.4289 | 122.4014 | -122.5891 | -122.5433 | 122.4518 | 122.4426 | 59.7107 | 59.61
84.7656 | 122.6669 | -59.7839 | 62.7457 | -0.094528 | 0.0010575 | 0.063948 | 0.077022 | 0.0014527 | -0.0024994 | 0.00074764 | -0.021667 | 0.0018628 | 0.066315 | 0.058272 | -0.0067099 | -0.00050847 | 0.00010689 | -0.082397 | 62.645 | -59.848 | 62.6816 | -59.7336 | -60.1227 | -0.10529 | -0.16937 | 62.6038 | -59.8251 | 62.6587 | -59.903 | -60.0082 | -59.8434 | -0.064086 | -0.10071 | -0.064087 | 0.050354 | 59.6786 | -0.33875 | 59.7427 | -0.27466 | -0.041198 | -0.14191 | -0.086976 | -0.11902 | -0.059509 | -0.2243 | -0.018311 | -0.18311 | 0.11444 | 122.5296 | -0.07782 | 122.4838 | 122.493 | 122.4289 | 122.4289 | 122.3877 | -122.5937 | -122.5708 | 122.4655 | 122.4426 | 59.7015 | 59.6146
85.7656 | 122.6303 | -59.7565 | 62.7457 | -0.025863 | 0.00020288 | 0.063948 | 0.07574 | 0.0029479 | -0.0001496 | -0.0030976 | -0.033874 | -0.001128 | 0.066101 | 0.065535 | -0.0075643 | 0.00098693 | -0.0022431 | -0.068665 | 62.6404 | -59.848 | 62.6907 | -59.7473 | -60.1089 | -0.09613 | -0.16022 | 62.6129 | -59.7977 | 62.6587 | -59.8984 | -60.0266 | -59.8389 | -0.091552 | -0.10529 | -0.054932 | 0.009156 | 59.6603 | -0.35248 | 59.7519 | -0.26093 | -0.041198 | -0.13275 | -0.086976 | -0.14191 | -0.082397 | -0.27008 | -0.041199 | -0.22888 | 0.10071 | 122.5388 | -0.10071 | 122.4564 | 122.4884 | 122.4106 | 122.3969 | 122.3694 | -122.5937 | -122.5433 | 122.4472 | 122.4152 | 59.6878 | 59.5963
86.7656 | 122.6349 | -59.761 | 62.7319 | -0.07164 | 0.0016983 | 0.063948 | 0.078303 | 0.0023071 | -0.0022858 | -0.00074776 | -0.030823 | -0.001128 | 0.063965 | 0.059767 | -0.0082053 | 0.0012005 | -0.00096131 | -0.068665 | 62.6358 | -59.8526 | 62.6816 | -59.7244 | -60.1089 | -0.086975 | -0.16022 | 62.6358 | -59.7931 | 62.6724 | -59.8984 | -60.0311 | -59.8343 | -0.091553 | -0.096131 | -0.050354 | 0.036621 | 59.6741 | -0.3479 | 59.7656 | -0.25635 | -0.032044 | -0.096131 | -0.05951 | -0.13733 | -0.073243 | -0.27008 | -0.041199 | -0.23804 | 0.12817 | 122.5342 | -0.10529 | 122.4655 | 122.4884 | 122.4289 | 122.3969 | 122.3969 | -122.5845 | -122.525 | 122.4426 | 122.4335 | 59.6924 | 59.6008
87.7656 | 122.6898 | -59.7885 | 62.7228 | -0.07164 | 0.0019119 | 0.062666 | 0.076808 | -4.2682e-05 | -0.0024994 | -0.00032036 | -0.012512 | -0.00027343 | 0.066956 | 0.060836 | -0.0052145 | 0.0016277 | 0.0026703 | -0.086975 | 62.6312 | -59.8709 | 62.6678 | -59.7382 | -60.1089 | -0.11902 | -0.15106 | 62.6312 | -59.7977 | 62.6999 | -59.8663 | -59.9854 | -59.816 | -0.082398 | -0.091552 | -0.054931 | 0.050354 | 59.6695 | -0.32043 | 59.7519 | -0.23804 | -0.009155 | -0.091552 | -0.022888 | -0.07782 | -0.027466 | -0.19684 | -0.018311 | -0.18768 | 0.13275 | 122.5388 | -0.068665 | 122.4976 | 122.5021 | 122.4289 | 122.4197 | 122.4197 | -122.5937 | -122.5204 | 122.4564 | 122.4884 | 59.7015 | 59.6375
88.7656 | 122.6532 | -59.7702 | 62.7457 | -0.06401 | 0.00084388 | 0.065871 | 0.076808 | -0.0026063 | -0.0003632 | 0.00010684 | -0.030823 | 0.00079477 | 0.063538 | 0.065322 | -0.0079917 | 0.00034613 | 0.0018159 | -0.068665 | 62.6404 | -59.8526 | 62.6953 | -59.7473 | -60.0906 | -0.09613 | -0.14648 | 62.6404 | -59.7885 | 62.6678 | -59.9075 | -60.0082 | -59.8297 | -0.082397 | -0.10529 | -0.050355 | 0.022889 | 59.6741 | -0.32043 | 59.7565 | -0.23804 | -0.01831 | -0.10529 | -0.07782 | -0.13733 | -0.059509 | -0.23804 | -0.041199 | -0.21973 | 0.10529 | 122.5479 | -0.11902 | 122.4564 | 122.493 | 122.4289 | 122.4106 | 122.4106 | -122.5983 | -122.5342 | 122.4655 | 122.4381 | 59.7015 | 59.6237
89.7656 | 122.6486 | -59.7748 | 62.7365 | -0.07164 | 0.0010575 | 0.061812 | 0.076381 | 0.0012391 | 6.4004e-05 | 0.00074764 | -0.015564 | 0.00036737 | 0.065247 | 0.065322 | -0.0054281 | 0.0026959 | -0.0013885 | -0.059509 | 62.645 | -59.8114 | 62.7136 | -59.7244 | -60.0998 | -0.09613 | -0.15106 | 62.6312 | -59.8068 | 62.6724 | -59.8938 | -60.0128 | -59.8343 | -0.036621 | -0.091553 | -0.022888 | 0.050354 | 59.6786 | -0.32501 | 59.7153 | -0.28839 | -0.032044 | -0.10529 | -0.064087 | -0.11902 | -0.05951 | -0.23804 | -0.027466 | -0.20599 | 0.086975 | 122.525 | -0.086975 | 122.4792 | 122.4564 | 122.4381 | 122.4197 | 122.406 | -122.5479 | -122.5433 | 122.4884 | 122.4472 | 59.7153 | 59.6237
90.7656 | 122.6944 | -59.7748 | 62.7457 | -0.056381 | 0.0016983 | 0.063094 | 0.076167 | 0.0038025 | -0.0020722 | 0.0024566 | -0.021667 | -5.9826e-05 | 0.06546 | 0.066176 | -0.0062827 | 0.0035503 | 0.00074769 | -0.086975 | 62.6495 | -59.8389 | 62.6816 | -59.7427 | -60.1181 | -0.11444 | -0.16479 | 62.6083 | -59.8022 | 62.6907 | -59.8709 | -59.9899 | -59.8297 | -0.064087 | -0.096131 | -0.064087 | 0.032043 | 59.6603 | -0.34332 | 59.7244 | -0.27924 | -0.027466 | -0.13733 | -0.054932 | -0.096131 | -0.054932 | -0.21515 | -0.027466 | -0.18768 | 0.09613 | 122.5204 | -0.068665 | 122.493 | 122.4884 | 122.4106 | 122.4243 | 122.3831 | -122.5845 | -122.5479 | 122.4564 | 122.4655 | 59.6878 | 59.61
91.7656 | 122.6852 | -59.7839 | 62.7228 | -0.07164 | 0.0019119 | 0.06288 | 0.077022 | -0.00046988 | -0.0014312 | -0.00010676 | -0.030823 | 0.001222 | 0.06546 | 0.058699 | -0.0056417 | 0.0012005 | 0.0013885 | -0.086975 | 62.6358 | -59.8434 | 62.6724 | -59.7427 | -60.1273 | -0.10529 | -0.15106 | 62.6083 | -59.8022 | 62.6862 | -59.8572 | -60.0037 | -59.8068 | -0.059509 | -0.086975 | -0.050354 | 0.041199 | 59.6786 | -0.34332 | 59.7382 | -0.28381 | -0.01831 | -0.11444 | -0.036621 | -0.073242 | -0.022888 | -0.21973 | -0.004578 | -0.20142 | 0.10071 | 122.5159 | -0.054932 | 122.4884 | 122.4792 | 122.4106 | 122.4197 | 122.3923 | -122.5662 | -122.525 | 122.4564 | 122.4701 | 59.697 | 59.6329
92.7656 | 122.6532 | -59.7885 | 62.764 | -0.07164 | 0.00084388 | 0.064162 | 0.076381 | 0.0014527 | -0.0001496 | -0.00096136 | -0.030823 | -0.00027343 | 0.065033 | 0.062758 | -0.0075643 | 0.0029095 | -0.00053411 | -0.086975 | 62.645 | -59.8618 | 62.6633 | -59.729 | -60.1227 | -0.12817 | -0.16022 | 62.6312 | -59.8114 | 62.6907 | -59.8755 | -59.9945 | -59.8206 | -0.073242 | -0.11902 | -0.10071 | 0.059509 | 59.6603 | -0.33417 | 59.7336 | -0.26093 | -0.022888 | -0.13275 | -0.073242 | -0.086975 | -0.032044 | -0.20599 | -0.009156 | -0.18311 | 0.13275 | 122.525 | -0.064087 | 122.5021 | 122.5067 | 122.4426 | 122.4335 | 122.4197 | -122.6257 | -122.5754 | 122.4518 | 122.4792 | 59.7015 | 59.6283
93.7656 | 122.644 | -59.7977 | 62.7365 | -0.07164 | -1.0718e-05 | 0.063521 | 0.079799 | 0.0010253 | -0.0003632 | -0.0043792 | -0.018616 | 0.0016492 | 0.066956 | 0.065322 | -0.0052145 | 0.0026959 | 0.0013885 | -0.082397 | 62.645 | -59.8343 | 62.6587 | -59.7336 | -60.1181 | -0.13275 | -0.16479 | 62.6312 | -59.816 | 62.6862 | -59.8709 | -60.0037 | -59.816 | -0.036622 | -0.091553 | -0.07782 | 0.064086 | 59.6649 | -0.32043 | 59.7015 | -0.28381 | -0.018311 | -0.10529 | -0.050354 | -0.073243 | -0.018311 | -0.20599 | 0 | -0.18768 | 0.10071 | 122.493 | -0.054932 | 122.5021 | 122.4792 | 122.4472 | 122.4426 | 122.4289 | -122.5708 | -122.5525 | 122.4564 | 122.4838 | 59.7153 | 59.6329
94.7656 | 122.7402 | -59.7427 | 62.7319 | -0.094528 | 0.00084388 | 0.063307 | 0.077876 | 0.00038452 | 0.0009186 | 0.001175 | -0.0094604 | -0.00027343 | 0.063965 | 0.060836 | -0.0062827 | 0.0029095 | -0.0028839 | -0.10071 | 62.6312 | -59.8343 | 62.6953 | -59.7107 | -60.0952 | -0.10071 | -0.13275 | 62.5671 | -59.8022 | 62.7136 | -59.8022 | -59.9579 | -59.761 | -0.091553 | -0.10071 | -0.036622 | 0.032044 | 59.642 | -0.35248 | 59.7336 | -0.26093 | -0.059509 | -0.1648 | -0.018311 | -0.059509 | -0.01831 | -0.21515 | 0.041199 | -0.15564 | 0.1236 | 122.5296 | 0 | 122.5159 | 122.4655 | 122.3694 | 122.374 | 122.3099 | -122.5662 | -122.5342 | 122.438 | 122.4564 | 59.642 | 59.61
95.7656 | 122.6624 | -59.7748 | 62.7319 | -0.079269 | 0.0021255 | 0.065443 | 0.077663 | 0.0018799 | -0.0003632 | 0.001175 | -0.027771 | -5.9826e-05 | 0.064179 | 0.065108 | -0.0064963 | 0.0020551 | -0.00010671 | -0.086975 | 62.6358 | -59.8572 | 62.6724 | -59.7519 | -60.1273 | -0.11444 | -0.15106 | 62.5992 | -59.8022 | 62.6907 | -59.8755 | -59.9945 | -59.8022 | -0.082398 | -0.096131 | -0.05951 | 0.022888 | 59.6603 | -0.35248 | 59.7427 | -0.27008 | -0.027466 | -0.13275 | -0.041199 | -0.10071 | -0.027466 | -0.21973 | 0 | -0.19226 | 0.10529 | 122.5296 | -0.073242 | 122.493 | 122.493 | 122.4014 | 122.4106 | 122.374 | -122.5891 | -122.5342 | 122.4472 | 122.4655 | 59.6878 | 59.6237
96.7656 | 122.7448 | -59.7565 | 62.7228 | -0.041122 | 0.00020288 | 0.06523 | 0.077663 | -0.00046988 | -0.0014312 | 0.0024566 | -0.015564 | 0.0018628 | 0.064606 | 0.060195 | -0.0060691 | 0.0026959 | 0.0013885 | -0.09613 | 62.6358 | -59.8022 | 62.6953 | -59.697 | -60.0998 | -0.10986 | -0.13275 | 62.5809 | -59.7977 | 62.7274 | -59.8251 | -59.9533 | -59.7839 | -0.045776 | -0.086975 | -0.027466 | 0.05951 | 59.6466 | -0.34332 | 59.6924 | -0.29755 | -0.041198 | -0.14191 | 0.004578 | -0.068664 | -0.027466 | -0.19684 | 0.013732 | -0.15564 | 0.10529 | 122.4976 | -0.027466 | 122.525 | 122.438 | 122.3785 | 122.3923 | 122.3373 | -122.525 | -122.5204 | 122.4518 | 122.4838 | 59.6603 | 59.6237
97.7656 | 122.699 | -59.7519 | 62.7228 | -0.033493 | 0.0010575 | 0.064375 | 0.079158 | -0.0028199 | 0.0002778 | -0.00010676 | -0.033874 | 0.0010084 | 0.068024 | 0.058913 | -0.0069235 | 0.0014141 | 0.0020295 | -0.10986 | 62.6312 | -59.8572 | 62.6953 | -59.7061 | -60.0861 | -0.09613 | -0.1236 | 62.6129 | -59.8022 | 62.7457 | -59.8343 | -59.9396 | -59.7702 | -0.10529 | -0.091552 | -0.027466 | 0.045776 | 59.6558 | -0.33417 | 59.761 | -0.22888 | -0.050354 | -0.10986 | 0.022889 | -0.082398 | -0.018311 | -0.18768 | 0.032043 | -0.13733 | 0.15106 | 122.5525 | -0.032044 | 122.5479 | 122.4884 | 122.4152 | 122.3831 | 122.3648 | -122.58 | -122.525 | 122.4472 | 122.4976 | 59.642 | 59.6283
98.7656 | 122.7081 | -59.7519 | 62.7228 | -0.14793 | 0.00063028 | 0.061812 | 0.078944 | -0.0017517 | -0.0031402 | -0.00010676 | -0.018616 | 0.0016492 | 0.063538 | 0.061904 | -0.0082053 | -0.00029487 | 0.0024567 | -0.091553 | 62.6358 | -59.8389 | 62.6999 | -59.7244 | -60.0861 | -0.10529 | -0.1236 | 62.5946 | -59.8022 | 62.7228 | -59.8343 | -59.9396 | -59.7885 | -0.086975 | -0.086975 | -0.022888 | 0.027466 | 59.6466 | -0.33417 | 59.7336 | -0.24719 | -0.050354 | -0.12817 | 0 | -0.082398 | -0.036621 | -0.18768 | 0.013733 | -0.13733 | 0.11444 | 122.5388 | -0.032044 | 122.525 | 122.4747 | 122.3969 | 122.3877 | 122.3465 | -122.5616 | -122.525 | 122.4518 | 122.4747 | 59.6603 | 59.6283
99.7656 | 122.699 | -59.7519 | 62.7182 | -0.06401 | 0.0010575 | 0.065016 | 0.078517 | -0.0011109 | -0.0007904 | -0.0020294 | -0.030823 | 0.00058097 | 0.063324 | 0.057418 | -0.0075643 | 0.0014141 | 0.0039521 | -0.10071 | 62.6495 | -59.8572 | 62.6816 | -59.7107 | -60.1044 | -0.10071 | -0.1236 | 62.6175 | -59.8068 | 62.7228 | -59.8434 | -59.9487 | -59.7977 | -0.10529 | -0.068665 | -0.036621 | 0.041199 | 59.6512 | -0.35248 | 59.7565 | -0.24719 | -0.054932 | -0.10071 | 0.004577 | -0.091553 | -0.045776 | -0.19684 | 0.009156 | -0.14191 | 0.14648 | 122.5388 | -0.036621 | 122.5296 | 122.5067 | 122.4243 | 122.4014 | 122.3694 | -122.5754 | -122.525 | 122.4335 | 122.4747 | 59.6512 | 59.6283
100.7656 | 122.7768 | -59.7336 | 62.7182 | -0.10216 | 0.00063028 | 0.064375 | 0.078303 | 0.0042297 | 0.0009186 | -0.001175 | -0.0064086 | 0.00058097 | 0.064179 | 0.05934 | -0.0064963 | 0.0039777 | -0.0030975 | -0.073242 | 62.6358 | -59.8251 | 62.7548 | -59.6146 | -60.0174 | -0.054932 | -0.050354 | 62.5854 | -59.7839 | 62.7365 | -59.5642 | -59.7427 | -59.6649 | -0.091552 | -0.082398 | 0.036621 | 0.11902 | 59.6786 | -0.28381 | 59.7702 | -0.19226 | -0.050354 | -0.13275 | 0.01831 | 0.16937 | 0.068665 | -0.009155 | 0.11902 | 0.041199 | 0.21057 | 122.58 | 0.21973 | 122.5204 | 122.4609 | 122.3694 | 122.3694 | 122.319 | -122.5433 | -122.5021 | 122.4884 | 122.4701 | 59.6603 | 59.6832
101.7656 | 122.731 | -59.7748 | 62.6587 | -0.048752 | 0.00020288 | 0.067152 | 0.076594 | -0.0021789 | -0.0007904 | 0.0018158 | -0.015564 | 0.00058097 | 0.063965 | 0.069594 | -0.0056417 | 0.0026959 | -0.0020295 | -0.082397 | 62.6175 | -59.8251 | 62.7548 | -59.6375 | -60.0311 | -0.045776 | -0.059509 | 62.5763 | -59.7656 | 62.7869 | -59.7336 | -59.9075 | -59.8114 | -0.050354 | -0.041198 | 0.096131 | 0.13733 | 59.729 | -0.25635 | 59.7794 | -0.20599 | 0.009155 | -0.082397 | 0.12817 | 0.041198 | -0.036621 | -0.13275 | -0.045776 | -0.14191 | 0.18768 | 122.58 | 0.032043 | 122.5525 | 122.4426 | 122.3419 | 122.3923 | 122.3511 | -122.4838 | -122.4243 | 122.5296 | 122.5616 | 59.6924 | 59.7153
102.7656 | 122.7173 | -59.7473 | 62.7182 | -0.11742 | 0.00041648 | 0.062453 | 0.077235 | 0.00081172 | -0.0014312 | -0.00096136 | -0.070496 | 0.00058097 | 0.066315 | 0.070021 | -0.0084189 | 0.0014141 | -0.0013885 | -0.09613 | 62.6266 | -59.8343 | 62.6907 | -59.7153 | -60.1044 | -0.11902 | -0.13275 | 62.6221 | -59.8022 | 62.7182 | -59.8343 | -59.9533 | -59.7839 | -0.086976 | -0.091553 | -0.027466 | 0.032043 | 59.6283 | -0.35706 | 59.7153 | -0.27008 | -0.054932 | -0.096131 | 0 | -0.086976 | -0.036622 | -0.20599 | 0.01831 | -0.15106 | 0.11902 | 122.525 | -0.032044 | 122.5204 | 122.4609 | 122.4243 | 122.374 | 122.3694 | -122.5525 | -122.5204 | 122.438 | 122.4655 | 59.6512 | 59.6146
103.7656 | 122.699 | -59.7702 | 62.7182 | -0.06401 | 0.0016983 | 0.064803 | 0.075954 | 0.0010253 | 0.0013458 | -0.0018158 | -0.033874 | -0.00027343 | 0.064179 | 0.053572 | -0.0073507 | 0.0014141 | -0.00053411 | -0.10529 | 62.6404 | -59.8526 | 62.6816 | -59.7107 | -60.1044 | -0.11444 | -0.14648 | 62.59 | -59.8022 | 62.7319 | -59.8343 | -59.9579 | -59.7931 | -0.082397 | -0.07782 | -0.036621 | 0.05951 | 59.6558 | -0.33417 | 59.7382 | -0.25177 | -0.032043 | -0.12817 | 0.013733 | -0.064087 | -0.022888 | -0.18768 | 0.009155 | -0.15564 | 0.14191 | 122.5342 | -0.032044 | 122.5342 | 122.493 | 122.3923 | 122.4106 | 122.3602 | -122.5708 | -122.5204 | 122.4518 | 122.5021 | 59.6649 | 59.6237
104.7656 | 122.7814 | -59.7427 | 62.677 | -0.086899 | 0.0023391 | 0.060103 | 0.075954 | -0.0013245 | -0.0014312 | 0.00074764 | -0.030823 | -0.00027343 | 0.064606 | 0.057631 | -0.0060691 | 0.0016277 | 0.0033111 | -0.07782 | 62.6083 | -59.816 | 62.7548 | -59.6466 | -60.0128 | -0.041199 | -0.064087 | 62.5809 | -59.7519 | 62.796 | -59.7427 | -59.8618 | -59.7015 | -0.073242 | -0.068665 | 0.07782 | 0.096131 | 59.7015 | -0.27008 | 59.7748 | -0.19684 | -0.009155 | -0.09613 | 0.11902 | 0 | 0.041199 | -0.11902 | 0.050354 | -0.10986 | 0.16937 | 122.5708 | 0.009155 | 122.5479 | 122.4243 | 122.3328 | 122.3511 | 122.3236 | -122.493 | -122.4289 | 122.4976 | 122.5388 | 59.6649 | 59.6786
105.7656 | 122.7814 | -59.761 | 62.709 | -0.06401 | 0.0012711 | 0.064375 | 0.076808 | 0.0027343 | -0.0005768 | 0.00010684 | -0.018616 | 0.001222 | 0.06247 | 0.066176 | -0.0052145 | 0.0012005 | 0.00010689 | -0.068665 | 62.6266 | -59.8434 | 62.7594 | -59.6237 | -60.0311 | -0.036621 | -0.082397 | 62.5442 | -59.7794 | 62.8052 | -59.7473 | -59.8618 | -59.697 | -0.082398 | -0.082397 | 0.050354 | 0.13733 | 59.7244 | -0.27008 | 59.8068 | -0.18768 | -0.018311 | -0.1648 | 0.096131 | 0.013733 | 0.064087 | -0.10071 | 0.082398 | -0.082397 | 0.21973 | 122.6028 | 0.032044 | 122.5845 | 122.4701 | 122.3236 | 122.3877 | 122.3053 | -122.5525 | -122.4884 | 122.5204 | 122.5662 | 59.6924 | 59.6786
106.7656 | 122.7768 | -59.7198 | 62.6862 | -0.10979 | -0.00022432 | 0.06523 | 0.078303 | 0.0018799 | -0.0007904 | 0.0026702 | -0.024719 | 0.00015377 | 0.06546 | 0.056777 | -0.0088461 | 0.0026959 | -0.00032051 | -0.073242 | 62.6083 | -59.8389 | 62.7594 | -59.6466 | -60.0174 | -0.032043 | -0.064087 | 62.5809 | -59.7839 | 62.796 | -59.7427 | -59.8526 | -59.6924 | -0.11902 | -0.07782 | 0.073242 | 0.073243 | 59.6878 | -0.29755 | 59.8068 | -0.17853 | -0.064087 | -0.10529 | 0.10986 | -0.022888 | 0.027466 | -0.13275 | 0.091553 | -0.068664 | 0.19226 | 122.5983 | 0.041199 | 122.58 | 122.4472 | 122.3648 | 122.3282 | 122.3007 | -122.525 | -122.4701 | 122.4792 | 122.5159 | 59.6466 | 59.6558
107.7656 | 122.7768 | -59.7382 | 62.6862 | -0.094528 | 0.0025529 | 0.068861 | 0.077663 | -0.0047425 | 0.001773 | -0.00096136 | -0.00030524 | 0.00079477 | 0.06546 | 0.059127 | -0.0077779 | 0.0046185 | -0.0024567 | -0.21973 | 62.5488 | -59.848 | 62.8235 | -59.5963 | -59.9899 | -0.013733 | -0.018311 | 62.5671 | -59.7702 | 62.796 | -59.7427 | -59.848 | -59.7198 | -0.10986 | -0.13733 | 0.13733 | 0.14191 | 59.7244 | -0.25177 | 59.8343 | -0.14191 | -0.032044 | -0.11902 | 0.10986 | -0.004578 | 0.01831 | -0.10986 | 0.050354 | -0.077819 | 0.25177 | 122.6715 | 0.027466 | 122.5662 | 122.3969 | 122.3373 | 122.287 | 122.3053 | -122.5342 | -122.4564 | 122.5616 | 122.5342 | 59.5184 | 59.7198
108.7656 | 122.8043 | -59.729 | 62.6862 | -0.13267 | -0.00022432 | 0.066084 | 0.074886 | 0.0018799 | -0.0003632 | -0.0020294 | -0.012512 | -0.0017688 | 0.063538 | 0.060622 | -0.0069235 | 0.00055973 | 0.00096129 | -0.22888 | 62.5305 | -59.8663 | 62.8098 | -59.5917 | -59.9945 | 0 | -0.018311 | 62.558 | -59.7565 | 62.8098 | -59.7473 | -59.8343 | -59.729 | -0.13733 | -0.15564 | 0.1236 | 0.13733 | 59.729 | -0.2655 | 59.8663 | -0.12817 | -0.027466 | -0.12817 | 0.1236 | -0.01831 | 0 | -0.10529 | 0.027466 | -0.07782 | 0.27466 | 122.6761 | 0.009156 | 122.5662 | 122.3969 | 122.3145 | 122.2595 | 122.287 | -122.5525 | -122.4426 | 122.5388 | 122.5388 | 59.5001 | 59.7107
109.7656 | 122.7814 | -59.7198 | 62.6724 | -0.07164 | -0.00065152 | 0.063094 | 0.077876 | -0.0026063 | -0.0001496 | -0.002243 | -0.039978 | -0.0019824 | 0.062897 | 0.068526 | -0.0073507 | 0.0026959 | 0.0020295 | -0.073242 | 62.6038 | -59.8297 | 62.7502 | -59.6649 | -60.022 | -0.041199 | -0.064087 | 62.5626 | -59.7839 | 62.8052 | -59.7519 | -59.8755 | -59.7015 | -0.10986 | -0.068664 | 0.07782 | 0.054932 | 59.6787 | -0.30212 | 59.7885 | -0.19226 | -0.064087 | -0.10986 | 0.13275 | -0.032043 | 0.018311 | -0.15564 | 0.082398 | -0.091552 | 0.16479 | 122.58 | 0.032044 | 122.5891 | 122.4335 | 122.3465 | 122.3236 | 122.2824 | -122.5021 | -122.4564 | 122.4701 | 122.525 | 59.6466 | 59.6558
110.7656 | 122.7585 | -59.7382 | 62.677 | -0.10979 | 0.00041648 | 0.062239 | 0.079799 | -0.00046988 | -0.0022858 | -0.0030976 | -0.018616 | -0.00091423 | 0.064606 | 0.061904 | -0.010128 | 0.0041913 | -0.0018157 | -0.073242 | 62.6312 | -59.8434 | 62.7686 | -59.6329 | -60.0266 | -0.054932 | -0.068665 | 62.5854 | -59.7748 | 62.8006 | -59.7519 | -59.8618 | -59.7061 | -0.10529 | -0.045776 | 0.091553 | 0.10529 | 59.6832 | -0.28839 | 59.7885 | -0.1831 | -0.036621 | -0.091553 | 0.1236 | -0.013733 | 0.032043 | -0.1236 | 0.068664 | -0.086975 | 0.21057 | 122.612 | 0.022888 | 122.5754 | 122.4747 | 122.3602 | 122.3694 | 122.3236 | -122.5204 | -122.4518 | 122.5067 | 122.5388 | 59.6649 | 59.6695
111.7656 | 122.7951 | -59.7153 | 62.6724 | -0.041122 | 0.00084388 | 0.064375 | 0.07574 | -0.0017517 | -0.0018586 | -0.00074776 | -0.018616 | -0.00091423 | 0.064179 | 0.064253 | -0.0064963 | -0.00093567 | 0.0016021 | 0.045776 | 62.6038 | -59.8022 | 62.8189 | -59.6008 | -59.9854 | -0.013733 | -0.022888 | 62.5626 | -59.7794 | 62.796 | -59.7382 | -59.8526 | -59.7061 | -0.086975 | -0.068664 | 0.14648 | 0.11444 | 59.7015 | -0.27008 | 59.7885 | -0.18311 | -0.064087 | -0.10986 | 0.1236 | -0.022888 | 0.009155 | -0.13733 | 0.073242 | -0.073242 | 0.20142 | 122.6212 | 0.041199 | 122.5754 | 122.406 | 122.3419 | 122.319 | 122.2778 | -122.4747 | -122.4518 | 122.5342 | 122.5113 | 59.761 | 59.6924
112.7656 | 122.6852 | -59.729 | 62.7777 | -0.041122 | 0.0025529 | 0.063521 | 0.077022 | -0.0023925 | -0.0035674 | -0.0013886 | -0.0064086 | 0.001222 | 0.062897 | 0.062758 | -0.0067099 | 0.0033367 | -0.0016021 | 0.050354 | 62.6587 | -59.7839 | 62.8098 | -59.5779 | -59.9579 | 0.086975 | 0.073242 | 62.6266 | -59.761 | 62.7365 | -59.7931 | -59.8709 | -59.7656 | -0.054932 | -0.11902 | 0.032043 | 0.15106 | 59.816 | -0.22888 | 59.8709 | -0.17395 | -0.032043 | -0.15106 | -0.041199 | -0.064087 | -0.036621 | -0.14191 | -0.004578 | -0.10986 | 0.20599 | 122.5937 | -0.032044 | 122.4976 | 122.4426 | 122.3877 | 122.3877 | 122.3557 | -122.5616 | -122.5388 | 122.5388 | 122.4655 | 59.7794 | 59.8022
113.7656 | 122.7768 | -59.7382 | 62.7045 | 0.012284 | -0.0015061 | 0.065657 | 0.079585 | 0.00017092 | -0.0003632 | -0.00074776 | -0.04303 | -0.00070063 | 0.064179 | 0.065962 | -0.0060691 | -8.1274e-05 | -0.0020295 | -0.027466 | 62.5854 | -59.8068 | 62.8006 | -59.5825 | -59.9579 | -0.009155 | -0.009155 | 62.5854 | -59.7427 | 62.8052 | -59.7427 | -59.8389 | -59.6878 | -0.068665 | -0.11902 | 0.09613 | 0.15564 | 59.729 | -0.21973 | 59.7977 | -0.15106 | -0.004578 | -0.11902 | 0.10071 | -0.004578 | 0.050354 | -0.10071 | 0.054932 | -0.09613 | 0.2243 | 122.6074 | 0 | 122.5479 | 122.3923 | 122.3282 | 122.3236 | 122.3236 | -122.5113 | -122.4472 | 122.5388 | 122.5433 | 59.7107 | 59.729
114.7656 | 122.731 | -59.7382 | 62.6816 | -0.10979 | 0.0012711 | 0.063521 | 0.07809 | -0.0015381 | -0.0007904 | 0.0016022 | -0.0094604 | -0.00070063 | 0.063324 | 0.064894 | -0.0073507 | 0.00055973 | -0.00010671 | -0.036621 | 62.5946 | -59.8022 | 62.7914 | -59.5734 | -59.9991 | -0.013733 | -0.004578 | 62.5809 | -59.7473 | 62.7914 | -59.761 | -59.8572 | -59.7427 | -0.064087 | -0.086976 | 0.10986 | 0.1648 | 59.7244 | -0.26093 | 59.7885 | -0.19684 | -0.009155 | -0.10071 | 0.10986 | -0.022888 | -0.004578 | -0.11902 | 0.004577 | -0.10986 | 0.22888 | 122.5937 | -0.013733 | 122.5388 | 122.3969 | 122.3282 | 122.3328 | 122.319 | -122.4838 | -122.4289 | 122.5296 | 122.5296 | 59.7015 | 59.7336
115.7656 | 122.7768 | -59.7473 | 62.7136 | -0.048752 | 0.0016983 | 0.064803 | 0.076808 | -0.0023925 | 0.0009186 | 0.00053404 | -0.0094604 | -0.00048703 | 0.063965 | 0.058058 | -0.0058553 | 0.0022687 | 0.00032049 | -0.054932 | 62.5946 | -59.7794 | 62.796 | -59.5688 | -60.0037 | -0.027466 | 0.009155 | 62.59 | -59.7382 | 62.7869 | -59.7656 | -59.8618 | -59.7244 | -0.032044 | -0.11902 | 0.082398 | 0.17853 | 59.7198 | -0.25635 | 59.7519 | -0.2243 | 0.009155 | -0.1236 | 0.073242 | -0.018311 | 0.022888 | -0.11444 | 0.013733 | -0.1236 | 0.21057 | 122.5754 | -0.027466 | 122.525 | 122.374 | 122.3282 | 122.3419 | 122.3373 | -122.493 | -122.4518 | 122.5433 | 122.5342 | 59.6924 | 59.7565
116.7656 | 122.7859 | -59.7473 | 62.7136 | -0.11742 | 0.0012711 | 0.064589 | 0.077235 | 0.0025207 | -0.0016448 | 0.00010684 | -0.052185 | 0.0014356 | 0.064392 | 0.070662 | -0.0075643 | 0.0026959 | -0.00053411 | -0.018311 | 62.59 | -59.7885 | 62.8052 | -59.5963 | -59.9945 | -0.032043 | -0.004578 | 62.5717 | -59.7656 | 62.8235 | -59.7427 | -59.8251 | -59.6786 | -0.041199 | -0.1236 | 0.091553 | 0.15106 | 59.7153 | -0.24719 | 59.7565 | -0.20599 | -0.018311 | -0.14191 | 0.10986 | 0.004577 | 0.068664 | -0.07782 | 0.086975 | -0.059509 | 0.19226 | 122.5937 | 0.022888 | 122.5891 | 122.3785 | 122.3373 | 122.3373 | 122.319 | -122.5021 | -122.4792 | 122.5525 | 122.5708 | 59.729 | 59.7427
117.7656 | 122.7859 | -59.7198 | 62.7319 | -0.025863 | 0.0016983 | 0.063094 | 0.076381 | 0.00017092 | -0.0007904 | -0.00096136 | 0.0057984 | -0.00070063 | 0.063538 | 0.062331 | -0.0064963 | 0.00013253 | -0.0022431 | 0.050354 | 62.6541 | -59.7748 | 62.851 | -59.5322 | -59.9075 | 0.11444 | 0.14191 | 62.5992 | -59.7473 | 62.8281 | -59.6786 | -59.7885 | -59.6878 | -0.054931 | -0.07782 | 0.11902 | 0.18768 | 59.8343 | -0.18768 | 59.8892 | -0.13275 | -0.027465 | -0.13275 | 0.09613 | 0.041199 | 0.032044 | -0.068664 | 0.059509 | -0.041199 | 0.24261 | 122.6257 | 0.068664 | 122.5754 | 122.4289 | 122.3465 | 122.374 | 122.319 | -122.5067 | -122.4792 | 122.5708 | 122.5479 | 59.7702 | 59.8618
118.7656 | 122.7539 | -59.7519 | 62.6907 | -0.11742 | 0.00063028 | 0.063307 | 0.076167 | 0.0016663 | -0.0012176 | -0.00074776 | -0.039978 | -0.00048703 | 0.062683 | 0.062117 | -0.0062827 | 0.0012005 | -0.00010671 | -0.036621 | 62.6129 | -59.8114 | 62.8098 | -59.5779 | -59.9945 | -0.013733 | -0.009155 | 62.5671 | -59.7748 | 62.7731 | -59.7656 | -59.8663 | -59.7382 | -0.059509 | -0.07782 | 0.11902 | 0.17395 | 59.7382 | -0.24262 | 59.7977 | -0.18311 | -0.022888 | -0.1236 | 0.082397 | -0.013733 | 0.013733 | -0.11444 | 0.036621 | -0.091553 | 0.23346 | 122.6212 | 0.009155 | 122.5479 | 122.4243 | 122.3419 | 122.3648 | 122.319 | -122.5021 | -122.4655 | 122.5616 | 122.525 | 59.7153 | 59.7427
119.7656 | 122.7448 | -59.7427 | 62.709 | -0.094528 | 0.00041648 | 0.065657 | 0.078303 | 0.0016663 | -0.0001496 | 0.0037384 | -0.036926 | 0.0010084 | 0.065674 | 0.064894 | -0.0069235 | 0.0029095 | -0.00010671 | -0.041199 | 62.6038 | -59.8206 | 62.8098 | -59.5825 | -59.9991 | -0.004578 | -0.013733 | 62.5534 | -59.761 | 62.7777 | -59.7565 | -59.8572 | -59.729 | -0.07782 | -0.10529 | 0.10071 | 0.16022 | 59.7382 | -0.25635 | 59.816 | -0.17853 | -0.01831 | -0.15564 | 0.068665 | -0.013733 | 0.013733 | -0.11444 | 0.032043 | -0.096131 | 0.23804 | 122.6303 | 0.004577 | 122.5388 | 122.4243 | 122.3145 | 122.3465 | 122.2961 | -122.5296 | -122.4701 | 122.5525 | 122.5204 | 59.7015 | 59.729
120.7656 | 122.7493 | -59.7244 | 62.6907 | -0.07164 | 0.00041648 | 0.063521 | 0.07574 | 0.00038452 | -0.0016448 | -0.0035248 | -0.018616 | 0.00079477 | 0.063965 | 0.057845 | -0.0064963 | 0.00013253 | -0.0011749 | -0.036621 | 62.5946 | -59.7977 | 62.8189 | -59.5779 | -59.9899 | -0.022888 | -0.004578 | 62.5626 | -59.7748 | 62.7914 | -59.7656 | -59.8709 | -59.7244 | -0.073242 | -0.096131 | 0.12817 | 0.14648 | 59.7015 | -0.2655 | 59.7748 | -0.19226 | -0.050354 | -0.12817 | 0.10071 | -0.041199 | 0 | -0.14648 | 0.050354 | -0.096131 | 0.21973 | 122.6166 | 0.009155 | 122.5662 | 122.3923 | 122.3373 | 122.319 | 122.287 | -122.4884 | -122.4655 | 122.5433 | 122.5159 | 59.6878 | 59.7198
121.7656 | 122.7631 | -59.7382 | 62.7136 | -0.056381 | -1.0718e-05 | 0.063734 | 0.076808 | -0.0038879 | -0.0039948 | 0.00032044 | -0.00030524 | 0.0010084 | 0.063538 | 0.062972 | -0.0079917 | 0.0018413 | -0.00032051 | -0.054932 | 62.6175 | -59.8114 | 62.7548 | -59.6283 | -60.0037 | -0.027466 | 0.16022 | 62.6175 | -59.7382 | 62.7548 | -59.7519 | -59.8846 | -59.7427 | -0.073242 | -0.09613 | 0.041199 | 0.10986 | 59.7107 | -0.2655 | 59.7839 | -0.19226 | 0 | -0.09613 | 0.041199 | -0.013733 | -0.004578 | -0.14648 | -0.004578 | -0.14648 | 0.1831 | 122.5662 | -0.013733 | 122.493 | 122.4289 | 122.3557 | 122.3557 | 122.3557 | -122.525 | -122.4518 | 122.493 | 122.493 | 59.6832 | 59.8984
122.7656 | 122.6852 | -59.7565 | 62.7914 | 0.050431 | -0.00065152 | 0.062025 | 0.077876 | 0.0016663 | -0.0016448 | -0.0020294 | -0.04303 | 0.00036737 | 0.064392 | 0.065962 | -0.0047873 | 0.0024823 | 0.0030975 | -0.12817 | 62.6862 | -59.8297 | 62.7136 | -59.6786 | -60.0357 | 0.027466 | 0.032043 | 62.6724 | -59.7519 | 62.7319 | -59.7839 | -59.903 | -59.7748 | -0.073242 | -0.10529 | -0.07782 | 0.07782 | 59.7839 | -0.27924 | 59.8572 | -0.20599 | 0.004578 | -0.11902 | -0.059509 | -0.027466 | -0.01831 | -0.14648 | -0.022888 | -0.15106 | 0.15106 | 122.5433 | -0.032044 | 122.4838 | 122.5159 | 122.4243 | 122.4426 | 122.4289 | -122.6212 | -122.5433 | 122.4701 | 122.4884 | 59.6283 | 59.7885
123.7656 | 122.7539 | -59.7336 | 62.6907 | -0.11742 | 0.0012711 | 0.063094 | 0.076808 | 0.0055115 | -0.0007904 | -0.0018158 | -0.033874 | 0.00036737 | 0.06482 | 0.063399 | -0.0058553 | 0.0012005 | -0.00053411 | -0.041199 | 62.5854 | -59.8022 | 62.8006 | -59.5642 | -60.0174 | -0.009155 | -0.027466 | 62.5763 | -59.7382 | 62.7823 | -59.7748 | -59.8572 | -59.7198 | -0.068664 | -0.10529 | 0.10986 | 0.16937 | 59.7244 | -0.28381 | 59.7931 | -0.21515 | -0.004577 | -0.11444 | 0.091553 | -0.041198 | 0.013733 | -0.1236 | 0.01831 | -0.11902 | 0.23804 | 122.6028 | -0.036621 | 122.5204 | 122.3877 | 122.3145 | 122.319 | 122.3099 | -122.493 | -122.4289 | 122.5342 | 122.5159 | 59.6924 | 59.7061
124.7656 | 122.7448 | -59.7336 | 62.7045 | -0.06401 | 0.0010575 | 0.063521 | 0.079372 | -0.00025628 | -0.0014312 | 0.00032044 | -0.039978 | -0.0015552 | 0.062042 | 0.064253 | -0.0062827 | -0.00072207 | -0.0013885 | -0.068665 | 62.6404 | -59.8068 | 62.7365 | -59.6924 | -60.054 | -0.050354 | -0.041199 | 62.5671 | -59.7656 | 62.7686 | -59.7656 | -59.8618 | -59.7244 | -0.073242 | -0.064087 | 0.032043 | 0.041199 | 59.6832 | -0.32043 | 59.7565 | -0.24719 | -0.032043 | -0.13733 | 0.064087 | -0.032043 | 0.009156 | -0.12817 | 0.041199 | -0.09613 | 0.11444 | 122.5433 | 0 | 122.5342 | 122.4472 | 122.3328 | 122.374 | 122.3007 | -122.5113 | -122.4701 | 122.4701 | 122.5021 | 59.6649 | 59.6924
125.7656 | 122.7448 | -59.7153 | 62.7045 | -0.12505 | 0.0019119 | 0.066084 | 0.076167 | -0.0013245 | -0.0029266 | 0.00096124 | -0.024719 | -0.00027343 | 0.062683 | 0.067671 | -0.0073507 | 0.00098693 | -0.0016021 | -0.054932 | 62.6129 | -59.7839 | 62.7228 | -59.6741 | -59.9991 | -0.009155 | -0.050354 | 62.6175 | -59.7839 | 62.764 | -59.7702 | -59.8938 | -59.7427 | -0.068665 | -0.091553 | 0.01831 | 0.041199 | 59.7061 | -0.28381 | 59.7748 | -0.21515 | -0.068665 | -0.086975 | 0.059509 | -0.054932 | -0.027466 | -0.17853 | 0.041199 | -0.10986 | 0.10986 | 122.5067 | 0.013733 | 122.5479 | 122.3969 | 122.4014 | 122.3282 | 122.3328 | -122.4884 | -122.4884 | 122.438 | 122.4792 | 59.6603 | 59.6649
126.7656 | 122.7676 | -59.7382 | 62.6953 | -0.056381 | -0.0027877 | 0.06288 | 0.077876 | -0.0026063 | -0.0014312 | 0.001175 | -0.012512 | -0.00048703 | 0.064606 | 0.065108 | -0.0075643 | 0.0012005 | -0.00074771 | 0.10986 | 62.6678 | -59.761 | 62.7686 | -59.642 | -60.0357 | -0.032043 | -0.068665 | 62.5992 | -59.761 | 62.764 | -59.7839 | -59.8801 | -59.7336 | -0.022888 | -0.027465 | 0.073243 | 0.09613 | 59.7061 | -0.29755 | 59.729 | -0.27466 | -0.022888 | -0.09613 | 0.068665 | -0.045777 | 0.004577 | -0.14191 | 0.027465 | -0.11902 | 0.11902 | 122.5296 | -0.022889 | 122.525 | 122.4289 | 122.3602 | 122.406 | 122.3373 | -122.4564 | -122.4564 | 122.5067 | 122.5021 | 59.848 | 59.6695
127.7656 | 122.7264 | -59.7198 | 62.7731 | -0.048752 | -0.00065152 | 0.063521 | 0.079799 | 0.0018799 | -0.0018586 | 0.00032044 | -0.09491 | -0.00027343 | 0.063538 | 0.06639 | -0.0082053 | 0.0029095 | -0.0013885 | 0.013733 | 62.677 | -59.816 | 62.7502 | -59.6649 | -60.0082 | 0.009155 | 0.013733 | 62.6724 | -59.7702 | 62.7548 | -59.7519 | -59.8846 | -59.7519 | -0.09613 | -0.09613 | -0.022888 | 0.054932 | 59.729 | -0.28839 | 59.8251 | -0.19226 | -0.050354 | -0.10071 | -0.01831 | -0.032043 | -0.032043 | -0.16479 | 0.018311 | -0.11444 | 0.15106 | 122.5662 | 0.018311 | 122.525 | 122.493 | 122.4426 | 122.3969 | 122.3923 | -122.5891 | -122.5433 | 122.4701 | 122.4747 | 59.7336 | 59.7336
128.7656 | 122.7768 | -59.7336 | 62.7182 | -0.010605 | 0.0021255 | 0.064162 | 0.076594 | -0.0041015 | -0.0012176 | -0.00074776 | 0.0088502 | -0.00091423 | 0.063751 | 0.060195 | -0.0064963 | 0.0014141 | -0.0018157 | -0.013733 | 62.6083 | -59.7794 | 62.7823 | -59.6054 | -59.9762 | 0.041199 | 0.018311 | 62.5854 | -59.7565 | 62.8189 | -59.7153 | -59.8114 | -59.697 | -0.045776 | -0.10986 | 0.064087 | 0.12817 | 59.7748 | -0.24261 | 59.8206 | -0.19684 | -0.022888 | -0.13275 | 0.10071 | 0.018311 | 0.036622 | -0.077819 | 0.05951 | -0.054931 | 0.17395 | 122.5616 | 0.041199 | 122.5754 | 122.3877 | 122.3419 | 122.3419 | 122.319 | -122.4976 | -122.4747 | 122.5159 | 122.5525 | 59.7198 | 59.7519
129.7656 | 122.7631 | -59.7382 | 62.7274 | -0.079269 | 0.0016983 | 0.063094 | 0.078303 | -0.00089728 | 0.0015594 | 0.0020294 | 0.0027466 | 0.0010084 | 0.06546 | 0.058913 | -0.0090597 | 0.00077333 | -0.0011749 | -0.009155 | 62.6312 | -59.7931 | 62.8006 | -59.5871 | -59.9854 | 0.045776 | 0.032043 | 62.5946 | -59.7427 | 62.8143 | -59.7244 | -59.8297 | -59.6695 | -0.054932 | -0.09613 | 0.073242 | 0.15106 | 59.7839 | -0.24719 | 59.8389 | -0.19226 | -0.004578 | -0.13275 | 0.086975 | 0.013733 | 0.068664 | -0.091553 | 0.073242 | -0.086975 | 0.20599 | 122.5937 | 0.018311 | 122.5571 | 122.4243 | 122.3373 | 122.3694 | 122.3328 | -122.5204 | -122.4701 | 122.5388 | 122.5525 | 59.729 | 59.7702
130.7656 | 122.7493 | -59.7473 | 62.7274 | -0.11742 | 0.0012711 | 0.064589 | 0.077022 | 0.0023071 | 6.4004e-05 | -0.0016022 | -0.027771 | 0.00036737 | 0.065888 | 0.062758 | -0.0064963 | 0.0037641 | 0.00032049 | -0.073242 | 62.6358 | -59.816 | 62.7594 | -59.6375 | -60.0128 | -0.009155 | -0.027466 | 62.5809 | -59.7748 | 62.7731 | -59.7565 | -59.8434 | -59.7244 | -0.068665 | -0.091553 | 0.032043 | 0.10986 | 59.7382 | -0.2655 | 59.8068 | -0.19684 | -0.027466 | -0.14648 | 0.045776 | -0.009156 | 0.022888 | -0.096131 | 0.050354 | -0.068665 | 0.17853 | 122.5754 | 0.01831 | 122.5479 | 122.4518 | 122.3557 | 122.3831 | 122.3282 | -122.5433 | -122.5021 | 122.5067 | 122.5204 | 59.6741 | 59.7198
131.7656 | 122.7722 | -59.7244 | 62.7365 | -0.07164 | 0.0034073 | 0.063307 | 0.07809 | 0.0033753 | -0.0007904 | -0.0024566 | -0.027771 | -0.00070063 | 0.066315 | 0.055922 | -0.0088461 | 0.0029095 | 0.0033111 | -0.018311 | 62.6175 | -59.761 | 62.8143 | -59.5779 | -59.9487 | 0.068665 | 0.045776 | 62.6038 | -59.7473 | 62.8281 | -59.7061 | -59.816 | -59.6878 | -0.036621 | -0.11902 | 0.07782 | 0.14648 | 59.7931 | -0.2243 | 59.8297 | -0.18768 | -0.022888 | -0.13275 | 0.091553 | 0.01831 | 0.036621 | -0.091553 | 0.059509 | -0.068665 | 0.1831 | 122.5754 | 0.041198 | 122.5754 | 122.3785 | 122.3511 | 122.3419 | 122.3282 | -122.4976 | -122.4838 | 122.5388 | 122.5525 | 59.7061 | 59.7702
132.7656 | 122.6852 | -59.7427 | 62.7548 | -0.048752 | 0.0021255 | 0.065657 | 0.080867 | -4.2682e-05 | -0.0012176 | -0.0013886 | -0.11017 | 0.0010084 | 0.064179 | 0.072371 | -0.0086325 | 0.0031231 | -0.00010671 | 0.009155 | 62.6678 | -59.8114 | 62.7686 | -59.6649 | -60.0403 | -0.036621 | -0.018311 | 62.6175 | -59.7794 | 62.7319 | -59.816 | -59.9304 | -59.7702 | -0.068664 | -0.086975 | 0.013733 | 0.07782 | 59.7061 | -0.29755 | 59.7748 | -0.22888 | -0.036621 | -0.13733 | -0.022888 | -0.073242 | -0.027466 | -0.18768 | 0.009155 | -0.15106 | 0.14648 | 122.58 | -0.036621 | 122.5113 | 122.4792 | 122.3969 | 122.4106 | 122.3602 | -122.5662 | -122.5342 | 122.5113 | 122.4747 | 59.7519 | 59.7244
133.7656 | 122.7951 | -59.7061 | 62.7274 | -0.10979 | -1.0718e-05 | 0.061385 | 0.077235 | -0.0015381 | -0.0014312 | -0.00074776 | -0.00030524 | -0.00070063 | 0.064606 | 0.057845 | -0.0067099 | 0.00013253 | -0.0026703 | 0 | 62.6495 | -59.7885 | 62.8189 | -59.5734 | -59.9487 | 0.064087 | 0.073242 | 62.59 | -59.7473 | 62.8235 | -59.6924 | -59.7839 | -59.6878 | -0.082397 | -0.07782 | 0.091553 | 0.13275 | 59.7702 | -0.24261 | 59.8526 | -0.16022 | -0.041198 | -0.13733 | 0.09613 | 0.013733 | 0.018311 | -0.07782 | 0.059509 | -0.036622 | 0.21515 | 122.6074 | 0.054931 | 122.5708 | 122.438 | 122.3373 | 122.3557 | 122.2961 | -122.5159 | -122.4747 | 122.525 | 122.5296 | 59.7061 | 59.7794
134.7656 | 122.7814 | -59.6924 | 62.7319 | -0.048752 | 0.0023391 | 0.062239 | 0.077663 | 0.00059812 | -0.0003632 | -0.001175 | 0.0027466 | -0.0017688 | 0.063538 | 0.063185 | -0.0050009 | 0.0026959 | -0.00032051 | -0.009155 | 62.6266 | -59.7977 | 62.8281 | -59.5688 | -59.9579 | 0.064087 | 0.073242 | 62.6221 | -59.761 | 62.8418 | -59.6878 | -59.7885 | -59.6649 | -0.10529 | -0.10529 | 0.09613 | 0.1236 | 59.7565 | -0.2655 | 59.8618 | -0.16022 | -0.068664 | -0.10986 | 0.10986 | 0.004578 | 0.027466 | -0.09613 | 0.09613 | -0.027466 | 0.22888 | 122.6257 | 0.073242 | 122.6028 | 122.4243 | 122.3831 | 122.319 | 122.3145 | -122.5296 | -122.493 | 122.5204 | 122.5342 | 59.6832 | 59.7656
135.7656 | 122.7814 | -59.6832 | 62.7365 | -0.048752 | -0.00086512 | 0.060103 | 0.078731 | 0.0010253 | 0.0013458 | 0.00096124 | -0.015564 | 0.0010084 | 0.065247 | 0.061476 | -0.0086325 | 0.0029095 | -0.0011749 | 0.37994 | 62.7274 | -59.7153 | 62.8326 | -59.4955 | -59.8846 | 0.07782 | 0.13275 | 62.6083 | -59.7382 | 62.8555 | -59.6649 | -59.7931 | -59.6649 | -0.032043 | -0.009155 | 0.096131 | 0.18768 | 59.761 | -0.20142 | 59.7931 | -0.16937 | -0.054931 | -0.12817 | 0.11902 | 0.018311 | 0.018311 | -0.10986 | 0.073242 | -0.054932 | 0.21973 | 122.5479 | 0.073242 | 122.5937 | 122.4426 | 122.3465 | 122.4106 | 122.2916 | -122.4518 | -122.4747 | 122.5159 | 122.5388 | 60.0632 | 59.816
136.7656 | 122.7859 | -59.6786 | 62.7411 | -0.010605 | 0.00084388 | 0.065443 | 0.078731 | 0.0033753 | -0.0003632 | 0.00074764 | -0.0064086 | 0.00015377 | 0.063538 | 0.059981 | -0.0097007 | 0.0018413 | 0.0016021 | -0.14191 | 62.6266 | -59.8022 | 62.8189 | -59.523 | -59.9075 | 0.10529 | 0.17395 | 62.5992 | -59.7382 | 62.8372 | -59.6741 | -59.7702 | -59.6466 | -0.1236 | -0.11444 | 0.07782 | 0.15564 | 59.7839 | -0.22888 | 59.9075 | -0.10529 | -0.059509 | -0.14191 | 0.09613 | 0.004578 | 0.032044 | -0.091553 | 0.091553 | -0.032044 | 0.27924 | 122.6212 | 0.064087 | 122.5754 | 122.4289 | 122.3373 | 122.3053 | 122.2778 | -122.5433 | -122.4792 | 122.4976 | 122.5159 | 59.5367 | 59.8526
137.7656 | 122.6624 | -59.697 | 62.7823 | -0.048752 | 0.0010575 | 0.063734 | 0.079158 | -0.0017517 | -0.0014312 | 0.00053404 | 0.0088502 | -0.0017688 | 0.065247 | 0.062331 | -0.0090597 | 0.0026959 | 0.0016021 | 0.018311 | 62.6404 | -59.7885 | 62.851 | -59.5276 | -59.9258 | 0.09613 | 0.13275 | 62.5992 | -59.7427 | 62.8326 | -59.6741 | -59.761 | -59.642 | -0.091553 | -0.14191 | 0.068664 | 0.16937 | 59.7931 | -0.22888 | 59.8846 | -0.13733 | -0.045777 | -0.18311 | 0.050354 | 0.022888 | 0.054931 | -0.064087 | 0.10071 | -0.01831 | 0.26093 | 122.6395 | 0.068665 | 122.5754 | 122.4289 | 122.3419 | 122.3373 | 122.2961 | -122.5708 | -122.525 | 122.5479 | 122.5296 | 59.7153 | 59.8297
138.7656 | 122.7997 | -59.6924 | 62.7411 | -0.056381 | 0.0019119 | 0.063948 | 0.080012 | -0.00068368 | 0.0004914 | 0.00010684 | -0.027771 | 0.00015377 | 0.061615 | 0.063613 | -0.0073507 | 0.0014141 | 0.00032049 | 0.050354 | 62.6221 | -59.7794 | 62.8555 | -59.5093 | -59.9304 | 0.13275 | 0.15564 | 62.6129 | -59.7382 | 62.8326 | -59.6695 | -59.7794 | -59.6695 | -0.086975 | -0.11902 | 0.11444 | 0.18311 | 59.8251 | -0.23804 | 59.9121 | -0.15106 | -0.045776 | -0.12817 | 0.091553 | 0.022888 | 0.022888 | -0.086975 | 0.068664 | -0.041199 | 0.27008 | 122.6349 | 0.068664 | 122.5708 | 122.4014 | 122.3511 | 122.3145 | 122.3053 | -122.5204 | -122.4792 | 122.5479 | 122.525 | 59.7427 | 59.848
139.7656 | 122.7905 | -59.7107 | 62.7319 | -0.041122 | 0.0034073 | 0.06523 | 0.077663 | -4.2682e-05 | -0.0024994 | -0.00053396 | -0.0064086 | 0.00036737 | 0.064606 | 0.062117 | -0.0084189 | 0.0026959 | -0.00010671 | 0.07782 | 62.6358 | -59.7702 | 62.8601 | -59.5093 | -59.8984 | 0.11444 | 0.13733 | 62.6221 | -59.7427 | 62.8326 | -59.6741 | -59.7839 | -59.6695 | -0.05951 | -0.096131 | 0.12817 | 0.20142 | 59.8251 | -0.18768 | 59.8846 | -0.12817 | -0.032044 | -0.10986 | 0.10071 | 0.036621 | 0.041198 | -0.073243 | 0.073242 | -0.041199 | 0.26093 | 122.6303 | 0.068665 | 122.5754 | 122.406 | 122.3648 | 122.3465 | 122.3328 | -122.5021 | -122.4747 | 122.5708 | 122.5433 | 59.7885 | 59.848
140.7656 | 122.7585 | -59.7198 | 62.7548 | -0.010605 | 0.0021255 | 0.06523 | 0.075313 | 0.0033753 | 0.0013458 | -0.002884 | -0.033874 | -0.0015552 | 0.06546 | 0.063399 | -0.0062827 | 0.0022687 | -0.0026703 | 0.032043 | 62.6175 | -59.7565 | 62.8647 | -59.523 | -59.9167 | 0.11444 | 0.14191 | 62.6083 | -59.761 | 62.8281 | -59.6924 | -59.7977 | -59.6786 | -0.036621 | -0.13733 | 0.10986 | 0.19684 | 59.8343 | -0.19684 | 59.8709 | -0.16022 | -0.041198 | -0.14648 | 0.073242 | 0.027466 | 0.041199 | -0.077819 | 0.082397 | -0.036621 | 0.23346 | 122.6212 | 0.068664 | 122.5891 | 122.374 | 122.3694 | 122.3373 | 122.3282 | -122.5113 | -122.5159 | 122.5845 | 122.5479 | 59.7519 | 59.8618
141.7656 | 122.7631 | -59.7244 | 62.7594 | -0.048752 | -0.00065152 | 0.061598 | 0.079799 | 0.0016663 | -0.0031402 | -0.0024566 | -0.00030524 | -0.0017688 | 0.064606 | 0.063613 | -0.0073507 | 0.00098693 | -0.00074771 | 0.07782 | 62.6266 | -59.7839 | 62.8647 | -59.5367 | -59.9258 | 0.1236 | 0.13733 | 62.6175 | -59.7336 | 62.8143 | -59.7015 | -59.8114 | -59.6695 | -0.05951 | -0.13275 | 0.10529 | 0.18768 | 59.848 | -0.20142 | 59.9075 | -0.14191 | -0.009156 | -0.14191 | 0.054932 | 0.022888 | 0.054931 | -0.086975 | 0.064087 | -0.077819 | 0.24719 | 122.6486 | 0.032044 | 122.5479 | 122.4106 | 122.3511 | 122.3511 | 122.3419 | -122.5433 | -122.493 | 122.5891 | 122.5388 | 59.8022 | 59.8618
142.7656 | 122.6532 | -59.7244 | 62.796 | -0.018234 | 0.0023391 | 0.061812 | 0.079799 | 0.0018799 | 0.0015594 | -0.002243 | -0.030823 | 0.0016492 | 0.064179 | 0.064681 | -0.0060691 | 0.0016277 | 0.00053409 | 0.036621 | 62.645 | -59.7702 | 62.7686 | -59.642 | -60.0174 | 0.059509 | 0.009155 | 62.6541 | -59.7839 | 62.7365 | -59.7839 | -59.7748 | -59.5688 | -0.045777 | -0.15106 | -0.027466 | 0.082397 | 59.7839 | -0.29297 | 59.8297 | -0.24719 | -0.05951 | -0.14191 | -0.05951 | -0.05951 | 0.15564 | -0.050354 | 0.21515 | 0.009156 | 0.12817 | 122.5388 | 0 | 122.5204 | 122.4152 | 122.4381 | 122.3694 | 122.3785 | -122.5662 | -122.58 | 122.493 | 122.4609 | 59.761 | 59.7336
143.7656 | 122.731 | -59.7107 | 62.7594 | -0.048752 | 0.0019119 | 0.063948 | 0.076808 | 0.0040161 | -0.0035674 | 0.001175 | -0.021667 | -0.00070063 | 0.063751 | 0.058272 | -0.0062827 | 0.0020551 | -0.00074771 | 0.068665 | 62.6633 | -59.7748 | 62.8281 | -59.5367 | -59.9304 | 0.10071 | 0.11444 | 62.6678 | -59.7336 | 62.7869 | -59.7198 | -59.8389 | -59.7107 | -0.064087 | -0.09613 | 0.068665 | 0.17395 | 59.8114 | -0.21973 | 59.8755 | -0.15564 | -0.022889 | -0.091552 | 0.027466 | -0.009156 | 0 | -0.12817 | 0.022889 | -0.10529 | 0.23804 | 122.6028 | 0.013733 | 122.5204 | 122.438 | 122.4014 | 122.374 | 122.3785 | -122.5342 | -122.493 | 122.5388 | 122.4976 | 59.7794 | 59.8251
144.7656 | 122.7219 | -59.7198 | 62.7777 | -0.086899 | -1.0718e-05 | 0.064162 | 0.078944 | -0.00046988 | 6.4004e-05 | -0.0026704 | -0.0033568 | 0.00079477 | 0.063965 | 0.069808 | -0.0077779 | 0.0014141 | 0.0016021 | 0.068665 | 62.6358 | -59.7839 | 62.8235 | -59.5551 | -59.935 | 0.07782 | 0.11902 | 62.6358 | -59.7382 | 62.7823 | -59.7336 | -59.848 | -59.7198 | -0.064087 | -0.14191 | 0.045776 | 0.1648 | 59.7977 | -0.21515 | 59.8618 | -0.15106 | -0.01831 | -0.14191 | 0.004578 | -0.013733 | 0 | -0.12817 | 0.01831 | -0.10986 | 0.22888 | 122.6074 | 0.004577 | 122.5204 | 122.4197 | 122.374 | 122.3557 | 122.3557 | -122.5616 | -122.5159 | 122.5433 | 122.5021 | 59.7885 | 59.8389
145.7656 | 122.6532 | -59.7336 | 62.764 | -0.025863 | 0.00084388 | 0.062666 | 0.078944 | -0.0060241 | -0.0042084 | 0.001175 | -0.070496 | 0.00464 | 0.065888 | 0.060836 | -0.0064963 | 0.0016277 | 0.0020295 | 0.009155 | 62.6953 | -59.7885 | 62.6633 | -59.8114 | -60.0815 | 0.036621 | 0.041199 | 62.6633 | -59.7977 | 62.7136 | -59.7931 | -59.8938 | -59.7885 | -0.054931 | -0.068665 | -0.10071 | -0.077819 | 59.7702 | -0.3479 | 59.8251 | -0.29297 | -0.064086 | -0.10071 | -0.050354 | -0.059509 | -0.054931 | -0.16022 | 0.009155 | -0.096131 | -0.022888 | 122.4518 | 0.004577 | 122.5113 | 122.4838 | 122.4609 | 122.4289 | 122.3969 | -122.5525 | -122.5616 | 122.3969 | 122.4472 | 59.7427 | 59.7748
146.7656 | 122.6486 | -59.7107 | 62.7686 | -0.056381 | 0.0031937 | 0.060744 | 0.079799 | 0.0018799 | -0.002713 | 0.001175 | -0.046081 | -0.00091423 | 0.06482 | 0.063826 | -0.0054281 | 0.0014141 | -0.00096131 | 0.19226 | 62.7136 | -59.7748 | 62.7182 | -59.6603 | -60.022 | 0.018311 | 0.013733 | 62.6541 | -59.7656 | 62.7365 | -59.8068 | -59.903 | -59.761 | -0.064087 | -0.054932 | -0.050354 | 0.050354 | 59.729 | -0.31128 | 59.7931 | -0.24719 | -0.054932 | -0.11444 | -0.032044 | -0.096131 | -0.050354 | -0.19226 | 0.004578 | -0.13733 | 0.11444 | 122.493 | -0.041199 | 122.5021 | 122.4884 | 122.4197 | 122.4243 | 122.3648 | -122.5433 | -122.5342 | 122.4289 | 122.4472 | 59.903 | 59.7244
147.7656 | 122.6852 | -59.729 | 62.7869 | -0.056381 | 0.00041648 | 0.062453 | 0.079585 | -0.0011109 | -0.0007904 | 0.00096124 | -0.046081 | 0.0014356 | 0.06482 | 0.062972 | -0.0082053 | 0.0022687 | -0.00010671 | -0.013733 | 62.677 | -59.8022 | 62.7182 | -59.6786 | -60.0037 | 0.041199 | 0.009155 | 62.6816 | -59.7702 | 62.7365 | -59.7931 | -59.9258 | -59.7794 | -0.073242 | -0.10986 | -0.068664 | 0.050354 | 59.7702 | -0.27466 | 59.8434 | -0.20142 | -0.041199 | -0.10529 | -0.050354 | -0.064087 | -0.050354 | -0.19684 | -0.009155 | -0.15564 | 0.1236 | 122.5204 | -0.022888 | 122.5067 | 122.4792 | 122.4518 | 122.406 | 122.4106 | -122.5891 | -122.5571 | 122.4472 | 122.4655 | 59.7153 | 59.7382
148.7656 | 122.6807 | -59.7382 | 62.7777 | -0.010605 | -0.00043792 | 0.062453 | 0.077235 | -0.0028199 | -0.0012176 | -0.00010676 | -0.036926 | 0.002931 | 0.06482 | 0.061904 | -0.0060691 | 0.0018413 | 0.0013885 | -0.013733 | 62.6907 | -59.816 | 62.7365 | -59.6649 | -60.0311 | 0.018311 | 0.018311 | 62.6404 | -59.7702 | 62.7274 | -59.7977 | -59.8984 | -59.7702 | -0.07782 | -0.086975 | -0.041199 | 0.073242 | 59.7565 | -0.29297 | 59.8343 | -0.21515 | -0.032044 | -0.13733 | -0.050354 | -0.059509 | -0.032044 | -0.16022 | 0 | -0.12817 | 0.15106 | 122.5525 | -0.027465 | 122.4976 | 122.5067 | 122.4106 | 122.4289 | 122.3785 | -122.5937 | -122.5479 | 122.4747 | 122.4655 | 59.7244 | 59.7565
149.7656 | 122.7036 | -59.7336 | 62.7777 | -0.025863 | -0.00086512 | 0.061598 | 0.079585 | 0.0050843 | -0.0005768 | -0.00074776 | -0.06134 | 0.001222 | 0.064392 | 0.067031 | -0.0060691 | 0.00098693 | 0.0024567 | 0.018311 | 62.6816 | -59.816 | 62.7457 | -59.6695 | -60.0266 | 0.022888 | 0.009155 | 62.6633 | -59.761 | 62.7731 | -59.7748 | -59.8892 | -59.7427 | -0.082397 | -0.09613 | -0.032043 | 0.064087 | 59.7565 | -0.29297 | 59.8389 | -0.21057 | -0.027465 | -0.11444 | -0.004578 | -0.041198 | -0.009155 | -0.15564 | 0.01831 | -0.12817 | 0.14648 | 122.5616 | -0.013733 | 122.5342 | 122.4976 | 122.4243 | 122.4152 | 122.3969 | -122.5937 | -122.5388 | 122.4792 | 122.5067 | 59.7519 | 59.7427
150.7656 | 122.6715 | -59.7473 | 62.7869 | -0.041122 | -0.00043792 | 0.060957 | 0.079158 | 0.0016663 | -0.0035674 | -0.001175 | -0.046081 | -5.9826e-05 | 0.066529 | 0.062758 | -0.0067099 | 0.0018413 | -0.00032051 | 0 | 62.6862 | -59.8068 | 62.7274 | -59.6649 | -60.0174 | 0.013733 | 0.004578 | 62.6633 | -59.7839 | 62.7228 | -59.8068 | -59.903 | -59.761 | -0.05951 | -0.10071 | -0.059509 | 0.082397 | 59.761 | -0.27008 | 59.8206 | -0.21057 | -0.036622 | -0.1236 | -0.064087 | -0.05951 | -0.013733 | -0.15564 | 0.022889 | -0.11902 | 0.14191 | 122.5342 | -0.022888 | 122.5067 | 122.493 | 122.4472 | 122.4335 | 122.4106 | -122.5937 | -122.5708 | 122.4747 | 122.4701 | 59.7473 | 59.7519
151.7656 | 122.6669 | -59.729 | 62.7914 | -0.0029755 | 0.00020288 | 0.062666 | 0.079372 | -0.0011109 | -0.0005768 | -0.00053396 | -0.06134 | 0.00036737 | 0.066101 | 0.063399 | -0.0047873 | 0.0022687 | 0.00010689 | 0 | 62.6724 | -59.7794 | 62.7274 | -59.6649 | -60.0266 | 0.022888 | 0.009155 | 62.6633 | -59.761 | 62.7228 | -59.7977 | -59.9075 | -59.7794 | -0.050354 | -0.11902 | -0.064087 | 0.064087 | 59.7519 | -0.29755 | 59.8022 | -0.24719 | -0.032043 | -0.12817 | -0.068665 | -0.068664 | -0.050354 | -0.17853 | -0.018311 | -0.14649 | 0.11444 | 122.5067 | -0.036621 | 122.4838 | 122.4518 | 122.4243 | 122.4014 | 122.3923 | -122.5708 | -122.5525 | 122.4564 | 122.4518 | 59.729 | 59.7382
152.7656 | 122.6898 | -59.7382 | 62.7457 | -0.033493 | -1.0718e-05 | 0.06288 | 0.078944 | 0.0016663 | 0.0011322 | 0.00053404 | -0.046081 | 0.0018628 | 0.066742 | 0.065322 | -0.0082053 | 0.0031231 | -0.0020295 | 0.018311 | 62.6724 | -59.8068 | 62.7594 | -59.6375 | -59.9991 | 0.036621 | 0.050354 | 62.6495 | -59.7748 | 62.7823 | -59.7382 | -59.8709 | -59.7336 | -0.068665 | -0.073243 | 0.013732 | 0.10071 | 59.7748 | -0.26093 | 59.8434 | -0.19226 | -0.036621 | -0.096131 | 0.036621 | 0 | 0.004577 | -0.13275 | 0.041198 | -0.096131 | 0.16937 | 122.5662 | 0.036621 | 122.5571 | 122.4792 | 122.4243 | 122.4106 | 122.3877 | -122.5525 | -122.5204 | 122.4976 | 122.5204 | 59.7565 | 59.7885
153.7656 | 122.7173 | -59.7473 | 62.7548 | -0.056381 | 0.0021255 | 0.062453 | 0.079585 | 0.0040161 | -0.0003632 | 0.00032044 | -0.046081 | 0.00079477 | 0.064606 | 0.057845 | -0.0075643 | 0.0014141 | -0.0052337 | 0.013733 | 62.6816 | -59.7885 | 62.7457 | -59.6375 | -59.9991 | 0.022888 | 0.032043 | 62.6541 | -59.7748 | 62.764 | -59.7656 | -59.8663 | -59.7519 | -0.041199 | -0.073242 | -0.009155 | 0.10986 | 59.7702 | -0.25177 | 59.8114 | -0.21057 | -0.027466 | -0.10071 | 0.009155 | -0.018311 | -0.004578 | -0.11902 | 0.022888 | -0.091553 | 0.15106 | 122.5342 | 0.009155 | 122.5388 | 122.4701 | 122.4289 | 122.4289 | 122.4014 | -122.5433 | -122.5296 | 122.493 | 122.5113 | 59.761 | 59.7794
154.7656 | 122.7127 | -59.7244 | 62.7594 | -0.048752 | 0.00041648 | 0.063521 | 0.079585 | 0.0016663 | -0.0014312 | 0.0020294 | -0.052185 | 0.0014356 | 0.065888 | 0.067885 | -0.0071371 | 0.0039777 | -0.00010671 | 0.009155 | 62.6816 | -59.8114 | 62.7731 | -59.6237 | -59.9945 | 0.013733 | 0.041199 | 62.6587 | -59.7656 | 62.764 | -59.7565 | -59.8984 | -59.7382 | -0.086975 | -0.077819 | 0.013733 | 0.10071 | 59.7382 | -0.27008 | 59.8251 | -0.18311 | -0.041199 | -0.10071 | 0.004578 | -0.032044 | -0.013733 | -0.17395 | 0.027466 | -0.13275 | 0.18768 | 122.5845 | 0.009155 | 122.5296 | 122.493 | 122.4243 | 122.406 | 122.3831 | -122.5708 | -122.525 | 122.4976 | 122.4884 | 59.7336 | 59.7656
155.7656 | 122.7036 | -59.729 | 62.7548 | -0.010605 | 0.0012711 | 0.062666 | 0.079372 | 0.0010253 | -0.0024994 | 0.0037384 | -0.046081 | 0.0010084 | 0.06482 | 0.062972 | -0.0079917 | 0.0035503 | -0.0018157 | 0.022888 | 62.6816 | -59.816 | 62.7457 | -59.6191 | -59.9991 | 0.022888 | 0.045776 | 62.6404 | -59.761 | 62.764 | -59.7473 | -59.8892 | -59.729 | -0.086975 | -0.073242 | -0.009155 | 0.10986 | 59.7519 | -0.27008 | 59.8389 | -0.18311 | -0.032043 | -0.11444 | 0.009155 | -0.01831 | 0 | -0.16022 | 0.032043 | -0.12817 | 0.19684 | 122.5616 | 0.013733 | 122.525 | 122.4976 | 122.4014 | 122.4106 | 122.3694 | -122.5708 | -122.5159 | 122.4747 | 122.493 | 59.7519 | 59.7748
156.7656 | 122.6807 | -59.7473 | 62.7365 | -0.20897 | 0.0021255 | 0.063521 | 0.079799 | -0.0015381 | -0.0024994 | 0.00074764 | -0.052185 | 0.00079477 | 0.065247 | 0.065535 | -0.0090597 | 0.0041913 | 0.00074769 | -0.009155 | 62.6358 | -59.8297 | 62.7686 | -59.5779 | -59.9854 | 0.027466 | 0.036621 | 62.6129 | -59.7794 | 62.764 | -59.7748 | -59.8892 | -59.729 | -0.082398 | -0.10071 | 0.032044 | 0.16937 | 59.7748 | -0.23804 | 59.8572 | -0.15564 | -0.032044 | -0.1236 | 0.027466 | -0.027466 | 0.01831 | -0.14191 | 0.050354 | -0.10986 | 0.25177 | 122.5983 | 0.004578 | 122.5433 | 122.4655 | 122.3923 | 122.3831 | 122.3602 | -122.5662 | -122.5159 | 122.5159 | 122.5113 | 59.7382 | 59.7839
157.7656 | 122.7036 | -59.7336 | 62.764 | -0.010605 | 0.00084388 | 0.062025 | 0.076594 | -4.2682e-05 | 0.000705 | -0.0013886 | -0.052185 | -0.00070063 | 0.066315 | 0.062545 | -0.0069235 | 0.00077333 | -0.00096131 | 0.013733 | 62.6495 | -59.8068 | 62.7594 | -59.6237 | -59.9854 | 0.027466 | 0.041199 | 62.6404 | -59.7656 | 62.7731 | -59.7656 | -59.8984 | -59.7244 | -0.073242 | -0.11444 | -0.004578 | 0.10986 | 59.761 | -0.25177 | 59.8343 | -0.17853 | -0.032043 | -0.1236 | 0.009155 | -0.032043 | 0.009156 | -0.16479 | 0.041199 | -0.13275 | 0.18311 | 122.5662 | 0 | 122.5388 | 122.4564 | 122.406 | 122.3831 | 122.374 | -122.5708 | -122.5296 | 122.493 | 122.5067 | 59.7473 | 59.7748
158.7656 | 122.7219 | -59.729 | 62.7548 | -0.010605 | 0.00084388 | 0.061385 | 0.079799 | -0.0011109 | -0.0029266 | -0.0043792 | -0.015564 | -0.00091423 | 0.066742 | 0.065535 | -0.0086325 | 0.0035503 | 0.0028839 | 0.013733 | 62.6907 | -59.8022 | 62.7548 | -59.6283 | -60.0082 | 0.041199 | 0.041199 | 62.6495 | -59.7748 | 62.764 | -59.7519 | -59.8984 | -59.7336 | -0.073242 | -0.064087 | 0 | 0.10071 | 59.7702 | -0.27924 | 59.8434 | -0.20599 | -0.045776 | -0.10529 | 0.009155 | -0.022888 | -0.004578 | -0.16937 | 0.041198 | -0.1236 | 0.17395 | 122.5571 | 0.022888 | 122.5388 | 122.493 | 122.4243 | 122.4197 | 122.3785 | -122.5571 | -122.5296 | 122.4838 | 122.493 | 59.7427 | 59.7702
159.7656 | 122.7127 | -59.7427 | 62.7365 | -0.041122 | 0.0016983 | 0.065871 | 0.079372 | 0.0042297 | 0.0004914 | 0.0013886 | -0.046081 | 0.0020764 | 0.06546 | 0.058058 | -0.0075643 | 0.0048321 | -0.00032051 | -0.15106 | 62.6221 | -59.8206 | 62.764 | -59.6237 | -59.9899 | 0.027466 | 0.036621 | 62.6266 | -59.7702 | 62.7411 | -59.7748 | -59.8846 | -59.7244 | -0.07782 | -0.11444 | 0.027466 | 0.11902 | 59.7702 | -0.24719 | 59.848 | -0.16937 | -0.027466 | -0.10986 | 0.004578 | -0.032043 | 0.018311 | -0.14191 | 0.045777 | -0.11444 | 0.19684 | 122.5845 | -0.004577 | 122.5113 | 122.4426 | 122.3969 | 122.3648 | 122.3694 | -122.5571 | -122.5067 | 122.5067 | 122.4838 | 59.5917 | 59.7794
160.7656 | 122.7173 | -59.761 | 62.7457 | -0.048752 | 0.0021255 | 0.066725 | 0.079585 | 0.0010253 | -0.0029266 | -0.00032036 | -0.030823 | 0.001222 | 0.064606 | 0.06938 | -0.0067099 | 0.0026959 | 0.0033111 | -0.086975 | 62.6495 | -59.816 | 62.7731 | -59.6191 | -59.9991 | 0.036621 | 0.059509 | 62.6495 | -59.761 | 62.7686 | -59.7748 | -59.8755 | -59.7153 | -0.054932 | -0.096131 | 0.027465 | 0.14191 | 59.7977 | -0.23804 | 59.8526 | -0.18311 | 0 | -0.096131 | 0.022888 | -0.013733 | 0.045776 | -0.11444 | 0.045776 | -0.11444 | 0.19684 | 122.5891 | -0.013733 | 122.5296 | 122.4655 | 122.4106 | 122.4106 | 122.4106 | -122.5616 | -122.5067 | 122.5342 | 122.5296 | 59.6741 | 59.8206
161.7656 | 122.6898 | -59.7336 | 62.7548 | -0.056381 | -0.00022432 | 0.067793 | 0.078944 | 0.0023071 | -0.0024994 | -0.0024566 | -0.036926 | 0.0010084 | 0.065674 | 0.065749 | -0.0064963 | 0.0026959 | -0.00074771 | -0.16479 | 62.6221 | -59.8297 | 62.7731 | -59.6191 | -59.9899 | 0.032043 | 0.032043 | 62.6175 | -59.7565 | 62.764 | -59.7656 | -59.8892 | -59.7336 | -0.09613 | -0.13275 | 0.01831 | 0.11444 | 59.7656 | -0.25635 | 59.8618 | -0.16022 | -0.022888 | -0.13733 | 0.009155 | -0.032043 | 0 | -0.15564 | 0.022888 | -0.13275 | 0.21057 | 122.6028 | -0.009155 | 122.5204 | 122.4518 | 122.374 | 122.3557 | 122.3511 | -122.5845 | -122.5113 | 122.5067 | 122.4976 | 59.5688 | 59.7656
162.7656 | 122.7402 | -59.7382 | 62.7594 | -0.056381 | 0.0046891 | 0.065443 | 0.077663 | 0.00038452 | -0.0033538 | 0.0020294 | -0.027771 | -0.00027343 | 0.066101 | 0.059767 | -0.0084189 | 0.0026959 | 0.0028839 | -0.16937 | 62.6175 | -59.8114 | 62.7777 | -59.6283 | -59.9762 | 0.036621 | 0.054932 | 62.6358 | -59.7702 | 62.7686 | -59.7748 | -59.8801 | -59.7244 | -0.073242 | -0.14191 | 0.018311 | 0.10986 | 59.7748 | -0.23804 | 59.848 | -0.1648 | -0.032044 | -0.1236 | 0.009156 | -0.036621 | 0.013733 | -0.14191 | 0.045777 | -0.10986 | 0.1831 | 122.5891 | -0.004577 | 122.5388 | 122.4289 | 122.406 | 122.3557 | 122.374 | -122.5708 | -122.5296 | 122.5159 | 122.5067 | 59.5688 | 59.7931
163.7656 | 122.6761 | -59.7382 | 62.7731 | -0.079269 | 0.00020288 | 0.062666 | 0.078303 | 0.0025207 | 0.0002778 | 0.00010684 | -0.036926 | 0.00079477 | 0.067383 | 0.067031 | -0.0062827 | 0.0031231 | -0.0022431 | -0.009155 | 62.6358 | -59.8114 | 62.7365 | -59.6375 | -60.0357 | -0.032043 | -0.013733 | 62.6312 | -59.7885 | 62.7182 | -59.8251 | -59.9442 | -59.7565 | -0.073242 | -0.13733 | -0.036621 | 0.10071 | 59.7061 | -0.29755 | 59.7794 | -0.22431 | -0.050354 | -0.14191 | -0.054931 | -0.086975 | -0.018311 | -0.20599 | 0.032043 | -0.15564 | 0.17395 | 122.5479 | -0.036621 | 122.5067 | 122.4472 | 122.4197 | 122.374 | 122.3694 | -122.5845 | -122.5616 | 122.4747 | 122.4564 | 59.729 | 59.7244
164.7656 | 122.7127 | -59.761 | 62.7365 | -0.010605 | 0.0014847 | 0.065443 | 0.078517 | 0.0029479 | 6.4004e-05 | 0.00053404 | -0.024719 | 0.00079477 | 0.065033 | 0.060836 | -0.0071371 | 0.0018413 | 0.0030975 | -0.068665 | 62.6083 | -59.8068 | 62.7731 | -59.6329 | -59.9991 | 0.041199 | 0.036621 | 62.6495 | -59.7656 | 62.7502 | -59.7656 | -59.8755 | -59.729 | -0.045777 | -0.12817 | 0.036621 | 0.12817 | 59.8022 | -0.23804 | 59.848 | -0.19226 | -0.004578 | -0.086975 | 0.013733 | -0.004578 | 0.032043 | -0.11444 | 0.036621 | -0.10986 | 0.17395 | 122.58 | 0 | 122.5159 | 122.4152 | 122.4152 | 122.3694 | 122.4106 | -122.5433 | -122.5021 | 122.5342 | 122.5113 | 59.6924 | 59.7977
165.7656 | 122.7219 | -59.7427 | 62.7594 | -0.018234 | 0.00020288 | 0.063521 | 0.08044 | 0.0029479 | -0.0020722 | -0.0018158 | -0.0064086 | -0.00070063 | 0.064179 | 0.066817 | -0.0071371 | 0.0029095 | -0.00074771 | 0.073242 | 62.6312 | -59.8068 | 62.7869 | -59.6054 | -60.022 | 0.022888 | 0.045776 | 62.6175 | -59.7702 | 62.7686 | -59.761 | -59.8846 | -59.7244 | -0.064087 | -0.12817 | 0.027466 | 0.13733 | 59.7656 | -0.27924 | 59.8297 | -0.21515 | -0.027466 | -0.14191 | 0.009156 | -0.01831 | 0.018311 | -0.14191 | 0.045777 | -0.11444 | 0.20142 | 122.5937 | 0.009156 | 122.5388 | 122.4381 | 122.3877 | 122.374 | 122.3602 | -122.5662 | -122.5296 | 122.5296 | 122.5113 | 59.816 | 59.7885
166.7656 | 122.6669 | -59.761 | 62.7777 | -0.041122 | 0.0010575 | 0.063521 | 0.078303 | 0.0042297 | -0.0007904 | -0.0013886 | -0.018616 | 0.0020764 | 0.065247 | 0.063613 | -0.0086325 | 0.0018413 | 0.0022431 | 0 | 62.645 | -59.7794 | 62.7457 | -59.6512 | -60.0357 | -0.032043 | -0.027466 | 62.6358 | -59.7794 | 62.7228 | -59.816 | -59.9304 | -59.7702 | -0.018311 | -0.13275 | -0.032043 | 0.10986 | 59.729 | -0.27466 | 59.7473 | -0.25635 | -0.018311 | -0.14191 | -0.054932 | -0.054932 | -0.009156 | -0.16937 | 0.009155 | -0.15106 | 0.12817 | 122.525 | -0.036621 | 122.5021 | 122.4243 | 122.4152 | 122.406 | 122.3969 | -122.5571 | -122.5571 | 122.5067 | 122.4838 | 59.761 | 59.7336
167.7656 | 122.6715 | -59.7336 | 62.7411 | -0.056381 | 0.0029801 | 0.064589 | 0.08044 | 0.0010253 | 0.0004914 | -0.00010676 | -0.018616 | -0.00091423 | 0.064392 | 0.063826 | -0.0079917 | 0.0035503 | -0.0033111 | -0.022888 | 62.6495 | -59.7839 | 62.7411 | -59.6375 | -60.0266 | -0.018311 | -0.022888 | 62.6038 | -59.7794 | 62.7136 | -59.816 | -59.935 | -59.7565 | -0.050354 | -0.091553 | 0 | 0.096131 | 59.7153 | -0.29297 | 59.7656 | -0.24261 | -0.045776 | -0.13733 | -0.027466 | -0.082397 | -0.022888 | -0.20142 | 0.022888 | -0.15564 | 0.14648 | 122.525 | -0.036621 | 122.493 | 122.4335 | 122.3831 | 122.3831 | 122.3373 | -122.525 | -122.5204 | 122.4747 | 122.4472 | 59.7107 | 59.7107
168.7656 | 122.6898 | -59.7427 | 62.7731 | -0.10979 | 0.0014847 | 0.063521 | 0.079158 | 0.0016663 | -0.002713 | -0.0013886 | 0.0057984 | 0.00036737 | 0.065033 | 0.06404 | -0.0067099 | 0.0018413 | -0.0022431 | 0.004578 | 62.6633 | -59.8206 | 62.7411 | -59.6329 | -60.0357 | -0.013733 | -0.041199 | 62.6266 | -59.7885 | 62.7274 | -59.8206 | -59.9304 | -59.7702 | -0.07782 | -0.10986 | -0.032043 | 0.10986 | 59.729 | -0.29297 | 59.8068 | -0.21515 | -0.045776 | -0.14648 | -0.045776 | -0.07782 | -0.027466 | -0.18768 | 0.01831 | -0.14191 | 0.18768 | 122.5616 | -0.032044 | 122.5159 | 122.4838 | 122.4152 | 122.406 | 122.3694 | -122.5937 | -122.5616 | 122.4838 | 122.4701 | 59.7473 | 59.7015
169.7656 | 122.6395 | -59.7794 | 62.7686 | -0.041122 | 0.0016983 | 0.062666 | 0.078517 | 0.0033753 | -0.0007904 | 0.00074764 | -0.018616 | 0.00058097 | 0.063111 | 0.060408 | -0.0060691 | 0.0039777 | 0.0011749 | -0.054932 | 62.6312 | -59.816 | 62.6816 | -59.7015 | -60.0815 | -0.082397 | -0.13275 | 62.6083 | -59.7885 | 62.6678 | -59.8572 | -59.9945 | -59.8251 | -0.036621 | -0.13733 | -0.086975 | 0.07782 | 59.697 | -0.30212 | 59.7336 | -0.2655 | -0.009155 | -0.16022 | -0.10071 | -0.07782 | -0.045776 | -0.21515 | -0.036621 | -0.20599 | 0.11444 | 122.4976 | -0.068665 | 122.4564 | 122.4472 | 122.3969 | 122.4106 | 122.3877 | -122.5845 | -122.5571 | 122.4609 | 122.4472 | 59.7244 | 59.6466
170.7656 | 122.6349 | -59.7794 | 62.7411 | -0.06401 | 0.00020288 | 0.063948 | 0.077876 | 0.0027343 | -0.0003632 | 0.00074764 | -0.049133 | 0.00229 | 0.066101 | 0.062545 | -0.0052145 | 0.0048321 | -0.00053411 | -0.050354 | 62.6495 | -59.8343 | 62.6862 | -59.6878 | -60.0906 | -0.09613 | -0.12817 | 62.6312 | -59.8114 | 62.6724 | -59.8663 | -59.9899 | -59.8068 | -0.054932 | -0.091553 | -0.054932 | 0.091553 | 59.6832 | -0.31128 | 59.7382 | -0.25635 | -0.032043 | -0.10986 | -0.068665 | -0.086975 | -0.027466 | -0.21057 | 0.004577 | -0.17853 | 0.14649 | 122.5204 | -0.054932 | 122.4838 | 122.4838 | 122.4426 | 122.4289 | 122.4106 | -122.5754 | -122.5525 | 122.4655 | 122.4518 | 59.729 | 59.6512
171.7656 | 122.6669 | -59.7427 | 62.7411 | -0.079269 | 0.00063028 | 0.064162 | 0.078517 | 0.0014527 | -0.0035674 | -0.00096136 | -0.0033568 | 0.001222 | 0.064606 | 0.062331 | -0.0079917 | 0.0024823 | 0.00032049 | -0.018311 | 62.645 | -59.8022 | 62.7365 | -59.6237 | -60.0128 | -0.018311 | -0.004578 | 62.6266 | -59.7794 | 62.7319 | -59.8206 | -59.9304 | -59.7519 | -0.059509 | -0.096131 | -0.004578 | 0.11902 | 59.7244 | -0.27008 | 59.7839 | -0.21057 | -0.036621 | -0.11444 | -0.009155 | -0.07782 | -0.009155 | -0.18768 | 0.027466 | -0.15106 | 0.17853 | 122.5388 | -0.041199 | 122.5113 | 122.4472 | 122.406 | 122.3877 | 122.3694 | -122.5433 | -122.5204 | 122.4792 | 122.4747 | 59.7244 | 59.7382
172.7656 | 122.6807 | -59.7473 | 62.7457 | -0.056381 | 0.0010575 | 0.065871 | 0.079158 | 0.00059812 | 0.0004914 | -0.0016022 | -0.027771 | 0.0014356 | 0.06546 | 0.067671 | -0.0079917 | 0.0012005 | 0.00096129 | -0.009155 | 62.6633 | -59.816 | 62.7411 | -59.6283 | -60.0357 | -0.018311 | 0.004578 | 62.6266 | -59.7839 | 62.7319 | -59.8068 | -59.9213 | -59.761 | -0.068665 | -0.082398 | -0.004578 | 0.11902 | 59.729 | -0.28839 | 59.7977 | -0.21973 | -0.036622 | -0.11902 | -0.013733 | -0.05951 | -0.013733 | -0.17395 | 0.022889 | -0.13733 | 0.18768 | 122.5571 | -0.022888 | 122.5159 | 122.4792 | 122.4106 | 122.4106 | 122.374 | -122.5616 | -122.5296 | 122.4884 | 122.4792 | 59.7382 | 59.7519
173.7656 | 122.6578 | -59.7565 | 62.7411 | -0.086899 | -0.0021469 | 0.064803 | 0.08044 | 0.0033753 | -0.0024994 | -0.0013886 | -0.033874 | -0.00091423 | 0.06546 | 0.061904 | -0.0090597 | 0.0031231 | 0.0016021 | -0.054932 | 62.6678 | -59.8114 | 62.6953 | -59.6878 | -60.0632 | -0.068665 | -0.09613 | 62.5946 | -59.7885 | 62.6953 | -59.8709 | -59.9716 | -59.7931 | -0.054931 | -0.073242 | -0.045777 | 0.068665 | 59.6878 | -0.3067 | 59.7427 | -0.25177 | -0.032043 | -0.14649 | -0.045777 | -0.11444 | -0.036621 | -0.21515 | -0.004578 | -0.18311 | 0.1236 | 122.5067 | -0.082398 | 122.4838 | 122.4792 | 122.3831 | 122.4243 | 122.3511 | -122.5525 | -122.5296 | 122.4518 | 122.4518 | 59.7015 | 59.6603
174.7656 | 122.6669 | -59.7519 | 62.7502 | -0.079269 | 0.0025529 | 0.064375 | 0.081721 | 0.0025207 | 0.0004914 | -0.00032036 | -0.039978 | -0.00070063 | 0.064179 | 0.065749 | -0.0075643 | 0.0014141 | 0.00074769 | -0.041199 | 62.6495 | -59.8251 | 62.7045 | -59.6924 | -60.0723 | -0.068665 | -0.091553 | 62.6358 | -59.7885 | 62.709 | -59.8526 | -59.9854 | -59.7977 | -0.073242 | -0.10071 | -0.045776 | 0.059509 | 59.6832 | -0.32044 | 59.7565 | -0.24719 | -0.036621 | -0.11444 | -0.041199 | -0.10071 | -0.045776 | -0.23346 | -0.009155 | -0.19684 | 0.13275 | 122.5296 | -0.064087 | 122.4976 | 122.4747 | 122.4243 | 122.4014 | 122.3877 | -122.5754 | -122.5388 | 122.4564 | 122.4609 | 59.7107 | 59.6603
175.7656 | 122.6349 | -59.7656 | 62.7228 | -0.086899 | 0.0014847 | 0.064589 | 0.078731 | 0.0010253 | -0.0022858 | -0.0018158 | -0.036926 | -0.00027343 | 0.065033 | 0.062117 | -0.0060691 | 0.0012005 | -0.0048065 | -0.041199 | 62.6358 | -59.8206 | 62.6999 | -59.6741 | -60.0632 | -0.059509 | -0.07782 | 62.6175 | -59.7794 | 62.6816 | -59.8572 | -59.9762 | -59.7839 | -0.054932 | -0.086975 | -0.022888 | 0.091553 | 59.7061 | -0.29755 | 59.761 | -0.24261 | -0.013733 | -0.10528 | -0.041198 | -0.091553 | -0.018311 | -0.21057 | -0.004578 | -0.19684 | 0.14648 | 122.5204 | -0.07782 | 122.4609 | 122.4564 | 122.3969 | 122.4014 | 122.3831 | -122.5433 | -122.5021 | 122.4655 | 122.4472 | 59.7244 | 59.6878
176.7656 | 122.6578 | -59.7519 | 62.7548 | -0.094528 | 0.00063028 | 0.065016 | 0.080012 | 0.00017092 | -0.0022858 | 0.00010684 | -0.0094604 | -0.00027343 | 0.066742 | 0.06404 | -0.0067099 | 0.0018413 | 0.0024567 | -0.041199 | 62.6312 | -59.8297 | 62.709 | -59.6695 | -60.0632 | -0.050354 | -0.068665 | 62.6175 | -59.7794 | 62.6862 | -59.8297 | -59.9716 | -59.7748 | -0.07782 | -0.1236 | -0.045777 | 0.082397 | 59.7015 | -0.31128 | 59.7794 | -0.23346 | -0.027466 | -0.13733 | -0.068665 | -0.07782 | -0.022888 | -0.21973 | 0.004578 | -0.19226 | 0.16022 | 122.5388 | -0.050354 | 122.4655 | 122.4609 | 122.3969 | 122.3831 | 122.3694 | -122.5845 | -122.5342 | 122.4609 | 122.438 | 59.7107 | 59.6832
177.7656 | 122.6349 | -59.7519 | 62.7548 | -0.094528 | 0.0027665 | 0.063521 | 0.078303 | 0.00017092 | -0.0016448 | -0.0026704 | 0.021057 | 0.0016492 | 0.065033 | 0.055709 | -0.0082053 | 0.00098693 | 0.0013885 | -0.09613 | 62.6312 | -59.8297 | 62.6495 | -59.7519 | -60.1318 | -0.13275 | -0.37537 | 62.5534 | -59.8434 | 62.6724 | -59.8755 | -59.9625 | -59.7748 | -0.07782 | -0.1236 | -0.10529 | 0 | 59.6191 | -0.37994 | 59.697 | -0.30212 | -0.091553 | -0.20142 | -0.082398 | -0.1236 | -0.022888 | -0.21057 | 0.068665 | -0.11902 | 0.07782 | 122.4792 | -0.032043 | 122.5159 | 122.4609 | 122.3969 | 122.3831 | 122.3053 | -122.5845 | -122.5983 | 122.4014 | 122.4243 | 59.6558 | 59.3765
178.7656 | 122.6669 | -59.7702 | 62.7457 | -0.07164 | -0.0010787 | 0.062025 | 0.077663 | 0.0025207 | 0.0015594 | -0.0016022 | -0.024719 | 0.00229 | 0.065674 | 0.066176 | -0.0064963 | 0.0029095 | 0.0020295 | -0.022888 | 62.6495 | -59.7977 | 62.6953 | -59.6512 | -60.054 | -0.050354 | -0.068665 | 62.6312 | -59.7748 | 62.6999 | -59.8389 | -59.9487 | -59.761 | -0.027465 | -0.096131 | -0.050355 | 0.11902 | 59.7198 | -0.28381 | 59.7473 | -0.25635 | -0.004577 | -0.11444 | -0.045777 | -0.068664 | 0.009156 | -0.17853 | 0.013733 | -0.17395 | 0.14648 | 122.493 | -0.064087 | 122.4747 | 122.4472 | 122.406 | 122.4197 | 122.4014 | -122.5433 | -122.5204 | 122.4655 | 122.4701 | 59.7473 | 59.7015
179.7656 | 122.6578 | -59.7565 | 62.7502 | -0.10216 | 0.0027665 | 0.065016 | 0.080653 | 0.0033753 | 0.0002778 | 0.00074764 | -0.027771 | 0.00079477 | 0.062683 | 0.066817 | -0.0077779 | 0.0012005 | 0.0039521 | -0.018311 | 62.6633 | -59.7885 | 62.6999 | -59.6649 | -60.0586 | -0.036621 | -0.054932 | 62.6221 | -59.7794 | 62.6999 | -59.8389 | -59.9533 | -59.7839 | -0.032043 | -0.086975 | -0.050354 | 0.091553 | 59.7198 | -0.30212 | 59.7519 | -0.27008 | -0.022888 | -0.12817 | -0.050354 | -0.082397 | -0.027466 | -0.19684 | -0.004578 | -0.17395 | 0.1236 | 122.4884 | -0.059509 | 122.4792 | 122.4518 | 122.4014 | 122.4197 | 122.3785 | -122.5388 | -122.5296 | 122.4564 | 122.4564 | 59.7382 | 59.7015
180.7656 | 122.6807 | -59.761 | 62.7594 | -0.06401 | 0.0021255 | 0.063734 | 0.079158 | 0.0029479 | -0.0022858 | -0.00074776 | -0.039978 | -5.9826e-05 | 0.06781 | 0.065749 | -0.0067099 | 0.0018413 | -0.00032051 | -0.07782 | 62.6312 | -59.8251 | 62.677 | -59.7153 | -60.0998 | -0.09613 | -0.13733 | 62.6221 | -59.7931 | 62.5626 | -60.2142 | -59.8068 | -59.6191 | -0.064087 | -0.12817 | -0.082397 | 0.045776 | 59.6649 | -0.33875 | 59.729 | -0.27466 | -0.032044 | -0.13733 | -0.19684 | -0.45319 | 0.14191 | -0.045777 | 0.17395 | -0.013733 | 0.10986 | 122.5021 | -0.42114 | 122.3557 | 122.4564 | 122.4152 | 122.3923 | 122.3831 | -122.5845 | -122.5525 | 122.438 | 122.3236 | 59.6832 | 59.6237
181.7656 | 122.5296 | -59.8068 | 62.7182 | -0.11742 | 0.0027665 | 0.064803 | 0.081081 | 0.0052979 | 0.0002778 | 0.00096124 | -0.033874 | 0.00079477 | 0.063751 | 0.062117 | -0.0082053 | 0.00077333 | -0.00010671 | -0.073242 | 62.6404 | -59.8068 | 62.6816 | -59.7153 | -60.1135 | -0.09613 | -0.15106 | 62.6312 | -59.8114 | 62.645 | -59.8892 | -60.1913 | -60.1273 | 0 | -0.07782 | -0.036621 | 0.091553 | 59.7107 | -0.3067 | 59.7107 | -0.3067 | -0.004577 | -0.086975 | -0.073243 | -0.082397 | -0.32043 | -0.38452 | -0.31586 | -0.37994 | 0.091553 | 122.4884 | -0.07782 | 122.4564 | 122.4472 | 122.4426 | 122.4472 | 122.4381 | -122.525 | -122.5296 | 122.4884 | 122.4518 | 59.7336 | 59.6558
182.7656 | 122.6028 | -59.7977 | 62.6816 | -0.10216 | 0.0021255 | 0.064589 | 0.081294 | 0.0014527 | -0.0001496 | -0.0020294 | -0.036926 | -0.00027343 | 0.064606 | 0.062117 | -0.0071371 | 0.0022687 | -0.00074771 | -0.050354 | 62.6587 | -59.8343 | 62.677 | -59.7061 | -60.1089 | -0.10529 | -0.14648 | 62.6175 | -59.7977 | 62.6678 | -59.8801 | -60.0037 | -59.8297 | -0.036622 | -0.022889 | -0.004578 | 0.091552 | 59.6924 | -0.31128 | 59.729 | -0.27466 | 0 | -0.064087 | -0.013733 | -0.082398 | -0.032044 | -0.20599 | -0.032044 | -0.20599 | 0.12817 | 122.5113 | -0.082398 | 122.4655 | 122.493 | 122.4152 | 122.4564 | 122.4152 | -122.5159 | -122.4792 | 122.4747 | 122.4655 | 59.7473 | 59.6512
183.7656 | 122.6395 | -59.7748 | 62.7411 | -0.010605 | 0.00084388 | 0.063307 | 0.081294 | 0.00038452 | -0.0005768 | 0.00010684 | -0.024719 | 0.0031446 | 0.064606 | 0.062331 | -0.0075643 | 0.0035503 | -0.0018157 | -0.050354 | 62.6678 | -59.8206 | 62.6404 | -59.7336 | -60.0998 | -0.1236 | -0.16022 | 62.6221 | -59.8206 | 62.6907 | -59.8709 | -59.967 | -59.7977 | -0.045777 | -0.073242 | -0.10071 | 0.041198 | 59.6512 | -0.32501 | 59.697 | -0.27923 | -0.045777 | -0.11902 | -0.050354 | -0.096131 | -0.022888 | -0.19226 | 0.022889 | -0.14648 | 0.086975 | 122.4609 | -0.050354 | 122.5113 | 122.4884 | 122.4426 | 122.4426 | 122.3969 | -122.5616 | -122.5616 | 122.4152 | 122.4655 | 59.7244 | 59.6146
184.7656 | 122.6624 | -59.7794 | 62.7228 | 0.18013 | -0.0017197 | 0.063948 | 0.080653 | 0.0018799 | -0.0012176 | -0.0024566 | -0.039978 | -0.00048703 | 0.065674 | 0.060408 | -0.0082053 | 0.00098693 | 0.0011749 | -0.07782 | 62.6678 | -59.8297 | 62.6541 | -59.729 | -60.0769 | -0.10529 | -0.16479 | 62.5854 | -59.7977 | 62.6724 | -59.848 | -60.0037 | -59.8022 | -0.050354 | -0.054931 | -0.068664 | 0.050354 | 59.6741 | -0.29755 | 59.7244 | -0.24719 | -0.01831 | -0.13733 | -0.050354 | -0.068664 | -0.022888 | -0.2243 | -0.004578 | -0.20599 | 0.10071 | 122.4838 | -0.050354 | 122.4701 | 122.4976 | 122.3831 | 122.4472 | 122.3648 | -122.5525 | -122.5204 | 122.4335 | 122.4518 | 59.7015 | 59.6146
185.7656 | 122.6257 | -59.7839 | 62.7594 | 0.004654 | -0.00065152 | 0.063734 | 0.081081 | 0.0023071 | -0.0012176 | -0.0035248 | -0.036926 | 0.0018628 | 0.066742 | 0.062117 | -0.0071371 | 0.00077333 | -0.0016021 | -0.059509 | 62.6266 | -59.8068 | 62.677 | -59.7061 | -60.0952 | -0.091553 | -0.13275 | 62.6221 | -59.7748 | 62.6816 | -59.8801 | -59.9899 | -59.7931 | -0.022888 | -0.13275 | -0.082397 | 0.07782 | 59.6924 | -0.31128 | 59.7153 | -0.28839 | 0.009156 | -0.13733 | -0.077819 | -0.09613 | -0.009155 | -0.20599 | -0.018311 | -0.21515 | 0.10071 | 122.4838 | -0.10529 | 122.4564 | 122.4335 | 122.3969 | 122.4106 | 122.406 | -122.5662 | -122.5342 | 122.4609 | 122.4655 | 59.7244 | 59.6512
186.7656 | 122.644 | -59.7794 | 62.7274 | -0.10216 | 0.0019119 | 0.06288 | 0.081935 | 0.0016663 | -0.0007904 | 0.00010684 | -0.039978 | 0.00229 | 0.063751 | 0.066817 | -0.0097007 | 0.0035503 | 0.0026703 | -0.054932 | 62.6266 | -59.8114 | 62.677 | -59.697 | -60.0769 | -0.09613 | -0.13733 | 62.6312 | -59.7794 | 62.6816 | -59.8618 | -60.0037 | -59.8022 | -0.032043 | -0.10071 | -0.050354 | 0.082398 | 59.6832 | -0.29755 | 59.7153 | -0.2655 | 0 | -0.09613 | -0.045776 | -0.082397 | -0.022888 | -0.2243 | -0.022888 | -0.2243 | 0.11444 | 122.4884 | -0.082397 | 122.4609 | 122.438 | 122.4106 | 122.406 | 122.4106 | -122.5388 | -122.5067 | 122.4564 | 122.4609 | 59.7244 | 59.642
187.7656 | 122.6395 | -59.7702 | 62.7136 | -0.094528 | 0.0027665 | 0.068861 | 0.080012 | -0.0013245 | -0.0020722 | 0.0016022 | -0.021667 | 0.0014356 | 0.06546 | 0.063826 | -0.0075643 | 0.0018413 | 0.00053409 | -0.39825 | 62.558 | -59.8663 | 62.645 | -59.761 | -60.0906 | -0.091553 | -0.15106 | 62.6083 | -59.7794 | 62.6862 | -59.8618 | -59.9716 | -59.816 | -0.09613 | -0.15564 | -0.068665 | 0.009156 | 59.6787 | -0.32043 | 59.7748 | -0.2243 | -0.009155 | -0.10529 | -0.027466 | -0.091552 | -0.045776 | -0.20142 | -0.036621 | -0.19226 | 0.10529 | 122.5113 | -0.082397 | 122.4655 | 122.4243 | 122.3877 | 122.3282 | 122.3785 | -122.58 | -122.493 | 122.4152 | 122.4564 | 59.3719 | 59.6191
188.7656 | 122.6624 | -59.7565 | 62.7274 | -0.086899 | 0.0014847 | 0.063521 | 0.08044 | -0.0015381 | 6.4004e-05 | -0.00010676 | -0.030823 | -5.9826e-05 | 0.064392 | 0.064681 | -0.0088461 | 0.0022687 | 0.00096129 | 0.013733 | 62.6221 | -59.8892 | 62.709 | -59.6603 | -60.1593 | -0.10071 | -0.15106 | 62.5992 | -59.7977 | 62.6862 | -59.8755 | -59.9625 | -59.7839 | -0.13275 | -0.10529 | -0.018311 | 0.096131 | 59.6558 | -0.40283 | 59.7885 | -0.27008 | -0.041198 | -0.12817 | -0.041199 | -0.11902 | -0.027466 | -0.20599 | 0.013732 | -0.16479 | 0.22888 | 122.5983 | -0.07782 | 122.4838 | 122.5113 | 122.3969 | 122.3785 | 122.3557 | -122.6166 | -122.525 | 122.4655 | 122.4426 | 59.7702 | 59.6054
189.7656 | 122.6532 | -59.7885 | 62.7136 | -0.10216 | 0.00041648 | 0.064162 | 0.078303 | 0.0023071 | -0.0052764 | 0.00010684 | -0.046081 | -0.00048703 | 0.065888 | 0.066176 | -0.0077779 | 0.0022687 | -0.0016021 | -0.09613 | 62.6862 | -59.8389 | 62.7777 | -59.7702 | -60.0037 | -0.050354 | -0.11902 | 62.6312 | -59.7885 | 62.6862 | -59.8755 | -59.9945 | -59.7794 | -0.050354 | -0.027466 | 0.064087 | 0.01831 | 59.7382 | -0.21515 | 59.7885 | -0.16479 | 0 | -0.082397 | -0.027466 | -0.086975 | 0.009155 | -0.20599 | 0.009155 | -0.20599 | 0.068664 | 122.6166 | -0.086975 | 122.4747 | 122.525 | 122.4197 | 122.4747 | 122.4197 | -122.5525 | -122.5021 | 122.5662 | 122.4747 | 59.6924 | 59.6695
190.7656 | 122.7036 | -59.7519 | 62.6953 | -0.06401 | 0.0016983 | 0.065657 | 0.080226 | -0.0015381 | -0.001004 | 0.00074764 | -0.024719 | 0.00015377 | 0.062897 | 0.055709 | -0.0082053 | 0.0039777 | -0.0022431 | -0.11444 | 62.645 | -59.8389 | 62.6678 | -59.7061 | -60.1135 | -0.10529 | -0.13275 | 62.6129 | -59.7931 | 62.7182 | -59.8297 | -59.9533 | -59.7656 | -0.086975 | -0.050354 | -0.027465 | 0.045776 | 59.6466 | -0.36163 | 59.7336 | -0.27466 | -0.041199 | -0.082397 | 0.022889 | -0.07782 | -0.013733 | -0.20142 | 0.027466 | -0.16022 | 0.13275 | 122.5067 | -0.036621 | 122.5113 | 122.4838 | 122.406 | 122.3969 | 122.3648 | -122.5342 | -122.4884 | 122.4197 | 122.4701 | 59.6375 | 59.6191
191.7656 | 122.6669 | -59.761 | 62.7136 | -0.086899 | 0.00020288 | 0.062025 | 0.080012 | -0.0011109 | -0.0024994 | -0.0018158 | -0.030823 | -0.001128 | 0.06482 | 0.061049 | -0.0077779 | 0.0012005 | 0.00032049 | -0.10529 | 62.6312 | -59.8343 | 62.6633 | -59.7107 | -60.0952 | -0.10071 | -0.13733 | 62.5992 | -59.7885 | 62.6999 | -59.8297 | -59.9442 | -59.7702 | -0.073243 | -0.082397 | -0.050354 | 0.050354 | 59.6603 | -0.33417 | 59.7336 | -0.26093 | -0.027466 | -0.11444 | -0.013733 | -0.068665 | -0.009156 | -0.18311 | 0.01831 | -0.15564 | 0.1236 | 122.4976 | -0.041199 | 122.4884 | 122.4655 | 122.3877 | 122.3923 | 122.3602 | -122.5479 | -122.5021 | 122.4243 | 122.4609 | 59.6558 | 59.6237
192.7656 | 122.6349 | -59.7427 | 62.7365 | -0.06401 | 0.0021255 | 0.065657 | 0.080012 | -0.00068368 | -0.0018586 | -0.0020294 | -0.070496 | 0.0010084 | 0.065247 | 0.066176 | -0.0094869 | 0.0018413 | 0.00032049 | -0.10071 | 62.6678 | -59.8389 | 62.8281 | -59.7198 | -60.0266 | -0.041199 | -0.13275 | 62.6358 | -59.7931 | 62.6816 | -59.8709 | -59.9945 | -59.8068 | -0.09613 | -0.068664 | 0.091553 | 0.022888 | 59.7015 | -0.28381 | 59.7977 | -0.18768 | -0.050354 | -0.10071 | -0.054931 | -0.12817 | -0.064087 | -0.25177 | -0.013733 | -0.20142 | 0.11902 | 122.6669 | -0.07782 | 122.4747 | 122.5067 | 122.4289 | 122.4106 | 122.3785 | -122.5754 | -122.5296 | 122.5708 | 122.4243 | 59.642 | 59.61
193.7656 | 122.6212 | -59.7748 | 62.7182 | -0.06401 | 0.0016983 | 0.063734 | 0.079372 | -0.0077331 | -0.0014312 | -0.00053396 | -0.036926 | -0.00091423 | 0.065247 | 0.064253 | -0.0086325 | 0.0024823 | 0.0018159 | -0.10071 | 62.6312 | -59.848 | 62.645 | -59.6924 | -60.0082 | -0.10529 | -0.12817 | 62.645 | -59.7839 | 62.6862 | -59.8892 | -59.9899 | -59.7702 | -0.073242 | -0.086975 | -0.073243 | 0.082397 | 59.6695 | -0.23346 | 59.7427 | -0.16022 | -0.009156 | -0.073243 | -0.032044 | -0.11444 | 0.004577 | -0.21515 | 0.013733 | -0.20599 | 0.15564 | 122.493 | -0.10529 | 122.4701 | 122.4792 | 122.4289 | 122.406 | 122.4197 | -122.5662 | -122.5021 | 122.4197 | 122.4609 | 59.6741 | 59.6466
194.7656 | 122.7036 | -59.761 | 62.7136 | -0.094528 | -0.0010787 | 0.064589 | 0.079585 | -0.00089728 | -0.0014312 | -0.0033112 | -0.046081 | 0.00079477 | 0.064606 | 0.061263 | -0.0086325 | 0.00055973 | 0.00032049 | -0.09613 | 62.6495 | -59.8206 | 62.677 | -59.7015 | -60.1135 | -0.10071 | -0.1236 | 62.5946 | -59.7748 | 62.7182 | -59.816 | -59.9487 | -59.7427 | -0.05951 | -0.064087 | -0.036621 | 0.059509 | 59.6603 | -0.35248 | 59.7198 | -0.29297 | -0.013733 | -0.11902 | 0.004578 | -0.054932 | 0.01831 | -0.18768 | 0.032043 | -0.17395 | 0.11902 | 122.4976 | -0.041199 | 122.493 | 122.4701 | 122.3694 | 122.4106 | 122.3557 | -122.5342 | -122.4884 | 122.438 | 122.4792 | 59.6649 | 59.6375
195.7656 | 122.6761 | -59.761 | 62.6999 | -0.094528 | 0.0014847 | 0.06288 | 0.081508 | 0.0010253 | 0.0002778 | -0.00032036 | -0.030823 | 0.00015377 | 0.06546 | 0.063826 | -0.0084189 | 0.0026959 | 0.0024567 | -0.091553 | 62.6404 | -59.8434 | 62.6633 | -59.7015 | -60.0952 | -0.10986 | -0.13275 | 62.5992 | -59.8114 | 62.7136 | -59.8206 | -59.9442 | -59.761 | -0.082398 | -0.059509 | -0.036621 | 0.059509 | 59.6512 | -0.33417 | 59.7336 | -0.25177 | -0.050354 | -0.10071 | 0.013733 | -0.05951 | 0 | -0.18311 | 0.050354 | -0.13275 | 0.14191 | 122.5067 | -0.009156 | 122.525 | 122.4838 | 122.4106 | 122.4014 | 122.3602 | -122.5433 | -122.5113 | 122.4243 | 122.4747 | 59.6695 | 59.6283
196.7656 | 122.6669 | -59.7519 | 62.7319 | -0.23186 | -0.00065152 | 0.06053 | 0.078731 | 0.0025207 | -0.0003632 | 0.0018158 | -0.06134 | -5.9826e-05 | 0.063965 | 0.059767 | -0.0073507 | 0.0014141 | -0.00010671 | 0.082397 | 62.645 | -59.8343 | 62.6495 | -59.697 | -60.1181 | -0.10529 | -0.16479 | 62.6221 | -59.7839 | 62.6678 | -59.8709 | -59.9945 | -59.8022 | -0.082398 | -0.086976 | -0.082398 | 0.054932 | 59.6466 | -0.36621 | 59.729 | -0.28381 | -0.032044 | -0.10986 | -0.064087 | -0.11902 | -0.050354 | -0.24262 | -0.01831 | -0.21057 | 0.13733 | 122.4838 | -0.086975 | 122.4518 | 122.4792 | 122.406 | 122.3969 | 122.374 | -122.5662 | -122.5159 | 122.4014 | 122.4197 | 59.8343 | 59.5871
197.7656 | 122.6944 | -59.7748 | 62.6953 | -0.0029755 | 0.00084388 | 0.063307 | 0.081081 | 0.0012391 | -0.0018586 | 0.00032044 | -0.039978 | -5.9826e-05 | 0.064179 | 0.059767 | -0.0088461 | 0.0022687 | 0.0039521 | -0.10986 | 62.6358 | -59.7931 | 62.6724 | -59.697 | -60.0769 | -0.11902 | -0.11444 | 62.6083 | -59.7839 | 62.7411 | -59.816 | -59.9304 | -59.7473 | -0.018311 | -0.059509 | -0.022888 | 0.07782 | 59.6558 | -0.30212 | 59.6741 | -0.28381 | -0.009156 | -0.086975 | 0.045777 | -0.041199 | 0.027466 | -0.15564 | 0.036622 | -0.14648 | 0.096131 | 122.4655 | -0.032043 | 122.525 | 122.4289 | 122.3923 | 122.4106 | 122.3831 | -122.4884 | -122.4792 | 122.4472 | 122.5159 | 59.6649 | 59.6603
198.7656 | 122.699 | -59.761 | 62.7182 | -0.094528 | 0.00063028 | 0.063307 | 0.079158 | -0.0011109 | -0.0018586 | -0.0018158 | -0.039978 | 0.0010084 | 0.063324 | 0.062758 | -0.0075643 | 0.0033367 | 0.0016021 | -0.091553 | 62.6358 | -59.816 | 62.677 | -59.6924 | -60.0906 | -0.09613 | -0.1236 | 62.6083 | -59.761 | 62.7365 | -59.8022 | -59.9167 | -59.7382 | -0.054932 | -0.082398 | -0.041199 | 0.068664 | 59.6649 | -0.32959 | 59.7198 | -0.27466 | 0 | -0.10986 | 0.01831 | -0.041199 | 0.022888 | -0.15564 | 0.022888 | -0.15564 | 0.1236 | 122.493 | -0.041199 | 122.4976 | 122.4518 | 122.3694 | 122.3969 | 122.3694 | -122.5342 | -122.4792 | 122.438 | 122.4976 | 59.6695 | 59.6375
199.7656 | 122.6669 | -59.7748 | 62.7045 | -0.10979 | 0.00020288 | 0.062025 | 0.081935 | -0.0017517 | 0.0004914 | -0.00096136 | -0.055237 | 0.00079477 | 0.063751 | 0.06938 | -0.0064963 | 0.0039777 | 0.0016021 | -0.086975 | 62.6404 | -59.8251 | 62.6587 | -59.7107 | -60.0906 | -0.10986 | -0.15564 | 62.6083 | -59.8022 | 62.7045 | -59.8618 | -59.9762 | -59.8022 | -0.050354 | -0.064087 | -0.045777 | 0.064087 | 59.6649 | -0.31586 | 59.7153 | -0.2655 | -0.027466 | -0.096131 | 0 | -0.086975 | -0.027466 | -0.20142 | 0 | -0.17395 | 0.11444 | 122.4838 | -0.059509 | 122.5067 | 122.4655 | 122.4106 | 122.4152 | 122.3831 | -122.5296 | -122.5067 | 122.4335 | 122.4792 | 59.6878 | 59.6191
200.7656 | 122.6395 | -59.7656 | 62.709 | -0.094528 | -0.0017197 | 0.064162 | 0.081508 | 0.00017092 | -0.0014312 | 0.001175 | -0.030823 | 0.0025036 | 0.063751 | 0.070662 | -0.0071371 | 0.0026959 | 0.0013885 | -0.09613 | 62.6221 | -59.8389 | 62.6724 | -59.7244 | -60.0998 | -0.10529 | -0.14648 | 62.6175 | -59.7839 | 62.6953 | -59.848 | -59.9716 | -59.7885 | -0.073242 | -0.086975 | -0.036621 | 0.041199 | 59.6603 | -0.33417 | 59.7336 | -0.26093 | -0.018311 | -0.091552 | -0.013733 | -0.082397 | -0.022888 | -0.20599 | -0.004577 | -0.18768 | 0.11444 | 122.5113 | -0.064086 | 122.4792 | 122.4609 | 122.4014 | 122.3877 | 122.3831 | -122.5479 | -122.493 | 122.438 | 122.4609 | 59.6695 | 59.6191
201.7656 | 122.7402 | -59.7702 | 62.677 | -0.07164 | 0.0012711 | 0.063521 | 0.08044 | 0.00017092 | -0.0020722 | 0.0016022 | -0.027771 | 0.001222 | 0.062897 | 0.060195 | -0.010769 | 0.0035503 | -0.00010671 | -0.10071 | 62.6083 | -59.8114 | 62.709 | -59.6649 | -60.0632 | -0.082397 | -0.091553 | 62.5992 | -59.7977 | 62.7502 | -59.7656 | -59.8755 | -59.7153 | -0.041198 | -0.068665 | 0.032043 | 0.10529 | 59.6878 | -0.29297 | 59.729 | -0.25177 | -0.027465 | -0.07782 | 0.073242 | 0.004578 | 0.054932 | -0.10528 | 0.082397 | -0.07782 | 0.14648 | 122.5204 | 0.032043 | 122.5479 | 122.4197 | 122.3969 | 122.3785 | 122.3694 | -122.4884 | -122.4747 | 122.4792 | 122.5204 | 59.6695 | 59.6787
202.7656 | 122.7631 | -59.729 | 62.7182 | -0.086899 | -0.0010787 | 0.065016 | 0.080012 | -0.0019653 | -0.0012176 | -0.0013886 | -0.018616 | 0.00079477 | 0.063324 | 0.067885 | -0.0075643 | 0.0050457 | -0.0026703 | -0.10071 | 62.6312 | -59.8297 | 62.7182 | -59.6466 | -60.0449 | -0.082397 | -0.09613 | 62.5534 | -59.7931 | 62.7731 | -59.7656 | -59.8709 | -59.697 | -0.10071 | -0.086975 | 0 | 0.082398 | 59.6466 | -0.31586 | 59.7473 | -0.21515 | -0.064087 | -0.16479 | 0.054931 | -0.036621 | 0.032044 | -0.14191 | 0.096131 | -0.07782 | 0.18311 | 122.5479 | 0.027466 | 122.5662 | 122.4609 | 122.3465 | 122.3602 | 122.2824 | -122.5479 | -122.5113 | 122.4472 | 122.5021 | 59.6283 | 59.6329
203.7656 | 122.7631 | -59.7565 | 62.6953 | -0.025863 | 0.00041648 | 0.064375 | 0.079799 | -4.2682e-05 | 0.000705 | 0.0016022 | -0.039978 | 0.00015377 | 0.063538 | 0.067885 | -0.0073507 | 0.0014141 | -0.0054473 | -0.09613 | 62.6266 | -59.816 | 62.7228 | -59.642 | -60.054 | -0.068665 | -0.073242 | 62.5671 | -59.7565 | 62.7731 | -59.7336 | -59.8434 | -59.6603 | -0.059509 | -0.068664 | 0.027466 | 0.11444 | 59.6878 | -0.29755 | 59.7473 | -0.23804 | 0 | -0.12817 | 0.07782 | 0.022888 | 0.096131 | -0.086975 | 0.096131 | -0.086975 | 0.17395 | 122.5388 | 0.022888 | 122.5296 | 122.4426 | 122.3236 | 122.3831 | 122.3236 | -122.5113 | -122.4518 | 122.4792 | 122.5296 | 59.6603 | 59.6832
204.7656 | 122.7219 | -59.7473 | 62.6678 | -0.13267 | 0.00063028 | 0.064803 | 0.080867 | -0.00046988 | 0.0004914 | 0.001175 | 0.030212 | -0.001128 | 0.063751 | 0.062331 | -0.0079917 | 0.0014141 | -0.0018157 | -0.050354 | 62.59 | -59.7931 | 62.7823 | -59.5734 | -59.9854 | -0.004578 | -0.018311 | 62.5534 | -59.7885 | 62.7686 | -59.7519 | -59.8618 | -59.7015 | -0.045777 | -0.07782 | 0.11444 | 0.17395 | 59.7427 | -0.23804 | 59.7885 | -0.19226 | -0.041199 | -0.11444 | 0.10071 | -0.004578 | 0.045776 | -0.11444 | 0.086975 | -0.073242 | 0.21973 | 122.5754 | 0.036621 | 122.5571 | 122.3831 | 122.3419 | 122.3373 | 122.3007 | -122.4609 | -122.4564 | 122.5296 | 122.5159 | 59.697 | 59.729
205.7656 | 122.7493 | -59.7473 | 62.6999 | -0.10216 | 0.00041648 | 0.065871 | 0.080226 | -0.0017517 | -0.0024994 | 0.00053404 | 0.024109 | 0.00015377 | 0.063111 | 0.060195 | -0.0071371 | 0.0026959 | 0.0030975 | -0.045776 | 62.6038 | -59.7702 | 62.764 | -59.5688 | -59.9808 | -0.009155 | -0.013733 | 62.558 | -59.7794 | 62.7686 | -59.7656 | -59.8389 | -59.697 | -0.022889 | -0.09613 | 0.064087 | 0.17853 | 59.7382 | -0.23346 | 59.761 | -0.21057 | -0.032044 | -0.14191 | 0.068665 | -0.018311 | 0.050354 | -0.091553 | 0.082398 | -0.059509 | 0.20142 | 122.5342 | 0.013733 | 122.5479 | 122.374 | 122.3373 | 122.3511 | 122.3053 | -122.4701 | -122.4792 | 122.5113 | 122.5159 | 59.7015 | 59.7336
206.7656 | 122.7493 | -59.7107 | 62.6999 | -0.079269 | 0.0016983 | 0.062666 | 0.078303 | -0.0028199 | -0.001004 | 0.00010684 | -0.015564 | -0.00091423 | 0.063111 | 0.063185 | -0.0071371 | -8.1274e-05 | -0.0016021 | -0.027466 | 62.59 | -59.7702 | 62.7731 | -59.5642 | -59.9762 | -0.032043 | -0.009155 | 62.5488 | -59.761 | 62.7823 | -59.7382 | -59.8297 | -59.6741 | -0.05951 | -0.10986 | 0.073242 | 0.14648 | 59.6786 | -0.2655 | 59.7382 | -0.20599 | -0.050354 | -0.15106 | 0.082398 | -0.027466 | 0.036621 | -0.11902 | 0.086975 | -0.068665 | 0.20599 | 122.5433 | 0.022888 | 122.5433 | 122.3602 | 122.3099 | 122.3007 | 122.2595 | -122.4701 | -122.4609 | 122.4838 | 122.493 | 59.6832 | 59.7015
207.7656 | 122.7402 | -59.7244 | 62.6724 | -0.06401 | 0.0012711 | 0.065657 | 0.079158 | -0.00046988 | -0.0007904 | -0.00053396 | -0.012512 | -0.0013416 | 0.063538 | 0.065535 | -0.0084189 | 0.0031231 | -0.0045929 | -0.032043 | 62.5946 | -59.7656 | 62.7869 | -59.5871 | -60.0082 | -0.018311 | -0.009155 | 62.5671 | -59.7565 | 62.8052 | -59.7244 | -59.8297 | -59.6832 | -0.041199 | -0.07782 | 0.11444 | 0.13733 | 59.7061 | -0.28381 | 59.7473 | -0.24262 | -0.032044 | -0.10529 | 0.13275 | 0 | 0.041198 | -0.10529 | 0.073242 | -0.073242 | 0.17853 | 122.5525 | 0.032044 | 122.5616 | 122.3602 | 122.3236 | 122.319 | 122.2916 | -122.438 | -122.4289 | 122.5113 | 122.5296 | 59.6924 | 59.7153
208.7656 | 122.7951 | -59.697 | 62.7319 | -0.041122 | 0.00041648 | 0.062239 | 0.078944 | -0.0017517 | -0.0007904 | -0.0016022 | 0.0057984 | -0.0013416 | 0.063538 | 0.062972 | -0.0075643 | 0.0012005 | 0.00032049 | 0.050354 | 62.6495 | -59.761 | 62.7869 | -59.0836 | -59.6466 | -0.059509 | 0.07782 | 62.558 | -59.7427 | 62.8281 | -59.6558 | -59.7519 | -59.6237 | -0.064087 | -0.082398 | 0.054931 | 0.6134 | 59.6375 | 0.050354 | 59.7015 | 0.11444 | -0.045777 | -0.17395 | 0.09613 | 0.041198 | 0.073242 | -0.054932 | 0.11902 | -0.009155 | 0.67749 | 122.5479 | 0.086975 | 122.5708 | 122.4106 | 122.3007 | 122.3465 | 122.2549 | -122.493 | -122.4747 | 122.4838 | 122.525 | 59.7473 | 59.7748
209.7656 | 122.7173 | -59.7427 | 62.7045 | -0.041122 | 0.0012711 | 0.065016 | 0.07809 | -0.00089728 | -0.0005768 | -0.0030976 | -0.018616 | 0.00015377 | 0.063751 | 0.067885 | -0.0086325 | 0.0031231 | 0.0026703 | -0.045776 | 62.5992 | -59.7885 | 62.7686 | -59.5734 | -59.9899 | -0.009155 | -0.018311 | 62.558 | -59.7519 | 62.764 | -59.7702 | -59.8572 | -59.7061 | -0.045776 | -0.10529 | 0.064087 | 0.16937 | 59.7336 | -0.24719 | 59.7794 | -0.20142 | -0.009155 | -0.14648 | 0.059509 | -0.027466 | 0.036621 | -0.11444 | 0.045776 | -0.10529 | 0.21515 | 122.5571 | -0.018311 | 122.5159 | 122.3877 | 122.3099 | 122.3419 | 122.3007 | -122.493 | -122.4564 | 122.5113 | 122.5067 | 59.697 | 59.7244
210.7656 | 122.7081 | -59.761 | 62.6816 | -0.07164 | 0.00084388 | 0.061812 | 0.079799 | 0.0031617 | -0.0014312 | 0.00074764 | -0.024719 | 0.001222 | 0.06247 | 0.059554 | -0.010128 | 0.0029095 | -0.0045929 | -0.041199 | 62.5946 | -59.7977 | 62.764 | -59.5871 | -60.022 | -0.013733 | -0.032043 | 62.5854 | -59.7839 | 62.7731 | -59.761 | -59.8801 | -59.697 | -0.036621 | -0.086976 | 0.082397 | 0.17395 | 59.7473 | -0.26093 | 59.7839 | -0.22431 | -0.022889 | -0.096131 | 0.091552 | 0 | 0.064087 | -0.11902 | 0.086976 | -0.09613 | 0.21057 | 122.5616 | 0.022889 | 122.5571 | 122.3923 | 122.3694 | 122.3557 | 122.3465 | -122.4792 | -122.4655 | 122.525 | 122.5342 | 59.7198 | 59.729
211.7656 | 122.7173 | -59.7336 | 62.6999 | -0.086899 | 0.0034073 | 0.060744 | 0.079372 | 0.0016663 | -0.0005768 | -0.0020294 | 0.027161 | 0.00058097 | 0.063111 | 0.060195 | -0.0064963 | 0.00034613 | 0.0024567 | -0.059509 | 62.6266 | -59.7839 | 62.7502 | -59.5093 | -59.8068 | 0.009155 | -0.11444 | 62.5763 | -59.7656 | 62.7411 | -59.7702 | -59.8892 | -59.7336 | -0.050354 | -0.073242 | 0.050354 | 0.22431 | 59.7427 | -0.073242 | 59.7931 | -0.022888 | -0.032043 | -0.1236 | 0.041199 | -0.036621 | 0 | -0.15564 | 0.032043 | -0.1236 | 0.27466 | 122.5342 | -0.004578 | 122.5067 | 122.4106 | 122.3419 | 122.3602 | 122.3099 | -122.4838 | -122.4655 | 122.4838 | 122.4747 | 59.6741 | 59.6191
212.7656 | 122.7036 | -59.7198 | 62.7228 | -0.094528 | 0.00020288 | 0.06288 | 0.081294 | -0.0013245 | 0.0009186 | 0.00032044 | -0.024719 | -5.9826e-05 | 0.06546 | 0.065962 | -0.0069235 | 0.00055973 | 0.00053409 | -0.059509 | 62.6083 | -59.7977 | 62.8601 | -59.4635 | -60.0906 | -0.041199 | -0.082397 | 62.5992 | -59.7519 | 62.7457 | -59.7794 | -59.8709 | -59.729 | -0.077819 | -0.11444 | 0.13733 | 0.25635 | 59.6787 | -0.37079 | 59.7565 | -0.29297 | -0.032043 | -0.1236 | 0.022889 | -0.059509 | -0.009155 | -0.15106 | 0.022888 | -0.11902 | 0.33417 | 122.6578 | -0.027466 | 122.4976 | 122.406 | 122.3511 | 122.3282 | 122.319 | -122.5204 | -122.4747 | 122.58 | 122.4655 | 59.6603 | 59.6375
213.7656 | 122.6852 | -59.7565 | 62.7594 | -0.041122 | 0.0025529 | 0.063094 | 0.080653 | 0.0014527 | -0.0024994 | -0.001175 | -0.11627 | 0.001222 | 0.064392 | 0.066603 | -0.0077779 | 0.0033367 | 0.00010689 | 0.009155 | 62.6404 | -59.7885 | 62.7686 | -59.6191 | -60.0266 | -0.009155 | 0.022888 | 62.6404 | -59.7565 | 62.7548 | -59.7885 | -59.9167 | -59.7198 | -0.032043 | -0.11902 | 0.009156 | 0.13733 | 59.7473 | -0.27008 | 59.7794 | -0.23804 | 0 | -0.11902 | -0.004577 | -0.032043 | 0.036621 | -0.16022 | 0.036621 | -0.16022 | 0.16937 | 122.5571 | -0.032043 | 122.5113 | 122.4289 | 122.3969 | 122.3969 | 122.3969 | -122.5479 | -122.5159 | 122.525 | 122.5113 | 59.7656 | 59.7794
214.7656 | 122.7356 | -59.7519 | 62.6907 | -0.1403 | 0.00041648 | 0.063734 | 0.081294 | -0.00089728 | -0.0029266 | 0.001175 | 0.0027466 | -0.00027343 | 0.064606 | 0.05934 | -0.0075643 | -8.1274e-05 | 0.00096129 | -0.036621 | 62.5854 | -59.7794 | 62.7548 | -59.5963 | -60.0174 | -0.009155 | -0.050354 | 62.5626 | -59.7748 | 62.7594 | -59.7656 | -59.8709 | -59.729 | -0.027466 | -0.10529 | 0.064087 | 0.15564 | 59.7427 | -0.2655 | 59.7702 | -0.23804 | -0.022888 | -0.12817 | 0.068664 | -0.013733 | 0.022888 | -0.11902 | 0.045776 | -0.096131 | 0.18311 | 122.5342 | 0.009155 | 122.5342 | 122.3648 | 122.3373 | 122.3373 | 122.3145 | -122.4701 | -122.4655 | 122.5067 | 122.5113 | 59.7153 | 59.7015
215.7656 | 122.7127 | -59.7107 | 62.7319 | -0.12505 | -0.00086512 | 0.062453 | 0.079585 | -0.0021789 | -0.0001496 | -0.0024566 | 0.0027466 | -0.00091423 | 0.063324 | 0.063185 | -0.0079917 | 0.0016277 | -0.00010671 | -0.054932 | 62.6083 | -59.7794 | 62.6678 | -59.61 | -60.0815 | -0.045776 | -0.068665 | 62.6083 | -59.7839 | 62.7594 | -59.7519 | -59.848 | -59.7107 | -0.068665 | -0.1236 | -0.064087 | 0.10071 | 59.6649 | -0.37079 | 59.7336 | -0.30212 | -0.073243 | -0.1236 | 0.027465 | -0.041199 | 0 | -0.13733 | 0.073243 | -0.064086 | 0.16937 | 122.4472 | 0.032044 | 122.5433 | 122.3877 | 122.3923 | 122.319 | 122.319 | -122.5113 | -122.5159 | 122.3785 | 122.4701 | 59.6558 | 59.642
216.7656 | 122.7356 | -59.7244 | 62.7136 | -0.06401 | -0.0012923 | 0.06288 | 0.079585 | -0.00089728 | 6.4004e-05 | -0.0018158 | -0.00030524 | -0.00091423 | 0.063324 | 0.063185 | -0.0079917 | 0.0020551 | -0.00096131 | -0.054932 | 62.6221 | -59.7885 | 62.7319 | -59.6603 | -60.0357 | -0.022888 | -0.054932 | 62.5809 | -59.7839 | 62.7548 | -59.761 | -59.848 | -59.7153 | -0.064087 | -0.091553 | 0.018311 | 0.064087 | 59.7015 | -0.31128 | 59.7656 | -0.24719 | -0.05951 | -0.13275 | 0.041199 | -0.036621 | 0.009155 | -0.1236 | 0.068665 | -0.064086 | 0.12817 | 122.5204 | 0.022889 | 122.5388 | 122.4106 | 122.3648 | 122.3465 | 122.3053 | -122.5021 | -122.4976 | 122.4564 | 122.4792 | 59.6695 | 59.6695
217.7656 | 122.7676 | -59.729 | 62.7182 | -0.07164 | 0.0040481 | 0.063521 | 0.079799 | -0.0019653 | -0.0031402 | -0.00053396 | -0.0033568 | -0.00027343 | 0.063111 | 0.062545 | -0.0077779 | 0.00013253 | -0.0018157 | -0.022888 | 62.6083 | -59.7565 | 62.7777 | -59.5871 | -59.9625 | 0.022888 | 0.027466 | 62.5992 | -59.7748 | 62.7914 | -59.7107 | -59.8114 | -59.6695 | -0.027466 | -0.10986 | 0.059509 | 0.14191 | 59.7519 | -0.23346 | 59.7794 | -0.20599 | -0.045776 | -0.11902 | 0.073242 | 0.018311 | 0.059509 | -0.082397 | 0.10529 | -0.036621 | 0.16937 | 122.5342 | 0.064087 | 122.5662 | 122.3648 | 122.374 | 122.3373 | 122.3282 | -122.4747 | -122.493 | 122.5067 | 122.5204 | 59.7061 | 59.7565
218.7656 | 122.6669 | -59.7427 | 62.7686 | -0.033493 | 0.00020288 | 0.062239 | 0.079585 | -0.0038879 | -0.0014312 | -0.00074776 | -0.082703 | 0.0018628 | 0.063751 | 0.070235 | -0.0094869 | 0.00034613 | -0.0035247 | -0.004578 | 62.677 | -59.7885 | 62.709 | -59.6741 | -60.0174 | 0.022888 | 0 | 62.677 | -59.7656 | 62.7411 | -59.7931 | -59.8984 | -59.7519 | -0.045776 | -0.091553 | -0.05951 | 0.068665 | 59.7656 | -0.27466 | 59.8114 | -0.22888 | -0.022888 | -0.091553 | -0.027466 | -0.050354 | -0.009155 | -0.15564 | 0.013733 | -0.13275 | 0.11444 | 122.4976 | -0.027466 | 122.5067 | 122.4655 | 122.4426 | 122.4197 | 122.4197 | -122.5571 | -122.5342 | 122.4518 | 122.4838 | 59.7382 | 59.7427
219.7656 | 122.7539 | -59.7061 | 62.7457 | -0.056381 | 0.0021255 | 0.063948 | 0.080653 | -0.0011109 | -0.0016448 | -0.003952 | 0.0088502 | -0.00070063 | 0.064179 | 0.060195 | -0.0069235 | -0.00029487 | 0.0026703 | -0.022888 | 62.6175 | -59.7931 | 62.7823 | -59.5688 | -59.9533 | 0.041199 | 0.032043 | 62.5946 | -59.7382 | 62.8052 | -59.7107 | -59.8114 | -59.6741 | -0.086975 | -0.12817 | 0.036621 | 0.13733 | 59.7473 | -0.24719 | 59.8343 | -0.16022 | -0.032043 | -0.15106 | 0.059509 | -0.004577 | 0.032044 | -0.10528 | 0.064087 | -0.073242 | 0.2243 | 122.5754 | 0.027466 | 122.5433 | 122.4106 | 122.3328 | 122.3236 | 122.3007 | -122.5388 | -122.4838 | 122.4884 | 122.5113 | 59.6832 | 59.7382
220.7656 | 122.7219 | -59.7427 | 62.7228 | -0.17845 | 0.0014847 | 0.063094 | 0.079799 | -0.0015381 | -0.0020722 | -0.0020294 | -0.018616 | -0.00091423 | 0.065033 | 0.057204 | -0.0064963 | 0.0020551 | 0.0026703 | -0.07782 | 62.6266 | -59.7885 | 62.7365 | -59.6054 | -60.0128 | 0 | -0.022888 | 62.6175 | -59.761 | 62.7594 | -59.7473 | -59.8663 | -59.7107 | -0.045776 | -0.09613 | 0.013733 | 0.13733 | 59.7427 | -0.27008 | 59.7885 | -0.2243 | -0.01831 | -0.10528 | 0.036621 | -0.004577 | 0.032044 | -0.1236 | 0.050354 | -0.10529 | 0.18311 | 122.525 | 0.013733 | 122.5204 | 122.4152 | 122.3785 | 122.3694 | 122.3602 | -122.5113 | -122.4838 | 122.4792 | 122.5021 | 59.6649 | 59.7198
221.7656 | 122.7539 | -59.7244 | 62.7045 | -0.1403 | 0.00041648 | 0.063094 | 0.080867 | 0.00017092 | -0.0016448 | 0.00096124 | -0.021667 | -0.00048703 | 0.064392 | 0.058699 | -0.0084189 | 0.0016277 | -0.0016021 | -0.032043 | 62.6175 | -59.8022 | 62.7502 | -59.6146 | -60.0128 | -0.004578 | -0.027466 | 62.5946 | -59.7656 | 62.7731 | -59.761 | -59.8434 | -59.7153 | -0.07782 | -0.086975 | 0.045776 | 0.10986 | 59.7198 | -0.28839 | 59.7977 | -0.21057 | -0.041199 | -0.10986 | 0.068664 | -0.036621 | 0.009155 | -0.11902 | 0.050354 | -0.07782 | 0.18768 | 122.5525 | 0.004578 | 122.5388 | 122.4197 | 122.3602 | 122.3419 | 122.319 | -122.5067 | -122.4701 | 122.4747 | 122.4976 | 59.6924 | 59.697
222.7656 | 122.7676 | -59.7336 | 62.7182 | -0.094528 | 0.0021255 | 0.063307 | 0.082149 | 0.0029479 | -0.001004 | -0.0013886 | -0.0094604 | -0.00048703 | 0.064179 | 0.059767 | -0.0084189 | 0.0020551 | 0.00032049 | -0.009155 | 62.6724 | -59.7748 | 62.7869 | -59.5779 | -59.9533 | 0.059509 | 0.059509 | 62.5763 | -59.7519 | 62.8143 | -59.6878 | -59.7977 | -59.6649 | -0.041198 | -0.045777 | 0.068664 | 0.15564 | 59.7931 | -0.21973 | 59.8343 | -0.17853 | -0.01831 | -0.14191 | 0.09613 | 0.045777 | 0.068665 | -0.064086 | 0.086975 | -0.045776 | 0.19684 | 122.5616 | 0.064087 | 122.5662 | 122.4472 | 122.3282 | 122.406 | 122.3099 | -122.493 | -122.4701 | 122.5204 | 122.5479 | 59.7244 | 59.7931
223.7656 | 122.7036 | -59.7244 | 62.7274 | -0.010605 | 0.0055435 | 0.063094 | 0.08044 | 0.0020935 | -0.0016448 | -0.00074776 | -0.12848 | 0.00036737 | 0.063538 | 0.063399 | -0.0094869 | 0.0018413 | -0.0018157 | -0.13275 | 62.5992 | -59.8068 | 62.7548 | -59.6008 | -59.9808 | 0.004578 | 0.054932 | 62.6495 | -59.7748 | 62.7731 | -59.7748 | -59.8755 | -59.7382 | -0.082398 | -0.12817 | 0.027466 | 0.1236 | 59.729 | -0.25635 | 59.8114 | -0.17395 | -0.050354 | -0.07782 | 0.045776 | -0.050354 | -0.013733 | -0.15106 | 0.036621 | -0.10071 | 0.20599 | 122.5616 | 0 | 122.5479 | 122.406 | 122.4243 | 122.3236 | 122.374 | -122.5342 | -122.5021 | 122.4792 | 122.4976 | 59.5917 | 59.7794
224.7656 | 122.7493 | -59.6878 | 62.7045 | -0.07164 | 0.0016983 | 0.063948 | 0.079799 | 0.0029479 | -0.0024994 | -0.0013886 | -0.018616 | -5.9826e-05 | 0.064392 | 0.072798 | -0.0067099 | 0.00055973 | -0.0011749 | -0.009155 | 62.6038 | -59.7794 | 62.7869 | -59.5551 | -59.9625 | 0.064087 | 0.050354 | 62.5992 | -59.761 | 62.8052 | -59.6786 | -59.7977 | -59.6741 | -0.091553 | -0.10071 | 0.082397 | 0.13275 | 59.7519 | -0.27466 | 59.8434 | -0.1831 | -0.073242 | -0.10529 | 0.10071 | 0.009155 | 0.013733 | -0.10986 | 0.086975 | -0.036621 | 0.2243 | 122.5662 | 0.082397 | 122.5662 | 122.3831 | 122.3602 | 122.2916 | 122.287 | -122.4838 | -122.4655 | 122.4747 | 122.493 | 59.6786 | 59.7382
225.7656 | 122.8043 | -59.7107 | 62.7411 | -0.056381 | 0.0012711 | 0.064803 | 0.08044 | -0.0043151 | 0.0004914 | -0.002243 | -0.070496 | -0.00070063 | 0.063965 | 0.066817 | -0.0075643 | 0.00098693 | 0.0016021 | 0.041199 | 62.6129 | -59.7656 | 62.8464 | -59.4955 | -59.8755 | 0.13275 | 0.35248 | 62.6495 | -59.7153 | 62.8555 | -59.6649 | -59.7748 | -59.6695 | -0.054932 | -0.12817 | 0.10529 | 0.21515 | 59.8434 | -0.16479 | 59.8984 | -0.10986 | -0.004578 | -0.091553 | 0.11444 | 0.045776 | 0.041198 | -0.064087 | 0.045776 | -0.059509 | 0.27008 | 122.612 | 0.050354 | 122.5708 | 122.3785 | 122.3648 | 122.3236 | 122.3602 | -122.5067 | -122.4564 | 122.5571 | 122.5662 | 59.7519 | 60.0632
226.7656 | 122.7905 | -59.7061 | 62.7182 | -0.06401 | -0.0012923 | 0.063094 | 0.080867 | -0.0019653 | -0.0018586 | 0.001175 | 0.18585 | -5.9826e-05 | 0.066101 | 0.063826 | -0.0090597 | 0.0026959 | -0.0013885 | 0.050354 | 62.6266 | -59.7702 | 62.851 | -59.491 | -59.8938 | 0.10071 | -0.054932 | 62.6312 | -59.7519 | 62.8464 | -59.697 | -59.7885 | -59.6603 | -0.064087 | -0.091553 | 0.13275 | 0.21515 | 59.8068 | -0.18768 | 59.8709 | -0.1236 | -0.045776 | -0.086975 | 0.12817 | 0.009156 | 0.045777 | -0.082397 | 0.091553 | -0.036621 | 0.27924 | 122.6212 | 0.054932 | 122.5983 | 122.3969 | 122.3831 | 122.3328 | 122.3373 | -122.4884 | -122.4701 | 122.5571 | 122.5525 | 59.7565 | 59.6512
227.7656 | 122.7631 | -59.7015 | 62.6907 | -0.048752 | 0.00063028 | 0.062239 | 0.079799 | -0.0026063 | -0.0001496 | 0.00053404 | -0.030823 | -5.9826e-05 | 0.06482 | 0.064253 | -0.0086325 | 0.00034613 | -0.0028839 | 0.004578 | 62.6221 | -59.729 | 62.8098 | -59.5642 | -59.9487 | 0.064087 | 0.07782 | 62.59 | -59.7382 | 62.8189 | -59.6832 | -59.7885 | -59.6512 | -0.027466 | -0.068665 | 0.11902 | 0.13733 | 59.7656 | -0.24719 | 59.7931 | -0.21973 | -0.036621 | -0.10071 | 0.12817 | 0.01831 | 0.050354 | -0.086975 | 0.086975 | -0.050354 | 0.1648 | 122.5388 | 0.054931 | 122.5571 | 122.3511 | 122.3282 | 122.3236 | 122.2916 | -122.4197 | -122.4289 | 122.5113 | 122.5204 | 59.7061 | 59.7794
228.7656 | 122.6761 | -59.7427 | 62.7502 | -0.018234 | 0.0025529 | 0.062666 | 0.08279 | 0.0040161 | -0.0018586 | 0.0013886 | -0.10406 | -0.00027343 | 0.062683 | 0.066817 | -0.0086325 | 0.0041913 | -0.0018157 | 0.036621 | 62.6862 | -59.7748 | 62.7686 | -59.6237 | -59.9808 | 0.027466 | 0.050354 | 62.6404 | -59.7656 | 62.7731 | -59.7656 | -59.8892 | -59.729 | -0.032043 | -0.064087 | 0.018311 | 0.11902 | 59.7702 | -0.23804 | 59.8022 | -0.20599 | -0.022888 | -0.10986 | 0.022888 | -0.022888 | 0.013733 | -0.14648 | 0.036621 | -0.1236 | 0.15106 | 122.5433 | 0 | 122.5388 | 122.4609 | 122.406 | 122.4289 | 122.3831 | -122.525 | -122.5159 | 122.5113 | 122.5159 | 59.7794 | 59.7931
229.7656 | 122.7814 | -59.7061 | 62.7319 | -0.041122 | 0.0019119 | 0.063948 | 0.081081 | 0.0014527 | -0.0012176 | -0.002243 | -0.039978 | 0.00058097 | 0.065247 | 0.057204 | -0.0086325 | 0.00098693 | -0.0013885 | 0.041199 | 62.6221 | -59.7565 | 62.8281 | -59.2575 | -59.4727 | 0.073242 | 0.1236 | 62.59 | -59.7427 | 62.8555 | -59.6603 | -59.761 | -59.6237 | -0.050354 | -0.10986 | 0.09613 | 0.44861 | 59.7794 | 0.23346 | 59.8297 | 0.28381 | -0.036621 | -0.14191 | 0.1236 | 0.045777 | 0.082398 | -0.054931 | 0.11902 | -0.01831 | 0.49896 | 122.5845 | 0.082398 | 122.5983 | 122.3785 | 122.3328 | 122.3282 | 122.2961 | -122.4884 | -122.4747 | 122.5342 | 122.5616 | 59.7473 | 59.8297
230.7656 | 122.7676 | -59.6924 | 62.7365 | -0.048752 | -0.00022432 | 0.063734 | 0.079799 | 0.0010253 | -0.0016448 | -0.0018158 | -0.055237 | -0.0017688 | 0.063751 | 0.065535 | -0.0082053 | 0.0026959 | -0.0039521 | 0.068665 | 62.6312 | -59.7656 | 62.764 | -59.1705 | -59.5322 | 0.013733 | 0.13275 | 62.5809 | -59.7473 | 62.8555 | -59.6375 | -59.761 | -59.6237 | -0.073242 | -0.10529 | 0.027466 | 0.52185 | 59.7061 | 0.16022 | 59.7794 | 0.23346 | -0.054931 | -0.15564 | 0.11902 | 0.054932 | 0.068665 | -0.068664 | 0.1236 | -0.013733 | 0.59509 | 122.5296 | 0.10986 | 122.6028 | 122.3969 | 122.3282 | 122.3236 | 122.2733 | -122.5021 | -122.4838 | 122.4564 | 122.5479 | 59.761 | 59.8251
231.7656 | 122.7722 | -59.6741 | 62.6999 | -0.07164 | 0.0019119 | 0.063094 | 0.081294 | 0.0038025 | -0.0003632 | -0.0026704 | -0.058289 | -5.9826e-05 | 0.06482 | 0.063399 | -0.0092733 | 0.00055973 | -0.0045929 | 0.059509 | 62.6129 | -59.7519 | 62.8418 | -59.1248 | -59.5917 | -0.059509 | 0.10071 | 62.5992 | -59.7473 | 62.8189 | -59.6512 | -59.7565 | -59.6146 | -0.07782 | -0.086975 | 0.14191 | 0.54932 | 59.6146 | 0.082397 | 59.6924 | 0.16022 | -0.073242 | -0.10071 | 0.11902 | 0.022888 | 0.059509 | -0.082398 | 0.13275 | -0.009156 | 0.62714 | 122.5937 | 0.09613 | 122.5662 | 122.3648 | 122.3465 | 122.287 | 122.2733 | -122.4518 | -122.4472 | 122.5159 | 122.493 | 59.7336 | 59.7748
232.7656 | 122.7585 | -59.6878 | 62.7777 | -0.056381 | 0.0012711 | 0.063094 | 0.080012 | 0.00059812 | -0.0012176 | -0.00096136 | -0.012512 | 0.0010084 | 0.063751 | 0.06169 | -0.0097007 | 0.00034613 | -0.0016021 | 0.073242 | 62.6266 | -59.7473 | 62.8189 | -59.5184 | -59.9213 | 0.10071 | 0.12817 | 62.6358 | -59.7198 | 62.8235 | -59.6878 | -59.7885 | -59.6695 | -0.059509 | -0.15106 | 0.041199 | 0.16937 | 59.7885 | -0.23346 | 59.848 | -0.17395 | -0.032044 | -0.14191 | 0.045776 | 0 | 0.01831 | -0.10071 | 0.050354 | -0.068664 | 0.22888 | 122.5662 | 0.032044 | 122.5433 | 122.374 | 122.3557 | 122.3145 | 122.3236 | -122.525 | -122.4976 | 122.5067 | 122.5113 | 59.761 | 59.816
233.7656 | 122.7539 | -59.7015 | 62.7502 | -0.056381 | 0.00020288 | 0.06288 | 0.080226 | -0.0015381 | -0.0024994 | -0.00074776 | -0.0064086 | 0.00036737 | 0.065674 | 0.066817 | -0.0075643 | 0.0016277 | -0.00053411 | 0.045776 | 62.6541 | -59.7336 | 62.8464 | -59.523 | -59.9075 | 0.10986 | 0.14191 | 62.6083 | -59.729 | 62.8189 | -59.6741 | -59.7748 | -59.6603 | -0.032044 | -0.09613 | 0.096131 | 0.17853 | 59.8114 | -0.20599 | 59.8434 | -0.17395 | -0.027466 | -0.14191 | 0.068665 | 0.027466 | 0.041199 | -0.073242 | 0.068665 | -0.045776 | 0.21057 | 122.58 | 0.054932 | 122.5479 | 122.3877 | 122.3373 | 122.3557 | 122.3099 | -122.4838 | -122.4792 | 122.5479 | 122.5204 | 59.7473 | 59.8434
234.7656 | 122.7951 | -59.697 | 62.7457 | -0.06401 | 0.00084388 | 0.061385 | 0.081721 | -0.0070923 | -0.0042084 | -0.0018158 | -0.039978 | -0.001128 | 0.065674 | 0.056349 | -0.0082053 | 0.0012005 | -0.0028839 | 0.041199 | 62.6038 | -59.7748 | 62.9242 | -59.7656 | -60.0128 | 0.091553 | 0.19684 | 62.5809 | -59.7519 | 62.8418 | -59.6512 | -59.7336 | -59.6329 | -0.07782 | -0.14191 | 0.17853 | -0.068665 | 59.7885 | -0.31586 | 59.8663 | -0.23804 | -0.054932 | -0.16479 | 0.09613 | 0.045776 | 0.064086 | -0.036622 | 0.11902 | 0.01831 | 0.009155 | 122.699 | 0.10071 | 122.5937 | 122.3785 | 122.3328 | 122.3007 | 122.2778 | -122.5204 | -122.4976 | 122.6212 | 122.5388 | 59.7382 | 59.8938
235.7656 | 122.7585 | -59.7107 | 62.7594 | -0.018234 | 0.0025529 | 0.064589 | 0.08044 | -0.0013245 | 0.0013458 | -0.0013886 | -0.0094604 | -0.00070063 | 0.065247 | 0.062331 | -0.0090597 | 0.0024823 | -0.00010671 | 0.059509 | 62.645 | -59.7427 | 62.8372 | -59.5184 | -59.9213 | 0.11902 | 0.14191 | 62.6312 | -59.7427 | 62.8143 | -59.6878 | -59.7748 | -59.6695 | -0.032044 | -0.11444 | 0.07782 | 0.19226 | 59.8297 | -0.21057 | 59.8618 | -0.17853 | -0.032044 | -0.12817 | 0.054932 | 0.022888 | 0.041198 | -0.064087 | 0.073242 | -0.032043 | 0.2243 | 122.58 | 0.054932 | 122.5571 | 122.3877 | 122.374 | 122.3557 | 122.3419 | -122.5021 | -122.5021 | 122.5479 | 122.525 | 59.7702 | 59.8526
236.7656 | 122.7173 | -59.7061 | 62.7365 | -0.018234 | 0.0016983 | 0.06288 | 0.081508 | 0.0018799 | -0.0024994 | 0.0033112 | -0.015564 | -0.001128 | 0.066315 | 0.058913 | -0.0082053 | 0.0029095 | 0.0016021 | 0.068665 | 62.6404 | -59.7382 | 62.8235 | -59.5184 | -59.8938 | 0.10986 | 0.15106 | 62.6083 | -59.761 | 62.796 | -59.6832 | -59.816 | -59.6695 | -0.032043 | -0.09613 | 0.086975 | 0.18768 | 59.816 | -0.18768 | 59.848 | -0.15564 | -0.054931 | -0.12817 | 0.05951 | 0.022888 | 0.036621 | -0.10986 | 0.091552 | -0.054932 | 0.21973 | 122.5616 | 0.077819 | 122.5571 | 122.3785 | 122.3694 | 122.3465 | 122.3145 | -122.4747 | -122.4976 | 122.5296 | 122.5021 | 59.7748 | 59.8572
237.7656 | 122.7402 | -59.6878 | 62.7548 | -0.07164 | 0.0016983 | 0.064375 | 0.080226 | 0.00081172 | -0.0014312 | 0.00010684 | -0.0033568 | -0.00070063 | 0.064606 | 0.068312 | -0.0084189 | 0.0029095 | -0.0011749 | 0.054932 | 62.6358 | -59.7519 | 62.8372 | -59.5276 | -59.8938 | 0.11444 | 0.14648 | 62.6083 | -59.7382 | 62.8098 | -59.6832 | -59.8206 | -59.6649 | -0.064087 | -0.11902 | 0.082397 | 0.16022 | 59.8022 | -0.20599 | 59.8663 | -0.14191 | -0.050354 | -0.14648 | 0.054931 | 0.004577 | 0.022888 | -0.13275 | 0.073242 | -0.082398 | 0.2243 | 122.5891 | 0.054931 | 122.5479 | 122.3877 | 122.3465 | 122.3236 | 122.2961 | -122.5067 | -122.493 | 122.525 | 122.4976 | 59.7427 | 59.8343
238.7656 | 122.731 | -59.7107 | 62.7457 | -0.048752 | 0.0027665 | 0.061385 | 0.080226 | 0.0018799 | -0.0029266 | -0.00053396 | -0.021667 | -0.0015552 | 0.066101 | 0.058699 | -0.0067099 | 0.0026959 | -0.00010671 | 0.068665 | 62.6495 | -59.7336 | 62.8189 | -59.523 | -59.9167 | 0.10071 | 0.13275 | 62.6221 | -59.7565 | 62.8006 | -59.6924 | -59.8022 | -59.6786 | -0.022889 | -0.096131 | 0.073242 | 0.18768 | 59.8114 | -0.20599 | 59.8343 | -0.18311 | -0.045777 | -0.1236 | 0.054931 | 0.01831 | 0.032043 | -0.091553 | 0.07782 | -0.045776 | 0.21057 | 122.5525 | 0.064087 | 122.5571 | 122.3831 | 122.3785 | 122.3602 | 122.3328 | -122.4792 | -122.5021 | 122.5296 | 122.5113 | 59.7794 | 59.8434
239.7656 | 122.7219 | -59.7198 | 62.764 | 0.004654 | 0.0023391 | 0.062453 | 0.079372 | 0.00017092 | 0.000705 | -0.0030976 | -0.027771 | 0.00058097 | 0.066529 | 0.067244 | -0.0082053 | 0.00055973 | 0.00074769 | 0.045776 | 62.6358 | -59.7519 | 62.8235 | -59.5139 | -59.8984 | 0.10986 | 0.1236 | 62.6266 | -59.7427 | 62.8006 | -59.697 | -59.7977 | -59.6786 | -0.032043 | -0.12817 | 0.059509 | 0.20599 | 59.8297 | -0.17853 | 59.8618 | -0.14648 | -0.022888 | -0.13733 | 0.036621 | 0.022889 | 0.041199 | -0.077819 | 0.064087 | -0.054931 | 0.23804 | 122.5754 | 0.045777 | 122.5433 | 122.3877 | 122.3694 | 122.3557 | 122.3465 | -122.5159 | -122.5067 | 122.5433 | 122.5204 | 59.7656 | 59.8434
240.7656 | 122.7631 | -59.6832 | 62.7319 | -0.27763 | 0.00084388 | 0.062453 | 0.081081 | 0.0012391 | -0.0016448 | -0.0035248 | 0.014954 | -0.00070063 | 0.062897 | 0.062758 | -0.0067099 | 0.0031231 | -0.00010671 | 0.059509 | 62.6129 | -59.7977 | 62.8464 | -59.5047 | -59.9075 | 0.11444 | 0.16022 | 62.6221 | -59.729 | 62.8235 | -59.6558 | -59.7565 | -59.6649 | -0.11444 | -0.11902 | 0.11444 | 0.17853 | 59.7977 | -0.2243 | 59.9121 | -0.10986 | -0.045776 | -0.10986 | 0.091552 | 0.027466 | 0.018311 | -0.073242 | 0.064087 | -0.027466 | 0.29297 | 122.644 | 0.073242 | 122.5525 | 122.4106 | 122.3511 | 122.2961 | 122.3053 | -122.5296 | -122.4609 | 122.5296 | 122.5067 | 59.7427 | 59.8434
241.7656 | 122.7539 | -59.6878 | 62.7228 | -0.10216 | 0.00084388 | 0.061598 | 0.081508 | 0.00081172 | 0.0004914 | -0.002884 | 0.011902 | 0.0010084 | 0.063324 | 0.062758 | -0.0079917 | 0.0016277 | -0.0020295 | 0.045776 | 62.6175 | -59.7519 | 62.851 | -59.4772 | -59.8755 | 0.13275 | 0.15564 | 62.6221 | -59.7519 | 62.8189 | -59.6512 | -59.7702 | -59.6512 | -0.064087 | -0.10528 | 0.12817 | 0.21057 | 59.8206 | -0.18768 | 59.8846 | -0.1236 | -0.064087 | -0.10071 | 0.096131 | 0.036621 | 0.036621 | -0.082398 | 0.10071 | -0.018311 | 0.27466 | 122.6028 | 0.10071 | 122.5708 | 122.3694 | 122.374 | 122.3053 | 122.3099 | -122.4747 | -122.4747 | 122.5388 | 122.5067 | 59.7336 | 59.8434
242.7656 | 122.7127 | -59.7061 | 62.7686 | -0.041122 | 0.0021255 | 0.063521 | 0.079372 | 0.0014527 | 0.000705 | -0.0037384 | 0.0057984 | 0.00015377 | 0.063751 | 0.067885 | -0.0075643 | 0.00077333 | 0.0024567 | 0.068665 | 62.6541 | -59.7473 | 62.8006 | -59.5505 | -59.9213 | 0.09613 | 0.1236 | 62.6221 | -59.729 | 62.7731 | -59.7015 | -59.8434 | -59.6878 | -0.041198 | -0.11444 | 0.032043 | 0.15564 | 59.8022 | -0.21515 | 59.8434 | -0.17395 | -0.022888 | -0.14648 | 0.004577 | 0.004578 | 0.018311 | -0.13733 | 0.041199 | -0.11444 | 0.19684 | 122.5479 | 0.027466 | 122.5021 | 122.4014 | 122.3511 | 122.3602 | 122.3282 | -122.5159 | -122.4976 | 122.5067 | 122.4792 | 59.7748 | 59.8297
243.7656 | 122.6395 | -59.729 | 62.7777 | -0.025863 | -0.0017197 | 0.060103 | 0.081081 | 0.0025207 | -0.0018586 | 0.00053404 | -0.06134 | 0.00058097 | 0.061615 | 0.065108 | -0.0084189 | 0.00055973 | -0.0039521 | 0.013733 | 62.6678 | -59.7702 | 62.7411 | -59.6329 | -60.0082 | 0.022888 | 0.17853 | 62.6724 | -59.7107 | 62.709 | -59.8114 | -59.8618 | -59.7702 | -0.041199 | -0.10986 | -0.036621 | 0.09613 | 59.7519 | -0.27924 | 59.7931 | -0.23804 | 0.018311 | -0.10529 | -0.068665 | -0.082397 | -0.041199 | -0.13275 | -0.05951 | -0.15106 | 0.13733 | 122.5113 | -0.10071 | 122.4197 | 122.4381 | 122.3831 | 122.3969 | 122.4014 | -122.5479 | -122.4884 | 122.4701 | 122.438 | 59.7427 | 59.9075
244.7656 | 122.6852 | -59.7107 | 62.7548 | -0.086899 | 0.0016983 | 0.064803 | 0.081294 | -0.0043151 | -0.0037812 | -0.00096136 | -0.027771 | -0.00027343 | 0.06247 | 0.059554 | -0.0073507 | 0.0041913 | -0.0016021 | 0.059509 | 62.645 | -59.7427 | 62.8098 | -59.5551 | -59.9167 | 0.09613 | 0.086975 | 62.6175 | -59.7382 | 62.7686 | -59.7382 | -59.8297 | -59.7107 | -0.032044 | -0.10986 | 0.054931 | 0.15564 | 59.8068 | -0.20599 | 59.8389 | -0.17395 | -0.027466 | -0.13733 | 0.013733 | -0.027466 | 0 | -0.11902 | 0.027466 | -0.091553 | 0.18768 | 122.5525 | 0 | 122.5067 | 122.3877 | 122.3557 | 122.3557 | 122.3282 | -122.4976 | -122.493 | 122.5204 | 122.4792 | 59.7702 | 59.7977
245.7656 | 122.6486 | -59.7382 | 62.7548 | -0.056381 | -0.00065152 | 0.063734 | 0.081294 | -0.0015381 | -0.0005768 | -0.00032036 | 0.06073 | 0.0016492 | 0.066529 | 0.062758 | -0.0073507 | 0.0033367 | 0.0011749 | -0.013733 | 62.6678 | -59.7748 | 62.7457 | -59.6375 | -60.0128 | 0.10071 | -0.14191 | 62.6724 | -59.7702 | 62.7228 | -59.7885 | -59.9442 | -59.7702 | -0.036621 | -0.086975 | -0.009155 | 0.10071 | 59.8389 | -0.27466 | 59.8755 | -0.23804 | -0.032044 | -0.082398 | -0.032044 | -0.050354 | -0.032044 | -0.20599 | 0 | -0.17395 | 0.13733 | 122.5204 | -0.01831 | 122.493 | 122.4426 | 122.4426 | 122.406 | 122.4106 | -122.5296 | -122.525 | 122.4838 | 122.4609 | 59.7244 | 59.5963
246.7656 | 122.6852 | -59.7336 | 62.7686 | -0.056381 | 0.0023391 | 0.063521 | 0.083003 | 0.00038452 | -0.0003632 | -0.0024566 | -0.039978 | 0.00036737 | 0.065033 | 0.066817 | -0.0090597 | 0.0041913 | 0.00096129 | 0.004578 | 62.7045 | -59.7839 | 62.7182 | -59.642 | -60.0174 | 0.009155 | 0.009155 | 62.6816 | -59.761 | 62.7319 | -59.7885 | -59.8984 | -59.7565 | -0.050354 | -0.064087 | -0.050354 | 0.091553 | 59.7427 | -0.28381 | 59.7931 | -0.23346 | -0.027465 | -0.086975 | -0.036621 | -0.054931 | -0.022888 | -0.16479 | 0.004577 | -0.13733 | 0.14191 | 122.5021 | -0.027466 | 122.493 | 122.4884 | 122.4426 | 122.4381 | 122.4152 | -122.5525 | -122.5296 | 122.4518 | 122.4655 | 59.7382 | 59.7427
247.7656 | 122.6532 | -59.7382 | 62.7777 | -0.018234 | 0.00020288 | 0.063307 | 0.083003 | 0.00017092 | 6.4004e-05 | -0.0013886 | -0.027771 | 0.00229 | 0.06482 | 0.05699 | -0.0073507 | 0.0026959 | 0.00096129 | -0.018311 | 62.6816 | -59.7794 | 62.8922 | -59.7565 | -60.228 | 0.004578 | 0.009155 | 62.6587 | -59.761 | 62.709 | -59.7794 | -59.8801 | -59.7565 | -0.041199 | -0.09613 | 0.11444 | -0.018311 | 59.7427 | -0.48981 | 59.7839 | -0.44861 | -0.022888 | -0.11902 | -0.068665 | -0.041199 | -0.018311 | -0.14191 | 0.004577 | -0.11902 | 0.022888 | 122.6715 | -0.018311 | 122.4701 | 122.4609 | 122.4197 | 122.4197 | 122.3969 | -122.5571 | -122.5388 | 122.6303 | 122.4472 | 59.7198 | 59.7473
248.7656 | 122.6395 | -59.7427 | 62.7823 | -0.048752 | 0.0010575 | 0.063094 | 0.081721 | 0.0035889 | -0.001004 | -0.002243 | -0.036926 | 0.0027174 | 0.063751 | 0.061049 | -0.0062827 | 0.0022687 | 0.00010689 | 0 | 62.677 | -59.7885 | 62.6907 | -59.6283 | -60.0494 | 0.032043 | 0 | 62.6724 | -59.761 | 62.6907 | -59.7794 | -59.9167 | -59.7794 | -0.045776 | -0.10529 | -0.091553 | 0.11444 | 59.7748 | -0.3067 | 59.8206 | -0.26093 | -0.01831 | -0.10986 | -0.091553 | -0.036621 | -0.036621 | -0.17395 | -0.018311 | -0.15564 | 0.16022 | 122.4792 | -0.018311 | 122.4518 | 122.4655 | 122.4335 | 122.4197 | 122.4152 | -122.5708 | -122.5433 | 122.4335 | 122.4335 | 59.7427 | 59.7427
249.7656 | 122.7081 | -59.7153 | 62.7686 | -0.041122 | 0.00041648 | 0.061385 | 0.080867 | 0.0035889 | -0.0003632 | -0.00032036 | -0.046081 | 0.0020764 | 0.064606 | 0.068099 | -0.0073507 | 0.00098693 | -0.0043793 | 0.004578 | 62.677 | -59.7931 | 62.709 | -59.6558 | -60.022 | 0.018311 | 0.018311 | 62.6633 | -59.7702 | 62.7457 | -59.7656 | -59.8755 | -59.7244 | -0.07782 | -0.091553 | -0.05951 | 0.059509 | 59.7336 | -0.3067 | 59.8114 | -0.22888 | -0.054932 | -0.10529 | -0.022888 | -0.050354 | -0.009155 | -0.16022 | 0.045777 | -0.10528 | 0.13733 | 122.5021 | 0.004578 | 122.5159 | 122.4701 | 122.4335 | 122.3923 | 122.3785 | -122.5616 | -122.5388 | 122.4243 | 122.4609 | 59.7198 | 59.7336
250.7656 | 122.6852 | -59.7244 | 62.7457 | -0.056381 | -1.0718e-05 | 0.063521 | 0.078944 | 0.0033753 | -0.0018586 | -0.00032036 | -0.039978 | 0.0014356 | 0.063965 | 0.062758 | -0.0097007 | 0.0035503 | 0.00032049 | -0.004578 | 62.6953 | -59.7656 | 62.7136 | -59.6603 | -60.0128 | 0.032043 | 0.013733 | 62.6724 | -59.7519 | 62.7457 | -59.7565 | -59.8892 | -59.7153 | -0.041199 | -0.050355 | -0.032044 | 0.064087 | 59.7565 | -0.28839 | 59.7977 | -0.24719 | -0.027466 | -0.073243 | 0 | -0.032044 | 0.009155 | -0.16479 | 0.036621 | -0.13733 | 0.10529 | 122.4792 | -0.004578 | 122.4976 | 122.4609 | 122.4243 | 122.4197 | 122.3969 | -122.5113 | -122.4976 | 122.438 | 122.4701 | 59.7198 | 59.7382
251.7656 | 122.6944 | -59.729 | 62.7594 | -0.06401 | 0.0010575 | 0.063307 | 0.081935 | 0.0018799 | -0.0048492 | -0.00010676 | -0.049133 | -0.00027343 | 0.06546 | 0.064681 | -0.0071371 | 0.0018413 | -0.0022431 | -0.004578 | 62.6724 | -59.7885 | 62.7228 | -59.6512 | -60.0174 | 0 | 0.013733 | 62.645 | -59.7656 | 62.7411 | -59.7519 | -59.8801 | -59.7244 | -0.059509 | -0.086975 | -0.036621 | 0.07782 | 59.729 | -0.28839 | 59.7885 | -0.22888 | -0.036621 | -0.11444 | -0.01831 | -0.022888 | 0.004578 | -0.15106 | 0.041199 | -0.11444 | 0.13733 | 122.5113 | 0.013733 | 122.5067 | 122.4609 | 122.4106 | 122.4014 | 122.374 | -122.5479 | -122.525 | 122.4518 | 122.4701 | 59.7244 | 59.7427
252.7656 | 122.7036 | -59.7198 | 62.7548 | 0.004654 | 0.0021255 | 0.063307 | 0.080653 | 0.0044433 | -0.0012176 | 0.00032044 | -0.067444 | 0.0014356 | 0.063751 | 0.062545 | -0.0062827 | 0.0014141 | -0.0018157 | 0.018311 | 62.6678 | -59.7794 | 62.7548 | -59.6008 | -59.9991 | 0.032043 | -0.17395 | 62.5992 | -59.7839 | 62.7823 | -59.7656 | -59.8663 | -59.7015 | -0.059509 | -0.086975 | 0 | 0.11902 | 59.7519 | -0.27923 | 59.8114 | -0.21973 | -0.064087 | -0.15564 | 0.027466 | -0.045776 | 0.018311 | -0.14648 | 0.082398 | -0.082397 | 0.17853 | 122.5342 | 0.018311 | 122.5662 | 122.4472 | 122.3831 | 122.3877 | 122.319 | -122.5342 | -122.5388 | 122.4747 | 122.5021 | 59.7382 | 59.5459
253.7656 | 122.7081 | -59.7382 | 62.7411 | -0.079269 | 0.0010575 | 0.064589 | 0.082362 | 0.0016663 | -0.0014312 | -0.0037384 | -0.024719 | -0.001128 | 0.066956 | 0.062972 | -0.0084189 | 0.0024823 | -0.0016021 | 0.027466 | 62.6495 | -59.761 | 62.7411 | -59.6008 | -60.3195 | -0.054932 | 0.073242 | 62.6541 | -59.7656 | 62.7548 | -59.7519 | -59.8526 | -59.7107 | -0.022888 | -0.091553 | 0 | 0.13733 | 59.6832 | -0.58136 | 59.7061 | -0.55847 | -0.027466 | -0.086975 | 0.013733 | -0.013733 | 0.027466 | -0.11444 | 0.054932 | -0.086975 | 0.16022 | 122.5021 | 0.013733 | 122.5204 | 122.4106 | 122.4197 | 122.3877 | 122.3923 | -122.5021 | -122.5067 | 122.4792 | 122.493 | 59.7656 | 59.8114
254.7656 | 122.7127 | -59.729 | 62.7777 | -0.06401 | 0.00020288 | 0.06523 | 0.081508 | 0.0042297 | -0.0033538 | 0.00074764 | -0.024719 | 0.0020764 | 0.06482 | 0.063826 | -0.0086325 | 0.0026959 | 0.0033111 | 0.009155 | 62.6816 | -59.7656 | 62.7365 | -59.6237 | -59.9854 | 0.036621 | 0.045776 | 62.6633 | -59.7656 | 62.7502 | -59.7565 | -59.8709 | -59.7107 | -0.036621 | -0.09613 | -0.041199 | 0.10529 | 59.7656 | -0.25635 | 59.8022 | -0.21973 | -0.036621 | -0.11444 | -0.027466 | -0.027466 | 0.018311 | -0.14191 | 0.054932 | -0.10529 | 0.14191 | 122.5021 | 0.009155 | 122.5159 | 122.4472 | 122.4289 | 122.4106 | 122.3923 | -122.5433 | -122.5433 | 122.4655 | 122.4792 | 59.7382 | 59.7748
255.7656 | 122.699 | -59.7427 | 62.7594 | -0.0029755 | 0.0014847 | 0.064375 | 0.080226 | -0.0013245 | -0.0037812 | 0.00032044 | -0.049133 | 0.00079477 | 0.063965 | 0.05934 | -0.0090597 | 0.0022687 | 0.00010689 | 0.009155 | 62.6724 | -59.7885 | 62.7319 | -59.6329 | -59.9762 | 0.036621 | 0.032043 | 62.6358 | -59.7702 | 62.7502 | -59.7382 | -59.8755 | -59.7015 | -0.045776 | -0.086975 | -0.027465 | 0.10986 | 59.7794 | -0.23346 | 59.8251 | -0.18768 | -0.027466 | -0.1236 | -0.009155 | 0.004578 | 0.041199 | -0.13275 | 0.068665 | -0.10528 | 0.15564 | 122.5204 | 0.032044 | 122.5204 | 122.4609 | 122.406 | 122.4152 | 122.3785 | -122.5479 | -122.5296 | 122.4747 | 122.493 | 59.7519 | 59.7748
256.7656 | 122.6669 | -59.7336 | 62.7457 | -0.056381 | 0.0016983 | 0.06523 | 0.079585 | -0.00025628 | -0.0007904 | -0.001175 | -0.049133 | 0.00036737 | 0.064392 | 0.067244 | -0.0077779 | 0.0024823 | 0.0018159 | -0.09613 | 62.6175 | -59.7885 | 62.7457 | -59.5642 | -59.9716 | 0.022888 | 0.041199 | 62.6266 | -59.7839 | 62.7502 | -59.7702 | -59.8801 | -59.7198 | -0.054931 | -0.12817 | 0 | 0.16937 | 59.7565 | -0.23804 | 59.8114 | -0.18311 | -0.050354 | -0.11902 | 0.004577 | -0.036621 | 0.013733 | -0.14648 | 0.064087 | -0.09613 | 0.2243 | 122.5342 | 0.013733 | 122.5342 | 122.406 | 122.4106 | 122.3511 | 122.3602 | -122.5342 | -122.5296 | 122.4792 | 122.4838 | 59.6375 | 59.7748
257.7656 | 122.699 | -59.729 | 62.7319 | -0.07164 | 0.00041648 | 0.061812 | 0.083217 | 0.0033753 | -0.0014312 | 0.00053404 | -0.049133 | 0.0010084 | 0.066529 | 0.058913 | -0.010128 | 0.0031231 | 0.00032049 | 0.054932 | 62.6541 | -59.8022 | 62.7594 | -59.5917 | -59.9991 | 0.027466 | 0.036621 | 62.6266 | -59.7702 | 62.7502 | -59.7656 | -59.8984 | -59.7336 | -0.073242 | -0.07782 | 0.027465 | 0.13733 | 59.7565 | -0.27008 | 59.8297 | -0.19684 | -0.041199 | -0.10529 | 0.01831 | -0.036621 | -0.004578 | -0.16937 | 0.036621 | -0.12817 | 0.21057 | 122.5616 | 0.004578 | 122.5204 | 122.4564 | 122.3969 | 122.3831 | 122.3557 | -122.5342 | -122.5021 | 122.4884 | 122.4792 | 59.7839 | 59.7656
258.7656 | 122.7127 | -59.7519 | 62.764 | -0.056381 | -0.00043792 | 0.063948 | 0.081935 | 0.0029479 | -0.0016448 | 0.002243 | -0.055237 | 0.00079477 | 0.065247 | 0.063826 | -0.0099143 | 0.0029095 | 0.0041657 | 0.022888 | 62.6724 | -59.7794 | 62.7457 | -59.5917 | -59.9899 | 0.004578 | 0.036621 | 62.6175 | -59.7839 | 62.7457 | -59.7702 | -59.8984 | -59.7244 | -0.027466 | -0.091553 | -0.01831 | 0.16022 | 59.7565 | -0.23804 | 59.7839 | -0.21057 | -0.032044 | -0.14648 | -0.01831 | -0.018311 | 0.027466 | -0.14648 | 0.05951 | -0.11444 | 0.18768 | 122.525 | 0.013733 | 122.5296 | 122.4518 | 122.4014 | 122.4243 | 122.3694 | -122.5433 | -122.5479 | 122.4976 | 122.4976 | 59.7748 | 59.7885
259.7656 | 122.6578 | -59.7382 | 62.7411 | -0.086899 | 0.00041648 | 0.063521 | 0.080226 | -0.0011109 | 0.0002778 | 0.0026702 | -0.049133 | 0.0014356 | 0.06546 | 0.062972 | -0.0077779 | 0.0037641 | -0.00096131 | -0.022888 | 62.6587 | -59.7839 | 62.6953 | -59.6558 | -60.0266 | -0.041199 | -0.059509 | 62.6129 | -59.7748 | 62.7045 | -59.8389 | -59.9304 | -59.761 | -0.045777 | -0.082398 | -0.045777 | 0.082397 | 59.697 | -0.28839 | 59.7427 | -0.24261 | -0.036621 | -0.12817 | -0.036621 | -0.10071 | -0.022888 | -0.19226 | 0.013733 | -0.15564 | 0.12817 | 122.4792 | -0.064087 | 122.4792 | 122.4426 | 122.3877 | 122.3969 | 122.3511 | -122.525 | -122.5159 | 122.4335 | 122.4426 | 59.7153 | 59.6787
260.7656 | 122.644 | -59.7748 | 62.7319 | -0.041122 | 0.0012711 | 0.064162 | 0.081935 | 0.00081172 | 0.0004914 | 0.0013886 | -0.04303 | 0.00015377 | 0.065674 | 0.06404 | -0.0088461 | 0.00098693 | 0.0028839 | -0.045776 | 62.6404 | -59.8022 | 62.6999 | -59.6512 | -60.054 | -0.064087 | -0.059509 | 62.6358 | -59.7794 | 62.6862 | -59.8297 | -59.9579 | -59.7656 | -0.027466 | -0.091553 | -0.032044 | 0.1236 | 59.7107 | -0.27924 | 59.7382 | -0.25177 | -0.004578 | -0.096131 | -0.045777 | -0.054932 | 0.009155 | -0.18311 | 0.013733 | -0.17853 | 0.15106 | 122.5021 | -0.050354 | 122.4655 | 122.4426 | 122.4152 | 122.4152 | 122.4106 | -122.5342 | -122.5113 | 122.4747 | 122.4609 | 59.729 | 59.7153
261.7656 | 122.6761 | -59.7198 | 62.7411 | -0.094528 | 0.00041648 | 0.063734 | 0.080653 | 0.0033753 | 0.000705 | -0.0020294 | -0.046081 | 0.0018628 | 0.065888 | 0.070449 | -0.0086325 | 0.0035503 | -0.0024567 | -0.004578 | 62.6724 | -59.7748 | 62.7548 | -59.61 | -60.0037 | 0 | -0.004578 | 62.6129 | -59.7794 | 62.7228 | -59.7885 | -59.8984 | -59.7336 | -0.054931 | -0.068665 | 0.013733 | 0.10986 | 59.7198 | -0.28381 | 59.7748 | -0.22888 | -0.059509 | -0.12817 | -0.018311 | -0.068664 | -0.013733 | -0.17853 | 0.045776 | -0.11902 | 0.16479 | 122.5296 | -0.009155 | 122.5021 | 122.4472 | 122.3923 | 122.3923 | 122.3328 | -122.5159 | -122.5204 | 122.4747 | 122.4426 | 59.7153 | 59.7153
262.7656 | 122.699 | -59.7427 | 62.7502 | -0.086899 | 0.0014847 | 0.063307 | 0.080867 | -0.0021789 | -0.0003632 | -0.0013886 | -0.033874 | 0.00079477 | 0.065247 | 0.065108 | -0.0094869 | 0.0029095 | -0.0030975 | -0.013733 | 62.6312 | -59.8068 | 62.7319 | -59.6054 | -60.0128 | -0.004578 | 0.013733 | 62.6266 | -59.7794 | 62.7182 | -59.7885 | -59.9167 | -59.7382 | -0.064087 | -0.11902 | -0.01831 | 0.13733 | 59.7382 | -0.27008 | 59.8022 | -0.20599 | -0.036621 | -0.1236 | -0.032043 | -0.045776 | 0.004578 | -0.17395 | 0.041199 | -0.13733 | 0.20142 | 122.5388 | -0.009155 | 122.4976 | 122.4381 | 122.406 | 122.374 | 122.3694 | -122.5571 | -122.5296 | 122.4747 | 122.4609 | 59.729 | 59.7565
263.7656 | 122.6349 | -59.7519 | 62.7365 | -0.10216 | 0.00041648 | 0.062666 | 0.081721 | 0.0020935 | -0.0012176 | 0.00010684 | -0.039978 | 0.0010084 | 0.065247 | 0.061904 | -0.010342 | 0.0033367 | -0.0013885 | -0.054932 | 62.6633 | -59.7839 | 62.6724 | -59.6924 | -60.0723 | -0.086975 | -0.11902 | 62.6312 | -59.7702 | 62.6678 | -59.8526 | -59.9762 | -59.7885 | -0.032044 | -0.073242 | -0.064087 | 0.059509 | 59.6649 | -0.32044 | 59.697 | -0.28839 | -0.018311 | -0.10529 | -0.068664 | -0.10071 | -0.036621 | -0.2243 | -0.01831 | -0.20599 | 0.091553 | 122.4564 | -0.082397 | 122.4381 | 122.4472 | 122.4014 | 122.4152 | 122.3831 | -122.5204 | -122.5067 | 122.4243 | 122.4197 | 59.697 | 59.6329
264.7656 | 122.644 | -59.7427 | 62.7045 | -0.041122 | -0.0015061 | 0.062453 | 0.079799 | -0.00046988 | -0.0031402 | -0.0018158 | -0.049133 | -5.9826e-05 | 0.065674 | 0.056777 | -0.0079917 | 0.0014141 | -0.0020295 | -0.059509 | 62.6724 | -59.816 | 62.6816 | -59.6924 | -60.0769 | -0.082397 | -0.10986 | 62.6312 | -59.7885 | 62.6633 | -59.8526 | -59.9762 | -59.7656 | -0.073242 | -0.032044 | -0.022888 | 0.050354 | 59.6603 | -0.33417 | 59.7336 | -0.26093 | -0.045776 | -0.073242 | -0.041199 | -0.10986 | -0.022888 | -0.23346 | 0.022888 | -0.18768 | 0.1236 | 122.4976 | -0.064087 | 122.4518 | 122.4884 | 122.4197 | 122.4152 | 122.374 | -122.5204 | -122.493 | 122.4243 | 122.406 | 59.6832 | 59.6329
265.7656 | 122.6624 | -59.7519 | 62.7457 | -0.07164 | 0.0014847 | 0.065871 | 0.082576 | 0.00081172 | -0.0014312 | -0.00032036 | -0.027771 | 0.00036737 | 0.064606 | 0.05934 | -0.0069235 | 0.0029095 | 0.00032049 | -0.045776 | 62.645 | -59.7977 | 62.677 | -59.7061 | -60.0769 | -0.082397 | -0.12817 | 62.6221 | -59.7702 | 62.6678 | -59.8709 | -59.9808 | -59.7702 | -0.045776 | -0.10071 | -0.068665 | 0.045776 | 59.6695 | -0.32501 | 59.7153 | -0.27924 | -0.018311 | -0.1236 | -0.07782 | -0.11902 | -0.018311 | -0.22888 | 0 | -0.21057 | 0.091552 | 122.4747 | -0.10071 | 122.4381 | 122.4426 | 122.3923 | 122.3969 | 122.374 | -122.5433 | -122.5159 | 122.4289 | 122.4197 | 59.7061 | 59.6237
266.7656 | 122.6303 | -59.7656 | 62.7457 | -0.26237 | 0.00084388 | 0.061171 | 0.080226 | 0.0027343 | -0.0016448 | -0.00096136 | -0.015564 | -0.0019824 | 0.06546 | 0.058486 | -0.0077779 | 0.0031231 | 0.0013885 | 0.086975 | 62.6266 | -59.7977 | 62.6587 | -59.6786 | -60.0998 | -0.10529 | -0.17395 | 62.6358 | -59.7885 | 62.677 | -59.8663 | -59.9991 | -59.7839 | -0.032043 | -0.11902 | -0.086976 | 0.086975 | 59.6603 | -0.33417 | 59.6924 | -0.30212 | -0.022888 | -0.10986 | -0.068665 | -0.10071 | -0.018311 | -0.23346 | 0.004577 | -0.21057 | 0.11902 | 122.4564 | -0.07782 | 122.4655 | 122.4243 | 122.4243 | 122.3923 | 122.4014 | -122.5433 | -122.5342 | 122.4243 | 122.4426 | 59.8526 | 59.5917
267.7656 | 122.6349 | -59.7748 | 62.7136 | -0.079269 | -0.0012923 | 0.063734 | 0.08279 | -0.0017517 | -0.0033538 | 0.00010684 | -0.027771 | 0.001222 | 0.065888 | 0.05464 | -0.0079917 | 0.0024823 | 0.00032049 | -0.036621 | 62.6678 | -59.7931 | 62.645 | -59.7382 | -60.1089 | -0.10529 | -0.15564 | 62.6221 | -59.7931 | 62.677 | -59.8572 | -59.9808 | -59.761 | -0.018311 | -0.045776 | -0.068665 | 0.036621 | 59.6695 | -0.33417 | 59.6878 | -0.31586 | -0.018311 | -0.091553 | -0.036621 | -0.082398 | 0.013733 | -0.20599 | 0.032044 | -0.18768 | 0.054932 | 122.438 | -0.064087 | 122.4701 | 122.4609 | 122.4152 | 122.4426 | 122.3969 | -122.5067 | -122.5067 | 122.4197 | 122.4518 | 59.7382 | 59.6191
268.7656 | 122.4976 | -59.8022 | 62.6587 | -0.033493 | -0.00022432 | 0.06288 | 0.081294 | 0.00017092 | -0.001004 | 0.001175 | -0.036926 | 0.00229 | 0.064392 | 0.065749 | -0.0069235 | 0.0031231 | 0.00074769 | -0.059509 | 62.6312 | -59.8022 | 62.6541 | -59.7198 | -60.1089 | -0.11444 | -0.14648 | 62.6221 | -59.8022 | 62.6633 | -59.9075 | -59.9854 | -59.7977 | 0 | -0.027465 | -0.004577 | 0.082397 | 59.6878 | -0.3067 | 59.6878 | -0.3067 | 0 | -0.036621 | 0.004578 | -0.10529 | 0.004578 | -0.18311 | 0.004578 | -0.18311 | 0.082397 | 122.4564 | -0.10529 | 122.4655 | 122.4335 | 122.4243 | 122.4335 | 122.4243 | -122.4609 | -122.4609 | 122.4564 | 122.4655 | 59.7427 | 59.6558
269.7656 | 122.6166 | -59.7427 | 62.7365 | -0.06401 | 0.0021255 | 0.063734 | 0.081294 | 0.0018799 | -0.0018586 | -0.00053396 | -0.027771 | -0.00048703 | 0.063751 | 0.062331 | -0.0088461 | 0.00077333 | -0.0037383 | -0.086975 | 62.6358 | -59.7885 | 62.645 | -59.7244 | -60.0906 | -0.10529 | -0.16937 | 62.6266 | -59.7748 | 62.4619 | -60.1501 | -59.6695 | -59.5688 | -0.045776 | -0.10071 | -0.091553 | 0.018311 | 59.6375 | -0.3479 | 59.6832 | -0.30212 | -0.032043 | -0.10986 | -0.27466 | -0.40741 | 0.17395 | 0.073242 | 0.20599 | 0.10529 | 0.064087 | 122.4335 | -0.37537 | 122.2366 | 122.4243 | 122.4014 | 122.3785 | 122.3694 | -122.525 | -122.5113 | 122.3877 | 122.2046 | 59.6558 | 59.5734
270.7656 | 122.6532 | -59.7702 | 62.7136 | -0.094528 | 0.0016983 | 0.062025 | 0.082362 | -0.0021789 | 0.0002778 | -0.00032036 | -0.0064086 | 0.0014356 | 0.06482 | 0.065962 | -0.0094869 | 0.0022687 | 0.0011749 | -0.11902 | 62.6404 | -59.8206 | 62.6541 | -59.7198 | -60.0769 | -0.10071 | -0.16022 | 62.6129 | -59.7977 | 62.6907 | -59.8434 | -59.967 | -59.7702 | -0.050354 | -0.073242 | -0.059509 | 0.050354 | 59.6695 | -0.3067 | 59.7198 | -0.25635 | -0.027465 | -0.10071 | -0.022888 | -0.073242 | 0 | -0.19684 | 0.027465 | -0.16937 | 0.10071 | 122.4747 | -0.045777 | 122.4884 | 122.4609 | 122.4106 | 122.4106 | 122.3831 | -122.5342 | -122.5113 | 122.4243 | 122.4609 | 59.6512 | 59.61
271.7656 | 122.6578 | -59.761 | 62.7182 | -0.033493 | 0.0010575 | 0.063094 | 0.083003 | -0.00046988 | -0.002713 | -0.00032036 | -0.024719 | -0.00091423 | 0.065247 | 0.070662 | -0.0071371 | 0.0039777 | -0.0026703 | -0.10071 | 62.6587 | -59.8206 | 62.6495 | -59.7153 | -60.0952 | -0.11444 | -0.16022 | 62.6266 | -59.8022 | 62.6953 | -59.848 | -59.9533 | -59.7839 | -0.05951 | -0.05951 | -0.068665 | 0.045776 | 59.6466 | -0.33417 | 59.7061 | -0.27466 | -0.041199 | -0.091553 | -0.022889 | -0.086975 | -0.022889 | -0.19226 | 0.01831 | -0.15106 | 0.10529 | 122.4701 | -0.045776 | 122.4976 | 122.4792 | 122.4289 | 122.4197 | 122.3877 | -122.5388 | -122.5204 | 122.4106 | 122.4564 | 59.6603 | 59.6008
272.7656 | 122.6807 | -59.7565 | 62.7182 | -0.06401 | 0.0010575 | 0.063521 | 0.081294 | -0.0041015 | -0.0024994 | 0.0016022 | -0.021667 | 0.001222 | 0.064392 | 0.058272 | -0.0075643 | 0.0033367 | 0.0022431 | -0.10986 | 62.6358 | -59.7977 | 62.6404 | -59.7107 | -60.1089 | -0.11444 | -0.14648 | 62.5946 | -59.7839 | 62.6953 | -59.8526 | -59.9625 | -59.7656 | -0.041198 | -0.082398 | -0.07782 | 0.045777 | 59.642 | -0.35248 | 59.6832 | -0.31128 | -0.027466 | -0.1236 | -0.022889 | -0.09613 | -0.009155 | -0.20599 | 0.018311 | -0.17853 | 0.086975 | 122.438 | -0.068664 | 122.4792 | 122.4335 | 122.3785 | 122.3923 | 122.3511 | -122.5159 | -122.5021 | 122.3969 | 122.4518 | 59.6466 | 59.61
273.7656 | 122.7448 | -59.761 | 62.6724 | -0.07164 | 0.0016983 | 0.06288 | 0.081721 | -0.00025628 | -0.0012176 | -0.00053396 | 0.011902 | 0.0020764 | 0.065247 | 0.053786 | -0.0082053 | 0.0022687 | -0.0011749 | -0.086975 | 62.6175 | -59.8022 | 62.7136 | -59.6375 | -60.0494 | -0.082397 | -0.086975 | 62.5763 | -59.7794 | 62.7594 | -59.761 | -59.8801 | -59.6832 | -0.041199 | -0.054931 | 0.041199 | 0.1236 | 59.6786 | -0.28839 | 59.7198 | -0.24719 | -0.018311 | -0.09613 | 0.086975 | 0 | 0.077819 | -0.11902 | 0.09613 | -0.10071 | 0.16479 | 122.5159 | 0.018311 | 122.5388 | 122.4197 | 122.3557 | 122.3785 | 122.3373 | -122.4747 | -122.4518 | 122.4747 | 122.5204 | 59.6741 | 59.6741
274.7656 | 122.7356 | -59.7382 | 62.6678 | -0.048752 | 0.00084388 | 0.06288 | 0.080226 | 0.0012391 | 0.0015594 | 0.00032044 | -0.015564 | 0.0014356 | 0.061829 | 0.062545 | -0.0079917 | 0.00013253 | 0.0024567 | -0.09613 | 62.6221 | -59.7794 | 62.6999 | -59.6283 | -60.0357 | -0.082397 | -0.07782 | 62.5671 | -59.7794 | 62.7731 | -59.7473 | -59.8526 | -59.6695 | -0.041199 | -0.045777 | 0.032043 | 0.10986 | 59.6558 | -0.29755 | 59.697 | -0.25635 | -0.041199 | -0.10071 | 0.10528 | -0.009155 | 0.068664 | -0.11444 | 0.10986 | -0.073242 | 0.15106 | 122.4792 | 0.032044 | 122.5525 | 122.4014 | 122.3465 | 122.3602 | 122.3053 | -122.4472 | -122.4472 | 122.438 | 122.5113 | 59.642 | 59.6603
275.7656 | 122.6715 | -59.7656 | 62.7228 | -0.041122 | 0.0010575 | 0.063734 | 0.081935 | -0.00025628 | -0.0031402 | 0.00074764 | -0.06134 | -0.00027343 | 0.064606 | 0.062331 | -0.0088461 | 0.0016277 | -0.0033111 | -0.10071 | 62.6541 | -59.8297 | 62.6541 | -59.697 | -60.0906 | -0.10529 | -0.13275 | 62.6083 | -59.7702 | 62.7045 | -59.8389 | -59.935 | -59.7519 | -0.064087 | -0.068664 | -0.068664 | 0.068665 | 59.6603 | -0.32501 | 59.7244 | -0.26093 | -0.004578 | -0.11444 | -0.01831 | -0.073242 | 0.013733 | -0.16937 | 0.018311 | -0.16479 | 0.13275 | 122.4838 | -0.068664 | 122.4747 | 122.4838 | 122.3785 | 122.4197 | 122.374 | -122.5525 | -122.493 | 122.4197 | 122.4701 | 59.6649 | 59.6329
276.7656 | 122.6624 | -59.7656 | 62.6953 | -0.025863 | -1.0718e-05 | 0.06288 | 0.082149 | -0.0026063 | -0.0001496 | -0.00096136 | -0.036926 | -0.00027343 | 0.063965 | 0.062331 | -0.010342 | 0.0018413 | -0.0013885 | -0.11444 | 62.6495 | -59.8114 | 62.6541 | -59.7015 | -60.0998 | -0.10986 | -0.11902 | 62.5992 | -59.7931 | 62.7228 | -59.816 | -59.9442 | -59.7519 | -0.045776 | -0.045776 | -0.041198 | 0.064087 | 59.6558 | -0.33417 | 59.7015 | -0.28839 | -0.027466 | -0.09613 | 0.027466 | -0.050354 | 0.013733 | -0.17853 | 0.041199 | -0.15106 | 0.10986 | 122.4655 | -0.022888 | 122.5159 | 122.4609 | 122.3923 | 122.4152 | 122.3648 | -122.5067 | -122.4884 | 122.4197 | 122.4884 | 59.6512 | 59.6466
277.7656 | 122.7676 | -59.7153 | 62.6678 | -0.10979 | 0.0014847 | 0.062239 | 0.081935 | -0.0034607 | -0.0001496 | -0.00010676 | 0.0027466 | -0.0013416 | 0.063111 | 0.060195 | -0.0090597 | 0.0012005 | 0.0016021 | -0.09613 | 62.6175 | -59.7885 | 62.7274 | -59.6237 | -60.0128 | -0.050354 | -0.073242 | 62.5992 | -59.7656 | 62.796 | -59.7244 | -59.8389 | -59.6603 | -0.073242 | -0.050354 | 0.059509 | 0.091553 | 59.6649 | -0.29755 | 59.7382 | -0.2243 | -0.050354 | -0.068665 | 0.12817 | -0.009155 | 0.054932 | -0.1236 | 0.10529 | -0.073242 | 0.1648 | 122.5159 | 0.041199 | 122.5616 | 122.406 | 122.3648 | 122.3328 | 122.3145 | -122.4564 | -122.4335 | 122.4426 | 122.5113 | 59.6191 | 59.642
278.7656 | 122.7722 | -59.729 | 62.6907 | -0.06401 | 0.00041648 | 0.064589 | 0.080653 | 0.00017092 | -0.0001496 | 0.0013886 | -0.021667 | -0.0017688 | 0.065674 | 0.063613 | -0.011623 | 0.0033367 | -0.00032051 | -0.07782 | 62.6038 | -59.8068 | 62.7365 | -59.642 | -59.9945 | -0.054932 | -0.068665 | 62.5763 | -59.7702 | 62.7869 | -59.729 | -59.8663 | -59.6603 | -0.07782 | -0.086975 | 0.045776 | 0.086975 | 59.6741 | -0.2655 | 59.7519 | -0.18768 | -0.041199 | -0.11444 | 0.09613 | 0 | 0.068665 | -0.13733 | 0.10986 | -0.09613 | 0.16479 | 122.5433 | 0.041199 | 122.5571 | 122.4106 | 122.3465 | 122.3328 | 122.3053 | -122.4976 | -122.4609 | 122.4655 | 122.5159 | 59.6512 | 59.6603
279.7656 | 122.7448 | -59.7244 | 62.7045 | -0.056381 | 0.0012711 | 0.064803 | 0.081294 | 0.0012391 | -0.0001496 | 0.00010684 | -0.024719 | 0.00079477 | 0.063324 | 0.06404 | -0.012478 | 0.0018413 | 0.00010689 | -0.082397 | 62.6129 | -59.7977 | 62.7365 | -59.6191 | -59.9991 | -0.036621 | -0.059509 | 62.5717 | -59.7748 | 62.7686 | -59.7382 | -59.8572 | -59.6512 | -0.073242 | -0.091553 | 0.032043 | 0.10529 | 59.6878 | -0.27466 | 59.761 | -0.20142 | -0.050354 | -0.13275 | 0.064087 | -0.013733 | 0.073242 | -0.13275 | 0.1236 | -0.082398 | 0.17853 | 122.5342 | 0.036621 | 122.5433 | 122.4106 | 122.3465 | 122.3373 | 122.2961 | -122.5021 | -122.4792 | 122.4609 | 122.493 | 59.642 | 59.6649
280.7656 | 122.7631 | -59.7336 | 62.6678 | -0.13267 | 0.00063028 | 0.063307 | 0.079799 | 0.0012391 | -0.0014312 | 0.0018158 | 0.011902 | -0.00027343 | 0.06546 | 0.059981 | -0.010128 | 0.00034613 | -0.0033111 | -0.050354 | 62.5946 | -59.7702 | 62.7731 | -59.5688 | -59.9533 | -0.022888 | -0.013733 | 62.5671 | -59.7565 | 62.7823 | -59.7336 | -59.8343 | -59.6512 | -0.036621 | -0.073243 | 0.10528 | 0.16479 | 59.7107 | -0.21973 | 59.7473 | -0.1831 | -0.022888 | -0.10071 | 0.11444 | 0 | 0.082398 | -0.10071 | 0.10529 | -0.07782 | 0.20142 | 122.5433 | 0.022888 | 122.5388 | 122.3648 | 122.3236 | 122.3282 | 122.3007 | -122.4381 | -122.4243 | 122.5067 | 122.5159 | 59.6832 | 59.7198
281.7656 | 122.7859 | -59.7061 | 62.6724 | -0.094528 | 0.00084388 | 0.064589 | 0.081935 | 0.0031617 | -0.0014312 | -0.0033112 | 0.0027466 | 0.0010084 | 0.062897 | 0.065962 | -0.010982 | 0.00098693 | -0.0035247 | -0.036621 | 62.6129 | -59.7702 | 62.7686 | -59.5734 | -60.0037 | -0.013733 | -0.004578 | 62.5717 | -59.7473 | 62.7869 | -59.7198 | -59.8068 | -59.6603 | -0.064087 | -0.059509 | 0.096131 | 0.13275 | 59.6924 | -0.29755 | 59.7565 | -0.23346 | -0.041198 | -0.10071 | 0.11444 | -0.013733 | 0.045777 | -0.10071 | 0.086975 | -0.05951 | 0.19684 | 122.5388 | 0.027465 | 122.5342 | 122.3831 | 122.319 | 122.319 | 122.2778 | -122.4426 | -122.4197 | 122.4747 | 122.493 | 59.6695 | 59.7015
282.7656 | 122.7127 | -59.7427 | 62.6358 | -0.094528 | 0.00063028 | 0.064375 | 0.08279 | 0.0020935 | -0.0003632 | 0.00096124 | -0.030823 | -5.9826e-05 | 0.064179 | 0.062972 | -0.0086325 | 0.0012005 | 0.00053409 | -0.059509 | 62.6266 | -59.7885 | 62.7411 | -59.6146 | -60.0174 | -0.032043 | -0.041199 | 62.5626 | -59.7794 | 62.8006 | -59.7427 | -59.8389 | -59.6603 | -0.045776 | -0.009155 | 0.10529 | 0.12817 | 59.7107 | -0.27466 | 59.7565 | -0.22888 | -0.036621 | -0.073242 | 0.16479 | 0 | 0.082398 | -0.09613 | 0.11902 | -0.059509 | 0.17395 | 122.5296 | 0.036621 | 122.58 | 122.4152 | 122.3419 | 122.3694 | 122.3053 | -122.4243 | -122.4152 | 122.4838 | 122.5433 | 59.6832 | 59.7015
283.7656 | 122.7676 | -59.7702 | 62.6541 | -0.010605 | 0.0014847 | 0.063307 | 0.082576 | -0.00046988 | -0.0035674 | 0.001175 | -0.04303 | -0.00070063 | 0.064606 | 0.059554 | -0.0097007 | 0.0031231 | -0.00010671 | -0.068665 | 62.6129 | -59.8022 | 62.7502 | -59.6008 | -59.9899 | -0.045776 | -0.036621 | 62.5763 | -59.7656 | 62.8052 | -59.7336 | -59.9396 | -59.848 | -0.032043 | -0.041199 | 0.09613 | 0.16937 | 59.7244 | -0.21973 | 59.7565 | -0.18768 | 0.004578 | -0.07782 | 0.15106 | 0.036621 | -0.077819 | -0.16937 | -0.082397 | -0.17395 | 0.20142 | 122.5525 | 0.032043 | 122.5708 | 122.4152 | 122.3419 | 122.3831 | 122.3465 | -122.4564 | -122.4197 | 122.5204 | 122.5754 | 59.7015 | 59.7336
284.7656 | 122.7631 | -59.7244 | 62.6678 | -0.094528 | 0.0010575 | 0.064803 | 0.080653 | -0.0021789 | -0.0020722 | 0.00010684 | -0.00030524 | 0.00058097 | 0.063751 | 0.059981 | -0.010982 | 0.0012005 | 0.00053409 | -0.032043 | 62.5763 | -59.7748 | 62.7777 | -59.5688 | -59.9716 | -0.022888 | -0.004578 | 62.5397 | -59.7656 | 62.7823 | -59.7061 | -59.8389 | -59.6695 | -0.050354 | -0.091553 | 0.10986 | 0.15564 | 59.7015 | -0.24719 | 59.7519 | -0.19684 | -0.041199 | -0.12817 | 0.11444 | 0.01831 | 0.054931 | -0.11444 | 0.09613 | -0.073242 | 0.20599 | 122.5525 | 0.059509 | 122.5479 | 122.3511 | 122.3053 | 122.3007 | 122.2641 | -122.4426 | -122.4335 | 122.5021 | 122.5067 | 59.6924 | 59.7198
285.7812 | 122.7173 | -59.7061 | 62.6907 | -0.10979 | 0.0029801 | 0.062239 | 0.080867 | -0.0023925 | 0.000705 | -0.004593 | 0.011902 | 0.0016492 | 0.065888 | 0.059554 | -0.0088461 | 0.0022687 | 0.0058747 | -0.064087 | 62.6083 | -59.7702 | 62.7365 | -59.6054 | -60.0174 | -0.027466 | -0.059509 | 62.5992 | -59.7748 | 62.7548 | -59.7748 | -59.848 | -59.7061 | -0.064087 | -0.082398 | 0.045776 | 0.10071 | 59.6787 | -0.31128 | 59.7427 | -0.24719 | -0.068664 | -0.091553 | 0.064087 | -0.068664 | 0 | -0.14191 | 0.068664 | -0.073242 | 0.1648 | 122.5067 | 0 | 122.5296 | 122.3785 | 122.374 | 122.3145 | 122.3053 | -122.4609 | -122.4655 | 122.4426 | 122.4609 | 59.642 | 59.6466
286.8438 | 122.7493 | -59.7153 | 62.6678 | -0.12505 | 0.00084388 | 0.063734 | 0.082362 | 0.0012391 | 0.0002778 | -0.0035248 | -0.021667 | -0.00048703 | 0.06482 | 0.06639 | -0.0090597 | -0.00072207 | 0.0013885 | -0.032043 | 62.5809 | -59.7656 | 62.7777 | -59.5734 | -59.9762 | -0.013733 | -0.018311 | 62.5626 | -59.7473 | 62.796 | -59.7336 | -59.8389 | -59.6741 | -0.050354 | -0.086975 | 0.10986 | 0.14191 | 59.7015 | -0.26093 | 59.7519 | -0.21057 | -0.032043 | -0.10529 | 0.12817 | -0.018311 | 0.041199 | -0.1236 | 0.073242 | -0.091553 | 0.19226 | 122.5433 | 0.013732 | 122.5433 | 122.3465 | 122.3099 | 122.2961 | 122.2778 | -122.4335 | -122.4152 | 122.493 | 122.5113 | 59.6832 | 59.697
287.8125 | 122.6349 | -59.7473 | 62.7686 | -0.025863 | 0.00084388 | 0.059676 | 0.081508 | 0.00081172 | -0.0007904 | -0.00096136 | -0.024719 | 0.0016492 | 0.065033 | 0.063613 | -0.0069235 | 0.00013253 | -0.0030975 | 0.004578 | 62.6724 | -59.7473 | 62.7411 | -59.6512 | -60.022 | 0.041199 | 0.032043 | 62.6587 | -59.7519 | 62.8372 | -59.8984 | -60.1089 | -59.8663 | 0 | -0.096131 | -0.027466 | 0.09613 | 59.7885 | -0.27466 | 59.7885 | -0.27466 | -0.004578 | -0.10986 | 0.068664 | -0.15106 | -0.11902 | -0.36163 | -0.11444 | -0.35706 | 0.09613 | 122.4884 | -0.14648 | 122.5891 | 122.4197 | 122.4106 | 122.4197 | 122.406 | -122.5159 | -122.5204 | 122.4884 | 122.5845 | 59.7519 | 59.7794
288.7656 | 122.7264 | -59.7382 | 62.7228 | -0.12505 | 0.0029801 | 0.062453 | 0.082362 | -0.00089728 | -0.0035674 | -0.0020294 | 0.0027466 | -0.00070063 | 0.063965 | 0.059127 | -0.0090597 | 0.0012005 | 0.00053409 | -0.054932 | 62.6083 | -59.7656 | 62.7411 | -59.6008 | -60.0174 | -0.032043 | -0.050354 | 62.5992 | -59.7794 | 62.7548 | -59.7565 | -59.8709 | -59.7061 | -0.027466 | -0.11444 | 0.018311 | 0.13733 | 59.7061 | -0.27924 | 59.7336 | -0.25177 | -0.041199 | -0.1236 | 0.032044 | -0.018311 | 0.032043 | -0.13275 | 0.073242 | -0.091553 | 0.16479 | 122.5067 | 0.022888 | 122.5342 | 122.374 | 122.3785 | 122.3465 | 122.3373 | -122.4884 | -122.5021 | 122.4792 | 122.493 | 59.6832 | 59.6878
289.7656 | 122.6486 | -59.7244 | 62.7731 | -0.06401 | 0.0021255 | 0.060957 | 0.082576 | 0.0010253 | 0.0013458 | -0.0033112 | -0.055237 | 0.00015377 | 0.062897 | 0.062117 | -0.010128 | 0.0029095 | -0.0030975 | -0.004578 | 62.6953 | -59.7839 | 62.709 | -59.6741 | -60.0082 | 0.036621 | -0.009155 | 62.6678 | -59.7382 | 62.7136 | -59.7839 | -59.8984 | -59.7427 | -0.05951 | -0.07782 | -0.064087 | 0.050354 | 59.761 | -0.28381 | 59.8206 | -0.2243 | -0.013733 | -0.10528 | -0.059509 | -0.05951 | -0.018311 | -0.17395 | -0.004578 | -0.16022 | 0.10986 | 122.493 | -0.045777 | 122.4518 | 122.4792 | 122.406 | 122.4197 | 122.3923 | -122.5571 | -122.5113 | 122.4335 | 122.438 | 59.7198 | 59.7153
290.7656 | 122.7448 | -59.7153 | 62.6907 | -0.11742 | 0.0031937 | 0.06523 | 0.081508 | -0.00089728 | -0.0018586 | -0.00096136 | -0.018616 | 0.00058097 | 0.063751 | 0.064894 | -0.0086325 | 0.00034613 | -0.00053411 | -0.041199 | 62.6038 | -59.7702 | 62.7686 | -59.5688 | -59.9854 | -0.018311 | 0 | 62.5717 | -59.7702 | 62.7777 | -59.7336 | -59.8526 | -59.6786 | -0.054932 | -0.086975 | 0.07782 | 0.14648 | 59.697 | -0.27008 | 59.7519 | -0.21515 | -0.054932 | -0.11902 | 0.086975 | -0.018311 | 0.036621 | -0.13733 | 0.091553 | -0.082397 | 0.20142 | 122.5388 | 0.036621 | 122.5479 | 122.374 | 122.3419 | 122.319 | 122.287 | -122.4609 | -122.4609 | 122.4838 | 122.493 | 59.6741 | 59.7153
291.7812 | 122.6486 | -59.7336 | 62.764 | -0.07164 | 0.00084388 | 0.061598 | 0.081935 | 0.0012391 | -0.0031402 | 0.0024566 | 0.0027466 | -0.00070063 | 0.063538 | 0.058699 | -0.0090597 | 0.00034613 | -0.0024567 | 0.050354 | 62.6907 | -59.7565 | 62.7731 | -59.5779 | -59.9442 | 0.07782 | 0.059509 | 62.6404 | -59.7519 | 62.7182 | -59.761 | -59.8572 | -59.7244 | -0.022888 | -0.073242 | 0.009155 | 0.15564 | 59.8114 | -0.21057 | 59.8343 | -0.18768 | -0.01831 | -0.1236 | -0.045776 | -0.027465 | 0.009156 | -0.1236 | 0.027466 | -0.10529 | 0.17853 | 122.5296 | -0.009155 | 122.4701 | 122.4472 | 122.3923 | 122.4243 | 122.374 | -122.5204 | -122.5159 | 122.5067 | 122.4518 | 59.7839 | 59.7931
292.7656 | 122.7219 | -59.7153 | 62.6816 | -0.07164 | 0.0010575 | 0.064162 | 0.080653 | -0.0043151 | -0.0016448 | -0.00053396 | -0.012512 | -0.00070063 | 0.062683 | 0.06169 | -0.0092733 | 0.0014141 | -0.00053411 | -0.054932 | 62.6129 | -59.7748 | 62.7548 | -59.5963 | -60.0128 | -0.018311 | -0.059509 | 62.6083 | -59.7519 | 62.7686 | -59.7656 | -59.8434 | -59.7061 | -0.059509 | -0.068665 | 0.073242 | 0.11902 | 59.697 | -0.29755 | 59.7565 | -0.23804 | -0.036621 | -0.073243 | 0.086975 | -0.050354 | 0.009155 | -0.12817 | 0.045776 | -0.091553 | 0.17853 | 122.5296 | -0.013733 | 122.5204 | 122.3877 | 122.3602 | 122.3282 | 122.3236 | -122.4564 | -122.4335 | 122.4701 | 122.4838 | 59.6603 | 59.6558
293.7656 | 122.7356 | -59.7336 | 62.7228 | -0.07164 | 0.00063028 | 0.062239 | 0.081294 | -0.0030335 | 6.4004e-05 | -0.0016022 | -0.030823 | -5.9826e-05 | 0.064179 | 0.060408 | -0.0084189 | 0.0024823 | -0.0016021 | -0.059509 | 62.59 | -59.7702 | 62.7411 | -59.6008 | -60.0174 | -0.027466 | -0.068665 | 62.5809 | -59.7565 | 62.7594 | -59.7519 | -59.8572 | -59.7061 | -0.036621 | -0.13275 | 0.018311 | 0.13275 | 59.7061 | -0.28381 | 59.7427 | -0.24719 | -0.022888 | -0.14191 | 0.036621 | -0.01831 | 0.027466 | -0.1236 | 0.050354 | -0.10071 | 0.16937 | 122.5113 | 0.004578 | 122.5159 | 122.3602 | 122.3373 | 122.3236 | 122.3145 | -122.493 | -122.4792 | 122.4747 | 122.493 | 59.6741 | 59.6649
294.7656 | 122.7036 | -59.729 | 62.7136 | -0.11742 | -0.00022432 | 0.063094 | 0.081935 | 0.0014527 | -0.0007904 | -0.0043792 | -0.018616 | -0.00048703 | 0.063965 | 0.05934 | -0.0094869 | 0.00034613 | -0.0030975 | -0.07782 | 62.6038 | -59.7702 | 62.7319 | -59.6146 | -59.9991 | -0.013733 | -0.041199 | 62.5992 | -59.761 | 62.7502 | -59.7519 | -59.8389 | -59.7015 | -0.041199 | -0.10986 | 0.018311 | 0.11444 | 59.7153 | -0.27008 | 59.7565 | -0.22888 | -0.032043 | -0.11444 | 0.036621 | -0.022888 | 0.027466 | -0.10986 | 0.059509 | -0.07782 | 0.15564 | 122.5021 | 0.009155 | 122.5113 | 122.374 | 122.3602 | 122.3328 | 122.3282 | -122.4838 | -122.4747 | 122.4609 | 122.4792 | 59.6512 | 59.6878
295.7656 | 122.7081 | -59.7244 | 62.6999 | -0.07164 | 0.0010575 | 0.064803 | 0.080653 | -0.0019653 | 0.0019866 | -0.00074776 | -0.021667 | -0.00048703 | 0.062897 | 0.068526 | -0.0088461 | 0.0014141 | -0.00032051 | -0.082397 | 62.6083 | -59.7748 | 62.7411 | -59.6237 | -60.0266 | -0.013733 | -0.032043 | 62.59 | -59.7748 | 62.764 | -59.7427 | -59.8663 | -59.6878 | -0.050354 | -0.091553 | 0.041199 | 0.10071 | 59.7107 | -0.30212 | 59.761 | -0.25177 | -0.050354 | -0.10986 | 0.064087 | -0.018311 | 0.036621 | -0.14191 | 0.086975 | -0.091553 | 0.15106 | 122.5159 | 0.032043 | 122.5388 | 122.3831 | 122.3648 | 122.3328 | 122.3145 | -122.4747 | -122.4747 | 122.4655 | 122.4884 | 59.642 | 59.6924
296.7812 | 122.6761 | -59.7244 | 62.7594 | -0.056381 | -0.00043792 | 0.062239 | 0.081508 | -0.0015381 | -0.0029266 | -0.0016022 | -0.10101 | 0.00058097 | 0.064392 | 0.073226 | -0.011196 | 0.0014141 | 0.0020295 | -0.009155 | 62.677 | -59.7702 | 62.7182 | -59.6603 | -60.0082 | 0.022888 | 0.009155 | 62.6724 | -59.761 | 62.7319 | -59.7794 | -59.8984 | -59.7153 | -0.045777 | -0.082397 | -0.041198 | 0.064087 | 59.7473 | -0.28381 | 59.7931 | -0.23804 | -0.036621 | -0.086975 | -0.027465 | -0.054932 | 0.009155 | -0.17395 | 0.045776 | -0.13733 | 0.10986 | 122.4884 | -0.018311 | 122.493 | 122.4472 | 122.4335 | 122.4014 | 122.3969 | -122.5296 | -122.5204 | 122.4426 | 122.4564 | 59.7153 | 59.7336
297.7656 | 122.6944 | -59.7198 | 62.7365 | -0.14793 | 0.0019119 | 0.063948 | 0.079585 | -0.0011109 | -0.001004 | -0.00074776 | -0.018616 | 0.00058097 | 0.063751 | 0.063185 | -0.010128 | 0.00098693 | 0.0016021 | -0.045776 | 62.5992 | -59.761 | 62.7411 | -59.6146 | -59.9899 | -0.027466 | -0.073242 | 62.6129 | -59.761 | 62.7548 | -59.7565 | -59.8389 | -59.7107 | -0.041198 | -0.13733 | 0.004578 | 0.10529 | 59.6924 | -0.27008 | 59.7336 | -0.22888 | -0.041198 | -0.1236 | 0.018311 | -0.036621 | 0.009156 | -0.11902 | 0.050354 | -0.07782 | 0.14648 | 122.5021 | 0.004577 | 122.5159 | 122.3602 | 122.374 | 122.319 | 122.3328 | -122.4976 | -122.4976 | 122.4609 | 122.4747 | 59.6741 | 59.6466
298.7656 | 122.7356 | -59.7336 | 62.6862 | -0.13267 | 0.0010575 | 0.064162 | 0.080653 | -0.0026063 | -0.0003632 | -0.0030976 | -0.0094604 | 0.00036737 | 0.063965 | 0.063613 | -0.010128 | 0.0018413 | 0.00053409 | -0.07782 | 62.6266 | -59.7794 | 62.7502 | -59.6237 | -60.0174 | -0.009155 | -0.041199 | 62.5992 | -59.7382 | 62.7686 | -59.7427 | -59.8572 | -59.697 | -0.045776 | -0.059509 | 0.064087 | 0.10986 | 59.7244 | -0.28381 | 59.7702 | -0.23804 | -0.004577 | -0.086975 | 0.082398 | -0.009155 | 0.036622 | -0.1236 | 0.041199 | -0.11902 | 0.15564 | 122.5296 | -0.004578 | 122.5067 | 122.406 | 122.3373 | 122.3602 | 122.3328 | -122.4655 | -122.4243 | 122.4838 | 122.5021 | 59.6558 | 59.6924
299.7656 | 122.7173 | -59.7382 | 62.6999 | -0.1403 | 0.0027665 | 0.062666 | 0.081508 | -0.00025628 | -0.0016448 | 0.0016022 | -0.00030524 | -0.00048703 | 0.063324 | 0.060408 | -0.010128 | 0.0020551 | -0.0016021 | -0.09613 | 62.6129 | -59.7748 | 62.7274 | -59.5963 | -60.0082 | -0.013733 | -0.041199 | 62.6129 | -59.761 | 62.7548 | -59.7473 | -59.8434 | -59.697 | -0.036621 | -0.086975 | 0.027466 | 0.14191 | 59.7244 | -0.27008 | 59.761 | -0.23346 | -0.022888 | -0.086975 | 0.054932 | -0.009155 | 0.041199 | -0.10529 | 0.064087 | -0.082398 | 0.17853 | 122.5021 | 0.013733 | 122.5159 | 122.3877 | 122.374 | 122.3511 | 122.3511 | -122.4747 | -122.4609 | 122.4655 | 122.493 | 59.642 | 59.697
300.7656 | 122.7448 | -59.7198 | 62.7228 | -0.048752 | 0.0010575 | 0.063307 | 0.083217 | -0.0030335 | -0.0007904 | -0.0018158 | -0.033874 | 0.00015377 | 0.065247 | 0.062545 | -0.0082053 | -8.1274e-05 | -0.0024567 | -0.022888 | 62.6312 | -59.7382 | 62.7777 | -59.5917 | -59.9625 | 0.059509 | 0.050354 | 62.5992 | -59.7382 | 62.8189 | -59.7015 | -59.7885 | -59.6466 | -0.01831 | -0.091552 | 0.054932 | 0.12817 | 59.7794 | -0.24261 | 59.7977 | -0.2243 | -0.01831 | -0.1236 | 0.096131 | 0.018311 | 0.073243 | -0.068664 | 0.091553 | -0.050354 | 0.14648 | 122.5159 | 0.036621 | 122.5571 | 122.3694 | 122.3373 | 122.3511 | 122.319 | -122.4609 | -122.4609 | 122.4976 | 122.5388 | 59.697 | 59.7702
301.7656 | 122.7356 | -59.7244 | 62.709 | -0.086899 | -1.0718e-05 | 0.061385 | 0.08044 | 0.00038452 | -0.0020722 | -0.002884 | -0.021667 | -0.00091423 | 0.064179 | 0.061904 | -0.010128 | 0.00077333 | 0.0016021 | -0.09613 | 62.5992 | -59.7748 | 62.7365 | -59.6008 | -60.0082 | -0.004578 | -0.032043 | 62.5992 | -59.7473 | 62.7548 | -59.7473 | -59.8389 | -59.7061 | -0.050354 | -0.10986 | 0.027466 | 0.1236 | 59.7198 | -0.28381 | 59.7702 | -0.23346 | -0.022888 | -0.10986 | 0.045777 | -0.022888 | 0.01831 | -0.11444 | 0.041198 | -0.091553 | 0.17395 | 122.5113 | 0 | 122.5021 | 122.374 | 122.3465 | 122.3236 | 122.3236 | -122.4838 | -122.4564 | 122.4609 | 122.4792 | 59.6283 | 59.6924
302.7656 | 122.7173 | -59.7336 | 62.7319 | -0.13267 | 0.00084388 | 0.06288 | 0.082362 | 0.0035889 | -0.001004 | -0.0016022 | -0.033874 | -0.00048703 | 0.063751 | 0.052504 | -0.0088461 | 0.0016277 | -0.0020295 | -0.091553 | 62.6038 | -59.7748 | 62.7411 | -59.6237 | -60.0128 | -0.004578 | -0.036621 | 62.5992 | -59.7473 | 62.7731 | -59.7473 | -59.8389 | -59.6924 | -0.041198 | -0.12817 | 0.009155 | 0.10986 | 59.729 | -0.27923 | 59.7702 | -0.23804 | -0.013732 | -0.13275 | 0.041198 | -0.013732 | 0.041199 | -0.10529 | 0.054931 | -0.091553 | 0.15106 | 122.5159 | 0 | 122.5204 | 122.3785 | 122.3465 | 122.3373 | 122.3328 | -122.5067 | -122.4792 | 122.4747 | 122.5067 | 59.642 | 59.697
303.7656 | 122.6669 | -59.7336 | 62.7182 | -0.079269 | 0.00020288 | 0.064803 | 0.084712 | -0.00046988 | -0.0003632 | -0.00096136 | -0.10406 | 0.0014356 | 0.063111 | 0.069594 | -0.010555 | 0.0029095 | 0.00096129 | 0.032043 | 62.6633 | -59.7748 | 62.6541 | -59.4727 | -59.9854 | 0.036621 | 0.045776 | 62.6587 | -59.7656 | 62.7869 | -59.7519 | -59.8846 | -59.7015 | -0.041198 | -0.054932 | -0.064087 | 0.26093 | 59.7702 | -0.25177 | 59.8114 | -0.21057 | -0.032043 | -0.05951 | 0.068664 | -0.01831 | 0.032044 | -0.15106 | 0.064087 | -0.11902 | 0.30212 | 122.4289 | 0.013733 | 122.5525 | 122.438 | 122.4243 | 122.3969 | 122.3923 | -122.493 | -122.4838 | 122.3877 | 122.5204 | 59.7656 | 59.7794
304.7656 | 122.6486 | -59.7336 | 62.7731 | -0.041122 | 0.0019119 | 0.062666 | 0.083003 | -0.00089728 | -0.0018586 | 0.00032044 | -0.09491 | 0.0031446 | 0.063324 | 0.065322 | -0.010342 | 0.0018413 | 0.00032049 | -0.004578 | 62.6724 | -59.8068 | 62.7182 | -59.6375 | -59.9991 | 0.009155 | 0.004578 | 62.6724 | -59.761 | 62.7228 | -59.7702 | -59.8984 | -59.729 | -0.073242 | -0.10071 | -0.054931 | 0.096131 | 59.7427 | -0.2655 | 59.816 | -0.19226 | -0.027465 | -0.10071 | -0.050354 | -0.036621 | 0.004578 | -0.16479 | 0.032043 | -0.13733 | 0.16937 | 122.525 | -0.009156 | 122.4838 | 122.4792 | 122.4335 | 122.406 | 122.406 | -122.58 | -122.5342 | 122.4518 | 122.4564 | 59.729 | 59.7382
305.7656 | 122.7631 | -59.7107 | 62.6999 | -0.06401 | 0.00063028 | 0.064162 | 0.081294 | 0.0018799 | -0.0012176 | -0.0020294 | 0.030212 | -0.0015552 | 0.065247 | 0.06169 | -0.0099143 | 0.0016277 | 0.00074769 | -0.027466 | 62.6221 | -59.761 | 62.764 | -59.5688 | -59.967 | 0.054932 | 0.027466 | 62.6083 | -59.7565 | 62.7869 | -59.6924 | -59.8022 | -59.6649 | -0.050354 | -0.07782 | 0.064087 | 0.14191 | 59.7656 | -0.25635 | 59.816 | -0.20599 | -0.045777 | -0.091553 | 0.086975 | 0.01831 | 0.045776 | -0.091553 | 0.091553 | -0.045776 | 0.19226 | 122.525 | 0.064087 | 122.5433 | 122.3831 | 122.3648 | 122.3328 | 122.319 | -122.4609 | -122.4564 | 122.4747 | 122.4976 | 59.6832 | 59.7382
306.7812 | 122.7448 | -59.729 | 62.7045 | -0.056381 | 0.0025529 | 0.062239 | 0.082149 | -0.0034607 | 0.0015594 | 0.0018158 | -0.064392 | -0.00048703 | 0.063538 | 0.055495 | -0.010342 | 0.0026959 | 0.00074769 | -0.036621 | 62.6129 | -59.7794 | 62.7777 | -59.5642 | -59.9716 | -0.013733 | -0.009155 | 62.5717 | -59.761 | 62.7823 | -59.7519 | -59.848 | -59.6878 | -0.050354 | -0.091553 | 0.073242 | 0.1648 | 59.7153 | -0.24261 | 59.7656 | -0.19226 | -0.032043 | -0.13275 | 0.07782 | -0.022888 | 0.041199 | -0.11902 | 0.073242 | -0.086975 | 0.21515 | 122.5571 | 0.009155 | 122.5433 | 122.3923 | 122.3328 | 122.3419 | 122.3007 | -122.4838 | -122.4655 | 122.5067 | 122.5113 | 59.6924 | 59.7198
307.7656 | 122.7905 | -59.6878 | 62.7136 | -0.06401 | 0.0012711 | 0.063094 | 0.082149 | 0.0016663 | 0.001773 | -0.0020294 | -0.015564 | 0.00079477 | 0.068024 | 0.067458 | -0.0086325 | -0.00029487 | -0.0039521 | 0.027466 | 62.645 | -59.7427 | 62.8006 | -59.523 | -59.9121 | 0.09613 | 0.14648 | 62.59 | -59.7427 | 62.8464 | -59.6329 | -59.7473 | -59.6146 | -0.054932 | -0.068665 | 0.086975 | 0.16479 | 59.7839 | -0.2243 | 59.8389 | -0.16937 | -0.054932 | -0.1236 | 0.13275 | 0.054931 | 0.073242 | -0.059509 | 0.12817 | -0.004577 | 0.21973 | 122.5433 | 0.10986 | 122.5891 | 122.3877 | 122.3328 | 122.3328 | 122.2778 | -122.4564 | -122.4564 | 122.4884 | 122.5342 | 59.7153 | 59.8343
308.7656 | 122.7997 | -59.6924 | 62.6907 | -0.10216 | 0.00020288 | 0.061171 | 0.082149 | 0.00059812 | -0.0020722 | -0.0020294 | -0.0064086 | 0.00079477 | 0.06546 | 0.061263 | -0.0090597 | 0.00098693 | -0.0022431 | 0.013733 | 62.6175 | -59.7656 | 62.8143 | -59.5139 | -59.9258 | 0.09613 | 0.13275 | 62.5854 | -59.7061 | 62.8372 | -59.6512 | -59.7565 | -59.6191 | -0.073242 | -0.073242 | 0.1236 | 0.17853 | 59.7885 | -0.23346 | 59.8618 | -0.16022 | -0.013733 | -0.10529 | 0.14648 | 0.041199 | 0.073242 | -0.064087 | 0.086975 | -0.050354 | 0.25177 | 122.58 | 0.054932 | 122.5433 | 122.3831 | 122.2916 | 122.3099 | 122.2778 | -122.4564 | -122.3969 | 122.5067 | 122.5296 | 59.7061 | 59.8251
309.7656 | 122.7722 | -59.6878 | 62.7548 | -0.048752 | 0.0016983 | 0.064375 | 0.083644 | -0.0036743 | -0.002713 | -0.0016022 | -0.030823 | -0.0015552 | 0.06546 | 0.061904 | -0.01141 | 0.0014141 | 0.00010689 | -0.059509 | 62.6404 | -59.7198 | 62.8098 | -59.5596 | -59.8526 | 0.10071 | 0.13275 | 62.6083 | -59.7565 | 62.8281 | -59.6695 | -59.7748 | -59.6237 | -0.032044 | -0.11444 | 0.054931 | 0.12817 | 59.7885 | -0.1648 | 59.8206 | -0.13275 | -0.068665 | -0.14648 | 0.073242 | 0.01831 | 0.064087 | -0.086975 | 0.13275 | -0.01831 | 0.16022 | 122.5296 | 0.086975 | 122.5845 | 122.3602 | 122.3648 | 122.3282 | 122.2961 | -122.4747 | -122.5113 | 122.4976 | 122.5159 | 59.6283 | 59.8206
310.7656 | 122.7585 | -59.7382 | 62.7274 | -0.086899 | 0.0027665 | 0.061812 | 0.083003 | 0.0010253 | -0.0001496 | 0.001175 | 0.088196 | 0.0010084 | 0.06482 | 0.063826 | -0.0092733 | 0.0024823 | 0.0016021 | -0.068665 | 62.6221 | -59.7748 | 62.7365 | -59.61 | -60.0082 | 0 | -0.11444 | 62.5946 | -59.7656 | 62.7502 | -59.7839 | -59.8434 | -59.7061 | -0.036621 | -0.10529 | 0.009155 | 0.12817 | 59.7382 | -0.27008 | 59.7748 | -0.23346 | -0.027466 | -0.13275 | 0.022888 | -0.045777 | 0.032043 | -0.10529 | 0.059509 | -0.07782 | 0.16479 | 122.5113 | -0.018311 | 122.5159 | 122.3969 | 122.3602 | 122.3602 | 122.3328 | -122.5021 | -122.493 | 122.4747 | 122.4884 | 59.6695 | 59.6237
311.7656 | 122.7585 | -59.7061 | 62.7319 | -0.10216 | -0.00065152 | 0.062666 | 0.081721 | 0.0035889 | -0.0012176 | 0.00010684 | -0.015564 | -0.00091423 | 0.066315 | 0.058699 | -0.0086325 | 0.0044049 | 0.00053409 | -0.041199 | 62.6175 | -59.7931 | 62.7502 | -59.6054 | -59.9762 | 0 | -0.004578 | 62.6221 | -59.7473 | 62.7777 | -59.7336 | -59.8343 | -59.6786 | -0.086975 | -0.11444 | 0.01831 | 0.10071 | 59.7061 | -0.27008 | 59.7931 | -0.18311 | -0.041198 | -0.10986 | 0.045776 | -0.027466 | 0.027466 | -0.12817 | 0.068664 | -0.086976 | 0.18768 | 122.5433 | 0.013732 | 122.525 | 122.4106 | 122.3694 | 122.3236 | 122.3282 | -122.525 | -122.4792 | 122.4564 | 122.4838 | 59.6649 | 59.7015
312.7656 | 122.7448 | -59.697 | 62.7411 | -0.12505 | 0.00041648 | 0.063307 | 0.083644 | -0.00068368 | -0.0033538 | 0.0018158 | -0.0064086 | -0.00027343 | 0.063324 | 0.065535 | -0.0094869 | 0.0022687 | -0.0011749 | 0.004578 | 62.6221 | -59.7519 | 62.7777 | -59.5779 | -59.935 | 0.07782 | 0.082397 | 62.6038 | -59.7519 | 62.8189 | -59.6878 | -59.7839 | -59.6237 | -0.054932 | -0.11902 | 0.036621 | 0.11902 | 59.7748 | -0.23804 | 59.8297 | -0.18311 | -0.054932 | -0.13733 | 0.07782 | 0.009155 | 0.073242 | -0.086976 | 0.12817 | -0.032044 | 0.17395 | 122.5296 | 0.064087 | 122.5708 | 122.374 | 122.3557 | 122.319 | 122.3007 | -122.493 | -122.493 | 122.4747 | 122.5159 | 59.7015 | 59.7794
313.7656 | 122.7676 | -59.697 | 62.6999 | -0.048752 | 0.0021255 | 0.060957 | 0.081721 | -0.00046988 | -0.0012176 | -0.00032036 | -0.018616 | -0.001128 | 0.06546 | 0.059981 | -0.0084189 | 0.00034613 | 0.0018159 | -0.004578 | 62.6175 | -59.7977 | 62.7869 | -59.5551 | -59.9487 | 0.064087 | 0.082397 | 62.5992 | -59.7656 | 62.8098 | -59.6878 | -59.7839 | -59.6329 | -0.10071 | -0.082397 | 0.086975 | 0.14191 | 59.761 | -0.25177 | 59.8618 | -0.15106 | -0.068665 | -0.10071 | 0.10986 | 0.009155 | 0.064086 | -0.086976 | 0.13275 | -0.018311 | 0.24261 | 122.5845 | 0.07782 | 122.5754 | 122.4152 | 122.3648 | 122.3145 | 122.2961 | -122.4976 | -122.4655 | 122.4838 | 122.5067 | 59.6924 | 59.7794
314.7656 | 122.6578 | -59.7061 | 62.7686 | -0.048752 | 0.00084388 | 0.062025 | 0.084071 | 0.0016663 | -0.0014312 | -0.0035248 | -0.049133 | -0.00070063 | 0.063965 | 0.061476 | -0.010555 | 0.0026959 | -0.0011749 | 0.064087 | 62.6541 | -59.7473 | 62.7777 | -59.5596 | -59.9258 | 0.086975 | 0.09613 | 62.6266 | -59.7427 | 62.7548 | -59.761 | -59.8572 | -59.7107 | -0.041198 | -0.11444 | 0.009155 | 0.14648 | 59.7931 | -0.21973 | 59.8343 | -0.17853 | -0.036621 | -0.14191 | -0.013733 | -0.054931 | -0.004577 | -0.15106 | 0.032044 | -0.11444 | 0.18768 | 122.525 | -0.01831 | 122.4976 | 122.4014 | 122.3694 | 122.3602 | 122.3328 | -122.5159 | -122.5113 | 122.4838 | 122.4609 | 59.7702 | 59.8022
315.7656 | 122.6166 | -59.7382 | 62.7457 | -0.056381 | -0.00065152 | 0.063521 | 0.08279 | -0.0015381 | -0.0014312 | -0.0013886 | -0.049133 | -0.00048703 | 0.065033 | 0.058272 | -0.0073507 | 0.0029095 | -0.0026703 | 0.064087 | 62.6678 | -59.7794 | 62.7914 | -59.5551 | -59.9487 | 0.082397 | 0.09613 | 62.6495 | -59.7519 | 62.764 | -59.761 | -59.8618 | -59.7244 | -0.041199 | -0.07782 | 0.045776 | 0.18311 | 59.8206 | -0.21057 | 59.8618 | -0.16937 | -0.013733 | -0.096131 | 0.01831 | -0.022888 | 0.013733 | -0.1236 | 0.027466 | -0.10986 | 0.2243 | 122.5708 | -0.009155 | 122.5159 | 122.4472 | 122.4014 | 122.406 | 122.3877 | -122.525 | -122.4976 | 122.5296 | 122.5021 | 59.8022 | 59.8343
316.7656 | 122.7676 | -59.7061 | 62.6953 | -0.06401 | 0.00041648 | 0.062239 | 0.082149 | 0.0016663 | -0.002713 | 0.00053404 | -0.0064086 | -0.00070063 | 0.064179 | 0.059127 | -0.01141 | 0.0044049 | -0.0016021 | 0.032043 | 62.6312 | -59.7519 | 62.8281 | -59.4864 | -59.8755 | 0.11444 | 0.17395 | 62.59 | -59.7244 | 62.6953 | -59.6008 | -59.8251 | -59.6695 | -0.045776 | -0.064086 | 0.13275 | 0.21973 | 59.8206 | -0.16937 | 59.8663 | -0.1236 | -0.01831 | -0.10529 | 0 | 0.10529 | 0.036621 | -0.11902 | 0.054931 | -0.10071 | 0.2655 | 122.58 | 0.1236 | 122.4197 | 122.3831 | 122.3145 | 122.3373 | 122.2961 | -122.4472 | -122.4197 | 122.5342 | 122.4014 | 59.7382 | 59.8801
317.7656 | 122.7722 | -59.7107 | 62.7182 | -0.06401 | -0.00043792 | 0.062025 | 0.08279 | -0.0030335 | -0.0042084 | -0.0026704 | -0.0064086 | -0.0013416 | 0.064179 | 0.059767 | -0.0088461 | 0.0031231 | -0.0050201 | -0.013733 | 62.6129 | -59.7565 | 62.7823 | -59.5779 | -59.9442 | 0.054932 | 0.068665 | 62.5946 | -59.7519 | 62.8052 | -59.6832 | -59.7885 | -59.6375 | -0.045777 | -0.10529 | 0.064087 | 0.13275 | 59.7656 | -0.23346 | 59.8114 | -0.18768 | -0.041199 | -0.1236 | 0.086975 | 0.027465 | 0.073242 | -0.07782 | 0.11444 | -0.036621 | 0.17853 | 122.5388 | 0.068664 | 122.5571 | 122.3694 | 122.3465 | 122.3236 | 122.3053 | -122.4747 | -122.4701 | 122.493 | 122.5159 | 59.697 | 59.7794
318.7656 | 122.7631 | -59.7061 | 62.7457 | -0.010605 | 0.00063028 | 0.064589 | 0.082149 | 0.00059812 | -0.0033538 | 0.00053404 | -0.00030524 | 0.0027174 | 0.062256 | 0.062117 | -0.010555 | 0.0029095 | 0.0020295 | 0.064087 | 62.6358 | -59.7565 | 62.8372 | -59.5001 | -59.903 | 0.10986 | 0.13733 | 62.6129 | -59.729 | 62.8281 | -59.6741 | -59.7794 | -59.6375 | -0.050354 | -0.10986 | 0.091552 | 0.20599 | 59.816 | -0.19684 | 59.8663 | -0.14648 | -0.022888 | -0.13275 | 0.082397 | 0.032044 | 0.068665 | -0.073242 | 0.091553 | -0.050354 | 0.25635 | 122.5937 | 0.054932 | 122.5571 | 122.3923 | 122.3419 | 122.3419 | 122.319 | -122.5021 | -122.4747 | 122.5433 | 122.5342 | 59.7702 | 59.8434
319.7656 | 122.7539 | -59.7198 | 62.7548 | -0.048752 | 0.0016983 | 0.062453 | 0.083217 | -0.00089728 | -0.0007904 | 0.00032044 | -0.012512 | 0.00015377 | 0.063965 | 0.065322 | -0.0099143 | 0.00077333 | -0.00032051 | -0.022888 | 62.6358 | -59.7702 | 62.764 | -59.5734 | -59.9396 | 0.050354 | 0.059509 | 62.5992 | -59.7427 | 62.8098 | -59.7015 | -59.816 | -59.642 | -0.050354 | -0.11902 | 0.009155 | 0.14649 | 59.7702 | -0.21973 | 59.8206 | -0.16937 | -0.022888 | -0.15564 | 0.054931 | 0.018311 | 0.07782 | -0.09613 | 0.10071 | -0.073242 | 0.19684 | 122.5342 | 0.041199 | 122.5525 | 122.406 | 122.3419 | 122.3557 | 122.319 | -122.525 | -122.4976 | 122.4838 | 122.5296 | 59.697 | 59.7794
320.7656 | 122.7631 | -59.7153 | 62.7182 | -0.06401 | 0.0010575 | 0.061812 | 0.083217 | 0.0044433 | -0.0022858 | -0.00096136 | 0.011902 | -0.00070063 | 0.064606 | 0.055922 | -0.0082053 | 0.0018413 | -0.0013885 | -0.009155 | 62.6312 | -59.7748 | 62.7914 | -59.5642 | -59.9396 | 0.045776 | 0.068665 | 62.6221 | -59.7244 | 62.8189 | -59.6924 | -59.8022 | -59.6466 | -0.059509 | -0.086975 | 0.073242 | 0.15106 | 59.761 | -0.2243 | 59.8206 | -0.16479 | -0.009155 | -0.096131 | 0.10071 | 0.022888 | 0.068665 | -0.086975 | 0.07782 | -0.07782 | 0.21057 | 122.5662 | 0.032043 | 122.5433 | 122.406 | 122.3465 | 122.3465 | 122.3373 | -122.493 | -122.4426 | 122.5067 | 122.5342 | 59.7061 | 59.7839
321.7656 | 122.7264 | -59.7244 | 62.7411 | -0.025863 | 0.0023391 | 0.062025 | 0.083644 | 0.0038025 | 6.4004e-05 | 0.00032044 | -0.033874 | -0.001128 | 0.064392 | 0.058058 | -0.010342 | 0.0020551 | -0.0013885 | 0.073242 | 62.6587 | -59.729 | 62.8464 | -59.5093 | -59.8938 | 0.10071 | 0.12817 | 62.6175 | -59.7153 | 62.8143 | -59.6695 | -59.7794 | -59.6329 | -0.004578 | -0.082398 | 0.10529 | 0.21515 | 59.8251 | -0.16937 | 59.8297 | -0.16479 | 0.009155 | -0.1236 | 0.073242 | 0.054931 | 0.091552 | -0.054932 | 0.082397 | -0.064087 | 0.21973 | 122.5754 | 0.045776 | 122.5296 | 122.3877 | 122.3328 | 122.3831 | 122.3419 | -122.4701 | -122.4564 | 122.5708 | 122.5388 | 59.7977 | 59.8526
322.7656 | 122.7402 | -59.6832 | 62.7502 | -0.10979 | 0.00020288 | 0.061812 | 0.082362 | 0.0014527 | -0.0020722 | -0.00096136 | -0.012512 | -0.00048703 | 0.063751 | 0.065322 | -0.010128 | 0.0024823 | -0.00096131 | 0.050354 | 62.645 | -59.7382 | 62.8418 | -59.5047 | -59.8709 | 0.13275 | 0.13275 | 62.59 | -59.7244 | 62.8235 | -59.6741 | -59.7702 | -59.642 | -0.054931 | -0.10529 | 0.091553 | 0.17853 | 59.816 | -0.18768 | 59.8709 | -0.13275 | -0.041198 | -0.16022 | 0.073242 | 0.009156 | 0.041199 | -0.086975 | 0.082397 | -0.045777 | 0.23346 | 122.58 | 0.050354 | 122.5479 | 122.3831 | 122.3145 | 122.3282 | 122.2733 | -122.4884 | -122.4747 | 122.525 | 122.5067 | 59.7336 | 59.816
323.7656 | 122.7814 | -59.6786 | 62.6999 | -0.056381 | 0.0014847 | 0.062666 | 0.08343 | 0.0010253 | -0.0016448 | -0.002243 | 0.18585 | -0.0017688 | 0.067169 | 0.058913 | -0.010555 | 0.00013253 | -0.0013885 | 0.045776 | 62.6129 | -59.7336 | 62.8326 | -59.4818 | -59.8846 | 0.1236 | 0.004578 | 62.6358 | -59.7198 | 62.8326 | -59.697 | -59.7794 | -59.6512 | -0.054932 | -0.086975 | 0.13275 | 0.19684 | 59.8022 | -0.20599 | 59.8572 | -0.15106 | -0.041199 | -0.064087 | 0.13275 | -0.01831 | 0.027466 | -0.10071 | 0.068665 | -0.059509 | 0.25177 | 122.5662 | 0.022889 | 122.5525 | 122.3465 | 122.3557 | 122.2916 | 122.3145 | -122.4335 | -122.4197 | 122.5113 | 122.5113 | 59.7244 | 59.6832
324.7656 | 122.7814 | -59.6832 | 62.7365 | -0.086899 | 0.0025529 | 0.062025 | 0.084285 | -0.00089728 | -0.0029266 | -0.00074776 | 0.027161 | 0.0025036 | 0.064606 | 0.064253 | -0.0092733 | 0.0014141 | -0.00074771 | 0.050354 | 62.6312 | -59.7748 | 62.8418 | -59.4727 | -59.8526 | 0.37079 | -0.086975 | 62.5946 | -59.761 | 62.8281 | -59.6603 | -59.7931 | -59.642 | -0.091552 | -0.10529 | 0.10529 | 0.21057 | 60.054 | -0.16937 | 60.1456 | -0.07782 | -0.077819 | -0.14191 | 0.091553 | 0.022889 | 0.041199 | -0.10986 | 0.11902 | -0.032044 | 0.30212 | 122.6166 | 0.10071 | 122.5891 | 122.406 | 122.3557 | 122.3145 | 122.2778 | -122.5113 | -122.4976 | 122.525 | 122.5113 | 59.7336 | 59.5963
325.7656 | 122.7631 | -59.7015 | 62.7594 | -0.033493 | 0.0019119 | 0.062239 | 0.08044 | 0.00059812 | -0.0037812 | -0.0030976 | 0.0057984 | 0.0014356 | 0.066101 | 0.062758 | -0.011196 | -0.00050847 | -0.0013885 | 0.050354 | 62.645 | -59.7473 | 62.97 | -59.111 | -59.9533 | -0.073242 | 0.10071 | 62.6083 | -59.7336 | 62.8235 | -59.6512 | -59.7336 | -59.6008 | -0.045776 | -0.11444 | 0.21057 | 0.59051 | 59.6283 | -0.25177 | 59.6741 | -0.20599 | -0.032044 | -0.15106 | 0.064087 | 0.050354 | 0.10071 | -0.032044 | 0.13275 | 0 | 0.63629 | 122.7173 | 0.082398 | 122.5571 | 122.3923 | 122.3419 | 122.3465 | 122.3099 | -122.5067 | -122.493 | 122.6715 | 122.525 | 59.7519 | 59.8022
326.7656 | 122.6303 | -59.7153 | 62.764 | 0.004654 | -0.00065152 | 0.063094 | 0.084285 | 0.0016663 | -0.001004 | 0.00010684 | -0.052185 | 0.0014356 | 0.064179 | 0.060408 | -0.010555 | 0.0020551 | -0.0020295 | 0.032043 | 62.6495 | -59.7656 | 62.764 | -59.5917 | -59.9579 | 0.064087 | 0.045776 | 62.6312 | -59.7427 | 62.7136 | -59.7839 | -59.8801 | -59.729 | -0.050354 | -0.11444 | 0 | 0.1236 | 59.7794 | -0.24262 | 59.8297 | -0.19226 | -0.027466 | -0.13275 | -0.050354 | -0.068665 | -0.013733 | -0.16479 | 0.013733 | -0.13733 | 0.17395 | 122.5296 | -0.041199 | 122.4564 | 122.4152 | 122.374 | 122.3648 | 122.3465 | -122.5296 | -122.5067 | 122.4792 | 122.4289 | 59.7473 | 59.761
327.8125 | 122.7173 | -59.7107 | 62.7411 | -0.033493 | 0.00041648 | 0.062453 | 0.081294 | -0.0011109 | -0.0035674 | -0.00096136 | -0.018616 | 0.00036737 | 0.065247 | 0.062972 | -0.0090597 | 0.0018413 | 0.00053409 | 0.068665 | 62.6404 | -59.7519 | 62.8235 | -59.5276 | -59.903 | 0.10986 | 0.14191 | 62.6266 | -59.7382 | 62.8098 | -59.6878 | -59.7794 | -59.6512 | -0.041199 | -0.10071 | 0.082397 | 0.1831 | 59.8206 | -0.19226 | 59.8618 | -0.15106 | -0.027466 | -0.11444 | 0.068664 | 0.022888 | 0.059509 | -0.068665 | 0.086975 | -0.041199 | 0.2243 | 122.5754 | 0.050354 | 122.5479 | 122.3923 | 122.3648 | 122.3511 | 122.3373 | -122.493 | -122.4792 | 122.5342 | 122.5204 | 59.7794 | 59.8526
328.7656 | 122.6624 | -59.697 | 62.8098 | -0.048752 | 0.00063028 | 0.066298 | 0.081935 | -0.00089728 | -0.0020722 | -0.00096136 | -0.039978 | 0.00079477 | 0.065033 | 0.067244 | -0.0073507 | 0.0022687 | -0.0026703 | 0.045776 | 62.6495 | -59.7748 | 62.7548 | -59.6146 | -59.9899 | 0.045776 | 0.032043 | 62.6358 | -59.7565 | 62.7274 | -59.7748 | -59.6924 | -59.5322 | -0.07782 | -0.16022 | -0.054931 | 0.082397 | 59.7427 | -0.29297 | 59.8206 | -0.21515 | -0.05951 | -0.17395 | -0.082397 | -0.07782 | 0.16479 | 0.004577 | 0.2243 | 0.064087 | 0.16022 | 122.5296 | -0.01831 | 122.4838 | 122.4243 | 122.3923 | 122.3465 | 122.3328 | -122.5845 | -122.5662 | 122.4518 | 122.4243 | 59.7427 | 59.729
329.7656 | 122.6257 | -59.7565 | 62.7869 | -0.056381 | 0.0014847 | 0.061812 | 0.084712 | 0.0031617 | 6.4004e-05 | -0.00010676 | -0.058289 | 0.00058097 | 0.065033 | 0.063613 | -0.0094869 | 0.0022687 | -0.0041657 | 0.050354 | 62.6724 | -59.7748 | 62.7365 | -59.5917 | -59.9487 | 0.054932 | 0.054932 | 62.6587 | -59.7473 | 62.6816 | -59.5413 | -60.0266 | -59.8938 | -0.01831 | -0.11444 | -0.050354 | 0.16479 | 59.8114 | -0.19226 | 59.8297 | -0.17395 | 0.009156 | -0.12817 | -0.10529 | 0.21515 | -0.13733 | -0.27008 | -0.14648 | -0.27924 | 0.1831 | 122.5113 | 0.20599 | 122.4289 | 122.4472 | 122.406 | 122.4289 | 122.4152 | -122.5616 | -122.5342 | 122.493 | 122.4381 | 59.8068 | 59.8114
330.7656 | 122.644 | -59.7244 | 62.7731 | -0.018234 | 0.0029801 | 0.06288 | 0.081721 | 0.0012391 | -0.0020722 | -0.003952 | -0.024719 | 0.00036737 | 0.066315 | 0.063613 | -0.0086325 | 0.00098693 | 0.00010689 | 0.027466 | 62.6862 | -59.7748 | 62.7045 | -59.642 | -60.0037 | 0.036621 | 0.027466 | 62.6541 | -59.7794 | 62.709 | -59.9075 | -59.9533 | -59.7198 | -0.050354 | -0.086975 | -0.068664 | 0.082397 | 59.761 | -0.27924 | 59.8114 | -0.22888 | -0.054932 | -0.11902 | -0.064087 | -0.18311 | 0.004577 | -0.22888 | 0.059509 | -0.17395 | 0.13275 | 122.4792 | -0.12817 | 122.4884 | 122.4609 | 122.4335 | 122.4106 | 122.3785 | -122.5479 | -122.5525 | 122.4289 | 122.4335 | 59.7519 | 59.7519
331.7656 | 122.6624 | -59.7336 | 62.7823 | -0.041122 | 0.0010575 | 0.060744 | 0.084499 | -0.0019653 | -0.0012176 | 0.00074764 | -0.030823 | 0.0016492 | 0.065674 | 0.060622 | -0.0079917 | -0.00072207 | 0.0018159 | 0.009155 | 62.6724 | -59.7565 | 62.7136 | -59.6466 | -60.0037 | 0.036621 | 0.027466 | 62.677 | -59.7336 | 62.7274 | -59.8114 | -59.8801 | -59.7061 | -0.022888 | -0.10986 | -0.068665 | 0.086976 | 59.7702 | -0.27008 | 59.7931 | -0.24719 | 0 | -0.10529 | -0.054932 | -0.077819 | 0.027466 | -0.14648 | 0.027466 | -0.14648 | 0.10986 | 122.4701 | -0.077819 | 122.4609 | 122.4289 | 122.4106 | 122.406 | 122.4106 | -122.5388 | -122.5159 | 122.4472 | 122.4609 | 59.7427 | 59.761
332.7656 | 122.6761 | -59.7015 | 62.7777 | -0.025863 | 0.0014847 | 0.061385 | 0.084071 | -0.00046988 | -0.0022858 | -0.002243 | -0.021667 | 0.0010084 | 0.065033 | 0.06169 | -0.0097007 | 0.0029095 | -0.0030975 | 0.059509 | 62.6358 | -59.7565 | 62.7914 | -59.5367 | -59.9258 | 0.086975 | 0.10071 | 62.6358 | -59.7382 | 62.764 | -59.7198 | -59.8343 | -59.6878 | -0.054932 | -0.14191 | 0.013733 | 0.16479 | 59.7885 | -0.2243 | 59.8434 | -0.16937 | -0.036621 | -0.14191 | -0.013733 | -0.018311 | 0.013733 | -0.13275 | 0.050354 | -0.096131 | 0.21973 | 122.5479 | 0.01831 | 122.5021 | 122.3923 | 122.374 | 122.3373 | 122.3373 | -122.5342 | -122.5159 | 122.493 | 122.4655 | 59.761 | 59.8022
333.7656 | 122.6303 | -59.7198 | 62.7686 | -0.033493 | 0.0027665 | 0.061385 | 0.083003 | -0.00089728 | -0.0024994 | -0.0030976 | -0.0094604 | 0.00036737 | 0.067597 | 0.070449 | -0.0092733 | 0.0024823 | -0.0018157 | -0.013733 | 62.6724 | -59.7565 | 62.7182 | -59.6375 | -59.9991 | 0.17395 | -0.10071 | 62.6724 | -59.7702 | 62.7045 | -59.7885 | -59.9075 | -59.7519 | -0.036621 | -0.096131 | -0.050354 | 0.082398 | 59.8938 | -0.27923 | 59.9304 | -0.24261 | -0.050354 | -0.096131 | -0.064087 | -0.068664 | -0.032043 | -0.18768 | 0.018311 | -0.13733 | 0.11902 | 122.4747 | -0.01831 | 122.4747 | 122.4289 | 122.4426 | 122.3923 | 122.3923 | -122.525 | -122.5388 | 122.4381 | 122.4243 | 59.7061 | 59.6191
334.7656 | 122.6486 | -59.7473 | 62.7823 | -0.033493 | 0.00063028 | 0.061171 | 0.082576 | -0.0017517 | -0.0022858 | -0.0058746 | -0.0064086 | 0.00079477 | 0.06482 | 0.05934 | -0.0075643 | -0.00072207 | -0.00096131 | -0.013733 | 62.6907 | -59.7748 | 62.851 | -59.4864 | -60.2692 | -0.032043 | 0.009155 | 62.6541 | -59.761 | 62.7182 | -59.7794 | -59.8709 | -59.7015 | -0.027466 | -0.091553 | 0.068664 | 0.26093 | 59.7153 | -0.52185 | 59.7427 | -0.49439 | -0.013733 | -0.12817 | -0.064087 | -0.032044 | 0.045776 | -0.1236 | 0.059509 | -0.10986 | 0.28839 | 122.6257 | -0.018311 | 122.4792 | 122.4655 | 122.4152 | 122.438 | 122.4014 | -122.5571 | -122.5433 | 122.5983 | 122.4655 | 59.7336 | 59.7565
335.7656 | 122.6898 | -59.7427 | 62.7777 | -0.010605 | 0.00063028 | 0.063094 | 0.081721 | -0.00068368 | -0.0016448 | -0.0020294 | -0.064392 | 0.00058097 | 0.063324 | 0.05934 | -0.0082053 | 0.0022687 | -0.0028839 | 0.004578 | 62.6862 | -59.7748 | 62.709 | -59.6466 | -60.0128 | 0.022888 | 0.013733 | 62.6724 | -59.7702 | 62.7274 | -59.7748 | -59.8618 | -59.7153 | -0.032043 | -0.091553 | -0.068665 | 0.096131 | 59.7656 | -0.27008 | 59.7977 | -0.23804 | -0.027466 | -0.10529 | -0.050354 | -0.032043 | 0.027466 | -0.11902 | 0.054932 | -0.091552 | 0.12817 | 122.4838 | -0.004577 | 122.4976 | 122.4609 | 122.4426 | 122.4289 | 122.4152 | -122.5525 | -122.5479 | 122.4518 | 122.4701 | 59.7473 | 59.7565
336.7812 | 122.6212 | -59.7519 | 62.7274 | -0.041122 | 0.0019119 | 0.061812 | 0.084285 | 0.00081172 | 6.4004e-05 | -0.0013886 | 0.0027466 | 0.001222 | 0.064392 | 0.064467 | -0.01141 | 0.0031231 | -0.00096131 | -0.086975 | 62.6404 | -59.8343 | 62.6404 | -59.8938 | -60.5392 | -0.13733 | -0.14191 | 62.645 | -59.7794 | 62.6999 | -59.8618 | -59.9579 | -59.7702 | -0.082398 | -0.086975 | -0.086975 | -0.14191 | 59.6146 | -0.78735 | 59.697 | -0.70496 | -0.027466 | -0.082398 | -0.027466 | -0.10986 | -0.018311 | -0.20599 | 0.009155 | -0.17853 | -0.059509 | 122.4747 | -0.082397 | 122.4792 | 122.4747 | 122.4243 | 122.3923 | 122.3969 | -122.5616 | -122.5067 | 122.3923 | 122.4518 | 59.6649 | 59.61
337.7656 | 122.6761 | -59.7382 | 62.764 | -0.025863 | -0.00043792 | 0.063521 | 0.082149 | 0.0033753 | -0.0020722 | -0.0013886 | -0.055237 | 0.00015377 | 0.063965 | 0.064467 | -0.0090597 | 0.0022687 | 0.0020295 | 0.004578 | 62.6724 | -59.7885 | 62.709 | -59.6466 | -60.0128 | 0.013733 | -0.004578 | 62.6541 | -59.7702 | 62.7319 | -59.761 | -59.8755 | -59.7107 | -0.050354 | -0.091553 | -0.054932 | 0.091553 | 59.7519 | -0.27466 | 59.8022 | -0.2243 | -0.032044 | -0.10986 | -0.032043 | -0.022888 | 0.027466 | -0.13733 | 0.05951 | -0.10528 | 0.14191 | 122.4976 | 0.009156 | 122.5021 | 122.4609 | 122.4243 | 122.4106 | 122.3923 | -122.5525 | -122.5342 | 122.4472 | 122.4701 | 59.7427 | 59.7336
338.7656 | 122.6532 | -59.7107 | 62.764 | -0.041122 | 0.0010575 | 0.062239 | 0.08343 | -0.00046988 | -0.0001496 | 0.0013886 | -0.046081 | 0.00036737 | 0.06546 | 0.062972 | -0.010342 | 0.0031231 | -0.00096131 | -0.004578 | 62.6816 | -59.761 | 62.7182 | -59.6512 | -60.0037 | 0.027466 | 0 | 62.6404 | -59.7565 | 62.7319 | -59.7656 | -59.8709 | -59.7015 | -0.050354 | -0.082397 | -0.045776 | 0.059509 | 59.7382 | -0.29297 | 59.7885 | -0.24262 | -0.045777 | -0.1236 | -0.032043 | -0.054932 | 0.009155 | -0.16022 | 0.054932 | -0.11444 | 0.10986 | 122.4792 | -0.009155 | 122.4884 | 122.4426 | 122.3969 | 122.3923 | 122.3511 | -122.525 | -122.5204 | 122.4289 | 122.4426 | 59.7061 | 59.7107
339.7656 | 122.6807 | -59.7153 | 62.7777 | 0.027542 | -1.0718e-05 | 0.061385 | 0.084499 | 0.0018799 | -0.0031402 | -0.00074776 | -0.027771 | 0.0018628 | 0.065247 | 0.060622 | -0.010128 | 0.0035503 | -0.0016021 | 0.004578 | 62.6953 | -59.7565 | 62.7045 | -59.6603 | -60.0082 | 0.027466 | 0.009155 | 62.645 | -59.7565 | 62.7411 | -59.7427 | -59.8892 | -59.7015 | -0.041199 | -0.082398 | -0.073242 | 0.054932 | 59.7427 | -0.29297 | 59.7839 | -0.25177 | -0.041199 | -0.13275 | -0.036621 | -0.027466 | 0.013733 | -0.17395 | 0.054932 | -0.13275 | 0.096131 | 122.4609 | 0.013733 | 122.4976 | 122.4518 | 122.4014 | 122.4106 | 122.3602 | -122.5342 | -122.5342 | 122.4197 | 122.4564 | 59.7198 | 59.7244
340.7656 | 122.7036 | -59.729 | 62.7548 | -0.018234 | -0.00065152 | 0.063307 | 0.084071 | 0.00081172 | 6.4004e-05 | -0.00032036 | -0.067444 | -0.00091423 | 0.064179 | 0.06169 | -0.0071371 | 0.0039777 | 0.00053409 | 0.032043 | 62.6541 | -59.7794 | 62.7319 | -59.6008 | -59.9899 | 0.032043 | 0.041199 | 62.6266 | -59.7565 | 62.6312 | -59.6329 | -59.8526 | -59.6695 | -0.050354 | -0.10071 | -0.022888 | 0.12817 | 59.761 | -0.26092 | 59.8114 | -0.21057 | -0.027466 | -0.12817 | -0.1236 | 0.09613 | 0.059509 | -0.1236 | 0.086975 | -0.09613 | 0.17853 | 122.5113 | 0.1236 | 122.3877 | 122.4335 | 122.3831 | 122.3831 | 122.3557 | -122.5342 | -122.5113 | 122.4609 | 122.3602 | 59.761 | 59.7702
341.7656 | 122.7585 | -59.7107 | 62.7319 | -0.086899 | -1.0718e-05 | 0.062666 | 0.08044 | 0.0012391 | -0.0003632 | -0.0020294 | 0.079041 | -0.0015552 | 0.063965 | 0.052504 | -0.0084189 | 0.0031231 | 0.0011749 | -0.036621 | 62.6175 | -59.7656 | 62.7502 | -59.5825 | -59.9533 | 0.041199 | 0.022888 | 62.5946 | -59.7794 | 62.7914 | -59.6924 | -59.7885 | -59.6375 | -0.054932 | -0.11444 | 0.01831 | 0.12817 | 59.7519 | -0.24262 | 59.8068 | -0.18768 | -0.068665 | -0.13733 | 0.059509 | 0.01831 | 0.073242 | -0.07782 | 0.14191 | -0.009155 | 0.1831 | 122.5159 | 0.086975 | 122.5708 | 122.3831 | 122.374 | 122.3282 | 122.3053 | -122.4976 | -122.5113 | 122.4609 | 122.5021 | 59.6741 | 59.7336
342.7656 | 122.6807 | -59.7427 | 62.7594 | 0.027542 | -1.0718e-05 | 0.06523 | 0.08343 | 0.0012391 | -0.0014312 | -0.0033112 | -0.070496 | 0.00036737 | 0.063965 | 0.062758 | -0.010982 | 0.0046185 | -0.0022431 | 0.036621 | 62.6724 | -59.7977 | 62.7594 | -59.6054 | -59.9762 | 0.041199 | 0.059509 | 62.6404 | -59.7519 | 62.6038 | -59.6054 | -59.8572 | -59.6786 | -0.054931 | -0.086975 | 0 | 0.13733 | 59.7839 | -0.23346 | 59.8389 | -0.17853 | -0.009155 | -0.11902 | -0.15564 | 0.13733 | 0.064087 | -0.11444 | 0.073242 | -0.10529 | 0.19226 | 122.5571 | 0.14648 | 122.3557 | 122.4701 | 122.3923 | 122.4152 | 122.3831 | -122.5571 | -122.5113 | 122.5021 | 122.3465 | 59.7794 | 59.8022
343.7656 | 122.7081 | -59.7244 | 62.7548 | -0.048752 | 0.0021255 | 0.064162 | 0.083217 | 0.0031617 | -0.0029266 | 0.00010684 | -0.052185 | 0.0018628 | 0.066101 | 0.063399 | -0.0088461 | 0.0039777 | 0.0013885 | 0.036621 | 62.6724 | -59.7885 | 62.7365 | -59.61 | -59.9899 | 0.036621 | 0.041199 | 62.6175 | -59.7565 | 62.6541 | -59.8526 | -59.7931 | -59.697 | -0.064087 | -0.082398 | -0.018311 | 0.11444 | 59.761 | -0.2655 | 59.8251 | -0.20142 | -0.032044 | -0.13733 | -0.10071 | -0.12817 | 0.027466 | -0.068665 | 0.05951 | -0.036621 | 0.17853 | 122.525 | -0.09613 | 122.4106 | 122.4609 | 122.374 | 122.3969 | 122.3419 | -122.5433 | -122.5113 | 122.4609 | 122.3785 | 59.761 | 59.7656
344.7656 | 122.7081 | -59.7427 | 62.7319 | -0.10216 | 0.0014847 | 0.064162 | 0.084712 | 0.0029479 | -0.0020722 | -0.0020294 | -0.036926 | -0.00027343 | 0.06546 | 0.062972 | -0.0092733 | 0.0024823 | 0.00053409 | 0.022888 | 62.6587 | -59.7885 | 62.7502 | -59.5871 | -59.9716 | 0.022888 | 0.054932 | 62.6312 | -59.7473 | 62.8143 | -59.9533 | -60.0449 | -59.7382 | -0.045776 | -0.073243 | 0.01831 | 0.15564 | 59.7656 | -0.22888 | 59.8114 | -0.18311 | -0.004577 | -0.10071 | 0.082397 | -0.21057 | 0.004578 | -0.30212 | 0.009155 | -0.29755 | 0.20142 | 122.5388 | -0.20599 | 122.5616 | 122.4472 | 122.3785 | 122.4014 | 122.374 | -122.5204 | -122.4792 | 122.493 | 122.5571 | 59.7656 | 59.7977
345.7656 | 122.6578 | -59.7519 | 62.796 | -0.010605 | -1.0718e-05 | 0.063521 | 0.082149 | -4.2682e-05 | -0.0020722 | 0.00010684 | 0.0057984 | 0.00036737 | 0.065674 | 0.063613 | -0.0082053 | 0.0020551 | -0.0026703 | 0 | 62.6862 | -59.7839 | 62.6953 | -59.6558 | -60.0128 | 0.004578 | 0 | 62.6587 | -59.7702 | 62.7136 | -59.7656 | -59.8709 | -59.7153 | -0.032044 | -0.10986 | -0.10071 | 0.09613 | 59.7565 | -0.26093 | 59.7885 | -0.22888 | -0.018311 | -0.13733 | -0.082398 | -0.013733 | 0.036621 | -0.11902 | 0.054932 | -0.10071 | 0.12817 | 122.4792 | 0.004578 | 122.4838 | 122.4701 | 122.4289 | 122.438 | 122.4106 | -122.58 | -122.5662 | 122.4472 | 122.4655 | 59.7519 | 59.7519
346.7812 | 122.6532 | -59.7473 | 62.7686 | -0.041122 | 0.00041648 | 0.061385 | 0.083217 | 0.0014527 | -0.0003632 | -0.0026704 | 0.042419 | 0.00229 | 0.065247 | 0.057631 | -0.0064963 | 0.0022687 | -0.0022431 | 0.013733 | 62.6862 | -59.7565 | 62.7045 | -59.6237 | -60.0082 | 0.027466 | 0.013733 | 62.6587 | -59.7473 | 62.6724 | -59.5642 | -60.0449 | -59.903 | -0.009156 | -0.082398 | -0.064087 | 0.1236 | 59.7748 | -0.26093 | 59.7839 | -0.25177 | 0 | -0.10986 | -0.096131 | 0.18311 | -0.15564 | -0.29755 | -0.15564 | -0.29755 | 0.13275 | 122.4609 | 0.18311 | 122.4197 | 122.4426 | 122.406 | 122.4335 | 122.406 | -122.525 | -122.5159 | 122.4518 | 122.4197 | 59.761 | 59.761
347.7656 | 122.7722 | -59.7336 | 62.7594 | -0.025863 | 0.00041648 | 0.061812 | 0.083644 | 0.0046569 | -0.0016448 | -0.00053396 | -0.033874 | 0.0016492 | 0.066315 | 0.072585 | -0.011623 | 0.00098693 | -0.00053411 | 0.032043 | 62.6587 | -59.7839 | 62.7365 | -59.5917 | -59.9579 | 0.045776 | 0.054932 | 62.6312 | -59.761 | 62.7365 | -59.761 | -59.8618 | -59.7061 | -0.050354 | -0.10071 | -0.022888 | 0.14191 | 59.7794 | -0.2243 | 59.8297 | -0.17395 | -0.027465 | -0.12817 | -0.022888 | -0.027465 | 0.027466 | -0.12817 | 0.054931 | -0.10071 | 0.19226 | 122.5204 | 0 | 122.4976 | 122.4426 | 122.3923 | 122.3923 | 122.3648 | -122.5433 | -122.5204 | 122.4701 | 122.4701 | 59.7656 | 59.7885
348.7656 | 122.6715 | -59.7427 | 62.7548 | -0.033493 | 0.00063028 | 0.06288 | 0.084285 | 0.0044433 | -0.0033538 | 0.0020294 | -0.033874 | -5.9826e-05 | 0.064606 | 0.063185 | -0.0088461 | 0.0022687 | 0.0041657 | 0.041199 | 62.677 | -59.7839 | 62.7502 | -59.5917 | -59.9899 | -0.004578 | 0.022888 | 62.6175 | -59.7473 | 62.7411 | -59.7702 | -59.8663 | -59.697 | -0.041199 | -0.07782 | -0.004578 | 0.15106 | 59.7382 | -0.24719 | 59.7794 | -0.20599 | -0.004577 | -0.13733 | -0.013733 | -0.027466 | 0.045777 | -0.1236 | 0.050354 | -0.11902 | 0.19226 | 122.5342 | -0.022889 | 122.4884 | 122.4609 | 122.3648 | 122.4197 | 122.3602 | -122.5388 | -122.5021 | 122.493 | 122.4838 | 59.7839 | 59.7656
349.7656 | 122.6532 | -59.7153 | 62.764 | -0.033493 | 0.0010575 | 0.063948 | 0.084285 | 0.0067933 | -0.0007904 | 0.00032044 | -0.058289 | -0.00091423 | 0.062897 | 0.051436 | -0.0099143 | 0.0020551 | 0.00053409 | 0.054932 | 62.6816 | -59.7931 | 62.7274 | -59.5825 | -59.9899 | 0 | 0.027466 | 62.6266 | -59.7473 | 62.7502 | -59.7702 | -59.8846 | -59.697 | -0.07782 | -0.082397 | -0.036621 | 0.13275 | 59.7153 | -0.27466 | 59.7931 | -0.19684 | -0.032043 | -0.13733 | -0.013733 | -0.054932 | 0.018311 | -0.16937 | 0.050354 | -0.13733 | 0.21057 | 122.5204 | -0.022889 | 122.4976 | 122.4747 | 122.374 | 122.3969 | 122.3419 | -122.5571 | -122.5113 | 122.4426 | 122.4655 | 59.7702 | 59.7427
350.7656 | 122.6669 | -59.7473 | 62.7502 | 0.05806 | -0.00043792 | 0.062239 | 0.08578 | 0.0014527 | -0.002713 | 0.00096124 | 0.0057984 | 0.0033582 | 0.066315 | 0.061476 | -0.0079917 | 0.0024823 | 0.0030975 | 0.018311 | 62.6587 | -59.7748 | 62.7274 | -59.6008 | -59.9762 | 0.022888 | 0.022888 | 62.6358 | -59.7931 | 62.7594 | -59.761 | -59.8801 | -59.7107 | -0.027466 | -0.091553 | -0.022888 | 0.14648 | 59.7702 | -0.22888 | 59.7977 | -0.20142 | -0.045777 | -0.11444 | 0.009155 | -0.013733 | 0.036621 | -0.13275 | 0.082398 | -0.086975 | 0.17395 | 122.5021 | 0.032044 | 122.5525 | 122.4335 | 122.4289 | 122.406 | 122.3831 | -122.525 | -122.5433 | 122.4747 | 122.5067 | 59.7656 | 59.7702
351.7812 | 122.6486 | -59.7336 | 62.7686 | -0.086899 | 0.0019119 | 0.063094 | 0.08279 | 0.0010253 | -0.0012176 | 0.00010684 | -0.04303 | 0.00079477 | 0.066529 | 0.060836 | -0.010128 | 0.0031231 | -0.0041657 | -0.032043 | 62.6358 | -59.8114 | 62.6953 | -59.6603 | -60.0357 | -0.050354 | -0.07782 | 62.645 | -59.7656 | 62.6862 | -59.8343 | -59.9579 | -59.7702 | -0.077819 | -0.13275 | -0.073243 | 0.073243 | 59.6832 | -0.30212 | 59.761 | -0.22431 | -0.032043 | -0.1236 | -0.082398 | -0.10071 | -0.036621 | -0.2243 | -0.004578 | -0.19226 | 0.15106 | 122.5067 | -0.068665 | 122.4518 | 122.4472 | 122.4106 | 122.3694 | 122.3785 | -122.58 | -122.5342 | 122.4289 | 122.4197 | 59.7015 | 59.6558
352.7656 | 122.6624 | -59.7427 | 62.7457 | -0.018234 | 0.0016983 | 0.060957 | 0.085353 | 0.0014527 | -0.0014312 | 0.001175 | -0.039978 | 0.002931 | 0.063965 | 0.067031 | -0.0088461 | 0.0035503 | 0.0026703 | -0.018311 | 62.6541 | -59.7748 | 62.7045 | -59.6329 | -60.022 | -0.041199 | -0.036621 | 62.6312 | -59.7748 | 62.709 | -59.816 | -59.9213 | -59.729 | -0.032043 | -0.091553 | -0.041199 | 0.10986 | 59.7015 | -0.27924 | 59.7336 | -0.24719 | -0.032043 | -0.11444 | -0.036622 | -0.073242 | 0.013733 | -0.17853 | 0.045776 | -0.14648 | 0.14191 | 122.4792 | -0.041199 | 122.4838 | 122.4289 | 122.406 | 122.3969 | 122.374 | -122.5204 | -122.5204 | 122.4472 | 122.4518 | 59.7244 | 59.7061
353.7656 | 122.6761 | -59.7977 | 62.7365 | -0.06401 | -0.0015061 | 0.063948 | 0.08343 | 0.0020935 | 0.0002778 | -0.0018158 | -0.027771 | 0.00229 | 0.066529 | 0.062331 | -0.010128 | 0.0022687 | -0.0043793 | -0.064087 | 62.6541 | -59.8251 | 62.6404 | -59.7427 | -60.0677 | -0.10986 | -0.15564 | 62.6129 | -59.7977 | 62.6587 | -59.7839 | -60.4614 | -60.0861 | -0.027466 | -0.082397 | -0.09613 | 0.054931 | 59.6878 | -0.27008 | 59.7153 | -0.24262 | 0 | -0.1236 | -0.07782 | 0.013732 | -0.28839 | -0.66376 | -0.28839 | -0.66376 | 0.082397 | 122.4655 | 0.013732 | 122.4564 | 122.4792 | 122.4106 | 122.4518 | 122.4106 | -122.5616 | -122.5342 | 122.438 | 122.4564 | 59.7336 | 59.642
354.7656 | 122.6898 | -59.7473 | 62.7457 | -0.11742 | -0.0015061 | 0.063521 | 0.083644 | 0.0040161 | 6.4004e-05 | -0.0024566 | -0.039978 | 0.0016492 | 0.06482 | 0.062117 | -0.010128 | 0.00098693 | 0.0033111 | 0.045776 | 62.6495 | -59.8114 | 62.7548 | -59.5917 | -59.9854 | 0.027466 | 0.041199 | 62.6083 | -59.7565 | 62.7457 | -59.7565 | -59.8755 | -59.6924 | -0.064087 | -0.096131 | 0.009155 | 0.15564 | 59.7748 | -0.23804 | 59.8389 | -0.17395 | -0.009156 | -0.13733 | 0 | -0.009156 | 0.054931 | -0.12817 | 0.064087 | -0.11902 | 0.21973 | 122.5662 | 0 | 122.5021 | 122.4609 | 122.3648 | 122.3969 | 122.3557 | -122.5571 | -122.5021 | 122.5021 | 122.493 | 59.7931 | 59.7885
355.7656 | 122.6212 | -59.7427 | 62.7365 | -0.025863 | -1.0718e-05 | 0.062453 | 0.083003 | 0.0020935 | -0.0018586 | -0.0013886 | -0.0094604 | 0.00079477 | 0.065033 | 0.065962 | -0.0094869 | 0.00034613 | 0.0033111 | -0.013733 | 62.645 | -59.7794 | 62.6953 | -59.6466 | -60.0266 | -0.041199 | -0.041199 | 62.6083 | -59.7794 | 62.709 | -59.7977 | -59.9258 | -59.729 | -0.036621 | -0.091553 | -0.041199 | 0.096131 | 59.7015 | -0.28381 | 59.7382 | -0.24719 | -0.036621 | -0.12817 | -0.027466 | -0.054931 | 0.013733 | -0.18311 | 0.050354 | -0.14648 | 0.13275 | 122.4747 | -0.01831 | 122.4884 | 122.4243 | 122.3877 | 122.3877 | 122.3511 | -122.5159 | -122.5159 | 122.438 | 122.4518 | 59.729 | 59.7015
356.7812 | 122.6395 | -59.7473 | 62.7457 | -0.06401 | 0.0014847 | 0.062666 | 0.081935 | -0.0021789 | -0.0022858 | 0.00010684 | -0.027771 | 0.00079477 | 0.065247 | 0.071089 | -0.010342 | 0.0039777 | -0.0013885 | -0.041199 | 62.6633 | -59.7977 | 62.6816 | -59.6466 | -60.0632 | -0.059509 | -0.073242 | 62.6266 | -59.7885 | 62.677 | -59.8114 | -59.935 | -59.7519 | -0.050354 | -0.082398 | -0.064087 | 0.10071 | 59.6878 | -0.31586 | 59.7382 | -0.2655 | -0.041199 | -0.11902 | -0.068665 | -0.064087 | -0.004578 | -0.18768 | 0.036621 | -0.14648 | 0.15106 | 122.4792 | -0.022888 | 122.4655 | 122.4609 | 122.4152 | 122.4106 | 122.374 | -122.5433 | -122.5342 | 122.4289 | 122.4243 | 59.7061 | 59.6741
357.7812 | 122.7493 | -59.7473 | 62.709 | -0.07164 | 0.00084388 | 0.060957 | 0.084712 | 0.0048705 | -0.0024994 | -0.00096136 | -0.0064086 | 0.00036737 | 0.065247 | 0.06404 | -0.0090597 | 0.0024823 | 0.0011749 | -0.086975 | 62.6129 | -59.8114 | 62.6953 | -59.6375 | -60.022 | -0.068665 | -0.086975 | 62.5809 | -59.7656 | 62.7686 | -59.7519 | -59.8526 | -59.6603 | -0.064087 | -0.09613 | -0.013733 | 0.10986 | 59.6786 | -0.27466 | 59.7427 | -0.21057 | -0.018311 | -0.12817 | 0.05951 | -0.004578 | 0.086975 | -0.10529 | 0.10529 | -0.086975 | 0.17395 | 122.5067 | 0.013733 | 122.5342 | 122.4243 | 122.3465 | 122.3602 | 122.3282 | -122.5204 | -122.4747 | 122.4426 | 122.5159 | 59.6603 | 59.6603
358.8281 | 122.644 | -59.7336 | 62.7777 | -0.041122 | 0.0016983 | 0.062666 | 0.08343 | -0.0013245 | 0.0002778 | -0.0016022 | 0.027161 | -5.9826e-05 | 0.063111 | 0.055281 | -0.0099143 | 0.0020551 | 0.0026703 | 0 | 62.6907 | -59.7839 | 62.6816 | -59.6466 | -60.0037 | 0.027466 | -0.004578 | 62.6587 | -59.761 | 62.6953 | -59.7885 | -59.8801 | -59.7244 | -0.050354 | -0.086975 | -0.09613 | 0.086976 | 59.761 | -0.27008 | 59.8114 | -0.21973 | -0.027465 | -0.11902 | -0.082398 | -0.054931 | 0.009156 | -0.14648 | 0.036621 | -0.11902 | 0.13733 | 122.4655 | -0.027466 | 122.4564 | 122.4747 | 122.4197 | 122.4243 | 122.3923 | -122.5616 | -122.5388 | 122.4152 | 122.4289 | 59.7336 | 59.729
359.7656 | 122.6669 | -59.7198 | 62.7502 | -0.06401 | 0.0027665 | 0.063307 | 0.084926 | -0.00068368 | -0.0012176 | 0.00010684 | -0.033874 | 0.00036737 | 0.063965 | 0.061476 | -0.010128 | 0.00013253 | 0.00096129 | 0.059509 | 62.6587 | -59.7977 | 62.7457 | -59.6054 | -59.9945 | 0.009155 | 0.022888 | 62.6358 | -59.7473 | 62.7319 | -59.7702 | -59.8892 | -59.697 | -0.077819 | -0.091553 | -0.004577 | 0.11444 | 59.729 | -0.27466 | 59.8068 | -0.19684 | -0.027465 | -0.11444 | -0.01831 | -0.050354 | 0.022889 | -0.16937 | 0.050354 | -0.14191 | 0.19226 | 122.5433 | -0.022889 | 122.4792 | 122.4564 | 122.3831 | 122.3785 | 122.3557 | -122.5479 | -122.4976 | 122.4655 | 122.4518 | 59.7794 | 59.7427
360.7656 | 122.6761 | -59.7336 | 62.7136 | -0.06401 | -0.0015061 | 0.061812 | 0.083644 | -0.0013245 | -0.0014312 | 0.00010684 | -0.030823 | -5.9826e-05 | 0.065247 | 0.060622 | -0.010342 | 0.0014141 | -0.0013885 | -0.086975 | 62.6495 | -59.8343 | 62.6358 | -59.7107 | -60.0861 | -0.10986 | -0.15106 | 62.6312 | -59.8022 | 62.677 | -59.8343 | -59.9625 | -59.7473 | -0.10071 | -0.064087 | -0.07782 | 0.022889 | 59.6237 | -0.35248 | 59.7244 | -0.25177 | -0.068664 | -0.082397 | -0.036621 | -0.10071 | -0.013732 | -0.22888 | 0.054932 | -0.16022 | 0.1236 | 122.4701 | -0.032044 | 122.4792 | 122.4838 | 122.4335 | 122.3831 | 122.3648 | -122.5479 | -122.5159 | 122.3694 | 122.4106 | 59.6466 | 59.5825
361.7812 | 122.6486 | -59.7244 | 62.7777 | -0.07164 | -1.0718e-05 | 0.062239 | 0.085353 | 0.00059812 | -0.0016448 | -0.0026704 | 0.030212 | 0.00036737 | 0.063965 | 0.062331 | -0.0086325 | 0.00098693 | -0.00096131 | -0.018311 | 62.6724 | -59.7885 | 62.6816 | -59.6512 | -60.0128 | 0.027466 | -0.013733 | 62.6633 | -59.7473 | 62.6953 | -59.7748 | -59.8938 | -59.729 | -0.064087 | -0.10529 | -0.09613 | 0.073242 | 59.7519 | -0.28839 | 59.816 | -0.2243 | -0.022888 | -0.11444 | -0.082398 | -0.050354 | -0.004578 | -0.16937 | 0.01831 | -0.14648 | 0.13733 | 122.4701 | -0.027466 | 122.4426 | 122.4609 | 122.4106 | 122.3969 | 122.3877 | -122.5662 | -122.525 | 122.406 | 122.4197 | 59.7061 | 59.7107
362.7656 | 122.6578 | -59.761 | 62.7411 | -0.07164 | -1.0718e-05 | 0.065657 | 0.084499 | 0.0035889 | -0.0001496 | 0.0016022 | -0.067444 | 0.0020764 | 0.065033 | 0.064467 | -0.0086325 | 0.0018413 | 0.0048065 | -0.013733 | 62.6312 | -59.7748 | 62.6953 | -59.6329 | -60.0174 | -0.054932 | -0.041199 | 62.6083 | -59.7931 | 62.6999 | -59.8022 | -59.9213 | -59.7427 | -0.013733 | -0.10986 | -0.045777 | 0.12817 | 59.7061 | -0.25635 | 59.7198 | -0.24262 | -0.032044 | -0.13275 | -0.041199 | -0.041199 | 0.01831 | -0.16022 | 0.050354 | -0.12817 | 0.14191 | 122.4701 | -0.009155 | 122.493 | 122.406 | 122.4014 | 122.3923 | 122.3694 | -122.5159 | -122.5342 | 122.4564 | 122.4609 | 59.7473 | 59.7198
363.7656 | 122.644 | -59.7977 | 62.7594 | -0.025863 | 0.0010575 | 0.064375 | 0.084926 | 0.0035889 | -0.0012176 | -0.0016022 | -0.04303 | -5.9826e-05 | 0.063538 | 0.059981 | -0.010555 | 0.0018413 | 0.0011749 | -0.068665 | 62.6541 | -59.8068 | 62.6495 | -59.729 | -60.0998 | -0.09613 | -0.16479 | 62.6175 | -59.8114 | 62.645 | -59.8572 | -60.3928 | -60.1318 | -0.009156 | -0.10529 | -0.10986 | 0.068664 | 59.7015 | -0.30212 | 59.7107 | -0.29297 | -0.013733 | -0.14191 | -0.11444 | -0.05951 | -0.33417 | -0.59509 | -0.32044 | -0.58136 | 0.07782 | 122.4564 | -0.045777 | 122.4564 | 122.4609 | 122.4289 | 122.4518 | 122.4152 | -122.5662 | -122.5708 | 122.4472 | 122.4426 | 59.729 | 59.6329
364.7656 | 122.6303 | -59.7519 | 62.7136 | -0.10216 | -0.0019333 | 0.064589 | 0.083644 | -0.0011109 | -0.0042084 | -0.001175 | -0.033874 | 0.00015377 | 0.064392 | 0.059981 | -0.0075643 | 0.00098693 | 0.0013885 | -0.10986 | 62.6678 | -59.7931 | 62.6495 | -59.729 | -60.1273 | -0.10986 | -0.14648 | 62.6175 | -59.7656 | 62.6724 | -59.8572 | -59.9487 | -59.7427 | -0.041199 | -0.045776 | -0.064087 | 0.022888 | 59.642 | -0.37537 | 59.6832 | -0.33417 | -0.013733 | -0.09613 | -0.041199 | -0.10529 | 0.009155 | -0.19684 | 0.022888 | -0.1831 | 0.064087 | 122.4426 | -0.091553 | 122.438 | 122.4609 | 122.3831 | 122.4197 | 122.3694 | -122.5067 | -122.4792 | 122.4014 | 122.4243 | 59.642 | 59.6054
365.7656 | 122.7219 | -59.7153 | 62.7274 | -0.025863 | 0.00084388 | 0.064803 | 0.082576 | -0.0038879 | -0.0001496 | -0.0037384 | 0.057678 | -0.0026232 | 0.063751 | 0.057845 | -0.0090597 | 0.00034613 | -0.0026703 | 0.059509 | 62.6541 | -59.7382 | 62.796 | -59.5139 | -59.8938 | 0.11444 | 0.1236 | 62.6129 | -59.7244 | 62.7869 | -59.6832 | -59.7931 | -59.6237 | -0.022888 | -0.073242 | 0.068665 | 0.20142 | 59.8297 | -0.17853 | 59.8526 | -0.15564 | -0.009155 | -0.11444 | 0.059509 | 0.032043 | 0.091553 | -0.07782 | 0.10071 | -0.068665 | 0.2243 | 122.5342 | 0.041198 | 122.5113 | 122.3923 | 122.3373 | 122.3694 | 122.3282 | -122.4655 | -122.4518 | 122.5113 | 122.5021 | 59.7748 | 59.8389
366.7656 | 122.7768 | -59.7336 | 62.7045 | -0.07164 | 0.00020288 | 0.06523 | 0.083003 | 0.0072205 | 0.0004914 | -0.0024566 | 0.0027466 | 0.00079477 | 0.066529 | 0.066176 | -0.010982 | 0.0022687 | 0.0022431 | -0.059509 | 62.5992 | -59.7977 | 62.7319 | -59.6191 | -60.0082 | -0.041199 | -0.036621 | 62.5717 | -59.7885 | 62.851 | -59.9579 | -59.7153 | -59.4818 | -0.064086 | -0.10529 | 0.027466 | 0.11444 | 59.6924 | -0.27466 | 59.7565 | -0.21057 | -0.054931 | -0.13275 | 0.14648 | -0.2243 | 0.25177 | 0.018311 | 0.3067 | 0.073242 | 0.17853 | 122.5296 | -0.16937 | 122.6395 | 122.3969 | 122.3602 | 122.3328 | 122.3053 | -122.5021 | -122.493 | 122.4655 | 122.5845 | 59.6741 | 59.697
367.7656 | 122.6578 | -59.761 | 62.7365 | -0.10216 | -1.0718e-05 | 0.064162 | 0.085567 | -0.00068368 | -0.0005768 | 0.00074764 | -0.055237 | 0.00015377 | 0.063751 | 0.060622 | -0.0092733 | 0.0018413 | -0.0033111 | -0.032043 | 62.645 | -59.8297 | 62.677 | -59.6924 | -60.0769 | -0.086975 | -0.1236 | 62.6312 | -59.7748 | 62.6541 | -59.8526 | -59.9716 | -59.7839 | -0.068665 | -0.091553 | -0.059509 | 0.068664 | 59.6741 | -0.31586 | 59.7427 | -0.24719 | -0.013733 | -0.10529 | -0.082397 | -0.091553 | -0.022889 | -0.21057 | -0.009156 | -0.19684 | 0.13733 | 122.5067 | -0.07782 | 122.4289 | 122.4747 | 122.406 | 122.406 | 122.3923 | -122.5662 | -122.5113 | 122.438 | 122.4152 | 59.729 | 59.6375
368.7656 | 122.6349 | -59.7702 | 62.7228 | -0.1403 | -0.00065152 | 0.065657 | 0.085353 | 0.0031617 | -0.0020722 | -0.00074776 | -0.046081 | 0.00229 | 0.065247 | 0.06404 | -0.0086325 | 0.0022687 | -0.0022431 | -0.19226 | 62.6083 | -59.8526 | 62.7045 | -59.6878 | -60.1822 | -0.07782 | -0.14191 | 62.6495 | -59.7885 | 62.6862 | -59.8572 | -59.9442 | -59.7565 | -0.082397 | -0.11444 | -0.01831 | 0.082398 | 59.6924 | -0.41199 | 59.7748 | -0.32959 | -0.01831 | -0.073242 | -0.036621 | -0.086975 | 0.013733 | -0.17395 | 0.032043 | -0.15564 | 0.1648 | 122.5571 | -0.068665 | 122.4747 | 122.4609 | 122.438 | 122.3785 | 122.4197 | -122.5754 | -122.5113 | 122.4747 | 122.4564 | 59.5779 | 59.6283
369.7656 | 122.6761 | -59.761 | 62.709 | -0.079269 | -0.00065152 | 0.063521 | 0.084712 | 0.0059387 | -0.0020722 | 0.00010684 | -0.030823 | 0.00036737 | 0.065033 | 0.059127 | -0.0077779 | 0.0018413 | 0.0039521 | -0.10986 | 62.6404 | -59.816 | 62.6678 | -59.7015 | -60.0952 | -0.10071 | -0.13275 | 62.59 | -59.7794 | 62.6953 | -59.8251 | -59.9304 | -59.7336 | -0.054932 | -0.068664 | -0.041198 | 0.059509 | 59.6603 | -0.33417 | 59.7153 | -0.27924 | -0.018311 | -0.11902 | -0.013733 | -0.064087 | 0.027465 | -0.16937 | 0.045776 | -0.15106 | 0.11444 | 122.4838 | -0.045776 | 122.4747 | 122.4564 | 122.3694 | 122.4014 | 122.3511 | -122.525 | -122.4884 | 122.4289 | 122.4564 | 59.6512 | 59.6283
370.7812 | 122.6578 | -59.7565 | 62.6678 | -0.025863 | 0.00041648 | 0.064803 | 0.084712 | -0.00046988 | -0.0007904 | 0.001175 | -0.036926 | -0.00027343 | 0.06546 | 0.065749 | -0.0090597 | 0.0018413 | 0.0018159 | -0.073242 | 62.6678 | -59.8251 | 62.6724 | -59.7061 | -60.0952 | -0.10071 | -0.13733 | 62.6358 | -59.7839 | 62.6495 | -59.8709 | -59.9945 | -59.7794 | -0.068664 | 0 | 0.004577 | 0.050354 | 59.6558 | -0.33875 | 59.7244 | -0.27008 | -0.027466 | -0.032044 | -0.018311 | -0.11444 | -0.022888 | -0.23804 | 0.004578 | -0.21057 | 0.11902 | 122.4976 | -0.086975 | 122.4335 | 122.493 | 122.4197 | 122.4243 | 122.3923 | -122.493 | -122.4518 | 122.4289 | 122.406 | 59.6832 | 59.6191
371.7656 | 122.7127 | -59.7427 | 62.677 | -0.11742 | 0.0023391 | 0.065443 | 0.082362 | 0.0012391 | -0.0005768 | -0.00032036 | 0.027161 | -0.0019824 | 0.064179 | 0.053359 | -0.0094869 | 0.00055973 | -0.00053411 | -0.045776 | 62.6129 | -59.7748 | 62.7548 | -59.5642 | -59.9808 | -0.013733 | -0.009155 | 62.5626 | -59.7427 | 62.7502 | -59.7382 | -59.8434 | -59.6786 | -0.032043 | -0.064087 | 0.07782 | 0.17853 | 59.729 | -0.23804 | 59.761 | -0.20599 | 0 | -0.11444 | 0.073242 | 0.004578 | 0.064087 | -0.10071 | 0.064087 | -0.10071 | 0.21057 | 122.5296 | 0.004578 | 122.493 | 122.3877 | 122.3053 | 122.3557 | 122.3053 | -122.4518 | -122.4197 | 122.4976 | 122.493 | 59.697 | 59.7336
372.7656 | 122.6395 | -59.7427 | 62.7686 | -0.06401 | 0.0021255 | 0.063094 | 0.084926 | 0.0042297 | -0.0012176 | -0.00053396 | -0.073547 | 0.0031446 | 0.064606 | 0.068312 | -0.012051 | 0.0014141 | -0.00074771 | -0.027466 | 62.645 | -59.8068 | 62.6816 | -59.6741 | -60.0861 | -0.073242 | -0.10986 | 62.6358 | -59.7702 | 62.677 | -59.848 | -59.9625 | -59.7656 | -0.064087 | -0.1236 | -0.086975 | 0.068665 | 59.6695 | -0.34332 | 59.7336 | -0.27924 | -0.027466 | -0.13275 | -0.091553 | -0.10529 | -0.022888 | -0.21973 | 0.004578 | -0.19226 | 0.13275 | 122.4884 | -0.077819 | 122.4472 | 122.4518 | 122.406 | 122.3877 | 122.3785 | -122.5754 | -122.5388 | 122.4243 | 122.4197 | 59.7153 | 59.6329
373.7656 | 122.6349 | -59.7565 | 62.7136 | -0.12505 | 0.00041648 | 0.06288 | 0.084071 | 0.0095703 | 0.001773 | -0.002243 | -0.0064086 | -5.9826e-05 | 0.064179 | 0.056349 | -0.010982 | 0.0031231 | 0.0022431 | -0.091553 | 62.6358 | -59.816 | 62.8464 | -59.4681 | -60.1318 | -0.07782 | -0.1831 | 62.6266 | -59.7794 | 62.677 | -59.8618 | -59.9762 | -59.761 | -0.059509 | -0.07782 | 0.13275 | 0.28839 | 59.6786 | -0.37537 | 59.7382 | -0.31586 | -0.022888 | -0.086975 | -0.036621 | -0.10529 | -0.004577 | -0.21973 | 0.018311 | -0.19684 | 0.3479 | 122.6624 | -0.082397 | 122.4564 | 122.4518 | 122.406 | 122.3923 | 122.3831 | -122.5296 | -122.493 | 122.6028 | 122.4335 | 59.6649 | 59.5734
374.7656 | 122.6486 | -59.7656 | 62.7228 | -0.06401 | 0.0034073 | 0.063307 | 0.085139 | 0.0031617 | -0.001004 | -0.00074776 | -0.012512 | 0.0018628 | 0.063965 | 0.062331 | -0.0090597 | 0.0026959 | 0.0016021 | -0.091553 | 62.6358 | -59.8114 | 62.8693 | -59.5184 | -60.141 | -0.073242 | -0.1831 | 62.6312 | -59.8114 | 62.6862 | -59.848 | -59.9716 | -59.7702 | -0.045776 | -0.086975 | 0.14648 | 0.24719 | 59.6924 | -0.37537 | 59.7382 | -0.32959 | -0.045776 | -0.091552 | -0.036621 | -0.082397 | -0.004578 | -0.20599 | 0.041198 | -0.16022 | 0.29297 | 122.6807 | -0.036621 | 122.4976 | 122.4472 | 122.4426 | 122.4014 | 122.3969 | -122.5342 | -122.5342 | 122.6349 | 122.4518 | 59.6741 | 59.5825
375.7656 | 122.7448 | -59.7061 | 62.709 | -0.094528 | 0.0014847 | 0.06288 | 0.083003 | 0.00081172 | -0.0007904 | -0.00074776 | 0.079041 | -0.00048703 | 0.065033 | 0.055709 | -0.0094869 | 0.0018413 | 0.0016021 | 0.032043 | 62.6312 | -59.7427 | 62.8189 | -59.5001 | -59.8938 | 0.11902 | 0.49439 | 62.6358 | -59.6741 | 62.7548 | -59.6237 | -59.697 | -59.6237 | -0.036621 | -0.077819 | 0.10986 | 0.20599 | 59.8251 | -0.18768 | 59.8618 | -0.15106 | 0.032044 | -0.073242 | 0.045777 | 0.082398 | 0.082398 | 0.009156 | 0.050354 | -0.022888 | 0.24262 | 122.5616 | 0.050354 | 122.4289 | 122.374 | 122.3099 | 122.3373 | 122.3419 | -122.4518 | -122.3831 | 122.525 | 122.4609 | 59.7382 | 60.2005
376.7656 | 122.7539 | -59.729 | 62.6862 | -0.14793 | 0.0010575 | 0.060316 | 0.083858 | 0.00081172 | -0.0012176 | -0.00032036 | -0.012512 | 0.00015377 | 0.063538 | 0.058272 | -0.011837 | 0.0020551 | -0.00053411 | -0.07782 | 62.6129 | -59.7794 | 62.7319 | -59.6146 | -60.0037 | -0.050354 | -0.041199 | 62.5671 | -59.7656 | 62.7823 | -59.7336 | -59.8343 | -59.6558 | -0.050354 | -0.073242 | 0.045777 | 0.11444 | 59.6787 | -0.27466 | 59.729 | -0.2243 | -0.036621 | -0.11902 | 0.096131 | -0.004578 | 0.073242 | -0.10529 | 0.10986 | -0.068665 | 0.1648 | 122.5113 | 0.032043 | 122.5479 | 122.3923 | 122.3328 | 122.3419 | 122.2961 | -122.4655 | -122.4518 | 122.4609 | 122.5113 | 59.6512 | 59.6878
377.7656 | 122.7402 | -59.7382 | 62.6541 | -0.10216 | -0.00022432 | 0.064589 | 0.084712 | -0.0013245 | 0.0013458 | -0.00096136 | -0.036926 | 0.00058097 | 0.064392 | 0.068526 | -0.011623 | 0.0024823 | -0.0016021 | -0.068665 | 62.5992 | -59.8068 | 62.7365 | -59.5917 | -60.0082 | -0.073242 | -0.032043 | 62.5626 | -59.7702 | 62.7686 | -59.7336 | -59.8389 | -59.6558 | -0.068665 | -0.054932 | 0.082397 | 0.14648 | 59.6649 | -0.27008 | 59.7336 | -0.20142 | -0.032044 | -0.091553 | 0.11444 | 0.004577 | 0.082397 | -0.10071 | 0.11444 | -0.068664 | 0.21515 | 122.5433 | 0.036621 | 122.5388 | 122.406 | 122.3328 | 122.3373 | 122.3007 | -122.4609 | -122.4243 | 122.4747 | 122.5067 | 59.6695 | 59.7061
378.7656 | 122.7539 | -59.7198 | 62.6862 | -0.10979 | 0.0014847 | 0.062453 | 0.084285 | 0.0067933 | -0.001004 | -0.0035248 | -0.0064086 | -0.00027343 | 0.064392 | 0.061049 | -0.010769 | 0.0033367 | -0.00053411 | -0.041199 | 62.5946 | -59.761 | 62.7502 | -59.5734 | -59.9762 | -0.022888 | -0.013733 | 62.5488 | -59.7427 | 62.7914 | -59.7244 | -59.8206 | -59.6741 | -0.041198 | -0.091553 | 0.064087 | 0.14649 | 59.697 | -0.25635 | 59.7382 | -0.21515 | -0.022888 | -0.13733 | 0.10529 | -0.004577 | 0.045777 | -0.10071 | 0.068665 | -0.07782 | 0.18768 | 122.5113 | 0.018311 | 122.5342 | 122.3557 | 122.2916 | 122.3145 | 122.2687 | -122.4472 | -122.4289 | 122.4701 | 122.5113 | 59.6787 | 59.7061
379.7656 | 122.6624 | -59.7702 | 62.6999 | 0.18776 | -0.0010787 | 0.063734 | 0.08578 | -0.0019653 | -0.0033538 | -0.0013886 | -0.070496 | 0.0014356 | 0.063538 | 0.068099 | -0.010128 | 0.0033367 | -0.0018157 | -0.050354 | 62.6678 | -59.816 | 62.6724 | -59.7107 | -60.0998 | -0.11902 | -0.16022 | 62.6083 | -59.8022 | 62.6816 | -59.8526 | -59.9762 | -59.7565 | -0.045776 | -0.032043 | -0.027466 | 0.05951 | 59.6512 | -0.32959 | 59.697 | -0.28381 | -0.032043 | -0.091553 | -0.01831 | -0.082397 | 0.013733 | -0.20599 | 0.045776 | -0.17395 | 0.10529 | 122.4884 | -0.050354 | 122.4838 | 122.4838 | 122.4106 | 122.4381 | 122.3785 | -122.5159 | -122.5021 | 122.4426 | 122.4518 | 59.7198 | 59.61
380.7656 | 122.7219 | -59.7107 | 62.7045 | -0.086899 | 0.0027665 | 0.062666 | 0.085353 | -0.0043151 | 6.4004e-05 | -0.0020294 | 0.057678 | 0.0016492 | 0.065247 | 0.060195 | -0.011837 | 0.0014141 | -0.0039521 | -0.045776 | 62.645 | -59.7702 | 62.7136 | -59.6008 | -59.9579 | 0.013733 | -0.013733 | 62.5671 | -59.7565 | 62.7502 | -59.7107 | -59.816 | -59.6695 | -0.05951 | -0.05951 | 0.009155 | 0.10986 | 59.7244 | -0.24719 | 59.7839 | -0.18768 | -0.045777 | -0.13733 | 0.045776 | 0 | 0.041198 | -0.10529 | 0.086975 | -0.059509 | 0.16937 | 122.4838 | 0.045777 | 122.5067 | 122.4152 | 122.3236 | 122.3557 | 122.2778 | -122.4747 | -122.4609 | 122.4243 | 122.4609 | 59.6649 | 59.697
381.7656 | 122.7859 | -59.697 | 62.709 | -0.048752 | 0.0019119 | 0.062666 | 0.084071 | -0.0021789 | -0.0022858 | -0.00053396 | 0.06073 | -0.00070063 | 0.064606 | 0.063826 | -0.012051 | 0.0014141 | -0.0030975 | 0.004578 | 62.6266 | -59.7427 | 62.7731 | -59.5413 | -59.9258 | 0.09613 | 0.10529 | 62.6083 | -59.7427 | 62.8143 | -59.6558 | -59.7656 | -59.6237 | -0.045777 | -0.082397 | 0.064087 | 0.15564 | 59.7931 | -0.22888 | 59.8389 | -0.18311 | -0.045777 | -0.10071 | 0.10529 | 0.041198 | 0.073242 | -0.068665 | 0.11902 | -0.022888 | 0.20142 | 122.5159 | 0.086975 | 122.5571 | 122.3694 | 122.3511 | 122.3236 | 122.3053 | -122.4518 | -122.4518 | 122.4701 | 122.5113 | 59.7015 | 59.8022
382.7656 | 122.6944 | -59.7427 | 62.6816 | -0.07164 | -0.00043792 | 0.062666 | 0.08578 | 0.00081172 | 0.0013458 | 0.0016022 | -0.06134 | -0.00070063 | 0.065674 | 0.065108 | -0.01141 | 0.0039777 | 0.00032049 | -0.09613 | 62.6358 | -59.8068 | 62.6816 | -59.6558 | -60.0632 | -0.10071 | -0.10071 | 62.6083 | -59.7885 | 62.7365 | -59.7702 | -59.8801 | -59.7061 | -0.064087 | -0.045777 | 0 | 0.086975 | 59.642 | -0.32043 | 59.7061 | -0.25635 | -0.045776 | -0.073243 | 0.054931 | -0.027466 | 0.036621 | -0.13733 | 0.082397 | -0.091553 | 0.15106 | 122.4884 | 0.01831 | 122.525 | 122.4426 | 122.3969 | 122.3785 | 122.3511 | -122.4884 | -122.4701 | 122.4243 | 122.4792 | 59.6466 | 59.642
383.7656 | 122.7356 | -59.7382 | 62.6633 | -0.048752 | 0.0027665 | 0.064803 | 0.086635 | 0.00081172 | 0.0004914 | 0.00032044 | -0.04303 | -0.0024096 | 0.065033 | 0.062331 | -0.0086325 | 0.0020551 | -0.00096131 | -0.10071 | 62.6358 | -59.8251 | 62.6816 | -59.6603 | -60.054 | -0.082397 | -0.10986 | 62.59 | -59.8114 | 62.7548 | -59.761 | -59.8755 | -59.6741 | -0.086975 | -0.027466 | 0.018311 | 0.07782 | 59.6558 | -0.31586 | 59.7427 | -0.22888 | -0.073242 | -0.073242 | 0.091553 | -0.022888 | 0.064087 | -0.13733 | 0.13733 | -0.064087 | 0.16479 | 122.5067 | 0.050354 | 122.5662 | 122.4609 | 122.4014 | 122.374 | 122.3282 | -122.4884 | -122.4747 | 122.4197 | 122.493 | 59.6375 | 59.6283
384.7656 | 122.7631 | -59.7153 | 62.6724 | -0.15556 | 0.0016983 | 0.064162 | 0.085994 | 0.0035889 | -0.0014312 | 0.002243 | -0.09491 | -0.0017688 | 0.063111 | 0.055068 | -0.0094869 | 0.0022687 | 0.00053409 | -0.027466 | 62.59 | -59.7885 | 62.5946 | -59.5001 | -59.6603 | 0.059509 | 0 | 62.5763 | -59.761 | 62.7823 | -59.6878 | -59.848 | -59.6558 | -0.073242 | -0.082397 | -0.07782 | 0.21515 | 59.7748 | 0.054932 | 59.848 | 0.12817 | -0.045776 | -0.09613 | 0.10986 | 0.027466 | 0.059509 | -0.13275 | 0.10528 | -0.086975 | 0.28839 | 122.3831 | 0.073242 | 122.5433 | 122.3785 | 122.3373 | 122.3053 | 122.2916 | -122.4609 | -122.4335 | 122.3099 | 122.4976 | 59.6878 | 59.7153
385.7656 | 122.644 | -59.7244 | 62.764 | -0.025863 | 0.00041648 | 0.062453 | 0.084071 | -0.0013245 | -0.001004 | 0.0013886 | -0.046081 | 0.0014356 | 0.065033 | 0.056777 | -0.010342 | 0.00055973 | -0.0022431 | -0.004578 | 62.6999 | -59.7931 | 62.6862 | -59.6603 | -60.0037 | 0.041199 | -0.013733 | 62.6633 | -59.761 | 62.7045 | -59.7839 | -59.8846 | -59.7153 | -0.068665 | -0.064087 | -0.07782 | 0.064087 | 59.7656 | -0.27924 | 59.8343 | -0.21057 | -0.036621 | -0.10071 | -0.059509 | -0.05951 | 0.009155 | -0.16022 | 0.045776 | -0.1236 | 0.13275 | 122.4792 | -0.022889 | 122.4655 | 122.493 | 122.4243 | 122.4243 | 122.3877 | -122.5571 | -122.525 | 122.4106 | 122.4289 | 59.7198 | 59.7107
386.7656 | 122.6532 | -59.7107 | 62.7502 | -0.07164 | 0.0010575 | 0.060744 | 0.084285 | 0.0014527 | -0.0033538 | -0.00096136 | 0.014954 | 0.00015377 | 0.065674 | 0.055281 | -0.0088461 | 0.0018413 | -0.00010671 | 0.054932 | 62.645 | -59.761 | 62.7731 | -59.5413 | -59.935 | 0.07782 | 0.07782 | 62.6312 | -59.7336 | 62.7457 | -59.7198 | -59.8343 | -59.6924 | -0.050354 | -0.10529 | 0.022888 | 0.16937 | 59.7885 | -0.22431 | 59.8389 | -0.17395 | -0.022889 | -0.11902 | -0.004577 | -0.009156 | 0.01831 | -0.1236 | 0.041199 | -0.10071 | 0.21973 | 122.5342 | 0.013733 | 122.4792 | 122.406 | 122.3648 | 122.3557 | 122.3419 | -122.5113 | -122.4838 | 122.4838 | 122.4564 | 59.7656 | 59.7885
387.7656 | 122.7493 | -59.729 | 62.6862 | -0.094528 | 0.0016983 | 0.062666 | 0.087917 | 0.00038452 | 0.0013458 | -0.00074776 | -0.064392 | 0.00036737 | 0.064606 | 0.063399 | -0.011196 | 0.0018413 | -0.0011749 | -0.068665 | 62.6221 | -59.8068 | 62.7274 | -59.6237 | -60.0128 | -0.054932 | -0.064087 | 62.5854 | -59.7656 | 62.7731 | -59.7198 | -59.8572 | -59.642 | -0.07782 | -0.064087 | 0.041199 | 0.10529 | 59.6741 | -0.28381 | 59.7519 | -0.20599 | -0.036621 | -0.10071 | 0.086975 | 0.009155 | 0.086975 | -0.12817 | 0.1236 | -0.091553 | 0.18311 | 122.5342 | 0.045776 | 122.5388 | 122.4289 | 122.3511 | 122.3511 | 122.3145 | -122.493 | -122.4518 | 122.4564 | 122.5021 | 59.6603 | 59.6649
388.7656 | 122.7356 | -59.729 | 62.6999 | -0.079269 | 0.00084388 | 0.062239 | 0.084926 | -0.00046988 | 0.0015594 | 0.00032044 | -0.0094604 | 0.00015377 | 0.063751 | 0.054213 | -0.0090597 | 0.0018413 | -0.0028839 | -0.032043 | 62.5946 | -59.7702 | 62.7548 | -59.5688 | -59.9899 | -0.022888 | -0.018311 | 62.5717 | -59.7839 | 62.7686 | -59.7336 | -59.848 | -59.6695 | -0.041199 | -0.10529 | 0.054932 | 0.16022 | 59.7061 | -0.26092 | 59.7473 | -0.21973 | -0.054932 | -0.12817 | 0.068665 | -0.004578 | 0.059509 | -0.11902 | 0.11444 | -0.064086 | 0.20142 | 122.525 | 0.050354 | 122.5525 | 122.3648 | 122.3557 | 122.3236 | 122.3007 | -122.4701 | -122.4838 | 122.4838 | 122.4976 | 59.697 | 59.7107
389.7656 | 122.7127 | -59.729 | 62.7136 | -0.10979 | 0.0012711 | 0.062666 | 0.086208 | -0.0019653 | -0.0020722 | -0.0030976 | 0.018005 | -0.001128 | 0.065888 | 0.061049 | -0.0090597 | -0.00029487 | 0.00010689 | -0.068665 | 62.6221 | -59.761 | 62.7319 | -59.6283 | -60.0037 | -0.018311 | 0.20599 | 62.6175 | -59.7565 | 62.7319 | -59.7519 | -59.8572 | -59.7153 | -0.032043 | -0.091553 | 0.018311 | 0.10071 | 59.7107 | -0.27466 | 59.7427 | -0.24262 | -0.027466 | -0.09613 | 0.018311 | -0.022888 | 0.013733 | -0.12817 | 0.041199 | -0.10071 | 0.13275 | 122.493 | 0.004578 | 122.4884 | 122.3831 | 122.374 | 122.3511 | 122.3465 | -122.4747 | -122.4701 | 122.4609 | 122.4609 | 59.6603 | 59.935
390.7656 | 122.7722 | -59.7198 | 62.6816 | -0.13267 | 0.0019119 | 0.063948 | 0.084285 | 0.0012391 | -0.0005768 | -0.0018158 | -0.049133 | 0.00058097 | 0.064606 | 0.063399 | -0.01141 | 0.0031231 | -0.0041657 | -0.036621 | 62.6129 | -59.7839 | 62.7686 | -59.5688 | -59.967 | -0.022888 | 0 | 62.5626 | -59.761 | 62.8006 | -59.7153 | -59.816 | -59.642 | -0.064087 | -0.068665 | 0.086975 | 0.15106 | 59.697 | -0.24719 | 59.761 | -0.18311 | -0.041198 | -0.11902 | 0.11902 | 0.004578 | 0.07782 | -0.09613 | 0.11902 | -0.054932 | 0.21515 | 122.5525 | 0.045776 | 122.5616 | 122.3969 | 122.3236 | 122.3328 | 122.2824 | -122.4655 | -122.4426 | 122.4884 | 122.5204 | 59.6832 | 59.7198
391.7656 | 122.731 | -59.6786 | 62.7274 | -0.048752 | 0.00063028 | 0.063094 | 0.087276 | -0.00089728 | -0.0033538 | -0.001175 | -0.0064086 | -0.00070063 | 0.063324 | 0.060836 | -0.012264 | 0.00077333 | 0.0011749 | -0.013733 | 62.645 | -59.697 | 62.8555 | -59.5917 | -59.903 | 0.13275 | 0.13275 | 62.6038 | -59.729 | 62.8052 | -59.6558 | -59.7565 | -59.6054 | -0.01831 | -0.082398 | 0.12817 | 0.086975 | 59.8114 | -0.2243 | 59.8297 | -0.20599 | -0.050354 | -0.1236 | 0.07782 | 0.022888 | 0.073242 | -0.07782 | 0.1236 | -0.027466 | 0.10528 | 122.5525 | 0.073242 | 122.5342 | 122.3419 | 122.3328 | 122.3236 | 122.2824 | -122.4243 | -122.4564 | 122.5342 | 122.4838 | 59.6649 | 59.8114
392.7656 | 122.6944 | -59.7107 | 62.7136 | -0.056381 | -0.00022432 | 0.061812 | 0.081935 | -0.00089728 | -0.0020722 | -0.001175 | -0.027771 | -0.00070063 | 0.061615 | 0.060408 | -0.0077779 | -8.1274e-05 | -0.0016021 | -0.036621 | 62.5946 | -59.7794 | 62.7502 | -59.5871 | -60.0037 | -0.013733 | -0.041199 | 62.5763 | -59.7794 | 62.7457 | -59.761 | -59.8526 | -59.6878 | -0.068665 | -0.11902 | 0.036621 | 0.1236 | 59.697 | -0.29297 | 59.7656 | -0.2243 | -0.068665 | -0.13733 | 0.032044 | -0.050354 | 0.022888 | -0.14191 | 0.091553 | -0.073242 | 0.19226 | 122.5296 | 0.018311 | 122.525 | 122.374 | 122.3557 | 122.3053 | 122.287 | -122.493 | -122.493 | 122.4609 | 122.4564 | 59.6741 | 59.6695
393.7656 | 122.7127 | -59.7565 | 62.6953 | -0.12505 | -0.00043792 | 0.063521 | 0.087276 | -0.00046988 | -0.0033538 | -0.001175 | -0.018616 | -0.0019824 | 0.064179 | 0.061049 | -0.011196 | 0.00034613 | 0.00074769 | -0.032043 | 62.6221 | -59.7931 | 62.7319 | -59.6054 | -59.9945 | -0.027466 | -0.045776 | 62.5626 | -59.7565 | 62.7457 | -59.7565 | -59.848 | -59.6878 | -0.036621 | -0.073242 | 0.036622 | 0.15106 | 59.729 | -0.23804 | 59.7656 | -0.20142 | 0 | -0.13275 | 0.050355 | 0 | 0.068665 | -0.091552 | 0.068665 | -0.091552 | 0.18768 | 122.525 | 0 | 122.5021 | 122.4152 | 122.319 | 122.3785 | 122.319 | -122.4884 | -122.4518 | 122.4884 | 122.5021 | 59.7244 | 59.7107
394.7656 | 122.6852 | -59.7382 | 62.7274 | -0.086899 | 0.00041648 | 0.062666 | 0.084285 | -0.0021789 | -0.0001496 | -0.00053396 | -0.015564 | 0.00058097 | 0.06546 | 0.056777 | -0.0094869 | 0.0018413 | -0.0024567 | -0.050354 | 62.6312 | -59.7702 | 62.7411 | -59.6466 | -60.0174 | -0.022888 | -0.050354 | 62.59 | -59.7702 | 62.764 | -59.761 | -59.8389 | -59.6924 | -0.032044 | -0.09613 | 0.013733 | 0.091553 | 59.7153 | -0.27924 | 59.7473 | -0.24719 | -0.032044 | -0.13733 | 0.036621 | -0.022888 | 0.045776 | -0.10071 | 0.07782 | -0.068664 | 0.1236 | 122.5113 | 0.009156 | 122.5342 | 122.4014 | 122.3602 | 122.3694 | 122.3282 | -122.4976 | -122.4976 | 122.4792 | 122.5021 | 59.6878 | 59.6878
395.7656 | 122.6944 | -59.7061 | 62.7182 | -0.1403 | -0.00086512 | 0.061598 | 0.083858 | -0.0017517 | -0.0022858 | 0.0020294 | -0.018616 | 0.00079477 | 0.062042 | 0.061904 | -0.01141 | 0.0035503 | 0.0039521 | 0.13275 | 62.6678 | -59.729 | 62.7045 | -59.6146 | -60.0082 | -0.032043 | -0.054932 | 62.5992 | -59.761 | 62.7502 | -59.7519 | -59.8434 | -59.6741 | -0.022888 | -0.050354 | -0.013733 | 0.091553 | 59.6741 | -0.30212 | 59.697 | -0.27924 | -0.054931 | -0.11902 | 0.032043 | -0.045776 | 0.032044 | -0.13733 | 0.086975 | -0.082398 | 0.11444 | 122.4335 | 0.009155 | 122.5113 | 122.3969 | 122.3602 | 122.374 | 122.3053 | -122.4472 | -122.4792 | 122.4106 | 122.4564 | 59.8389 | 59.6512
396.7656 | 122.7768 | -59.7153 | 62.7136 | -0.07164 | 0.00041648 | 0.063734 | 0.083644 | -0.0045289 | -0.0007904 | 0.00053404 | -0.027771 | -0.002196 | 0.063751 | 0.060408 | -0.010128 | 0.0018413 | -0.0037383 | -0.032043 | 62.6312 | -59.7656 | 62.7548 | -59.5871 | -59.9533 | 0.045776 | 0.027466 | 62.6129 | -59.7519 | 62.7823 | -59.697 | -59.7931 | -59.6466 | -0.050354 | -0.082397 | 0.041199 | 0.12817 | 59.761 | -0.23804 | 59.8114 | -0.18768 | -0.036621 | -0.10071 | 0.068665 | 0.018311 | 0.068665 | -0.07782 | 0.10529 | -0.041199 | 0.17853 | 122.5204 | 0.054932 | 122.5342 | 122.3969 | 122.3648 | 122.3465 | 122.3282 | -122.4792 | -122.4655 | 122.4701 | 122.4976 | 59.6832 | 59.7427
397.7656 | 122.7219 | -59.7244 | 62.709 | 0.12672 | 0.0016983 | 0.065016 | 0.085567 | 0.00081172 | 6.4004e-05 | -0.0020294 | -0.024719 | -0.00027343 | 0.063538 | 0.062545 | -0.0099143 | -0.00029487 | -0.0035247 | -0.17395 | 62.6221 | -59.8068 | 62.7319 | -59.6466 | -59.9899 | -0.013733 | -0.036621 | 62.6083 | -59.7656 | 62.7502 | -59.7473 | -59.8434 | -59.6741 | -0.082398 | -0.086975 | 0.022889 | 0.07782 | 59.7107 | -0.2655 | 59.7931 | -0.1831 | -0.041199 | -0.10071 | 0.041199 | -0.022888 | 0.050354 | -0.11902 | 0.091553 | -0.07782 | 0.16022 | 122.5388 | 0.018311 | 122.5159 | 122.4289 | 122.374 | 122.3465 | 122.3328 | -122.5159 | -122.4747 | 122.4564 | 122.4747 | 59.5505 | 59.6878
398.7656 | 122.7905 | -59.6786 | 62.7274 | -0.048752 | 0.00041648 | 0.063307 | 0.084712 | -0.00068368 | -0.0018586 | -0.0013886 | 0.0088502 | -0.00091423 | 0.063538 | 0.057631 | -0.010128 | 0.0014141 | -0.0022431 | 0.036621 | 62.6221 | -59.761 | 62.8143 | -59.4955 | -59.9075 | 0.10529 | 0.14191 | 62.6129 | -59.7107 | 62.8372 | -59.761 | -59.2941 | -59.285 | -0.082397 | -0.10529 | 0.086975 | 0.18311 | 59.7839 | -0.22888 | 59.8663 | -0.14649 | -0.032043 | -0.11444 | 0.10986 | -0.082397 | 0.39368 | 0.38452 | 0.42572 | 0.41656 | 0.2655 | 122.5754 | -0.050354 | 122.5479 | 122.3831 | 122.3236 | 122.3007 | 122.2916 | -122.4884 | -122.438 | 122.493 | 122.5159 | 59.7153 | 59.8206
399.7656 | 122.7219 | -59.7153 | 62.7045 | -0.025863 | 0.00063028 | 0.061812 | 0.084071 | 0.00038452 | -0.0029266 | 0.0016022 | -0.018616 | -0.001128 | 0.061188 | 0.059981 | -0.010555 | -0.0011493 | -0.0013885 | -0.12817 | 62.6129 | -59.761 | 62.7182 | -59.6237 | -59.9899 | -0.013733 | -0.027466 | 62.5763 | -59.761 | 62.764 | -59.7519 | -59.8343 | -59.6649 | -0.045776 | -0.091553 | 0.013733 | 0.091553 | 59.7015 | -0.27466 | 59.7473 | -0.22888 | -0.045776 | -0.12817 | 0.059509 | -0.036621 | 0.050354 | -0.11902 | 0.09613 | -0.073243 | 0.13733 | 122.4792 | 0.009155 | 122.525 | 122.374 | 122.3373 | 122.3282 | 122.2916 | -122.4655 | -122.4655 | 122.4335 | 122.4792 | 59.5871 | 59.6878
400.7656 | 122.7219 | -59.7382 | 62.6999 | -0.13267 | 0.0031937 | 0.061812 | 0.084926 | -0.0011109 | 0.0002778 | -0.0026704 | -0.018616 | -0.00091423 | 0.062897 | 0.065322 | -0.010982 | -0.00029487 | -0.0026703 | -0.10986 | 62.6221 | -59.7839 | 62.709 | -59.6146 | -59.9991 | -0.004578 | -0.027466 | 62.6358 | -59.7839 | 62.7594 | -59.7382 | -59.8343 | -59.6603 | -0.045777 | -0.07782 | 0.009155 | 0.1236 | 59.7336 | -0.26093 | 59.7794 | -0.21515 | -0.045777 | -0.064087 | 0.059509 | 0 | 0.07782 | -0.096131 | 0.1236 | -0.050354 | 0.16937 | 122.493 | 0.045777 | 122.5433 | 122.406 | 122.4197 | 122.3602 | 122.374 | -122.4838 | -122.4838 | 122.4472 | 122.4976 | 59.6283 | 59.7107
401.7656 | 122.6166 | -59.7427 | 62.7731 | -0.018234 | -0.00065152 | 0.062666 | 0.086208 | 0.0014527 | -0.0048492 | -0.0013886 | -0.073547 | 0.00229 | 0.061615 | 0.067031 | -0.010342 | -0.00050847 | -0.00053411 | 0.013733 | 62.6862 | -59.7702 | 62.7228 | -59.6237 | -60.0128 | 0.041199 | 0.027466 | 62.677 | -59.7107 | 62.7548 | -59.8297 | -59.8663 | -59.7198 | -0.027466 | -0.086975 | -0.050354 | 0.11902 | 59.7839 | -0.27008 | 59.8114 | -0.24261 | 0.032044 | -0.09613 | -0.01831 | -0.086975 | 0.022888 | -0.1236 | -0.009156 | -0.15564 | 0.14649 | 122.493 | -0.11902 | 122.4655 | 122.4564 | 122.3877 | 122.4289 | 122.4197 | -122.5433 | -122.4838 | 122.4655 | 122.4976 | 59.7565 | 59.7702
402.7656 | 122.7539 | -59.7198 | 62.6907 | -0.025863 | -0.00022432 | 0.061598 | 0.083858 | 0.00038452 | -0.0022858 | 0.0026702 | -0.0033568 | -5.9826e-05 | 0.063324 | 0.062545 | -0.011623 | 0.0018413 | -0.0018157 | 0.036621 | 62.6175 | -59.7473 | 62.8189 | -59.4955 | -59.8892 | 0.11444 | 0.15106 | 62.6038 | -59.7382 | 63.0295 | -59.3399 | -60.1135 | -59.8846 | -0.027465 | -0.073242 | 0.12817 | 0.22431 | 59.8343 | -0.16937 | 59.8618 | -0.14191 | -0.01831 | -0.086975 | 0.33875 | 0.37994 | -0.16479 | -0.39368 | -0.14648 | -0.37537 | 0.25177 | 122.5662 | 0.39825 | 122.7676 | 122.3648 | 122.3419 | 122.3373 | 122.3236 | -122.438 | -122.4289 | 122.5388 | 122.7493 | 59.7565 | 59.8709
403.7656 | 122.6898 | -59.729 | 62.6999 | -0.2166 | 0.0027665 | 0.06053 | 0.085139 | 0.0020935 | -0.0037812 | -0.0030976 | -0.033874 | -5.9826e-05 | 0.066101 | 0.060836 | -0.010128 | 0.00077333 | -0.0011749 | -0.018311 | 62.6175 | -59.8022 | 62.7274 | -59.6146 | -59.9899 | -0.013733 | -0.027466 | 62.6175 | -59.7519 | 62.7686 | -59.7244 | -59.8251 | -59.6695 | -0.073242 | -0.082397 | 0.027466 | 0.11444 | 59.7153 | -0.26092 | 59.7885 | -0.18768 | -0.022888 | -0.082397 | 0.068665 | 0.004578 | 0.059509 | -0.09613 | 0.082397 | -0.073242 | 0.18768 | 122.5296 | 0.027466 | 122.5204 | 122.4197 | 122.3694 | 122.3465 | 122.3465 | -122.5021 | -122.4518 | 122.4564 | 122.4976 | 59.7107 | 59.7015
404.7656 | 122.7585 | -59.6832 | 62.7228 | -0.07164 | -0.00086512 | 0.063307 | 0.085353 | 0.0010253 | -0.0007904 | -0.00053396 | -0.033874 | -5.9826e-05 | 0.063538 | 0.062972 | -0.010769 | 0.00055973 | -0.0033111 | -0.009155 | 62.6358 | -59.7702 | 62.7731 | -59.5779 | -59.9533 | 0.041199 | 0.036621 | 62.6083 | -59.7473 | 62.796 | -59.697 | -59.7748 | -59.6375 | -0.086975 | -0.086975 | 0.050354 | 0.10529 | 59.7244 | -0.27008 | 59.8114 | -0.1831 | -0.064086 | -0.11444 | 0.073243 | -0.013732 | 0.045777 | -0.091552 | 0.10986 | -0.027466 | 0.19226 | 122.5433 | 0.050354 | 122.5433 | 122.406 | 122.3557 | 122.319 | 122.2916 | -122.493 | -122.4701 | 122.4564 | 122.4792 | 59.6741 | 59.7198
405.7656 | 122.7722 | -59.7015 | 62.7136 | -0.094528 | 0.0016983 | 0.062453 | 0.08578 | -0.0017517 | -0.0003632 | -0.0033112 | -0.018616 | -0.001128 | 0.063965 | 0.062972 | -0.0094869 | -0.00072207 | -0.0026703 | -0.009155 | 62.6266 | -59.7794 | 62.764 | -59.5734 | -59.9304 | 0.050354 | 0.022888 | 62.5992 | -59.7427 | 62.8235 | -59.6832 | -59.761 | -59.6329 | -0.07782 | -0.086975 | 0.050354 | 0.12817 | 59.7519 | -0.22888 | 59.8297 | -0.15106 | -0.041199 | -0.11444 | 0.10986 | 0.01831 | 0.068664 | -0.059509 | 0.10986 | -0.01831 | 0.20599 | 122.5433 | 0.059509 | 122.5662 | 122.406 | 122.3419 | 122.3282 | 122.3007 | -122.493 | -122.4564 | 122.4655 | 122.525 | 59.6924 | 59.7244
406.7656 | 122.7539 | -59.6786 | 62.709 | -0.086899 | 0.0027665 | 0.062666 | 0.084285 | -0.0034607 | 6.4004e-05 | -0.00074776 | -0.021667 | -5.9826e-05 | 0.063538 | 0.06169 | -0.01141 | -0.00072207 | -0.0041657 | 0.050354 | 62.6266 | -59.761 | 62.8189 | -59.5093 | -59.8984 | 0.10986 | 0.14191 | 62.5992 | -59.7061 | 62.8189 | -59.642 | -59.7656 | -59.6237 | -0.082397 | -0.082397 | 0.10986 | 0.16937 | 59.7885 | -0.21973 | 59.8709 | -0.13733 | -0.027466 | -0.10986 | 0.10986 | 0.036621 | 0.054932 | -0.086975 | 0.082398 | -0.059509 | 0.25177 | 122.58 | 0.064087 | 122.525 | 122.3877 | 122.3053 | 122.3053 | 122.2778 | -122.4701 | -122.4152 | 122.4976 | 122.4976 | 59.729 | 59.8206
407.7656 | 122.7173 | -59.7061 | 62.709 | -0.048752 | 0.0016983 | 0.062666 | 0.083644 | -0.0030335 | -0.001004 | -0.0026704 | -0.018616 | -0.00027343 | 0.064606 | 0.061904 | -0.010342 | 0.0022687 | -0.0013885 | -0.068665 | 62.6175 | -59.7702 | 62.7228 | -59.6008 | -60.0037 | -0.013733 | -0.041199 | 62.6083 | -59.7748 | 62.7502 | -59.7336 | -59.8434 | -59.6786 | -0.064087 | -0.091552 | 0.013733 | 0.10529 | 59.6924 | -0.29755 | 59.7565 | -0.23346 | -0.068664 | -0.10071 | 0.041199 | -0.027466 | 0.027466 | -0.13733 | 0.09613 | -0.068665 | 0.16937 | 122.493 | 0.041198 | 122.525 | 122.3877 | 122.3831 | 122.3236 | 122.3145 | -122.4792 | -122.4838 | 122.4289 | 122.4564 | 59.6375 | 59.6649
408.7656 | 122.6807 | -59.7015 | 62.6999 | -0.14793 | 0.0012711 | 0.063734 | 0.086208 | -0.0028199 | -0.0001496 | -0.002884 | -0.058289 | -0.0015552 | 0.062683 | 0.062331 | -0.0099143 | 0.0012005 | -0.0024567 | -0.041199 | 62.6038 | -59.7794 | 62.7228 | -59.61 | -59.9991 | -0.004578 | -0.022888 | 62.6175 | -59.7473 | 62.7502 | -59.7473 | -59.8251 | -59.6878 | -0.07782 | -0.09613 | 0.022888 | 0.091553 | 59.697 | -0.29755 | 59.7748 | -0.21973 | -0.045776 | -0.082397 | 0.050354 | -0.045776 | 0.013733 | -0.1236 | 0.059509 | -0.07782 | 0.16937 | 122.5021 | 0 | 122.4976 | 122.3831 | 122.3648 | 122.3053 | 122.319 | -122.4792 | -122.4472 | 122.4243 | 122.4518 | 59.6603 | 59.6786
409.7656 | 122.7539 | -59.6924 | 62.7182 | -0.07164 | 0.00020288 | 0.061598 | 0.084285 | -0.0023925 | -0.0031402 | -0.00032036 | -0.024719 | -0.0017688 | 0.066956 | 0.062545 | -0.012264 | 0.0022687 | 0.00074769 | 0.059509 | 62.645 | -59.7427 | 62.8143 | -59.5047 | -59.8938 | 0.10986 | 0.14648 | 62.6083 | -59.7061 | 62.8098 | -59.6512 | -59.7565 | -59.6329 | -0.050354 | -0.073243 | 0.09613 | 0.18768 | 59.8022 | -0.20142 | 59.8526 | -0.15106 | -0.013733 | -0.10986 | 0.091552 | 0.041199 | 0.059509 | -0.064087 | 0.073242 | -0.050354 | 0.23804 | 122.5571 | 0.054932 | 122.5159 | 122.3877 | 122.3145 | 122.3373 | 122.3007 | -122.4609 | -122.4243 | 122.5067 | 122.5021 | 59.7519 | 59.8389
410.7656 | 122.7219 | -59.697 | 62.7411 | -0.07164 | 0.00041648 | 0.062666 | 0.083858 | -0.00046988 | -0.0003632 | -0.0013886 | -0.027771 | -0.00091423 | 0.062256 | 0.067671 | -0.0097007 | 0.0018413 | 0.00010689 | 0.050354 | 62.6175 | -59.7336 | 62.8189 | -59.5093 | -59.8984 | 0.11444 | 0.13733 | 62.6175 | -59.7198 | 62.8326 | -59.6603 | -59.7656 | -59.6329 | -0.036622 | -0.1236 | 0.07782 | 0.18768 | 59.8114 | -0.20142 | 59.848 | -0.16479 | -0.022889 | -0.1236 | 0.091553 | 0.036621 | 0.064086 | -0.068665 | 0.086975 | -0.045776 | 0.22431 | 122.5525 | 0.05951 | 122.5525 | 122.3511 | 122.3373 | 122.3145 | 122.3145 | -122.4747 | -122.4609 | 122.5159 | 122.5296 | 59.7473 | 59.8343
411.7656 | 122.5937 | -59.7656 | 62.7182 | -0.079269 | 0.0031937 | 0.063734 | 0.087489 | 0.0016663 | -0.0024994 | -0.0024566 | -0.14679 | -0.00027343 | 0.063324 | 0.065749 | -0.0090597 | 0.0044049 | -0.0054473 | -0.050354 | 62.6495 | -59.8343 | 62.677 | -59.6832 | -60.0906 | -0.10529 | -0.11902 | 62.6587 | -59.7794 | 62.6907 | -59.8618 | -59.9808 | -59.7656 | -0.068665 | -0.068665 | -0.041199 | 0.082397 | 59.6603 | -0.32501 | 59.729 | -0.25635 | -0.013733 | -0.05951 | -0.027466 | -0.09613 | 0 | -0.21515 | 0.013733 | -0.20142 | 0.15106 | 122.5113 | -0.082397 | 122.4701 | 122.4838 | 122.438 | 122.4152 | 122.4243 | -122.5525 | -122.4976 | 122.4426 | 122.4564 | 59.7153 | 59.6466
412.7656 | 122.7493 | -59.7107 | 62.7045 | -0.094528 | -1.0718e-05 | 0.063307 | 0.087276 | 0.0020935 | -0.0005768 | -0.001175 | -0.0033568 | -0.0013416 | 0.06247 | 0.064894 | -0.0077779 | -0.00029487 | -0.00096131 | 0.050354 | 62.645 | -59.7427 | 62.8281 | -59.4727 | -59.8755 | 0.1236 | 0.032043 | 62.6312 | -59.7061 | 62.8784 | -59.7473 | -59.761 | -59.5734 | -0.032044 | -0.05951 | 0.1236 | 0.23804 | 59.8343 | -0.16479 | 59.8663 | -0.13275 | 0.004577 | -0.073242 | 0.17395 | -0.036621 | 0.13733 | -0.050354 | 0.13275 | -0.054931 | 0.27008 | 122.5708 | -0.041198 | 122.5845 | 122.3877 | 122.3373 | 122.3557 | 122.3419 | -122.4472 | -122.4106 | 122.5388 | 122.5891 | 59.761 | 59.7427
413.7656 | 122.7768 | -59.697 | 62.7045 | -0.048752 | -0.00022432 | 0.063521 | 0.086421 | -0.0030335 | -0.0018586 | -0.002884 | -0.024719 | 0.00079477 | 0.065674 | 0.066603 | -0.010128 | -0.0020039 | 0.0018159 | 0.054932 | 62.6404 | -59.7656 | 62.8189 | -59.4818 | -59.8709 | 0.1236 | 0.050354 | 62.6129 | -59.6695 | 62.8784 | -59.7107 | -59.7702 | -59.6008 | -0.068665 | -0.064087 | 0.11444 | 0.21515 | 59.8206 | -0.17395 | 59.8892 | -0.10529 | 0.027465 | -0.091553 | 0.17395 | -0.013733 | 0.09613 | -0.073243 | 0.068665 | -0.10071 | 0.28381 | 122.5845 | -0.041198 | 122.5479 | 122.406 | 122.2824 | 122.3373 | 122.3099 | -122.4701 | -122.374 | 122.5159 | 122.5754 | 59.7519 | 59.7473
414.7656 | 122.7859 | -59.697 | 62.7182 | -0.056381 | -1.0718e-05 | 0.064803 | 0.084499 | -0.00025628 | -0.0018586 | 0.0013886 | -0.0094604 | -0.0017688 | 0.064392 | 0.062331 | -0.010555 | 0.00034613 | -0.0026703 | 0.054932 | 62.6129 | -59.761 | 62.8372 | -59.491 | -59.8755 | 0.12817 | 0.14191 | 62.6266 | -59.6878 | 62.8876 | -59.7519 | -59.7473 | -59.5779 | -0.064087 | -0.10529 | 0.11902 | 0.20599 | 59.8251 | -0.17853 | 59.8892 | -0.11444 | 0.009155 | -0.091553 | 0.16937 | -0.054932 | 0.11902 | -0.050354 | 0.10986 | -0.059509 | 0.27008 | 122.5983 | -0.064087 | 122.5754 | 122.374 | 122.3145 | 122.3099 | 122.3236 | -122.4792 | -122.406 | 122.5342 | 122.5845 | 59.7519 | 59.8389
415.7656 | 122.7585 | -59.697 | 62.6999 | -0.094528 | 0.0010575 | 0.063094 | 0.083858 | -0.0021789 | -0.0031402 | 0.00096124 | -0.039978 | -0.0017688 | 0.065674 | 0.06938 | -0.0077779 | 0.00034613 | -0.0045929 | -0.009155 | 62.6312 | -59.7565 | 62.7777 | -59.5459 | -59.9258 | 0.045776 | 0.073242 | 62.5992 | -59.7519 | 62.8143 | -59.6741 | -59.761 | -59.6237 | -0.05951 | -0.068664 | 0.07782 | 0.15106 | 59.7427 | -0.22888 | 59.8022 | -0.16937 | -0.054932 | -0.10071 | 0.11444 | 0.022888 | 0.073242 | -0.064087 | 0.12817 | -0.009155 | 0.21057 | 122.5342 | 0.07782 | 122.5662 | 122.3877 | 122.3511 | 122.3282 | 122.2961 | -122.4564 | -122.4518 | 122.4747 | 122.5113 | 59.6878 | 59.7702
416.7656 | 122.6624 | -59.7336 | 62.7731 | -0.048752 | 0.00020288 | 0.062666 | 0.085567 | -0.00068368 | -0.0022858 | -0.0026704 | -0.079651 | 0.00015377 | 0.064392 | 0.061904 | -0.0099143 | 0.00077333 | -0.0033111 | 0.004578 | 62.6907 | -59.7839 | 62.6999 | -59.6649 | -60.0037 | 0.027466 | -0.009155 | 62.6541 | -59.7656 | 62.7319 | -59.7748 | -59.8709 | -59.697 | -0.050354 | -0.082397 | -0.073242 | 0.068665 | 59.761 | -0.27008 | 59.8114 | -0.21973 | -0.032043 | -0.11902 | -0.041198 | -0.041198 | 0.036622 | -0.13733 | 0.068665 | -0.10529 | 0.11902 | 122.4838 | -0.009155 | 122.4976 | 122.4747 | 122.4197 | 122.4243 | 122.3877 | -122.5571 | -122.5388 | 122.4335 | 122.4655 | 59.7382 | 59.7244
417.7656 | 122.7127 | -59.6741 | 62.7594 | -0.041122 | -1.0718e-05 | 0.063307 | 0.084499 | -0.0011109 | -0.0018586 | 0.00096124 | -0.00030524 | 0.0014356 | 0.063111 | 0.057631 | -0.0099143 | 0.0020551 | -0.0033111 | 0.064087 | 62.645 | -59.7382 | 62.8189 | -59.4955 | -59.8938 | 0.11444 | 0.12817 | 62.5854 | -59.7198 | 62.8098 | -59.6603 | -59.7656 | -59.6054 | -0.064087 | -0.11444 | 0.05951 | 0.17853 | 59.7885 | -0.21973 | 59.8526 | -0.15564 | -0.045777 | -0.17395 | 0.050354 | 0.013733 | 0.068664 | -0.091553 | 0.11444 | -0.045776 | 0.24262 | 122.5571 | 0.05951 | 122.5296 | 122.3831 | 122.3053 | 122.319 | 122.2595 | -122.4976 | -122.4792 | 122.493 | 122.4838 | 59.7382 | 59.8022
418.7656 | 122.6257 | -59.7244 | 62.7777 | -0.025863 | 0.0012711 | 0.063307 | 0.08813 | -0.00046988 | -0.0020722 | 0.00074764 | -0.033874 | -0.00048703 | 0.066101 | 0.06169 | -0.010769 | 0.0018413 | -0.0026703 | -0.004578 | 62.6862 | -59.7748 | 62.7686 | -59.404 | -60.1776 | -0.10071 | 0.059509 | 62.677 | -59.7702 | 62.7182 | -59.7794 | -59.8618 | -59.7107 | -0.050354 | -0.091553 | -0.009155 | 0.32043 | 59.6237 | -0.45319 | 59.6741 | -0.40283 | -0.045777 | -0.10071 | -0.059509 | -0.054932 | 0.013733 | -0.13733 | 0.05951 | -0.091552 | 0.37079 | 122.5433 | -0.009155 | 122.4884 | 122.4609 | 122.4472 | 122.4106 | 122.4014 | -122.5525 | -122.5479 | 122.493 | 122.4426 | 59.7198 | 59.7839
419.7656 | 122.6166 | -59.7061 | 62.7548 | -0.079269 | 0.00041648 | 0.061812 | 0.088557 | 0.00059812 | -0.0022858 | -0.0026704 | -0.11017 | -0.00070063 | 0.065247 | 0.059981 | -0.0094869 | 0.0026959 | -0.0016021 | -0.009155 | 62.6633 | -59.7748 | 62.6953 | -59.4452 | -59.816 | -0.082397 | 0.086975 | 62.6495 | -59.7748 | 62.7136 | -59.7794 | -59.8892 | -59.7015 | -0.068664 | -0.091553 | -0.05951 | 0.26093 | 59.6237 | -0.10986 | 59.6924 | -0.041199 | -0.068664 | -0.10529 | -0.041199 | -0.073242 | 0.004578 | -0.1831 | 0.073242 | -0.11444 | 0.32959 | 122.4701 | -0.004578 | 122.4884 | 122.438 | 122.4243 | 122.3694 | 122.3557 | -122.5296 | -122.5296 | 122.4014 | 122.4197 | 59.697 | 59.7931
420.7656 | 122.7356 | -59.6924 | 62.7411 | -0.094528 | 0.0012711 | 0.061171 | 0.084285 | 0.00038452 | -0.0005768 | -0.004593 | 0.0027466 | -5.9826e-05 | 0.066101 | 0.058913 | -0.0084189 | 0.00055973 | -0.0018157 | 0.050354 | 62.6587 | -59.7519 | 62.8281 | -59.4955 | -59.8801 | 0.12817 | 0.13733 | 62.6175 | -59.7565 | 62.8189 | -59.6649 | -59.761 | -59.61 | -0.059509 | -0.082398 | 0.086975 | 0.19684 | 59.8206 | -0.18768 | 59.8801 | -0.12817 | -0.064087 | -0.1236 | 0.07782 | 0.027466 | 0.082398 | -0.068664 | 0.14648 | -0.004577 | 0.25635 | 122.58 | 0.091553 | 122.5754 | 122.4106 | 122.374 | 122.3511 | 122.3099 | -122.493 | -122.4976 | 122.5204 | 122.5113 | 59.7427 | 59.8297
421.7656 | 122.6395 | -59.7473 | 62.7548 | -0.06401 | 0.0010575 | 0.062239 | 0.087917 | 0.0025207 | -0.0018586 | -0.00096136 | -0.09491 | 0.00079477 | 0.065033 | 0.065535 | -0.010982 | 0.0041913 | 0.0016021 | -0.004578 | 62.6404 | -59.8251 | 62.7182 | -59.6283 | -60.0311 | -0.013733 | -0.013733 | 62.6358 | -59.761 | 62.7365 | -59.8068 | -59.8984 | -59.7198 | -0.07782 | -0.11444 | -0.036621 | 0.11902 | 59.7336 | -0.28381 | 59.8114 | -0.20599 | -0.013733 | -0.11902 | -0.018311 | -0.05951 | 0.027465 | -0.15106 | 0.041198 | -0.13733 | 0.19684 | 122.5433 | -0.045777 | 122.4976 | 122.4655 | 122.3969 | 122.3877 | 122.3831 | -122.58 | -122.5159 | 122.4655 | 122.4838 | 59.7427 | 59.7336
422.7656 | 122.7448 | -59.7107 | 62.6907 | -0.079269 | 0.00063028 | 0.062666 | 0.083217 | 0.0023071 | -0.0054902 | -0.0013886 | 0.0057984 | -0.0013416 | 0.065247 | 0.061049 | -0.013973 | -0.0011493 | 0.0022431 | 0.036621 | 62.645 | -59.7153 | 62.8052 | -59.4635 | -59.8755 | 0.11902 | 0.15106 | 62.59 | -59.7198 | 62.7686 | -59.9442 | -59.729 | -59.523 | -0.004578 | -0.045777 | 0.11444 | 0.24719 | 59.8297 | -0.16479 | 59.8343 | -0.16022 | -0.009156 | -0.10071 | 0.07782 | -0.23346 | 0.18768 | -0.018311 | 0.19684 | -0.009155 | 0.25177 | 122.5204 | -0.2243 | 122.4884 | 122.3602 | 122.3099 | 122.3557 | 122.3007 | -122.406 | -122.4106 | 122.5159 | 122.4792 | 59.7473 | 59.8618
423.7656 | 122.7585 | -59.6878 | 62.7411 | -0.06401 | 0.0012711 | 0.063948 | 0.083858 | 0.00038452 | 0.0019866 | -0.00053396 | 0.039368 | 0.00015377 | 0.065888 | 0.05934 | -0.011837 | 0.0022687 | 0.00074769 | 0.054932 | 62.6495 | -59.7061 | 62.8052 | -59.4864 | -59.8938 | 0.10529 | 0.13275 | 62.6038 | -59.7382 | 62.8189 | -59.6512 | -59.7473 | -59.6146 | -0.018311 | -0.091553 | 0.064087 | 0.20142 | 59.7931 | -0.20599 | 59.8114 | -0.18768 | -0.050354 | -0.13733 | 0.07782 | 0.036621 | 0.073242 | -0.059509 | 0.1236 | -0.009155 | 0.21973 | 122.5113 | 0.086975 | 122.5571 | 122.3557 | 122.3419 | 122.3373 | 122.2916 | -122.4472 | -122.4792 | 122.493 | 122.5067 | 59.7427 | 59.8206
424.7656 | 122.6944 | -59.7061 | 62.7548 | -0.07164 | 0.0021255 | 0.060744 | 0.084926 | 0.0014527 | 0.0004914 | -0.0033112 | -0.0094604 | -0.00070063 | 0.063751 | 0.062331 | -0.011623 | 0.00055973 | -0.0056609 | 0.059509 | 62.6541 | -59.7427 | 62.8006 | -59.5322 | -59.9167 | 0.10529 | 0.10529 | 62.6541 | -59.7473 | 62.7411 | -59.7198 | -59.8251 | -59.6603 | -0.036621 | -0.10071 | 0.045776 | 0.17395 | 59.8114 | -0.21057 | 59.848 | -0.17395 | -0.041198 | -0.10071 | -0.013733 | -0.013733 | 0.045777 | -0.11902 | 0.086975 | -0.07782 | 0.21057 | 122.5433 | 0.027465 | 122.4884 | 122.3969 | 122.4014 | 122.3602 | 122.3602 | -122.4976 | -122.5021 | 122.5067 | 122.4472 | 59.7656 | 59.8114
425.7656 | 122.6395 | -59.7244 | 62.7731 | -0.025863 | 0.00020288 | 0.062025 | 0.086848 | 0.00017092 | -0.0024994 | 0.0024566 | -0.049133 | 0.0020764 | 0.063751 | 0.058272 | -0.010769 | 0.0012005 | 0.0048065 | 0 | 62.6907 | -59.7839 | 62.6953 | -59.642 | -60.0082 | 0.032043 | 0.013733 | 62.6633 | -59.761 | 62.7136 | -59.7931 | -59.8709 | -59.7061 | -0.05951 | -0.082397 | -0.07782 | 0.082397 | 59.7565 | -0.28381 | 59.816 | -0.2243 | -0.036621 | -0.10986 | -0.059509 | -0.068665 | 0.01831 | -0.14648 | 0.054931 | -0.10986 | 0.14191 | 122.4792 | -0.032044 | 122.4747 | 122.4747 | 122.4243 | 122.4152 | 122.3877 | -122.5571 | -122.5342 | 122.4197 | 122.438 | 59.7244 | 59.7382
426.7656 | 122.6349 | -59.7336 | 62.764 | -0.06401 | 0.0016983 | 0.06288 | 0.086421 | 0.0067933 | 0.0002778 | -0.0018158 | -0.10712 | -0.001128 | 0.063965 | 0.062972 | -0.0094869 | 0.0031231 | -0.0013885 | 0.004578 | 62.6404 | -59.7794 | 62.7182 | -59.61 | -59.9991 | -0.009155 | 0.013733 | 62.6587 | -59.7382 | 62.7457 | -59.7656 | -59.8984 | -59.7015 | -0.045776 | -0.1236 | -0.045776 | 0.1236 | 59.7244 | -0.2655 | 59.7702 | -0.21973 | -0.004577 | -0.10529 | -0.01831 | -0.032043 | 0.032044 | -0.16479 | 0.036621 | -0.16022 | 0.16937 | 122.4976 | -0.027466 | 122.4838 | 122.4197 | 122.3969 | 122.374 | 122.3923 | -122.5433 | -122.5021 | 122.4518 | 122.4792 | 59.7382 | 59.7473
427.7656 | 122.7173 | -59.7153 | 62.7777 | -0.041122 | 0.0025529 | 0.06288 | 0.08578 | -0.0015381 | -0.0020722 | 0.00096124 | -0.0033568 | -0.0013416 | 0.063111 | 0.058913 | -0.010982 | 0.0012005 | 0.0035247 | 0.064087 | 62.6266 | -59.7153 | 62.7823 | -59.523 | -59.9075 | 0.10529 | 0.11444 | 62.6358 | -59.7427 | 62.7731 | -59.7015 | -59.8022 | -59.6512 | 0 | -0.15106 | 0.004578 | 0.19226 | 59.8206 | -0.19226 | 59.8206 | -0.19226 | -0.027466 | -0.14191 | -0.004578 | 0.013733 | 0.064087 | -0.086975 | 0.091553 | -0.059509 | 0.19226 | 122.4976 | 0.041199 | 122.5159 | 122.3419 | 122.3785 | 122.3419 | 122.3511 | -122.493 | -122.5204 | 122.4976 | 122.4884 | 59.7794 | 59.8297
428.7656 | 122.699 | -59.6924 | 62.764 | -0.048752 | 0.00020288 | 0.061171 | 0.084712 | -0.0013245 | -0.0007904 | 0.0026702 | -0.0064086 | -0.00048703 | 0.062897 | 0.05699 | -0.010769 | 0.0022687 | 0.0033111 | 0.059509 | 62.6221 | -59.7565 | 62.8006 | -59.5276 | -59.9075 | 0.10986 | 0.12817 | 62.6221 | -59.7336 | 62.7731 | -59.6924 | -59.7839 | -59.6512 | -0.064087 | -0.14191 | 0.036621 | 0.16479 | 59.8022 | -0.21515 | 59.8663 | -0.15106 | -0.041199 | -0.14191 | 0.009155 | 0 | 0.041199 | -0.091553 | 0.082398 | -0.050354 | 0.22888 | 122.5571 | 0.041199 | 122.5067 | 122.3785 | 122.3557 | 122.3145 | 122.3145 | -122.5204 | -122.4976 | 122.493 | 122.4655 | 59.7519 | 59.8206
429.7656 | 122.6349 | -59.7244 | 62.7594 | -0.033493 | -0.00043792 | 0.061812 | 0.083217 | -0.0021789 | -0.0014312 | -0.00010676 | -0.0033568 | 0.0031446 | 0.06482 | 0.060622 | -0.0088461 | 0.0016277 | 0.00074769 | 0.022888 | 62.6541 | -59.7748 | 62.7182 | -59.6054 | -59.9762 | 0.068665 | 0.041199 | 62.6724 | -59.7656 | 62.7045 | -59.7656 | -59.8663 | -59.7198 | -0.050354 | -0.10529 | -0.041198 | 0.11902 | 59.7931 | -0.25177 | 59.8434 | -0.20142 | -0.041199 | -0.086975 | -0.054931 | -0.041199 | 0.004577 | -0.14191 | 0.045776 | -0.10071 | 0.16937 | 122.493 | 0 | 122.4701 | 122.4289 | 122.438 | 122.3785 | 122.3969 | -122.5342 | -122.525 | 122.4426 | 122.4289 | 59.7473 | 59.7656
430.7656 | 122.6303 | -59.7565 | 62.7548 | -0.056381 | 0.0010575 | 0.063948 | 0.086848 | 0.0050843 | 0.0013458 | 0.00074764 | -0.088806 | 0.0031446 | 0.064392 | 0.063613 | -0.010769 | 0.0018413 | -0.0020295 | -0.004578 | 62.6358 | -59.7931 | 62.6953 | -59.6603 | -60.0403 | -0.054932 | -0.050354 | 62.6404 | -59.7748 | 62.7136 | -59.8206 | -59.935 | -59.7336 | -0.036621 | -0.11902 | -0.05951 | 0.096131 | 59.7015 | -0.28381 | 59.7382 | -0.24719 | -0.01831 | -0.11444 | -0.041199 | -0.064087 | 0.022888 | -0.17853 | 0.041198 | -0.16022 | 0.13275 | 122.4884 | -0.045777 | 122.4884 | 122.4289 | 122.4152 | 122.3923 | 122.3969 | -122.5479 | -122.5296 | 122.4518 | 122.4701 | 59.7519 | 59.7061
431.7656 | 122.6303 | -59.7153 | 62.7777 | -0.010605 | 0.00020288 | 0.061385 | 0.085353 | -0.0030335 | -0.0007904 | -0.0020294 | -0.04303 | -5.9826e-05 | 0.064392 | 0.059554 | -0.0088461 | 0.0016277 | -0.00074771 | 0.19226 | 62.7502 | -59.7244 | 62.6404 | -59.642 | -59.9945 | 0.013733 | 0.004578 | 62.6587 | -59.7336 | 62.7136 | -59.7794 | -59.8801 | -59.697 | -0.009155 | -0.027466 | -0.13733 | 0.073242 | 59.729 | -0.27924 | 59.7382 | -0.27008 | -0.018311 | -0.11902 | -0.064087 | -0.064087 | 0.018311 | -0.16479 | 0.036622 | -0.14648 | 0.082397 | 122.3648 | -0.045776 | 122.4472 | 122.4747 | 122.3923 | 122.4655 | 122.374 | -122.5021 | -122.5113 | 122.3557 | 122.4289 | 59.9075 | 59.7198
432.7656 | 122.6303 | -59.7382 | 62.8098 | 0.004654 | -0.00043792 | 0.060316 | 0.085994 | 0.0014527 | -0.001004 | -0.0026704 | 0.018005 | 0.00079477 | 0.066956 | 0.063826 | -0.0097007 | 0.00098693 | 0.0028839 | 0.050354 | 62.6678 | -59.7427 | 62.7411 | -59.5505 | -59.9579 | 0.064087 | 0.068665 | 62.6633 | -59.7519 | 62.7365 | -59.7702 | -59.8663 | -59.7015 | -0.004578 | -0.14191 | -0.068664 | 0.18768 | 59.8022 | -0.21973 | 59.8068 | -0.21515 | -0.013733 | -0.14648 | -0.073242 | -0.032044 | 0.036621 | -0.12817 | 0.050354 | -0.11444 | 0.19226 | 122.4838 | -0.018311 | 122.4884 | 122.4106 | 122.4152 | 122.406 | 122.4014 | -122.5525 | -122.5616 | 122.4792 | 122.4747 | 59.7885 | 59.8068
433.7656 | 122.6532 | -59.7427 | 62.7869 | -0.025863 | 0.0010575 | 0.063094 | 0.084926 | 0.0033753 | -0.0039948 | 0.0016022 | -0.033874 | 0.0020764 | 0.067597 | 0.064894 | -0.0099143 | 0.0022687 | -0.00074771 | -0.013733 | 62.677 | -59.7931 | 62.7228 | -59.8251 | -60.2142 | 0.045776 | -0.013733 | 62.6495 | -59.7748 | 62.7136 | -59.7885 | -59.8709 | -59.7153 | -0.050354 | -0.10986 | -0.064087 | -0.082397 | 59.7885 | -0.4715 | 59.8389 | -0.42114 | -0.032043 | -0.13733 | -0.073242 | -0.045776 | 0.027466 | -0.12817 | 0.059509 | -0.096131 | -0.032043 | 122.5159 | -0.013733 | 122.4884 | 122.4701 | 122.4243 | 122.4197 | 122.3923 | -122.58 | -122.5616 | 122.4655 | 122.4564 | 59.729 | 59.729
434.7656 | 122.6624 | -59.7061 | 62.7777 | -0.07164 | -0.00065152 | 0.061812 | 0.085567 | -0.00046988 | -0.0022858 | -0.00053396 | -0.058289 | 0.0020764 | 0.065033 | 0.058913 | -0.0075643 | 0.0016277 | 0.00032049 | 0.004578 | 62.6724 | -59.7977 | 62.6862 | -59.6512 | -59.9899 | 0.022888 | 0.004578 | 62.6678 | -59.761 | 62.7182 | -59.7839 | -59.8755 | -59.7244 | -0.091552 | -0.10529 | -0.091553 | 0.054932 | 59.729 | -0.28381 | 59.8206 | -0.19226 | -0.054931 | -0.10986 | -0.059509 | -0.07782 | -0.01831 | -0.16937 | 0.036621 | -0.11444 | 0.14648 | 122.4838 | -0.022889 | 122.4792 | 122.4701 | 122.4289 | 122.3785 | 122.374 | -122.5754 | -122.5388 | 122.3923 | 122.4243 | 59.7107 | 59.7107
435.7656 | 122.731 | -59.6878 | 62.7411 | -0.094528 | 0.0014847 | 0.062239 | 0.084712 | -0.0021789 | -0.0024994 | -0.0013886 | 0.027161 | -0.0015552 | 0.064392 | 0.062972 | -0.0097007 | 0.0026959 | 0.00096129 | 0.068665 | 62.6404 | -59.7473 | 62.8098 | -59.5001 | -59.8984 | 0.11444 | 0.14191 | 62.6175 | -59.6878 | 62.8052 | -59.6786 | -59.7519 | -59.6054 | -0.059509 | -0.10071 | 0.068664 | 0.18768 | 59.8022 | -0.21057 | 59.8618 | -0.15106 | 0 | -0.1236 | 0.064087 | 0.009155 | 0.082397 | -0.064087 | 0.082397 | -0.064087 | 0.24719 | 122.5571 | 0.009155 | 122.493 | 122.3877 | 122.3053 | 122.3282 | 122.3053 | -122.4884 | -122.4289 | 122.4976 | 122.493 | 59.7565 | 59.8297
436.7656 | 122.699 | -59.7198 | 62.7457 | -0.041122 | -1.0718e-05 | 0.062666 | 0.087703 | 0.0044433 | -0.0050628 | 0.00053404 | -0.027771 | -5.9826e-05 | 0.065674 | 0.065535 | -0.010128 | 0.0016277 | -0.0013885 | 0.027466 | 62.6724 | -59.8068 | 62.7136 | -59.6237 | -59.9716 | 0.022888 | 0.041199 | 62.6495 | -59.7565 | 62.7502 | -59.7336 | -59.8618 | -59.6786 | -0.086975 | -0.073243 | -0.032044 | 0.096131 | 59.7427 | -0.25177 | 59.8297 | -0.16479 | -0.036621 | -0.096131 | 0.004577 | -0.013733 | 0.041199 | -0.14191 | 0.07782 | -0.10529 | 0.18311 | 122.5204 | 0.022888 | 122.5067 | 122.4792 | 122.406 | 122.3923 | 122.3694 | -122.5525 | -122.5021 | 122.4335 | 122.4701 | 59.7473 | 59.761
437.7656 | 122.6349 | -59.7061 | 62.7869 | -0.048752 | 0.0014847 | 0.061171 | 0.087276 | 0.00059812 | -0.0018586 | -0.0026704 | -0.018616 | 0.001222 | 0.063751 | 0.059767 | -0.0099143 | 0.0018413 | 0.0011749 | -0.004578 | 62.6816 | -59.7748 | 62.6862 | -59.642 | -60.0128 | 0.022888 | 0.009155 | 62.6495 | -59.7794 | 62.7182 | -59.7702 | -59.8846 | -59.7153 | -0.068664 | -0.10529 | -0.10071 | 0.064087 | 59.729 | -0.3067 | 59.7977 | -0.23804 | -0.073242 | -0.13733 | -0.068664 | -0.064087 | -0.009155 | -0.17853 | 0.064087 | -0.10529 | 0.13275 | 122.4609 | 0.009155 | 122.4976 | 122.4564 | 122.4289 | 122.3877 | 122.3557 | -122.5616 | -122.5662 | 122.3923 | 122.4243 | 59.7015 | 59.7153
438.7656 | 122.7264 | -59.7015 | 62.764 | -0.018234 | 0.0012711 | 0.061812 | 0.085353 | 0.0016663 | -0.0024994 | -0.00053396 | 0.036316 | 0.00079477 | 0.06482 | 0.065962 | -0.012264 | 0.0029095 | -0.00032051 | 0.054932 | 62.6541 | -59.7565 | 62.7914 | -59.523 | -59.9167 | 0.10071 | 0.11902 | 62.6312 | -59.7153 | 62.7731 | -59.7015 | -59.7839 | -59.6329 | -0.054932 | -0.10986 | 0.027466 | 0.17853 | 59.8022 | -0.21515 | 59.8572 | -0.16022 | -0.013733 | -0.13275 | 0.009155 | 0 | 0.068664 | -0.082398 | 0.082397 | -0.068665 | 0.23346 | 122.5479 | 0.013733 | 122.4884 | 122.4106 | 122.3465 | 122.3557 | 122.3328 | -122.5204 | -122.4792 | 122.493 | 122.4747 | 59.7565 | 59.8206
439.7656 | 122.6486 | -59.7382 | 62.7777 | -0.06401 | 0.0019119 | 0.061598 | 0.085994 | -0.0011109 | -0.0020722 | -0.0020294 | -0.0033568 | -0.002196 | 0.064606 | 0.057845 | -0.010128 | 0.00055973 | -0.0024567 | 0.050354 | 62.645 | -59.7473 | 62.7319 | -59.5871 | -59.9533 | 0.07782 | 0.050354 | 62.6404 | -59.7336 | 62.7228 | -59.7702 | -59.8663 | -59.7198 | -0.009155 | -0.13275 | -0.045776 | 0.15106 | 59.816 | -0.21515 | 59.8251 | -0.20599 | 0.004577 | -0.13733 | -0.054932 | -0.032044 | 0.01831 | -0.12817 | 0.013733 | -0.13275 | 0.16022 | 122.4792 | -0.036621 | 122.4564 | 122.3923 | 122.374 | 122.3831 | 122.3785 | -122.525 | -122.5113 | 122.4701 | 122.4609 | 59.7885 | 59.7885
440.7656 | 122.6212 | -59.7198 | 62.7731 | -0.048752 | -0.00043792 | 0.060316 | 0.086208 | 0.0050843 | -0.001004 | 0.0020294 | -0.0064086 | -0.0017688 | 0.064179 | 0.067244 | -0.0079917 | -8.1274e-05 | -0.0024567 | -0.004578 | 62.6953 | -59.7794 | 62.6587 | -59.5551 | -59.9991 | -0.004578 | -0.004578 | 62.677 | -59.7565 | 62.709 | -59.7931 | -59.9075 | -59.7519 | -0.059509 | -0.07782 | -0.11444 | 0.1648 | 59.7153 | -0.27923 | 59.7748 | -0.21973 | -0.036621 | -0.09613 | -0.064087 | -0.073242 | -0.032043 | -0.18768 | 0.004578 | -0.15106 | 0.2243 | 122.438 | -0.036621 | 122.4655 | 122.4747 | 122.4335 | 122.4152 | 122.3969 | -122.5525 | -122.5296 | 122.3785 | 122.4289 | 59.7153 | 59.7153
441.7656 | 122.6532 | -59.7656 | 62.7274 | -0.1403 | 0.0012711 | 0.062239 | 0.086208 | 0.0016663 | -0.0024994 | 0.0024566 | -0.088806 | 0.0035718 | 0.062683 | 0.065749 | -0.010769 | 0.0035503 | -0.00074771 | 0.004578 | 62.6633 | -59.8114 | 62.6358 | -59.7015 | -60.0998 | -0.11444 | -0.13275 | 62.6358 | -59.7931 | 62.6816 | -59.8526 | -59.9533 | -59.7565 | -0.045776 | -0.064087 | -0.091553 | 0.064087 | 59.6512 | -0.33417 | 59.697 | -0.28839 | -0.027466 | -0.091553 | -0.045776 | -0.086975 | 0.009155 | -0.18768 | 0.036621 | -0.16022 | 0.10986 | 122.4472 | -0.059509 | 122.4747 | 122.4747 | 122.4289 | 122.4289 | 122.4014 | -122.5388 | -122.5204 | 122.4014 | 122.4472 | 59.7702 | 59.6329
442.7656 | 122.612 | -59.7244 | 62.7594 | -0.06401 | -0.0015061 | 0.063521 | 0.086635 | -0.0019653 | -0.001004 | 0.00053404 | 0.13397 | -0.00048703 | 0.063751 | 0.060408 | -0.0092733 | 0.0020551 | -0.0020295 | -0.009155 | 62.6953 | -59.7794 | 62.6816 | -59.6283 | -60.0128 | 0.041199 | -0.045776 | 62.6907 | -59.761 | 62.6862 | -59.7839 | -59.9304 | -59.7473 | -0.054932 | -0.064087 | -0.077819 | 0.09613 | 59.7656 | -0.28839 | 59.8206 | -0.23346 | -0.036621 | -0.068664 | -0.073242 | -0.05951 | -0.022888 | -0.20599 | 0.013733 | -0.16937 | 0.15106 | 122.4609 | -0.022889 | 122.4472 | 122.4747 | 122.4518 | 122.4197 | 122.4152 | -122.5388 | -122.5204 | 122.406 | 122.4106 | 59.7153 | 59.6787
443.8281 | 122.7493 | -59.7153 | 62.6724 | 0.080948 | 0.00063028 | 0.064162 | 0.087489 | 0.0010253 | 0.0015594 | -0.00010676 | -0.015564 | -5.9826e-05 | 0.067597 | 0.058699 | -0.010982 | 0.0031231 | 0.0030975 | -0.059509 | 62.6083 | -59.7839 | 62.7686 | -59.5596 | -59.967 | -0.009155 | -0.004578 | 62.5626 | -59.7794 | 62.7823 | -59.7153 | -59.8114 | -59.6283 | -0.068665 | -0.064087 | 0.096131 | 0.15564 | 59.7061 | -0.25177 | 59.7748 | -0.18311 | -0.064087 | -0.10986 | 0.10986 | 0 | 0.086975 | -0.09613 | 0.15106 | -0.032043 | 0.2243 | 122.5525 | 0.064087 | 122.5616 | 122.3923 | 122.3419 | 122.3236 | 122.2778 | -122.4564 | -122.4518 | 122.4838 | 122.4976 | 59.6558 | 59.7107
444.7656 | 122.6028 | -59.7153 | 62.7136 | -0.10216 | 0.00041648 | 0.062239 | 0.084499 | -0.00025628 | 6.4004e-05 | -0.0026704 | -0.015564 | -0.00048703 | 0.063965 | 0.061904 | -0.011623 | 0.0018413 | -0.0016021 | 0.027466 | 62.6953 | -59.7519 | 62.7182 | -59.61 | -60.0174 | 0.027466 | 0.041199 | 62.6633 | -59.7565 | 62.645 | -59.5322 | -59.9533 | -59.8618 | -0.036621 | -0.018311 | 0.004578 | 0.10529 | 59.7427 | -0.30212 | 59.7794 | -0.2655 | -0.041199 | -0.050354 | -0.068665 | 0.18311 | -0.14648 | -0.23804 | -0.10529 | -0.19684 | 0.14191 | 122.4701 | 0.2243 | 122.4014 | 122.4472 | 122.4197 | 122.4106 | 122.3785 | -122.4655 | -122.4701 | 122.4335 | 122.3602 | 59.7427 | 59.7565
445.7656 | 122.6532 | -59.7107 | 62.764 | -0.018234 | 0.0010575 | 0.062025 | 0.087703 | 0.0042297 | -0.0031402 | -0.001175 | -0.012512 | 0.00058097 | 0.062042 | 0.06169 | -0.01141 | 0.0022687 | -0.00032051 | -0.004578 | 62.6816 | -59.8068 | 62.709 | -59.642 | -59.9899 | 0.032043 | 0.009155 | 62.6587 | -59.7565 | 62.6999 | -59.7885 | -59.8984 | -59.729 | -0.096131 | -0.082397 | -0.054932 | 0.068664 | 59.7427 | -0.27924 | 59.8389 | -0.1831 | -0.045777 | -0.10529 | -0.064087 | -0.07782 | -0.018311 | -0.18768 | 0.027466 | -0.14191 | 0.16479 | 122.5159 | -0.032043 | 122.4564 | 122.4884 | 122.4152 | 122.3923 | 122.3694 | -122.5708 | -122.5204 | 122.4197 | 122.4106 | 59.7061 | 59.7198
446.7656 | 122.5845 | -59.7473 | 62.7182 | -0.086899 | 0.0023391 | 0.063521 | 0.087276 | 0.00059812 | -0.0018586 | -0.0026704 | -0.070496 | 0.00079477 | 0.066101 | 0.06404 | -0.0094869 | 0.0020551 | 0.0011749 | 0.022888 | 62.6587 | -59.7748 | 62.7411 | -59.5963 | -59.967 | 0.022888 | 0.059509 | 62.6495 | -59.761 | 62.7457 | -59.7427 | -59.8251 | -59.7519 | -0.027466 | -0.05951 | 0.022888 | 0.15106 | 59.7702 | -0.21973 | 59.7977 | -0.19226 | -0.013733 | -0.068665 | 0.027466 | 0.004577 | -0.004578 | -0.07782 | 0.009155 | -0.064087 | 0.17853 | 122.5159 | 0.01831 | 122.5067 | 122.4335 | 122.4106 | 122.406 | 122.3969 | -122.493 | -122.4792 | 122.4884 | 122.493 | 59.7702 | 59.8068
447.7656 | 122.6303 | -59.729 | 62.7686 | -0.033493 | 0.0014847 | 0.062666 | 0.086208 | -0.0032471 | -0.0046356 | -0.0030976 | 0.024109 | -5.9826e-05 | 0.066315 | 0.059981 | -0.0090597 | -0.0013629 | 0.0026703 | 0.054932 | 62.6678 | -59.7565 | 62.7502 | -59.5596 | -59.9304 | 0.07782 | 0.073242 | 62.6541 | -59.7427 | 62.7319 | -59.761 | -59.8663 | -59.7107 | -0.027466 | -0.10071 | -0.018311 | 0.16937 | 59.8068 | -0.20142 | 59.8343 | -0.17395 | -0.013733 | -0.11444 | -0.036621 | -0.032043 | 0.018311 | -0.13733 | 0.032044 | -0.1236 | 0.19684 | 122.5067 | -0.01831 | 122.4747 | 122.4243 | 122.3969 | 122.3969 | 122.3831 | -122.525 | -122.5113 | 122.4792 | 122.4609 | 59.7839 | 59.8022
448.7656 | 122.7539 | -59.697 | 62.7457 | -0.033493 | 0.0012711 | 0.062025 | 0.084499 | 0.0018799 | -0.0024994 | 0.00010684 | 0.045471 | -0.0017688 | 0.063538 | 0.057631 | -0.010982 | 0.00034613 | 0.0020295 | 0.064087 | 62.645 | -59.7153 | 62.796 | -59.4955 | -59.8755 | 0.11902 | 0.12817 | 62.5992 | -59.7336 | 62.8143 | -59.6603 | -59.761 | -59.6237 | -0.018311 | -0.10071 | 0.050354 | 0.20142 | 59.816 | -0.17853 | 59.8343 | -0.16022 | -0.036622 | -0.14648 | 0.068664 | 0.036621 | 0.073242 | -0.064087 | 0.10986 | -0.027465 | 0.21973 | 122.5113 | 0.073243 | 122.5479 | 122.3602 | 122.3328 | 122.3419 | 122.2961 | -122.4609 | -122.4792 | 122.493 | 122.5113 | 59.761 | 59.8251
449.7656 | 122.644 | -59.7336 | 62.7869 | -0.079269 | 0.00084388 | 0.061598 | 0.088771 | 0.0027343 | -0.0029266 | -0.002884 | 0.079041 | -0.00048703 | 0.065888 | 0.060408 | -0.0097007 | 0.00055973 | 0.0026703 | -0.018311 | 62.6862 | -59.7794 | 62.6816 | -59.6329 | -59.9991 | 0.059509 | -0.13733 | 62.6816 | -59.7519 | 62.6953 | -59.7885 | -59.9442 | -59.7427 | -0.045776 | -0.10071 | -0.10529 | 0.10071 | 59.7931 | -0.2655 | 59.8389 | -0.21973 | -0.01831 | -0.10529 | -0.091553 | -0.054931 | -0.009155 | -0.21057 | 0.009155 | -0.19226 | 0.14648 | 122.4609 | -0.036621 | 122.4472 | 122.4655 | 122.4335 | 122.4197 | 122.4152 | -122.5662 | -122.5388 | 122.4152 | 122.4289 | 59.7153 | 59.5963
450.7656 | 122.6532 | -59.7198 | 62.7594 | -0.033493 | 0.0012711 | 0.060957 | 0.08813 | 0.0025207 | -0.0022858 | -0.0013886 | -0.021667 | 0.00079477 | 0.065674 | 0.063613 | -0.0090597 | 0.0014141 | 0.0033111 | 0.013733 | 62.6999 | -59.7931 | 62.6816 | -59.642 | -60.0128 | 0.018311 | 0.013733 | 62.6678 | -59.7702 | 62.709 | -59.7931 | -59.8846 | -59.7244 | -0.073242 | -0.059509 | -0.077819 | 0.07782 | 59.7382 | -0.29297 | 59.8114 | -0.21973 | -0.050354 | -0.091552 | -0.050354 | -0.073242 | -0.004577 | -0.16479 | 0.045777 | -0.11444 | 0.15106 | 122.4747 | -0.022888 | 122.4792 | 122.493 | 122.4381 | 122.4197 | 122.3877 | -122.5525 | -122.5296 | 122.4014 | 122.4289 | 59.7336 | 59.7336
451.7656 | 122.6166 | -59.7473 | 62.7319 | -0.079269 | -1.0718e-05 | 0.063734 | 0.089198 | 0.0027343 | -0.0037812 | -0.0016022 | -0.097961 | 0.0010084 | 0.066956 | 0.060408 | -0.010555 | 0.0033367 | -0.0022431 | -0.032043 | 62.6266 | -59.816 | 62.6724 | -59.6695 | -60.0449 | -0.073242 | -0.086975 | 62.6312 | -59.761 | 62.6862 | -59.8343 | -59.9487 | -59.761 | -0.068665 | -0.10529 | -0.05951 | 0.077819 | 59.6741 | -0.29755 | 59.7427 | -0.22888 | -0.013733 | -0.10071 | -0.045777 | -0.086976 | -0.013733 | -0.20142 | 0 | -0.18768 | 0.14648 | 122.4884 | -0.073243 | 122.4472 | 122.4426 | 122.3923 | 122.374 | 122.3785 | -122.5479 | -122.493 | 122.4197 | 122.4335 | 59.7153 | 59.6603
452.7656 | 122.6349 | -59.7198 | 62.7731 | -0.079269 | 0.0021255 | 0.06288 | 0.085353 | -0.0023925 | -0.001004 | -0.002243 | 0.011902 | 0.00058097 | 0.06482 | 0.054 | -0.010342 | 0.00055973 | 0.0033111 | 0.027466 | 62.6678 | -59.7702 | 62.7182 | -59.6054 | -59.9762 | 0.064087 | 0.009155 | 62.6678 | -59.761 | 62.6953 | -59.761 | -59.8755 | -59.7244 | -0.050354 | -0.10528 | -0.054931 | 0.11444 | 59.7839 | -0.25635 | 59.8343 | -0.20599 | -0.041198 | -0.10528 | -0.07782 | -0.041198 | -0.004577 | -0.15564 | 0.036621 | -0.11444 | 0.1648 | 122.4884 | 0 | 122.4564 | 122.4381 | 122.4289 | 122.3877 | 122.3877 | -122.5433 | -122.5342 | 122.4381 | 122.4152 | 59.7473 | 59.729
453.7656 | 122.6074 | -59.7061 | 62.7823 | 0.004654 | -0.00043792 | 0.060957 | 0.087062 | -0.0038879 | -0.002713 | 0.0020294 | 0.0027466 | -0.00027343 | 0.065033 | 0.068099 | -0.012905 | 0.0022687 | -0.00074771 | -0.013733 | 62.7136 | -59.761 | 62.6907 | -59.6329 | -60.0311 | 0.018311 | 0.013733 | 62.6541 | -59.761 | 62.7045 | -59.7748 | -59.8755 | -59.7061 | -0.054931 | -0.068665 | -0.091553 | 0.073242 | 59.7244 | -0.32501 | 59.7794 | -0.27008 | -0.054931 | -0.12817 | -0.07782 | -0.068664 | 0 | -0.16937 | 0.054931 | -0.11444 | 0.12817 | 122.4518 | -0.013733 | 122.4655 | 122.4747 | 122.4152 | 122.4197 | 122.3602 | -122.5433 | -122.5433 | 122.3969 | 122.4106 | 59.6924 | 59.7198
454.7656 | 122.6669 | -59.729 | 62.7823 | -0.056381 | 0.00084388 | 0.061171 | 0.089198 | 0.00017092 | -0.0029266 | -0.0020294 | -0.04303 | 0.00036737 | 0.065888 | 0.062758 | -0.011196 | 0.0026959 | 0.0030975 | 0 | 62.677 | -59.7931 | 62.6862 | -59.6512 | -59.9899 | 0.027466 | 0.013733 | 62.6724 | -59.7427 | 62.709 | -59.7519 | -59.8801 | -59.7061 | -0.064087 | -0.10529 | -0.096131 | 0.07782 | 59.7565 | -0.26092 | 59.8206 | -0.19684 | -0.013733 | -0.10986 | -0.073243 | -0.022888 | 0.022888 | -0.15106 | 0.036621 | -0.13733 | 0.14191 | 122.4792 | -0.009155 | 122.4518 | 122.4701 | 122.4152 | 122.406 | 122.4014 | -122.5754 | -122.525 | 122.4152 | 122.438 | 59.729 | 59.7427
455.7656 | 122.7173 | -59.6649 | 62.7411 | -0.10216 | 0.0016983 | 0.061812 | 0.085353 | -0.0015381 | -0.0035674 | -0.0033112 | 0.030212 | 0.001222 | 0.061615 | 0.056349 | -0.010982 | 0.0016277 | -0.00010671 | 0.073242 | 62.6358 | -59.729 | 62.8006 | -59.4955 | -59.8846 | 0.13275 | 0.13275 | 62.6312 | -59.7061 | 62.8052 | -59.6603 | -59.7656 | -59.6191 | -0.064087 | -0.10529 | 0.059509 | 0.16937 | 59.7977 | -0.21973 | 59.8618 | -0.15564 | -0.041199 | -0.10986 | 0.064087 | 0.004578 | 0.045776 | -0.10071 | 0.086975 | -0.059509 | 0.23346 | 122.5296 | 0.045777 | 122.5113 | 122.3648 | 122.3373 | 122.3007 | 122.2961 | -122.4701 | -122.4472 | 122.4655 | 122.4701 | 59.7382 | 59.7977
456.7656 | 122.644 | -59.7244 | 62.7411 | -0.056381 | 0.00020288 | 0.062025 | 0.088344 | 0.0020935 | -0.0003632 | 0.00096124 | -0.085754 | 0.001222 | 0.065247 | 0.060836 | -0.011196 | 0.0039777 | -0.00032051 | -0.004578 | 62.645 | -59.8251 | 62.7182 | -59.6237 | -60.022 | -0.032043 | 0 | 62.645 | -59.761 | 62.7182 | -59.7794 | -59.9121 | -59.729 | -0.10071 | -0.096131 | -0.022888 | 0.10071 | 59.6924 | -0.29755 | 59.7931 | -0.19684 | -0.036621 | -0.096131 | -0.022888 | -0.054932 | -0.004578 | -0.18768 | 0.032043 | -0.15106 | 0.20142 | 122.5433 | -0.018311 | 122.4792 | 122.4701 | 122.406 | 122.3694 | 122.3694 | -122.5662 | -122.5021 | 122.4426 | 122.4426 | 59.7198 | 59.7244
457.7656 | 122.644 | -59.7473 | 62.764 | -0.048752 | -0.00022432 | 0.061812 | 0.08578 | -0.0030335 | -0.0022858 | 0.00053404 | -0.015564 | 0.00015377 | 0.064179 | 0.067458 | -0.010982 | 0.00055973 | 0.00010689 | 0.022888 | 62.6999 | -59.7748 | 62.6862 | -59.6283 | -60.0037 | 0.041199 | -0.027466 | 62.6404 | -59.7198 | 62.7274 | -59.8114 | -59.8755 | -59.7198 | -0.027466 | -0.064087 | -0.07782 | 0.11902 | 59.7885 | -0.25635 | 59.816 | -0.22888 | 0.027465 | -0.1236 | -0.036621 | -0.064087 | 0.027465 | -0.12817 | 0 | -0.15564 | 0.14648 | 122.4609 | -0.091552 | 122.4472 | 122.4747 | 122.3602 | 122.4472 | 122.3877 | -122.5388 | -122.4838 | 122.4335 | 122.4747 | 59.7702 | 59.7198
458.7656 | 122.6486 | -59.7336 | 62.7777 | -0.025863 | 0.00084388 | 0.063948 | 0.086421 | 0.0010253 | -0.0048492 | -0.0020294 | -0.012512 | 0.0016492 | 0.065674 | 0.061904 | -0.0092733 | 0.0020551 | -0.00010671 | 0.013733 | 62.6953 | -59.7748 | 62.677 | -59.6466 | -60.0174 | 0.032043 | 0.009155 | 62.6633 | -59.7519 | 62.7045 | -59.7794 | -59.8755 | -59.7153 | -0.041198 | -0.082398 | -0.10071 | 0.086976 | 59.7656 | -0.28381 | 59.8068 | -0.24262 | -0.01831 | -0.11444 | -0.073242 | -0.045776 | 0.018311 | -0.14191 | 0.036621 | -0.1236 | 0.12817 | 122.4518 | -0.027466 | 122.4564 | 122.4701 | 122.4152 | 122.4289 | 122.3969 | -122.5525 | -122.5296 | 122.4106 | 122.4381 | 59.7473 | 59.7427
459.7656 | 122.7219 | -59.7061 | 62.7457 | -0.12505 | 0.0016983 | 0.062453 | 0.085139 | -0.0017517 | -0.0005768 | -0.0018158 | 0.039368 | 0.001222 | 0.06546 | 0.064894 | -0.010982 | 0.0031231 | 0.00010689 | 0.064087 | 62.6312 | -59.7427 | 62.7823 | -59.5322 | -59.8938 | 0.10529 | 0.11902 | 62.6221 | -59.7153 | 62.7686 | -59.697 | -59.8114 | -59.6329 | -0.036621 | -0.11444 | 0.036621 | 0.17395 | 59.8114 | -0.18768 | 59.848 | -0.15106 | -0.009155 | -0.1236 | 0.022888 | 0.009156 | 0.073242 | -0.10528 | 0.082397 | -0.09613 | 0.21057 | 122.525 | 0.018311 | 122.4838 | 122.374 | 122.3373 | 122.3373 | 122.3282 | -122.4884 | -122.4609 | 122.4884 | 122.4747 | 59.7702 | 59.8251
460.7656 | 122.6349 | -59.7244 | 62.7869 | -0.048752 | 0.0025529 | 0.061812 | 0.087276 | 0.0018799 | -0.0029266 | -0.0035248 | -0.0094604 | -0.00027343 | 0.063751 | 0.059127 | -0.010555 | 0.00034613 | 0.0026703 | 0.036621 | 62.6724 | -59.7656 | 62.6999 | -59.5871 | -59.967 | 0.050354 | 0.054932 | 62.6816 | -59.7473 | 62.6953 | -59.7702 | -59.8709 | -59.7336 | -0.041199 | -0.11444 | -0.086975 | 0.13733 | 59.7748 | -0.24262 | 59.816 | -0.20142 | -0.022888 | -0.10529 | -0.091553 | -0.045777 | -0.009156 | -0.14648 | 0.013732 | -0.1236 | 0.17853 | 122.4655 | -0.022889 | 122.4426 | 122.438 | 122.4289 | 122.3969 | 122.406 | -122.5525 | -122.5342 | 122.4243 | 122.4197 | 59.761 | 59.7794
461.7656 | 122.6624 | -59.7519 | 62.7365 | -0.06401 | 0.0019119 | 0.063521 | 0.085994 | 0.0038025 | 0.0015594 | 0.00010684 | -0.097961 | 0.00036737 | 0.06482 | 0.065535 | -0.01141 | 0.0024823 | -0.0022431 | -0.022888 | 62.6541 | -59.7977 | 62.6862 | -59.6558 | -60.0311 | -0.059509 | -0.045776 | 62.6358 | -59.761 | 62.6999 | -59.816 | -59.9213 | -59.7473 | -0.045776 | -0.082397 | -0.050354 | 0.09613 | 59.6924 | -0.27924 | 59.7382 | -0.23346 | -0.009155 | -0.10071 | -0.036621 | -0.064087 | 0.004578 | -0.16937 | 0.013733 | -0.16022 | 0.14191 | 122.4838 | -0.054932 | 122.4609 | 122.4518 | 122.3969 | 122.406 | 122.3877 | -122.5342 | -122.4976 | 122.438 | 122.4518 | 59.729 | 59.7061
462.7656 | 122.6349 | -59.7198 | 62.7594 | -0.07164 | 0.0010575 | 0.064375 | 0.085353 | -0.0026063 | -0.0024994 | -0.00053396 | -0.0094604 | 0.00079477 | 0.064392 | 0.059127 | -0.0071371 | 0.0022687 | -0.0024567 | 0.027466 | 62.7228 | -59.7198 | 62.6953 | -59.7107 | -59.9945 | 0.041199 | 0.004578 | 62.6724 | -59.761 | 62.6907 | -59.7931 | -59.8984 | -59.7107 | 0 | -0.036621 | -0.064087 | 0.009156 | 59.761 | -0.27466 | 59.761 | -0.27466 | -0.041198 | -0.086975 | -0.068664 | -0.073242 | 0.009156 | -0.17853 | 0.050354 | -0.13733 | 0.009156 | 122.4152 | -0.032044 | 122.4518 | 122.4426 | 122.4335 | 122.4426 | 122.3923 | -122.4792 | -122.5204 | 122.4152 | 122.4106 | 59.7473 | 59.7244
463.7656 | 122.7173 | -59.7061 | 62.7365 | -0.1403 | 0.0021255 | 0.06288 | 0.086421 | -4.2682e-05 | 6.4004e-05 | -0.0026704 | 0.036316 | 0.00079477 | 0.065247 | 0.060622 | -0.011623 | 0.0022687 | 0.00074769 | 0.059509 | 62.6495 | -59.7473 | 62.796 | -59.5093 | -59.8938 | 0.11444 | 0.14648 | 62.6129 | -59.7382 | 62.7869 | -59.6558 | -59.7702 | -59.61 | -0.041198 | -0.086975 | 0.05951 | 0.19684 | 59.8206 | -0.18768 | 59.8618 | -0.14648 | -0.032043 | -0.1236 | 0.050354 | 0.050354 | 0.096131 | -0.064087 | 0.12817 | -0.032044 | 0.23804 | 122.5433 | 0.082397 | 122.525 | 122.3969 | 122.3511 | 122.3557 | 122.319 | -122.4838 | -122.4747 | 122.5021 | 122.493 | 59.7656 | 59.8526
464.7656 | 122.6486 | -59.697 | 62.7823 | -0.07164 | -0.00043792 | 0.063948 | 0.087703 | -0.00046988 | -0.0020722 | -0.0037384 | 0.0027466 | -5.9826e-05 | 0.066529 | 0.064681 | -0.011623 | 0.0012005 | 0.0013885 | 0.050354 | 62.645 | -59.7473 | 62.7365 | -59.5642 | -59.9487 | 0.082397 | 0.073242 | 62.6541 | -59.7473 | 62.7136 | -59.7427 | -59.8389 | -59.6878 | -0.050354 | -0.13733 | -0.045777 | 0.13275 | 59.7794 | -0.25177 | 59.8297 | -0.20142 | -0.050354 | -0.12817 | -0.068665 | -0.045777 | 0.009155 | -0.14191 | 0.059509 | -0.091553 | 0.18311 | 122.4838 | 0.004577 | 122.4609 | 122.3923 | 122.4014 | 122.3419 | 122.3511 | -122.5296 | -122.5296 | 122.4335 | 122.4106 | 59.7473 | 59.7702
465.7656 | 122.6669 | -59.697 | 62.7731 | -0.018234 | -0.0012923 | 0.062239 | 0.087917 | -0.00046988 | -0.0022858 | -0.00010676 | -0.049133 | 0.00229 | 0.065033 | 0.058913 | -0.0094869 | 0.0018413 | -0.00096131 | 0.022888 | 62.677 | -59.7702 | 62.6999 | -59.642 | -59.9991 | 0.032043 | 0.004578 | 62.6587 | -59.7519 | 62.7045 | -59.7702 | -59.8801 | -59.697 | -0.073243 | -0.09613 | -0.073242 | 0.054931 | 59.729 | -0.30212 | 59.8022 | -0.22888 | -0.054932 | -0.11444 | -0.068664 | -0.073243 | 0 | -0.18311 | 0.054932 | -0.12817 | 0.12817 | 122.4701 | -0.018311 | 122.4564 | 122.4472 | 122.4106 | 122.374 | 122.3557 | -122.5433 | -122.525 | 122.3969 | 122.4014 | 59.7198 | 59.7015
466.7812 | 122.7402 | -59.7153 | 62.6953 | -0.086899 | 0.0016983 | 0.063307 | 0.08578 | -0.00068368 | -0.0031402 | -0.00032036 | 0.054627 | -0.00070063 | 0.066315 | 0.06938 | -0.010769 | -0.0013629 | -0.0013885 | -0.018311 | 62.6312 | -59.7656 | 62.7182 | -59.5917 | -59.9533 | 0.009155 | 0 | 62.5946 | -59.7565 | 62.764 | -59.7107 | -59.8114 | -59.6466 | -0.050354 | -0.064086 | 0.022889 | 0.1236 | 59.7244 | -0.23804 | 59.7748 | -0.18768 | -0.041199 | -0.10071 | 0.068665 | 0.004578 | 0.068665 | -0.09613 | 0.10986 | -0.054931 | 0.17395 | 122.4838 | 0.045777 | 122.5204 | 122.3969 | 122.3511 | 122.3465 | 122.3099 | -122.4609 | -122.4518 | 122.4335 | 122.4792 | 59.697 | 59.7153
467.7656 | 122.6944 | -59.7107 | 62.7319 | 0.027542 | -0.0021469 | 0.062666 | 0.087489 | -0.0015381 | -0.0005768 | 0.0016022 | -0.076599 | 0.0016492 | 0.064606 | 0.066603 | -0.01141 | 0.0029095 | 0.00096129 | 0.041199 | 62.6907 | -59.7839 | 62.7365 | -59.6146 | -59.9716 | 0.032043 | 0.059509 | 62.6404 | -59.7702 | 62.7594 | -59.7427 | -59.8526 | -59.6695 | -0.073243 | -0.041199 | 0.004577 | 0.09613 | 59.7427 | -0.26093 | 59.816 | -0.18768 | -0.05951 | -0.091553 | 0.027465 | -0.032044 | 0.041198 | -0.14191 | 0.10071 | -0.082397 | 0.16937 | 122.5204 | 0.027466 | 122.5296 | 122.4747 | 122.4106 | 122.4014 | 122.3511 | -122.5159 | -122.5021 | 122.4472 | 122.4701 | 59.7519 | 59.7702
468.7656 | 122.6578 | -59.729 | 62.796 | -0.018234 | -0.0023605 | 0.062453 | 0.085139 | -0.00089728 | -0.0052764 | -0.00053396 | -0.027771 | 0.0018628 | 0.066101 | 0.060195 | -0.011196 | -0.0017901 | -0.00053411 | 0 | 62.7045 | -59.7839 | 62.6678 | -59.8434 | -60.1639 | 0.07782 | 0.009155 | 62.6404 | -59.7702 | 62.709 | -59.7794 | -59.8572 | -59.7244 | -0.054932 | -0.091553 | -0.12817 | -0.11444 | 59.8068 | -0.43487 | 59.8618 | -0.37994 | -0.041199 | -0.15564 | -0.086976 | -0.050354 | 0.004578 | -0.12817 | 0.045777 | -0.086975 | -0.059509 | 122.4518 | -0.009155 | 122.4792 | 122.4884 | 122.4106 | 122.4335 | 122.3694 | -122.58 | -122.5662 | 122.3969 | 122.438 | 59.729 | 59.7382
469.7656 | 122.644 | -59.7061 | 62.7777 | -0.06401 | -0.00043792 | 0.063094 | 0.088344 | -0.0038879 | -0.0052764 | -0.0035248 | -0.021667 | 0.00229 | 0.065247 | 0.059981 | -0.010555 | 0.0022687 | 0.0024567 | -0.004578 | 62.6633 | -59.7656 | 62.7182 | -59.8297 | -60.2371 | 0.041199 | -0.013733 | 62.6633 | -59.7885 | 62.6953 | -59.7839 | -59.8663 | -59.697 | -0.059509 | -0.11444 | -0.059509 | -0.1236 | 59.7473 | -0.53101 | 59.8068 | -0.4715 | -0.082397 | -0.11444 | -0.082398 | -0.07782 | 0.009156 | -0.16022 | 0.091553 | -0.07782 | -0.064087 | 122.4838 | 0.004577 | 122.4838 | 122.4289 | 122.4518 | 122.3694 | 122.3694 | -122.5433 | -122.5662 | 122.4243 | 122.4014 | 59.7015 | 59.6924
470.7656 | 122.6532 | -59.7244 | 62.7731 | -0.041122 | -0.00022432 | 0.063094 | 0.086208 | -0.0015381 | -0.0020722 | -0.00053396 | -0.036926 | 0.0010084 | 0.063965 | 0.065535 | -0.013332 | 0.0022687 | -0.0022431 | 0.009155 | 62.6907 | -59.7839 | 62.6816 | -59.6512 | -59.9991 | 0.022888 | 0.013733 | 62.6633 | -59.7656 | 62.7182 | -59.7748 | -59.8984 | -59.7015 | -0.05951 | -0.082397 | -0.091552 | 0.073242 | 59.7473 | -0.27466 | 59.8068 | -0.21515 | -0.041199 | -0.10986 | -0.054931 | -0.050354 | 0.022888 | -0.17395 | 0.064087 | -0.13275 | 0.13275 | 122.4655 | -0.009155 | 122.4838 | 122.4747 | 122.4289 | 122.4152 | 122.3877 | -122.5571 | -122.5388 | 122.406 | 122.4426 | 59.7336 | 59.7382
471.7656 | 122.7448 | -59.7244 | 62.6999 | -0.094528 | 0.0012711 | 0.063521 | 0.086208 | -4.2682e-05 | -0.0037812 | -0.00074776 | -0.015564 | -0.00091423 | 0.062683 | 0.059127 | -0.012478 | 0.0018413 | 0.0022431 | -0.027466 | 62.5992 | -59.7839 | 62.7502 | -59.5505 | -59.9579 | -0.022888 | 0.004578 | 62.6129 | -59.7702 | 62.7686 | -59.7015 | -59.816 | -59.642 | -0.05951 | -0.10071 | 0.050354 | 0.17395 | 59.7015 | -0.23346 | 59.761 | -0.17395 | -0.045777 | -0.086975 | 0.068665 | 0.022888 | 0.082397 | -0.091553 | 0.12817 | -0.045776 | 0.23346 | 122.5342 | 0.068665 | 122.5388 | 122.3831 | 122.3831 | 122.3236 | 122.3373 | -122.4838 | -122.4701 | 122.4747 | 122.493 | 59.697 | 59.729
472.7656 | 122.6303 | -59.7244 | 62.7457 | 0.019913 | 0.00041648 | 0.064162 | 0.086848 | -0.0019653 | -0.0039948 | -0.0033112 | -0.097961 | -0.001128 | 0.065247 | 0.062117 | -0.0092733 | 0.0026959 | -0.0030975 | -0.004578 | 62.6907 | -59.7656 | 62.6816 | -59.5734 | -59.7061 | -0.027466 | 0.07782 | 62.6541 | -59.7656 | 62.6816 | -59.7702 | -59.8892 | -59.6878 | -0.041199 | -0.054932 | -0.064087 | 0.15106 | 59.697 | 0.01831 | 59.7382 | 0.059509 | -0.041199 | -0.091553 | -0.064087 | -0.045777 | 0.036621 | -0.16479 | 0.07782 | -0.1236 | 0.19226 | 122.4472 | -0.004578 | 122.4472 | 122.4564 | 122.4197 | 122.4152 | 122.3785 | -122.5113 | -122.5113 | 122.406 | 122.406 | 59.7198 | 59.8022
473.7656 | 122.6715 | -59.7198 | 62.7457 | 0.004654 | 0.00063028 | 0.062025 | 0.086848 | -0.00046988 | -0.0003632 | 0.00074764 | -0.046081 | 0.00036737 | 0.06546 | 0.065962 | -0.0088461 | 0.0016277 | -0.00032051 | 0.013733 | 62.6907 | -59.7839 | 62.7274 | -59.6008 | -59.9899 | 0.032043 | 0.032043 | 62.6541 | -59.7427 | 62.7548 | -59.7519 | -59.8709 | -59.6878 | -0.064087 | -0.054932 | -0.018311 | 0.11902 | 59.7519 | -0.27008 | 59.816 | -0.20599 | -0.022888 | -0.091553 | 0.009155 | -0.032043 | 0.032044 | -0.15106 | 0.054932 | -0.12817 | 0.18311 | 122.5113 | -0.009155 | 122.4976 | 122.4747 | 122.3969 | 122.4106 | 122.374 | -122.5296 | -122.4884 | 122.4472 | 122.4747 | 59.7336 | 59.7519
474.7656 | 122.6624 | -59.7015 | 62.7319 | -0.056381 | 0.0014847 | 0.062453 | 0.088771 | 0.00017092 | -0.002713 | -0.0030976 | -0.06134 | 0.0016492 | 0.067383 | 0.06169 | -0.011837 | 0.0012005 | -0.0013885 | 0.027466 | 62.6816 | -59.7702 | 62.7228 | -59.6054 | -59.9808 | 0.018311 | 0.045776 | 62.6495 | -59.7702 | 62.7411 | -59.729 | -59.8709 | -59.6741 | -0.068665 | -0.050354 | -0.009156 | 0.09613 | 59.7198 | -0.27924 | 59.7885 | -0.21057 | -0.068665 | -0.082398 | 0.009155 | -0.027466 | 0.027466 | -0.16937 | 0.096131 | -0.10071 | 0.1648 | 122.493 | 0.041199 | 122.5113 | 122.4518 | 122.4197 | 122.3831 | 122.3511 | -122.5021 | -122.5021 | 122.4243 | 122.4426 | 59.729 | 59.7473
475.7656 | 122.6715 | -59.7382 | 62.7365 | -0.086899 | 0.00020288 | 0.063948 | 0.088557 | 0.0046569 | -0.001004 | -0.00074776 | -0.073547 | 0.00079477 | 0.066101 | 0.064894 | -0.010342 | 0.0018413 | -0.00010671 | -0.004578 | 62.645 | -59.7931 | 62.7045 | -59.61 | -60.0266 | -0.050354 | -0.036621 | 62.645 | -59.7748 | 62.7045 | -59.7931 | -59.9213 | -59.729 | -0.054932 | -0.091553 | -0.032043 | 0.12817 | 59.6878 | -0.28839 | 59.7427 | -0.23346 | -0.036621 | -0.091553 | -0.032043 | -0.054932 | 0.009155 | -0.18311 | 0.045776 | -0.14648 | 0.18311 | 122.4976 | -0.018311 | 122.4792 | 122.438 | 122.4197 | 122.3831 | 122.3831 | -122.5296 | -122.5113 | 122.4426 | 122.4426 | 59.7336 | 59.7015
476.7656 | 122.731 | -59.6878 | 62.6816 | -0.086899 | -0.00065152 | 0.065016 | 0.087062 | 0.0027343 | -0.0007904 | -0.0018158 | 0.0088502 | -0.002196 | 0.063111 | 0.058699 | -0.011837 | 0.0037641 | -0.00096131 | -0.027466 | 62.6221 | -59.761 | 62.7319 | -59.5596 | -59.9579 | -0.022888 | -0.004578 | 62.5717 | -59.7748 | 62.7777 | -59.7107 | -59.816 | -59.6237 | -0.073242 | -0.05951 | 0.050354 | 0.12817 | 59.6649 | -0.27008 | 59.7382 | -0.19684 | -0.086975 | -0.10986 | 0.09613 | -0.022888 | 0.064087 | -0.12817 | 0.15106 | -0.041199 | 0.20142 | 122.493 | 0.064087 | 122.5525 | 122.3831 | 122.3465 | 122.3099 | 122.2595 | -122.4426 | -122.4564 | 122.4197 | 122.4655 | 59.6603 | 59.6832
477.7656 | 122.6532 | -59.7153 | 62.7411 | -0.018234 | 0.0010575 | 0.062453 | 0.087062 | 0.0010253 | -0.0033538 | -0.00010676 | -0.015564 | 0.00036737 | 0.066529 | 0.059767 | -0.011623 | 0.0035503 | -0.00096131 | -0.013733 | 62.6953 | -59.7794 | 62.6862 | -59.642 | -59.9945 | 0.022888 | 0 | 62.6404 | -59.7519 | 62.6999 | -59.7656 | -59.8846 | -59.7015 | -0.064087 | -0.045777 | -0.054932 | 0.073242 | 59.7382 | -0.27924 | 59.8022 | -0.21515 | -0.036621 | -0.10071 | -0.041199 | -0.050354 | 0.013733 | -0.16937 | 0.050354 | -0.13275 | 0.13733 | 122.4655 | -0.013733 | 122.4518 | 122.4747 | 122.3923 | 122.4106 | 122.3557 | -122.5204 | -122.493 | 122.4014 | 122.4152 | 59.7015 | 59.7153
478.7656 | 122.6578 | -59.729 | 62.7182 | -0.094528 | -0.00065152 | 0.064589 | 0.086421 | 0.0020935 | -0.0005768 | -0.0024566 | -0.04303 | 0.00079477 | 0.064179 | 0.06169 | -0.011623 | 0.0016277 | -0.0030975 | 0.013733 | 62.6862 | -59.7977 | 62.6907 | -59.5825 | -59.9396 | 0.013733 | 0.059509 | 62.6266 | -59.7794 | 62.7548 | -59.7565 | -59.8618 | -59.6695 | -0.068664 | -0.032044 | -0.027466 | 0.14648 | 59.7427 | -0.21057 | 59.8114 | -0.14191 | -0.050354 | -0.091553 | 0.036621 | -0.027466 | 0.059509 | -0.13275 | 0.10986 | -0.082397 | 0.21515 | 122.4884 | 0.022888 | 122.5342 | 122.4838 | 122.406 | 122.4152 | 122.3557 | -122.5159 | -122.4976 | 122.4197 | 122.4838 | 59.7427 | 59.7885
479.7656 | 122.6624 | -59.7244 | 62.7777 | -0.018234 | -0.00022432 | 0.06288 | 0.088557 | -0.0017517 | -0.0020722 | -0.00074776 | -0.0033568 | 0.001222 | 0.064606 | 0.062972 | -0.0092733 | 0.0018413 | -0.0037383 | -0.004578 | 62.6907 | -59.7885 | 62.6724 | -59.6512 | -60.0037 | 0.032043 | 0.013733 | 62.6724 | -59.7519 | 62.7045 | -59.7794 | -59.8846 | -59.7107 | -0.064087 | -0.086975 | -0.10529 | 0.073242 | 59.7565 | -0.27924 | 59.8206 | -0.21515 | -0.027466 | -0.10529 | -0.073242 | -0.054932 | 0.013733 | -0.16022 | 0.041199 | -0.13275 | 0.13733 | 122.4609 | -0.027466 | 122.4564 | 122.4792 | 122.4243 | 122.4152 | 122.3969 | -122.5662 | -122.5296 | 122.3969 | 122.4289 | 59.7198 | 59.7382
480.7656 | 122.6852 | -59.7198 | 62.7594 | -0.07164 | 0.00020288 | 0.063734 | 0.087917 | 0.0010253 | -0.0020722 | 0.0013886 | -0.021667 | 0.0010084 | 0.065247 | 0.059127 | -0.010982 | 0.00013253 | -0.0026703 | 0.009155 | 62.6678 | -59.7702 | 62.6999 | -59.6191 | -59.9762 | 0.027466 | 0.032043 | 62.6587 | -59.7519 | 62.7411 | -59.7382 | -59.8434 | -59.6878 | -0.050354 | -0.091552 | -0.059509 | 0.10071 | 59.7473 | -0.25635 | 59.7977 | -0.20599 | -0.032043 | -0.10071 | -0.01831 | -0.01831 | 0.032044 | -0.1236 | 0.064087 | -0.091553 | 0.15106 | 122.4701 | 0.013733 | 122.493 | 122.4381 | 122.4106 | 122.3877 | 122.3785 | -122.5296 | -122.5113 | 122.4197 | 122.4609 | 59.729 | 59.7519
481.7656 | 122.699 | -59.7198 | 62.709 | -0.16319 | 0.0027665 | 0.06288 | 0.086635 | -0.00046988 | -0.0003632 | 0.0013886 | 0.0027466 | -0.0017688 | 0.063538 | 0.064467 | -0.010128 | 0.0012005 | 0.0018159 | -0.032043 | 62.6129 | -59.7839 | 62.7457 | -59.5459 | -59.9625 | -0.013733 | 0.004578 | 62.5717 | -59.7473 | 62.764 | -59.7519 | -59.8297 | -59.6649 | -0.064087 | -0.09613 | 0.036622 | 0.17395 | 59.7061 | -0.24261 | 59.7702 | -0.17853 | -0.027465 | -0.13733 | 0.054932 | -0.032043 | 0.054932 | -0.10986 | 0.082397 | -0.082398 | 0.23804 | 122.5296 | -0.004578 | 122.5113 | 122.3969 | 122.319 | 122.3328 | 122.2916 | -122.493 | -122.4564 | 122.4655 | 122.4838 | 59.6878 | 59.7244
482.7656 | 122.7081 | -59.6924 | 62.7548 | -0.025863 | 0.0012711 | 0.061385 | 0.088771 | -0.0043151 | -0.002713 | 0.00010684 | -0.064392 | 0.00015377 | 0.065247 | 0.061263 | -0.011196 | 0.0026959 | -0.0011749 | 0.045776 | 62.6541 | -59.7839 | 62.7182 | -59.6008 | -59.9991 | 0.022888 | 0.086975 | 62.6175 | -59.7794 | 62.7228 | -59.6878 | -59.8709 | -59.6878 | -0.091553 | -0.10071 | -0.036621 | 0.091553 | 59.7153 | -0.3067 | 59.8068 | -0.21515 | -0.086975 | -0.13733 | -0.032044 | 0.004578 | 0.004578 | -0.17853 | 0.091553 | -0.091553 | 0.18311 | 122.5021 | 0.091553 | 122.5021 | 122.4381 | 122.3969 | 122.3465 | 122.3099 | -122.5388 | -122.5342 | 122.4106 | 122.4152 | 59.7382 | 59.7794
483.7656 | 122.6532 | -59.7336 | 62.7228 | -0.07164 | 0.0016983 | 0.063734 | 0.089412 | 0.0035889 | -0.0029266 | 0.00096124 | -0.06134 | 0.0016492 | 0.065033 | 0.062972 | -0.011196 | 0.0026959 | 0.00053409 | -0.032043 | 62.645 | -59.8114 | 62.6999 | -59.6649 | -60.0449 | -0.064087 | -0.064087 | 62.6175 | -59.7702 | 62.6816 | -59.816 | -59.9304 | -59.7382 | -0.077819 | -0.07782 | -0.022888 | 0.068665 | 59.6695 | -0.31128 | 59.7473 | -0.23346 | -0.036621 | -0.10528 | -0.041198 | -0.082397 | -0.004577 | -0.19684 | 0.032044 | -0.16022 | 0.14648 | 122.5113 | -0.045776 | 122.4518 | 122.4564 | 122.3877 | 122.3785 | 122.3511 | -122.5342 | -122.493 | 122.4335 | 122.4152 | 59.7015 | 59.6695
484.7656 | 122.6349 | -59.7198 | 62.7686 | -0.018234 | -0.0025741 | 0.062239 | 0.086421 | 0.0016663 | -0.0012176 | -0.00053396 | 0.018005 | 0.00079477 | 0.063965 | 0.065749 | -0.0090597 | 0.0024823 | -0.0018157 | 0.059509 | 62.7411 | -59.7656 | 62.6678 | -59.6375 | -60.0311 | 0.027466 | 0.013733 | 62.6541 | -59.761 | 62.6907 | -59.7794 | -59.8984 | -59.6878 | -0.045776 | -0.027466 | -0.10071 | 0.082398 | 59.7473 | -0.31128 | 59.7931 | -0.2655 | -0.041198 | -0.11444 | -0.07782 | -0.059509 | 0.032044 | -0.17853 | 0.073242 | -0.13733 | 0.12817 | 122.4335 | -0.018311 | 122.4518 | 122.5067 | 122.4152 | 122.4609 | 122.374 | -122.5342 | -122.5296 | 122.3877 | 122.4106 | 59.7794 | 59.7336
485.7656 | 122.6624 | -59.7198 | 62.7594 | -0.041122 | 0.0010575 | 0.062666 | 0.089625 | 0.0050843 | 6.4004e-05 | -0.0026704 | -0.070496 | -0.00027343 | 0.064606 | 0.063613 | -0.0099143 | 0.0033367 | -0.0022431 | 0.041199 | 62.677 | -59.7885 | 62.6999 | -59.5963 | -59.9716 | 0.032043 | 0.073242 | 62.645 | -59.7336 | 62.7411 | -59.7427 | -59.8572 | -59.6878 | -0.068664 | -0.082397 | -0.059509 | 0.1236 | 59.7519 | -0.25177 | 59.8206 | -0.18311 | -0.013733 | -0.11444 | -0.01831 | -0.022888 | 0.032044 | -0.13733 | 0.045777 | -0.1236 | 0.19226 | 122.4884 | -0.009155 | 122.4747 | 122.4655 | 122.3785 | 122.3969 | 122.3648 | -122.5479 | -122.493 | 122.4197 | 122.4609 | 59.761 | 59.7931
486.7656 | 122.6852 | -59.7015 | 62.709 | -0.086899 | 0.00063028 | 0.064162 | 0.088771 | 0.0010253 | -0.0033538 | -0.002243 | -0.055237 | 0.00036737 | 0.066101 | 0.06169 | -0.010769 | 0.0026959 | 0.0013885 | -0.086975 | 62.6358 | -59.8206 | 62.645 | -59.6649 | -60.0723 | -0.09613 | -0.11902 | 62.5992 | -59.7839 | 62.7228 | -59.7794 | -59.8892 | -59.7061 | -0.11902 | -0.073242 | -0.064087 | 0.036621 | 59.6054 | -0.37079 | 59.7244 | -0.25177 | -0.082398 | -0.10986 | 0.013733 | -0.07782 | -0.004578 | -0.18768 | 0.07782 | -0.10529 | 0.15564 | 122.4655 | 0.004578 | 122.5067 | 122.4564 | 122.3831 | 122.3373 | 122.3007 | -122.5296 | -122.493 | 122.3465 | 122.4243 | 59.6146 | 59.5825
487.7656 | 122.6257 | -59.7153 | 62.7411 | -0.094528 | 0.0021255 | 0.063948 | 0.088344 | -0.00089728 | -0.0014312 | 0.00096124 | -0.055237 | 0.0018628 | 0.065247 | 0.061263 | -0.01141 | 0.0020551 | 0.0011749 | -0.009155 | 62.6633 | -59.7656 | 62.709 | -59.6191 | -60.0128 | -0.013733 | -0.009155 | 62.6266 | -59.761 | 62.709 | -59.7748 | -59.8938 | -59.7198 | -0.050354 | -0.07782 | -0.032044 | 0.09613 | 59.7015 | -0.29755 | 59.7519 | -0.24719 | -0.045776 | -0.11444 | -0.032044 | -0.059509 | -0.004578 | -0.17853 | 0.041198 | -0.13275 | 0.14648 | 122.4747 | -0.013733 | 122.4701 | 122.4289 | 122.3877 | 122.3785 | 122.3419 | -122.5067 | -122.5021 | 122.4243 | 122.4243 | 59.7061 | 59.7061
488.7656 | 122.6807 | -59.7153 | 62.7411 | -0.07164 | 0.00041648 | 0.062239 | 0.087489 | 0.0035889 | -0.0007904 | -0.002884 | -0.012512 | -0.00070063 | 0.063965 | 0.065535 | -0.011196 | 0.00098693 | -0.0020295 | 0.013733 | 62.6816 | -59.7839 | 62.709 | -59.6146 | -59.9808 | 0.013733 | 0.004578 | 62.645 | -59.7336 | 62.7365 | -59.7427 | -59.8526 | -59.6786 | -0.068665 | -0.059509 | -0.032044 | 0.10071 | 59.729 | -0.2655 | 59.7977 | -0.19684 | -0.018311 | -0.096131 | -0.004578 | -0.027466 | 0.036621 | -0.13733 | 0.054932 | -0.11902 | 0.16937 | 122.493 | -0.009155 | 122.4701 | 122.4655 | 122.3785 | 122.3969 | 122.3602 | -122.525 | -122.4747 | 122.4243 | 122.4518 | 59.729 | 59.7198
489.7656 | 122.6761 | -59.7107 | 62.7411 | -0.07164 | 0.0025529 | 0.062666 | 0.088985 | 0.00017092 | -0.001004 | -0.0018158 | -0.039978 | 0.00079477 | 0.066315 | 0.062758 | -0.01141 | 0.00034613 | -0.0022431 | 0.036621 | 62.645 | -59.7931 | 62.7228 | -59.6008 | -59.9716 | 0.022888 | 0.059509 | 62.6358 | -59.7427 | 62.6999 | -59.9396 | -59.7839 | -59.5551 | -0.082398 | -0.096131 | -0.018311 | 0.10986 | 59.7336 | -0.26093 | 59.816 | -0.17853 | -0.032044 | -0.10529 | -0.041199 | -0.22888 | 0.15564 | -0.073243 | 0.18768 | -0.041199 | 0.19226 | 122.5159 | -0.19684 | 122.4426 | 122.438 | 122.3785 | 122.3557 | 122.3465 | -122.5342 | -122.4838 | 122.4335 | 122.4106 | 59.7473 | 59.7702
490.7656 | 122.7264 | -59.6878 | 62.6907 | -0.086899 | 0.0010575 | 0.06288 | 0.087917 | -0.00046988 | -0.0016448 | -0.00074776 | 0.063782 | 0.0014356 | 0.064392 | 0.055709 | -0.010555 | 0.00055973 | -0.00053411 | -0.041199 | 62.6541 | -59.7839 | 62.5809 | -59.642 | -59.9579 | -0.009155 | -0.036621 | 62.5809 | -59.7794 | 62.7228 | -59.7519 | -59.8389 | -59.6558 | -0.096131 | -0.036621 | -0.10986 | 0.045776 | 59.6786 | -0.27008 | 59.7748 | -0.17395 | -0.091553 | -0.10986 | 0.032043 | -0.064087 | 0.032043 | -0.15106 | 0.1236 | -0.059509 | 0.14191 | 122.3648 | 0.027466 | 122.5021 | 122.4381 | 122.3602 | 122.3419 | 122.2687 | -122.4747 | -122.4701 | 122.2687 | 122.4106 | 59.6466 | 59.6512
491.7656 | 122.6669 | -59.7198 | 62.764 | -0.13267 | 0.0031937 | 0.060744 | 0.088771 | 0.00081172 | -0.0012176 | -0.0013886 | -0.070496 | -0.00027343 | 0.065247 | 0.063826 | -0.011623 | 0.0012005 | -0.00032051 | 0.09613 | 62.6678 | -59.7885 | 62.7365 | -59.5871 | -59.9762 | 0.018311 | 0.041199 | 62.6404 | -59.7656 | 62.7365 | -59.7519 | -59.8709 | -59.6924 | -0.068664 | -0.09613 | -0.027466 | 0.13275 | 59.7382 | -0.25635 | 59.8068 | -0.18768 | -0.045776 | -0.1236 | -0.027466 | -0.032043 | 0.027466 | -0.15106 | 0.073242 | -0.10529 | 0.20142 | 122.525 | 0.013733 | 122.5021 | 122.4564 | 122.406 | 122.3877 | 122.3602 | -122.5525 | -122.5296 | 122.4564 | 122.4564 | 59.816 | 59.761
492.7656 | 122.6532 | -59.7153 | 62.7548 | -0.056381 | -0.00043792 | 0.063948 | 0.087062 | 0.00081172 | -0.0014312 | -0.0020294 | -0.012512 | -0.00048703 | 0.06482 | 0.062331 | -0.010769 | 0.0016277 | 0.0018159 | 0.009155 | 62.7045 | -59.7748 | 62.6816 | -59.6329 | -59.9808 | 0.004578 | 0 | 62.6495 | -59.7565 | 62.709 | -59.7656 | -59.8846 | -59.6924 | -0.059509 | -0.050354 | -0.073242 | 0.082397 | 59.7198 | -0.2655 | 59.7794 | -0.20599 | -0.041199 | -0.10529 | -0.045777 | -0.050354 | 0.022888 | -0.16937 | 0.064087 | -0.12817 | 0.14191 | 122.4564 | -0.009155 | 122.4655 | 122.4792 | 122.406 | 122.4197 | 122.3648 | -122.5296 | -122.5113 | 122.3969 | 122.4243 | 59.7244 | 59.7153
493.7656 | 122.612 | -59.7382 | 62.7777 | -0.056381 | 0.0012711 | 0.063948 | 0.087917 | 0.00059812 | -0.0031402 | -0.0033112 | 0.018005 | -0.00091423 | 0.06546 | 0.060622 | -0.011837 | 0.0012005 | -0.0013885 | 0 | 62.6862 | -59.7977 | 62.6724 | -59.6466 | -60.0082 | 0.018311 | -0.004578 | 62.677 | -59.7519 | 62.6953 | -59.7748 | -59.8846 | -59.7061 | -0.059509 | -0.091553 | -0.10529 | 0.091553 | 59.7565 | -0.27008 | 59.816 | -0.21057 | -0.013733 | -0.10071 | -0.082398 | -0.036621 | 0.032043 | -0.14648 | 0.045776 | -0.13275 | 0.15106 | 122.4701 | -0.022888 | 122.4472 | 122.4838 | 122.4289 | 122.4243 | 122.4152 | -122.5754 | -122.5296 | 122.4106 | 122.4335 | 59.7382 | 59.7336
494.7656 | 122.6624 | -59.7015 | 62.7594 | -0.06401 | -0.0025741 | 0.061598 | 0.086635 | 0.0020935 | -0.0029266 | -0.0048066 | -0.018616 | 0.001222 | 0.06546 | 0.065749 | -0.010982 | 0.0029095 | -0.00010671 | 0.022888 | 62.677 | -59.761 | 62.7136 | -59.6237 | -59.9854 | 0.027466 | 0.032043 | 62.6266 | -59.7519 | 62.7411 | -59.7519 | -59.8526 | -59.6878 | -0.059509 | -0.082397 | -0.045776 | 0.07782 | 59.729 | -0.28381 | 59.7885 | -0.22431 | -0.050354 | -0.13275 | -0.01831 | -0.050354 | 0.013733 | -0.15106 | 0.064087 | -0.10071 | 0.13733 | 122.4747 | 0 | 122.493 | 122.438 | 122.3785 | 122.3785 | 122.3282 | -122.5204 | -122.5113 | 122.4152 | 122.4426 | 59.7244 | 59.7336
495.7656 | 122.6761 | -59.7198 | 62.7319 | -0.056381 | 0.0025529 | 0.063521 | 0.088557 | 0.0038025 | 0.0028412 | -0.0035248 | -0.036926 | 0.0035718 | 0.067383 | 0.06169 | -0.010982 | 0.0018413 | -0.00053411 | 0.032043 | 62.677 | -59.7702 | 62.7274 | -59.6054 | -59.9854 | 0.018311 | -0.13275 | 62.59 | -59.7931 | 62.7686 | -59.7336 | -59.8801 | -59.6786 | -0.050354 | -0.054932 | -0.004578 | 0.11444 | 59.7382 | -0.2655 | 59.7885 | -0.21515 | -0.073242 | -0.14191 | 0.036621 | -0.013733 | 0.041199 | -0.16022 | 0.11444 | -0.086975 | 0.1648 | 122.4976 | 0.059509 | 122.5616 | 122.4472 | 122.3831 | 122.3969 | 122.3099 | -122.5021 | -122.525 | 122.4472 | 122.4884 | 59.7519 | 59.5871
496.7656 | 122.6486 | -59.7198 | 62.7548 | 0.019913 | -0.00086512 | 0.062239 | 0.087276 | 0.0025207 | -0.002713 | 0.0020294 | -0.046081 | 0.00229 | 0.065888 | 0.065322 | -0.012051 | 0.0024823 | -0.00096131 | 0 | 62.6907 | -59.7748 | 62.677 | -59.6329 | -60.0128 | 0.009155 | 0.022888 | 62.6495 | -59.7565 | 62.7274 | -59.7336 | -59.8755 | -59.6695 | -0.054931 | -0.064087 | -0.07782 | 0.086975 | 59.729 | -0.29297 | 59.7839 | -0.23804 | -0.036621 | -0.10529 | -0.027466 | -0.013733 | 0.050354 | -0.15564 | 0.086975 | -0.11902 | 0.14191 | 122.4518 | 0.022888 | 122.4838 | 122.4655 | 122.406 | 122.4106 | 122.3694 | -122.5296 | -122.5113 | 122.3969 | 122.4472 | 59.7198 | 59.7427
497.7656 | 122.6303 | -59.7198 | 62.7686 | -0.17082 | -0.0012923 | 0.06053 | 0.089198 | 0.00059812 | -0.0016448 | -0.00074776 | 0.021057 | 0.00036737 | 0.065247 | 0.059554 | -0.0097007 | 0.00034613 | -0.0013885 | 0.036621 | 62.7045 | -59.7977 | 62.6678 | -59.6375 | -60.0128 | 0.022888 | -0.009155 | 62.6587 | -59.7519 | 62.7045 | -59.7702 | -59.8892 | -59.729 | -0.077819 | -0.064087 | -0.10071 | 0.082398 | 59.7427 | -0.29297 | 59.8206 | -0.21515 | -0.032043 | -0.10986 | -0.064087 | -0.050354 | -0.009155 | -0.16937 | 0.022888 | -0.13733 | 0.16022 | 122.4655 | -0.018311 | 122.4564 | 122.5021 | 122.4106 | 122.4243 | 122.3785 | -122.5662 | -122.5204 | 122.3877 | 122.4243 | 59.7565 | 59.7107
498.7656 | 122.6624 | -59.729 | 62.7686 | -0.07164 | -0.00043792 | 0.061385 | 0.089625 | 0.00017092 | -0.004422 | 0.00074764 | 0.0088502 | 0.00015377 | 0.065674 | 0.061476 | -0.010555 | 0.0016277 | -0.0033111 | 0.009155 | 62.6907 | -59.7748 | 62.6724 | -59.6603 | -59.9991 | 0.022888 | 0.018311 | 62.677 | -59.7336 | 62.7136 | -59.761 | -59.8663 | -59.6786 | -0.045776 | -0.07782 | -0.096131 | 0.068665 | 59.7519 | -0.27008 | 59.7977 | -0.2243 | -0.004578 | -0.091553 | -0.054932 | -0.032043 | 0.050354 | -0.13733 | 0.054932 | -0.13275 | 0.11444 | 122.4472 | -0.027465 | 122.4472 | 122.4655 | 122.4106 | 122.4197 | 122.406 | -122.5433 | -122.5021 | 122.4014 | 122.4426 | 59.7382 | 59.7473
499.7656 | 122.6532 | -59.7198 | 62.7502 | -0.041122 | 0.00041648 | 0.063521 | 0.088771 | 0.00081172 | -0.0020722 | 0.00074764 | -0.033874 | 0.0016492 | 0.065247 | 0.062331 | -0.013332 | 0.0026959 | 0.0026703 | 0.009155 | 62.6404 | -59.7885 | 62.709 | -59.5871 | -60.0037 | 0 | 0.054932 | 62.6358 | -59.7473 | 62.7365 | -59.7656 | -59.8709 | -59.6695 | -0.068664 | -0.10986 | -0.041199 | 0.13275 | 59.7198 | -0.28381 | 59.7885 | -0.21515 | -0.027465 | -0.11444 | -0.013733 | -0.045776 | 0.050354 | -0.15106 | 0.077819 | -0.1236 | 0.20142 | 122.4976 | -0.018311 | 122.4838 | 122.4289 | 122.3831 | 122.3602 | 122.3557 | -122.5388 | -122.4976 | 122.4289 | 122.4564 | 59.729 | 59.7748
500.7656 | 122.5937 | -59.7015 | 62.7045 | -0.10979 | 0.0016983 | 0.064162 | 0.086848 | 0.00017092 | -0.0014312 | 0.00010684 | -0.018616 | -5.9826e-05 | 0.065888 | 0.062331 | -0.010982 | 0.0024823 | -0.0011749 | 0.036621 | 62.6678 | -59.761 | 62.7182 | -59.6008 | -59.9533 | 0.054932 | 0.050354 | 62.6175 | -59.7473 | 62.7365 | -59.7336 | -59.8618 | -59.5917 | -0.059509 | -0.036621 | 0.013733 | 0.10071 | 59.7565 | -0.25177 | 59.816 | -0.19226 | -0.045776 | -0.086975 | 0.032043 | -0.032044 | 0.10986 | -0.16022 | 0.15564 | -0.11444 | 0.16022 | 122.4792 | 0.013732 | 122.4838 | 122.4289 | 122.3648 | 122.3694 | 122.319 | -122.4655 | -122.4518 | 122.4197 | 122.438 | 59.7382 | 59.7519
501.7656 | 122.6852 | -59.7198 | 62.7594 | -0.048752 | 0.0025529 | 0.06288 | 0.090053 | 0.0038025 | -0.0012176 | 0.00032044 | -0.04303 | -0.00027343 | 0.063965 | 0.071944 | -0.01141 | -0.00093567 | 0.00053409 | -0.059509 | 62.6541 | -59.8206 | 62.6312 | -59.7153 | -60.1135 | -0.1236 | -0.16479 | 62.6312 | -59.7839 | 62.7777 | -59.6649 | -60.0311 | -59.8251 | -0.10071 | -0.10529 | -0.12817 | 0.004578 | 59.5963 | -0.39368 | 59.697 | -0.29297 | -0.064087 | -0.12817 | 0.018311 | 0.054932 | -0.10528 | -0.31128 | -0.041198 | -0.24719 | 0.10529 | 122.4518 | 0.11902 | 122.5616 | 122.4747 | 122.4152 | 122.374 | 122.3511 | -122.58 | -122.5433 | 122.3511 | 122.4976 | 59.6603 | 59.5551
502.7656 | 122.6715 | -59.7153 | 62.7502 | -0.086899 | 0.00041648 | 0.06288 | 0.086848 | 0.00081172 | -0.0016448 | -0.001175 | -0.024719 | -0.00091423 | 0.065674 | 0.054213 | -0.011837 | 0.0014141 | 0.00074769 | 0.032043 | 62.6541 | -59.7977 | 62.7136 | -59.5917 | -59.9762 | 0.045776 | 0.064087 | 62.6266 | -59.7748 | 62.7365 | -59.7427 | -59.8663 | -59.6695 | -0.082397 | -0.09613 | -0.036621 | 0.1236 | 59.761 | -0.26093 | 59.8434 | -0.17853 | -0.059509 | -0.1236 | -0.013733 | -0.027466 | 0.045776 | -0.15106 | 0.10529 | -0.091553 | 0.20599 | 122.5113 | 0.032043 | 122.5113 | 122.4518 | 122.4014 | 122.3694 | 122.3419 | -122.5479 | -122.525 | 122.4289 | 122.4518 | 59.7473 | 59.7794
503.7656 | 122.6852 | -59.7198 | 62.7228 | 0.080948 | 0.0023391 | 0.063948 | 0.08813 | 0.0018799 | -0.0012176 | 0.001175 | -0.064392 | 0.00015377 | 0.063111 | 0.061049 | -0.011623 | 0.00098693 | -0.0020295 | 0.027466 | 62.677 | -59.7748 | 62.7365 | -59.6054 | -59.9899 | 0 | 0.027466 | 62.6541 | -59.7656 | 62.7365 | -59.7656 | -59.8709 | -59.6832 | -0.054931 | -0.045776 | 0.013733 | 0.11444 | 59.7198 | -0.27008 | 59.7748 | -0.21515 | -0.045776 | -0.068664 | 0.013733 | -0.045776 | 0.036621 | -0.15106 | 0.082397 | -0.10529 | 0.16937 | 122.5113 | 0 | 122.5021 | 122.4518 | 122.4197 | 122.3969 | 122.374 | -122.4976 | -122.4884 | 122.4564 | 122.4564 | 59.7473 | 59.7473
504.7656 | 122.6898 | -59.7107 | 62.7686 | -0.025863 | 0.00041648 | 0.063948 | 0.088771 | 0.0044433 | -0.0012176 | -0.0013886 | -0.015564 | -0.00027343 | 0.064606 | 0.06404 | -0.010342 | 0.0022687 | -0.00053411 | 0.004578 | 62.6862 | -59.7565 | 62.6724 | -59.642 | -59.9899 | 0.032043 | 0 | 62.6495 | -59.7519 | 62.7045 | -59.7702 | -59.8709 | -59.6786 | -0.045777 | -0.082398 | -0.096131 | 0.068664 | 59.7427 | -0.27924 | 59.7885 | -0.23346 | -0.041199 | -0.11902 | -0.064087 | -0.05951 | 0.032043 | -0.16022 | 0.073242 | -0.11902 | 0.11444 | 122.4289 | -0.018311 | 122.4564 | 122.4426 | 122.4014 | 122.3969 | 122.3602 | -122.525 | -122.5204 | 122.3831 | 122.4152 | 59.7153 | 59.7107
505.7656 | 122.6852 | -59.7244 | 62.7411 | -0.07164 | -1.0718e-05 | 0.060957 | 0.088344 | 0.0029479 | 0.0009186 | -0.0020294 | -0.036926 | -0.00048703 | 0.06482 | 0.062117 | -0.012478 | 0.0026959 | 0.0018159 | 0.013733 | 62.6816 | -59.7885 | 62.7136 | -59.5963 | -59.9762 | 0.022888 | 0.036621 | 62.6404 | -59.7473 | 62.7319 | -59.7336 | -59.848 | -59.6649 | -0.064087 | -0.059509 | -0.027466 | 0.12817 | 59.7473 | -0.25177 | 59.8114 | -0.18768 | -0.022888 | -0.10071 | -0.009155 | -0.009156 | 0.059509 | -0.1236 | 0.082397 | -0.10071 | 0.19226 | 122.5021 | 0.013732 | 122.4792 | 122.4701 | 122.3877 | 122.406 | 122.3648 | -122.5296 | -122.4884 | 122.438 | 122.4564 | 59.7382 | 59.761
506.7656 | 122.6578 | -59.7336 | 62.7731 | -0.06401 | 0.0019119 | 0.062666 | 0.089625 | 0.0038025 | -0.0014312 | -0.0013886 | -0.024719 | -0.00048703 | 0.06247 | 0.065322 | -0.012691 | 0.0022687 | 0.00074769 | -0.013733 | 62.645 | -59.7794 | 62.6907 | -59.6283 | -60.0311 | -0.050354 | -0.022888 | 62.6312 | -59.7702 | 62.6862 | -59.7885 | -59.9213 | -59.7107 | -0.045776 | -0.12817 | -0.082397 | 0.10529 | 59.6832 | -0.29755 | 59.729 | -0.25177 | -0.036621 | -0.14191 | -0.086975 | -0.054931 | 0.022889 | -0.18768 | 0.05951 | -0.15106 | 0.15106 | 122.4701 | -0.01831 | 122.4564 | 122.4243 | 122.4014 | 122.3785 | 122.3648 | -122.5525 | -122.5433 | 122.4243 | 122.4197 | 59.7198 | 59.7107
507.7656 | 122.6303 | -59.729 | 62.7731 | -0.041122 | 0.00063028 | 0.062666 | 0.088985 | 0.0027343 | 0.0011322 | -0.0013886 | -0.027771 | 0.0016492 | 0.067169 | 0.059981 | -0.01141 | 0.0016277 | -0.00010671 | -0.018311 | 62.6587 | -59.8022 | 62.6862 | -59.6283 | -60.0266 | -0.032043 | -0.022888 | 62.6266 | -59.7931 | 62.6999 | -59.8022 | -59.8984 | -59.7061 | -0.073242 | -0.11444 | -0.086975 | 0.10071 | 59.697 | -0.29755 | 59.7702 | -0.2243 | -0.064087 | -0.14648 | -0.073242 | -0.073242 | 0.022888 | -0.16937 | 0.086975 | -0.10529 | 0.17395 | 122.4884 | -0.009155 | 122.493 | 122.4609 | 122.4197 | 122.3877 | 122.3557 | -122.5754 | -122.5662 | 122.4152 | 122.4289 | 59.7107 | 59.7061
508.7656 | 122.699 | -59.7565 | 62.6633 | -0.10216 | 0.0025529 | 0.062666 | 0.088771 | -0.0015381 | -0.0012176 | -0.00053396 | -0.021667 | -0.00027343 | 0.063751 | 0.061476 | -0.0090597 | 0.0022687 | 0.00032049 | -0.064087 | 62.6541 | -59.7885 | 62.6266 | -59.7107 | -60.0769 | -0.10986 | -0.15106 | 62.6221 | -59.7839 | 62.6312 | -59.8618 | -59.9808 | -59.7656 | -0.032043 | -0.009155 | -0.036621 | 0.045777 | 59.6466 | -0.32043 | 59.6787 | -0.28839 | -0.027466 | -0.041199 | -0.032043 | -0.10529 | -0.009155 | -0.2243 | 0.018311 | -0.19684 | 0.07782 | 122.4152 | -0.077819 | 122.4152 | 122.4426 | 122.406 | 122.4106 | 122.3785 | -122.4518 | -122.4472 | 122.3831 | 122.3877 | 59.6924 | 59.6054
509.7656 | 122.6349 | -59.7565 | 62.7319 | -0.13267 | 0.0025529 | 0.06523 | 0.09048 | 0.0046569 | -0.001004 | -0.00096136 | -0.030823 | -0.00027343 | 0.065033 | 0.064894 | -0.011623 | 0.0031231 | -0.00032051 | -0.013733 | 62.6633 | -59.7885 | 62.6816 | -59.6329 | -60.0082 | -0.041199 | -0.032043 | 62.6312 | -59.761 | 62.7136 | -59.8114 | -59.9258 | -59.7107 | -0.032043 | -0.068665 | -0.050354 | 0.1236 | 59.7153 | -0.25177 | 59.7473 | -0.21973 | -0.004577 | -0.10071 | -0.018311 | -0.054931 | 0.045777 | -0.16937 | 0.050354 | -0.1648 | 0.15564 | 122.4701 | -0.050354 | 122.4747 | 122.4518 | 122.3923 | 122.4197 | 122.3877 | -122.5204 | -122.493 | 122.4381 | 122.4701 | 59.7427 | 59.7244
510.7656 | 122.6486 | -59.7382 | 62.7319 | -0.086899 | -0.0012923 | 0.063948 | 0.088557 | 0.0020935 | 6.4004e-05 | -0.00010676 | -0.030823 | 0.001222 | 0.06546 | 0.062545 | -0.011196 | 0.00055973 | -0.0043793 | -0.032043 | 62.6678 | -59.7794 | 62.6999 | -59.6329 | -60.0403 | -0.027466 | -0.054932 | 62.6312 | -59.7748 | 62.6907 | -59.7977 | -59.9258 | -59.7198 | -0.041199 | -0.064087 | -0.032044 | 0.10529 | 59.7107 | -0.30212 | 59.7519 | -0.26093 | -0.036621 | -0.10071 | -0.041199 | -0.059509 | 0.01831 | -0.18768 | 0.054931 | -0.15106 | 0.14648 | 122.4792 | -0.022888 | 122.4655 | 122.4472 | 122.406 | 122.406 | 122.3694 | -122.5113 | -122.5067 | 122.438 | 122.4289 | 59.7061 | 59.6832
511.7656 | 122.6532 | -59.7382 | 62.7457 | -0.033493 | 0.0010575 | 0.062239 | 0.08813 | 0.0018799 | -0.0024994 | -0.0018158 | -0.039978 | 0.00015377 | 0.066315 | 0.061049 | -0.011623 | 0.0026959 | 0.00032049 | -0.018311 | 62.6541 | -59.8114 | 62.6724 | -59.6329 | -60.0311 | -0.036621 | -0.045776 | 62.6358 | -59.7885 | 62.6953 | -59.8022 | -59.9304 | -59.7198 | -0.073242 | -0.091553 | -0.073243 | 0.10529 | 59.7015 | -0.29297 | 59.7748 | -0.21973 | -0.050354 | -0.10986 | -0.050355 | -0.064087 | 0.01831 | -0.19226 | 0.068664 | -0.14191 | 0.17853 | 122.4838 | -0.013733 | 122.4838 | 122.4655 | 122.4243 | 122.3923 | 122.374 | -122.5571 | -122.5342 | 122.4106 | 122.4335 | 59.7198 | 59.6924
512.7656 | 122.6807 | -59.7153 | 62.7274 | -0.06401 | 0.0014847 | 0.062666 | 0.087917 | -0.0019653 | -0.0029266 | -0.00096136 | -0.0064086 | -0.00027343 | 0.063965 | 0.063613 | -0.012905 | 0.0026959 | -0.00053411 | 0.022888 | 62.6816 | -59.7839 | 62.7136 | -59.5917 | -59.9442 | 0.022888 | 0.041199 | 62.6541 | -59.7565 | 62.7365 | -59.7427 | -59.8526 | -59.6695 | -0.068665 | -0.045776 | -0.013733 | 0.1236 | 59.7382 | -0.22888 | 59.8068 | -0.16022 | -0.041199 | -0.073242 | 0.009155 | -0.027466 | 0.045776 | -0.13733 | 0.086975 | -0.09613 | 0.19226 | 122.4976 | 0.013733 | 122.493 | 122.4655 | 122.4106 | 122.3969 | 122.3694 | -122.5113 | -122.4838 | 122.4289 | 122.4518 | 59.7382 | 59.7565
513.7656 | 122.6715 | -59.7336 | 62.7457 | -0.048752 | 0.0010575 | 0.064375 | 0.087703 | -4.2682e-05 | -0.0020722 | 0.002243 | -0.0033568 | 0.0014356 | 0.06482 | 0.058486 | -0.012691 | 0.0022687 | 0.0024567 | 0.045776 | 62.6633 | -59.7885 | 62.6999 | -59.6054 | -59.9854 | 0.013733 | 0.027466 | 62.6038 | -59.7382 | 62.7182 | -59.761 | -59.8801 | -59.6741 | -0.054931 | -0.082398 | -0.045777 | 0.12817 | 59.7473 | -0.25177 | 59.8022 | -0.19684 | -0.004577 | -0.14191 | -0.027466 | -0.027465 | 0.05951 | -0.14648 | 0.064087 | -0.14191 | 0.18311 | 122.4884 | -0.022888 | 122.4564 | 122.4518 | 122.3419 | 122.3969 | 122.3373 | -122.5342 | -122.4838 | 122.4335 | 122.4518 | 59.7794 | 59.761
514.7656 | 122.6166 | -59.7336 | 62.7274 | -0.094528 | 0.0012711 | 0.064803 | 0.087703 | 0.0023071 | -0.001004 | -0.0013886 | -0.046081 | -5.9826e-05 | 0.063538 | 0.059767 | -0.013119 | 0.0044049 | -0.00010671 | -0.086975 | 62.6541 | -59.7931 | 62.6038 | -59.7427 | -60.1089 | -0.13733 | -0.09613 | 62.6221 | -59.8114 | 62.6083 | -59.8068 | -59.9121 | -59.7336 | -0.059509 | -0.073242 | -0.1236 | -0.009155 | 59.5963 | -0.37537 | 59.6558 | -0.31586 | -0.077819 | -0.10529 | -0.11902 | -0.073242 | 0 | -0.17853 | 0.077819 | -0.10071 | 0.050354 | 122.3969 | 0.004577 | 122.4197 | 122.4472 | 122.4335 | 122.3877 | 122.3557 | -122.5204 | -122.5388 | 122.3373 | 122.3419 | 59.6466 | 59.6375
515.7656 | 122.6212 | -59.7519 | 62.7228 | -0.10979 | 0.0027665 | 0.062453 | 0.087917 | 0.00038452 | -0.0022858 | -0.00074776 | -0.15289 | 0.00229 | 0.065888 | 0.065962 | -0.013973 | 0.0012005 | -0.0011749 | -0.086975 | 62.645 | -59.8022 | 62.5854 | -59.7336 | -60.1135 | -0.10529 | -0.3479 | 62.5854 | -59.7885 | 62.6907 | -59.8984 | -59.9533 | -59.6832 | -0.050354 | -0.07782 | -0.13733 | 0.01831 | 59.6466 | -0.36163 | 59.697 | -0.31128 | -0.036621 | -0.13733 | -0.032043 | -0.14648 | 0.068664 | -0.20142 | 0.10529 | -0.16479 | 0.068664 | 122.3877 | -0.10986 | 122.4792 | 122.4472 | 122.374 | 122.3969 | 122.3373 | -122.525 | -122.5113 | 122.3373 | 122.4426 | 59.6649 | 59.404
516.7656 | 122.7493 | -59.697 | 62.6724 | -0.10979 | -0.00022432 | 0.06288 | 0.084926 | 0.00081172 | 0.0004914 | -0.00010676 | 0.024109 | -0.00048703 | 0.064179 | 0.064467 | -0.013546 | 0.0014141 | -0.00032051 | -0.09613 | 62.5717 | -59.816 | 62.7411 | -59.4955 | -59.9945 | -0.018311 | -0.013733 | 62.5626 | -59.7473 | 62.7686 | -59.697 | -59.8114 | -59.6329 | -0.11902 | -0.10071 | 0.068665 | 0.20142 | 59.6786 | -0.29755 | 59.7977 | -0.17853 | -0.050354 | -0.10986 | 0.096131 | 0 | 0.064086 | -0.11444 | 0.11444 | -0.064087 | 0.32043 | 122.5571 | 0.050354 | 122.5159 | 122.3877 | 122.3099 | 122.2687 | 122.2595 | -122.4884 | -122.4197 | 122.438 | 122.4655 | 59.6008 | 59.6832
517.7656 | 122.5845 | -59.7427 | 62.7228 | -0.079269 | -0.00043792 | 0.063734 | 0.089198 | 0.0014527 | -0.002713 | -0.00032036 | -0.049133 | 0.0010084 | 0.064606 | 0.058699 | -0.010769 | 0.0018413 | 0.0028839 | -0.045776 | 62.677 | -59.8022 | 62.6495 | -59.6695 | -60.0586 | -0.073242 | -0.1236 | 62.6266 | -59.7885 | 62.6678 | -59.8206 | -59.967 | -59.7427 | -0.059509 | -0.045776 | -0.073242 | 0.073242 | 59.6695 | -0.31586 | 59.729 | -0.25635 | -0.045776 | -0.09613 | -0.054931 | -0.07782 | 0 | -0.2243 | 0.045776 | -0.17853 | 0.13275 | 122.4518 | -0.032044 | 122.4564 | 122.4792 | 122.4152 | 122.4197 | 122.3694 | -122.525 | -122.5113 | 122.3923 | 122.4106 | 59.697 | 59.6191
518.7656 | 122.5937 | -59.7656 | 62.7594 | -0.033493 | 0.0014847 | 0.061385 | 0.090053 | 0.00059812 | -0.0005768 | 0.00096124 | -0.049133 | 0.001222 | 0.065674 | 0.060408 | -0.014187 | 0.0029095 | 0.0018159 | -0.073242 | 62.6678 | -59.8068 | 62.6587 | -59.6924 | -60.0677 | -0.10986 | -0.13275 | 62.6221 | -59.7656 | 62.645 | -59.8618 | -59.9762 | -59.7427 | -0.041199 | -0.091552 | -0.10071 | 0.073242 | 59.6558 | -0.30212 | 59.697 | -0.26093 | 0 | -0.13733 | -0.11444 | -0.09613 | 0.022888 | -0.21057 | 0.022888 | -0.21057 | 0.11444 | 122.4655 | -0.09613 | 122.4106 | 122.4747 | 122.3877 | 122.4335 | 122.3877 | -122.5662 | -122.525 | 122.4243 | 122.4106 | 59.6924 | 59.6329
519.7656 | 122.6349 | -59.7565 | 62.7182 | -0.20897 | 0.00020288 | 0.06288 | 0.09048 | -0.0047425 | -0.0020722 | -0.00053396 | -0.06134 | 0.00058097 | 0.063751 | 0.060836 | -0.012478 | 0.00098693 | -0.0016021 | -0.045776 | 62.6633 | -59.7977 | 62.59 | -59.729 | -60.0723 | -0.10986 | -0.14191 | 62.6358 | -59.7977 | 62.677 | -59.8389 | -59.9625 | -59.7198 | -0.041198 | -0.054932 | -0.12817 | 0.027466 | 59.6466 | -0.31586 | 59.6878 | -0.27466 | -0.041198 | -0.082398 | -0.041199 | -0.082397 | 0.036621 | -0.20599 | 0.077819 | -0.16479 | 0.068664 | 122.3877 | -0.041199 | 122.4747 | 122.4609 | 122.4335 | 122.4197 | 122.3923 | -122.5159 | -122.5159 | 122.3465 | 122.4335 | 59.7107 | 59.6146
520.7656 | 122.5891 | -59.7473 | 62.7502 | -0.094528 | 0.0023391 | 0.063521 | 0.086421 | -0.0015381 | 0.0004914 | -0.002243 | -0.033874 | -0.00048703 | 0.066742 | 0.063185 | -0.010982 | 0.0073955 | 0.00032049 | -0.07782 | 62.6541 | -59.8068 | 62.6221 | -59.729 | -60.0998 | -0.10986 | -0.16479 | 62.6129 | -59.816 | 62.439 | -59.523 | -59.6695 | -59.6695 | -0.05951 | -0.09613 | -0.12817 | 0.01831 | 59.6375 | -0.35248 | 59.697 | -0.29297 | -0.068665 | -0.13733 | -0.31128 | 0.2243 | 0.077819 | 0.077819 | 0.14648 | 0.14648 | 0.07782 | 122.4289 | 0.29297 | 122.2549 | 122.4609 | 122.4289 | 122.4014 | 122.3602 | -122.5571 | -122.5662 | 122.3694 | 122.1863 | 59.6695 | 59.5825
521.7656 | 122.6166 | -59.761 | 62.7274 | -0.048752 | 0.0023391 | 0.063734 | 0.089198 | 0.0010253 | -0.0016448 | -0.00096136 | -0.21698 | -0.00091423 | 0.063324 | 0.062117 | -0.0099143 | 0.0020551 | 0.0030975 | -0.09613 | 62.6587 | -59.8068 | 62.6038 | -59.7382 | -60.1089 | -0.13275 | -0.29297 | 62.5671 | -59.7748 | 62.7045 | -59.8709 | -59.935 | -59.6878 | -0.045777 | -0.068665 | -0.1236 | 0.022888 | 59.6283 | -0.3479 | 59.6741 | -0.30212 | -0.013733 | -0.16022 | -0.022888 | -0.10986 | 0.073242 | -0.17395 | 0.086975 | -0.16022 | 0.068665 | 122.4106 | -0.096131 | 122.4792 | 122.4655 | 122.3419 | 122.4197 | 122.3282 | -122.5342 | -122.5021 | 122.3648 | 122.4655 | 59.6649 | 59.4681
522.7656 | 122.6578 | -59.761 | 62.677 | -0.010605 | 0.0014847 | 0.063521 | 0.086421 | 0.0044433 | 0.0013458 | -0.00074776 | -0.033874 | 0.00079477 | 0.065033 | 0.055922 | -0.012264 | 0.0029095 | -0.0035247 | -0.10529 | 62.6404 | -59.816 | 62.6175 | -59.6786 | -60.0861 | -0.11444 | -0.14191 | 62.6129 | -59.7748 | 62.6907 | -59.8068 | -59.9258 | -59.7153 | -0.054932 | -0.036621 | -0.059509 | 0.082397 | 59.6466 | -0.32501 | 59.7015 | -0.27008 | -0.013733 | -0.064087 | 0.013733 | -0.045777 | 0.045776 | -0.1648 | 0.059509 | -0.15106 | 0.13733 | 122.4335 | -0.032044 | 122.4655 | 122.4564 | 122.3877 | 122.4014 | 122.374 | -122.493 | -122.4518 | 122.3785 | 122.4518 | 59.6558 | 59.6191
523.7656 | 122.7539 | -59.729 | 62.6816 | -0.079269 | -0.00043792 | 0.065443 | 0.08813 | -0.0013245 | -0.0031402 | 0.00010684 | 0.0027466 | -0.00048703 | 0.062042 | 0.057631 | -0.011623 | -0.00050847 | 0.00010689 | -0.09613 | 62.6221 | -59.7931 | 62.6999 | -59.6146 | -59.9808 | -0.045776 | -0.064087 | 62.5854 | -59.7748 | 62.7731 | -59.7382 | -59.8389 | -59.61 | -0.064087 | -0.05951 | 0.01831 | 0.11444 | 59.6832 | -0.25177 | 59.7473 | -0.18768 | -0.045776 | -0.096131 | 0.091552 | -0.009155 | 0.11902 | -0.10986 | 0.16479 | -0.064087 | 0.17853 | 122.493 | 0.036621 | 122.5479 | 122.4152 | 122.3602 | 122.3511 | 122.3145 | -122.4747 | -122.4564 | 122.4289 | 122.5021 | 59.6329 | 59.6649
524.7656 | 122.7264 | -59.7061 | 62.6678 | -0.14793 | 0.00063028 | 0.06288 | 0.086848 | -0.0026063 | 6.4004e-05 | -0.0033112 | 0.021057 | -0.00048703 | 0.065247 | 0.057204 | -0.010769 | 0.00055973 | -0.00053411 | -0.022888 | 62.6038 | -59.7748 | 62.7457 | -59.5551 | -59.9854 | -0.022888 | -0.009155 | 62.5671 | -59.7565 | 62.7777 | -59.7061 | -59.816 | -59.6329 | -0.068664 | -0.064087 | 0.07782 | 0.15106 | 59.6832 | -0.27924 | 59.7519 | -0.21057 | -0.050354 | -0.10071 | 0.10986 | 0 | 0.073242 | -0.10986 | 0.1236 | -0.059509 | 0.21973 | 122.5204 | 0.050354 | 122.5342 | 122.3785 | 122.3236 | 122.3099 | 122.2733 | -122.4426 | -122.4243 | 122.4518 | 122.4838 | 59.6832 | 59.697
525.7656 | 122.6349 | -59.7656 | 62.6999 | -0.23186 | -0.0012923 | 0.059676 | 0.088344 | -0.0019653 | -0.001004 | -0.0018158 | -0.049133 | -0.001128 | 0.06482 | 0.066817 | -0.012478 | 0.0020551 | -0.0018157 | 0.15564 | 62.645 | -59.8114 | 62.6129 | -59.7015 | -60.0677 | -0.10986 | -0.16022 | 62.6266 | -59.7702 | 62.6633 | -59.8526 | -59.9762 | -59.7565 | -0.045776 | -0.054932 | -0.086975 | 0.064087 | 59.6558 | -0.30212 | 59.7015 | -0.25635 | -0.004578 | -0.073242 | -0.036621 | -0.086975 | 0.009155 | -0.21057 | 0.013733 | -0.20599 | 0.10986 | 122.4243 | -0.082397 | 122.4335 | 122.4564 | 122.3969 | 122.4106 | 122.3923 | -122.5113 | -122.4701 | 122.3785 | 122.4289 | 59.9213 | 59.6054
526.7656 | 122.699 | -59.7244 | 62.6816 | -0.12505 | 0.00020288 | 0.063948 | 0.087062 | 0.0010253 | 0.0004914 | 0.00074764 | -0.027771 | 0.00015377 | 0.06247 | 0.063826 | -0.010982 | 0.0035503 | -0.00032051 | -0.068665 | 62.6175 | -59.8022 | 62.7136 | -59.5688 | -59.9899 | -0.041199 | -0.036621 | 62.5717 | -59.7565 | 62.6495 | -59.5963 | -59.5551 | -59.4589 | -0.07782 | -0.064087 | 0.032043 | 0.15564 | 59.6832 | -0.2655 | 59.761 | -0.18768 | -0.032044 | -0.10986 | -0.032044 | 0.12817 | 0.2655 | 0.16937 | 0.29755 | 0.20142 | 0.23346 | 122.5159 | 0.16022 | 122.406 | 122.4197 | 122.3282 | 122.3419 | 122.2961 | -122.4838 | -122.4381 | 122.438 | 122.374 | 59.6558 | 59.6878
527.7656 | 122.7585 | -59.7336 | 62.6816 | -0.11742 | 0.0036209 | 0.063734 | 0.087703 | -0.0017517 | -0.0022858 | -0.0013886 | -0.0094604 | 0.0014356 | 0.064392 | 0.06404 | -0.01376 | 0.0014141 | 0.0028839 | -0.018311 | 62.5854 | -59.7656 | 62.7411 | -59.5596 | -59.9716 | -0.032043 | -0.013733 | 62.558 | -59.7656 | 62.7731 | -59.7198 | -59.8206 | -59.6191 | -0.032043 | -0.096131 | 0.059509 | 0.17395 | 59.7015 | -0.23804 | 59.7336 | -0.20599 | -0.032043 | -0.1236 | 0.091552 | 0.013733 | 0.11444 | -0.086975 | 0.14648 | -0.054932 | 0.20599 | 122.5067 | 0.045776 | 122.5388 | 122.3511 | 122.3236 | 122.319 | 122.2916 | -122.4472 | -122.4472 | 122.4747 | 122.5067 | 59.7153 | 59.7198
528.7656 | 122.7402 | -59.697 | 62.6678 | -0.12505 | 0.00063028 | 0.062025 | 0.087276 | 0.0018799 | -0.0022858 | -0.0030976 | -0.0094604 | -0.00027343 | 0.063751 | 0.056563 | -0.013973 | 0.0031231 | 0.00096129 | -0.036621 | 62.6038 | -59.7656 | 62.7365 | -59.5505 | -59.9716 | -0.027466 | -0.018311 | 62.558 | -59.7702 | 62.7777 | -59.7244 | -59.8206 | -59.6237 | -0.068665 | -0.064087 | 0.068664 | 0.14648 | 59.6695 | -0.27466 | 59.7382 | -0.20599 | -0.073243 | -0.10986 | 0.10986 | -0.027466 | 0.073242 | -0.1236 | 0.14649 | -0.050354 | 0.21515 | 122.5021 | 0.045777 | 122.5479 | 122.3694 | 122.3282 | 122.3007 | 122.2549 | -122.4335 | -122.4381 | 122.4335 | 122.4747 | 59.6603 | 59.6786
529.7656 | 122.7356 | -59.7061 | 62.6907 | -0.10216 | 0.00084388 | 0.062666 | 0.089198 | -0.00025628 | -0.0012176 | 0.0013886 | -0.021667 | -5.9826e-05 | 0.065033 | 0.053786 | -0.012478 | 0.0029095 | -0.00010671 | -0.050354 | 62.5854 | -59.7885 | 62.7457 | -59.5688 | -59.9945 | -0.027466 | -0.10071 | 62.5442 | -59.7931 | 62.7457 | -59.6512 | -59.8572 | -59.6283 | -0.082397 | -0.10529 | 0.054932 | 0.13733 | 59.6787 | -0.28839 | 59.761 | -0.20599 | -0.086975 | -0.14648 | 0.054932 | 0.054932 | 0.07782 | -0.15106 | 0.16479 | -0.064087 | 0.21973 | 122.5342 | 0.14191 | 122.5388 | 122.374 | 122.3373 | 122.2916 | 122.2504 | -122.4792 | -122.4838 | 122.4518 | 122.4518 | 59.6558 | 59.6054
530.7656 | 122.7081 | -59.6878 | 62.677 | -0.079269 | 0.0023391 | 0.063521 | 0.088344 | 0.00038452 | 0.0009186 | -0.0041656 | -0.018616 | -0.0017688 | 0.06482 | 0.065535 | -0.012905 | 0.00013253 | -0.00074771 | -0.041199 | 62.6083 | -59.8068 | 62.7457 | -59.5642 | -59.9625 | -0.018311 | -0.018311 | 62.59 | -59.7244 | 62.7777 | -59.7198 | -59.8206 | -59.6329 | -0.11902 | -0.068665 | 0.068665 | 0.1236 | 59.6695 | -0.27466 | 59.7885 | -0.15564 | -0.036621 | -0.086975 | 0.10071 | -0.032044 | 0.054931 | -0.13275 | 0.091552 | -0.096131 | 0.24262 | 122.5525 | 0.004577 | 122.5021 | 122.4152 | 122.3145 | 122.2961 | 122.2778 | -122.4838 | -122.4014 | 122.4335 | 122.4655 | 59.6466 | 59.6695
531.7656 | 122.6898 | -59.7336 | 62.6907 | -0.094528 | 0.0021255 | 0.063307 | 0.087062 | -0.0026063 | 0.0013458 | -0.002884 | 0.0057984 | -0.00070063 | 0.063751 | 0.060408 | -0.012264 | 0.00055973 | -0.00096131 | -0.036621 | 62.6266 | -59.7519 | 62.7182 | -59.5688 | -60.0037 | -0.032043 | -0.045776 | 62.5763 | -59.7336 | 62.7228 | -59.7427 | -59.8389 | -59.6512 | -0.01831 | -0.064087 | 0.027466 | 0.16479 | 59.7015 | -0.27008 | 59.7198 | -0.25177 | 0 | -0.11444 | 0.032043 | -0.009155 | 0.082398 | -0.10529 | 0.082398 | -0.10529 | 0.1831 | 122.4701 | -0.009155 | 122.4564 | 122.3785 | 122.3099 | 122.3602 | 122.3099 | -122.4426 | -122.4243 | 122.4518 | 122.4564 | 59.697 | 59.6878
532.7656 | 122.7493 | -59.7153 | 62.6587 | -0.094528 | -0.00022432 | 0.063094 | 0.087489 | 0.0012391 | -0.0018586 | 0.0018158 | -0.021667 | 0.0010084 | 0.064392 | 0.06169 | -0.010982 | 0.0014141 | -0.00074771 | -0.036621 | 62.6266 | -59.7656 | 62.7548 | -59.5596 | -59.9762 | -0.032043 | -0.009155 | 62.5671 | -59.761 | 62.7777 | -59.7153 | -59.8114 | -59.6329 | -0.050354 | -0.032043 | 0.096131 | 0.15564 | 59.6832 | -0.26093 | 59.7336 | -0.21057 | -0.045776 | -0.091552 | 0.11902 | 0 | 0.082397 | -0.09613 | 0.12817 | -0.050354 | 0.20599 | 122.5204 | 0.045776 | 122.5388 | 122.3923 | 122.3282 | 122.3419 | 122.2824 | -122.4243 | -122.4197 | 122.4701 | 122.493 | 59.6787 | 59.7061
533.7656 | 122.7539 | -59.729 | 62.6907 | -0.1403 | -1.0718e-05 | 0.062666 | 0.089412 | -0.00025628 | -0.0016448 | 0.00053404 | -0.052185 | -0.00048703 | 0.065247 | 0.059767 | -0.012905 | 0.0035503 | -0.0016021 | -0.054932 | 62.6083 | -59.7702 | 62.7594 | -59.5734 | -59.9854 | -0.027466 | -0.21973 | 62.5397 | -59.8114 | 62.7869 | -59.6786 | -59.848 | -59.6146 | -0.041199 | -0.082398 | 0.068664 | 0.15564 | 59.7015 | -0.25635 | 59.7427 | -0.21515 | -0.082397 | -0.15106 | 0.09613 | 0.050354 | 0.11444 | -0.11902 | 0.19684 | -0.036621 | 0.19684 | 122.5296 | 0.13275 | 122.5983 | 122.3785 | 122.3511 | 122.3373 | 122.2687 | -122.4609 | -122.5021 | 122.4884 | 122.5159 | 59.6741 | 59.5093
534.7656 | 122.7585 | -59.7107 | 62.6495 | -0.10216 | 0.0010575 | 0.064589 | 0.088985 | -0.0015381 | -0.0003632 | 0.001175 | -0.049133 | -5.9826e-05 | 0.062683 | 0.062545 | -0.01376 | 0.0018413 | -0.0016021 | -0.045776 | 62.5946 | -59.7931 | 62.7228 | -59.5917 | -59.9762 | -0.036621 | 0.036621 | 62.5717 | -59.7794 | 62.7548 | -59.7153 | -59.8206 | -59.6146 | -0.082398 | -0.054932 | 0.073242 | 0.11902 | 59.6741 | -0.2655 | 59.7565 | -0.18311 | -0.068665 | -0.07782 | 0.10529 | -0.004578 | 0.09613 | -0.10986 | 0.1648 | -0.041199 | 0.20142 | 122.5159 | 0.064087 | 122.5342 | 122.3877 | 122.3511 | 122.3053 | 122.2824 | -122.4426 | -122.4289 | 122.4335 | 122.4655 | 59.6649 | 59.7473
535.7656 | 122.699 | -59.7336 | 62.6953 | -0.12505 | 0.0027665 | 0.062453 | 0.087703 | -0.0038879 | -0.0018586 | 0.00096124 | -0.04303 | -0.00048703 | 0.063751 | 0.063826 | -0.0099143 | 0.0016277 | -0.00053411 | -0.073242 | 62.6266 | -59.7656 | 62.709 | -59.6146 | -59.9167 | 0.17853 | -0.11444 | 62.6083 | -59.7473 | 62.7228 | -59.7382 | -59.8526 | -59.6603 | -0.032043 | -0.068664 | 0.013733 | 0.11902 | 59.9121 | -0.18311 | 59.9442 | -0.15106 | -0.013732 | -0.086975 | 0.027466 | -0.004577 | 0.073243 | -0.11902 | 0.086975 | -0.10529 | 0.15106 | 122.4747 | 0.009155 | 122.4701 | 122.3923 | 122.3557 | 122.3602 | 122.3419 | -122.4609 | -122.4426 | 122.4426 | 122.4564 | 59.6603 | 59.6191
536.7656 | 122.7539 | -59.6832 | 62.7228 | -0.033493 | -0.00086512 | 0.06288 | 0.090907 | -0.0075195 | -0.0005768 | -0.0037384 | -0.0064086 | -0.00048703 | 0.061402 | 0.055709 | -0.011196 | 0.00098693 | -0.0043793 | 0.045776 | 62.6495 | -59.7153 | 62.5626 | -59.5871 | -59.7839 | 0.091553 | 0.14191 | 62.59 | -59.7336 | 62.8143 | -59.6237 | -59.7427 | -59.6008 | -0.032043 | -0.073242 | -0.16022 | 0.096131 | 59.7748 | -0.10071 | 59.8068 | -0.068665 | -0.050354 | -0.13275 | 0.091553 | 0.05951 | 0.082398 | -0.059509 | 0.13275 | -0.009155 | 0.12817 | 122.2778 | 0.10986 | 122.5479 | 122.3648 | 122.3236 | 122.3328 | 122.2733 | -122.438 | -122.4564 | 122.2458 | 122.4976 | 59.729 | 59.8251
537.7656 | 122.7539 | -59.7198 | 62.6724 | -0.10979 | 0.0012711 | 0.062666 | 0.089839 | -0.00089728 | -0.0016448 | -0.0026704 | -0.052185 | -0.0013416 | 0.063965 | 0.068526 | -0.014614 | 0.0020551 | -0.00010671 | -0.018311 | 62.6083 | -59.761 | 62.7594 | -59.5596 | -59.9716 | -0.032043 | -0.009155 | 62.5992 | -59.7656 | 62.7869 | -59.697 | -59.8389 | -59.6191 | -0.041198 | -0.064087 | 0.086975 | 0.16022 | 59.6878 | -0.25177 | 59.729 | -0.21057 | -0.045776 | -0.073242 | 0.11444 | 0.022889 | 0.10071 | -0.11902 | 0.14648 | -0.073242 | 0.20142 | 122.5204 | 0.068665 | 122.5525 | 122.3694 | 122.3648 | 122.3282 | 122.319 | -122.4335 | -122.438 | 122.4792 | 122.5067 | 59.7015 | 59.7107
538.7656 | 122.7356 | -59.7153 | 62.6816 | -0.18608 | 0.0012711 | 0.063094 | 0.089625 | 0.00038452 | 6.4004e-05 | 0.0024566 | -0.073547 | -0.00070063 | 0.063751 | 0.065962 | -0.012051 | 0.00098693 | -0.0043793 | 0 | 62.6221 | -59.8022 | 62.7548 | -59.5596 | -59.9762 | -0.036621 | -0.004578 | 62.59 | -59.7519 | 62.7731 | -59.7015 | -59.7931 | -59.6283 | -0.086975 | -0.05951 | 0.073242 | 0.15564 | 59.6787 | -0.26093 | 59.7656 | -0.17395 | -0.036621 | -0.091553 | 0.091552 | 0.013733 | 0.086975 | -0.07782 | 0.1236 | -0.041199 | 0.24261 | 122.5571 | 0.050354 | 122.525 | 122.4243 | 122.3419 | 122.3373 | 122.3053 | -122.4838 | -122.4335 | 122.4701 | 122.4884 | 59.7153 | 59.7107
539.7656 | 122.7448 | -59.7153 | 62.6724 | 0.042801 | 0.0014847 | 0.063948 | 0.090053 | -0.0015381 | -0.001004 | 0.00032044 | -0.058289 | -0.00070063 | 0.063324 | 0.062972 | -0.013332 | 0.0031231 | -0.0016021 | 0.009155 | 62.6083 | -59.7656 | 62.7731 | -59.5551 | -59.967 | -0.018311 | -0.022888 | 62.59 | -59.7427 | 62.764 | -59.7107 | -59.8251 | -59.61 | -0.050354 | -0.064087 | 0.10071 | 0.16022 | 59.697 | -0.25177 | 59.7473 | -0.20142 | -0.027466 | -0.082397 | 0.091553 | 0.004578 | 0.10529 | -0.10986 | 0.13275 | -0.082397 | 0.21057 | 122.5388 | 0.032044 | 122.5067 | 122.374 | 122.3328 | 122.3236 | 122.3053 | -122.438 | -122.4152 | 122.4884 | 122.4792 | 59.7244 | 59.6924
540.7656 | 122.6852 | -59.697 | 62.6633 | -0.12505 | 0.0031937 | 0.063948 | 0.087489 | 0.0012391 | 0.0004914 | -0.00053396 | -0.046081 | -0.00091423 | 0.063965 | 0.063185 | -0.0099143 | 0.0024823 | 0.00032049 | -0.045776 | 62.5992 | -59.7748 | 62.7594 | -59.5642 | -59.967 | -0.009155 | -0.009155 | 62.5671 | -59.761 | 62.7686 | -59.7382 | -59.8297 | -59.6512 | -0.07782 | -0.064087 | 0.09613 | 0.13275 | 59.6878 | -0.27008 | 59.7656 | -0.19226 | -0.064087 | -0.09613 | 0.10529 | -0.041199 | 0.045776 | -0.13275 | 0.10986 | -0.068665 | 0.21057 | 122.5342 | 0.022888 | 122.5296 | 122.374 | 122.3282 | 122.2961 | 122.2641 | -122.438 | -122.4243 | 122.4564 | 122.4655 | 59.6512 | 59.6878
541.7656 | 122.7264 | -59.7015 | 62.6633 | -0.11742 | 0.0027665 | 0.063307 | 0.089625 | 0.00081172 | 6.4004e-05 | -0.00010676 | -0.039978 | -0.001128 | 0.064179 | 0.065322 | -0.012264 | 0.0039777 | -0.0022431 | -0.041199 | 62.5992 | -59.7931 | 62.764 | -59.5596 | -59.9762 | -0.018311 | -0.018311 | 62.5671 | -59.7565 | 62.7823 | -59.7244 | -59.8251 | -59.6329 | -0.091553 | -0.064087 | 0.10071 | 0.14191 | 59.6832 | -0.27466 | 59.7748 | -0.18311 | -0.054932 | -0.09613 | 0.11902 | -0.022888 | 0.068664 | -0.1236 | 0.1236 | -0.068664 | 0.23346 | 122.5571 | 0.032044 | 122.5388 | 122.3923 | 122.3236 | 122.3007 | 122.2687 | -122.4564 | -122.4197 | 122.4655 | 122.4838 | 59.6603 | 59.6832
542.7656 | 122.7127 | -59.7153 | 62.6633 | -0.13267 | -0.00086512 | 0.063094 | 0.088557 | 0.00038452 | -0.0014312 | -0.0030976 | -0.04303 | 0.00036737 | 0.063538 | 0.060195 | -0.012264 | 0.0035503 | 0.0024567 | -0.041199 | 62.59 | -59.7839 | 62.7686 | -59.5367 | -59.967 | -0.022888 | -0.004578 | 62.6129 | -59.7382 | 62.7823 | -59.7153 | -59.8343 | -59.6146 | -0.068665 | -0.073242 | 0.10529 | 0.17853 | 59.6924 | -0.25177 | 59.761 | -0.18311 | -0.022888 | -0.050354 | 0.11902 | 0 | 0.10071 | -0.11902 | 0.1236 | -0.096131 | 0.24719 | 122.5525 | 0.022888 | 122.5204 | 122.374 | 122.3511 | 122.3053 | 122.3282 | -122.4472 | -122.4014 | 122.4838 | 122.4976 | 59.6741 | 59.7107
543.7656 | 122.7173 | -59.7153 | 62.6999 | -0.079269 | 0.00041648 | 0.063948 | 0.089198 | -0.0023925 | -0.0016448 | -0.0030976 | 0.011902 | -0.00048703 | 0.064179 | 0.063185 | -0.012905 | 0.0016277 | -0.0022431 | -0.050354 | 62.6221 | -59.7656 | 62.8647 | -59.5139 | -60.2097 | -0.059509 | -0.068665 | 62.59 | -59.7656 | 62.7365 | -59.7198 | -59.8434 | -59.6603 | -0.050354 | -0.07782 | 0.16479 | 0.20142 | 59.6558 | -0.49439 | 59.7061 | -0.44403 | -0.050354 | -0.10986 | 0.036621 | -0.004578 | 0.054932 | -0.12817 | 0.10529 | -0.07782 | 0.25177 | 122.6303 | 0.045776 | 122.5021 | 122.3877 | 122.3557 | 122.3373 | 122.3053 | -122.4655 | -122.4655 | 122.58 | 122.4518 | 59.6649 | 59.6466
544.7656 | 122.6669 | -59.7244 | 62.6862 | -0.079269 | 0.00020288 | 0.063307 | 0.087276 | -0.00068368 | -0.0016448 | 0.00074764 | 0.079041 | 0.00015377 | 0.065033 | 0.061904 | -0.011837 | 0.0012005 | -0.0037383 | -0.068665 | 62.6175 | -59.7702 | 62.7182 | -59.5963 | -59.9854 | -0.013733 | -0.17853 | 62.5992 | -59.7565 | 62.7274 | -59.7656 | -59.8297 | -59.6695 | -0.045777 | -0.068664 | 0.032044 | 0.12817 | 59.7107 | -0.26093 | 59.7565 | -0.21515 | -0.032044 | -0.086975 | 0.041199 | -0.041199 | 0.054931 | -0.10529 | 0.086975 | -0.073242 | 0.17395 | 122.4884 | -0.009155 | 122.4838 | 122.3877 | 122.3557 | 122.3419 | 122.3236 | -122.4564 | -122.4426 | 122.4426 | 122.4518 | 59.6558 | 59.5459
545.7656 | 122.7264 | -59.7061 | 62.6541 | -0.17845 | 0.00063028 | 0.061812 | 0.087703 | -0.0011109 | 0.0013458 | -0.00032036 | -0.070496 | -0.002196 | 0.065247 | 0.061049 | -0.012905 | 0.0031231 | -0.0035247 | 0.004578 | 62.6175 | -59.7977 | 62.7686 | -59.5551 | -59.9716 | -0.022888 | 0 | 62.5809 | -59.7519 | 62.8052 | -59.7061 | -59.8022 | -59.6237 | -0.091552 | -0.036621 | 0.11444 | 0.15106 | 59.6832 | -0.2655 | 59.7748 | -0.17395 | -0.045776 | -0.073242 | 0.15106 | 0 | 0.082398 | -0.09613 | 0.12817 | -0.050354 | 0.24261 | 122.5662 | 0.045776 | 122.5571 | 122.4152 | 122.3328 | 122.3236 | 122.287 | -122.4518 | -122.406 | 122.4747 | 122.5113 | 59.7107 | 59.7061
546.7656 | 122.7081 | -59.7198 | 62.6953 | -0.086899 | 0.00041648 | 0.062453 | 0.088344 | -0.0023925 | 6.4004e-05 | 0.001175 | 0.0027466 | -5.9826e-05 | 0.063111 | 0.063399 | -0.012051 | 0.0012005 | 0.0024567 | -0.059509 | 62.6358 | -59.7885 | 62.7365 | -59.61 | -59.9808 | 0.009155 | -0.036621 | 62.5946 | -59.761 | 62.7319 | -59.7244 | -59.8251 | -59.6466 | -0.068664 | -0.059509 | 0.041199 | 0.10986 | 59.729 | -0.26092 | 59.7977 | -0.19226 | -0.041198 | -0.10071 | 0.036622 | -0.004577 | 0.073243 | -0.10528 | 0.11444 | -0.064087 | 0.17853 | 122.525 | 0.036621 | 122.493 | 122.4243 | 122.3557 | 122.3557 | 122.3145 | -122.4838 | -122.4564 | 122.4564 | 122.4518 | 59.6603 | 59.6832
547.7656 | 122.7448 | -59.7153 | 62.6587 | -0.14793 | 0.0021255 | 0.063307 | 0.091334 | 0.0038025 | -0.001004 | -0.0026704 | -0.064392 | -0.0013416 | 0.06546 | 0.068526 | -0.01141 | 0.0031231 | 0.00053409 | -0.018311 | 62.5946 | -59.7794 | 62.9196 | -59.5413 | -60.0677 | -0.027466 | -0.009155 | 62.5809 | -59.7427 | 62.7914 | -59.6878 | -59.8114 | -59.5779 | -0.064087 | -0.064087 | 0.26093 | 0.17395 | 59.6878 | -0.35248 | 59.7519 | -0.28839 | -0.027466 | -0.077819 | 0.13275 | 0.027466 | 0.13733 | -0.09613 | 0.16479 | -0.068664 | 0.23804 | 122.699 | 0.054932 | 122.5342 | 122.374 | 122.3236 | 122.3099 | 122.2961 | -122.438 | -122.4014 | 122.6349 | 122.5067 | 59.697 | 59.7061
548.7656 | 122.7493 | -59.7061 | 62.6678 | -0.048752 | 0.0016983 | 0.062666 | 0.088557 | 0.0020935 | -0.0003632 | -0.002243 | -0.024719 | -0.00048703 | 0.064392 | 0.067671 | -0.012691 | 0.0041913 | -0.0035247 | -0.027466 | 62.59 | -59.7931 | 62.7457 | -59.5688 | -60.1501 | -0.25177 | 0.09613 | 62.59 | -59.761 | 62.796 | -59.6832 | -59.8022 | -59.6375 | -0.086975 | -0.07782 | 0.07782 | 0.13733 | 59.4543 | -0.44403 | 59.5413 | -0.35706 | -0.054931 | -0.07782 | 0.12817 | 0.022888 | 0.068665 | -0.09613 | 0.1236 | -0.041199 | 0.2243 | 122.5388 | 0.077819 | 122.5571 | 122.3831 | 122.3511 | 122.2961 | 122.2961 | -122.4609 | -122.4289 | 122.4518 | 122.5021 | 59.6787 | 59.8022
549.7656 | 122.6852 | -59.729 | 62.6724 | -0.15556 | 0.0014847 | 0.063094 | 0.088344 | -0.0021789 | -0.0018586 | -0.002243 | -0.030823 | -0.0013416 | 0.065247 | 0.06404 | -0.011623 | 0.00098693 | 0.00074769 | -0.054932 | 62.6175 | -59.7794 | 62.7182 | -59.5734 | -59.9945 | -0.036621 | -0.032043 | 62.59 | -59.7702 | 62.7548 | -59.7382 | -59.8297 | -59.6558 | -0.050354 | -0.054931 | 0.045777 | 0.15564 | 59.6924 | -0.2655 | 59.7427 | -0.21515 | -0.041199 | -0.082397 | 0.082398 | -0.009155 | 0.073242 | -0.10071 | 0.11444 | -0.059509 | 0.20599 | 122.4976 | 0.032044 | 122.525 | 122.3969 | 122.3602 | 122.3465 | 122.319 | -122.4518 | -122.4426 | 122.4472 | 122.4838 | 59.6741 | 59.697
550.7656 | 122.644 | -59.729 | 62.7594 | 0.019913 | 0.0012711 | 0.063521 | 0.08813 | -0.00025628 | -0.0029266 | 0.00053404 | -0.046081 | 0.0010084 | 0.065033 | 0.063613 | -0.010555 | 0.0020551 | -0.0013885 | 0.036621 | 62.6816 | -59.761 | 62.7365 | -59.5688 | -59.967 | 0.059509 | 0.032043 | 62.6678 | -59.7473 | 62.7319 | -59.7656 | -59.8572 | -59.6878 | -0.032043 | -0.077819 | -0.022888 | 0.16022 | 59.7885 | -0.23804 | 59.8206 | -0.20599 | -0.01831 | -0.091552 | -0.027465 | -0.036621 | 0.041199 | -0.12817 | 0.059509 | -0.10986 | 0.19226 | 122.4976 | -0.018311 | 122.4792 | 122.4426 | 122.4152 | 122.4106 | 122.3969 | -122.5204 | -122.5067 | 122.4655 | 122.4609 | 59.7656 | 59.761
551.7656 | 122.7356 | -59.6649 | 62.7136 | -0.07164 | 0.0019119 | 0.063734 | 0.087703 | -0.0021789 | -0.0012176 | -0.0016022 | 0.088196 | 0.0018628 | 0.066956 | 0.063613 | -0.012478 | 0.00098693 | 0.00096129 | 0.050354 | 62.6266 | -59.761 | 62.8326 | -59.4452 | -59.8251 | 0.39368 | -0.19684 | 62.5992 | -59.7565 | 62.8372 | -59.6649 | -59.7656 | -59.5871 | -0.09613 | -0.086975 | 0.11902 | 0.21973 | 60.0586 | -0.16022 | 60.1547 | -0.064087 | -0.091553 | -0.11444 | 0.1236 | 0 | 0.07782 | -0.10071 | 0.16937 | -0.009155 | 0.31586 | 122.5937 | 0.091553 | 122.5937 | 122.3877 | 122.3557 | 122.2916 | 122.2641 | -122.4747 | -122.4701 | 122.4976 | 122.5021 | 59.7153 | 59.4681
552.7656 | 122.731 | -59.6878 | 62.6953 | -0.056381 | 0.0010575 | 0.063307 | 0.089839 | 0.0018799 | -0.0001496 | -0.00032036 | -0.064392 | 0.00058097 | 0.062897 | 0.064253 | -0.012691 | 0.0031231 | -0.0026703 | 0.10529 | 62.6129 | -59.7656 | 62.7777 | -59.5367 | -59.935 | -0.045776 | -0.022888 | 62.5671 | -59.7656 | 62.796 | -59.6924 | -59.8343 | -59.61 | -0.07782 | -0.082397 | 0.082398 | 0.15106 | 59.642 | -0.24719 | 59.7198 | -0.16937 | -0.07782 | -0.12817 | 0.10071 | -0.004578 | 0.07782 | -0.14649 | 0.15564 | -0.068665 | 0.22888 | 122.5433 | 0.073242 | 122.5616 | 122.3785 | 122.3328 | 122.3007 | 122.2549 | -122.4609 | -122.4609 | 122.4655 | 122.4838 | 59.7931 | 59.6649
553.7656 | 122.7127 | -59.7153 | 62.7319 | -0.06401 | -0.0012923 | 0.063734 | 0.087703 | 0.0027343 | -0.0003632 | -0.0026704 | -0.027771 | -0.003905 | 0.065888 | 0.060836 | -0.013973 | 0.0018413 | 0.0035247 | -0.027466 | 62.6266 | -59.7748 | 62.709 | -59.5963 | -60.0037 | -0.013733 | -0.041199 | 62.5992 | -59.7748 | 62.7457 | -59.729 | -59.848 | -59.6649 | -0.059509 | -0.10529 | -0.022889 | 0.11902 | 59.7015 | -0.28839 | 59.761 | -0.22888 | -0.059509 | -0.13275 | 0.013733 | -0.013733 | 0.050354 | -0.13275 | 0.10986 | -0.073242 | 0.17853 | 122.4838 | 0.045776 | 122.5204 | 122.4014 | 122.374 | 122.3419 | 122.3145 | -122.5067 | -122.5067 | 122.4243 | 122.4609 | 59.6878 | 59.6741
554.7656 | 122.7173 | -59.7015 | 62.6724 | -0.12505 | 0.0029801 | 0.063948 | 0.090266 | -4.2682e-05 | -0.0003632 | -0.00010676 | -0.064392 | -0.002196 | 0.065033 | 0.055709 | -0.012051 | 0.0020551 | 0.0026703 | -0.032043 | 62.59 | -59.8068 | 62.7548 | -59.5459 | -59.9762 | -0.022888 | -0.004578 | 62.5626 | -59.7565 | 62.8006 | -59.7107 | -59.8114 | -59.6283 | -0.10529 | -0.082397 | 0.082398 | 0.15564 | 59.6786 | -0.27466 | 59.7839 | -0.16937 | -0.054932 | -0.10986 | 0.12817 | -0.009155 | 0.073242 | -0.10986 | 0.12817 | -0.054931 | 0.26093 | 122.5616 | 0.045777 | 122.5571 | 122.3969 | 122.319 | 122.2916 | 122.2641 | -122.4792 | -122.4289 | 122.4564 | 122.5021 | 59.6695 | 59.697
555.7656 | 122.7127 | -59.7244 | 62.6541 | -0.15556 | 0.0021255 | 0.062666 | 0.087276 | -0.00089728 | -0.0018586 | -0.0016022 | -0.16205 | -0.00091423 | 0.064179 | 0.06404 | -0.013119 | 0.0026959 | -0.0033111 | -0.032043 | 62.5946 | -59.7748 | 62.764 | -59.5688 | -59.9808 | -0.09613 | 0.19684 | 62.5809 | -59.7473 | 62.8098 | -59.6924 | -59.7565 | -59.5963 | -0.050354 | -0.05951 | 0.10986 | 0.15564 | 59.6283 | -0.25635 | 59.6786 | -0.20599 | -0.022888 | -0.073242 | 0.15564 | 0.032043 | 0.12817 | -0.032044 | 0.15106 | -0.009156 | 0.20599 | 122.5388 | 0.054931 | 122.5571 | 122.3694 | 122.3282 | 122.319 | 122.3053 | -122.4289 | -122.4014 | 122.4884 | 122.5342 | 59.6924 | 59.9213
556.7656 | 122.7264 | -59.7198 | 62.6907 | -0.11742 | 0.0010575 | 0.061812 | 0.087703 | -0.0023925 | -0.0003632 | -0.0026704 | -0.0064086 | -0.00048703 | 0.063111 | 0.059767 | -0.012691 | 0.0016277 | 0.00096129 | -0.041199 | 62.6495 | -59.7977 | 62.7319 | -59.5779 | -59.9808 | 0.032043 | -0.009155 | 62.5809 | -59.7427 | 62.7823 | -59.7015 | -59.7977 | -59.6329 | -0.077819 | -0.041199 | 0.041199 | 0.14191 | 59.7519 | -0.26092 | 59.8297 | -0.18311 | -0.022888 | -0.10986 | 0.091553 | 0.018311 | 0.086975 | -0.077819 | 0.10986 | -0.054931 | 0.21973 | 122.5296 | 0.041199 | 122.525 | 122.4472 | 122.3236 | 122.3694 | 122.3007 | -122.4884 | -122.4335 | 122.4518 | 122.5021 | 59.6787 | 59.7107
557.7656 | 122.6303 | -59.7107 | 62.764 | -0.041122 | -0.0017197 | 0.058821 | 0.088771 | -0.0019653 | -0.0033538 | -0.0026704 | -0.076599 | 0.00036737 | 0.06482 | 0.062758 | -0.013332 | 0.0016277 | 0.0013885 | 0.09613 | 62.7457 | -59.7702 | 62.6587 | -59.6237 | -60.0266 | 0.013733 | 0.018311 | 62.6678 | -59.7748 | 62.7045 | -59.7702 | -59.8801 | -59.697 | -0.05951 | -0.01831 | -0.10529 | 0.086975 | 59.7244 | -0.31586 | 59.7839 | -0.25635 | -0.064087 | -0.09613 | -0.059509 | -0.05951 | 0.013733 | -0.16937 | 0.07782 | -0.10529 | 0.14649 | 122.4289 | 0.004577 | 122.4792 | 122.5159 | 122.4426 | 122.4564 | 122.3785 | -122.5342 | -122.5388 | 122.3694 | 122.4152 | 59.8068 | 59.729
558.7656 | 122.6944 | -59.7015 | 62.6862 | -0.06401 | 0.0012711 | 0.06288 | 0.089198 | -0.00025628 | -0.0014312 | -0.002243 | -0.04303 | -0.00027343 | 0.064179 | 0.064681 | -0.011196 | 0.0026959 | -0.00032051 | -0.027466 | 62.6175 | -59.7656 | 62.7411 | -59.5459 | -59.9854 | -0.018311 | -0.027466 | 62.5488 | -59.7565 | 62.764 | -59.729 | -59.816 | -59.6558 | -0.064087 | -0.068664 | 0.054932 | 0.15564 | 59.6832 | -0.28381 | 59.7473 | -0.21973 | -0.054932 | -0.13733 | 0.07782 | -0.027466 | 0.045776 | -0.11444 | 0.10071 | -0.059509 | 0.21973 | 122.5067 | 0.027466 | 122.5204 | 122.3831 | 122.3053 | 122.319 | 122.2504 | -122.4518 | -122.4426 | 122.4426 | 122.4655 | 59.6741 | 59.6741
559.7656 | 122.6257 | -59.7061 | 62.6816 | -0.10979 | -1.0718e-05 | 0.06288 | 0.088985 | -0.00068368 | -0.002713 | -0.0020294 | -0.052185 | -0.0013416 | 0.06546 | 0.064253 | -0.012478 | 0.0026959 | -0.0011749 | -0.054932 | 62.6129 | -59.761 | 62.709 | -59.6146 | -59.9899 | -0.032043 | -0.059509 | 62.5854 | -59.7519 | 62.7365 | -59.7702 | -59.5871 | -59.4223 | -0.054931 | -0.068665 | 0.027465 | 0.091553 | 59.6741 | -0.28381 | 59.729 | -0.22888 | -0.045776 | -0.096131 | 0.054931 | -0.064087 | 0.28381 | 0.11902 | 0.32959 | 0.16479 | 0.14648 | 122.4701 | -0.018311 | 122.4884 | 122.374 | 122.3373 | 122.319 | 122.2916 | -122.4426 | -122.4335 | 122.4152 | 122.4426 | 59.6512 | 59.6466
560.7656 | 122.7173 | -59.7198 | 62.6678 | -0.11742 | -0.00065152 | 0.062453 | 0.09048 | 0.00081172 | -0.0005768 | 0.00010684 | -0.10712 | -5.9826e-05 | 0.06546 | 0.061904 | -0.013119 | 0.0012005 | -0.0037383 | -0.068665 | 62.6221 | -59.8022 | 62.7045 | -59.6329 | -60.0266 | -0.07782 | -0.086975 | 62.5946 | -59.7656 | 62.7777 | -59.7565 | -59.8297 | -59.6191 | -0.082397 | -0.045777 | 0.036621 | 0.086975 | 59.642 | -0.3067 | 59.7244 | -0.2243 | -0.045776 | -0.073243 | 0.10986 | -0.036621 | 0.10071 | -0.10986 | 0.14648 | -0.064087 | 0.16937 | 122.5067 | 0.009155 | 122.5433 | 122.4243 | 122.3602 | 122.3419 | 122.3145 | -122.4701 | -122.4335 | 122.4243 | 122.4976 | 59.6512 | 59.6329
561.7656 | 122.699 | -59.7198 | 62.6724 | -0.13267 | 0.0010575 | 0.058394 | 0.087276 | -0.0011109 | -0.0024994 | 0.0018158 | -0.0033568 | -0.00048703 | 0.064179 | 0.05464 | -0.012478 | 0.0014141 | -0.00010671 | 0.09613 | 62.6541 | -59.7473 | 62.6633 | -59.5871 | -59.9945 | -0.032043 | -0.073242 | 62.6038 | -59.7656 | 62.7594 | -59.729 | -59.8389 | -59.6558 | -0.027465 | -0.01831 | -0.009155 | 0.13275 | 59.6878 | -0.27466 | 59.7153 | -0.24719 | -0.045776 | -0.068664 | 0.086975 | -0.009155 | 0.064087 | -0.11902 | 0.10986 | -0.073242 | 0.16022 | 122.4106 | 0.036621 | 122.525 | 122.4014 | 122.3694 | 122.374 | 122.3236 | -122.4197 | -122.438 | 122.3831 | 122.4792 | 59.816 | 59.6466
562.7656 | 122.7493 | -59.7061 | 62.7274 | 0.20302 | -0.0023605 | 0.064589 | 0.087703 | -0.0017517 | 0.0011322 | -0.0048066 | 0.0088502 | -0.0013416 | 0.062683 | 0.06169 | -0.011623 | 0.0016277 | 0.0011749 | -0.068665 | 62.6816 | -59.7382 | 62.8372 | -59.4589 | -59.9258 | 0.11902 | 0.12817 | 62.5992 | -59.7244 | 62.8235 | -59.6512 | -59.7336 | -59.5734 | -0.032043 | -0.045776 | 0.10986 | 0.24719 | 59.8251 | -0.21973 | 59.8572 | -0.18768 | -0.01831 | -0.12817 | 0.09613 | 0.054932 | 0.13275 | -0.027466 | 0.15106 | -0.009156 | 0.27924 | 122.5754 | 0.073242 | 122.5479 | 122.4197 | 122.3236 | 122.3877 | 122.3053 | -122.4655 | -122.4518 | 122.5433 | 122.5296 | 59.6375 | 59.8343
563.7656 | 122.6944 | -59.7336 | 62.6953 | -0.11742 | 0.00020288 | 0.06288 | 0.090907 | 0.0025207 | -0.0001496 | -0.00053396 | -0.027771 | -5.9826e-05 | 0.064179 | 0.066603 | -0.012264 | 0.0026959 | -0.0018157 | -0.050354 | 62.5946 | -59.7702 | 62.7228 | -59.5596 | -60.0037 | -0.027466 | -0.036621 | 62.6083 | -59.7702 | 62.7594 | -59.7473 | -59.8297 | -59.6512 | -0.036621 | -0.10071 | 0.027466 | 0.17395 | 59.7061 | -0.27008 | 59.7427 | -0.23346 | -0.036621 | -0.086975 | 0.064087 | -0.013732 | 0.082398 | -0.09613 | 0.11902 | -0.059509 | 0.21057 | 122.493 | 0.022889 | 122.5296 | 122.3648 | 122.3785 | 122.3282 | 122.3419 | -122.4655 | -122.4655 | 122.4564 | 122.493 | 59.6832 | 59.697
564.7656 | 122.7493 | -59.7153 | 62.6724 | -0.12505 | 0.0010575 | 0.063307 | 0.089625 | 0.0029479 | -0.0012176 | -0.00010676 | -0.064392 | 0.0010084 | 0.062897 | 0.068953 | -0.014828 | 0.00098693 | -0.0018157 | -0.036621 | 62.5854 | -59.7656 | 62.7594 | -59.5596 | -59.967 | -0.022888 | -0.022888 | 62.5626 | -59.7702 | 62.7869 | -59.7153 | -59.8114 | -59.6191 | -0.050354 | -0.086975 | 0.086975 | 0.15564 | 59.6924 | -0.25177 | 59.7427 | -0.20142 | -0.054932 | -0.10986 | 0.11444 | 0 | 0.09613 | -0.09613 | 0.15106 | -0.041198 | 0.20599 | 122.525 | 0.054932 | 122.5571 | 122.3511 | 122.3328 | 122.3007 | 122.2778 | -122.438 | -122.4426 | 122.4747 | 122.5021 | 59.6787 | 59.6924
565.7656 | 122.7448 | -59.697 | 62.677 | -0.14793 | 0.0014847 | 0.062025 | 0.088985 | -4.2682e-05 | -0.0012176 | 0.001175 | -0.046081 | 0.0020764 | 0.064392 | 0.066817 | -0.012691 | 0.0014141 | -0.0018157 | 0.14648 | 62.6266 | -59.7473 | 62.7686 | -59.5413 | -59.9396 | -0.045776 | -0.013733 | 62.5626 | -59.7473 | 62.7869 | -59.7015 | -59.8206 | -59.6237 | -0.050354 | -0.050354 | 0.091553 | 0.15564 | 59.6512 | -0.24262 | 59.7015 | -0.19226 | -0.050354 | -0.11444 | 0.10986 | -0.004578 | 0.073242 | -0.1236 | 0.1236 | -0.073243 | 0.20599 | 122.5159 | 0.045776 | 122.5342 | 122.374 | 122.3099 | 122.3236 | 122.2595 | -122.4243 | -122.4243 | 122.4655 | 122.4838 | 59.8434 | 59.6832
566.7656 | 122.6807 | -59.7015 | 62.6907 | -0.079269 | -0.00022432 | 0.062453 | 0.089839 | -0.0021789 | 6.4004e-05 | -0.0018158 | -0.0064086 | -0.00048703 | 0.065247 | 0.062758 | -0.011623 | -0.0013629 | -0.00053411 | -0.064087 | 62.6221 | -59.7794 | 62.7136 | -59.5963 | -60.0037 | -0.032043 | -0.073242 | 62.59 | -59.761 | 62.7594 | -59.7565 | -59.8297 | -59.6466 | -0.07782 | -0.068665 | 0.022888 | 0.10529 | 59.6695 | -0.30212 | 59.7473 | -0.2243 | -0.059509 | -0.10071 | 0.068664 | -0.054932 | 0.054932 | -0.12817 | 0.11444 | -0.068665 | 0.18311 | 122.493 | 0.004577 | 122.5204 | 122.4014 | 122.3511 | 122.3236 | 122.2916 | -122.4701 | -122.4518 | 122.4152 | 122.4609 | 59.6375 | 59.6283
567.7656 | 122.6761 | -59.7336 | 62.7228 | -0.048752 | 0.00084388 | 0.063734 | 0.09048 | 0.00038452 | -0.0031402 | -0.002243 | -0.09491 | 0.001222 | 0.062897 | 0.067031 | -0.012264 | 0.0039777 | 0.00053409 | -0.009155 | 62.6907 | -59.7931 | 62.7182 | -59.6237 | -59.9762 | 0.022888 | 0.018311 | 62.6633 | -59.7519 | 62.7457 | -59.729 | -59.8618 | -59.6649 | -0.059509 | -0.032043 | -0.004577 | 0.10986 | 59.7565 | -0.24261 | 59.816 | -0.18311 | -0.01831 | -0.059509 | 0.022889 | 0.004578 | 0.068665 | -0.12817 | 0.086975 | -0.10986 | 0.16937 | 122.5113 | 0.022888 | 122.4976 | 122.4838 | 122.4152 | 122.4243 | 122.3969 | -122.5159 | -122.4747 | 122.4518 | 122.4792 | 59.7244 | 59.7519
568.7656 | 122.731 | -59.7244 | 62.6633 | -0.086899 | 0.0027665 | 0.061385 | 0.089625 | 0.00081172 | -0.0012176 | 0.00053404 | -0.091858 | -0.0015552 | 0.064179 | 0.057845 | -0.013546 | 0.0029095 | -0.00010671 | -0.004578 | 62.59 | -59.7885 | 62.7548 | -59.5551 | -59.9533 | -0.18768 | 0.17853 | 62.5763 | -59.7565 | 62.7914 | -59.6924 | -59.7885 | -59.5963 | -0.064087 | -0.073242 | 0.091553 | 0.16937 | 59.5367 | -0.22888 | 59.6008 | -0.16479 | -0.032044 | -0.086975 | 0.12817 | 0.032043 | 0.12817 | -0.064087 | 0.16022 | -0.032043 | 0.23346 | 122.5433 | 0.064087 | 122.5479 | 122.3785 | 122.3328 | 122.3145 | 122.3007 | -122.4518 | -122.4197 | 122.4792 | 122.5159 | 59.7198 | 59.903
569.7656 | 122.7402 | -59.7107 | 62.6999 | -0.12505 | 0.00041648 | 0.064162 | 0.089625 | -0.0017517 | -0.0014312 | -0.0018158 | 0.021057 | -0.00070063 | 0.065674 | 0.057204 | -0.01141 | -8.1274e-05 | -0.00032051 | -0.018311 | 62.6358 | -59.7336 | 62.7182 | -59.5779 | -59.9442 | 0.032043 | 0.018311 | 62.59 | -59.7427 | 62.7686 | -59.6786 | -59.7977 | -59.6146 | -0.022889 | -0.064087 | 0.018311 | 0.13275 | 59.7427 | -0.23346 | 59.7656 | -0.21057 | -0.032044 | -0.10986 | 0.068665 | 0.032043 | 0.09613 | -0.086975 | 0.12817 | -0.054931 | 0.15564 | 122.4518 | 0.064087 | 122.5113 | 122.3694 | 122.3328 | 122.3465 | 122.3007 | -122.4335 | -122.4426 | 122.4289 | 122.4792 | 59.6924 | 59.729
570.7656 | 122.7264 | -59.7061 | 62.6678 | -0.079269 | 0.00084388 | 0.063521 | 0.089198 | 0.00017092 | 6.4004e-05 | -0.001175 | -0.055237 | -0.0013416 | 0.064179 | 0.064681 | -0.012905 | 0.0037641 | -0.00074771 | -0.032043 | 62.5946 | -59.7748 | 62.7594 | -59.5551 | -59.9533 | -0.009155 | -0.009155 | 62.5809 | -59.7473 | 62.7914 | -59.7153 | -59.8114 | -59.642 | -0.068664 | -0.073243 | 0.091552 | 0.15106 | 59.697 | -0.24719 | 59.7656 | -0.17853 | -0.041198 | -0.086975 | 0.1236 | -0.009155 | 0.064087 | -0.10528 | 0.10529 | -0.064087 | 0.21973 | 122.5342 | 0.032043 | 122.5388 | 122.3694 | 122.3282 | 122.3007 | 122.287 | -122.4426 | -122.4152 | 122.4655 | 122.4976 | 59.6741 | 59.697
571.7656 | 122.7448 | -59.6878 | 62.7319 | 0.042801 | -0.0019333 | 0.063734 | 0.088985 | 0.0016663 | 6.4004e-05 | -0.001175 | 0.011902 | 0.00058097 | 0.063751 | 0.058913 | -0.013119 | 0.00077333 | -0.00053411 | 0.032043 | 62.7045 | -59.7519 | 62.8189 | -59.4635 | -59.9075 | 0.10071 | 0.11444 | 62.6083 | -59.729 | 62.8098 | -59.6512 | -59.7382 | -59.5779 | -0.064087 | -0.027466 | 0.086975 | 0.2243 | 59.7885 | -0.21973 | 59.8526 | -0.15564 | -0.041199 | -0.1236 | 0.077819 | 0.036621 | 0.10986 | -0.050354 | 0.15106 | -0.009155 | 0.28839 | 122.5708 | 0.07782 | 122.5388 | 122.4564 | 122.3373 | 122.3923 | 122.2961 | -122.4838 | -122.4609 | 122.5067 | 122.4976 | 59.7198 | 59.8022
572.7656 | 122.7081 | -59.7107 | 62.6678 | -0.16319 | -1.0718e-05 | 0.063094 | 0.088985 | 0.00081172 | 0.0004914 | -0.001175 | -0.039978 | -0.00048703 | 0.066101 | 0.065108 | -0.013973 | 0.0031231 | -0.0022431 | -0.032043 | 62.59 | -59.7519 | 62.764 | -59.5551 | -59.9808 | -0.018311 | -0.018311 | 62.5717 | -59.7473 | 62.7823 | -59.7153 | -59.8251 | -59.6237 | -0.041199 | -0.07782 | 0.09613 | 0.15564 | 59.6924 | -0.27008 | 59.7336 | -0.22888 | -0.036621 | -0.096131 | 0.11444 | -0.004578 | 0.086975 | -0.11444 | 0.1236 | -0.07782 | 0.19684 | 122.5159 | 0.032043 | 122.5296 | 122.3419 | 122.319 | 122.3007 | 122.2824 | -122.4197 | -122.4152 | 122.4747 | 122.493 | 59.6786 | 59.6924
573.7656 | 122.7127 | -59.7153 | 62.6953 | -0.079269 | 0.0014847 | 0.063948 | 0.089625 | 0.0018799 | -0.0020722 | 0.00096124 | -0.046081 | -0.002196 | 0.063965 | 0.062758 | -0.012051 | 0.0022687 | 0.0011749 | -0.036621 | 62.6038 | -59.7931 | 62.7548 | -59.5505 | -59.9762 | -0.027466 | -0.004578 | 62.5854 | -59.7748 | 62.7823 | -59.7015 | -59.8251 | -59.6283 | -0.07782 | -0.091552 | 0.05951 | 0.16479 | 59.6878 | -0.26093 | 59.7656 | -0.18311 | -0.059509 | -0.10986 | 0.086976 | 0.013733 | 0.086975 | -0.10986 | 0.14648 | -0.050354 | 0.24261 | 122.5479 | 0.073242 | 122.5571 | 122.3969 | 122.3602 | 122.319 | 122.3007 | -122.4884 | -122.4701 | 122.4701 | 122.4976 | 59.6787 | 59.7107
574.7656 | 122.7173 | -59.697 | 62.6999 | -0.17845 | 0.00041648 | 0.063094 | 0.088344 | -4.2682e-05 | -0.0012176 | -0.0020294 | -0.018616 | -0.0017688 | 0.064392 | 0.066603 | -0.012691 | 0.0024823 | -0.00010671 | -0.064087 | 62.5946 | -59.7794 | 62.7136 | -59.5871 | -60.0128 | -0.036621 | -0.064087 | 62.5854 | -59.7656 | 62.7548 | -59.7336 | -59.8251 | -59.6603 | -0.082398 | -0.10529 | 0.013733 | 0.10986 | 59.6603 | -0.31586 | 59.7427 | -0.23346 | -0.068665 | -0.11444 | 0.054932 | -0.036622 | 0.036621 | -0.12817 | 0.10529 | -0.059509 | 0.19226 | 122.493 | 0.032043 | 122.5204 | 122.374 | 122.3511 | 122.2916 | 122.2824 | -122.4792 | -122.4655 | 122.4106 | 122.4518 | 59.6329 | 59.6329
575.7656 | 122.7036 | -59.6832 | 62.7045 | -0.10979 | -0.0036423 | 0.061171 | 0.089625 | -0.00025628 | -0.002713 | -0.001175 | -0.0094604 | 0.00015377 | 0.063538 | 0.060195 | -0.011623 | 0.0020551 | -0.0016021 | 0.10986 | 62.6587 | -59.7565 | 62.7228 | -59.6054 | -60.0128 | -0.013733 | -0.041199 | 62.6083 | -59.761 | 62.7548 | -59.7198 | -59.8206 | -59.642 | -0.073242 | -0.045777 | 0.01831 | 0.07782 | 59.6695 | -0.32959 | 59.7427 | -0.25635 | -0.077819 | -0.096131 | 0.050354 | -0.036621 | 0.041199 | -0.13733 | 0.11902 | -0.05951 | 0.15106 | 122.4792 | 0.041198 | 122.5159 | 122.4152 | 122.3694 | 122.3419 | 122.2916 | -122.4609 | -122.4655 | 122.406 | 122.4381 | 59.7931 | 59.642
576.7656 | 122.731 | -59.7153 | 62.6816 | -0.11742 | 0.00020288 | 0.064162 | 0.089839 | 0.00038452 | -0.0012176 | -0.0026704 | -0.064392 | -0.0026232 | 0.06247 | 0.068953 | -0.014828 | 0.0033367 | -0.00032051 | -0.018311 | 62.6038 | -59.8068 | 62.7457 | -59.5551 | -59.9716 | -0.027466 | -0.009155 | 62.5809 | -59.7473 | 62.7777 | -59.7153 | -59.8297 | -59.6466 | -0.091553 | -0.07782 | 0.064087 | 0.16022 | 59.6878 | -0.25635 | 59.7794 | -0.16479 | -0.032043 | -0.10071 | 0.09613 | 0 | 0.068665 | -0.11444 | 0.10071 | -0.082398 | 0.25177 | 122.5525 | 0.032043 | 122.525 | 122.4106 | 122.3282 | 122.319 | 122.2961 | -122.4884 | -122.4289 | 122.4609 | 122.493 | 59.697 | 59.7061
577.7656 | 122.7127 | -59.6878 | 62.7228 | -0.06401 | 0.0019119 | 0.062239 | 0.088985 | 0.00059812 | -0.0016448 | -0.00096136 | -0.0033568 | -0.00070063 | 0.063111 | 0.056777 | -0.01141 | 0.0020551 | -0.0016021 | 0.054932 | 62.6633 | -59.7794 | 62.8006 | -59.5139 | -59.9121 | 0.11444 | 0.1236 | 62.6175 | -59.729 | 62.8052 | -59.6558 | -59.7565 | -59.5963 | -0.091553 | -0.059509 | 0.07782 | 0.17395 | 59.8022 | -0.2243 | 59.8938 | -0.13275 | -0.041199 | -0.10528 | 0.082398 | 0.032043 | 0.091553 | -0.068665 | 0.13275 | -0.027466 | 0.2655 | 122.58 | 0.073242 | 122.5342 | 122.4426 | 122.3465 | 122.3511 | 122.3053 | -122.5021 | -122.4518 | 122.4884 | 122.493 | 59.7427 | 59.8114
578.7656 | 122.7264 | -59.7061 | 62.7136 | -0.086899 | -0.00022432 | 0.060957 | 0.089625 | 0.0027343 | -0.0012176 | 0.00053404 | -0.024719 | -5.9826e-05 | 0.06482 | 0.060195 | -0.010555 | 0.0020551 | -0.00096131 | -0.032043 | 62.6129 | -59.761 | 62.7228 | -59.5963 | -59.9716 | 0.009155 | -0.018311 | 62.6083 | -59.7656 | 62.764 | -59.7244 | -59.8297 | -59.6329 | -0.054931 | -0.10071 | 0.009155 | 0.10986 | 59.7153 | -0.2655 | 59.7702 | -0.21057 | -0.059509 | -0.10529 | 0.050354 | -0.01831 | 0.073242 | -0.1236 | 0.13275 | -0.064087 | 0.16479 | 122.4838 | 0.041199 | 122.5296 | 122.374 | 122.374 | 122.319 | 122.3145 | -122.4747 | -122.4792 | 122.4289 | 122.4701 | 59.6741 | 59.6878
579.7656 | 122.7356 | -59.6786 | 62.7136 | -0.025863 | -0.00086512 | 0.060103 | 0.089412 | 0.00017092 | -0.0014312 | -0.0026704 | -0.0064086 | -5.9826e-05 | 0.064392 | 0.059981 | -0.012905 | 0.0012005 | -0.00032051 | 0 | 62.6404 | -59.7839 | 62.7731 | -59.5367 | -59.9213 | 0.082397 | 0.10529 | 62.6038 | -59.729 | 62.8143 | -59.6466 | -59.7198 | -59.5779 | -0.10529 | -0.073242 | 0.059509 | 0.14191 | 59.761 | -0.24262 | 59.8663 | -0.13733 | -0.050354 | -0.10986 | 0.10071 | 0.032044 | 0.10071 | -0.041199 | 0.15106 | 0.009155 | 0.24719 | 122.5571 | 0.082398 | 122.5433 | 122.4243 | 122.3328 | 122.319 | 122.2824 | -122.4976 | -122.4426 | 122.4518 | 122.493 | 59.6786 | 59.7839
580.7656 | 122.6761 | -59.7473 | 62.677 | -0.056381 | -0.00022432 | 0.060957 | 0.089625 | -4.2682e-05 | -0.0029266 | -0.002884 | -0.064392 | -0.00048703 | 0.06482 | 0.065322 | -0.01141 | 0.00055973 | -0.0013885 | -0.050354 | 62.6175 | -59.7885 | 62.7319 | -59.5688 | -59.9808 | -0.041199 | -0.041199 | 62.5854 | -59.7427 | 62.7548 | -59.7336 | -59.8526 | -59.6603 | -0.041199 | -0.059509 | 0.054932 | 0.17853 | 59.7061 | -0.23346 | 59.7473 | -0.19226 | 0.004577 | -0.091553 | 0.07782 | 0.013732 | 0.086975 | -0.10529 | 0.082398 | -0.10986 | 0.21973 | 122.5204 | 0.009155 | 122.4976 | 122.406 | 122.3282 | 122.3648 | 122.3328 | -122.4655 | -122.4197 | 122.4792 | 122.5021 | 59.697 | 59.7061
581.7656 | 122.7585 | -59.6832 | 62.7136 | -0.094528 | 0.00063028 | 0.061598 | 0.088985 | 0.00038452 | -0.0037812 | -0.0035248 | -0.00030524 | -0.0013416 | 0.063538 | 0.057845 | -0.012905 | 0.0031231 | -0.0028839 | 0.018311 | 62.6495 | -59.761 | 62.7914 | -59.4772 | -59.8938 | 0.10529 | 0.13275 | 62.59 | -59.7244 | 62.8464 | -59.6237 | -59.7198 | -59.5734 | -0.077819 | -0.064087 | 0.07782 | 0.20599 | 59.7885 | -0.21057 | 59.8663 | -0.13275 | -0.041198 | -0.1236 | 0.13275 | 0.05951 | 0.10986 | -0.036621 | 0.15106 | 0.004577 | 0.28381 | 122.5525 | 0.10071 | 122.5708 | 122.4106 | 122.3145 | 122.3328 | 122.2733 | -122.4747 | -122.438 | 122.4747 | 122.5296 | 59.7015 | 59.816
582.7656 | 122.7036 | -59.7107 | 62.6999 | 0.065689 | -0.00043792 | 0.065016 | 0.089198 | -0.00089728 | -0.0042084 | 0.00096124 | -0.012512 | -0.00070063 | 0.063538 | 0.05699 | -0.013119 | 0.0014141 | -0.0022431 | -0.13275 | 62.6587 | -59.7794 | 62.7045 | -59.6237 | -59.9762 | -0.004578 | -0.036621 | 62.5992 | -59.7702 | 62.7548 | -59.7244 | -59.8297 | -59.6375 | -0.068665 | -0.041199 | 0.004578 | 0.086975 | 59.7061 | -0.2655 | 59.7748 | -0.19684 | -0.05951 | -0.10071 | 0.054932 | -0.013733 | 0.073242 | -0.11902 | 0.13275 | -0.059509 | 0.15564 | 122.4838 | 0.045777 | 122.525 | 122.438 | 122.3694 | 122.3694 | 122.3099 | -122.4792 | -122.4701 | 122.4152 | 122.4655 | 59.5779 | 59.6741
583.7656 | 122.7264 | -59.6924 | 62.6907 | -0.079269 | -0.00065152 | 0.06288 | 0.09048 | 0.00017092 | -0.0012176 | 0.00032044 | -0.015564 | -0.0015552 | 0.064392 | 0.060195 | -0.0099143 | 0.0046185 | -0.0011749 | 0.050354 | 62.6312 | -59.7565 | 62.8189 | -59.4681 | -59.8938 | 0.13275 | 0.16937 | 62.6038 | -59.7153 | 62.6724 | -59.5459 | -59.7427 | -59.6146 | -0.064087 | -0.059509 | 0.12817 | 0.2243 | 59.8251 | -0.20142 | 59.8892 | -0.13733 | -0.022888 | -0.086975 | -0.018311 | 0.14648 | 0.07782 | -0.050354 | 0.10071 | -0.027466 | 0.28839 | 122.5754 | 0.16937 | 122.3877 | 122.3877 | 122.319 | 122.3236 | 122.2961 | -122.4472 | -122.406 | 122.5113 | 122.3648 | 59.7427 | 59.8618
584.7656 | 122.7173 | -59.6832 | 62.7731 | -0.079269 | 0.0014847 | 0.064803 | 0.089625 | 0.0025207 | -0.0007904 | -0.002243 | -0.018616 | -0.00091423 | 0.065033 | 0.068526 | -0.013119 | 0.0014141 | -0.0011749 | 0.050354 | 62.6541 | -59.7427 | 62.796 | -59.4955 | -59.8984 | 0.11444 | 0.13733 | 62.6358 | -59.729 | 62.8052 | -59.6603 | -59.7519 | -59.6054 | -0.059509 | -0.11902 | 0.022889 | 0.18768 | 59.7977 | -0.21515 | 59.8572 | -0.15564 | -0.045776 | -0.13733 | 0.032044 | 0.022889 | 0.07782 | -0.068664 | 0.1236 | -0.022888 | 0.24719 | 122.5388 | 0.068665 | 122.5342 | 122.3969 | 122.3648 | 122.3373 | 122.319 | -122.5159 | -122.5021 | 122.4792 | 122.4884 | 59.7336 | 59.8206
585.7656 | 122.5983 | -59.7015 | 62.7914 | -0.041122 | 0.0029801 | 0.061171 | 0.090053 | -4.2682e-05 | -0.0042084 | -0.00010676 | -0.04303 | 0.00036737 | 0.063111 | 0.05934 | -0.010128 | 0.0026959 | 0.0045929 | 0.032043 | 62.6816 | -59.761 | 62.7045 | -59.6054 | -59.9716 | 0.045776 | 0.036621 | 62.6587 | -59.7519 | 62.7228 | -59.7519 | -59.8938 | -59.7061 | -0.059509 | -0.10986 | -0.086975 | 0.09613 | 59.7473 | -0.27008 | 59.8068 | -0.21057 | -0.050354 | -0.13275 | -0.068665 | -0.050354 | -0.004578 | -0.19226 | 0.045776 | -0.14191 | 0.15564 | 122.4655 | 0 | 122.4747 | 122.4426 | 122.4106 | 122.3831 | 122.3602 | -122.5525 | -122.5433 | 122.406 | 122.4243 | 59.7336 | 59.7382
586.7656 | 122.7356 | -59.6649 | 62.7274 | -0.010605 | 0.0053299 | 0.065657 | 0.090266 | -0.00025628 | -0.0012176 | -0.0035248 | 0.021057 | -0.00070063 | 0.063965 | 0.066176 | -0.012264 | 0.0039777 | 0.0011749 | -0.16022 | 62.6221 | -59.7519 | 62.8052 | -59.5184 | -59.8801 | 0.13733 | 0.16022 | 62.6083 | -59.7198 | 62.8098 | -59.642 | -59.7336 | -59.5871 | -0.086975 | -0.10529 | 0.07782 | 0.14648 | 59.8022 | -0.21515 | 59.8892 | -0.12817 | -0.054932 | -0.11902 | 0.082397 | 0.022888 | 0.07782 | -0.068665 | 0.13275 | -0.013733 | 0.23346 | 122.5571 | 0.07782 | 122.5296 | 122.374 | 122.3282 | 122.287 | 122.2733 | -122.4792 | -122.4472 | 122.4701 | 122.4747 | 59.5047 | 59.8251
587.7656 | 122.6669 | -59.7153 | 62.764 | -0.056381 | 0.0012711 | 0.062666 | 0.091548 | -0.00025628 | -0.0020722 | -0.00053396 | -0.021667 | -5.9826e-05 | 0.063751 | 0.060408 | -0.012264 | 0.0022687 | 0.0018159 | 0.059509 | 62.6404 | -59.7702 | 62.764 | -59.523 | -59.9213 | 0.10071 | 0.091553 | 62.645 | -59.7473 | 62.7686 | -59.7198 | -59.8206 | -59.642 | -0.054932 | -0.1236 | 0 | 0.19226 | 59.816 | -0.20599 | 59.8709 | -0.15106 | -0.032043 | -0.11902 | 0.004578 | -0.004578 | 0.073242 | -0.10529 | 0.10529 | -0.073243 | 0.24719 | 122.5342 | 0.027465 | 122.5159 | 122.4106 | 122.3923 | 122.3557 | 122.3602 | -122.5342 | -122.5113 | 122.4792 | 122.4838 | 59.7748 | 59.8068
588.7656 | 122.7402 | -59.6832 | 62.6953 | -0.10216 | 0.00063028 | 0.063521 | 0.092403 | -0.0011109 | 0.0032684 | 0.00074764 | -0.0094604 | -5.9826e-05 | 0.06546 | 0.057418 | -0.011623 | 0.0012005 | -0.00053411 | 0.009155 | 62.6358 | -59.7839 | 62.764 | -59.5413 | -59.9258 | 0.064087 | 0.045776 | 62.6083 | -59.7519 | 62.8098 | -59.6603 | -59.761 | -59.6008 | -0.10071 | -0.059509 | 0.068665 | 0.14191 | 59.7473 | -0.24261 | 59.848 | -0.14191 | -0.068664 | -0.086975 | 0.11444 | 0.022889 | 0.082398 | -0.077819 | 0.15106 | -0.009155 | 0.24261 | 122.5479 | 0.091553 | 122.5616 | 122.4197 | 122.3602 | 122.319 | 122.2916 | -122.4792 | -122.4472 | 122.4472 | 122.493 | 59.6924 | 59.729
589.7656 | 122.7676 | -59.6878 | 62.7365 | -0.033493 | 0.00020288 | 0.062666 | 0.091121 | 0.0033753 | -0.0029266 | -0.00010676 | 0.1004 | 0.0016492 | 0.066529 | 0.056777 | -0.01141 | 0.0018413 | -0.00010671 | 0.064087 | 62.6404 | -59.7794 | 62.8098 | -59.4543 | -59.8572 | 0.22888 | -0.13733 | 62.5809 | -59.7702 | 62.8372 | -59.6649 | -59.7931 | -59.6008 | -0.091553 | -0.09613 | 0.073242 | 0.23346 | 59.9167 | -0.16937 | 60.0082 | -0.07782 | -0.082398 | -0.15564 | 0.10071 | 0.022888 | 0.086975 | -0.10529 | 0.16937 | -0.022888 | 0.32501 | 122.5891 | 0.10529 | 122.6074 | 122.4197 | 122.3511 | 122.3282 | 122.2687 | -122.5159 | -122.5067 | 122.4976 | 122.525 | 59.7519 | 59.5505
590.7656 | 122.7448 | -59.6695 | 62.6953 | -0.048752 | 0.0025529 | 0.062666 | 0.090266 | 0.00038452 | -0.0029266 | 0.00032044 | -0.024719 | 0.00058097 | 0.063111 | 0.062758 | -0.01376 | 0.0018413 | 0.00032049 | 0.068665 | 62.6404 | -59.7382 | 62.8281 | -59.7931 | -60.1273 | 0.14191 | 0.12817 | 62.59 | -59.7244 | 62.8235 | -59.6512 | -59.7015 | -59.5825 | -0.068664 | -0.054931 | 0.13275 | -0.1236 | 59.8114 | -0.45776 | 59.8801 | -0.3891 | -0.054931 | -0.10529 | 0.12817 | 0.018311 | 0.086975 | -0.032043 | 0.14191 | 0.022888 | -0.054932 | 122.5662 | 0.073242 | 122.5479 | 122.3785 | 122.3145 | 122.3099 | 122.2595 | -122.4335 | -122.4197 | 122.4976 | 122.493 | 59.7382 | 59.7977
591.7656 | 122.5342 | -59.7061 | 62.8006 | -0.018234 | -1.0718e-05 | 0.060957 | 0.090907 | -0.00046988 | -0.0031402 | 0.00053404 | -0.027771 | -0.00091423 | 0.064179 | 0.062545 | -0.013119 | 0.00098693 | -0.0011749 | 0.036621 | 62.6678 | -59.7885 | 62.7182 | -59.6054 | -59.9716 | 0.064087 | 0.041199 | 62.6633 | -59.7473 | 62.7182 | -59.7702 | -59.8755 | -59.7107 | -0.082397 | -0.13275 | -0.082397 | 0.10071 | 59.7702 | -0.2655 | 59.8526 | -0.18311 | -0.041198 | -0.13733 | -0.082397 | -0.064087 | -0.004577 | -0.16937 | 0.036621 | -0.12817 | 0.18311 | 122.5067 | -0.022889 | 122.4655 | 122.4564 | 122.4106 | 122.374 | 122.3694 | -122.5891 | -122.5479 | 122.4243 | 122.4243 | 59.7427 | 59.7473
592.7656 | 122.6944 | -59.6878 | 62.7548 | -0.048752 | 0.0021255 | 0.06288 | 0.089839 | -0.0013245 | -0.0020722 | -0.0024566 | -0.036926 | -0.0013416 | 0.063324 | 0.056349 | -0.013546 | 0.00077333 | -0.00096131 | 0.064087 | 62.645 | -59.7382 | 62.8006 | -59.523 | -59.8892 | 0.11444 | 0.1236 | 62.6358 | -59.7107 | 62.7869 | -59.6924 | -59.8068 | -59.6283 | -0.050354 | -0.10986 | 0.045776 | 0.16479 | 59.8022 | -0.20142 | 59.8526 | -0.15106 | -0.022888 | -0.11902 | 0.032043 | -0.004578 | 0.059509 | -0.11902 | 0.082397 | -0.096131 | 0.21515 | 122.5388 | 0.01831 | 122.4976 | 122.3831 | 122.3465 | 122.3328 | 122.3236 | -122.493 | -122.4655 | 122.4884 | 122.4747 | 59.7519 | 59.8114
593.7656 | 122.6395 | -59.7153 | 62.7777 | -0.086899 | 0.0014847 | 0.061385 | 0.089412 | -0.0013245 | -0.0005768 | 0.00032044 | -0.04303 | 0.00229 | 0.065888 | 0.063185 | -0.012905 | 0.0016277 | 0.00032049 | 0.022888 | 62.7045 | -59.7794 | 62.6816 | -59.61 | -59.9762 | 0.036621 | 0.013733 | 62.6587 | -59.7519 | 62.7594 | -59.9716 | -60.022 | -59.697 | -0.064087 | -0.073242 | -0.09613 | 0.10529 | 59.7519 | -0.26093 | 59.816 | -0.19684 | -0.036621 | -0.11902 | -0.018311 | -0.25635 | 0.018311 | -0.3067 | 0.054932 | -0.27008 | 0.16937 | 122.4609 | -0.21973 | 122.5113 | 122.4838 | 122.4106 | 122.4197 | 122.374 | -122.5571 | -122.5296 | 122.3969 | 122.4747 | 59.7382 | 59.729
594.7656 | 122.7264 | -59.6832 | 62.7274 | -0.10979 | 0.0010575 | 0.064589 | 0.089839 | 0.0020935 | -0.0029266 | -0.002243 | -0.0094604 | -0.0017688 | 0.062683 | 0.059127 | -0.012478 | 0.0018413 | -0.00096131 | 0.050354 | 62.6358 | -59.761 | 62.7869 | -59.4955 | -59.848 | 0.11444 | 0.14191 | 62.6266 | -59.7244 | 62.8098 | -59.6283 | -59.761 | -59.5917 | -0.077819 | -0.091553 | 0.059509 | 0.18768 | 59.7977 | -0.16479 | 59.8755 | -0.086975 | -0.041198 | -0.10071 | 0.082397 | 0.054932 | 0.091553 | -0.077819 | 0.13275 | -0.036621 | 0.2655 | 122.5479 | 0.09613 | 122.5342 | 122.3969 | 122.3511 | 122.319 | 122.3099 | -122.4884 | -122.4518 | 122.4701 | 122.493 | 59.7336 | 59.8251
595.7656 | 122.7081 | -59.6741 | 62.7411 | -0.1403 | 0.0031937 | 0.062239 | 0.090907 | -0.0013245 | -0.0022858 | -0.001175 | -0.030823 | -0.00091423 | 0.061615 | 0.065108 | -0.013546 | -0.00093567 | 0.0039521 | 0.068665 | 62.6221 | -59.7565 | 62.796 | -59.4772 | -59.8526 | 0.11444 | 0.14648 | 62.6129 | -59.7336 | 62.8052 | -59.6558 | -59.7565 | -59.5917 | -0.082398 | -0.11902 | 0.054932 | 0.19684 | 59.7885 | -0.17853 | 59.8709 | -0.09613 | -0.05951 | -0.12817 | 0.064087 | 0.01831 | 0.082397 | -0.082398 | 0.14191 | -0.022888 | 0.27924 | 122.5525 | 0.07782 | 122.5388 | 122.3785 | 122.3465 | 122.2961 | 122.287 | -122.4976 | -122.4747 | 122.4701 | 122.4792 | 59.7427 | 59.8206
596.7656 | 122.6578 | -59.6832 | 62.7319 | -0.079269 | 0.0042619 | 0.062666 | 0.090694 | 0.00059812 | -0.001004 | -0.0020294 | -0.0064086 | -0.00048703 | 0.065033 | 0.060836 | -0.01141 | 0.0022687 | 0.00010689 | 0.064087 | 62.6541 | -59.761 | 62.7823 | -59.523 | -59.9075 | 0.10529 | 0.09613 | 62.6266 | -59.7336 | 62.7731 | -59.7015 | -59.816 | -59.6512 | -0.077819 | -0.07782 | 0.050354 | 0.16022 | 59.7885 | -0.2243 | 59.8663 | -0.14649 | -0.050354 | -0.10529 | 0.041198 | -0.01831 | 0.032044 | -0.13275 | 0.082398 | -0.082397 | 0.23804 | 122.5433 | 0.032044 | 122.5067 | 122.4152 | 122.3602 | 122.3373 | 122.3099 | -122.493 | -122.4655 | 122.4655 | 122.4564 | 59.7473 | 59.7794
597.7656 | 122.6578 | -59.6832 | 62.764 | -0.11742 | 0.0023391 | 0.061598 | 0.089198 | 0.0031617 | -0.0029266 | -0.0018158 | -0.033874 | 0.0010084 | 0.063324 | 0.060622 | -0.012051 | -0.0011493 | -0.0022431 | 0.068665 | 62.645 | -59.7794 | 62.7777 | -59.5276 | -59.9167 | 0.10529 | 0.10986 | 62.6495 | -59.7336 | 62.764 | -59.697 | -59.8114 | -59.6329 | -0.09613 | -0.11902 | 0.013733 | 0.15564 | 59.7885 | -0.23346 | 59.8846 | -0.13733 | -0.050354 | -0.11444 | 0 | -0.013732 | 0.050354 | -0.12817 | 0.10071 | -0.077819 | 0.25177 | 122.5571 | 0.036622 | 122.4976 | 122.4243 | 122.3831 | 122.3282 | 122.3328 | -122.5433 | -122.4976 | 122.4609 | 122.4472 | 59.7519 | 59.7931
598.7656 | 122.6257 | -59.7244 | 62.7548 | -0.086899 | 0.0021255 | 0.063734 | 0.091762 | -0.0032471 | -0.0016448 | -0.00010676 | -0.076599 | -0.00027343 | 0.065888 | 0.061049 | -0.013332 | -0.0015765 | 0.00053409 | 0.036621 | 62.6953 | -59.7748 | 62.6816 | -59.6191 | -59.9899 | 0.041199 | 0.022888 | 62.6587 | -59.7473 | 62.7548 | -59.9533 | -60.0174 | -59.6878 | -0.050354 | -0.05951 | -0.073242 | 0.10529 | 59.7656 | -0.2655 | 59.816 | -0.21515 | -0.022888 | -0.096131 | 0 | -0.22888 | 0.036621 | -0.29297 | 0.059509 | -0.27008 | 0.15564 | 122.4564 | -0.20599 | 122.5021 | 122.4701 | 122.406 | 122.4197 | 122.3831 | -122.5296 | -122.5021 | 122.406 | 122.4792 | 59.761 | 59.7473
599.7656 | 122.6166 | -59.7336 | 62.7457 | -0.048752 | 0.0034073 | 0.062453 | 0.091975 | 0.00081172 | -0.0024994 | -0.0013886 | -0.0094604 | 0.0016492 | 0.065674 | 0.060408 | -0.013119 | 0.0031231 | -0.0037383 | 0.032043 | 62.677 | -59.7794 | 62.7136 | -59.6054 | -59.9991 | 0.041199 | 0.036621 | 62.6587 | -59.7565 | 62.7502 | -59.5734 | -60.0449 | -59.8801 | -0.045776 | -0.068665 | -0.032044 | 0.12817 | 59.7748 | -0.2655 | 59.8206 | -0.21973 | -0.022888 | -0.086976 | 0.004577 | 0.16022 | -0.14648 | -0.31128 | -0.1236 | -0.28839 | 0.17395 | 122.493 | 0.18311 | 122.5067 | 122.4564 | 122.4152 | 122.4106 | 122.3923 | -122.525 | -122.5021 | 122.4472 | 122.4838 | 59.7656 | 59.7702
600.7656 | 122.6303 | -59.697 | 62.8006 | -0.0029755 | 0.0023391 | 0.061598 | 0.088557 | 0.0029479 | -0.0016448 | -0.0013886 | -0.021667 | 0.001222 | 0.063751 | 0.065962 | -0.014187 | 0.0022687 | -0.0020295 | 0.032043 | 62.6907 | -59.7748 | 62.6953 | -59.5963 | -59.9579 | 0.054932 | 0.054932 | 62.6633 | -59.761 | 62.6999 | -59.7473 | -59.7565 | -59.491 | -0.07782 | -0.10986 | -0.10529 | 0.10071 | 59.7519 | -0.26093 | 59.8297 | -0.18311 | -0.064087 | -0.13733 | -0.10071 | -0.050354 | 0.20599 | -0.05951 | 0.27008 | 0.004577 | 0.17853 | 122.4701 | 0.013733 | 122.4609 | 122.4655 | 122.4243 | 122.3877 | 122.3602 | -122.5754 | -122.5616 | 122.3923 | 122.3969 | 59.729 | 59.7519
601.7656 | 122.6761 | -59.7244 | 62.7777 | 0.012284 | 0.0014847 | 0.061385 | 0.089839 | 0.0023071 | -0.0035674 | -0.0030976 | -0.073547 | 0.0010084 | 0.062683 | 0.05699 | -0.012905 | 0.0018413 | 0.0016021 | 0.018311 | 62.6999 | -59.7702 | 62.6862 | -59.6329 | -59.9899 | 0.018311 | 0.009155 | 62.6678 | -59.7656 | 62.7411 | -59.7565 | -59.8663 | -59.6649 | -0.045777 | -0.07782 | -0.091553 | 0.091552 | 59.7427 | -0.2655 | 59.7885 | -0.21973 | -0.041199 | -0.10986 | -0.036621 | -0.032044 | 0.059509 | -0.14191 | 0.10071 | -0.10071 | 0.13733 | 122.4564 | 0.009155 | 122.5067 | 122.4701 | 122.4335 | 122.4243 | 122.3923 | -122.5479 | -122.5433 | 122.4106 | 122.4655 | 59.7427 | 59.7336
602.7656 | 122.6395 | -59.697 | 62.7686 | 0.13435 | -0.00043792 | 0.064162 | 0.090907 | 0.0018799 | -0.001004 | -0.0026704 | -0.049133 | 0.0010084 | 0.065033 | 0.058913 | -0.012478 | 0.0016277 | 0.00032049 | -0.050354 | 62.7228 | -59.7702 | 62.6816 | -59.6283 | -60.0403 | 0.004578 | 0.027466 | 62.6816 | -59.7748 | 62.6953 | -59.7702 | -59.8846 | -59.6695 | -0.073243 | -0.045777 | -0.086975 | 0.068664 | 59.7015 | -0.34332 | 59.7748 | -0.27008 | -0.07782 | -0.086975 | -0.073243 | -0.073243 | 0.027465 | -0.18768 | 0.10529 | -0.10986 | 0.14191 | 122.4518 | 0.004577 | 122.4701 | 122.493 | 122.4564 | 122.4197 | 122.3785 | -122.5388 | -122.5433 | 122.3785 | 122.3923 | 59.6466 | 59.7244
603.7656 | 122.6532 | -59.7153 | 62.7686 | -0.018234 | -1.0718e-05 | 0.061171 | 0.091334 | 0.0046569 | -0.0020722 | -0.003952 | -0.064392 | 0.00079477 | 0.063324 | 0.060836 | -0.012051 | 0.0020551 | 0.0028839 | 0.009155 | 62.7045 | -59.7794 | 62.6816 | -59.6283 | -59.9991 | 0.018311 | -0.013733 | 62.6358 | -59.7702 | 62.7365 | -59.7427 | -59.8618 | -59.6649 | -0.064087 | -0.064087 | -0.086975 | 0.086975 | 59.7336 | -0.28381 | 59.7977 | -0.21973 | -0.054932 | -0.13275 | -0.032044 | -0.027466 | 0.050354 | -0.14648 | 0.10529 | -0.091552 | 0.15106 | 122.4609 | 0.027466 | 122.5067 | 122.4838 | 122.406 | 122.4197 | 122.3511 | -122.5479 | -122.5388 | 122.3969 | 122.4518 | 59.7244 | 59.7015
604.7656 | 122.6715 | -59.7198 | 62.7274 | 0.004654 | 0.0031937 | 0.063734 | 0.089412 | -0.00046988 | -0.0020722 | -0.0016022 | -0.052185 | 0.0018628 | 0.06781 | 0.063399 | -0.013546 | 0.0026959 | -0.0030975 | 0.027466 | 62.6907 | -59.7794 | 62.7136 | -59.5871 | -59.9945 | 0.027466 | 0.059509 | 62.6404 | -59.7656 | 62.7594 | -59.7244 | -59.8709 | -59.6603 | -0.059509 | -0.036621 | -0.013733 | 0.13275 | 59.7473 | -0.27466 | 59.8068 | -0.21515 | -0.045776 | -0.086975 | 0.032043 | -0.004577 | 0.05951 | -0.15106 | 0.10529 | -0.10529 | 0.19226 | 122.493 | 0.041199 | 122.525 | 122.4701 | 122.406 | 122.4106 | 122.3602 | -122.5067 | -122.493 | 122.4335 | 122.4792 | 59.7473 | 59.7794
605.7656 | 122.6303 | -59.7107 | 62.7777 | -0.048752 | 0.00063028 | 0.062025 | 0.090053 | -0.00068368 | -0.0035674 | 0.00032044 | 0.027161 | 0.0031446 | 0.067383 | 0.064467 | -0.012264 | 0.0031231 | 0.0024567 | -0.018311 | 62.6999 | -59.7656 | 62.6724 | -59.6237 | -60.0037 | 0.16022 | -0.20142 | 62.6633 | -59.761 | 62.6999 | -59.7748 | -59.9258 | -59.6924 | -0.054932 | -0.07782 | -0.10529 | 0.086975 | 59.8709 | -0.29297 | 59.9258 | -0.23804 | -0.050354 | -0.11444 | -0.07782 | -0.064087 | 0.01831 | -0.21515 | 0.068664 | -0.1648 | 0.14191 | 122.438 | -0.013733 | 122.4609 | 122.4655 | 122.4243 | 122.4106 | 122.374 | -122.5433 | -122.5388 | 122.3831 | 122.4106 | 59.6924 | 59.5093
606.7656 | 122.6166 | -59.7061 | 62.7686 | -0.06401 | 0.0014847 | 0.061812 | 0.09048 | 0.00038452 | -0.0029266 | -0.0035248 | -0.0064086 | 0.001222 | 0.065888 | 0.057204 | -0.010769 | 0.0037641 | -0.0028839 | 0.009155 | 62.6999 | -59.7565 | 62.6907 | -59.6008 | -59.9899 | 0.045776 | 0.018311 | 62.6678 | -59.7473 | 62.6633 | -59.7153 | -59.8801 | -59.697 | -0.050354 | -0.068665 | -0.07782 | 0.10529 | 59.7519 | -0.28381 | 59.8022 | -0.23346 | -0.041198 | -0.10071 | -0.10529 | -0.009155 | 0.009156 | -0.17395 | 0.050354 | -0.13275 | 0.15564 | 122.4472 | 0.032043 | 122.4106 | 122.4564 | 122.4152 | 122.406 | 122.374 | -122.525 | -122.5159 | 122.3969 | 122.3694 | 59.7153 | 59.7244
607.7656 | 122.5708 | -59.729 | 62.764 | -0.086899 | -1.0718e-05 | 0.06288 | 0.092189 | 0.0025207 | -0.0035674 | -0.002243 | 0.0057984 | 0.00036737 | 0.06482 | 0.058913 | -0.013119 | 0.0018413 | -0.00074771 | 0.018311 | 62.6862 | -59.7656 | 62.709 | -59.6191 | -59.9945 | 0.041199 | 0.027466 | 62.677 | -59.7382 | 62.6678 | -59.5367 | -60.0037 | -59.8434 | -0.036621 | -0.07782 | -0.054932 | 0.10986 | 59.7702 | -0.2655 | 59.8068 | -0.22888 | -0.009155 | -0.086975 | -0.09613 | 0.19226 | -0.11444 | -0.27466 | -0.10529 | -0.2655 | 0.14648 | 122.4747 | 0.20142 | 122.406 | 122.4518 | 122.4152 | 122.4152 | 122.406 | -122.5296 | -122.5021 | 122.438 | 122.3969 | 59.7473 | 59.7565
608.7656 | 122.6807 | -59.6786 | 62.7594 | -0.10216 | -0.00043792 | 0.062025 | 0.088771 | -0.0036743 | 6.4004e-05 | -0.00096136 | 0.036316 | 0.00079477 | 0.065247 | 0.062972 | -0.011196 | -0.00072207 | -0.00032051 | 0.054932 | 62.6633 | -59.7336 | 62.7777 | -59.5139 | -59.8846 | 0.10529 | 0.13275 | 62.6175 | -59.7244 | 62.7777 | -59.6878 | -59.7885 | -59.61 | -0.054932 | -0.09613 | 0.018311 | 0.16479 | 59.7839 | -0.20599 | 59.8389 | -0.15106 | -0.045776 | -0.14191 | 0.018311 | -0.009155 | 0.068665 | -0.10986 | 0.11444 | -0.064087 | 0.21973 | 122.5113 | 0.036621 | 122.5021 | 122.3969 | 122.3419 | 122.3419 | 122.2961 | -122.493 | -122.4838 | 122.4564 | 122.4564 | 59.7336 | 59.8114
609.7656 | 122.6212 | -59.7107 | 62.7869 | -0.041122 | 0.00020288 | 0.062453 | 0.091762 | -0.0015381 | -0.0014312 | -0.0026704 | -0.021667 | 0.0010084 | 0.065033 | 0.06169 | -0.013546 | -0.00029487 | -0.0020295 | 0.054932 | 62.6633 | -59.7519 | 62.7228 | -59.5917 | -59.967 | 0.054932 | 0.073242 | 62.6633 | -59.7382 | 62.6816 | -59.761 | -59.8801 | -59.7015 | -0.041199 | -0.1236 | -0.064087 | 0.11902 | 59.7656 | -0.25635 | 59.8068 | -0.21515 | -0.027466 | -0.1236 | -0.10529 | -0.050354 | 0.009155 | -0.16937 | 0.036621 | -0.14191 | 0.16022 | 122.4747 | -0.022888 | 122.4197 | 122.4152 | 122.4014 | 122.374 | 122.374 | -122.5388 | -122.525 | 122.4335 | 122.3923 | 59.7656 | 59.7839
610.7656 | 122.612 | -59.729 | 62.7594 | -0.025863 | 0.0031937 | 0.063307 | 0.090907 | 0.00059812 | -0.0012176 | -0.0030976 | 0.018005 | -0.00091423 | 0.065033 | 0.070021 | -0.013119 | 0.0029095 | -0.00053411 | 0.050354 | 62.677 | -59.7519 | 62.7319 | -59.5734 | -59.9442 | 0.068665 | 0.036621 | 62.6541 | -59.7336 | 62.6953 | -59.7382 | -59.8389 | -59.6878 | -0.022888 | -0.082397 | -0.027465 | 0.15564 | 59.7977 | -0.21515 | 59.8206 | -0.19226 | -0.004578 | -0.10529 | -0.064087 | -0.009155 | 0.041199 | -0.10986 | 0.045777 | -0.10529 | 0.17853 | 122.4838 | -0.004577 | 122.4289 | 122.4289 | 122.3877 | 122.406 | 122.3831 | -122.5113 | -122.493 | 122.4609 | 122.4243 | 59.7794 | 59.7656
611.7656 | 122.6212 | -59.7061 | 62.7548 | -0.056381 | 0.00084388 | 0.060744 | 0.090053 | -0.0023925 | -0.0029266 | -0.00096136 | -0.024719 | 0.0010084 | 0.063751 | 0.061904 | -0.012478 | 0.0048321 | 0.0011749 | -0.013733 | 62.7182 | -59.7656 | 62.558 | -59.7794 | -59.9167 | 0.041199 | 0.041199 | 62.6541 | -59.7565 | 62.6862 | -59.7656 | -59.8755 | -59.7153 | -0.059509 | -0.036621 | -0.19684 | -0.073242 | 59.7473 | -0.21057 | 59.8068 | -0.15106 | -0.050354 | -0.10071 | -0.068665 | -0.059509 | -0.009155 | -0.16937 | 0.041199 | -0.11902 | -0.013733 | 122.3236 | -0.009155 | 122.4426 | 122.4838 | 122.4106 | 122.4243 | 122.3602 | -122.5204 | -122.5113 | 122.2641 | 122.3923 | 59.6924 | 59.7473
612.7656 | 122.6486 | -59.7382 | 62.7731 | -0.086899 | 0.00041648 | 0.062239 | 0.090053 | 0.00081172 | -0.0012176 | -0.003952 | -0.052185 | 0.00015377 | 0.066101 | 0.060408 | -0.0097007 | 0.0024823 | 0.00010689 | -0.022888 | 62.6862 | -59.7794 | 62.6541 | -59.4177 | -59.848 | -0.07782 | 0.091553 | 62.6678 | -59.7336 | 62.7136 | -59.761 | -59.8709 | -59.6878 | -0.041199 | -0.086975 | -0.11902 | 0.32043 | 59.6603 | -0.10986 | 59.7015 | -0.068664 | 0.004577 | -0.10528 | -0.059509 | -0.022888 | 0.050354 | -0.13275 | 0.045777 | -0.13733 | 0.36163 | 122.4335 | -0.027465 | 122.4472 | 122.4655 | 122.4014 | 122.4243 | 122.406 | -122.5525 | -122.5067 | 122.3923 | 122.4518 | 59.7153 | 59.8297
613.7656 | 122.6166 | -59.7336 | 62.7869 | -0.056381 | 0.00084388 | 0.06053 | 0.090694 | -0.0011109 | -0.0029266 | -0.00032036 | -0.012512 | 0.00058097 | 0.063111 | 0.064894 | -0.011623 | 0.00077333 | -0.00074771 | -0.013733 | 62.6953 | -59.7748 | 62.6907 | -59.6237 | -59.9991 | 0.045776 | 0.28839 | 62.7457 | -59.7015 | 62.6678 | -59.7748 | -59.8709 | -59.7061 | -0.041198 | -0.091553 | -0.09613 | 0.10986 | 59.7794 | -0.2655 | 59.8206 | -0.2243 | 0.032044 | -0.041198 | -0.11902 | -0.041198 | 0.027466 | -0.13733 | -0.004578 | -0.16937 | 0.15106 | 122.4655 | -0.073242 | 122.3694 | 122.4701 | 122.4472 | 122.4289 | 122.4792 | -122.5616 | -122.4884 | 122.4243 | 122.4014 | 59.7198 | 60.022
614.7656 | 122.5845 | -59.7244 | 62.764 | -0.048752 | 0.0019119 | 0.062025 | 0.090266 | 0.00017092 | -0.0035674 | -0.00096136 | -0.0094604 | 0.0010084 | 0.066529 | 0.063399 | -0.011196 | 0.00098693 | 0.0020295 | 0.027466 | 62.6907 | -59.7885 | 62.6862 | -59.6237 | -59.9808 | 0.045776 | 0.018311 | 62.6633 | -59.7565 | 62.6862 | -59.9487 | -59.8892 | -59.6375 | -0.064087 | -0.073242 | -0.07782 | 0.10071 | 59.7702 | -0.25635 | 59.8343 | -0.19226 | -0.032044 | -0.10071 | -0.07782 | -0.2243 | 0.086975 | -0.16479 | 0.11902 | -0.13275 | 0.1648 | 122.4747 | -0.19226 | 122.4426 | 122.4792 | 122.4197 | 122.4152 | 122.3877 | -122.5525 | -122.5204 | 122.4106 | 122.4106 | 59.7519 | 59.7427
615.8281 | 122.6852 | -59.7153 | 62.7319 | -0.1403 | -0.00022432 | 0.061812 | 0.090053 | 0.00017092 | -0.0001496 | -0.001175 | 0.011902 | -0.00027343 | 0.065674 | 0.060408 | -0.012051 | 0.00077333 | 0.00010689 | -0.064087 | 62.6404 | -59.7656 | 62.6907 | -59.5917 | -59.967 | -0.009155 | -0.013733 | 62.6175 | -59.7565 | 62.7457 | -59.729 | -59.8114 | -59.6329 | -0.050354 | -0.091553 | -0.041199 | 0.1236 | 59.7061 | -0.25177 | 59.7565 | -0.20142 | -0.041199 | -0.11444 | 0.013733 | -0.013733 | 0.082397 | -0.09613 | 0.1236 | -0.054931 | 0.17395 | 122.4564 | 0.027466 | 122.5021 | 122.406 | 122.374 | 122.3557 | 122.3328 | -122.4976 | -122.4884 | 122.406 | 122.4609 | 59.6512 | 59.7015
616.7656 | 122.6807 | -59.7153 | 62.7548 | -0.11742 | 0.0016983 | 0.06288 | 0.092616 | 0.0016663 | -0.0012176 | -0.00010676 | -0.0094604 | 0.0010084 | 0.06482 | 0.066817 | -0.013332 | 0.0018413 | -0.0039521 | 0.068665 | 62.6358 | -59.7473 | 62.7686 | -59.5184 | -59.8938 | 0.11444 | 0.1236 | 62.6175 | -59.7198 | 62.7365 | -59.697 | -59.7931 | -59.61 | -0.032043 | -0.11902 | 0.013733 | 0.19684 | 59.8297 | -0.17853 | 59.8618 | -0.14648 | -0.004578 | -0.13733 | -0.018311 | 0.018311 | 0.10529 | -0.07782 | 0.10986 | -0.073242 | 0.22888 | 122.5159 | 0.022889 | 122.4564 | 122.3831 | 122.3373 | 122.3511 | 122.3328 | -122.5021 | -122.4747 | 122.4838 | 122.4518 | 59.7839 | 59.8389
617.7656 | 122.6212 | -59.7153 | 62.7686 | -0.07164 | 0.00084388 | 0.061171 | 0.091975 | 0.0014527 | -0.001004 | -0.0026704 | -0.00030524 | 0.00015377 | 0.06482 | 0.061904 | -0.013332 | 0.0022687 | -0.0016021 | 0.041199 | 62.6633 | -59.7519 | 62.6953 | -59.6237 | -59.9762 | 0.068665 | 0.041199 | 62.6724 | -59.7656 | 62.6907 | -59.7519 | -59.8663 | -59.7107 | -0.036621 | -0.10529 | -0.073243 | 0.091553 | 59.7839 | -0.26093 | 59.8206 | -0.2243 | -0.050354 | -0.096131 | -0.07782 | -0.036621 | 0.004578 | -0.15106 | 0.054932 | -0.10071 | 0.12817 | 122.4472 | 0.013733 | 122.4564 | 122.4152 | 122.438 | 122.3785 | 122.3877 | -122.5204 | -122.5342 | 122.4106 | 122.406 | 59.7565 | 59.7565
618.7656 | 122.6303 | -59.697 | 62.7731 | 0.019913 | 0.00063028 | 0.064589 | 0.088557 | -0.00068368 | -0.0016448 | -0.00032036 | -0.024719 | 0.0014356 | 0.066315 | 0.060622 | -0.012264 | 0.0029095 | 0.0022431 | -0.15564 | 62.7228 | -59.7702 | 62.677 | -59.6512 | -60.0174 | 0.041199 | 0.027466 | 62.6724 | -59.7565 | 62.6953 | -59.7748 | -59.8801 | -59.6878 | -0.073243 | -0.050354 | -0.09613 | 0.045776 | 59.7382 | -0.32044 | 59.8114 | -0.24719 | -0.05951 | -0.10071 | -0.07782 | -0.07782 | 0.009155 | -0.18311 | 0.068665 | -0.1236 | 0.11902 | 122.4472 | -0.01831 | 122.4518 | 122.493 | 122.4289 | 122.4197 | 122.3694 | -122.5433 | -122.5296 | 122.374 | 122.3923 | 59.5413 | 59.7244
619.7656 | 122.6074 | -59.6924 | 62.7731 | 0.035172 | -0.0019333 | 0.061598 | 0.088771 | 0.0033753 | -0.0020722 | -0.0024566 | -0.018616 | 0.0010084 | 0.06546 | 0.057631 | -0.013332 | 0.0018413 | 0.0018159 | 0.041199 | 62.7319 | -59.7519 | 62.645 | -59.6191 | -60.0128 | 0.018311 | 0 | 62.6495 | -59.7427 | 62.6999 | -59.7565 | -59.8755 | -59.6649 | -0.059509 | -0.041198 | -0.12817 | 0.073242 | 59.7107 | -0.32043 | 59.7702 | -0.26093 | -0.050354 | -0.1236 | -0.073242 | -0.064087 | 0.027466 | -0.1831 | 0.07782 | -0.13275 | 0.13275 | 122.3969 | -0.013733 | 122.4426 | 122.4838 | 122.3923 | 122.4243 | 122.3419 | -122.525 | -122.5159 | 122.3373 | 122.3923 | 59.7336 | 59.6924
620.7656 | 122.612 | -59.7153 | 62.764 | -0.07164 | 0.0023391 | 0.060957 | 0.091548 | 0.0014527 | -0.0031402 | -0.0013886 | -0.021667 | 0.00015377 | 0.065674 | 0.060836 | -0.012051 | 0.0018413 | -0.0020295 | 0.027466 | 62.7182 | -59.7565 | 62.677 | -59.6832 | -59.9899 | 0.036621 | 0.027466 | 62.6678 | -59.7382 | 62.6953 | -59.761 | -59.8892 | -59.6786 | -0.041199 | -0.045776 | -0.086975 | 0.032043 | 59.7519 | -0.27466 | 59.7931 | -0.23346 | -0.022888 | -0.09613 | -0.068665 | -0.045776 | 0.036621 | -0.17395 | 0.059509 | -0.15106 | 0.073242 | 122.4335 | -0.022888 | 122.4335 | 122.4747 | 122.406 | 122.4335 | 122.3831 | -122.5204 | -122.5021 | 122.3923 | 122.4106 | 59.7427 | 59.7427
621.7656 | 122.6074 | -59.7153 | 62.764 | -0.033493 | 0.0021255 | 0.061812 | 0.092616 | 0.0018799 | -0.0022858 | 0.00053404 | -0.030823 | 0.0020764 | 0.065033 | 0.059981 | -0.013332 | 0.00013253 | 0.0011749 | -0.013733 | 62.6816 | -59.7427 | 62.709 | -59.6649 | -60.0037 | 0.036621 | 0.004578 | 62.677 | -59.7427 | 62.6999 | -59.7702 | -59.9167 | -59.6924 | -0.027466 | -0.082397 | -0.054932 | 0.050354 | 59.7519 | -0.28839 | 59.7794 | -0.26093 | -0.027466 | -0.086975 | -0.064087 | -0.054932 | 0.022888 | -0.20142 | 0.050354 | -0.17395 | 0.07782 | 122.4518 | -0.027466 | 122.4426 | 122.4243 | 122.4197 | 122.3969 | 122.3923 | -122.5067 | -122.5067 | 122.4243 | 122.4152 | 59.7015 | 59.7198
622.7656 | 122.6395 | -59.729 | 62.764 | -0.10979 | 0.00041648 | 0.062025 | 0.089839 | 0.00059812 | -0.0033538 | -0.0033112 | -0.00030524 | 0.00058097 | 0.066529 | 0.066603 | -0.011837 | 0.00034613 | 0.0024567 | 0.050354 | 62.6541 | -59.761 | 62.7182 | -59.5779 | -59.9442 | 0.068665 | 0.064087 | 62.6541 | -59.729 | 62.7045 | -59.7565 | -59.8572 | -59.6878 | -0.032043 | -0.10986 | -0.045776 | 0.15106 | 59.7977 | -0.21515 | 59.8297 | -0.18311 | 0 | -0.10986 | -0.059509 | -0.027466 | 0.041199 | -0.12817 | 0.041199 | -0.12817 | 0.1831 | 122.4792 | -0.027466 | 122.4335 | 122.4152 | 122.3831 | 122.3831 | 122.3831 | -122.525 | -122.493 | 122.4472 | 122.4335 | 59.7794 | 59.7931
623.7656 | 122.6395 | -59.6924 | 62.7686 | -0.10979 | 0.00041648 | 0.063734 | 0.089839 | -0.00046988 | -0.0020722 | 0.00010684 | 0.021057 | 0.00015377 | 0.065033 | 0.055709 | -0.011837 | 0.0020551 | -0.00096131 | 0.045776 | 62.6724 | -59.7702 | 62.7365 | -59.5642 | -59.9396 | 0.082397 | 0.064087 | 62.6587 | -59.7519 | 62.7182 | -59.7519 | -59.8709 | -59.697 | -0.07782 | -0.096131 | -0.032044 | 0.12817 | 59.7748 | -0.24719 | 59.8526 | -0.16937 | -0.059509 | -0.10986 | -0.050354 | -0.059509 | -0.004577 | -0.17853 | 0.054932 | -0.11902 | 0.20599 | 122.5067 | 0 | 122.4701 | 122.4426 | 122.4106 | 122.3648 | 122.3511 | -122.5388 | -122.5204 | 122.4289 | 122.4106 | 59.7382 | 59.7565
624.7656 | 122.6303 | -59.7153 | 62.764 | -0.041122 | -0.00022432 | 0.061598 | 0.091334 | -0.0023925 | -0.0024994 | -0.0018158 | -0.036926 | 0.00015377 | 0.064392 | 0.065535 | -0.01376 | 0.0033367 | -0.0028839 | 0.009155 | 62.6999 | -59.7656 | 62.5763 | -59.8251 | -60.0082 | 0.07782 | 0.022888 | 62.6633 | -59.7336 | 62.6907 | -59.7656 | -59.8663 | -59.6924 | -0.050354 | -0.064087 | -0.18768 | -0.10986 | 59.7931 | -0.29297 | 59.8434 | -0.24262 | -0.018311 | -0.10071 | -0.073242 | -0.050354 | 0.022888 | -0.15106 | 0.041199 | -0.13275 | -0.059509 | 122.3419 | -0.032043 | 122.4243 | 122.4655 | 122.3969 | 122.4152 | 122.3785 | -122.5296 | -122.4976 | 122.2916 | 122.406 | 59.7244 | 59.7382
625.7656 | 122.6532 | -59.7198 | 62.7686 | -0.079269 | 0.00063028 | 0.063094 | 0.089198 | -0.00068368 | -0.0016448 | 0.00096124 | -0.067444 | -0.00048703 | 0.065247 | 0.068099 | -0.014187 | 0.0012005 | -0.00032051 | 0.036621 | 62.6816 | -59.7931 | 62.7136 | -59.5917 | -59.9716 | 0.027466 | 0.054932 | 62.6633 | -59.7565 | 62.7411 | -59.729 | -59.8526 | -59.6649 | -0.073242 | -0.086975 | -0.054932 | 0.12817 | 59.7473 | -0.25177 | 59.8206 | -0.17853 | -0.036621 | -0.10529 | -0.027466 | -0.009155 | 0.054932 | -0.13275 | 0.091553 | -0.09613 | 0.20142 | 122.5067 | 0.027466 | 122.4976 | 122.4747 | 122.4197 | 122.4014 | 122.3831 | -122.5616 | -122.525 | 122.4335 | 122.4609 | 59.7565 | 59.7748
626.7656 | 122.6395 | -59.7015 | 62.7777 | -0.048752 | -0.00065152 | 0.062239 | 0.091762 | -0.0019653 | -0.0007904 | -0.0030976 | -0.046081 | 0.00079477 | 0.06482 | 0.062972 | -0.012478 | 0.0016277 | 0.0050201 | 0.009155 | 62.6862 | -59.7748 | 62.6953 | -59.642 | -59.9945 | 0.022888 | 0.018311 | 62.6541 | -59.7656 | 62.6953 | -59.7794 | -59.8846 | -59.6878 | -0.073242 | -0.091553 | -0.082398 | 0.059509 | 59.7244 | -0.29297 | 59.7977 | -0.21973 | -0.064087 | -0.1236 | -0.082398 | -0.07782 | 0.013733 | -0.18311 | 0.07782 | -0.11902 | 0.13275 | 122.4701 | -0.013733 | 122.4609 | 122.4609 | 122.4197 | 122.3877 | 122.3557 | -122.5525 | -122.5433 | 122.3969 | 122.3969 | 59.7107 | 59.7198
627.7656 | 122.6349 | -59.7198 | 62.7731 | -0.018234 | -0.0010787 | 0.062666 | 0.091334 | 0.0029479 | -0.002713 | -0.002884 | -0.039978 | 0.0018628 | 0.065033 | 0.059127 | -0.013332 | 0.0020551 | -0.0024567 | 0.004578 | 62.6862 | -59.7839 | 62.6541 | -59.642 | -59.9899 | 0.022888 | -0.009155 | 62.6587 | -59.7382 | 62.6999 | -59.7656 | -59.8709 | -59.6786 | -0.064087 | -0.086975 | -0.11902 | 0.07782 | 59.7427 | -0.27008 | 59.8068 | -0.20599 | -0.01831 | -0.11444 | -0.073242 | -0.045776 | 0.041199 | -0.15106 | 0.059509 | -0.13275 | 0.14191 | 122.4381 | -0.027466 | 122.438 | 122.4701 | 122.3969 | 122.406 | 122.3785 | -122.5571 | -122.5113 | 122.374 | 122.4197 | 59.7244 | 59.7107
628.7656 | 122.6486 | -59.7061 | 62.7594 | -0.033493 | 0.00020288 | 0.062025 | 0.091762 | -0.0011109 | -0.0001496 | -0.0050202 | -0.015564 | 0.0020764 | 0.065674 | 0.059767 | -0.015255 | 0.0014141 | -0.00074771 | 0 | 62.6907 | -59.7702 | 62.6678 | -59.6375 | -59.9945 | 0.022888 | 0 | 62.6587 | -59.7748 | 62.7182 | -59.7702 | -59.8801 | -59.6832 | -0.064087 | -0.068664 | -0.091552 | 0.068665 | 59.729 | -0.28839 | 59.7931 | -0.2243 | -0.068664 | -0.10071 | -0.041198 | -0.064087 | 0.022888 | -0.17395 | 0.091552 | -0.10529 | 0.13275 | 122.4381 | 0.004577 | 122.493 | 122.4609 | 122.4335 | 122.3969 | 122.3648 | -122.5296 | -122.5342 | 122.374 | 122.4243 | 59.7061 | 59.7061
629.7656 | 122.6166 | -59.7244 | 62.7594 | 0.019913 | -0.0015061 | 0.062666 | 0.090694 | -0.0011109 | -0.0067718 | -0.0024566 | 0.011902 | -5.9826e-05 | 0.066956 | 0.060408 | -0.013332 | 0.0014141 | 0.0048065 | -0.004578 | 62.6953 | -59.7794 | 62.8693 | -59.5963 | -60.3241 | -0.073242 | -0.004578 | 62.6495 | -59.7702 | 62.7045 | -59.7702 | -59.8618 | -59.6649 | -0.054932 | -0.064087 | 0.10986 | 0.12817 | 59.6512 | -0.59967 | 59.7061 | -0.54474 | -0.045777 | -0.10986 | -0.054931 | -0.045777 | 0.059509 | -0.13733 | 0.10529 | -0.091552 | 0.18311 | 122.6486 | 0 | 122.4747 | 122.4747 | 122.4197 | 122.4197 | 122.374 | -122.5388 | -122.5296 | 122.5937 | 122.4289 | 59.7198 | 59.7198
630.7656 | 122.6166 | -59.7107 | 62.8006 | -0.048752 | 0.00084388 | 0.062025 | 0.090907 | -0.0021789 | -0.0050628 | -0.0067292 | -0.0094604 | 0.0018628 | 0.065033 | 0.063185 | -0.012478 | 0.0033367 | -0.0011749 | -0.009155 | 62.6862 | -59.7748 | 62.7136 | -59.3765 | -60.0906 | -0.09613 | 0.064087 | 62.6633 | -59.7748 | 62.677 | -59.761 | -59.8663 | -59.6741 | -0.064087 | -0.11444 | -0.086975 | 0.33417 | 59.6146 | -0.37994 | 59.6786 | -0.31586 | -0.064087 | -0.13733 | -0.1236 | -0.050354 | 0.036621 | -0.15564 | 0.10071 | -0.091553 | 0.39825 | 122.4884 | 0.013733 | 122.4518 | 122.4609 | 122.438 | 122.3969 | 122.374 | -122.5754 | -122.5754 | 122.4243 | 122.3877 | 59.7015 | 59.7748
631.7656 | 122.6395 | -59.7244 | 62.764 | -0.041122 | -0.00065152 | 0.062453 | 0.092616 | -0.0030335 | -0.0031402 | -0.0037384 | -0.046081 | 0.00036737 | 0.063324 | 0.071089 | -0.012691 | 0.0022687 | -0.0030975 | 0.027466 | 62.6907 | -59.7931 | 62.6724 | -59.6375 | -59.9945 | 0.022888 | 0.009155 | 62.6862 | -59.7336 | 62.7045 | -59.7702 | -59.8801 | -59.6924 | -0.068665 | -0.073242 | -0.091553 | 0.086975 | 59.7473 | -0.27008 | 59.816 | -0.20142 | -0.009156 | -0.07782 | -0.059509 | -0.045777 | 0.032043 | -0.15564 | 0.041199 | -0.14648 | 0.15564 | 122.4655 | -0.036621 | 122.4381 | 122.4838 | 122.4197 | 122.4152 | 122.4106 | -122.5571 | -122.4976 | 122.3969 | 122.4289 | 59.7519 | 59.7336
632.7656 | 122.6624 | -59.7061 | 62.7548 | -0.025863 | 0.0021255 | 0.061812 | 0.091762 | -0.00089728 | -0.0018586 | 0.00074764 | -0.052185 | 0.0010084 | 0.062683 | 0.068099 | -0.013546 | 0.00077333 | -0.0011749 | 0.013733 | 62.6816 | -59.7656 | 62.7182 | -59.61 | -59.9716 | 0.045776 | 0.045776 | 62.6358 | -59.7427 | 62.7365 | -59.7244 | -59.8709 | -59.6512 | -0.059509 | -0.073242 | -0.036621 | 0.096131 | 59.7519 | -0.2655 | 59.8114 | -0.20599 | -0.036621 | -0.11902 | -0.018311 | -0.01831 | 0.054932 | -0.16479 | 0.091553 | -0.12817 | 0.15564 | 122.4838 | 0.018311 | 122.4792 | 122.4472 | 122.3785 | 122.3877 | 122.3419 | -122.5204 | -122.4976 | 122.4243 | 122.4426 | 59.7198 | 59.7519
633.7656 | 122.6624 | -59.729 | 62.7319 | -0.033493 | 0.0023391 | 0.062453 | 0.090053 | 0.0050843 | -0.0020722 | -0.001175 | -0.055237 | 0.0010084 | 0.066742 | 0.068312 | -0.010982 | 0.00098693 | 0.0020295 | -0.022888 | 62.645 | -59.816 | 62.7274 | -59.5642 | -59.9899 | 0.027466 | 0.064087 | 62.6495 | -59.7382 | 62.7319 | -59.7244 | -59.8572 | -59.6558 | -0.086975 | -0.086976 | -0.004578 | 0.1648 | 59.7565 | -0.26092 | 59.8434 | -0.17395 | -0.009155 | -0.082398 | 0 | 0.004578 | 0.073242 | -0.12817 | 0.082397 | -0.11902 | 0.25177 | 122.5433 | 0.013733 | 122.4701 | 122.4609 | 122.3877 | 122.374 | 122.3785 | -122.5479 | -122.4701 | 122.4564 | 122.4609 | 59.7061 | 59.7931
634.7656 | 122.6624 | -59.7015 | 62.7457 | -0.056381 | 0.0010575 | 0.062453 | 0.090266 | 0.0035889 | -0.0024994 | -0.00053396 | -0.06134 | -0.00070063 | 0.065888 | 0.059554 | -0.012478 | 0.00098693 | 0.0033111 | 0.013733 | 62.677 | -59.7519 | 62.7045 | -59.6146 | -59.967 | 0.036621 | 0.059509 | 62.6541 | -59.761 | 62.7365 | -59.7382 | -59.848 | -59.6512 | -0.050354 | -0.068665 | -0.041199 | 0.086975 | 59.7382 | -0.2655 | 59.7885 | -0.21515 | -0.059509 | -0.091553 | -0.009156 | -0.036621 | 0.050354 | -0.14648 | 0.10986 | -0.086975 | 0.13733 | 122.4564 | 0.022888 | 122.4976 | 122.4289 | 122.4152 | 122.3785 | 122.3557 | -122.4976 | -122.5067 | 122.406 | 122.438 | 59.7153 | 59.761
635.7656 | 122.6624 | -59.7153 | 62.7502 | -0.048752 | -1.0718e-05 | 0.062453 | 0.089198 | 0.0033753 | -0.0018586 | -0.002884 | -0.070496 | -0.0017688 | 0.064392 | 0.064253 | -0.013546 | 0.0018413 | -0.0013885 | 0.013733 | 62.6724 | -59.7885 | 62.6953 | -59.6008 | -59.967 | 0.050354 | 0.054932 | 62.6404 | -59.7565 | 62.7319 | -59.7473 | -59.8618 | -59.6603 | -0.073242 | -0.07782 | -0.054932 | 0.11444 | 59.7656 | -0.25177 | 59.8389 | -0.17853 | -0.041199 | -0.10986 | -0.01831 | -0.032043 | 0.054932 | -0.14648 | 0.096131 | -0.10529 | 0.18768 | 122.4838 | 0.009156 | 122.4884 | 122.4609 | 122.3969 | 122.3877 | 122.3557 | -122.5388 | -122.5067 | 122.4106 | 122.4472 | 59.729 | 59.7702
636.7656 | 122.644 | -59.7153 | 62.764 | 0.027542 | 0.00084388 | 0.061812 | 0.091334 | -0.0011109 | -0.0001496 | -0.00032036 | 0.014954 | -5.9826e-05 | 0.063538 | 0.068099 | -0.011196 | 0.0016277 | 0.0011749 | 0.009155 | 62.7045 | -59.7656 | 62.6816 | -59.6375 | -59.9945 | 0.036621 | 0 | 62.6495 | -59.7519 | 62.6999 | -59.761 | -59.8755 | -59.6786 | -0.050354 | -0.059509 | -0.082397 | 0.07782 | 59.7519 | -0.27924 | 59.8022 | -0.22888 | -0.036621 | -0.11444 | -0.064087 | -0.045776 | 0.036621 | -0.16022 | 0.073242 | -0.1236 | 0.12817 | 122.4472 | -0.009155 | 122.4518 | 122.4701 | 122.4014 | 122.4197 | 122.3648 | -122.5296 | -122.5159 | 122.3969 | 122.4152 | 59.7244 | 59.7153
637.7656 | 122.6715 | -59.7107 | 62.7365 | -0.079269 | 0.0019119 | 0.064375 | 0.090907 | 0.0018799 | -0.0042084 | 0.001175 | -0.033874 | 0.00036737 | 0.062683 | 0.055495 | -0.013973 | 0.0031231 | -0.00010671 | 0.036621 | 62.6587 | -59.7794 | 62.709 | -59.5871 | -59.9716 | 0.041199 | 0.045776 | 62.6358 | -59.7473 | 62.7228 | -59.7519 | -59.8526 | -59.6832 | -0.068665 | -0.07782 | -0.027466 | 0.1236 | 59.7519 | -0.26093 | 59.8206 | -0.19226 | -0.036621 | -0.10071 | -0.013733 | -0.041199 | 0.027465 | -0.14191 | 0.064086 | -0.10529 | 0.19226 | 122.4884 | -0.004578 | 122.4701 | 122.438 | 122.3831 | 122.3694 | 122.3465 | -122.5159 | -122.4838 | 122.4197 | 122.4335 | 59.7473 | 59.7565
638.7656 | 122.5571 | -59.7382 | 62.7045 | 0.012284 | 0.00084388 | 0.062453 | 0.089625 | 0.0014527 | -0.0024994 | -0.0026704 | -0.039978 | -0.00091423 | 0.066529 | 0.062545 | -0.01376 | 0.0026959 | -0.0020295 | 0.013733 | 62.6724 | -59.761 | 62.7182 | -59.5642 | -59.967 | 0.032043 | 0.041199 | 62.6404 | -59.7519 | 62.7457 | -59.729 | -59.8434 | -59.5688 | -0.022888 | -0.032044 | 0.013733 | 0.17395 | 59.7702 | -0.22888 | 59.7931 | -0.20599 | -0.013733 | -0.064087 | 0.041199 | 0.009155 | 0.16937 | -0.10529 | 0.1831 | -0.091553 | 0.19684 | 122.4792 | 0.022888 | 122.4976 | 122.4335 | 122.3923 | 122.4106 | 122.3785 | -122.4655 | -122.4564 | 122.4564 | 122.4838 | 59.7519 | 59.7794
639.7656 | 122.6486 | -59.7244 | 62.7365 | -0.033493 | 0.0014847 | 0.062666 | 0.091975 | 0.0020935 | -0.0024994 | -0.00032036 | -0.033874 | 0.0010084 | 0.066956 | 0.055281 | -0.012051 | 0.0020551 | -0.0026703 | 0.032043 | 62.677 | -59.7656 | 62.7182 | -59.5917 | -59.9945 | 0.004578 | 0.018311 | 62.6266 | -59.7473 | 62.7228 | -59.7473 | -59.8709 | -59.6649 | -0.041199 | -0.059509 | -0.01831 | 0.13275 | 59.729 | -0.27008 | 59.7702 | -0.22888 | -0.022888 | -0.10986 | -0.013733 | -0.022888 | 0.059509 | -0.14648 | 0.082397 | -0.1236 | 0.17395 | 122.4838 | 0 | 122.4701 | 122.4426 | 122.374 | 122.4014 | 122.3511 | -122.5021 | -122.4838 | 122.4426 | 122.4472 | 59.7565 | 59.7427
640.7656 | 122.6349 | -59.729 | 62.7365 | -0.086899 | 0.00041648 | 0.062453 | 0.090907 | 0.0016663 | -0.0012176 | 0.0028838 | -0.046081 | 0.00015377 | 0.066315 | 0.055068 | -0.012905 | 0.0039777 | -0.00074771 | 0.013733 | 62.6678 | -59.7702 | 62.7045 | -59.6054 | -59.9899 | 0.004578 | 0.004578 | 62.6404 | -59.7473 | 62.7182 | -59.7656 | -59.8846 | -59.6741 | -0.041199 | -0.068664 | -0.032043 | 0.1236 | 59.7336 | -0.26092 | 59.7748 | -0.21973 | -0.01831 | -0.09613 | -0.01831 | -0.036621 | 0.054932 | -0.15564 | 0.073242 | -0.13733 | 0.1648 | 122.4747 | -0.018311 | 122.4655 | 122.4381 | 122.3877 | 122.3969 | 122.3694 | -122.5067 | -122.4838 | 122.4335 | 122.4472 | 59.7427 | 59.7336
641.7656 | 122.6074 | -59.729 | 62.6999 | -0.033493 | 0.0010575 | 0.063521 | 0.091334 | 0.0020935 | -0.0014312 | -0.00096136 | -0.046081 | 0.0014356 | 0.063751 | 0.064253 | -0.013119 | 0.0018413 | -0.0028839 | -0.041199 | 62.6541 | -59.8022 | 62.645 | -59.6375 | -60.0494 | -0.064087 | -0.082397 | 62.6404 | -59.7702 | 62.6678 | -59.8206 | -59.9258 | -59.7244 | -0.073242 | -0.045776 | -0.054932 | 0.091553 | 59.6649 | -0.32043 | 59.7382 | -0.24719 | -0.041199 | -0.059509 | -0.032043 | -0.091553 | 0.004578 | -0.19684 | 0.045777 | -0.15564 | 0.16479 | 122.4472 | -0.050354 | 122.4381 | 122.4564 | 122.4106 | 122.3831 | 122.3694 | -122.5021 | -122.4701 | 122.374 | 122.3969 | 59.6878 | 59.6466
642.7656 | 122.6669 | -59.7061 | 62.7182 | -0.086899 | 0.0023391 | 0.064162 | 0.091975 | 0.0020935 | 0.000705 | -0.00053396 | -0.052185 | 0.00229 | 0.066101 | 0.063399 | -0.012691 | 0.0014141 | -0.0018157 | 0.004578 | 62.6678 | -59.7839 | 62.6907 | -59.6008 | -59.9899 | -0.022888 | 0 | 62.6404 | -59.7244 | 62.7045 | -59.7748 | -59.8984 | -59.6695 | -0.07782 | -0.050354 | -0.027466 | 0.10529 | 59.6832 | -0.28381 | 59.761 | -0.20599 | -0.01831 | -0.07782 | -0.013733 | -0.068664 | 0.036621 | -0.19226 | 0.054931 | -0.17395 | 0.18311 | 122.4747 | -0.050354 | 122.4289 | 122.4518 | 122.3648 | 122.374 | 122.3465 | -122.5021 | -122.4426 | 122.3969 | 122.4106 | 59.7107 | 59.7061
643.7656 | 122.6807 | -59.6878 | 62.7502 | -0.094528 | 0.00063028 | 0.061385 | 0.089625 | 0.0016663 | -0.0024994 | 0.00096124 | -0.1651 | -0.00070063 | 0.062683 | 0.060195 | -0.011623 | 0.0022687 | -0.00074771 | 0.013733 | 62.6633 | -59.7931 | 62.709 | -59.5871 | -59.9808 | 0.009155 | 0.09613 | 62.6358 | -59.7427 | 62.7182 | -59.7244 | -59.8526 | -59.642 | -0.10529 | -0.086975 | -0.041199 | 0.10071 | 59.697 | -0.29297 | 59.8022 | -0.18768 | -0.054932 | -0.11444 | -0.032043 | -0.036621 | 0.045776 | -0.1648 | 0.10071 | -0.10986 | 0.20599 | 122.5021 | 0.018311 | 122.4609 | 122.4564 | 122.3785 | 122.3511 | 122.3236 | -122.5433 | -122.493 | 122.3969 | 122.406 | 59.7015 | 59.7839
644.7656 | 122.6303 | -59.7473 | 62.7228 | -0.079269 | 0.0025529 | 0.063948 | 0.089625 | -0.0015381 | -0.0012176 | -0.0018158 | -0.052185 | 0.0010084 | 0.066529 | 0.062117 | -0.013332 | 0.0024823 | 0.0024567 | -0.004578 | 62.6816 | -59.7885 | 62.6907 | -59.61 | -60.022 | -0.027466 | -0.027466 | 62.6266 | -59.7427 | 62.709 | -59.7977 | -59.8892 | -59.6786 | -0.041199 | -0.041198 | -0.032043 | 0.13733 | 59.7198 | -0.27466 | 59.761 | -0.23346 | 0.004577 | -0.09613 | -0.013733 | -0.050354 | 0.068664 | -0.14191 | 0.064087 | -0.14648 | 0.17853 | 122.4792 | -0.054931 | 122.4518 | 122.4701 | 122.3694 | 122.4289 | 122.374 | -122.5113 | -122.4655 | 122.438 | 122.4564 | 59.7427 | 59.7198
645.7656 | 122.6257 | -59.7427 | 62.7319 | -0.06401 | 0.0014847 | 0.060957 | 0.091975 | 0.0018799 | -0.0007904 | -0.0013886 | -0.039978 | 0.001222 | 0.066742 | 0.061263 | -0.012478 | 0.0016277 | -0.0026703 | -0.009155 | 62.6678 | -59.7885 | 62.6724 | -59.6054 | -60.0128 | -0.022888 | -0.032043 | 62.6221 | -59.7519 | 62.6862 | -59.7748 | -59.9167 | -59.697 | -0.045776 | -0.064087 | -0.05951 | 0.13733 | 59.7198 | -0.27008 | 59.7656 | -0.2243 | -0.009155 | -0.10986 | -0.045777 | -0.032043 | 0.045777 | -0.17395 | 0.054932 | -0.1648 | 0.18311 | 122.4609 | -0.022888 | 122.438 | 122.4564 | 122.374 | 122.4106 | 122.3648 | -122.5204 | -122.4838 | 122.4152 | 122.4289 | 59.7336 | 59.7107
646.7656 | 122.4792 | -59.7885 | 62.6495 | -0.07164 | 0.0019119 | 0.065016 | 0.092189 | -0.00089728 | -0.001004 | -0.0016022 | -0.033874 | 0.00015377 | 0.066742 | 0.054 | -0.013332 | 0.0014141 | 0.0016021 | -0.073242 | 62.6587 | -59.8114 | 62.6175 | -59.7153 | -60.1044 | -0.10529 | -0.17853 | 62.6358 | -59.816 | 62.6266 | -59.8526 | -59.9762 | -59.5779 | -0.022888 | 0.009155 | -0.032043 | 0.073242 | 59.6832 | -0.31586 | 59.7061 | -0.29297 | -0.027466 | -0.013733 | -0.022888 | -0.064087 | 0.21057 | -0.18768 | 0.23804 | -0.16022 | 0.09613 | 122.4289 | -0.036621 | 122.4426 | 122.4701 | 122.4518 | 122.4472 | 122.4243 | -122.4609 | -122.4655 | 122.406 | 122.4152 | 59.7153 | 59.61
647.7656 | 122.5891 | -59.729 | 62.7136 | -0.07164 | 0.0012711 | 0.061812 | 0.092189 | 0.0016663 | -0.001004 | -0.00010676 | -0.033874 | 0.00058097 | 0.063538 | 0.055281 | -0.012478 | 0.0069683 | -0.0013885 | -0.086975 | 62.6816 | -59.8022 | 62.5946 | -59.7107 | -60.1089 | -0.12817 | -0.17395 | 62.6312 | -59.7794 | 62.4161 | -59.5322 | -59.6466 | -59.6283 | -0.073242 | -0.032043 | -0.11902 | 0.018311 | 59.6008 | -0.37994 | 59.6741 | -0.3067 | -0.050354 | -0.082397 | -0.29755 | 0.19684 | 0.10071 | 0.082398 | 0.15106 | 0.13275 | 0.091553 | 122.3969 | 0.24719 | 122.1954 | 122.4838 | 122.4106 | 122.4106 | 122.3602 | -122.5159 | -122.493 | 122.3236 | 122.1451 | 59.642 | 59.5551
648.7656 | 122.8683 | -59.6512 | 62.7731 | -0.086899 | -0.00086512 | 0.062453 | 0.090266 | 0.0018799 | -0.001004 | -0.0026704 | 0.10345 | -0.00070063 | 0.062683 | 0.054427 | -0.012691 | 0.00055973 | 0.00053409 | 0.022888 | 62.6541 | -59.7473 | 62.7731 | -59.491 | -59.8755 | 0.11902 | 0.14648 | 62.5946 | -59.729 | 62.8189 | -59.6329 | -59.7519 | -59.5505 | -0.09613 | -0.11902 | 0 | 0.16022 | 59.7702 | -0.2243 | 59.8663 | -0.12817 | -0.07782 | -0.17853 | 0.045777 | 0.01831 | 0.10071 | -0.10071 | 0.17853 | -0.022888 | 0.25635 | 122.5204 | 0.09613 | 122.5479 | 122.4014 | 122.3236 | 122.3053 | 122.2458 | -122.5204 | -122.5021 | 122.4243 | 122.4701 | 59.6741 | 59.7977
649.7656 | 122.6395 | -59.729 | 62.7182 | -0.13267 | -1.0718e-05 | 0.060103 | 0.092616 | 0.0020935 | -0.002713 | 0.00010684 | -0.021667 | 0.00015377 | 0.063324 | 0.064253 | -0.014614 | 0.00055973 | 0.00074769 | -0.082397 | 62.6358 | -59.8068 | 62.6266 | -59.6786 | -60.0861 | -0.091553 | -0.11902 | 62.6083 | -59.7794 | 62.6907 | -59.8251 | -59.9167 | -59.6924 | -0.07782 | -0.082398 | -0.091553 | 0.050354 | 59.6375 | -0.35706 | 59.7153 | -0.27924 | -0.050354 | -0.10986 | -0.027466 | -0.09613 | 0.036621 | -0.18768 | 0.086975 | -0.13733 | 0.12817 | 122.4335 | -0.045776 | 122.4701 | 122.4426 | 122.3877 | 122.3648 | 122.3373 | -122.525 | -122.4976 | 122.3557 | 122.4197 | 59.6466 | 59.61
650.7656 | 122.6028 | -59.7336 | 62.7274 | -0.12505 | -0.00043792 | 0.064375 | 0.092616 | 0.0033753 | -0.0022858 | 0.002243 | -0.06134 | -0.00091423 | 0.066742 | 0.067671 | -0.013332 | 0.0016277 | 0.0028839 | -0.050354 | 62.6678 | -59.8206 | 62.6358 | -59.6786 | -60.0632 | -0.10071 | -0.14648 | 62.6358 | -59.7931 | 62.6587 | -59.8572 | -59.9762 | -59.7198 | -0.086975 | -0.059509 | -0.091553 | 0.054932 | 59.6329 | -0.32959 | 59.7198 | -0.24261 | -0.059509 | -0.091553 | -0.068665 | -0.1236 | 0.013733 | -0.24261 | 0.073242 | -0.18311 | 0.14191 | 122.4564 | -0.064087 | 122.4518 | 122.4884 | 122.4289 | 122.4014 | 122.3694 | -122.5479 | -122.5204 | 122.3694 | 122.3923 | 59.6832 | 59.5871
651.7656 | 122.5983 | -59.7565 | 62.7045 | 0.14198 | -0.0019333 | 0.06288 | 0.092403 | 0.00081172 | -0.001004 | 0.0018158 | -0.055237 | -0.00048703 | 0.064179 | 0.068099 | -0.012264 | 0.00098693 | -0.00010671 | -0.086975 | 62.6953 | -59.8206 | 62.6312 | -59.7061 | -60.0952 | -0.10986 | -0.16022 | 62.6266 | -59.7794 | 62.6678 | -59.8206 | -59.9533 | -59.7015 | -0.064087 | -0.009156 | -0.073242 | 0.050354 | 59.6466 | -0.33875 | 59.7107 | -0.27466 | -0.022888 | -0.07782 | -0.036621 | -0.064087 | 0.054932 | -0.19684 | 0.07782 | -0.17395 | 0.11444 | 122.4518 | -0.041199 | 122.4472 | 122.5159 | 122.406 | 122.4518 | 122.3831 | -122.525 | -122.4838 | 122.3877 | 122.4243 | 59.6695 | 59.5963
652.7656 | 122.6349 | -59.7427 | 62.6999 | 0.050431 | 0.00084388 | 0.063521 | 0.090907 | -0.0051697 | 0.0011322 | -0.0024566 | -0.018616 | -5.9826e-05 | 0.063751 | 0.056136 | -0.0144 | 0.0020551 | 0.00010689 | -0.12817 | 62.6358 | -59.8114 | 62.6129 | -59.7198 | -60.1044 | -0.12817 | -0.13275 | 62.6495 | -59.7977 | 62.6633 | -59.8434 | -59.9396 | -59.7153 | -0.068664 | -0.064087 | -0.086975 | 0.022888 | 59.6146 | -0.36163 | 59.6832 | -0.29297 | -0.054931 | -0.050354 | -0.036621 | -0.10071 | 0.027466 | -0.19684 | 0.082397 | -0.14191 | 0.091552 | 122.4243 | -0.045777 | 122.4609 | 122.4472 | 122.4472 | 122.3785 | 122.3923 | -122.5113 | -122.4976 | 122.3557 | 122.406 | 59.6146 | 59.61
653.7656 | 122.7493 | -59.6832 | 62.7182 | -0.29289 | 0.0021255 | 0.062453 | 0.090053 | -0.0023925 | -0.001004 | -0.0024566 | 0.079041 | -0.0013416 | 0.064606 | 0.065535 | -0.013119 | -8.1274e-05 | -0.0024567 | -0.045776 | 62.6587 | -59.7427 | 62.7594 | -59.4955 | -59.8755 | 0.10986 | 0.13275 | 62.6129 | -59.729 | 62.796 | -59.642 | -59.7336 | -59.5734 | -0.059509 | -0.05951 | 0.041198 | 0.18768 | 59.7931 | -0.19226 | 59.8526 | -0.13275 | -0.045776 | -0.10529 | 0.07782 | 0.041199 | 0.10986 | -0.050354 | 0.15564 | -0.004578 | 0.24719 | 122.5021 | 0.086975 | 122.525 | 122.4014 | 122.3419 | 122.3419 | 122.2961 | -122.4609 | -122.4472 | 122.4426 | 122.4792 | 59.6375 | 59.816
654.7656 | 122.7402 | -59.7153 | 62.6999 | -0.094528 | -0.00022432 | 0.062025 | 0.092189 | 0.00081172 | -0.001004 | -0.00074776 | -0.024719 | -0.00027343 | 0.064606 | 0.058486 | -0.013973 | 0.00055973 | 0.00074769 | -0.07782 | 62.6358 | -59.7977 | 62.6816 | -59.6283 | -60.0311 | -0.064087 | -0.059509 | 62.5854 | -59.7702 | 62.7502 | -59.7336 | -59.8251 | -59.6054 | -0.082397 | -0.064087 | -0.01831 | 0.086975 | 59.6512 | -0.31586 | 59.7336 | -0.23346 | -0.054932 | -0.11444 | 0.050354 | -0.018311 | 0.10986 | -0.10986 | 0.1648 | -0.054931 | 0.16937 | 122.4792 | 0.036621 | 122.5204 | 122.4335 | 122.3557 | 122.3511 | 122.3007 | -122.4976 | -122.4701 | 122.3969 | 122.4655 | 59.6375 | 59.6558
655.7656 | 122.7493 | -59.7015 | 62.6633 | -0.06401 | 0.00020288 | 0.063094 | 0.092189 | 0.0014527 | -0.0005768 | -0.00032036 | -0.033874 | -5.9826e-05 | 0.064179 | 0.065535 | -0.013332 | 0.0031231 | -0.0054473 | -0.073242 | 62.6266 | -59.7839 | 62.7045 | -59.6191 | -60.022 | -0.050354 | -0.054932 | 62.5946 | -59.761 | 62.7594 | -59.7198 | -59.8251 | -59.6054 | -0.082398 | -0.036621 | 0.041199 | 0.082397 | 59.6512 | -0.32044 | 59.7336 | -0.23804 | -0.059509 | -0.068665 | 0.09613 | -0.018311 | 0.09613 | -0.1236 | 0.15564 | -0.064087 | 0.16479 | 122.4884 | 0.041198 | 122.5204 | 122.4106 | 122.3557 | 122.3282 | 122.2961 | -122.4472 | -122.4243 | 122.406 | 122.4609 | 59.6283 | 59.6466
656.7656 | 122.6669 | -59.7473 | 62.6999 | -0.06401 | 0.00041648 | 0.063307 | 0.093471 | -4.2682e-05 | -0.0020722 | -0.0020294 | -0.06134 | 0.0014356 | 0.065033 | 0.06639 | -0.015041 | 0.0020551 | 0.0024567 | -0.086975 | 62.6678 | -59.8297 | 62.6266 | -59.6786 | -60.0632 | -0.086975 | -0.13275 | 62.6266 | -59.7839 | 62.6862 | -59.8022 | -59.9213 | -59.6832 | -0.082398 | -0.032043 | -0.073242 | 0.068664 | 59.6603 | -0.31586 | 59.7427 | -0.23346 | -0.036622 | -0.073242 | -0.013733 | -0.054932 | 0.064086 | -0.17395 | 0.10071 | -0.13733 | 0.15106 | 122.4564 | -0.01831 | 122.4701 | 122.4976 | 122.4106 | 122.4152 | 122.374 | -122.5296 | -122.4838 | 122.374 | 122.4335 | 59.6603 | 59.6146
657.7656 | 122.731 | -59.7427 | 62.6541 | -0.13267 | 0.00063028 | 0.065016 | 0.090053 | 0.0025207 | 0.0002778 | -0.0016022 | -0.027771 | 0.001222 | 0.062897 | 0.062972 | -0.013119 | -0.00050847 | -0.0043793 | -0.064087 | 62.6221 | -59.7931 | 62.6999 | -59.5779 | -59.9716 | -0.032043 | -0.032043 | 62.5946 | -59.7794 | 62.7777 | -59.6786 | -59.9899 | -59.761 | -0.050354 | -0.032044 | 0.045776 | 0.16479 | 59.7107 | -0.22888 | 59.761 | -0.17853 | -0.036621 | -0.05951 | 0.1236 | 0.064087 | -0.01831 | -0.24719 | 0.018311 | -0.21057 | 0.21515 | 122.493 | 0.10071 | 122.5571 | 122.4152 | 122.374 | 122.3648 | 122.3373 | -122.4472 | -122.4335 | 122.4426 | 122.5204 | 59.6786 | 59.7107
658.7656 | 122.7448 | -59.6832 | 62.6999 | -0.0029755 | 0.00084388 | 0.062239 | 0.089839 | -0.0045289 | -0.0012176 | 0.00032044 | -0.0094604 | -0.00048703 | 0.064179 | 0.058913 | -0.015041 | 0.00077333 | -0.0011749 | 0.064087 | 62.6358 | -59.7473 | 62.5488 | -59.7702 | -59.8206 | 0.16479 | 0.15106 | 62.5854 | -59.7336 | 62.7823 | -59.6466 | -59.7244 | -59.5825 | -0.064086 | -0.064087 | -0.15106 | -0.086975 | 59.848 | -0.13733 | 59.9121 | -0.073243 | -0.050354 | -0.11444 | 0.082398 | 0.036622 | 0.10071 | -0.041198 | 0.15106 | 0.009156 | -0.022889 | 122.2961 | 0.086976 | 122.5159 | 122.3831 | 122.319 | 122.319 | 122.2687 | -122.4472 | -122.4335 | 122.2321 | 122.4655 | 59.7473 | 59.8343
659.7656 | 122.6852 | -59.7198 | 62.7045 | -0.10979 | 0.0023391 | 0.062666 | 0.093471 | 0.00038452 | -0.0022858 | -0.0033112 | 0.027161 | -0.00027343 | 0.061829 | 0.057418 | -0.015682 | 0.0029095 | 0.00096129 | -0.045776 | 62.6038 | -59.7839 | 62.7136 | -59.5734 | -59.9854 | -0.018311 | -0.041199 | 62.5946 | -59.7519 | 62.7319 | -59.7519 | -59.848 | -59.642 | -0.064087 | -0.10071 | 0.009155 | 0.14649 | 59.7015 | -0.2655 | 59.7656 | -0.20142 | -0.032043 | -0.10986 | 0.027466 | -0.032043 | 0.07782 | -0.12817 | 0.10986 | -0.09613 | 0.21057 | 122.4976 | 0 | 122.4838 | 122.3877 | 122.3465 | 122.3236 | 122.3145 | -122.4884 | -122.4564 | 122.4335 | 122.4518 | 59.6741 | 59.6787
660.7656 | 122.7264 | -59.6878 | 62.6862 | -0.086899 | -1.0718e-05 | 0.064375 | 0.091334 | 0.00081172 | 6.4004e-05 | 0.0013886 | -0.012512 | -0.00027343 | 0.063324 | 0.055709 | -0.015469 | 0.0024823 | -0.0030975 | -0.041199 | 62.6129 | -59.7702 | 62.7502 | -59.5367 | -59.9762 | -0.022888 | -0.013733 | 62.59 | -59.7382 | 62.7731 | -59.7061 | -59.8114 | -59.6054 | -0.082398 | -0.073242 | 0.064087 | 0.15106 | 59.6649 | -0.28839 | 59.7473 | -0.20599 | -0.050354 | -0.09613 | 0.086975 | -0.018311 | 0.082397 | -0.1236 | 0.13275 | -0.073242 | 0.23346 | 122.5204 | 0.032043 | 122.5113 | 122.3831 | 122.3282 | 122.3007 | 122.2778 | -122.4564 | -122.4243 | 122.438 | 122.4609 | 59.6466 | 59.6741
661.7656 | 122.699 | -59.6924 | 62.677 | -0.12505 | 0.00020288 | 0.063094 | 0.089839 | 0.00081172 | -0.002713 | -0.0020294 | -0.0094604 | -0.00027343 | 0.063324 | 0.062117 | -0.015469 | 0.00098693 | -0.0011749 | -0.032043 | 62.6038 | -59.7794 | 62.7411 | -59.5367 | -59.9579 | -0.032043 | -0.013733 | 62.5854 | -59.7473 | 62.7823 | -59.7198 | -59.8206 | -59.6146 | -0.086975 | -0.073242 | 0.064087 | 0.15564 | 59.6603 | -0.2655 | 59.7473 | -0.17853 | -0.054931 | -0.091553 | 0.10529 | -0.027466 | 0.07782 | -0.12817 | 0.13275 | -0.073243 | 0.24262 | 122.5204 | 0.027465 | 122.5296 | 122.3831 | 122.3328 | 122.2961 | 122.2778 | -122.4564 | -122.4243 | 122.4335 | 122.4747 | 59.6603 | 59.6786
662.7656 | 122.7081 | -59.7198 | 62.6816 | -0.10979 | 0.0010575 | 0.061812 | 0.091762 | -0.00068368 | 0.0015594 | -0.0024566 | 0.0088502 | -0.00070063 | 0.06482 | 0.061476 | -0.013973 | 0.0012005 | -0.0026703 | -0.032043 | 62.6038 | -59.7382 | 62.7411 | -59.5551 | -59.9625 | -0.022888 | -0.004578 | 62.5809 | -59.7794 | 62.7686 | -59.7015 | -59.816 | -59.6146 | -0.01831 | -0.07782 | 0.059509 | 0.1648 | 59.697 | -0.24261 | 59.7153 | -0.2243 | -0.059509 | -0.10071 | 0.086975 | 0.018311 | 0.10529 | -0.09613 | 0.1648 | -0.036621 | 0.18311 | 122.4792 | 0.07782 | 122.5479 | 122.3419 | 122.3602 | 122.3236 | 122.3007 | -122.4197 | -122.4609 | 122.4609 | 122.4884 | 59.6878 | 59.7153
663.7656 | 122.5983 | -59.7382 | 62.764 | -0.06401 | -0.00043792 | 0.062239 | 0.092403 | -4.2682e-05 | -0.0031402 | -0.0018158 | -0.030823 | 0.00058097 | 0.06482 | 0.058486 | -0.012905 | 0.00055973 | -0.0016021 | 0.004578 | 62.6953 | -59.7748 | 62.6862 | -59.6237 | -59.9991 | 0.027466 | 0.009155 | 62.677 | -59.7427 | 62.7548 | -59.5825 | -60.0586 | -59.8801 | -0.036621 | -0.068665 | -0.07782 | 0.11444 | 59.7656 | -0.26093 | 59.8022 | -0.2243 | -0.004578 | -0.086975 | -0.009155 | 0.15564 | -0.14191 | -0.32043 | -0.13733 | -0.31586 | 0.15106 | 122.4609 | 0.16022 | 122.4976 | 122.4701 | 122.4197 | 122.4335 | 122.4152 | -122.5388 | -122.5067 | 122.4243 | 122.493 | 59.7427 | 59.7473
664.7656 | 122.7127 | -59.7153 | 62.677 | -0.07164 | 0.0012711 | 0.062453 | 0.091975 | 0.0040161 | -0.0029266 | 0.0013886 | -0.064392 | -0.0024096 | 0.061829 | 0.06404 | -0.014614 | 0.0029095 | 0.00032049 | -0.032043 | 62.6175 | -59.7931 | 62.7228 | -59.5779 | -59.9579 | -0.18768 | 0.1831 | 62.6038 | -59.7748 | 62.7869 | -59.6786 | -59.7931 | -59.6054 | -0.07782 | -0.059509 | 0.045776 | 0.13733 | 59.5276 | -0.24262 | 59.6054 | -0.1648 | -0.059509 | -0.073242 | 0.10986 | 0.036621 | 0.10986 | -0.07782 | 0.16937 | -0.018311 | 0.21515 | 122.5159 | 0.09613 | 122.5616 | 122.4106 | 122.3785 | 122.3328 | 122.319 | -122.4701 | -122.4518 | 122.438 | 122.5021 | 59.6832 | 59.8984
665.7656 | 122.6898 | -59.7198 | 62.6953 | -0.1403 | 0.00020288 | 0.061812 | 0.089839 | 0.0010253 | -0.0022858 | -0.0020294 | -0.018616 | -0.001128 | 0.061615 | 0.059767 | -0.013332 | 0.0018413 | -0.0028839 | -0.054932 | 62.6083 | -59.7702 | 62.7045 | -59.5779 | -60.0037 | -0.032043 | -0.059509 | 62.5992 | -59.7748 | 62.7365 | -59.7519 | -59.8251 | -59.6283 | -0.050354 | -0.086975 | 0.009156 | 0.14191 | 59.6878 | -0.28381 | 59.7382 | -0.23346 | -0.054931 | -0.09613 | 0.041199 | -0.032043 | 0.091553 | -0.10528 | 0.14648 | -0.050354 | 0.19226 | 122.4747 | 0.022888 | 122.5113 | 122.3785 | 122.374 | 122.3282 | 122.319 | -122.4655 | -122.4701 | 122.4243 | 122.4564 | 59.6649 | 59.6603
666.7656 | 122.7448 | -59.729 | 62.6816 | -0.11742 | 0.0019119 | 0.063948 | 0.089839 | 0.00038452 | -0.0012176 | 0.00053404 | -0.027771 | -0.0024096 | 0.060974 | 0.058913 | -0.015896 | 0.00034613 | -0.0043793 | -0.036621 | 62.6129 | -59.7931 | 62.7319 | -59.5459 | -59.9579 | -0.022888 | -0.013733 | 62.5671 | -59.7519 | 62.7914 | -59.7244 | -59.816 | -59.6283 | -0.064087 | -0.068665 | 0.050354 | 0.18311 | 59.7061 | -0.22888 | 59.7702 | -0.1648 | -0.022888 | -0.11444 | 0.10986 | 0.004578 | 0.10071 | -0.086975 | 0.1236 | -0.064087 | 0.24719 | 122.525 | 0.027466 | 122.5433 | 122.406 | 122.319 | 122.3419 | 122.2961 | -122.4747 | -122.4335 | 122.4609 | 122.5204 | 59.6924 | 59.7153
667.7656 | 122.6807 | -59.7015 | 62.6999 | -0.086899 | 0.0010575 | 0.061171 | 0.089839 | 0.0016663 | 0.0004914 | -0.0037384 | -0.015564 | -5.9826e-05 | 0.062256 | 0.059981 | -0.012905 | 0.0020551 | -0.00053411 | -0.054932 | 62.6358 | -59.8114 | 62.6907 | -59.3948 | -59.8068 | -0.082397 | -0.041199 | 62.6038 | -59.7656 | 62.7365 | -59.7336 | -59.8434 | -59.6466 | -0.10986 | -0.064087 | -0.009155 | 0.3067 | 59.6191 | -0.10529 | 59.729 | 0.004577 | -0.064087 | -0.09613 | 0.036621 | -0.032044 | 0.054932 | -0.14191 | 0.11902 | -0.07782 | 0.41656 | 122.5021 | 0.032043 | 122.5021 | 122.4472 | 122.3694 | 122.3373 | 122.3053 | -122.5113 | -122.4655 | 122.3923 | 122.438 | 59.6466 | 59.6603
668.7656 | 122.6212 | -59.7153 | 62.7686 | -0.086899 | 0.0010575 | 0.062666 | 0.091548 | -0.00089728 | 0.0004914 | -0.0054474 | -0.046081 | 0.00079477 | 0.063751 | 0.067458 | -0.01376 | 0.0014141 | -0.0022431 | -0.13733 | 62.6862 | -59.8022 | 62.6724 | -59.6466 | -60.0082 | 0.018311 | 0.009155 | 62.6495 | -59.7565 | 62.709 | -59.7748 | -59.8801 | -59.6786 | -0.086975 | -0.082398 | -0.096131 | 0.068665 | 59.7336 | -0.29297 | 59.8206 | -0.20599 | -0.041199 | -0.11902 | -0.05951 | -0.059509 | 0.036621 | -0.16479 | 0.07782 | -0.1236 | 0.15564 | 122.4747 | -0.01831 | 122.4655 | 122.4884 | 122.406 | 122.4014 | 122.3648 | -122.5708 | -122.525 | 122.3877 | 122.4243 | 59.5779 | 59.7244
669.7656 | 122.7036 | -59.7061 | 62.7045 | -0.12505 | 0.00041648 | 0.063307 | 0.090266 | 0.0014527 | -0.0014312 | -0.0018158 | -0.024719 | -0.00091423 | 0.063751 | 0.059554 | -0.01376 | 0.0022687 | -0.0039521 | -0.054932 | 62.6083 | -59.7794 | 62.6999 | -59.5734 | -59.9762 | -0.004578 | -0.022888 | 62.5809 | -59.7702 | 62.7411 | -59.7244 | -59.8389 | -59.642 | -0.073242 | -0.096131 | -0.004578 | 0.13275 | 59.7015 | -0.27008 | 59.7748 | -0.19684 | -0.064087 | -0.1236 | 0.036621 | -0.01831 | 0.064087 | -0.13275 | 0.12817 | -0.068664 | 0.20599 | 122.4792 | 0.045777 | 122.5113 | 122.3877 | 122.3511 | 122.3145 | 122.287 | -122.4838 | -122.4747 | 122.406 | 122.4472 | 59.6512 | 59.6832
670.7656 | 122.7402 | -59.6878 | 62.6907 | -0.13267 | 0.0027665 | 0.064589 | 0.092403 | 0.00081172 | -0.0024994 | -0.00096136 | -0.036926 | -0.00091423 | 0.062042 | 0.059767 | -0.0144 | 0.0020551 | -0.0016021 | -0.013733 | 62.5992 | -59.7977 | 62.7411 | -59.5367 | -59.967 | -0.022888 | 0 | 62.59 | -59.761 | 62.7731 | -59.7015 | -59.8251 | -59.6054 | -0.10986 | -0.091553 | 0.050354 | 0.15106 | 59.6649 | -0.27924 | 59.7748 | -0.16937 | -0.073242 | -0.10071 | 0.082397 | -0.013733 | 0.082397 | -0.13733 | 0.15564 | -0.064087 | 0.26093 | 122.5388 | 0.059509 | 122.5342 | 122.3969 | 122.3511 | 122.287 | 122.2778 | -122.4884 | -122.4518 | 122.4289 | 122.4609 | 59.6741 | 59.6878
671.7656 | 122.7448 | -59.7015 | 62.709 | -0.15556 | 0.00084388 | 0.063734 | 0.091334 | -0.0026063 | 0.000705 | -0.00053396 | -0.039978 | -0.00027343 | 0.062683 | 0.063613 | -0.013973 | 0.0022687 | -0.0022431 | -0.004578 | 62.6083 | -59.761 | 62.7457 | -59.5459 | -59.9579 | -0.027466 | 0 | 62.5809 | -59.7565 | 62.7777 | -59.697 | -59.8068 | -59.6237 | -0.059509 | -0.10071 | 0.036622 | 0.15564 | 59.6741 | -0.25635 | 59.7336 | -0.19684 | -0.054932 | -0.12817 | 0.068665 | 0.004578 | 0.07782 | -0.10529 | 0.13275 | -0.050354 | 0.21515 | 122.5067 | 0.05951 | 122.5342 | 122.3694 | 122.3373 | 122.3099 | 122.2824 | -122.4701 | -122.4655 | 122.4472 | 122.4792 | 59.697 | 59.7015
672.7656 | 122.6944 | -59.7015 | 62.6999 | -0.11742 | 0.00084388 | 0.062239 | 0.090694 | 0.00038452 | -0.001004 | -0.00010676 | -0.024719 | -0.00070063 | 0.066529 | 0.05464 | -0.01141 | 0.0016277 | -0.0022431 | -0.050354 | 62.5854 | -59.7794 | 62.7365 | -59.5459 | -59.967 | -0.027466 | -0.004578 | 62.5946 | -59.7656 | 62.7548 | -59.729 | -59.8343 | -59.642 | -0.07782 | -0.11444 | 0.036621 | 0.15564 | 59.6741 | -0.2655 | 59.7519 | -0.18768 | -0.064087 | -0.10529 | 0.054932 | -0.027466 | 0.059509 | -0.13275 | 0.1236 | -0.068665 | 0.23346 | 122.5159 | 0.036621 | 122.5204 | 122.3648 | 122.3602 | 122.287 | 122.2961 | -122.4792 | -122.4655 | 122.438 | 122.4564 | 59.6512 | 59.697
673.7656 | 122.699 | -59.7153 | 62.6587 | -0.10216 | 0.00063028 | 0.062453 | 0.09283 | 0.0010253 | -0.0018586 | -0.0013886 | -0.0064086 | -0.0019824 | 0.065888 | 0.061904 | -0.0144 | 0.0014141 | -0.0041657 | -0.059509 | 62.6221 | -59.7794 | 62.7136 | -59.5871 | -60.0082 | -0.027466 | -0.050354 | 62.5946 | -59.7702 | 62.8052 | -59.8572 | -59.848 | -59.6283 | -0.064087 | -0.036621 | 0.054932 | 0.12817 | 59.6878 | -0.29297 | 59.7519 | -0.22888 | -0.054932 | -0.064087 | 0.14649 | -0.14191 | 0.086975 | -0.13275 | 0.14191 | -0.077819 | 0.19226 | 122.493 | -0.086975 | 122.5754 | 122.4014 | 122.3648 | 122.3373 | 122.3099 | -122.438 | -122.4289 | 122.4289 | 122.5204 | 59.6558 | 59.6649
674.7656 | 122.6898 | -59.7107 | 62.6953 | -0.15556 | 0.00041648 | 0.062666 | 0.091762 | 0.00017092 | -0.0018586 | -0.0018158 | -0.021667 | -0.00048703 | 0.063324 | 0.058272 | -0.0144 | 0.0031231 | -0.0028839 | -0.064087 | 62.6266 | -59.7885 | 62.6907 | -59.6191 | -59.9991 | -0.032043 | -0.045776 | 62.5946 | -59.7336 | 62.8372 | -59.5642 | -59.9808 | -59.7427 | -0.07782 | -0.068664 | -0.004577 | 0.091552 | 59.6786 | -0.28839 | 59.7565 | -0.21057 | -0.022889 | -0.10071 | 0.14191 | 0.14648 | -0.032044 | -0.27008 | -0.009155 | -0.24719 | 0.16937 | 122.4792 | 0.16937 | 122.5708 | 122.4152 | 122.3282 | 122.3373 | 122.3053 | -122.4838 | -122.4289 | 122.4014 | 122.5479 | 59.6466 | 59.6649
675.7656 | 122.7173 | -59.7061 | 62.709 | -0.10979 | 0.00063028 | 0.061812 | 0.090053 | -0.0023925 | 0.0019866 | -0.00074776 | -0.012512 | 0.00058097 | 0.06247 | 0.062117 | -0.014187 | 0.0029095 | 0.00032049 | -0.032043 | 62.6266 | -59.8022 | 62.7136 | -59.6054 | -59.967 | 0.004578 | -0.032043 | 62.6175 | -59.7473 | 62.7502 | -59.7244 | -59.8022 | -59.6237 | -0.09613 | -0.082397 | 0.004578 | 0.10071 | 59.7107 | -0.26093 | 59.8068 | -0.1648 | -0.041198 | -0.091552 | 0.041199 | -0.01831 | 0.082398 | -0.09613 | 0.1236 | -0.054932 | 0.19684 | 122.5159 | 0.022888 | 122.4976 | 122.4289 | 122.3648 | 122.3328 | 122.3236 | -122.5113 | -122.4564 | 122.4197 | 122.4564 | 59.6741 | 59.6741
676.7656 | 122.6395 | -59.7107 | 62.7274 | -0.10979 | 0.0012711 | 0.062666 | 0.090694 | -0.0043151 | -0.0031402 | -0.003952 | -0.012512 | 0.00036737 | 0.063965 | 0.059981 | -0.014614 | 0.0031231 | -0.0011749 | -0.07782 | 62.6404 | -59.7839 | 62.7136 | -59.5963 | -59.9991 | -0.041199 | -0.054932 | 62.5809 | -59.7473 | 62.7502 | -59.7382 | -59.8343 | -59.642 | -0.073243 | -0.086975 | -0.013733 | 0.11444 | 59.6695 | -0.28839 | 59.7427 | -0.21515 | -0.036621 | -0.14648 | 0.022888 | -0.027466 | 0.068664 | -0.1236 | 0.10529 | -0.086976 | 0.18768 | 122.4976 | 0.009155 | 122.4976 | 122.4243 | 122.3282 | 122.3511 | 122.2916 | -122.5113 | -122.4747 | 122.4243 | 122.4609 | 59.6329 | 59.6558
677.7656 | 122.7081 | -59.7061 | 62.6862 | -0.10216 | 0.0012711 | 0.062666 | 0.093043 | -0.0023925 | 0.000705 | -0.0013886 | -0.058289 | -5.9826e-05 | 0.064392 | 0.066603 | -0.013973 | 0.0018413 | 0.0030975 | -0.022888 | 62.5992 | -59.7748 | 62.7365 | -59.5413 | -59.9854 | -0.027466 | 0.009155 | 62.558 | -59.761 | 62.7823 | -59.7061 | -59.8297 | -59.6191 | -0.068664 | -0.086975 | 0.050354 | 0.16479 | 59.6787 | -0.27924 | 59.7473 | -0.21057 | -0.054931 | -0.12817 | 0.096131 | 0 | 0.086975 | -0.1236 | 0.14191 | -0.068665 | 0.23346 | 122.5113 | 0.054931 | 122.5433 | 122.374 | 122.319 | 122.3053 | 122.2641 | -122.4609 | -122.4472 | 122.4426 | 122.4884 | 59.6832 | 59.7153
678.7656 | 122.7173 | -59.6924 | 62.6587 | -0.11742 | 0.0016983 | 0.062666 | 0.092403 | 0.0031617 | -0.0003632 | 0.00010684 | -0.067444 | -0.00027343 | 0.064392 | 0.065108 | -0.0144 | 0.00055973 | -0.0041657 | -0.027466 | 62.5992 | -59.7794 | 62.7686 | -59.5322 | -59.9533 | -0.022888 | 0.009155 | 62.5671 | -59.7702 | 62.7777 | -59.7015 | -59.8206 | -59.6146 | -0.086975 | -0.059509 | 0.10986 | 0.16022 | 59.6695 | -0.26093 | 59.7565 | -0.17395 | -0.07782 | -0.091552 | 0.11902 | -0.009155 | 0.07782 | -0.12817 | 0.15564 | -0.050354 | 0.24719 | 122.5479 | 0.068665 | 122.5479 | 122.3785 | 122.3373 | 122.2916 | 122.2595 | -122.438 | -122.4289 | 122.4609 | 122.4701 | 59.6649 | 59.7015
679.7656 | 122.6624 | -59.7382 | 62.6999 | -0.12505 | 0.00063028 | 0.059035 | 0.091334 | 0.0042297 | -0.0018586 | 0.00053404 | -0.055237 | -0.00091423 | 0.064606 | 0.060195 | -0.015255 | 0.0022687 | 0.0026703 | -0.059509 | 62.6266 | -59.7931 | 62.709 | -59.5917 | -59.9854 | -0.027466 | -0.032043 | 62.6129 | -59.7565 | 62.7365 | -59.7336 | -59.8251 | -59.642 | -0.054932 | -0.073242 | 0.009155 | 0.14648 | 59.7107 | -0.24719 | 59.7656 | -0.19226 | -0.018311 | -0.086975 | 0.036621 | 0.004577 | 0.09613 | -0.086975 | 0.11444 | -0.068664 | 0.20142 | 122.5021 | 0.022888 | 122.493 | 122.4197 | 122.3694 | 122.3648 | 122.3511 | -122.493 | -122.4564 | 122.4472 | 122.4747 | 59.6787 | 59.7061
680.7656 | 122.6715 | -59.7107 | 62.6816 | -0.10216 | 0.00041648 | 0.061598 | 0.093898 | 0.0014527 | -0.0018586 | -0.00074776 | -0.039978 | -5.9826e-05 | 0.063751 | 0.060408 | -0.01376 | 0.0020551 | -0.0024567 | -0.036621 | 62.5854 | -59.7702 | 62.7228 | -59.5596 | -59.9854 | -0.036621 | -0.041199 | 62.5809 | -59.7519 | 62.7457 | -59.7473 | -59.848 | -59.6375 | -0.05951 | -0.096131 | 0.041198 | 0.15106 | 59.6741 | -0.27466 | 59.7336 | -0.21515 | -0.041199 | -0.10071 | 0.064087 | -0.036621 | 0.073242 | -0.13733 | 0.11444 | -0.09613 | 0.21057 | 122.493 | 0.004578 | 122.4976 | 122.3557 | 122.3328 | 122.2961 | 122.2916 | -122.4518 | -122.4335 | 122.4335 | 122.4564 | 59.6741 | 59.6695
681.7656 | 122.7127 | -59.7107 | 62.6907 | -0.10216 | 0.0012711 | 0.061385 | 0.091121 | 0.0010253 | 0.0004914 | -0.0018158 | -0.10712 | 0.0010084 | 0.063111 | 0.062758 | -0.012478 | 0.0014141 | -0.00010671 | -0.059509 | 62.6266 | -59.7931 | 62.7136 | -59.6603 | -59.6878 | 0.10529 | -0.041199 | 62.5992 | -59.7702 | 62.7502 | -59.7153 | -59.8526 | -59.6558 | -0.082398 | -0.064087 | 0.022888 | 0.050354 | 59.816 | 0.022888 | 59.8984 | 0.10529 | -0.05951 | -0.091553 | 0.059509 | -0.004578 | 0.054931 | -0.14191 | 0.11444 | -0.082397 | 0.13275 | 122.5067 | 0.054932 | 122.5204 | 122.4197 | 122.3694 | 122.3373 | 122.3099 | -122.4838 | -122.4609 | 122.4243 | 122.4609 | 59.6512 | 59.6695
682.7656 | 122.6898 | -59.729 | 62.7045 | -0.10979 | 0.00041648 | 0.062025 | 0.090266 | -0.00089728 | -0.0029266 | -0.0018158 | 0.027161 | 0.0014356 | 0.064392 | 0.061263 | -0.012905 | 0.0020551 | -0.0030975 | -0.073242 | 62.6129 | -59.7702 | 62.7136 | -59.5963 | -59.9762 | -0.018311 | 0.07782 | 62.6221 | -59.729 | 62.7502 | -59.7473 | -59.8434 | -59.6466 | -0.041199 | -0.091553 | 0.009155 | 0.13275 | 59.7107 | -0.24719 | 59.7519 | -0.20599 | 0 | -0.082398 | 0.045776 | -0.01831 | 0.082398 | -0.11444 | 0.082398 | -0.11444 | 0.17395 | 122.4838 | -0.01831 | 122.4792 | 122.3831 | 122.3511 | 122.3419 | 122.3511 | -122.4747 | -122.4335 | 122.4426 | 122.4792 | 59.6558 | 59.8068
683.7656 | 122.7036 | -59.697 | 62.709 | -0.10979 | -1.0718e-05 | 0.061171 | 0.091762 | 0.0010253 | -0.0012176 | 0.00032044 | -0.033874 | 0.001222 | 0.062897 | 0.060195 | -0.013546 | -0.0013629 | -0.0050201 | -0.041199 | 62.6221 | -59.7748 | 62.7228 | -59.5825 | -59.9533 | 0.013733 | -0.013733 | 62.6083 | -59.7427 | 62.7594 | -59.7015 | -59.8068 | -59.6146 | -0.07782 | -0.086975 | 0.013733 | 0.11444 | 59.7107 | -0.25635 | 59.7885 | -0.17853 | -0.045777 | -0.10071 | 0.050354 | -0.004578 | 0.082397 | -0.10986 | 0.12817 | -0.064087 | 0.19226 | 122.4976 | 0.041199 | 122.5021 | 122.3969 | 122.3511 | 122.319 | 122.3053 | -122.4838 | -122.4518 | 122.4197 | 122.4564 | 59.6558 | 59.6832
684.7656 | 122.699 | -59.7107 | 62.7045 | -0.086899 | -1.0718e-05 | 0.062239 | 0.089198 | 0.00017092 | -0.0003632 | -0.002884 | -0.049133 | 0.0010084 | 0.066101 | 0.060408 | -0.013332 | 0.0020551 | -0.0054473 | -0.036621 | 62.6083 | -59.761 | 62.7365 | -59.5551 | -59.9854 | -0.032043 | -0.018311 | 62.5626 | -59.761 | 62.7594 | -59.7336 | -59.8297 | -59.6375 | -0.050354 | -0.096131 | 0.032043 | 0.15564 | 59.6786 | -0.27466 | 59.729 | -0.22431 | -0.050354 | -0.14191 | 0.054931 | -0.022889 | 0.073242 | -0.11902 | 0.1236 | -0.068665 | 0.20599 | 122.4976 | 0.027465 | 122.5204 | 122.3694 | 122.3236 | 122.319 | 122.2733 | -122.4655 | -122.4655 | 122.4472 | 122.4701 | 59.6741 | 59.6924
685.7656 | 122.7173 | -59.7153 | 62.6999 | -0.06401 | -0.0019333 | 0.063948 | 0.091334 | -0.00046988 | -0.0012176 | -0.00074776 | -0.052185 | -0.0015552 | 0.063751 | 0.064894 | -0.012478 | 0.0024823 | -0.00053411 | -0.041199 | 62.6221 | -59.7702 | 62.7228 | -59.5596 | -59.9762 | -0.036621 | -0.004578 | 62.6175 | -59.7565 | 62.7548 | -59.7244 | -59.816 | -59.6283 | -0.054932 | -0.07782 | 0.022888 | 0.15564 | 59.6787 | -0.26093 | 59.7336 | -0.20599 | -0.041199 | -0.082397 | 0.054932 | -0.009155 | 0.086975 | -0.10071 | 0.12817 | -0.059509 | 0.21057 | 122.493 | 0.032044 | 122.5113 | 122.3923 | 122.374 | 122.3373 | 122.3328 | -122.4701 | -122.4564 | 122.438 | 122.4701 | 59.6741 | 59.7107
686.7656 | 122.6761 | -59.7473 | 62.6953 | -0.11742 | 0.00041648 | 0.063307 | 0.090266 | 0.0010253 | -0.0005768 | -0.00053396 | -0.046081 | -0.00048703 | 0.06482 | 0.052077 | -0.015255 | 0.00055973 | 0.0020295 | -0.068665 | 62.6358 | -59.7931 | 62.7136 | -59.5963 | -59.9854 | -0.027466 | -0.068665 | 62.5992 | -59.729 | 62.6816 | -59.7794 | -59.816 | -59.6283 | -0.045777 | -0.059509 | 0.018311 | 0.15106 | 59.7198 | -0.23804 | 59.7656 | -0.19226 | 0.01831 | -0.09613 | -0.013732 | -0.032044 | 0.11902 | -0.068665 | 0.10071 | -0.086975 | 0.19684 | 122.5067 | -0.050354 | 122.4106 | 122.4289 | 122.3282 | 122.3831 | 122.3465 | -122.4884 | -122.4243 | 122.4609 | 122.4289 | 59.6786 | 59.6786
687.7656 | 122.6898 | -59.7244 | 62.7045 | -0.079269 | 0.00084388 | 0.06288 | 0.091548 | -0.0015381 | 6.4004e-05 | -0.0013886 | -0.021667 | -0.0024096 | 0.062683 | 0.066176 | -0.012264 | -0.00072207 | -0.0052337 | -0.073242 | 62.6129 | -59.7931 | 62.6907 | -59.6008 | -59.9945 | -0.032043 | -0.050354 | 62.59 | -59.7702 | 62.8601 | -59.8801 | -59.8846 | -59.6329 | -0.068665 | -0.091553 | -0.013733 | 0.1236 | 59.6924 | -0.27008 | 59.761 | -0.20142 | -0.045777 | -0.11444 | 0.15564 | -0.15564 | 0.091552 | -0.16022 | 0.13733 | -0.11444 | 0.19226 | 122.4838 | -0.10986 | 122.6303 | 122.406 | 122.3602 | 122.3373 | 122.3145 | -122.4976 | -122.4747 | 122.4152 | 122.5845 | 59.6512 | 59.6741
688.7656 | 122.7127 | -59.7107 | 62.6862 | -0.11742 | 0.0036209 | 0.062453 | 0.092189 | 0.00038452 | -0.0007904 | -0.0026704 | -0.018616 | 0.001222 | 0.063324 | 0.065535 | -0.013546 | 0.0012005 | 0.0013885 | -0.032043 | 62.6495 | -59.761 | 62.6953 | -59.5825 | -59.9762 | 0 | -0.013733 | 62.5992 | -59.761 | 62.7731 | -59.7061 | -59.8068 | -59.61 | -0.050354 | -0.036621 | 0.009155 | 0.12817 | 59.7107 | -0.2655 | 59.761 | -0.21515 | -0.050354 | -0.086975 | 0.086975 | 0.004577 | 0.10071 | -0.096131 | 0.15106 | -0.045777 | 0.17853 | 122.4564 | 0.054931 | 122.5342 | 122.4106 | 122.3602 | 122.3602 | 122.3099 | -122.4472 | -122.4472 | 122.406 | 122.4838 | 59.6786 | 59.697
689.7656 | 122.6944 | -59.7015 | 62.6724 | -0.10216 | -0.00043792 | 0.061385 | 0.093043 | -0.0021789 | -0.001004 | -0.0020294 | -0.024719 | -0.001128 | 0.062683 | 0.061263 | -0.013119 | 0.00055973 | -0.0041657 | -0.041199 | 62.6404 | -59.7748 | 62.7365 | -59.5963 | -59.967 | 0.009155 | -0.022888 | 62.5992 | -59.7565 | 62.7686 | -59.7198 | -59.7885 | -59.61 | -0.073242 | -0.032043 | 0.064087 | 0.10529 | 59.7107 | -0.2655 | 59.7839 | -0.19226 | -0.054932 | -0.073242 | 0.096131 | -0.018311 | 0.091553 | -0.086975 | 0.14648 | -0.032043 | 0.17853 | 122.5113 | 0.036621 | 122.525 | 122.4152 | 122.3557 | 122.3419 | 122.3007 | -122.4472 | -122.4289 | 122.438 | 122.4701 | 59.6603 | 59.6786
690.7656 | 122.6898 | -59.7061 | 62.709 | -0.10216 | 0.00020288 | 0.061598 | 0.090053 | 0.0025207 | -0.0035674 | -0.00032036 | -0.039978 | -0.00027343 | 0.064179 | 0.063826 | -0.014187 | 0.0018413 | -0.0020295 | -0.054932 | 62.6404 | -59.7839 | 62.7045 | -59.5825 | -59.9899 | 0.009155 | -0.022888 | 62.5992 | -59.761 | 62.7686 | -59.7107 | -59.8114 | -59.6191 | -0.07782 | -0.068664 | -0.004577 | 0.1236 | 59.7153 | -0.28381 | 59.7931 | -0.20599 | -0.054931 | -0.10986 | 0.05951 | -0.004577 | 0.086975 | -0.10528 | 0.14191 | -0.050354 | 0.20142 | 122.4884 | 0.050354 | 122.5296 | 122.4243 | 122.3602 | 122.3465 | 122.3053 | -122.493 | -122.4701 | 122.4106 | 122.4747 | 59.6512 | 59.6832
691.7656 | 122.7127 | -59.7015 | 62.6953 | -0.10216 | 0.0016983 | 0.061598 | 0.091762 | -0.0026063 | -0.004422 | 0.00074764 | -0.018616 | -0.0015552 | 0.063324 | 0.070876 | -0.015041 | 0.00077333 | -0.0011749 | -0.041199 | 62.6495 | -59.7839 | 62.6953 | -59.5825 | -59.9808 | 0.004578 | -0.022888 | 62.6038 | -59.761 | 62.7686 | -59.7107 | -59.8068 | -59.6146 | -0.082398 | -0.045776 | 0 | 0.11902 | 59.7061 | -0.27924 | 59.7885 | -0.19684 | -0.059509 | -0.091552 | 0.073243 | -0.009155 | 0.086975 | -0.10529 | 0.14648 | -0.045777 | 0.20142 | 122.4792 | 0.050354 | 122.5296 | 122.4335 | 122.3648 | 122.3511 | 122.3053 | -122.4792 | -122.4564 | 122.3969 | 122.4701 | 59.6603 | 59.6786
692.7656 | 122.6898 | -59.7198 | 62.6862 | -0.12505 | 0.00020288 | 0.060957 | 0.09048 | 0.0031617 | -0.0014312 | -0.001175 | -0.046081 | 0.001222 | 0.063324 | 0.063399 | -0.012264 | -8.1274e-05 | 0.0035247 | -0.07782 | 62.6175 | -59.7839 | 62.6907 | -59.5963 | -59.9762 | -0.027466 | -0.09613 | 62.59 | -59.7336 | 62.7548 | -59.7656 | -59.8389 | -59.6146 | -0.064087 | -0.068664 | 0.004578 | 0.1236 | 59.6924 | -0.25635 | 59.7565 | -0.19226 | -0.013733 | -0.09613 | 0.068665 | -0.045776 | 0.10529 | -0.11902 | 0.11902 | -0.10529 | 0.18768 | 122.4747 | -0.032043 | 122.4884 | 122.4014 | 122.3236 | 122.3373 | 122.3099 | -122.4701 | -122.4197 | 122.4106 | 122.4747 | 59.642 | 59.6237
693.7656 | 122.7036 | -59.7107 | 62.7136 | -0.07164 | -0.00022432 | 0.063094 | 0.092189 | -4.2682e-05 | -0.0012176 | -0.0013886 | -0.027771 | -0.00048703 | 0.067383 | 0.065322 | -0.013973 | 0.0020551 | -0.0028839 | -0.036621 | 62.6312 | -59.7839 | 62.709 | -59.5825 | -59.9808 | 0.004578 | -0.013733 | 62.6221 | -59.7565 | 62.7731 | -59.697 | -59.8022 | -59.6283 | -0.073243 | -0.082397 | -0.004578 | 0.12817 | 59.7153 | -0.27008 | 59.7885 | -0.19684 | -0.045777 | -0.091553 | 0.059509 | 0.013733 | 0.082397 | -0.091553 | 0.12817 | -0.045776 | 0.20142 | 122.493 | 0.05951 | 122.5296 | 122.4152 | 122.3785 | 122.3419 | 122.3328 | -122.4976 | -122.4701 | 122.4197 | 122.4838 | 59.6741 | 59.697
694.7656 | 122.7676 | -59.6878 | 62.709 | -0.06401 | 0.0021255 | 0.062239 | 0.091121 | -0.0013245 | -0.0018586 | -0.004593 | -0.012512 | 0.00036737 | 0.06482 | 0.065108 | -0.0144 | 0.0020551 | -0.00096131 | 0 | 62.6495 | -59.7565 | 62.764 | -59.5413 | -59.903 | 0.064087 | 0.091553 | 62.59 | -59.7336 | 62.8052 | -59.642 | -59.7244 | -59.5642 | -0.068665 | -0.059509 | 0.054932 | 0.14648 | 59.7519 | -0.21515 | 59.8206 | -0.14648 | -0.045777 | -0.11902 | 0.096131 | 0.045776 | 0.1236 | -0.036621 | 0.16937 | 0.009156 | 0.21515 | 122.5204 | 0.091553 | 122.5388 | 122.406 | 122.3236 | 122.3373 | 122.2778 | -122.4655 | -122.4426 | 122.4518 | 122.493 | 59.6878 | 59.7794
695.7656 | 122.7448 | -59.697 | 62.7182 | -0.11742 | 0.00041648 | 0.063094 | 0.093898 | 0.00017092 | -0.0001496 | -0.002884 | -0.039978 | -5.9826e-05 | 0.064179 | 0.058913 | -0.015255 | 0.0024823 | -0.0013885 | 0.013733 | 62.645 | -59.7656 | 62.7777 | -59.5322 | -59.9075 | 0.068665 | 0.09613 | 62.6083 | -59.7107 | 62.8189 | -59.6329 | -59.7427 | -59.5642 | -0.068665 | -0.073243 | 0.059509 | 0.16479 | 59.7656 | -0.21057 | 59.8343 | -0.14191 | -0.013733 | -0.10986 | 0.10071 | 0.064086 | 0.13275 | -0.045777 | 0.14648 | -0.032044 | 0.23346 | 122.5433 | 0.077819 | 122.5296 | 122.4106 | 122.319 | 122.3419 | 122.3053 | -122.4838 | -122.4289 | 122.4747 | 122.5159 | 59.7107 | 59.7931
696.7656 | 122.7493 | -59.6924 | 62.709 | -0.086899 | 0.0014847 | 0.062666 | 0.091975 | 0.00059812 | -0.0007904 | -0.0018158 | -0.033874 | -0.0013416 | 0.063965 | 0.057418 | -0.012478 | 0.0020551 | 0.0016021 | 0.013733 | 62.6266 | -59.7565 | 62.7731 | -59.523 | -59.9121 | 0.07782 | 0.10071 | 62.5809 | -59.7427 | 62.8143 | -59.6329 | -59.7244 | -59.5596 | -0.064087 | -0.082397 | 0.064087 | 0.16937 | 59.7702 | -0.21973 | 59.8343 | -0.15564 | -0.050354 | -0.12817 | 0.10529 | 0.059509 | 0.13275 | -0.032043 | 0.18311 | 0.018311 | 0.23346 | 122.5296 | 0.10986 | 122.5571 | 122.3831 | 122.3236 | 122.319 | 122.2733 | -122.4655 | -122.4518 | 122.4655 | 122.5067 | 59.7061 | 59.7931
697.7656 | 122.731 | -59.6924 | 62.709 | -0.1403 | 0.0023391 | 0.06288 | 0.093471 | 0.0020935 | -0.0022858 | -0.002884 | -0.027771 | -0.00048703 | 0.064392 | 0.062972 | -0.014614 | 0.00013253 | 0.0018159 | 0.013733 | 62.6541 | -59.7748 | 62.764 | -59.5276 | -59.903 | 0.059509 | 0.10986 | 62.6129 | -59.7244 | 62.8326 | -59.6512 | -59.7382 | -59.5688 | -0.082397 | -0.054931 | 0.054932 | 0.16479 | 59.7519 | -0.21057 | 59.8343 | -0.12817 | -0.032043 | -0.09613 | 0.1236 | 0.041199 | 0.1236 | -0.045776 | 0.15564 | -0.013733 | 0.24719 | 122.5388 | 0.073242 | 122.5571 | 122.4289 | 122.3373 | 122.3465 | 122.3053 | -122.4838 | -122.4335 | 122.4564 | 122.525 | 59.7061 | 59.8022
698.7656 | 122.7356 | -59.6832 | 62.7228 | -0.086899 | 0.0012711 | 0.060744 | 0.092189 | -0.0032471 | -0.002713 | -0.00010676 | -0.036926 | -0.00027343 | 0.064392 | 0.061476 | -0.015469 | 0.00098693 | -0.0013885 | -0.027466 | 62.6266 | -59.7977 | 62.7228 | -59.5734 | -59.9579 | -0.004578 | 0.004578 | 62.6358 | -59.7519 | 62.7686 | -59.7061 | -59.7977 | -59.6237 | -0.11444 | -0.09613 | 0 | 0.10986 | 59.6786 | -0.27466 | 59.7931 | -0.16022 | -0.068664 | -0.086975 | 0.045777 | -0.022888 | 0.05951 | -0.11444 | 0.12817 | -0.045776 | 0.2243 | 122.5204 | 0.045776 | 122.5204 | 122.4243 | 122.3877 | 122.3099 | 122.319 | -122.5204 | -122.4747 | 122.406 | 122.4518 | 59.6558 | 59.6878
699.7656 | 122.7173 | -59.6924 | 62.7182 | -0.10979 | -0.0015061 | 0.063094 | 0.091121 | 0.0012391 | 0.0002778 | -0.0035248 | -0.0094604 | -0.00027343 | 0.063324 | 0.06169 | -0.016323 | 0.00077333 | -0.0011749 | 0.004578 | 62.645 | -59.7519 | 62.7548 | -59.5322 | -59.9167 | 0.059509 | 0.086975 | 62.6129 | -59.7427 | 62.8235 | -59.6558 | -59.7473 | -59.5734 | -0.059509 | -0.073243 | 0.036621 | 0.16022 | 59.7519 | -0.2243 | 59.8114 | -0.1648 | -0.050354 | -0.10529 | 0.10529 | 0.036621 | 0.11902 | -0.054931 | 0.16937 | -0.004577 | 0.21973 | 122.5067 | 0.086975 | 122.5662 | 122.3969 | 122.3557 | 122.3373 | 122.3053 | -122.4701 | -122.4609 | 122.4472 | 122.5159 | 59.697 | 59.7794
700.7656 | 122.7402 | -59.697 | 62.6999 | -0.07164 | 0.00020288 | 0.061385 | 0.091975 | -4.2682e-05 | 6.4004e-05 | 0.001175 | -0.030823 | 0.00015377 | 0.064392 | 0.063826 | -0.0144 | 0.00077333 | 0.0024567 | -0.004578 | 62.6221 | -59.7748 | 62.7594 | -59.5505 | -59.9075 | 0.073242 | 0.064087 | 62.6083 | -59.7382 | 62.8052 | -59.6649 | -59.761 | -59.5596 | -0.07782 | -0.07782 | 0.059509 | 0.14648 | 59.7702 | -0.21057 | 59.848 | -0.13275 | -0.041199 | -0.091553 | 0.10529 | 0.032043 | 0.13733 | -0.064087 | 0.17853 | -0.022888 | 0.2243 | 122.5342 | 0.073242 | 122.5433 | 122.3969 | 122.3465 | 122.319 | 122.3053 | -122.4747 | -122.438 | 122.4564 | 122.5021 | 59.6924 | 59.761
701.7656 | 122.7264 | -59.6741 | 62.6907 | -0.079269 | 0.00084388 | 0.060103 | 0.093043 | 0.00059812 | -0.0001496 | -0.0033112 | -0.012512 | -0.001128 | 0.06482 | 0.054854 | -0.015469 | 0.0048321 | 0.00053409 | 0.036621 | 62.6175 | -59.7519 | 62.7823 | -59.4543 | -59.8663 | 0.12817 | 0.16479 | 62.6083 | -59.7153 | 62.6312 | -59.6054 | -59.6786 | -59.523 | -0.07782 | -0.073242 | 0.091553 | 0.21973 | 59.8022 | -0.19226 | 59.8801 | -0.11444 | -0.041199 | -0.082398 | -0.059509 | 0.068664 | 0.15106 | -0.004578 | 0.19226 | 0.036621 | 0.29755 | 122.5342 | 0.10986 | 122.3465 | 122.3694 | 122.3236 | 122.2916 | 122.2824 | -122.4426 | -122.406 | 122.4564 | 122.3053 | 59.7107 | 59.8389
702.7656 | 122.6852 | -59.6741 | 62.6953 | -0.018234 | 0.00084388 | 0.060744 | 0.094539 | -4.2682e-05 | -0.0022858 | -0.0035248 | -0.030823 | -5.9826e-05 | 0.063965 | 0.055709 | -0.013546 | 0.0029095 | -0.0033111 | 0.041199 | 62.6266 | -59.7794 | 62.8098 | -59.4818 | -59.8755 | 0.10071 | 0.17395 | 62.5854 | -59.7107 | 62.9196 | -59.317 | -59.8892 | -59.7656 | -0.10529 | -0.068664 | 0.11444 | 0.19226 | 59.7748 | -0.20142 | 59.8801 | -0.09613 | -0.036621 | -0.10986 | 0.22431 | 0.35706 | -0.091553 | -0.21515 | -0.054932 | -0.17853 | 0.29755 | 122.5891 | 0.39368 | 122.6303 | 122.406 | 122.2961 | 122.3007 | 122.2595 | -122.4747 | -122.406 | 122.4838 | 122.5937 | 59.7153 | 59.848
703.7656 | 122.7493 | -59.6695 | 62.7777 | -0.06401 | 0.0010575 | 0.060957 | 0.093898 | 0.0029479 | -0.0018586 | 0.0013886 | -0.015564 | -0.0028368 | 0.063751 | 0.060195 | -0.01376 | 0.00034613 | -0.00010671 | 0.041199 | 62.6358 | -59.7565 | 62.7914 | -59.4864 | -59.8846 | 0.11444 | 0.14648 | 62.6312 | -59.7198 | 62.8372 | -59.6191 | -59.7336 | -59.5551 | -0.086975 | -0.14191 | 0.013733 | 0.18311 | 59.7839 | -0.21515 | 59.8709 | -0.12817 | -0.050354 | -0.14648 | 0.059509 | 0.050354 | 0.11444 | -0.064087 | 0.1648 | -0.013733 | 0.27008 | 122.5479 | 0.10071 | 122.5571 | 122.3923 | 122.3511 | 122.3053 | 122.3007 | -122.5342 | -122.4976 | 122.4609 | 122.5067 | 59.7107 | 59.816
704.7656 | 122.7631 | -59.6649 | 62.6999 | -0.048752 | 0.00063028 | 0.062239 | 0.09048 | -0.0017517 | -0.0035674 | -0.0018158 | -0.018616 | 0.0010084 | 0.063324 | 0.061476 | -0.014828 | 0.0020551 | 0.00096129 | 0.027466 | 62.645 | -59.7473 | 62.7731 | -59.5139 | -59.9075 | 0.091553 | 0.1236 | 62.6083 | -59.7427 | 62.8281 | -59.6146 | -59.7107 | -59.5688 | -0.082397 | -0.054932 | 0.073242 | 0.15106 | 59.7565 | -0.24262 | 59.8389 | -0.16022 | -0.07782 | -0.091553 | 0.12817 | 0.050354 | 0.09613 | -0.045776 | 0.17395 | 0.032044 | 0.23346 | 122.5204 | 0.12817 | 122.5708 | 122.3923 | 122.3511 | 122.3099 | 122.2733 | -122.4472 | -122.4426 | 122.438 | 122.493 | 59.6924 | 59.7885
705.7656 | 122.7264 | -59.6878 | 62.6953 | -0.12505 | 0.0016983 | 0.062453 | 0.094325 | -4.2682e-05 | -0.0016448 | 0.00010684 | -0.04303 | 0.00079477 | 0.062683 | 0.05934 | -0.013119 | 0.0024823 | -0.00053411 | -0.027466 | 62.6495 | -59.7839 | 62.7182 | -59.5871 | -59.9579 | 0.018311 | 0.004578 | 62.6129 | -59.7519 | 62.7686 | -59.7015 | -59.7931 | -59.6008 | -0.096131 | -0.045776 | 0.022889 | 0.10071 | 59.7061 | -0.27008 | 59.8022 | -0.17395 | -0.064087 | -0.082397 | 0.073243 | -0.013733 | 0.086975 | -0.10529 | 0.15106 | -0.041199 | 0.19684 | 122.5021 | 0.050354 | 122.5204 | 122.4335 | 122.3648 | 122.3373 | 122.3007 | -122.4792 | -122.4472 | 122.406 | 122.4564 | 59.6603 | 59.6924
706.7656 | 122.7219 | -59.7015 | 62.709 | -0.025863 | -0.0017197 | 0.060957 | 0.093257 | -4.2682e-05 | -0.0022858 | -0.00032036 | -0.015564 | -5.9826e-05 | 0.063538 | 0.063826 | -0.014187 | 0.0033367 | -0.0030975 | -0.041199 | 62.6312 | -59.8022 | 62.7182 | -59.5963 | -59.9808 | 0.009155 | 0 | 62.6038 | -59.7656 | 62.7502 | -59.6878 | -59.8114 | -59.6054 | -0.10071 | -0.077819 | 0.009156 | 0.10529 | 59.7107 | -0.27924 | 59.8114 | -0.17853 | -0.064087 | -0.10529 | 0.041199 | 0.013733 | 0.09613 | -0.10986 | 0.16022 | -0.045776 | 0.20599 | 122.5204 | 0.07782 | 122.5159 | 122.4335 | 122.3694 | 122.3328 | 122.3053 | -122.5113 | -122.4747 | 122.4197 | 122.4518 | 59.6603 | 59.7015
707.7656 | 122.731 | -59.729 | 62.6999 | -0.094528 | 0.0034073 | 0.059889 | 0.091762 | 0.00038452 | 0.0013458 | -0.002243 | -0.039978 | 0.0010084 | 0.062897 | 0.061904 | -0.015041 | 0.0022687 | 0.0016021 | -0.009155 | 62.6587 | -59.7519 | 62.7594 | -59.5276 | -59.9258 | 0.059509 | 0.068665 | 62.6221 | -59.7153 | 62.8098 | -59.6466 | -59.7519 | -59.5871 | -0.022888 | -0.041199 | 0.059509 | 0.20142 | 59.7885 | -0.19684 | 59.8114 | -0.17395 | 0.013733 | -0.07782 | 0.10986 | 0.082398 | 0.14191 | -0.022888 | 0.12817 | -0.036621 | 0.2243 | 122.5113 | 0.068665 | 122.525 | 122.4106 | 122.3373 | 122.3877 | 122.3511 | -122.4518 | -122.4152 | 122.4884 | 122.5388 | 59.7198 | 59.7977
708.7656 | 122.7676 | -59.6878 | 62.6907 | -0.086899 | 0.00041648 | 0.061812 | 0.093043 | 0.00059812 | -0.0022858 | -0.00010676 | -0.018616 | 0.00058097 | 0.063538 | 0.05934 | -0.01675 | 0.0016277 | -0.00010671 | 0.036621 | 62.6358 | -59.7473 | 62.796 | -59.4772 | -59.8572 | 0.11444 | 0.17853 | 62.6221 | -59.7153 | 62.883 | -59.9258 | -59.8801 | -59.5596 | -0.059509 | -0.054932 | 0.10529 | 0.21057 | 59.8022 | -0.16937 | 59.8618 | -0.10986 | -0.027466 | -0.068665 | 0.19226 | -0.23804 | 0.12817 | -0.19226 | 0.15564 | -0.16479 | 0.27008 | 122.5433 | -0.21057 | 122.5983 | 122.3831 | 122.3373 | 122.3236 | 122.3099 | -122.438 | -122.406 | 122.4838 | 122.5708 | 59.7244 | 59.8663
709.7656 | 122.7768 | -59.6466 | 62.7228 | -0.11742 | -0.00065152 | 0.062025 | 0.093043 | -0.0011109 | -0.0007904 | -0.0013886 | -0.030823 | 0.001222 | 0.063538 | 0.062331 | -0.013332 | 0.0024823 | -0.00053411 | 0.032043 | 62.6175 | -59.7656 | 62.7914 | -59.4772 | -59.8709 | 0.10986 | 0.15106 | 62.6129 | -59.7244 | 62.8326 | -59.7198 | -59.3079 | -59.2392 | -0.11902 | -0.10528 | 0.068665 | 0.16937 | 59.7565 | -0.22431 | 59.8755 | -0.10529 | -0.07782 | -0.10986 | 0.10986 | -0.073243 | 0.40741 | 0.33874 | 0.48523 | 0.41656 | 0.28839 | 122.5571 | 0.004577 | 122.5571 | 122.3831 | 122.3373 | 122.2641 | 122.2595 | -122.4884 | -122.4472 | 122.438 | 122.4792 | 59.6786 | 59.7977
710.7656 | 122.7676 | -59.697 | 62.7045 | -0.041122 | -0.00043792 | 0.062025 | 0.092403 | 0.00081172 | 0.0004914 | 0.00010684 | -0.012512 | -5.9826e-05 | 0.064606 | 0.062117 | -0.016323 | -8.1274e-05 | -0.0026703 | 0.022888 | 62.6495 | -59.7519 | 62.7869 | -59.5001 | -59.8938 | 0.10986 | 0.14191 | 62.6266 | -59.7382 | 62.8326 | -59.6283 | -59.7244 | -59.5551 | -0.054932 | -0.054932 | 0.082397 | 0.19684 | 59.8068 | -0.19684 | 59.8618 | -0.14191 | -0.041199 | -0.07782 | 0.12817 | 0.068664 | 0.14191 | -0.027466 | 0.18311 | 0.013733 | 0.25177 | 122.5388 | 0.10986 | 122.5708 | 122.4014 | 122.3648 | 122.3465 | 122.3236 | -122.4564 | -122.4426 | 122.4838 | 122.5296 | 59.7198 | 59.8389
711.7656 | 122.7585 | -59.6832 | 62.6862 | -0.1403 | 0.0025529 | 0.062025 | 0.092616 | 0.0010253 | -0.0018586 | -0.0033112 | -0.030823 | 0.0014356 | 0.063965 | 0.065535 | -0.012051 | 0.0031231 | -0.00053411 | 0.022888 | 62.6587 | -59.7748 | 62.7823 | -59.5001 | -59.8801 | 0.091553 | 0.1236 | 62.5809 | -59.7153 | 62.8235 | -59.6375 | -59.7198 | -59.5413 | -0.091552 | -0.027466 | 0.096131 | 0.18311 | 59.7748 | -0.19684 | 59.8663 | -0.10529 | -0.032043 | -0.10529 | 0.13733 | 0.045777 | 0.14191 | -0.036621 | 0.17395 | -0.004578 | 0.27466 | 122.5571 | 0.07782 | 122.5388 | 122.4335 | 122.2961 | 122.3419 | 122.2641 | -122.4609 | -122.4014 | 122.4655 | 122.5067 | 59.7061 | 59.8068
712.7656 | 122.7081 | -59.697 | 62.709 | -0.15556 | 0.0019119 | 0.062666 | 0.092616 | -0.0015381 | -0.0050628 | -0.00096136 | -0.036926 | -5.9826e-05 | 0.065033 | 0.058058 | -0.014828 | 0.0018413 | 0.0026703 | -0.027466 | 62.6541 | -59.7702 | 62.7182 | -59.5871 | -59.9533 | 0.022888 | 0 | 62.6312 | -59.7565 | 62.7731 | -59.6741 | -59.8022 | -59.5963 | -0.073243 | -0.054931 | 0.009156 | 0.10986 | 59.7198 | -0.25635 | 59.7931 | -0.1831 | -0.05951 | -0.077819 | 0.064087 | 0.022888 | 0.10071 | -0.10529 | 0.16022 | -0.045776 | 0.18311 | 122.4884 | 0.082398 | 122.5296 | 122.4243 | 122.3877 | 122.3511 | 122.3282 | -122.4792 | -122.4655 | 122.4152 | 122.4701 | 59.6695 | 59.697
713.7656 | 122.7127 | -59.7153 | 62.7319 | -0.10979 | 0.00084388 | 0.062239 | 0.090694 | -0.00068368 | -0.001004 | -0.00096136 | -0.021667 | 0.00058097 | 0.064392 | 0.067458 | -0.015041 | 0.0031231 | -0.00074771 | -0.032043 | 62.6816 | -59.7794 | 62.7136 | -59.5871 | -59.9533 | 0.013733 | 0 | 62.6175 | -59.7427 | 62.7777 | -59.7061 | -59.7977 | -59.6008 | -0.064087 | -0.050354 | -0.018311 | 0.12817 | 59.729 | -0.23804 | 59.7931 | -0.17395 | -0.027466 | -0.11444 | 0.045776 | 0.009155 | 0.11444 | -0.082397 | 0.14191 | -0.054931 | 0.19226 | 122.493 | 0.036621 | 122.5204 | 122.4609 | 122.3602 | 122.3969 | 122.3328 | -122.5113 | -122.4747 | 122.4289 | 122.493 | 59.6832 | 59.7153
714.7656 | 122.7402 | -59.6786 | 62.7182 | -0.056381 | -0.00043792 | 0.06053 | 0.09283 | -0.0017517 | -0.002713 | -0.0016022 | -0.0094604 | -0.00070063 | 0.06546 | 0.067031 | -0.016537 | 0.0022687 | -0.0030975 | 0.018311 | 62.6221 | -59.7565 | 62.7686 | -59.5184 | -59.8984 | 0.073242 | 0.10529 | 62.6221 | -59.7382 | 62.8052 | -59.6512 | -59.729 | -59.5596 | -0.07782 | -0.096131 | 0.050354 | 0.16022 | 59.7519 | -0.21973 | 59.8297 | -0.14191 | -0.059509 | -0.096131 | 0.086975 | 0.027466 | 0.11902 | -0.050354 | 0.17853 | 0.009155 | 0.23804 | 122.525 | 0.086975 | 122.5433 | 122.3785 | 122.3602 | 122.3007 | 122.3007 | -122.4747 | -122.4564 | 122.4472 | 122.4838 | 59.697 | 59.7839
715.7656 | 122.7585 | -59.6741 | 62.7045 | -0.079269 | 0.0010575 | 0.060103 | 0.092616 | -0.0013245 | -0.002713 | -0.002243 | -0.12238 | -0.00048703 | 0.06482 | 0.066817 | -0.013332 | 0.0016277 | 0.00074769 | 0.045776 | 62.6633 | -59.7336 | 62.8098 | -59.111 | -59.5139 | -0.050354 | 0.2243 | 62.6038 | -59.7382 | 62.8098 | -59.5825 | -59.7427 | -59.5596 | -0.05951 | -0.041199 | 0.10529 | 0.56305 | 59.6237 | 0.16022 | 59.6832 | 0.21973 | -0.064087 | -0.10071 | 0.10529 | 0.091552 | 0.11444 | -0.068665 | 0.17853 | -0.004578 | 0.62256 | 122.5433 | 0.15564 | 122.5479 | 122.3969 | 122.3419 | 122.3373 | 122.2778 | -122.4381 | -122.4426 | 122.4838 | 122.4838 | 59.7198 | 59.8984
716.7656 | 122.7539 | -59.6832 | 62.7045 | -0.1403 | -1.0718e-05 | 0.061598 | 0.092403 | -0.0011109 | -0.0003632 | -0.0026704 | 0.1004 | -0.00070063 | 0.067169 | 0.063826 | -0.014614 | 0.0012005 | -0.0030975 | 0.050354 | 62.6633 | -59.7427 | 62.8143 | -59.4452 | -59.8434 | 0.22888 | -0.10529 | 62.6129 | -59.7565 | 62.8372 | -59.642 | -59.7656 | -59.5917 | -0.059509 | -0.041199 | 0.10986 | 0.23804 | 59.9121 | -0.16022 | 59.9716 | -0.10071 | -0.073242 | -0.091553 | 0.13275 | 0.041199 | 0.091553 | -0.082397 | 0.16479 | -0.009155 | 0.29755 | 122.5571 | 0.11444 | 122.5937 | 122.406 | 122.3694 | 122.3465 | 122.2961 | -122.4472 | -122.4609 | 122.4976 | 122.5204 | 59.7336 | 59.5779
717.7656 | 122.7493 | -59.6695 | 62.7182 | -0.10979 | 0.00063028 | 0.061598 | 0.090907 | -0.00025628 | -0.002713 | -0.00032036 | -0.024719 | -0.00027343 | 0.060547 | 0.063613 | -0.016109 | -0.00050847 | -0.00096131 | 0.041199 | 62.6175 | -59.7519 | 62.8052 | -59.4543 | -59.8618 | 0.13275 | 0.43488 | 62.6862 | -59.6649 | 62.796 | -59.6924 | -59.6924 | -59.5505 | -0.082397 | -0.10071 | 0.086975 | 0.21515 | 59.8022 | -0.19226 | 59.8846 | -0.10986 | 0.004578 | -0.032044 | 0.07782 | -0.022888 | 0.11902 | -0.022888 | 0.11444 | -0.027466 | 0.29755 | 122.5571 | -0.027466 | 122.4609 | 122.3694 | 122.3511 | 122.287 | 122.3557 | -122.4701 | -122.3831 | 122.4747 | 122.4655 | 59.7107 | 60.1044
718.7656 | 122.731 | -59.697 | 62.6907 | -0.033493 | 0.0019119 | 0.06053 | 0.090907 | -0.00068368 | -0.0007904 | -0.00096136 | -0.00030524 | 0.0025036 | 0.063965 | 0.065108 | -0.012905 | 0.0052593 | -0.00096131 | 0.041199 | 62.6312 | -59.7519 | 62.8235 | -59.4727 | -59.8526 | 0.12817 | 0.19684 | 62.6221 | -59.697 | 62.6266 | -59.5413 | -59.7061 | -59.5642 | -0.054932 | -0.059509 | 0.13275 | 0.2243 | 59.8251 | -0.15564 | 59.8801 | -0.10071 | 0 | -0.068665 | -0.064087 | 0.15564 | 0.13275 | -0.009156 | 0.13275 | -0.009156 | 0.27924 | 122.5754 | 0.15564 | 122.3236 | 122.3831 | 122.319 | 122.3282 | 122.319 | -122.4426 | -122.3877 | 122.5204 | 122.3236 | 59.7382 | 59.8938
719.7656 | 122.731 | -59.6878 | 62.709 | -0.1403 | 0.00084388 | 0.061812 | 0.093471 | 0.0023071 | -0.0016448 | -0.001175 | -0.012512 | 0.00036737 | 0.063751 | 0.064467 | -0.013546 | 0.0018413 | -0.0026703 | -0.013733 | 62.6358 | -59.7656 | 62.7365 | -59.5596 | -59.9258 | 0.045776 | 0.054932 | 62.6129 | -59.7473 | 62.8006 | -59.6558 | -59.7748 | -59.5779 | -0.07782 | -0.073242 | 0.027466 | 0.12817 | 59.7336 | -0.23804 | 59.8114 | -0.16022 | -0.059509 | -0.09613 | 0.091553 | 0.032043 | 0.10986 | -0.086975 | 0.16937 | -0.027466 | 0.20599 | 122.5021 | 0.091552 | 122.5479 | 122.4014 | 122.3602 | 122.3236 | 122.3007 | -122.4747 | -122.4564 | 122.4243 | 122.4884 | 59.6741 | 59.7427
720.7656 | 122.7539 | -59.6924 | 62.7228 | -0.07164 | 0.0019119 | 0.061812 | 0.092403 | 0.0016663 | -0.0001496 | -0.00096136 | -0.012512 | -0.00091423 | 0.063538 | 0.060408 | -0.015469 | 0.0012005 | -0.0013885 | -0.009155 | 62.6404 | -59.7931 | 62.7274 | -59.5688 | -59.935 | 0.054932 | 0.041199 | 62.6266 | -59.7427 | 62.796 | -59.6695 | -59.7656 | -59.5871 | -0.10071 | -0.082397 | 0.004578 | 0.1236 | 59.7473 | -0.24262 | 59.848 | -0.14191 | -0.050354 | -0.09613 | 0.073243 | 0.022888 | 0.10529 | -0.073242 | 0.15564 | -0.022888 | 0.2243 | 122.5204 | 0.073242 | 122.5388 | 122.4335 | 122.3694 | 122.3328 | 122.319 | -122.5159 | -122.4655 | 122.4197 | 122.4884 | 59.6832 | 59.7336
721.7656 | 122.7219 | -59.6878 | 62.7319 | -0.025863 | 0.0031937 | 0.061812 | 0.092403 | 0.00081172 | -0.0020722 | -0.0013886 | -0.039978 | -0.00091423 | 0.064606 | 0.064681 | -0.017391 | -0.00029487 | -0.0037383 | 0 | 62.6358 | -59.7702 | 62.796 | -59.4955 | -59.8526 | 0.1236 | 0.1236 | 62.6358 | -59.7153 | 62.8281 | -59.6375 | -59.7382 | -59.5779 | -0.082398 | -0.096131 | 0.064087 | 0.19226 | 59.8114 | -0.1648 | 59.8938 | -0.082397 | -0.027466 | -0.096131 | 0.09613 | 0.050354 | 0.10986 | -0.050354 | 0.13733 | -0.022888 | 0.27466 | 122.5662 | 0.07782 | 122.5433 | 122.406 | 122.3511 | 122.3236 | 122.3236 | -122.5021 | -122.4472 | 122.4838 | 122.5159 | 59.6878 | 59.8114
722.7656 | 122.7493 | -59.6786 | 62.7136 | -0.20134 | 0.0016983 | 0.061171 | 0.092616 | -0.0017517 | -0.0016448 | -0.00074776 | -0.021667 | 0.00015377 | 0.065888 | 0.061904 | -0.012691 | 0.0014141 | 0.0024567 | 0.10986 | 62.6221 | -59.7519 | 62.8143 | -59.4635 | -59.8984 | 0.11902 | 0.15106 | 62.5992 | -59.7107 | 62.8235 | -59.6237 | -59.7473 | -59.5688 | -0.073242 | -0.091553 | 0.10071 | 0.21515 | 59.7977 | -0.21973 | 59.8709 | -0.14648 | -0.032043 | -0.11444 | 0.10986 | 0.054932 | 0.10986 | -0.068664 | 0.14191 | -0.036621 | 0.28839 | 122.5662 | 0.086975 | 122.5342 | 122.374 | 122.3099 | 122.3007 | 122.2778 | -122.4655 | -122.4243 | 122.493 | 122.5021 | 59.7885 | 59.8297
723.7656 | 122.731 | -59.6878 | 62.7228 | -0.22423 | 0.0021255 | 0.06288 | 0.093257 | -0.00046988 | -0.0012176 | 0.00053404 | -0.033874 | -0.00048703 | 0.066101 | 0.068312 | -0.01376 | 0.0018413 | -0.0030975 | -0.045776 | 62.6175 | -59.7656 | 62.7914 | -59.491 | -59.8801 | 0.12817 | 0.17853 | 62.6358 | -59.7153 | 62.8189 | -59.6191 | -59.7244 | -59.5596 | -0.07782 | -0.10528 | 0.068665 | 0.19684 | 59.816 | -0.19226 | 59.8938 | -0.11444 | -0.027466 | -0.086975 | 0.096131 | 0.068664 | 0.12817 | -0.036621 | 0.15564 | -0.009155 | 0.27466 | 122.5571 | 0.09613 | 122.5342 | 122.3831 | 122.3511 | 122.3053 | 122.3236 | -122.4884 | -122.438 | 122.4792 | 122.5067 | 59.642 | 59.8663
724.7656 | 122.7402 | -59.6832 | 62.7502 | -0.32341 | 0.0042619 | 0.061171 | 0.09518 | -4.2682e-05 | -0.0024994 | -0.00096136 | -0.012512 | -0.00070063 | 0.063111 | 0.062331 | -0.015041 | 0.00077333 | -0.0013885 | 0.07782 | 62.645 | -59.7382 | 62.7869 | -59.4727 | -59.8618 | 0.10071 | 0.17853 | 62.6221 | -59.7565 | 62.8098 | -59.6329 | -59.7382 | -59.5688 | -0.054931 | -0.10529 | 0.036621 | 0.21057 | 59.7839 | -0.17853 | 59.8389 | -0.1236 | -0.073242 | -0.12817 | 0.059509 | 0.050354 | 0.11444 | -0.054931 | 0.18768 | 0.018311 | 0.2655 | 122.525 | 0.1236 | 122.5662 | 122.3831 | 122.3785 | 122.3282 | 122.3053 | -122.4884 | -122.5067 | 122.4701 | 122.493 | 59.761 | 59.8618
725.7656 | 122.7402 | -59.6695 | 62.7228 | -0.086899 | 0.0012711 | 0.06053 | 0.093684 | 0.0016663 | -0.0005768 | -0.0030976 | -0.015564 | -0.00070063 | 0.065674 | 0.063399 | -0.013332 | 0.0024823 | -0.0037383 | 0.07782 | 62.6266 | -59.7702 | 62.8189 | -59.4589 | -59.9075 | 0.10986 | 0.13275 | 62.6266 | -59.697 | 62.8235 | -59.6329 | -59.7565 | -59.5734 | -0.10071 | -0.09613 | 0.096131 | 0.21057 | 59.7794 | -0.23804 | 59.8801 | -0.13733 | -0.027465 | -0.09613 | 0.10071 | 0.036621 | 0.096131 | -0.086975 | 0.1236 | -0.05951 | 0.31128 | 122.5891 | 0.064086 | 122.5204 | 122.3969 | 122.3236 | 122.2961 | 122.2961 | -122.493 | -122.4197 | 122.4884 | 122.493 | 59.7473 | 59.8022
726.7656 | 122.6807 | -59.6558 | 62.7686 | -0.079269 | -0.00086512 | 0.061171 | 0.093898 | 0.0055115 | -0.0050628 | -0.0035248 | -0.015564 | 0.0014356 | 0.06546 | 0.058058 | -0.0144 | 0.0018413 | -0.0022431 | 0.022888 | 62.6266 | -59.7519 | 62.7731 | -59.4864 | -59.8709 | 0.10986 | 0.15564 | 62.6129 | -59.7153 | 62.8372 | -59.6054 | -59.7153 | -59.5413 | -0.09613 | -0.14191 | 0.004577 | 0.16937 | 59.7656 | -0.21515 | 59.8618 | -0.11902 | -0.059509 | -0.15564 | 0.068664 | 0.050354 | 0.11444 | -0.059509 | 0.17395 | 0 | 0.2655 | 122.525 | 0.10986 | 122.5525 | 122.3785 | 122.3282 | 122.2824 | 122.2687 | -122.5204 | -122.4838 | 122.4289 | 122.493 | 59.6787 | 59.8114
727.7656 | 122.7951 | -59.6512 | 62.8052 | -0.079269 | 0.0012711 | 0.062025 | 0.091762 | -0.0011109 | -0.0016448 | 0.00010684 | -0.012512 | -0.00048703 | 0.06482 | 0.064253 | -0.014828 | 0.00077333 | -0.0022431 | 0.018311 | 62.6404 | -59.7794 | 62.7686 | -59.4864 | -59.8618 | 0.10986 | 0.15106 | 62.6221 | -59.7198 | 62.8464 | -59.6008 | -59.7153 | -59.5505 | -0.12817 | -0.1648 | -0.036621 | 0.16479 | 59.761 | -0.21057 | 59.8892 | -0.082397 | -0.068665 | -0.18311 | 0.041199 | 0.050354 | 0.10071 | -0.064087 | 0.16937 | 0.004578 | 0.29297 | 122.5479 | 0.11902 | 122.5662 | 122.4197 | 122.3419 | 122.2916 | 122.2733 | -122.5845 | -122.525 | 122.4197 | 122.4976 | 59.6695 | 59.8022
728.7656 | 122.7173 | -59.6832 | 62.7274 | -0.086899 | 0.0038345 | 0.062453 | 0.090694 | 0.0025207 | 0.0015594 | -0.00010676 | -0.027771 | -0.00070063 | 0.065247 | 0.060408 | -0.016537 | 0.0012005 | 0.0013885 | 0.027466 | 62.6312 | -59.7702 | 62.8006 | -59.4864 | -59.8526 | 0.1236 | 0.13275 | 62.6404 | -59.729 | 62.8143 | -59.6375 | -59.7519 | -59.5734 | -0.086975 | -0.09613 | 0.073242 | 0.19684 | 59.8068 | -0.16937 | 59.8938 | -0.082397 | -0.045776 | -0.086975 | 0.086975 | 0.045777 | 0.10986 | -0.068664 | 0.15564 | -0.022888 | 0.28381 | 122.5708 | 0.091553 | 122.5433 | 122.4014 | 122.3694 | 122.3145 | 122.3236 | -122.4976 | -122.4564 | 122.4838 | 122.4976 | 59.7107 | 59.816
729.7656 | 122.6395 | -59.6878 | 62.7548 | -0.06401 | 0.0016983 | 0.063521 | 0.093684 | 0.0046569 | -0.0022858 | -0.0037384 | -0.027771 | -0.00048703 | 0.06482 | 0.059767 | -0.0144 | 0.00077333 | 0.0013885 | 0.073242 | 62.6587 | -59.7427 | 62.7594 | -59.5276 | -59.903 | 0.10071 | 0.10986 | 62.6495 | -59.7565 | 62.7548 | -59.7015 | -59.8206 | -59.6375 | -0.054932 | -0.096131 | 0.004577 | 0.16022 | 59.7885 | -0.21515 | 59.8434 | -0.16022 | -0.068665 | -0.10529 | 0 | -0.013733 | 0.050354 | -0.13275 | 0.11902 | -0.064087 | 0.21515 | 122.5021 | 0.054932 | 122.5113 | 122.4014 | 122.406 | 122.3465 | 122.3373 | -122.4976 | -122.5113 | 122.4472 | 122.4426 | 59.761 | 59.7977
730.7656 | 122.644 | -59.6924 | 62.7548 | -0.018234 | 0.0025529 | 0.061171 | 0.093471 | -0.0017517 | -0.0012176 | -0.0020294 | -0.049133 | 0.001222 | 0.065247 | 0.057418 | -0.013546 | 0.0031231 | 0.00074769 | 0.064087 | 62.6678 | -59.7839 | 62.7502 | -59.5413 | -59.903 | 0.091553 | 0.10071 | 62.6541 | -59.7336 | 62.7411 | -59.7153 | -59.7977 | -59.6466 | -0.091553 | -0.086975 | -0.004578 | 0.15106 | 59.7839 | -0.21057 | 59.8755 | -0.11902 | -0.041199 | -0.10071 | -0.013733 | -0.022888 | 0.045777 | -0.10529 | 0.086976 | -0.064086 | 0.24261 | 122.5342 | 0.018311 | 122.4747 | 122.4518 | 122.3877 | 122.3602 | 122.3465 | -122.5388 | -122.4884 | 122.4426 | 122.4335 | 59.7565 | 59.7931
731.7656 | 122.6395 | -59.7061 | 62.764 | -0.079269 | 0.00020288 | 0.06288 | 0.093898 | 0.0018799 | -0.0022858 | -0.002884 | -0.027771 | 0.00036737 | 0.062897 | 0.068312 | -0.01376 | 0.00055973 | -0.0045929 | 0.068665 | 62.6495 | -59.761 | 62.764 | -59.5459 | -59.9213 | 0.086975 | 0.10529 | 62.6495 | -59.729 | 62.7411 | -59.7153 | -59.8297 | -59.6558 | -0.054931 | -0.11444 | 0 | 0.16022 | 59.7931 | -0.21515 | 59.848 | -0.16022 | -0.022888 | -0.11444 | -0.022888 | -0.009155 | 0.050354 | -0.1236 | 0.073242 | -0.10071 | 0.21515 | 122.525 | 0.013733 | 122.4701 | 122.4106 | 122.3785 | 122.3557 | 122.3557 | -122.525 | -122.493 | 122.4701 | 122.4472 | 59.7748 | 59.8114
732.7656 | 122.644 | -59.7244 | 62.7457 | -0.033493 | -0.00022432 | 0.063094 | 0.093898 | 0.0012391 | -0.0016448 | 0.00032044 | -0.024719 | -0.0017688 | 0.064606 | 0.064681 | -0.013332 | 0.0016277 | 0.0045929 | 0.050354 | 62.6953 | -59.761 | 62.7411 | -59.5413 | -59.9213 | 0.09613 | 0.07782 | 62.6404 | -59.7382 | 62.7228 | -59.7473 | -59.8343 | -59.6466 | -0.036621 | -0.050355 | -0.004578 | 0.1831 | 59.8206 | -0.19684 | 59.8572 | -0.16022 | -0.013733 | -0.10529 | -0.022889 | -0.022888 | 0.07782 | -0.10986 | 0.091553 | -0.096131 | 0.21973 | 122.5021 | -0.009155 | 122.4609 | 122.4564 | 122.3785 | 122.4197 | 122.3648 | -122.5067 | -122.4838 | 122.4655 | 122.4472 | 59.7748 | 59.8022
733.7656 | 122.6898 | -59.6649 | 62.7731 | -0.048752 | 0.0019119 | 0.064803 | 0.093043 | -0.00025628 | -0.0012176 | -0.002243 | -0.00030524 | -5.9826e-05 | 0.063965 | 0.057631 | -0.014828 | 0.0031231 | -0.0024567 | 0.050354 | 62.6587 | -59.7748 | 62.8143 | -59.4727 | -59.8663 | 0.11444 | 0.13733 | 62.6312 | -59.7153 | 62.7914 | -59.6558 | -59.7565 | -59.5779 | -0.10986 | -0.11444 | 0.041199 | 0.19226 | 59.7794 | -0.20142 | 59.8892 | -0.091553 | -0.050354 | -0.14191 | 0.018311 | 0.009155 | 0.086975 | -0.091553 | 0.13733 | -0.041199 | 0.30212 | 122.5891 | 0.059509 | 122.5067 | 122.4335 | 122.3465 | 122.3236 | 122.2961 | -122.5479 | -122.4884 | 122.4792 | 122.4564 | 59.7153 | 59.8022
734.7656 | 122.6212 | -59.697 | 62.7594 | -0.079269 | 0.0010575 | 0.061812 | 0.094539 | -0.0019653 | -0.0018586 | -0.002243 | -0.039978 | 0.0014356 | 0.06482 | 0.062972 | -0.012691 | 0.0014141 | 0.0033111 | 0.050354 | 62.6816 | -59.7565 | 62.7365 | -59.5596 | -59.9167 | 0.059509 | 0.054932 | 62.6678 | -59.7382 | 62.7228 | -59.7473 | -59.8618 | -59.6649 | -0.05951 | -0.077819 | -0.022888 | 0.13733 | 59.7565 | -0.21973 | 59.816 | -0.16022 | -0.041199 | -0.091552 | -0.036621 | -0.050354 | 0.032043 | -0.1648 | 0.073242 | -0.1236 | 0.19684 | 122.493 | -0.009155 | 122.4609 | 122.4381 | 122.406 | 122.3785 | 122.3648 | -122.5159 | -122.4976 | 122.4335 | 122.4197 | 59.7473 | 59.7519
735.7656 | 122.6257 | -59.7244 | 62.7731 | -0.11742 | 0.0021255 | 0.061598 | 0.095821 | -0.0028199 | -0.0024994 | 0.0016022 | -0.049133 | 0.001222 | 0.063111 | 0.06938 | -0.013332 | 0.0026959 | -0.0028839 | 0.045776 | 62.677 | -59.7519 | 62.7274 | -59.5596 | -59.935 | 0.050354 | 0.054932 | 62.677 | -59.7519 | 62.7045 | -59.7427 | -59.8663 | -59.6786 | -0.027466 | -0.09613 | -0.045776 | 0.16479 | 59.7748 | -0.21057 | 59.8022 | -0.18311 | -0.027466 | -0.09613 | -0.068664 | -0.018311 | 0.045776 | -0.14191 | 0.073242 | -0.11444 | 0.19226 | 122.4792 | 0.009155 | 122.4564 | 122.4289 | 122.4289 | 122.4014 | 122.4014 | -122.525 | -122.525 | 122.4518 | 122.4289 | 59.7702 | 59.7794
736.7656 | 122.612 | -59.7015 | 62.7686 | -0.10979 | 0.0012711 | 0.062239 | 0.093898 | 0.0050843 | -0.0024994 | -0.0018158 | -0.06134 | 0.00058097 | 0.065674 | 0.064681 | -0.014828 | 0.00055973 | -0.0022431 | -0.16022 | 62.6816 | -59.8068 | 62.6541 | -59.642 | -59.9945 | 0.050354 | 0.009155 | 62.6816 | -59.7656 | 62.709 | -59.7519 | -59.8526 | -59.6649 | -0.10529 | -0.086975 | -0.11444 | 0.059509 | 59.7519 | -0.29297 | 59.8572 | -0.18768 | -0.064087 | -0.086975 | -0.05951 | -0.050354 | 0.036621 | -0.15106 | 0.10071 | -0.086975 | 0.16479 | 122.4609 | 0.013733 | 122.4747 | 122.4884 | 122.4472 | 122.3831 | 122.3831 | -122.5754 | -122.5342 | 122.3557 | 122.4106 | 59.5413 | 59.7107
737.7656 | 122.612 | -59.7061 | 62.7548 | -0.17845 | -0.00022432 | 0.059676 | 0.092616 | 0.00059812 | 6.4004e-05 | -0.002243 | -0.052185 | 0.0014356 | 0.065247 | 0.065749 | -0.015896 | 0.0014141 | 0.0016021 | 0.050354 | 62.6953 | -59.7839 | 62.6816 | -59.6191 | -60.0082 | 0.032043 | 0.004578 | 62.6678 | -59.761 | 62.6999 | -59.7656 | -59.8709 | -59.6741 | -0.07782 | -0.05951 | -0.073242 | 0.086975 | 59.7382 | -0.30212 | 59.816 | -0.2243 | -0.054931 | -0.086975 | -0.054932 | -0.059509 | 0.032044 | -0.16479 | 0.086975 | -0.10986 | 0.16479 | 122.4655 | -0.004578 | 122.4609 | 122.4792 | 122.4289 | 122.4014 | 122.374 | -122.5388 | -122.5159 | 122.3877 | 122.406 | 59.7565 | 59.7107
738.7656 | 122.6303 | -59.7015 | 62.7731 | -0.025863 | 0.00063028 | 0.063948 | 0.093257 | 0.0018799 | -0.0057038 | 0.00010684 | -0.058289 | 0.0010084 | 0.066101 | 0.058913 | -0.012051 | 0.0018413 | -0.0020295 | -0.036621 | 62.6953 | -59.7885 | 62.6495 | -59.642 | -59.9854 | 0.036621 | 0.009155 | 62.709 | -59.7565 | 62.7136 | -59.7565 | -59.8892 | -59.6695 | -0.086975 | -0.07782 | -0.1236 | 0.059509 | 59.7382 | -0.28381 | 59.8251 | -0.19684 | -0.054932 | -0.064087 | -0.059509 | -0.054932 | 0.032043 | -0.18768 | 0.086975 | -0.13275 | 0.14648 | 122.438 | 0 | 122.4701 | 122.4838 | 122.4655 | 122.3969 | 122.4106 | -122.5616 | -122.5296 | 122.3511 | 122.4152 | 59.6649 | 59.7107
739.7656 | 122.6486 | -59.7198 | 62.6999 | -0.086899 | -0.00086512 | 0.064162 | 0.09518 | 0.0027343 | -0.0016448 | -0.0030976 | -0.09491 | 0.0018628 | 0.065247 | 0.062331 | -0.01376 | 0.0020551 | -0.0026703 | -0.086975 | 62.6541 | -59.816 | 62.6221 | -59.6649 | -60.0723 | -0.11444 | -0.11902 | 62.6221 | -59.7748 | 62.6999 | -59.7977 | -59.9075 | -59.6832 | -0.09613 | -0.045776 | -0.07782 | 0.054932 | 59.6054 | -0.35248 | 59.7015 | -0.25635 | -0.054931 | -0.07782 | 0 | -0.077819 | 0.036621 | -0.18768 | 0.091552 | -0.13275 | 0.15106 | 122.438 | -0.022888 | 122.4747 | 122.4701 | 122.3969 | 122.374 | 122.3419 | -122.5159 | -122.4747 | 122.3419 | 122.4197 | 59.6329 | 59.6008
740.7656 | 122.6074 | -59.7153 | 62.7823 | -0.041122 | 0.0019119 | 0.061812 | 0.093043 | 0.0035889 | -0.0024994 | -0.004593 | -0.0033568 | -0.001128 | 0.063538 | 0.053572 | -0.012478 | 0.0024823 | 0.0028839 | 0.009155 | 62.6907 | -59.761 | 62.6724 | -59.5963 | -59.9762 | 0.032043 | 0.018311 | 62.677 | -59.7473 | 62.5534 | -59.7198 | -59.8068 | -59.6375 | -0.045776 | -0.091553 | -0.10986 | 0.11902 | 59.7473 | -0.26093 | 59.7931 | -0.21515 | -0.032043 | -0.10529 | -0.22888 | -0.004578 | 0.07782 | -0.091553 | 0.10986 | -0.05951 | 0.16479 | 122.4335 | 0.027465 | 122.3007 | 122.4518 | 122.4243 | 122.406 | 122.3923 | -122.5433 | -122.5296 | 122.3877 | 122.2687 | 59.7244 | 59.7336
741.7656 | 122.6212 | -59.6924 | 62.7686 | -0.07164 | -0.00043792 | 0.062453 | 0.093257 | -4.2682e-05 | -0.0012176 | -0.0016022 | -0.04303 | 0.0016492 | 0.069092 | 0.063613 | -0.014828 | 0.0041913 | -0.0011749 | -0.013733 | 62.6724 | -59.7794 | 62.6633 | -59.6375 | -59.9762 | 0.022888 | 0.022888 | 62.6724 | -59.7427 | 62.709 | -59.7748 | -59.8709 | -59.6695 | -0.086975 | -0.096131 | -0.10529 | 0.054932 | 59.7153 | -0.28381 | 59.8022 | -0.19684 | -0.050354 | -0.096131 | -0.05951 | -0.082397 | 0.022888 | -0.17853 | 0.073242 | -0.12817 | 0.14191 | 122.4426 | -0.032043 | 122.4518 | 122.4518 | 122.4152 | 122.3648 | 122.3648 | -122.5479 | -122.5113 | 122.3557 | 122.4014 | 59.6786 | 59.7153
742.7656 | 122.6486 | -59.7244 | 62.7319 | -0.0029755 | 0.0025529 | 0.060957 | 0.093684 | -0.00068368 | -0.0012176 | 0.00053404 | -0.039978 | 0.00079477 | 0.06482 | 0.063826 | -0.014614 | 0.0018413 | 0.00074769 | 0.004578 | 62.7182 | -59.7656 | 62.6587 | -59.6329 | -59.9899 | 0.018311 | -0.004578 | 62.6678 | -59.7519 | 62.6999 | -59.7656 | -59.8709 | -59.6695 | -0.041199 | -0.013733 | -0.073243 | 0.091552 | 59.7427 | -0.2655 | 59.7839 | -0.2243 | -0.027466 | -0.064087 | -0.032044 | -0.041199 | 0.054931 | -0.14648 | 0.082397 | -0.11902 | 0.13275 | 122.4243 | -0.013733 | 122.4518 | 122.4838 | 122.4197 | 122.4426 | 122.3923 | -122.4976 | -122.4838 | 122.3831 | 122.4243 | 59.729 | 59.7198
743.7656 | 122.6715 | -59.7153 | 62.7457 | -0.048752 | 0.0021255 | 0.063094 | 0.093471 | 0.0044433 | -0.0029266 | -0.00074776 | -0.055237 | -5.9826e-05 | 0.06482 | 0.058913 | -0.014187 | 0.00013253 | -0.0024567 | 0.013733 | 62.6724 | -59.7839 | 62.7136 | -59.5871 | -59.9579 | 0.041199 | 0.050354 | 62.6633 | -59.7427 | 62.7548 | -59.729 | -59.8526 | -59.6466 | -0.068665 | -0.073243 | -0.032044 | 0.12817 | 59.7565 | -0.24262 | 59.8251 | -0.17395 | -0.027466 | -0.082398 | 0.009155 | -0.013733 | 0.068665 | -0.13733 | 0.096131 | -0.10986 | 0.19684 | 122.4976 | 0.013733 | 122.4976 | 122.4564 | 122.406 | 122.3877 | 122.3785 | -122.5296 | -122.4884 | 122.4289 | 122.4701 | 59.729 | 59.7656
744.7656 | 122.731 | -59.697 | 62.6724 | -0.086899 | 0.0019119 | 0.063307 | 0.094112 | -0.0034607 | -0.0016448 | -0.0013886 | 0.0057984 | 0.00015377 | 0.066101 | 0.062117 | -0.013546 | 0.0022687 | -0.0030975 | -0.032043 | 62.5809 | -59.7794 | 62.7411 | -59.5367 | -59.935 | -0.032043 | 0 | 62.5809 | -59.7794 | 62.7823 | -59.6924 | -59.8114 | -59.6054 | -0.082398 | -0.091552 | 0.068665 | 0.16022 | 59.6649 | -0.23804 | 59.7473 | -0.15564 | -0.082398 | -0.091552 | 0.10986 | 0.004577 | 0.091552 | -0.11444 | 0.17395 | -0.032043 | 0.24262 | 122.5204 | 0.086975 | 122.5616 | 122.3602 | 122.3602 | 122.2778 | 122.2778 | -122.4518 | -122.4518 | 122.438 | 122.4792 | 59.6649 | 59.697
745.7656 | 122.6395 | -59.7153 | 62.7457 | -0.033493 | -1.0718e-05 | 0.061385 | 0.094966 | -0.0026063 | -0.0012176 | 0.00096124 | -0.064392 | 0.00058097 | 0.063324 | 0.06639 | -0.014187 | 0.0018413 | 0.0022431 | 0.013733 | 62.6816 | -59.7794 | 62.6907 | -59.5825 | -59.9625 | 0.032043 | 0.045776 | 62.645 | -59.7565 | 62.7502 | -59.7382 | -59.8709 | -59.6512 | -0.064087 | -0.064087 | -0.054932 | 0.13275 | 59.7473 | -0.24719 | 59.8114 | -0.1831 | -0.041199 | -0.10071 | 0.004577 | -0.022888 | 0.064087 | -0.15564 | 0.10529 | -0.11444 | 0.19684 | 122.4701 | 0.018311 | 122.5067 | 122.4609 | 122.4014 | 122.3969 | 122.3602 | -122.525 | -122.5021 | 122.406 | 122.4655 | 59.729 | 59.761
746.7656 | 122.6166 | -59.7382 | 62.764 | -0.07164 | -0.0012923 | 0.060957 | 0.093257 | 0.0020935 | -0.0037812 | -0.0013886 | -0.039978 | -0.00070063 | 0.06781 | 0.068953 | -0.014187 | 0.0018413 | -0.0024567 | 0.004578 | 62.7136 | -59.7748 | 62.6587 | -59.6329 | -59.9899 | 0.022888 | 0 | 62.677 | -59.7336 | 62.7045 | -59.7519 | -59.8801 | -59.6558 | -0.036621 | -0.050354 | -0.10529 | 0.10529 | 59.761 | -0.25177 | 59.7977 | -0.21515 | 0.004577 | -0.086975 | -0.059509 | -0.013733 | 0.082397 | -0.14191 | 0.07782 | -0.14648 | 0.14191 | 122.4335 | -0.01831 | 122.4381 | 122.4884 | 122.4106 | 122.4518 | 122.4152 | -122.5388 | -122.4976 | 122.3969 | 122.4426 | 59.7427 | 59.7382
747.7656 | 122.644 | -59.7244 | 62.7548 | -0.033493 | 0.00041648 | 0.061812 | 0.092616 | 0.00038452 | 0.0004914 | -0.00096136 | -0.024719 | 0.00015377 | 0.065674 | 0.060836 | -0.013119 | 0.0014141 | -0.0013885 | -0.004578 | 62.709 | -59.7839 | 62.6724 | -59.6191 | -59.9854 | 0.027466 | -0.004578 | 62.6907 | -59.7565 | 62.6999 | -59.7519 | -59.8572 | -59.6512 | -0.05951 | -0.045777 | -0.082398 | 0.10529 | 59.7519 | -0.26093 | 59.8114 | -0.20142 | -0.032044 | -0.064087 | -0.054932 | -0.027466 | 0.073242 | -0.13275 | 0.10529 | -0.10071 | 0.16479 | 122.4564 | 0.004578 | 122.4564 | 122.493 | 122.4472 | 122.4335 | 122.4152 | -122.5388 | -122.5113 | 122.3969 | 122.4243 | 59.7198 | 59.7198
748.7656 | 122.6852 | -59.7198 | 62.7228 | -0.048752 | -0.00086512 | 0.063734 | 0.093684 | -0.00068368 | -0.0022858 | -0.002243 | -0.046081 | -0.0024096 | 0.062897 | 0.057631 | -0.012691 | 0.0037641 | -0.00096131 | 0.027466 | 62.677 | -59.7885 | 62.6907 | -59.5917 | -59.9625 | 0.036621 | 0.045776 | 62.6816 | -59.7565 | 62.7502 | -59.7382 | -59.8526 | -59.6375 | -0.068664 | -0.045776 | -0.032043 | 0.12817 | 59.7565 | -0.24261 | 59.8251 | -0.17395 | -0.036621 | -0.041198 | 0.027466 | -0.01831 | 0.082398 | -0.13275 | 0.11902 | -0.09613 | 0.19684 | 122.4792 | 0.018311 | 122.5067 | 122.4655 | 122.4381 | 122.3969 | 122.4014 | -122.5113 | -122.4792 | 122.4106 | 122.4701 | 59.7473 | 59.7656
749.7656 | 122.7219 | -59.7198 | 62.709 | -0.14793 | 0.0016983 | 0.061812 | 0.091548 | 0.0038025 | -0.0012176 | -0.003952 | 0.063782 | 0.0010084 | 0.064392 | 0.052504 | -0.011837 | 0.0024823 | -0.0028839 | -0.068665 | 62.6221 | -59.7794 | 62.677 | -59.5871 | -59.9762 | 0.17395 | -0.13275 | 62.5809 | -59.7748 | 62.7045 | -59.7198 | -59.8297 | -59.642 | -0.059509 | -0.086975 | -0.032043 | 0.13275 | 59.8938 | -0.25635 | 59.9533 | -0.19684 | -0.054931 | -0.12817 | -0.004577 | 0 | 0.07782 | -0.10986 | 0.13275 | -0.054932 | 0.19226 | 122.4564 | 0.054931 | 122.4792 | 122.4014 | 122.3557 | 122.3419 | 122.3007 | -122.4884 | -122.4838 | 122.3969 | 122.4243 | 59.6512 | 59.5871
750.7656 | 122.6624 | -59.7015 | 62.7045 | -0.079269 | -0.00022432 | 0.062666 | 0.094966 | -0.0011109 | -0.0029266 | -0.00053396 | -0.085754 | -0.001128 | 0.065674 | 0.070235 | -0.014187 | 0.0014141 | -0.0024567 | -0.16479 | 62.6358 | -59.7885 | 62.709 | -59.5779 | -59.9625 | 0.022888 | 0.032043 | 62.6541 | -59.7473 | 62.7365 | -59.7473 | -59.8572 | -59.6558 | -0.086975 | -0.068665 | 0.004577 | 0.1236 | 59.7244 | -0.26093 | 59.8114 | -0.17395 | -0.045776 | -0.050354 | 0.032043 | -0.045776 | 0.045776 | -0.15564 | 0.091552 | -0.10986 | 0.21057 | 122.4976 | 0 | 122.4838 | 122.4243 | 122.4014 | 122.3373 | 122.3557 | -122.493 | -122.4518 | 122.4106 | 122.438 | 59.5367 | 59.7336
751.7656 | 122.6624 | -59.7198 | 62.7365 | -0.041122 | 0.0029801 | 0.063307 | 0.094325 | 0.00059812 | -0.0024994 | 0.00053404 | -0.052185 | 0.0014356 | 0.065888 | 0.060622 | -0.014614 | 0.0024823 | 0.00032049 | -0.073242 | 62.6358 | -59.8114 | 62.7365 | -59.5688 | -59.9625 | 0.036621 | 0.045776 | 62.6495 | -59.7565 | 62.7411 | -59.729 | -59.8663 | -59.642 | -0.091552 | -0.10071 | 0 | 0.15106 | 59.7565 | -0.24261 | 59.848 | -0.15106 | -0.036621 | -0.086975 | 0.004578 | -0.009155 | 0.07782 | -0.14648 | 0.11444 | -0.10986 | 0.24261 | 122.5479 | 0.027466 | 122.4976 | 122.4472 | 122.406 | 122.3557 | 122.3694 | -122.5479 | -122.493 | 122.4564 | 122.4609 | 59.6466 | 59.7656
752.7656 | 122.6532 | -59.729 | 62.7228 | -0.056381 | -0.00043792 | 0.062453 | 0.095393 | -0.00046988 | -0.0003632 | -0.00096136 | -0.024719 | -0.00048703 | 0.066101 | 0.062758 | -0.014614 | 0.0018413 | 0.0020295 | 0.059509 | 62.6678 | -59.8114 | 62.6999 | -59.5551 | -59.9899 | 0.027466 | 0.032043 | 62.6404 | -59.761 | 62.7457 | -59.7519 | -59.8572 | -59.6329 | -0.082397 | -0.054931 | -0.022888 | 0.17395 | 59.7565 | -0.26092 | 59.8389 | -0.17853 | -0.032043 | -0.082397 | 0.022889 | -0.022888 | 0.09613 | -0.12817 | 0.12817 | -0.096131 | 0.25635 | 122.5113 | 0.009155 | 122.5067 | 122.4792 | 122.4014 | 122.3969 | 122.3694 | -122.5342 | -122.4838 | 122.4289 | 122.4747 | 59.7885 | 59.761
753.7656 | 122.6669 | -59.7015 | 62.7411 | -0.07164 | 0.0014847 | 0.063307 | 0.094539 | -0.00089728 | -0.0001496 | 0.00074764 | -0.033874 | 0.00015377 | 0.06546 | 0.064894 | -0.015896 | 0.0022687 | -0.00074771 | 0.004578 | 62.6907 | -59.7885 | 62.6953 | -59.5779 | -59.9762 | 0.032043 | 0.013733 | 62.6541 | -59.7565 | 62.7319 | -59.7244 | -59.8572 | -59.642 | -0.086975 | -0.050354 | -0.045777 | 0.1236 | 59.7336 | -0.27466 | 59.8206 | -0.18768 | -0.054932 | -0.086975 | -0.009155 | -0.022888 | 0.059509 | -0.15564 | 0.11444 | -0.10071 | 0.21057 | 122.4838 | 0.032044 | 122.4884 | 122.4792 | 122.4106 | 122.3923 | 122.3557 | -122.5296 | -122.4976 | 122.3969 | 122.4335 | 59.7061 | 59.7153
754.7656 | 122.6349 | -59.7382 | 62.6999 | -0.041122 | 0.0023391 | 0.062666 | 0.093471 | 0.0044433 | 6.4004e-05 | -0.0048066 | -0.046081 | 0.00229 | 0.064179 | 0.05934 | -0.013332 | 0.0014141 | -0.00010671 | -0.14191 | 62.6953 | -59.7885 | 62.5946 | -59.7015 | -60.0632 | -0.10529 | -0.14191 | 62.6358 | -59.7839 | 62.6541 | -59.8251 | -59.9579 | -59.7061 | -0.050354 | -0.004578 | -0.10529 | 0.036621 | 59.6329 | -0.32501 | 59.6832 | -0.27466 | -0.045777 | -0.064087 | -0.045776 | -0.086975 | 0.032043 | -0.21973 | 0.07782 | -0.17395 | 0.086975 | 122.3831 | -0.041198 | 122.4381 | 122.4838 | 122.4197 | 122.4335 | 122.374 | -122.4884 | -122.4838 | 122.3328 | 122.3923 | 59.5963 | 59.5963
755.7656 | 122.6257 | -59.7382 | 62.7228 | -0.12505 | 0.0021255 | 0.06053 | 0.092189 | -0.00046988 | -0.001004 | 0.00010684 | -0.039978 | 0.00015377 | 0.065674 | 0.065749 | -0.012691 | 0.0037641 | 0.0013885 | -0.009155 | 62.6724 | -59.7977 | 62.6724 | -59.61 | -60.0128 | -0.032043 | -0.032043 | 62.645 | -59.7565 | 62.6907 | -59.7748 | -59.9121 | -59.6878 | -0.059509 | -0.050354 | -0.050354 | 0.12817 | 59.7061 | -0.27466 | 59.7656 | -0.21515 | -0.018311 | -0.07782 | -0.032043 | -0.036621 | 0.050354 | -0.17395 | 0.068665 | -0.15564 | 0.18768 | 122.4701 | -0.01831 | 122.4472 | 122.4701 | 122.4014 | 122.4106 | 122.3831 | -122.5204 | -122.4792 | 122.4106 | 122.4289 | 59.729 | 59.7061
756.7656 | 122.6257 | -59.7382 | 62.7274 | -0.13267 | -1.0718e-05 | 0.063734 | 0.093257 | 0.0038025 | -0.0016448 | 0.00074764 | -0.04303 | -0.00048703 | 0.064179 | 0.068953 | -0.0144 | 0.0041913 | 0.0030975 | -0.018311 | 62.6633 | -59.7839 | 62.6587 | -59.6008 | -59.9945 | -0.027466 | -0.036621 | 62.6541 | -59.7702 | 62.709 | -59.7977 | -59.903 | -59.6786 | -0.045777 | -0.064087 | -0.068665 | 0.13733 | 59.7107 | -0.25635 | 59.7565 | -0.21057 | -0.032044 | -0.073242 | -0.018311 | -0.059509 | 0.059509 | -0.16479 | 0.091553 | -0.13275 | 0.18311 | 122.4426 | -0.027465 | 122.4792 | 122.4472 | 122.4243 | 122.4014 | 122.3923 | -122.5113 | -122.4976 | 122.3969 | 122.4472 | 59.7198 | 59.7015
757.7656 | 122.3969 | -59.761 | 62.6312 | -0.10979 | 0.0016983 | 0.063948 | 0.094112 | -0.0036743 | -0.0012176 | 0.00096124 | -0.027771 | 0.00015377 | 0.064179 | 0.062331 | -0.01376 | 0.0024823 | -0.00053411 | -0.064087 | 62.6633 | -59.8114 | 62.6083 | -59.7015 | -60.0632 | -0.091553 | -0.16479 | 62.6221 | -59.7794 | 62.6358 | -59.8572 | -59.9716 | -59.5963 | -0.050354 | 0.032043 | -0.022889 | 0.059509 | 59.6695 | -0.30212 | 59.7198 | -0.25177 | -0.018311 | -0.009156 | 0.004577 | -0.096131 | 0.16479 | -0.21057 | 0.18311 | -0.19226 | 0.10986 | 122.4197 | -0.07782 | 122.4152 | 122.4747 | 122.4014 | 122.4243 | 122.3831 | -122.4426 | -122.4106 | 122.3694 | 122.3969 | 59.697 | 59.5963
758.7656 | 122.6532 | -59.7565 | 62.7411 | -0.10216 | 0.0010575 | 0.062666 | 0.093257 | 0.00017092 | -0.0016448 | -0.0018158 | -0.033874 | 0.00058097 | 0.062897 | 0.063826 | -0.013546 | 0.0022687 | -0.00074771 | -0.032043 | 62.677 | -59.8114 | 62.6678 | -59.61 | -60.022 | -0.054932 | -0.045776 | 62.6541 | -59.7839 | 62.6907 | -59.8022 | -59.9075 | -59.6741 | -0.054931 | -0.064087 | -0.073242 | 0.14648 | 59.7015 | -0.2655 | 59.7565 | -0.21057 | -0.027466 | -0.086975 | -0.050354 | -0.045776 | 0.082398 | -0.15106 | 0.10986 | -0.1236 | 0.20142 | 122.4792 | -0.01831 | 122.4747 | 122.4884 | 122.4381 | 122.4335 | 122.4106 | -122.5525 | -122.525 | 122.4243 | 122.4472 | 59.7244 | 59.7107
759.7656 | 122.612 | -59.7427 | 62.7274 | -0.056381 | 0.0016983 | 0.06288 | 0.094966 | 0.0031617 | 0.0004914 | 0.0016022 | -0.039978 | 0.0010084 | 0.065674 | 0.061476 | -0.015682 | 0.00034613 | -0.00053411 | -0.036621 | 62.6358 | -59.8022 | 62.6495 | -59.6329 | -60.0357 | -0.068665 | -0.073242 | 62.6358 | -59.7519 | 62.6862 | -59.7977 | -59.9304 | -59.697 | -0.059509 | -0.091553 | -0.07782 | 0.10986 | 59.6741 | -0.29297 | 59.7336 | -0.23346 | -0.009155 | -0.091553 | -0.041199 | -0.054931 | 0.045777 | -0.18768 | 0.054932 | -0.17853 | 0.16937 | 122.4518 | -0.045776 | 122.438 | 122.438 | 122.3877 | 122.3785 | 122.3785 | -122.5296 | -122.4792 | 122.3923 | 122.4289 | 59.7061 | 59.6695
760.7656 | 122.6395 | -59.7336 | 62.7274 | -0.025863 | -0.00043792 | 0.063948 | 0.094966 | 0.00059812 | -0.001004 | 0.00032044 | -0.030823 | 0.0020764 | 0.065888 | 0.052931 | -0.016109 | 0.0012005 | -0.00074771 | 0.004578 | 62.6724 | -59.7839 | 62.6907 | -59.5871 | -59.9808 | -0.004578 | 0.004578 | 62.6633 | -59.761 | 62.7228 | -59.7519 | -59.8755 | -59.6603 | -0.050354 | -0.054932 | -0.036621 | 0.14648 | 59.729 | -0.24719 | 59.7794 | -0.19684 | -0.027465 | -0.064087 | -0.004578 | -0.01831 | 0.073243 | -0.14191 | 0.10071 | -0.11444 | 0.19684 | 122.4747 | 0.009155 | 122.4838 | 122.4564 | 122.4243 | 122.406 | 122.3969 | -122.5113 | -122.4884 | 122.4243 | 122.4564 | 59.7382 | 59.7382
761.7656 | 122.6349 | -59.7198 | 62.7319 | -0.048752 | 0.0014847 | 0.06288 | 0.095607 | 0.0027343 | -0.0012176 | -0.0013886 | -0.0064086 | -0.00027343 | 0.067169 | 0.063185 | -0.015469 | 0.0014141 | -0.0016021 | -0.009155 | 62.6862 | -59.7839 | 62.6816 | -59.6008 | -59.9808 | -0.018311 | -0.004578 | 62.6495 | -59.7427 | 62.6999 | -59.761 | -59.8755 | -59.6558 | -0.064087 | -0.045777 | -0.050354 | 0.11902 | 59.7015 | -0.26092 | 59.7656 | -0.19684 | -0.022888 | -0.082398 | -0.032044 | -0.041198 | 0.064087 | -0.15564 | 0.086975 | -0.13275 | 0.18311 | 122.4655 | -0.01831 | 122.4426 | 122.4701 | 122.3923 | 122.406 | 122.3694 | -122.5159 | -122.4747 | 122.4014 | 122.4197 | 59.7107 | 59.7153
762.7656 | 122.5937 | -59.7565 | 62.7457 | -0.11742 | 0.00020288 | 0.063734 | 0.094539 | 0.0025207 | -0.0005768 | -0.0024566 | -0.024719 | -0.00070063 | 0.064179 | 0.061049 | -0.014187 | 0.0022687 | -0.00010671 | -0.073242 | 62.6541 | -59.8022 | 62.6266 | -59.6603 | -60.0494 | -0.091553 | -0.1236 | 62.6312 | -59.761 | 62.6633 | -59.8297 | -59.9716 | -59.7061 | -0.045776 | -0.091553 | -0.11902 | 0.096131 | 59.6649 | -0.29297 | 59.7107 | -0.24719 | -0.004577 | -0.11444 | -0.082398 | -0.073242 | 0.050354 | -0.21515 | 0.054931 | -0.21057 | 0.14191 | 122.4289 | -0.068665 | 122.4243 | 122.4564 | 122.3923 | 122.4106 | 122.3877 | -122.5479 | -122.5067 | 122.3831 | 122.4197 | 59.6832 | 59.6329
763.7656 | 122.6715 | -59.7382 | 62.6999 | -0.15556 | -0.00043792 | 0.062666 | 0.093898 | 0.0010253 | -0.0001496 | -0.0016022 | -0.024719 | 0.00036737 | 0.063538 | 0.058913 | -0.014614 | 0.0026959 | -0.0024567 | -0.10071 | 62.6358 | -59.8206 | 62.6312 | -59.6329 | -60.0449 | -0.10071 | -0.14191 | 62.59 | -59.7656 | 62.6953 | -59.7565 | -59.8755 | -59.6603 | -0.082398 | -0.064087 | -0.068664 | 0.10529 | 59.6375 | -0.3067 | 59.7198 | -0.2243 | -0.027466 | -0.10986 | -0.004578 | -0.018311 | 0.07782 | -0.13733 | 0.10529 | -0.10986 | 0.18768 | 122.4518 | 0.009155 | 122.4609 | 122.4564 | 122.3557 | 122.374 | 122.3282 | -122.5204 | -122.4655 | 122.3694 | 122.4335 | 59.6375 | 59.5963
764.7656 | 122.6166 | -59.7382 | 62.6999 | -0.10979 | 0.0016983 | 0.061385 | 0.094112 | 0.0016663 | -0.002713 | -0.0013886 | -0.049133 | 0.0010084 | 0.065247 | 0.066817 | -0.015896 | 0.0020551 | 0.0052337 | -0.082397 | 62.6495 | -59.8114 | 62.5946 | -59.6832 | -60.0677 | -0.1236 | -0.15106 | 62.6404 | -59.7977 | 62.6724 | -59.8206 | -59.9442 | -59.7061 | -0.073242 | -0.050354 | -0.10529 | 0.054931 | 59.6146 | -0.32959 | 59.6878 | -0.25635 | -0.059509 | -0.059509 | -0.027466 | -0.082398 | 0.032043 | -0.20599 | 0.091552 | -0.14648 | 0.12817 | 122.406 | -0.022889 | 122.4701 | 122.4609 | 122.438 | 122.3877 | 122.3785 | -122.5113 | -122.4976 | 122.3328 | 122.4106 | 59.6558 | 59.5871
765.7656 | 122.6486 | -59.7198 | 62.7228 | -0.10216 | -0.00022432 | 0.063094 | 0.094966 | 0.0012391 | -0.0012176 | -0.0041656 | -0.0094604 | 0.00015377 | 0.066315 | 0.061904 | -0.015041 | 0.0024823 | -0.00010671 | -0.11902 | 62.6587 | -59.8297 | 62.6038 | -59.6924 | -60.0723 | -0.11444 | -0.13733 | 62.6221 | -59.7748 | 62.6633 | -59.8068 | -59.9304 | -59.7107 | -0.10986 | -0.064087 | -0.11902 | 0.027466 | 59.6054 | -0.35248 | 59.7153 | -0.24262 | -0.054931 | -0.10071 | -0.059509 | -0.086975 | 0.009156 | -0.21057 | 0.064087 | -0.15564 | 0.13733 | 122.4335 | -0.032044 | 122.438 | 122.4884 | 122.3969 | 122.3785 | 122.3419 | -122.5525 | -122.4976 | 122.3236 | 122.3831 | 59.6008 | 59.5825
766.7656 | 122.6578 | -59.7473 | 62.7136 | -0.056381 | -1.0718e-05 | 0.062453 | 0.093257 | 0.0048705 | -0.0018586 | -0.0030976 | -0.024719 | -0.00027343 | 0.066101 | 0.058486 | -0.013973 | 0.0026959 | 0.0035247 | -0.10529 | 62.6587 | -59.8206 | 62.6083 | -59.6512 | -60.0723 | -0.10071 | -0.13275 | 62.6129 | -59.8068 | 62.6862 | -59.7794 | -59.9258 | -59.6878 | -0.073243 | -0.054932 | -0.10529 | 0.09613 | 59.6466 | -0.32501 | 59.7198 | -0.25177 | -0.05951 | -0.10071 | -0.027466 | -0.032044 | 0.059509 | -0.17853 | 0.11902 | -0.11902 | 0.16937 | 122.4289 | 0.027466 | 122.493 | 122.4792 | 122.4197 | 122.406 | 122.3602 | -122.5342 | -122.5204 | 122.3557 | 122.4335 | 59.642 | 59.6146
767.7656 | 122.6212 | -59.7565 | 62.7045 | -0.048752 | -0.0010787 | 0.063734 | 0.096461 | 0.0020935 | -0.0001496 | -0.0033112 | -0.0033568 | 0.00058097 | 0.065033 | 0.065108 | -0.014187 | 0.0014141 | 0.0030975 | -0.11902 | 62.6633 | -59.8251 | 62.8235 | -59.6695 | -60.173 | -0.091553 | -0.16937 | 62.6221 | -59.761 | 62.677 | -59.8389 | -59.9396 | -59.6741 | -0.068664 | -0.041199 | 0.11902 | 0.086975 | 59.6649 | -0.41656 | 59.7336 | -0.3479 | -0.004577 | -0.082398 | -0.027466 | -0.082397 | 0.082398 | -0.1831 | 0.086975 | -0.17853 | 0.15564 | 122.6486 | -0.07782 | 122.438 | 122.4884 | 122.3831 | 122.4197 | 122.3785 | -122.5296 | -122.4655 | 122.58 | 122.4335 | 59.6375 | 59.5871
768.7656 | 122.612 | -59.7473 | 62.7136 | -0.16319 | 0.0010575 | 0.062025 | 0.095607 | -0.0019653 | -0.0022858 | -0.00032036 | -0.036926 | 0.0010084 | 0.065033 | 0.063185 | -0.014614 | 0.0039777 | 0.0013885 | -0.1236 | 62.59 | -59.8206 | 62.5946 | -59.7336 | -60.0632 | -0.091553 | -0.14648 | 62.6495 | -59.8022 | 62.6862 | -59.8206 | -59.9487 | -59.7153 | -0.073243 | -0.1236 | -0.11902 | 0.013732 | 59.6558 | -0.31586 | 59.729 | -0.24261 | -0.054932 | -0.064087 | -0.027466 | -0.073243 | 0.032043 | -0.20142 | 0.086975 | -0.14648 | 0.086975 | 122.4152 | -0.018311 | 122.4884 | 122.4106 | 122.4518 | 122.3373 | 122.3969 | -122.5342 | -122.5159 | 122.3419 | 122.4335 | 59.6237 | 59.6008
769.7656 | 122.699 | -59.7107 | 62.6587 | -0.13267 | 0.00041648 | 0.064162 | 0.093898 | 0.00038452 | -0.0001496 | 0.00032044 | -0.0064086 | -0.001128 | 0.063538 | 0.067671 | -0.014828 | 0.0016277 | -0.0016021 | -0.050354 | 62.645 | -59.7977 | 62.7045 | -59.5596 | -59.9579 | -0.032043 | -0.045776 | 62.59 | -59.7656 | 62.6541 | -59.5688 | -59.5551 | -59.4315 | -0.086975 | -0.013733 | 0.045777 | 0.15106 | 59.6786 | -0.24719 | 59.7656 | -0.16022 | -0.054932 | -0.068664 | -0.004577 | 0.14191 | 0.27923 | 0.15564 | 0.33417 | 0.21057 | 0.23804 | 122.5021 | 0.19684 | 122.4197 | 122.4426 | 122.3557 | 122.3557 | 122.3007 | -122.4564 | -122.4243 | 122.4152 | 122.3648 | 59.6603 | 59.6649
770.7656 | 122.7402 | -59.7015 | 62.677 | -0.10216 | 0.0023391 | 0.062666 | 0.094966 | 0.0040161 | -0.0012176 | -0.0013886 | -0.0064086 | -0.00070063 | 0.062683 | 0.057845 | -0.014828 | 0.00055973 | -0.00096131 | -0.027466 | 62.5763 | -59.7977 | 62.7182 | -59.5551 | -59.9533 | -0.032043 | -0.004578 | 62.5763 | -59.7931 | 62.7457 | -59.6786 | -59.8251 | -59.5917 | -0.09613 | -0.10071 | 0.041199 | 0.14648 | 59.6695 | -0.25177 | 59.7656 | -0.15564 | -0.091553 | -0.10071 | 0.068665 | 0.022888 | 0.10986 | -0.1236 | 0.20142 | -0.032043 | 0.24261 | 122.5159 | 0.11444 | 122.5388 | 122.374 | 122.3694 | 122.2778 | 122.2778 | -122.4747 | -122.4701 | 122.4197 | 122.4472 | 59.6741 | 59.697
771.7656 | 122.7356 | -59.6924 | 62.677 | -0.17082 | 0.00041648 | 0.063521 | 0.093684 | 0.00081172 | -0.0001496 | -0.0024566 | 0.030212 | -0.00091423 | 0.063751 | 0.060836 | -0.016109 | 0.00034613 | 0.00010689 | -0.036621 | 62.59 | -59.761 | 62.7274 | -59.5505 | -59.9579 | -0.027466 | -0.004578 | 62.5809 | -59.7519 | 62.7594 | -59.7061 | -59.8206 | -59.6146 | -0.068664 | -0.086975 | 0.050354 | 0.14191 | 59.6649 | -0.2655 | 59.7336 | -0.19684 | -0.059509 | -0.09613 | 0.082397 | -0.013733 | 0.07782 | -0.12817 | 0.13733 | -0.068665 | 0.21057 | 122.4884 | 0.045776 | 122.5113 | 122.3511 | 122.3328 | 122.2824 | 122.2733 | -122.438 | -122.4289 | 122.4197 | 122.4518 | 59.6558 | 59.6878
772.7656 | 122.7448 | -59.697 | 62.677 | -0.14793 | 0.0014847 | 0.061812 | 0.093684 | 0.0023071 | 0.0009186 | -0.00096136 | 0.094299 | -0.0013416 | 0.063111 | 0.06404 | -0.016109 | 0.0016277 | -0.0026703 | -0.032043 | 62.6083 | -59.7702 | 62.7228 | -59.5047 | -60.2554 | -0.10071 | -0.064087 | 62.6038 | -59.7519 | 62.7869 | -59.7198 | -59.8068 | -59.6054 | -0.073243 | -0.068665 | 0.045776 | 0.19226 | 59.5963 | -0.55847 | 59.6695 | -0.48523 | -0.054932 | -0.073242 | 0.10986 | -0.022889 | 0.091552 | -0.10986 | 0.14648 | -0.054932 | 0.2655 | 122.493 | 0.032043 | 122.5388 | 122.3785 | 122.3557 | 122.3053 | 122.3007 | -122.4472 | -122.4289 | 122.4197 | 122.4838 | 59.6649 | 59.6329
773.7656 | 122.7448 | -59.7061 | 62.6724 | -0.094528 | 0.00041648 | 0.062666 | 0.093043 | 0.00081172 | -0.0018586 | 0.0035248 | -0.04303 | 0.00036737 | 0.062897 | 0.063399 | -0.015255 | 0.0014141 | -0.0026703 | -0.032043 | 62.5946 | -59.7977 | 62.5671 | -59.5093 | -59.6466 | 0.068665 | 0.004578 | 62.59 | -59.7473 | 62.7731 | -59.6924 | -59.8297 | -59.5963 | -0.091552 | -0.07782 | -0.10529 | 0.19684 | 59.7748 | 0.05951 | 59.8663 | 0.15106 | -0.041198 | -0.082397 | 0.10071 | 0.013733 | 0.10986 | -0.1236 | 0.15106 | -0.082398 | 0.28839 | 122.3648 | 0.054931 | 122.5204 | 122.3923 | 122.3373 | 122.3007 | 122.2961 | -122.4701 | -122.4197 | 122.2733 | 122.4792 | 59.6741 | 59.7107
774.7656 | 122.7081 | -59.7061 | 62.6999 | -0.15556 | -0.00022432 | 0.061385 | 0.094966 | -0.00046988 | 6.4004e-05 | 0.00096124 | -0.052185 | -5.9826e-05 | 0.064179 | 0.058272 | -0.017178 | 0.0018413 | -0.00010671 | -0.091553 | 62.6221 | -59.8206 | 62.6495 | -59.6191 | -60.0174 | -0.073242 | -0.064087 | 62.5992 | -59.7839 | 62.7502 | -59.7107 | -59.8434 | -59.6054 | -0.11444 | -0.07782 | -0.050354 | 0.086975 | 59.6329 | -0.31128 | 59.7473 | -0.19684 | -0.07782 | -0.10071 | 0.050354 | -0.004577 | 0.10071 | -0.13733 | 0.17853 | -0.059509 | 0.20142 | 122.4701 | 0.073243 | 122.5342 | 122.4426 | 122.3831 | 122.3282 | 122.3053 | -122.5204 | -122.4838 | 122.3557 | 122.4564 | 59.6146 | 59.642
775.7656 | 122.7356 | -59.7244 | 62.6907 | -0.13267 | 0.00063028 | 0.061171 | 0.095607 | 0.0014527 | -0.0007904 | -0.0016022 | -0.049133 | 0.00015377 | 0.064179 | 0.068312 | -0.014828 | -0.00029487 | 0.00053409 | -0.07782 | 62.6404 | -59.8022 | 62.6724 | -59.6191 | -60.0082 | -0.073242 | -0.050354 | 62.5671 | -59.7794 | 62.7594 | -59.7061 | -59.8389 | -59.6008 | -0.07782 | -0.050354 | -0.018311 | 0.10529 | 59.6512 | -0.28381 | 59.729 | -0.20599 | -0.054932 | -0.1236 | 0.068664 | 0.01831 | 0.1236 | -0.11444 | 0.17853 | -0.059509 | 0.1831 | 122.4747 | 0.073242 | 122.5388 | 122.4426 | 122.3465 | 122.3648 | 122.2916 | -122.493 | -122.4701 | 122.3969 | 122.4838 | 59.6466 | 59.6741
776.7656 | 122.731 | -59.7244 | 62.6633 | -0.094528 | 0.00020288 | 0.064803 | 0.09518 | 0.0020935 | -0.0018586 | -0.001175 | -0.012512 | -0.00027343 | 0.063111 | 0.05699 | -0.015041 | 0.0020551 | -0.0018157 | -0.21515 | 62.5488 | -59.8068 | 62.7777 | -59.5459 | -59.9854 | -0.009155 | -0.009155 | 62.5717 | -59.7244 | 62.7777 | -59.697 | -59.7977 | -59.6146 | -0.082398 | -0.11444 | 0.11444 | 0.17853 | 59.7153 | -0.26093 | 59.7977 | -0.17853 | 0 | -0.091553 | 0.11444 | 0.027466 | 0.10986 | -0.073242 | 0.10986 | -0.073242 | 0.26093 | 122.5845 | 0.027466 | 122.5021 | 122.3557 | 122.2961 | 122.2733 | 122.2961 | -122.4701 | -122.3877 | 122.5021 | 122.5021 | 59.5093 | 59.7153
777.7656 | 122.6761 | -59.7015 | 62.6953 | -0.1403 | 0.0034073 | 0.06053 | 0.093471 | 0.00038452 | -0.0007904 | -0.0037384 | 0.0027466 | -0.0017688 | 0.064392 | 0.056777 | -0.015041 | -8.1274e-05 | -0.0026703 | -0.050354 | 62.5992 | -59.761 | 62.7319 | -59.5459 | -59.9625 | -0.022888 | -0.018311 | 62.5626 | -59.729 | 62.7548 | -59.7244 | -59.816 | -59.6237 | -0.059509 | -0.09613 | 0.036622 | 0.15564 | 59.6786 | -0.26093 | 59.7382 | -0.20142 | -0.027466 | -0.13275 | 0.05951 | -0.022888 | 0.07782 | -0.11444 | 0.10529 | -0.086975 | 0.21515 | 122.493 | 0.004578 | 122.4838 | 122.3602 | 122.2916 | 122.3007 | 122.2641 | -122.4564 | -122.4243 | 122.4335 | 122.4564 | 59.6512 | 59.6832
778.7656 | 122.699 | -59.6924 | 62.6999 | -0.12505 | 0.00041648 | 0.063307 | 0.094752 | -0.00046988 | -0.0033538 | -0.002243 | 0.0057984 | 0.00058097 | 0.063751 | 0.061049 | -0.016537 | 0.00055973 | -0.0016021 | -0.064087 | 62.6083 | -59.7977 | 62.7228 | -59.5459 | -59.9625 | -0.027466 | -0.009155 | 62.5763 | -59.7244 | 62.764 | -59.729 | -59.8251 | -59.61 | -0.10529 | -0.091553 | 0.022888 | 0.14648 | 59.6649 | -0.27008 | 59.7702 | -0.16479 | -0.032043 | -0.1236 | 0.064087 | -0.036621 | 0.082398 | -0.13275 | 0.11444 | -0.10071 | 0.25177 | 122.5204 | -0.004578 | 122.4884 | 122.406 | 122.3007 | 122.3007 | 122.2687 | -122.4976 | -122.4243 | 122.4152 | 122.4564 | 59.6283 | 59.6832
779.7656 | 122.6898 | -59.7061 | 62.709 | -0.086899 | 0.0016983 | 0.062453 | 0.092189 | -0.0013245 | -0.0005768 | -0.0026704 | 0.0088502 | -0.0019824 | 0.063751 | 0.06404 | -0.014614 | -0.0032855 | 0.0013885 | -0.068665 | 62.6312 | -59.7656 | 62.6907 | -59.5871 | -59.9854 | -0.027466 | -0.064087 | 62.6083 | -59.7565 | 62.8418 | -59.6512 | -59.967 | -59.6924 | -0.059509 | -0.077819 | -0.01831 | 0.11902 | 59.6787 | -0.27924 | 59.7382 | -0.21973 | -0.050354 | -0.10071 | 0.13275 | 0.054932 | 0.013733 | -0.26093 | 0.064087 | -0.21057 | 0.17853 | 122.4564 | 0.10529 | 122.5983 | 122.3969 | 122.3648 | 122.3373 | 122.3145 | -122.4747 | -122.4655 | 122.3969 | 122.5479 | 59.6375 | 59.642
780.7656 | 122.6898 | -59.7107 | 62.677 | -0.13267 | 0.0021255 | 0.063734 | 0.09518 | 0.0025207 | -0.0016448 | -0.00053396 | -0.0033568 | -5.9826e-05 | 0.062256 | 0.065962 | -0.014614 | -8.1274e-05 | -0.0041657 | -0.041199 | 62.6038 | -59.7748 | 62.709 | -59.5551 | -59.967 | -0.013733 | -0.004578 | 62.6038 | -59.761 | 62.764 | -59.729 | -59.8389 | -59.6146 | -0.064087 | -0.073242 | 0.032043 | 0.15564 | 59.697 | -0.25635 | 59.761 | -0.19226 | -0.050354 | -0.073242 | 0.086975 | -0.018311 | 0.09613 | -0.12817 | 0.14648 | -0.07782 | 0.21973 | 122.4838 | 0.032043 | 122.525 | 122.3785 | 122.3648 | 122.3145 | 122.3145 | -122.4518 | -122.438 | 122.4197 | 122.4747 | 59.6695 | 59.7061
781.7656 | 122.731 | -59.729 | 62.6724 | -0.07164 | 0.0016983 | 0.06288 | 0.095821 | -0.00046988 | -0.001004 | -0.0020294 | -0.024719 | -0.001128 | 0.064392 | 0.062117 | -0.016109 | 0.0022687 | -0.00096131 | -0.036621 | 62.6312 | -59.7656 | 62.7411 | -59.5505 | -59.9442 | -0.027466 | 0 | 62.5809 | -59.7702 | 62.7777 | -59.6878 | -59.8022 | -59.5779 | -0.036621 | -0.041198 | 0.068665 | 0.17853 | 59.7015 | -0.21515 | 59.7382 | -0.17853 | -0.041199 | -0.091552 | 0.10529 | 0.041199 | 0.15106 | -0.073242 | 0.19226 | -0.032043 | 0.21515 | 122.5067 | 0.082398 | 122.5479 | 122.3969 | 122.3511 | 122.3602 | 122.3099 | -122.438 | -122.4426 | 122.4701 | 122.5067 | 59.6924 | 59.729
782.7656 | 122.7264 | -59.697 | 62.6816 | 0.042801 | 0.00084388 | 0.065016 | 0.094966 | 0.0012391 | 0.0002778 | -0.0026704 | -0.055237 | -0.001128 | 0.061615 | 0.063613 | -0.016109 | 0.00013253 | 0.00053409 | -0.073242 | 62.5992 | -59.7839 | 62.7365 | -59.5505 | -59.9533 | -0.036621 | 0 | 62.5946 | -59.7473 | 62.7869 | -59.6878 | -59.8114 | -59.5642 | -0.086976 | -0.082398 | 0.054931 | 0.14648 | 59.6603 | -0.25635 | 59.7473 | -0.16937 | -0.050354 | -0.086976 | 0.10529 | 0.009155 | 0.13275 | -0.11444 | 0.18311 | -0.064087 | 0.23346 | 122.5204 | 0.059509 | 122.5342 | 122.3831 | 122.3419 | 122.2961 | 122.2916 | -122.4655 | -122.4289 | 122.4335 | 122.4838 | 59.6237 | 59.697
783.7656 | 122.7036 | -59.7198 | 62.6907 | -0.10216 | -1.0718e-05 | 0.062666 | 0.093043 | 0.0029479 | -0.0001496 | -0.00096136 | -0.030823 | 0.00015377 | 0.061615 | 0.061049 | -0.016323 | 0.0022687 | 0.0016021 | -0.041199 | 62.6266 | -59.7702 | 62.7319 | -59.5459 | -59.967 | -0.013733 | -0.004578 | 62.5763 | -59.761 | 62.7686 | -59.7153 | -59.8343 | -59.6191 | -0.050354 | -0.064087 | 0.041199 | 0.17395 | 59.7061 | -0.24719 | 59.7565 | -0.19684 | -0.041198 | -0.11444 | 0.07782 | 0.004578 | 0.10071 | -0.11444 | 0.14191 | -0.073243 | 0.22431 | 122.5021 | 0.045776 | 122.5296 | 122.3969 | 122.3373 | 122.3465 | 122.2961 | -122.4609 | -122.4518 | 122.4518 | 122.4884 | 59.6787 | 59.7153
784.7656 | 122.6257 | -59.7061 | 62.6999 | -0.079269 | 0.0034073 | 0.06288 | 0.092403 | -0.0019653 | -0.0003632 | -0.0033112 | -0.018616 | -0.0015552 | 0.064179 | 0.061263 | -0.014187 | 0.0020551 | -0.0016021 | -0.073242 | 62.6221 | -59.7839 | 62.6907 | -59.5917 | -59.9808 | -0.032043 | -0.050354 | 62.5946 | -59.7565 | 62.6816 | -59.5093 | -59.6786 | -59.6146 | -0.07782 | -0.07782 | -0.009155 | 0.11444 | 59.6741 | -0.27466 | 59.7519 | -0.19684 | -0.050354 | -0.10529 | -0.01831 | 0.19684 | 0.091553 | 0.027466 | 0.14191 | 0.07782 | 0.19226 | 122.4747 | 0.24719 | 122.4381 | 122.406 | 122.3511 | 122.3282 | 122.3007 | -122.4838 | -122.4564 | 122.3969 | 122.3877 | 59.6329 | 59.6558
785.7656 | 122.7859 | -59.7015 | 62.7411 | -0.19371 | 0.0014847 | 0.063521 | 0.095821 | -0.0026063 | 0.0004914 | -0.003952 | -0.015564 | -0.0013416 | 0.063751 | 0.066603 | -0.0144 | 0.0037641 | -0.0024567 | -0.064087 | 62.6266 | -59.7748 | 62.6999 | -59.5963 | -59.9991 | -0.045776 | -0.054932 | 62.5946 | -59.7519 | 62.7365 | -59.7244 | -59.8022 | -59.5871 | -0.073242 | -0.11444 | -0.041199 | 0.10529 | 59.6558 | -0.29755 | 59.729 | -0.2243 | -0.050354 | -0.14649 | -0.004578 | -0.022888 | 0.11444 | -0.10071 | 0.16479 | -0.050354 | 0.17853 | 122.4747 | 0.027466 | 122.4884 | 122.4014 | 122.3465 | 122.3282 | 122.2961 | -122.5159 | -122.493 | 122.4014 | 122.438 | 59.6375 | 59.6466
786.7656 | 122.6761 | -59.7198 | 62.7228 | -0.1403 | 0.00084388 | 0.062025 | 0.094966 | -0.0021789 | -0.0024994 | 0.00074764 | -0.049133 | -5.9826e-05 | 0.061188 | 0.064894 | -0.016323 | 0.00055973 | 0.0018159 | -0.068665 | 62.6358 | -59.7885 | 62.6953 | -59.5963 | -59.9945 | -0.036621 | -0.068665 | 62.5946 | -59.7519 | 62.7319 | -59.7198 | -59.8572 | -59.6329 | -0.068664 | -0.086975 | -0.027466 | 0.1236 | 59.6832 | -0.27466 | 59.7519 | -0.20599 | -0.032043 | -0.12817 | 0.009156 | 0 | 0.086975 | -0.13733 | 0.11902 | -0.10529 | 0.19226 | 122.4838 | 0.032043 | 122.4838 | 122.4243 | 122.3465 | 122.3557 | 122.3145 | -122.5113 | -122.4747 | 122.4152 | 122.4518 | 59.6512 | 59.6512
787.7656 | 122.6898 | -59.7244 | 62.6907 | -0.056381 | 0.0016983 | 0.062239 | 0.094966 | 0.00059812 | -0.0022858 | -0.0020294 | -0.033874 | -0.00070063 | 0.064179 | 0.060195 | -0.017178 | -0.00029487 | -0.0018157 | -0.13733 | 62.6175 | -59.7702 | 62.6678 | -59.61 | -59.9716 | -0.018311 | -0.041199 | 62.5992 | -59.7244 | 62.7365 | -59.7153 | -59.8206 | -59.6237 | -0.045777 | -0.073242 | -0.022888 | 0.11444 | 59.7061 | -0.24719 | 59.7519 | -0.20142 | 0 | -0.091553 | 0.045776 | 0.009155 | 0.10071 | -0.096131 | 0.10071 | -0.096131 | 0.16022 | 122.4381 | 0.009155 | 122.4609 | 122.3877 | 122.3236 | 122.3419 | 122.3236 | -122.4609 | -122.4152 | 122.3923 | 122.4609 | 59.5871 | 59.6832
788.7656 | 122.6807 | -59.6924 | 62.6633 | -0.10216 | -0.0012923 | 0.064375 | 0.095821 | 0.00017092 | -0.0007904 | -0.00053396 | -0.046081 | -0.001128 | 0.064392 | 0.060195 | -0.016109 | 0.0014141 | -0.0013885 | -0.032043 | 62.6266 | -59.7839 | 62.7457 | -59.5413 | -59.9625 | -0.032043 | 0.013733 | 62.5717 | -59.761 | 62.7777 | -59.7015 | -59.7977 | -59.6008 | -0.091553 | -0.036621 | 0.082398 | 0.15106 | 59.6603 | -0.27008 | 59.7519 | -0.17853 | -0.068664 | -0.091553 | 0.11444 | -0.009155 | 0.091553 | -0.10529 | 0.16022 | -0.036621 | 0.24261 | 122.5296 | 0.059509 | 122.5388 | 122.4106 | 122.3328 | 122.319 | 122.2641 | -122.4472 | -122.4243 | 122.4381 | 122.4701 | 59.6603 | 59.7061
789.7656 | 122.699 | -59.7015 | 62.6724 | -0.11742 | 0.0019119 | 0.062666 | 0.094539 | -0.00089728 | 0.0002778 | -0.002243 | -0.064392 | -0.00048703 | 0.063751 | 0.067458 | -0.015469 | 0.00034613 | -0.0026703 | -0.036621 | 62.6175 | -59.7748 | 62.7548 | -59.5413 | -59.9579 | -0.013733 | -0.004578 | 62.6038 | -59.7656 | 62.7914 | -59.6878 | -59.8022 | -59.5917 | -0.073242 | -0.054931 | 0.082398 | 0.16022 | 59.6878 | -0.25635 | 59.761 | -0.18311 | -0.064087 | -0.068664 | 0.11902 | 0.013733 | 0.10986 | -0.10071 | 0.17395 | -0.036621 | 0.23346 | 122.5296 | 0.07782 | 122.5571 | 122.3923 | 122.3694 | 122.319 | 122.3053 | -122.4472 | -122.438 | 122.4564 | 122.493 | 59.6649 | 59.697
790.7656 | 122.7173 | -59.7061 | 62.6862 | -0.1403 | -0.00043792 | 0.062666 | 0.093257 | -0.0034607 | -0.0029266 | -0.0018158 | -0.018616 | -0.00027343 | 0.06247 | 0.055495 | -0.015469 | 0.00034613 | 0.0028839 | -0.045776 | 62.6175 | -59.7839 | 62.6999 | -59.5734 | -59.9854 | -0.018311 | -0.045776 | 62.6083 | -59.7656 | 62.7411 | -59.7473 | -59.8343 | -59.6375 | -0.07782 | -0.068664 | 0.013733 | 0.13275 | 59.6878 | -0.27924 | 59.7656 | -0.20142 | -0.059509 | -0.07782 | 0.054932 | -0.041198 | 0.068665 | -0.12817 | 0.12817 | -0.068665 | 0.21057 | 122.4838 | 0.018311 | 122.5067 | 122.4014 | 122.374 | 122.3236 | 122.3145 | -122.4701 | -122.4518 | 122.406 | 122.4472 | 59.6603 | 59.6603
791.7656 | 122.6715 | -59.6878 | 62.7182 | -0.07164 | 0.0023391 | 0.06053 | 0.09283 | -0.0017517 | -0.0020722 | -0.002884 | -0.13153 | -0.00048703 | 0.06482 | 0.058486 | -0.014614 | 0.00013253 | 0.0037385 | -0.068665 | 62.6495 | -59.7748 | 62.6907 | -59.5917 | -59.7198 | 0.10986 | -0.036621 | 62.59 | -59.7702 | 62.7228 | -59.7382 | -59.8434 | -59.642 | -0.086975 | -0.068665 | -0.027466 | 0.09613 | 59.7977 | -0.032044 | 59.8846 | 0.054931 | -0.082398 | -0.12817 | 0.004577 | -0.050354 | 0.045776 | -0.15564 | 0.12817 | -0.073242 | 0.1831 | 122.4655 | 0.032044 | 122.493 | 122.4243 | 122.3602 | 122.3373 | 122.2778 | -122.493 | -122.4884 | 122.3785 | 122.4106 | 59.6191 | 59.6512
792.7656 | 122.6669 | -59.7153 | 62.6999 | -0.06401 | 0.0010575 | 0.062453 | 0.094325 | -0.0011109 | 0.0019866 | 0.00074764 | -0.024719 | -0.0036914 | 0.061829 | 0.070449 | -0.015469 | 0.00098693 | 0.0013885 | -0.050354 | 62.645 | -59.761 | 62.6999 | -59.5779 | -59.9808 | -0.027466 | 0.16937 | 62.6724 | -59.7382 | 62.7365 | -59.7198 | -59.8526 | -59.642 | -0.045776 | -0.054932 | 0 | 0.13733 | 59.6878 | -0.2655 | 59.7336 | -0.21973 | -0.022888 | -0.027466 | 0.036621 | -0.004578 | 0.073242 | -0.13733 | 0.09613 | -0.11444 | 0.1831 | 122.4609 | 0.01831 | 122.4747 | 122.406 | 122.4106 | 122.3602 | 122.3877 | -122.4609 | -122.438 | 122.4152 | 122.4518 | 59.6649 | 59.8846
793.7656 | 122.6578 | -59.7061 | 62.6862 | -0.086899 | 0.0016983 | 0.062239 | 0.095607 | -0.0017517 | -0.0016448 | 0.0013886 | -0.030823 | 0.00079477 | 0.063538 | 0.061904 | -0.016537 | 0.0016277 | -0.0011749 | -0.073242 | 62.6266 | -59.7977 | 62.6999 | -59.5963 | -59.9854 | -0.022888 | -0.064087 | 62.6175 | -59.7519 | 62.7502 | -59.7336 | -59.8663 | -59.6375 | -0.091552 | -0.059509 | 0.013733 | 0.10986 | 59.6832 | -0.27924 | 59.7748 | -0.18768 | -0.045776 | -0.068664 | 0.064087 | -0.027466 | 0.068665 | -0.16022 | 0.11444 | -0.11444 | 0.20142 | 122.4976 | 0.01831 | 122.5021 | 122.4243 | 122.3694 | 122.3328 | 122.3236 | -122.4838 | -122.438 | 122.406 | 122.4564 | 59.6329 | 59.642
794.7656 | 122.7127 | -59.7198 | 62.677 | -0.025863 | -0.0012923 | 0.060744 | 0.092403 | -0.0013245 | -0.0016448 | 0.0016022 | -0.064392 | -0.0026232 | 0.062683 | 0.061476 | -0.015255 | 0.00077333 | -0.0016021 | -0.064087 | 62.6175 | -59.7794 | 62.709 | -59.5963 | -59.9854 | -0.050354 | -0.064087 | 62.5992 | -59.7565 | 62.8967 | -59.7885 | -59.9213 | -59.6649 | -0.059509 | -0.059509 | 0.032043 | 0.1236 | 59.6695 | -0.2655 | 59.729 | -0.20599 | -0.036621 | -0.07782 | 0.21973 | -0.068664 | 0.054932 | -0.20142 | 0.091553 | -0.16479 | 0.18311 | 122.4884 | -0.032043 | 122.6532 | 122.3969 | 122.3557 | 122.3373 | 122.319 | -122.4564 | -122.4335 | 122.4289 | 122.6166 | 59.6558 | 59.6558
795.7656 | 122.7631 | -59.7107 | 62.7045 | -0.11742 | 0.00084388 | 0.063307 | 0.093471 | 0.00081172 | 0.0013458 | -0.002884 | -0.033874 | 0.0010084 | 0.063965 | 0.059981 | -0.015041 | 0.00034613 | -0.0022431 | -0.059509 | 62.6266 | -59.7931 | 62.6907 | -59.5963 | -59.9808 | -0.045776 | -0.050354 | 62.6038 | -59.7565 | 62.7502 | -59.729 | -59.697 | -59.4498 | -0.082398 | -0.07782 | -0.013733 | 0.11444 | 59.6649 | -0.27008 | 59.7473 | -0.18768 | -0.045777 | -0.10071 | 0.045776 | -0.018311 | 0.26093 | 0.013733 | 0.3067 | 0.05951 | 0.19684 | 122.4838 | 0.027466 | 122.5067 | 122.4197 | 122.3602 | 122.3373 | 122.3145 | -122.4976 | -122.4609 | 122.4014 | 122.4609 | 59.6512 | 59.6603
796.7656 | 122.7036 | -59.7061 | 62.6633 | -0.17845 | -0.00043792 | 0.063948 | 0.093471 | -0.0011109 | 0.0004914 | -0.00053396 | -0.055237 | -0.00048703 | 0.064392 | 0.058058 | -0.014828 | 0.0012005 | 0.0011749 | -0.032043 | 62.6221 | -59.7839 | 62.7411 | -59.5413 | -59.9442 | -0.045776 | 0.004578 | 62.5671 | -59.7382 | 62.7594 | -59.7015 | -59.8251 | -59.6237 | -0.07782 | -0.041199 | 0.07782 | 0.16479 | 59.6603 | -0.23804 | 59.7382 | -0.16022 | -0.032043 | -0.09613 | 0.09613 | 0.004578 | 0.082398 | -0.11902 | 0.11444 | -0.086975 | 0.24261 | 122.525 | 0.036621 | 122.4976 | 122.406 | 122.3053 | 122.3282 | 122.2733 | -122.4472 | -122.4014 | 122.4472 | 122.4655 | 59.6741 | 59.7107
797.7656 | 122.6898 | -59.7153 | 62.709 | -0.07164 | 0.00020288 | 0.06053 | 0.095607 | 0.0029479 | -0.0003632 | 0.001175 | -0.052185 | -0.00070063 | 0.06546 | 0.06169 | -0.016537 | 0.0012005 | 0.0028839 | -0.059509 | 62.6266 | -59.7839 | 62.6907 | -59.5871 | -59.9854 | -0.041199 | -0.068665 | 62.6038 | -59.7702 | 62.7411 | -59.7198 | -59.8297 | -59.6237 | -0.068665 | -0.082397 | -0.01831 | 0.12817 | 59.6741 | -0.27008 | 59.7427 | -0.20142 | -0.054932 | -0.10529 | 0.032044 | -0.004578 | 0.091553 | -0.11444 | 0.14649 | -0.059509 | 0.19684 | 122.4747 | 0.050354 | 122.5113 | 122.4106 | 122.374 | 122.3419 | 122.319 | -122.493 | -122.4792 | 122.406 | 122.4564 | 59.6558 | 59.6466
798.7656 | 122.6715 | -59.7153 | 62.6999 | -0.11742 | 0.0027665 | 0.062453 | 0.09518 | 0.00038452 | 6.4004e-05 | -0.0013886 | -0.036926 | 0.00079477 | 0.065033 | 0.055068 | -0.015896 | 0.00013253 | -0.00032051 | -0.054932 | 62.6495 | -59.7794 | 62.5946 | -59.6558 | -59.967 | -0.036621 | -0.036621 | 62.6038 | -59.7702 | 62.7411 | -59.7153 | -59.8343 | -59.6283 | -0.064087 | -0.050354 | -0.10529 | 0.059509 | 59.6787 | -0.25177 | 59.7427 | -0.18768 | -0.054932 | -0.09613 | 0.041199 | 0 | 0.086975 | -0.11902 | 0.14191 | -0.064087 | 0.1236 | 122.374 | 0.054932 | 122.5113 | 122.4289 | 122.374 | 122.3648 | 122.319 | -122.4792 | -122.4701 | 122.3099 | 122.4564 | 59.6603 | 59.6787
799.7656 | 122.6807 | -59.697 | 62.6953 | -0.094528 | -0.00022432 | 0.061171 | 0.095393 | 0.0020935 | -0.0031402 | -0.00074776 | -0.018616 | -0.00027343 | 0.064179 | 0.062758 | -0.017391 | 0.0016277 | -0.0018157 | -0.059509 | 62.6358 | -59.7839 | 62.6953 | -59.5825 | -60.0082 | 0.16022 | -0.10071 | 62.6129 | -59.7565 | 62.7182 | -59.729 | -59.8343 | -59.6146 | -0.086976 | -0.059509 | 0 | 0.11444 | 59.8572 | -0.31128 | 59.9442 | -0.2243 | -0.05951 | -0.082397 | 0.022889 | -0.032044 | 0.082397 | -0.13733 | 0.14191 | -0.07782 | 0.20142 | 122.4792 | 0.027466 | 122.4747 | 122.4197 | 122.3694 | 122.3328 | 122.3099 | -122.4792 | -122.4518 | 122.3923 | 122.4152 | 59.6375 | 59.5963
800.7656 | 122.6852 | -59.7198 | 62.7136 | -0.07164 | 0.0019119 | 0.059889 | 0.092616 | 0.00038452 | -0.0016448 | -0.0033112 | -0.055237 | -0.00027343 | 0.063538 | 0.058913 | -0.0144 | 0.0029095 | -0.0043793 | -0.068665 | 62.6358 | -59.7702 | 62.6999 | -59.5779 | -59.9762 | -0.013733 | -0.013733 | 62.6358 | -59.7244 | 62.7228 | -59.7244 | -59.7977 | -59.6191 | -0.050354 | -0.07782 | -0.013733 | 0.14191 | 59.7061 | -0.25635 | 59.7565 | -0.20599 | -0.004577 | -0.07782 | 0.009155 | -0.004577 | 0.10071 | -0.077819 | 0.10529 | -0.073242 | 0.19226 | 122.4701 | 0 | 122.4472 | 122.406 | 122.3602 | 122.3557 | 122.3557 | -122.4838 | -122.438 | 122.4197 | 122.4426 | 59.6512 | 59.7061
801.7656 | 122.6715 | -59.7107 | 62.6816 | -0.094528 | 0.0023391 | 0.063307 | 0.094752 | 0.0016663 | -0.0018586 | -0.0035248 | -0.055237 | 0.0016492 | 0.062683 | 0.057418 | -0.015682 | 0.00013253 | -0.0037383 | -0.064087 | 62.6038 | -59.7656 | 62.709 | -59.5871 | -59.9808 | -0.032043 | -0.045776 | 62.5992 | -59.7519 | 62.8006 | -59.8114 | -59.8343 | -59.6191 | -0.054932 | -0.07782 | 0.027465 | 0.1236 | 59.6786 | -0.27008 | 59.7336 | -0.21515 | -0.041199 | -0.082398 | 0.11902 | -0.10071 | 0.091552 | -0.1236 | 0.13275 | -0.082398 | 0.17853 | 122.4747 | -0.059509 | 122.5525 | 122.3694 | 122.3511 | 122.3145 | 122.3099 | -122.4472 | -122.4335 | 122.4197 | 122.5113 | 59.6466 | 59.6649
802.7656 | 122.6898 | -59.7107 | 62.6724 | -0.11742 | 0.0031937 | 0.06053 | 0.093043 | -0.0013245 | -0.0003632 | -0.0020294 | -0.06134 | 0.0010084 | 0.065247 | 0.067458 | -0.015041 | 0.0022687 | -0.0050201 | -0.036621 | 62.6266 | -59.7885 | 62.7365 | -59.5367 | -59.9716 | -0.009155 | -0.004578 | 62.5992 | -59.7656 | 62.7731 | -59.7153 | -59.8206 | -59.6191 | -0.07782 | -0.045776 | 0.064087 | 0.17395 | 59.7015 | -0.26093 | 59.7794 | -0.18311 | -0.054932 | -0.073242 | 0.10071 | -0.004578 | 0.091552 | -0.10986 | 0.14648 | -0.054932 | 0.25177 | 122.525 | 0.050354 | 122.5388 | 122.4152 | 122.3648 | 122.3373 | 122.3099 | -122.4609 | -122.438 | 122.4472 | 122.4838 | 59.6741 | 59.7061
803.7656 | 122.6761 | -59.7015 | 62.7182 | -0.12505 | 0.0019119 | 0.060744 | 0.093898 | 0.00038452 | 0.000705 | 0.00053404 | -0.052185 | 0.00015377 | 0.064179 | 0.067885 | -0.014614 | -0.00072207 | -0.0037383 | -0.068665 | 62.6312 | -59.7885 | 62.6953 | -59.6008 | -59.9808 | -0.036621 | -0.059509 | 62.6312 | -59.7473 | 62.7548 | -59.7336 | -59.8114 | -59.6191 | -0.086975 | -0.086975 | -0.022889 | 0.10071 | 59.6649 | -0.27924 | 59.7519 | -0.19226 | -0.045776 | -0.086975 | 0.036621 | -0.032044 | 0.082397 | -0.10986 | 0.12817 | -0.064087 | 0.18768 | 122.4838 | 0.013732 | 122.5021 | 122.4197 | 122.3785 | 122.3328 | 122.3328 | -122.5067 | -122.4655 | 122.3969 | 122.4564 | 59.6329 | 59.642
804.7656 | 122.7081 | -59.7015 | 62.6907 | 0.050431 | -0.00086512 | 0.062025 | 0.09518 | 0.0012391 | -0.0012176 | -0.0020294 | -0.039978 | -0.0017688 | 0.065247 | 0.053786 | -0.016537 | 0.00077333 | -0.0069427 | 0.009155 | 62.645 | -59.7748 | 62.7045 | -59.61 | -59.9762 | -0.018311 | -0.036621 | 62.6175 | -59.7473 | 62.7502 | -59.7107 | -59.816 | -59.6146 | -0.073242 | -0.045777 | 0.013733 | 0.091553 | 59.6832 | -0.27466 | 59.7565 | -0.20142 | -0.045776 | -0.073242 | 0.059509 | -0.009155 | 0.086975 | -0.11444 | 0.13275 | -0.068665 | 0.16479 | 122.4792 | 0.036621 | 122.4976 | 122.4197 | 122.3648 | 122.3465 | 122.319 | -122.4655 | -122.438 | 122.406 | 122.4518 | 59.7107 | 59.6649
805.7656 | 122.7219 | -59.7198 | 62.6862 | -0.07164 | 0.00020288 | 0.059676 | 0.093257 | 0.00038452 | -0.0035674 | -0.00053396 | -0.018616 | -5.9826e-05 | 0.063965 | 0.060622 | -0.01376 | 0.00055973 | -0.0037383 | -0.027466 | 62.6541 | -59.7839 | 62.7365 | -59.5505 | -59.935 | 0.045776 | 0.032043 | 62.6221 | -59.7336 | 62.7869 | -59.6512 | -59.7794 | -59.5825 | -0.064087 | -0.032043 | 0.050354 | 0.16937 | 59.7656 | -0.21515 | 59.8297 | -0.15106 | -0.013733 | -0.064087 | 0.10071 | 0.068665 | 0.13733 | -0.059509 | 0.15106 | -0.045776 | 0.23346 | 122.5204 | 0.082398 | 122.5204 | 122.4381 | 122.3557 | 122.374 | 122.3419 | -122.4701 | -122.4197 | 122.4564 | 122.5067 | 59.6924 | 59.7519
806.7656 | 122.6898 | -59.7061 | 62.6999 | -0.10216 | 0.0012711 | 0.062453 | 0.096889 | -0.0032471 | -0.0022858 | -0.0020294 | -0.036926 | -0.002196 | 0.063324 | 0.063399 | -0.013332 | 0.0016277 | -0.0024567 | -0.064087 | 62.6404 | -59.7565 | 62.59 | -59.6512 | -59.9533 | -0.013733 | -0.041199 | 62.6175 | -59.7702 | 62.7457 | -59.7198 | -59.8251 | -59.6054 | -0.050354 | -0.059509 | -0.10986 | 0.054932 | 59.6924 | -0.24719 | 59.7427 | -0.19684 | -0.064087 | -0.082397 | 0.045777 | -0.013733 | 0.10071 | -0.11902 | 0.1648 | -0.054931 | 0.10529 | 122.3465 | 0.050354 | 122.5159 | 122.3969 | 122.3877 | 122.3465 | 122.3236 | -122.4564 | -122.4701 | 122.2961 | 122.4518 | 59.642 | 59.6649
807.7656 | 122.6944 | -59.6878 | 62.709 | -0.12505 | 0.00063028 | 0.062666 | 0.096461 | -4.2682e-05 | -0.002713 | -0.00096136 | -0.064392 | 0.00015377 | 0.064179 | 0.052718 | -0.016323 | 0.00034613 | -0.00010671 | -0.054932 | 62.6358 | -59.7839 | 62.6678 | -59.3857 | -59.8618 | -0.09613 | -0.050354 | 62.5946 | -59.7656 | 62.7411 | -59.7061 | -59.8343 | -59.6283 | -0.096131 | -0.073242 | -0.041198 | 0.30212 | 59.5917 | -0.17395 | 59.6878 | -0.077819 | -0.07782 | -0.11444 | 0.032044 | -0.018311 | 0.059509 | -0.14649 | 0.13733 | -0.068665 | 0.39825 | 122.4518 | 0.059509 | 122.5067 | 122.4197 | 122.3602 | 122.3236 | 122.2824 | -122.493 | -122.4747 | 122.3557 | 122.4289 | 59.6329 | 59.6375
808.7656 | 122.6761 | -59.7198 | 62.6862 | -0.086899 | -0.0012923 | 0.061171 | 0.096675 | 0.0027343 | -0.0024994 | -0.00096136 | -0.058289 | -0.0026232 | 0.06482 | 0.057631 | -0.016109 | 0.0029095 | -0.0011749 | -0.064087 | 62.6358 | -59.7885 | 62.6953 | -59.5963 | -59.9442 | 0.15564 | -0.10986 | 62.5809 | -59.7702 | 62.7228 | -59.7198 | -59.8206 | -59.6237 | -0.068664 | -0.050354 | 0.009155 | 0.1236 | 59.8755 | -0.2243 | 59.9442 | -0.15564 | -0.050354 | -0.10529 | 0.036621 | 0 | 0.096131 | -0.10071 | 0.14649 | -0.050354 | 0.19226 | 122.4838 | 0.050354 | 122.493 | 122.4243 | 122.3511 | 122.3557 | 122.3007 | -122.4747 | -122.4564 | 122.4152 | 122.4426 | 59.6558 | 59.61
809.7656 | 122.7264 | -59.6786 | 62.7045 | -0.086899 | 0.0016983 | 0.062025 | 0.09518 | 0.0010253 | -0.0018586 | -0.002243 | -0.024719 | -0.00048703 | 0.066529 | 0.063399 | -0.014828 | 0.0029095 | -0.0024567 | -0.022888 | 62.6541 | -59.7702 | 62.7274 | -59.5871 | -59.9579 | 0.022888 | 0 | 62.6266 | -59.7244 | 62.7686 | -59.6878 | -59.7839 | -59.6008 | -0.091553 | -0.050354 | 0.022888 | 0.091553 | 59.7015 | -0.27924 | 59.7931 | -0.18768 | -0.045776 | -0.07782 | 0.064087 | -0.009155 | 0.07782 | -0.10529 | 0.1236 | -0.05951 | 0.18311 | 122.4976 | 0.036621 | 122.493 | 122.4243 | 122.3511 | 122.3328 | 122.3053 | -122.4747 | -122.4289 | 122.406 | 122.4472 | 59.6558 | 59.6786
810.7656 | 122.699 | -59.7198 | 62.6587 | -0.15556 | 0.00020288 | 0.063521 | 0.094325 | 0.00059812 | 0.0002778 | -0.0013886 | -0.067444 | -0.0013416 | 0.065033 | 0.06169 | -0.015255 | 0.00013253 | 0.00074769 | -0.036621 | 62.6175 | -59.7839 | 62.7136 | -59.5596 | -59.9625 | -0.022888 | -0.018311 | 62.6083 | -59.7565 | 62.7594 | -59.7382 | -59.8206 | -59.6146 | -0.064087 | -0.041198 | 0.054932 | 0.16022 | 59.697 | -0.24261 | 59.761 | -0.17853 | -0.036621 | -0.050354 | 0.10071 | -0.01831 | 0.10529 | -0.10071 | 0.14191 | -0.064087 | 0.2243 | 122.4976 | 0.018311 | 122.5159 | 122.4014 | 122.3648 | 122.3373 | 122.3282 | -122.4426 | -122.4152 | 122.4335 | 122.4792 | 59.6832 | 59.7015
811.7656 | 122.7081 | -59.697 | 62.7228 | -0.14793 | 0.0012711 | 0.062025 | 0.094112 | -0.0017517 | 0.0011322 | -0.0033112 | -0.024719 | -0.00070063 | 0.060974 | 0.063826 | -0.0144 | 0.00098693 | 0.0011749 | -0.036621 | 62.6129 | -59.7931 | 62.7182 | -59.5871 | -59.9625 | 0.009155 | -0.013733 | 62.6175 | -59.7565 | 62.7777 | -59.6832 | -59.7931 | -59.5779 | -0.096131 | -0.10986 | -0.004577 | 0.10986 | 59.7061 | -0.2655 | 59.8022 | -0.16937 | -0.05951 | -0.10528 | 0.054932 | 0.013732 | 0.11902 | -0.096131 | 0.17853 | -0.036621 | 0.20599 | 122.5113 | 0.073242 | 122.5342 | 122.406 | 122.374 | 122.3099 | 122.3145 | -122.5159 | -122.4792 | 122.4152 | 122.4747 | 59.6603 | 59.6832
812.7656 | 122.6944 | -59.6741 | 62.6862 | -0.06401 | 0.0031937 | 0.062239 | 0.09283 | 0.0029479 | 6.4004e-05 | 0.0013886 | -0.049133 | 0.00036737 | 0.064179 | 0.059127 | -0.015255 | 0.0018413 | -0.0016021 | -0.054932 | 62.6404 | -59.7794 | 62.709 | -59.5779 | -59.9625 | 0.009155 | -0.013733 | 62.5946 | -59.7382 | 62.7731 | -59.7015 | -59.7977 | -59.5917 | -0.10529 | -0.045776 | 0.022888 | 0.09613 | 59.6832 | -0.28839 | 59.7885 | -0.1831 | -0.064087 | -0.091553 | 0.086975 | -0.027466 | 0.082397 | -0.1236 | 0.14648 | -0.059509 | 0.20142 | 122.4884 | 0.036621 | 122.5113 | 122.4197 | 122.3328 | 122.3145 | 122.2687 | -122.4655 | -122.4243 | 122.3831 | 122.4472 | 59.6191 | 59.6603
813.7656 | 122.6852 | -59.6878 | 62.6724 | -0.094528 | 0.0021255 | 0.060316 | 0.094325 | -0.00089728 | -0.0007904 | -0.002884 | -0.027771 | -0.0013416 | 0.063111 | 0.059554 | -0.013119 | 0.0016277 | -0.0013885 | -0.041199 | 62.6358 | -59.7977 | 62.6953 | -59.5825 | -59.9762 | 0.004578 | -0.004578 | 62.6038 | -59.761 | 62.7548 | -59.697 | -59.7977 | -59.5963 | -0.10986 | -0.036621 | 0.022888 | 0.10528 | 59.6924 | -0.28839 | 59.8022 | -0.17853 | -0.073242 | -0.068664 | 0.082398 | -0.009155 | 0.091553 | -0.10986 | 0.16479 | -0.036621 | 0.21515 | 122.493 | 0.064087 | 122.5159 | 122.4335 | 122.3648 | 122.3236 | 122.2916 | -122.4701 | -122.4335 | 122.3831 | 122.4426 | 59.6466 | 59.6832
814.7656 | 122.699 | -59.6924 | 62.7045 | -0.10979 | 0.00063028 | 0.061598 | 0.095393 | -0.0011109 | -0.0016448 | -0.0035248 | -0.046081 | 0.0020764 | 0.064179 | 0.061476 | -0.015255 | 0.00098693 | -0.0024567 | -0.050354 | 62.6404 | -59.7931 | 62.6999 | -59.5734 | -59.9625 | -0.004578 | -0.009155 | 62.645 | -59.7656 | 62.764 | -59.6924 | -59.8114 | -59.6191 | -0.10071 | -0.064087 | -0.004578 | 0.11902 | 59.6878 | -0.27008 | 59.7885 | -0.16937 | -0.073242 | -0.05951 | 0.059509 | 0 | 0.073242 | -0.11902 | 0.14648 | -0.045776 | 0.21973 | 122.493 | 0.073242 | 122.5296 | 122.4335 | 122.4106 | 122.3328 | 122.3373 | -122.4976 | -122.4701 | 122.3923 | 122.4564 | 59.642 | 59.6832
815.7656 | 122.699 | -59.7107 | 62.7182 | -0.12505 | -0.00043792 | 0.062239 | 0.09518 | -0.0013245 | -0.0005768 | -0.00053396 | -0.021667 | -0.0013416 | 0.063538 | 0.068526 | -0.016323 | 0.0026959 | -0.0037383 | -0.041199 | 62.645 | -59.7839 | 62.7045 | -59.5734 | -59.9808 | 0.018311 | -0.036621 | 62.6175 | -59.7382 | 62.7686 | -59.7061 | -59.816 | -59.6054 | -0.073243 | -0.073243 | -0.013733 | 0.13733 | 59.729 | -0.27008 | 59.8022 | -0.19684 | -0.027466 | -0.10071 | 0.050354 | 0.004577 | 0.10529 | -0.10529 | 0.13275 | -0.07782 | 0.21057 | 122.4884 | 0.032043 | 122.5067 | 122.4289 | 122.3557 | 122.3557 | 122.3282 | -122.5021 | -122.4564 | 122.4152 | 122.4792 | 59.6695 | 59.6741
816.7656 | 122.6669 | -59.7015 | 62.7228 | -0.06401 | 0.00020288 | 0.062666 | 0.093471 | -0.00089728 | -0.0016448 | -0.0018158 | -0.06134 | -0.001128 | 0.066529 | 0.060622 | -0.016964 | 0.0024823 | 0.00032049 | -0.064087 | 62.6404 | -59.7885 | 62.6999 | -59.5871 | -59.9854 | -0.022888 | -0.059509 | 62.6129 | -59.7382 | 62.8143 | -59.5459 | -59.9213 | -59.697 | -0.086975 | -0.082397 | -0.022888 | 0.11444 | 59.6786 | -0.28381 | 59.7656 | -0.19684 | -0.036621 | -0.10986 | 0.091553 | 0.15564 | 0.004578 | -0.21973 | 0.041199 | -0.18311 | 0.20142 | 122.4884 | 0.19226 | 122.5525 | 122.4289 | 122.3511 | 122.3419 | 122.3145 | -122.5113 | -122.4609 | 122.4014 | 122.5159 | 59.6375 | 59.642
817.7656 | 122.6761 | -59.7153 | 62.6678 | -0.11742 | 0.0023391 | 0.061812 | 0.094539 | -0.0034607 | -0.0018586 | -0.0020294 | -0.033874 | -0.0013416 | 0.064392 | 0.062331 | -0.015041 | -0.0024311 | -0.0028839 | -0.054932 | 62.6358 | -59.7885 | 62.6953 | -59.5779 | -59.9854 | 0 | -0.059509 | 62.59 | -59.7382 | 62.8464 | -59.6649 | -59.9258 | -59.6786 | -0.073242 | -0.032044 | 0.027465 | 0.13733 | 59.7153 | -0.27008 | 59.7885 | -0.19684 | -0.022888 | -0.07782 | 0.17853 | 0.050354 | 0.036621 | -0.21057 | 0.059509 | -0.18768 | 0.21057 | 122.4838 | 0.073242 | 122.5845 | 122.4243 | 122.3282 | 122.3511 | 122.3053 | -122.4564 | -122.406 | 122.4106 | 122.5616 | 59.6603 | 59.6558
818.7656 | 122.699 | -59.7198 | 62.7319 | -0.10216 | 0.00041648 | 0.063094 | 0.096461 | 0.0014527 | -0.0031402 | -0.0048066 | -0.021667 | -0.00048703 | 0.063324 | 0.065749 | -0.015896 | -8.1274e-05 | 0.0028839 | -0.050354 | 62.6312 | -59.7794 | 62.7045 | -59.5825 | -59.967 | 0.018311 | 0 | 62.645 | -59.7565 | 62.7777 | -59.6878 | -59.8022 | -59.6054 | -0.059509 | -0.10071 | -0.027466 | 0.13733 | 59.7382 | -0.24719 | 59.7977 | -0.18768 | -0.036621 | -0.086976 | 0.045776 | 0.032044 | 0.11444 | -0.082397 | 0.15106 | -0.045776 | 0.19684 | 122.4838 | 0.068665 | 122.5342 | 122.4106 | 122.4014 | 122.3511 | 122.3648 | -122.5113 | -122.4884 | 122.4243 | 122.4976 | 59.6695 | 59.7198
819.7656 | 122.7356 | -59.6924 | 62.7045 | -0.079269 | 0.00084388 | 0.062025 | 0.093898 | 0.0016663 | -0.0035674 | 0.0018158 | -0.039978 | 0.00015377 | 0.06482 | 0.064894 | -0.017178 | -8.1274e-05 | -0.0016021 | -0.009155 | 62.6541 | -59.7702 | 62.7686 | -59.5322 | -59.9167 | 0.068665 | 0.07782 | 62.6175 | -59.7519 | 62.8006 | -59.642 | -59.7427 | -59.5596 | -0.07782 | -0.050354 | 0.064087 | 0.16022 | 59.761 | -0.2243 | 59.8389 | -0.14648 | -0.059509 | -0.086975 | 0.09613 | 0.050354 | 0.13275 | -0.050354 | 0.19226 | 0.009155 | 0.23804 | 122.5388 | 0.10986 | 122.5525 | 122.4243 | 122.3694 | 122.3465 | 122.3099 | -122.4747 | -122.4564 | 122.4609 | 122.493 | 59.6832 | 59.7702
820.7656 | 122.7081 | -59.6786 | 62.7136 | -0.07164 | -0.0012923 | 0.060957 | 0.096034 | -0.0030335 | -0.0031402 | 0.00010684 | -0.030823 | -0.001128 | 0.063751 | 0.063613 | -0.016323 | 0.0033367 | 0.0011749 | 0.009155 | 62.6541 | -59.7702 | 62.7502 | -59.5322 | -59.9167 | 0.064087 | 0.068665 | 62.6129 | -59.7656 | 62.8052 | -59.642 | -59.7565 | -59.5642 | -0.091553 | -0.059509 | 0.036621 | 0.14648 | 59.7427 | -0.23804 | 59.8343 | -0.14648 | -0.086975 | -0.10071 | 0.091553 | 0.036621 | 0.11444 | -0.07782 | 0.20142 | 0.009155 | 0.23804 | 122.5204 | 0.1236 | 122.5708 | 122.4243 | 122.3785 | 122.3328 | 122.2916 | -122.4838 | -122.4792 | 122.4289 | 122.4838 | 59.6878 | 59.7473
821.7656 | 122.7539 | -59.6649 | 62.7182 | -0.06401 | 0.0014847 | 0.062239 | 0.093471 | -0.0045289 | -0.0007904 | -0.0016022 | -0.039978 | -0.0019824 | 0.066742 | 0.066603 | -0.014614 | 0.0016277 | 0.00032049 | -0.013733 | 62.645 | -59.7519 | 62.7594 | -59.5139 | -59.9213 | 0.059509 | 0.07782 | 62.5946 | -59.7336 | 62.8052 | -59.6283 | -59.7519 | -59.5596 | -0.086975 | -0.073243 | 0.041198 | 0.15106 | 59.7244 | -0.25635 | 59.8114 | -0.16937 | -0.068665 | -0.1236 | 0.086975 | 0.036621 | 0.10529 | -0.086975 | 0.17395 | -0.01831 | 0.23804 | 122.5113 | 0.10529 | 122.5388 | 122.3969 | 122.3282 | 122.3099 | 122.2595 | -122.4701 | -122.4518 | 122.4243 | 122.4701 | 59.6512 | 59.7427
822.7656 | 122.7402 | -59.6832 | 62.7045 | -0.12505 | 0.0010575 | 0.064162 | 0.094539 | -0.00089728 | -0.0016448 | -0.0016022 | -0.024719 | -0.00027343 | 0.06482 | 0.065962 | -0.016537 | -8.1274e-05 | -0.0013885 | 0.013733 | 62.6541 | -59.761 | 62.7502 | -59.523 | -59.9075 | 0.064087 | 0.086975 | 62.6129 | -59.7382 | 62.8143 | -59.6466 | -59.7519 | -59.5505 | -0.077819 | -0.050354 | 0.045776 | 0.16022 | 59.7473 | -0.2243 | 59.8251 | -0.14649 | -0.054931 | -0.091553 | 0.10986 | 0.036622 | 0.13275 | -0.068664 | 0.18768 | -0.013733 | 0.23804 | 122.5113 | 0.091553 | 122.5525 | 122.4152 | 122.3511 | 122.3373 | 122.2961 | -122.4655 | -122.4426 | 122.4335 | 122.4976 | 59.697 | 59.7702
823.7656 | 122.7127 | -59.697 | 62.7365 | -0.094528 | 0.0010575 | 0.063948 | 0.095393 | -0.0030335 | -0.0005768 | -0.001175 | -0.030823 | -0.00027343 | 0.06546 | 0.059127 | -0.015896 | 0.0022687 | 0.00053409 | -0.045776 | 62.6175 | -59.7702 | 62.7228 | -59.5825 | -59.9625 | 0 | -0.022888 | 62.6312 | -59.7427 | 62.7548 | -59.7061 | -59.8068 | -59.5871 | -0.073243 | -0.11902 | -0.013733 | 0.11444 | 59.697 | -0.2655 | 59.7702 | -0.19226 | -0.045777 | -0.10529 | 0.018311 | -0.009156 | 0.10986 | -0.10986 | 0.15564 | -0.064087 | 0.18768 | 122.493 | 0.036621 | 122.4976 | 122.3877 | 122.374 | 122.3145 | 122.3282 | -122.5067 | -122.4792 | 122.4197 | 122.4518 | 59.6512 | 59.6741
824.7656 | 122.7539 | -59.6832 | 62.7228 | -0.094528 | -0.0012923 | 0.062453 | 0.09283 | -0.00068368 | -0.001004 | -0.002884 | -0.015564 | -0.00091423 | 0.064392 | 0.068526 | -0.014187 | 0.0020551 | 0.0033111 | -0.009155 | 62.6404 | -59.7336 | 62.7502 | -59.5413 | -59.9167 | 0.07782 | 0.082397 | 62.6083 | -59.7565 | 62.8098 | -59.6191 | -59.7427 | -59.5551 | -0.050354 | -0.082397 | 0.027466 | 0.14191 | 59.761 | -0.23346 | 59.8114 | -0.18311 | -0.073242 | -0.11444 | 0.086975 | 0.064087 | 0.12817 | -0.059509 | 0.20142 | 0.013733 | 0.19226 | 122.4838 | 0.13733 | 122.5662 | 122.374 | 122.3648 | 122.3236 | 122.2916 | -122.4564 | -122.4792 | 122.4335 | 122.493 | 59.6741 | 59.7656
825.7656 | 122.7356 | -59.6786 | 62.7228 | -0.10216 | 0.00084388 | 0.063094 | 0.093257 | -0.0015381 | -0.0022858 | 0.00053404 | -0.021667 | -0.001128 | 0.063751 | 0.064894 | -0.015041 | -0.00050847 | 0.0020295 | 0.041199 | 62.6541 | -59.7519 | 62.8052 | -59.4543 | -59.8297 | 0.13733 | 0.1236 | 62.645 | -59.6741 | 62.8876 | -59.7244 | -59.7244 | -59.5093 | -0.073242 | -0.068664 | 0.082398 | 0.2243 | 59.816 | -0.15106 | 59.8892 | -0.07782 | 0.004578 | -0.07782 | 0.1648 | -0.045776 | 0.16937 | -0.045776 | 0.1648 | -0.050354 | 0.29755 | 122.5571 | -0.050354 | 122.5616 | 122.406 | 122.319 | 122.3328 | 122.3236 | -122.4747 | -122.3969 | 122.4838 | 122.5662 | 59.7198 | 59.8022
826.7656 | 122.7814 | -59.6786 | 62.7182 | -0.06401 | 0.0021255 | 0.060957 | 0.095393 | -0.00046988 | -0.0031402 | 0.0016022 | -0.015564 | 0.0018628 | 0.063965 | 0.06639 | -0.010769 | 0.0016277 | -0.00032051 | 0.054932 | 62.6541 | -59.7656 | 62.8006 | -59.4635 | -59.848 | 0.11444 | 0.16022 | 62.6266 | -59.697 | 62.7914 | -59.5505 | -59.8022 | -59.5963 | -0.086975 | -0.064087 | 0.082397 | 0.21515 | 59.7931 | -0.16937 | 59.8801 | -0.082397 | -0.01831 | -0.091553 | 0.073242 | 0.12817 | 0.082398 | -0.1236 | 0.10071 | -0.10529 | 0.30212 | 122.5662 | 0.14648 | 122.4884 | 122.4197 | 122.3236 | 122.3328 | 122.3053 | -122.4838 | -122.4152 | 122.4792 | 122.4701 | 59.7336 | 59.8389
827.7656 | 122.6852 | -59.6695 | 62.709 | -0.079269 | -0.00043792 | 0.059889 | 0.092403 | -0.0036743 | 0.0004914 | -0.001175 | -0.015564 | 0.00036737 | 0.063324 | 0.057418 | -0.015682 | 0.0059003 | 0.00053409 | 0.036621 | 62.6541 | -59.761 | 62.8006 | -59.4543 | -59.8526 | 0.13733 | 0.17395 | 62.6312 | -59.7244 | 62.6175 | -59.5917 | -59.6695 | -59.5184 | -0.091552 | -0.054931 | 0.091553 | 0.21515 | 59.8068 | -0.18311 | 59.8984 | -0.091553 | -0.054931 | -0.077819 | -0.091552 | 0.07782 | 0.15106 | 0 | 0.20599 | 0.054931 | 0.3067 | 122.5616 | 0.13275 | 122.3419 | 122.4152 | 122.3557 | 122.3236 | 122.3007 | -122.4701 | -122.4335 | 122.4701 | 122.287 | 59.7061 | 59.8434
828.7656 | 122.7219 | -59.6878 | 62.6907 | -0.041122 | 0.00041648 | 0.06053 | 0.095393 | -0.0019653 | -0.0012176 | -0.0026704 | -0.018616 | 0.00079477 | 0.062897 | 0.059554 | -0.017818 | 0.0029095 | 0.0011749 | 0.041199 | 62.6541 | -59.7702 | 62.7869 | -59.4543 | -59.8618 | 0.10986 | 0.17853 | 62.6312 | -59.7107 | 62.7365 | -59.8755 | -59.6878 | -59.4727 | -0.082398 | -0.036621 | 0.09613 | 0.23346 | 59.7977 | -0.17395 | 59.8801 | -0.091552 | -0.022888 | -0.059509 | 0.045776 | -0.18768 | 0.21515 | 0 | 0.23804 | 0.022888 | 0.31586 | 122.5571 | -0.16479 | 122.4472 | 122.4243 | 122.3419 | 122.3419 | 122.319 | -122.4609 | -122.4014 | 122.4747 | 122.4243 | 59.729 | 59.8663
829.7656 | 122.6944 | -59.6832 | 62.7136 | -0.06401 | 0.00041648 | 0.062025 | 0.095607 | 0.00038452 | -0.0016448 | -0.0016022 | -0.015564 | -0.0030506 | 0.064392 | 0.056777 | -0.015896 | 0.0048321 | -0.00032051 | 0.041199 | 62.6358 | -59.7565 | 62.7823 | -59.4406 | -59.8618 | 0.11902 | 0.16022 | 62.6221 | -59.7107 | 62.6495 | -59.697 | -59.6649 | -59.4955 | -0.073242 | -0.07782 | 0.068665 | 0.24262 | 59.8022 | -0.17853 | 59.8755 | -0.10529 | -0.027465 | -0.091553 | -0.064087 | -0.013732 | 0.18768 | 0.018311 | 0.21515 | 0.045776 | 0.31586 | 122.5388 | 0.013733 | 122.3602 | 122.3923 | 122.3328 | 122.319 | 122.3053 | -122.4701 | -122.4243 | 122.4655 | 122.3328 | 59.7244 | 59.8434
830.7656 | 122.6303 | -59.7061 | 62.7869 | -0.10216 | 0.00084388 | 0.061812 | 0.095393 | -0.00068368 | -0.0016448 | -0.001175 | -0.039978 | -0.0017688 | 0.066742 | 0.064894 | -0.015469 | 0.0022687 | 0.00032049 | 0.050354 | 62.6404 | -59.761 | 62.7457 | -59.523 | -59.9167 | 0.09613 | 0.091553 | 62.6587 | -59.7244 | 62.7365 | -59.7336 | -59.8434 | -59.642 | -0.054931 | -0.14648 | -0.041198 | 0.18311 | 59.8022 | -0.21057 | 59.8572 | -0.15564 | -0.01831 | -0.12817 | -0.050354 | -0.027466 | 0.064087 | -0.13733 | 0.082397 | -0.11902 | 0.23804 | 122.5067 | -0.009156 | 122.4609 | 122.4014 | 122.3831 | 122.3465 | 122.3648 | -122.5479 | -122.5113 | 122.4518 | 122.4426 | 59.7565 | 59.7977
831.7656 | 122.7173 | -59.6695 | 62.6907 | -0.056381 | -0.00043792 | 0.061598 | 0.094752 | 0.00017092 | -0.0033538 | -0.0026704 | -0.027771 | 0.00036737 | 0.062042 | 0.062331 | -0.01675 | 0.0041913 | -0.00053411 | 0.045776 | 62.645 | -59.7519 | 62.7914 | -59.4543 | -59.8526 | 0.14191 | 0.17395 | 62.6221 | -59.7198 | 62.6312 | -59.5596 | -59.6649 | -59.5184 | -0.082397 | -0.045777 | 0.10071 | 0.21515 | 59.8114 | -0.18311 | 59.8938 | -0.10071 | -0.050354 | -0.068665 | -0.059509 | 0.10986 | 0.15106 | 0.004578 | 0.20142 | 0.054932 | 0.29755 | 122.5433 | 0.16022 | 122.3511 | 122.3969 | 122.3419 | 122.3145 | 122.2916 | -122.4426 | -122.4106 | 122.4609 | 122.3007 | 59.7153 | 59.8434
832.7656 | 122.7127 | -59.6878 | 62.7228 | -0.079269 | 0.0019119 | 0.060744 | 0.098384 | 0.00038452 | -0.0003632 | -0.0033112 | -0.0033568 | -0.00070063 | 0.064179 | 0.059981 | -0.014828 | 0.0037641 | -0.0022431 | 0.050354 | 62.6587 | -59.7565 | 62.8052 | -59.4681 | -59.8572 | 0.13275 | 0.16022 | 62.6266 | -59.7107 | 62.677 | -59.5184 | -59.7473 | -59.5917 | -0.068665 | -0.064087 | 0.082398 | 0.21973 | 59.8206 | -0.16937 | 59.8892 | -0.10071 | -0.022888 | -0.09613 | -0.045776 | 0.16937 | 0.09613 | -0.059509 | 0.11902 | -0.036621 | 0.28839 | 122.5616 | 0.19226 | 122.3877 | 122.4152 | 122.3373 | 122.3465 | 122.3145 | -122.4792 | -122.4335 | 122.493 | 122.3648 | 59.7382 | 59.848
833.7656 | 122.731 | -59.6695 | 62.7502 | -0.07164 | 0.00084388 | 0.063094 | 0.095821 | -0.00025628 | -0.004422 | -0.0037384 | -0.027771 | -0.001128 | 0.062256 | 0.068099 | -0.014828 | 0.0018413 | -0.0033111 | 0.059509 | 62.6724 | -59.7473 | 62.7823 | -59.4818 | -59.8755 | 0.11902 | 0.13275 | 62.6495 | -59.7153 | 62.8006 | -59.6329 | -59.7336 | -59.5688 | -0.077819 | -0.07782 | 0.032044 | 0.18768 | 59.7885 | -0.20599 | 59.8663 | -0.12817 | -0.045776 | -0.10071 | 0.050354 | 0.036621 | 0.10071 | -0.064087 | 0.14648 | -0.018311 | 0.2655 | 122.5296 | 0.082397 | 122.5159 | 122.4197 | 122.3648 | 122.3419 | 122.319 | -122.4976 | -122.4655 | 122.4518 | 122.4701 | 59.729 | 59.8022
834.7656 | 122.7219 | -59.6832 | 62.7365 | -0.086899 | 0.0023391 | 0.060316 | 0.094539 | 0.0027343 | -0.0022858 | -0.001175 | -0.021667 | 0.001222 | 0.065674 | 0.059981 | -0.014828 | 0.0016277 | -0.0026703 | 0.064087 | 62.6633 | -59.7519 | 62.8006 | -59.4864 | -59.8709 | 0.1236 | 0.14191 | 62.6266 | -59.7336 | 62.7914 | -59.6375 | -59.7427 | -59.5551 | -0.068664 | -0.073242 | 0.064087 | 0.19684 | 59.8068 | -0.18768 | 59.8755 | -0.11902 | -0.050354 | -0.10986 | 0.054932 | 0.045777 | 0.12817 | -0.059509 | 0.17853 | -0.009155 | 0.2655 | 122.5525 | 0.096131 | 122.525 | 122.4152 | 122.3602 | 122.3465 | 122.3099 | -122.4884 | -122.4701 | 122.4838 | 122.4747 | 59.7473 | 59.8251
835.7656 | 122.6349 | -59.7382 | 62.7274 | -0.12505 | 0.0012711 | 0.06288 | 0.09753 | 0.0012391 | -0.0020722 | -0.0016022 | -0.14984 | 0.001222 | 0.06482 | 0.070876 | -0.015469 | 0.0018413 | 0.0016021 | -0.073242 | 62.6541 | -59.816 | 62.6083 | -59.6878 | -60.0677 | -0.11444 | -0.14648 | 62.6358 | -59.7931 | 62.6999 | -59.8251 | -59.935 | -59.697 | -0.07782 | -0.073242 | -0.11902 | 0.050354 | 59.6237 | -0.32959 | 59.7015 | -0.25177 | -0.054932 | -0.091553 | -0.027466 | -0.086975 | 0.041199 | -0.19684 | 0.096131 | -0.14191 | 0.12817 | 122.4243 | -0.032043 | 122.493 | 122.4701 | 122.4289 | 122.3923 | 122.374 | -122.5433 | -122.5204 | 122.3465 | 122.438 | 59.6649 | 59.5917
836.7656 | 122.7127 | -59.6832 | 62.7274 | -0.094528 | 0.0016983 | 0.061385 | 0.094539 | -0.00046988 | -0.0022858 | -0.002243 | -0.0094604 | -0.00070063 | 0.061829 | 0.062331 | -0.015255 | 0.00013253 | -0.00074771 | 0.059509 | 62.6495 | -59.761 | 62.7777 | -59.5001 | -59.8892 | 0.10529 | 0.10986 | 62.6678 | -59.7153 | 62.796 | -59.6512 | -59.761 | -59.5825 | -0.077819 | -0.07782 | 0.050354 | 0.18311 | 59.7885 | -0.20599 | 59.8663 | -0.12817 | -0.032043 | -0.059509 | 0.068665 | 0.032044 | 0.10071 | -0.077819 | 0.13275 | -0.045776 | 0.26093 | 122.5388 | 0.064087 | 122.5113 | 122.4106 | 122.3831 | 122.3328 | 122.3511 | -122.4884 | -122.4426 | 122.4609 | 122.4792 | 59.7427 | 59.7931
837.7656 | 122.731 | -59.6786 | 62.7182 | -0.056381 | 0.0025529 | 0.061812 | 0.092616 | -0.0032471 | -0.0016448 | -0.00053396 | -0.036926 | -0.00048703 | 0.06546 | 0.060836 | -0.015041 | 0.0033367 | 0.00032049 | 0.059509 | 62.6724 | -59.7427 | 62.5534 | -59.6512 | -59.7565 | 0.10529 | 0.1831 | 62.5946 | -59.7198 | 62.8006 | -59.5963 | -59.7153 | -59.5459 | -0.064087 | -0.045777 | -0.16479 | 0.027466 | 59.7839 | -0.07782 | 59.848 | -0.013733 | -0.041199 | -0.1236 | 0.082397 | 0.082398 | 0.13275 | -0.036621 | 0.17395 | 0.004578 | 0.091553 | 122.2961 | 0.1236 | 122.5204 | 122.4152 | 122.3145 | 122.3511 | 122.2733 | -122.4609 | -122.4381 | 122.2321 | 122.4792 | 59.7382 | 59.8618
838.7656 | 122.7081 | -59.6695 | 62.7365 | -0.041122 | -0.00022432 | 0.061385 | 0.09518 | -0.0021789 | -0.0014312 | -0.002884 | -0.018616 | -0.00070063 | 0.064392 | 0.058058 | -0.014828 | 0.00013253 | 0.0043793 | 0.050354 | 62.6587 | -59.7244 | 62.7594 | -59.4818 | -59.8755 | 0.10986 | 0.15106 | 62.6312 | -59.7427 | 62.7731 | -59.6466 | -59.7656 | -59.5734 | -0.054931 | -0.07782 | 0.022888 | 0.18768 | 59.7794 | -0.20599 | 59.8343 | -0.15106 | -0.073242 | -0.10529 | 0.036621 | 0.022889 | 0.096131 | -0.09613 | 0.16937 | -0.022888 | 0.24261 | 122.4838 | 0.096131 | 122.5159 | 122.3831 | 122.374 | 122.3282 | 122.3007 | -122.4609 | -122.4792 | 122.4289 | 122.4426 | 59.7198 | 59.8206
839.7656 | 122.6898 | -59.6695 | 62.8418 | -0.079269 | -0.00086512 | 0.062239 | 0.095607 | -0.0028199 | -0.0024994 | 0.00053404 | -0.033874 | 0.0018628 | 0.066315 | 0.070876 | -0.015255 | 0.00055973 | -0.0033111 | 0.036621 | 62.6953 | -59.761 | 62.6862 | -59.5917 | -59.935 | 0.064087 | 0.036621 | 62.6633 | -59.7382 | 62.7182 | -59.7519 | -59.8709 | -59.642 | -0.091552 | -0.14648 | -0.15564 | 0.07782 | 59.7336 | -0.2655 | 59.8251 | -0.17395 | -0.068664 | -0.17853 | -0.1236 | -0.082397 | 0.027466 | -0.20142 | 0.09613 | -0.13275 | 0.16937 | 122.4472 | -0.013733 | 122.4564 | 122.4564 | 122.4014 | 122.3648 | 122.3328 | -122.6028 | -122.58 | 122.3557 | 122.3877 | 59.7061 | 59.7061
840.7656 | 122.6212 | -59.7382 | 62.7502 | -0.079269 | -1.0718e-05 | 0.061812 | 0.097743 | 0.0016663 | -0.001004 | -0.00010676 | -0.09491 | 0.00079477 | 0.065888 | 0.062117 | -0.015469 | 0.0016277 | -0.0013885 | -0.091553 | 62.645 | -59.8343 | 62.4985 | -60.0815 | -60.0586 | 0.14191 | -0.18768 | 62.6678 | -59.7794 | 62.6907 | -59.8389 | -59.9442 | -59.7061 | -0.096131 | -0.10529 | -0.25177 | -0.34332 | 59.8801 | -0.32043 | 59.9762 | -0.2243 | -0.041199 | -0.082397 | -0.059509 | -0.10071 | 0.032043 | -0.20599 | 0.073242 | -0.16479 | -0.24719 | 122.3328 | -0.059509 | 122.4701 | 122.4792 | 122.4472 | 122.3831 | 122.406 | -122.5845 | -122.5296 | 122.2366 | 122.4289 | 59.6466 | 59.5505
841.7656 | 122.5983 | -59.7107 | 62.764 | -0.018234 | 0.0025529 | 0.061812 | 0.094539 | 0.00038452 | -0.0005768 | -0.0020294 | -0.027771 | 0.0010084 | 0.065033 | 0.058058 | -0.015255 | 0.0026959 | 0.00010689 | 0.009155 | 62.677 | -59.761 | 62.6678 | -59.6283 | -59.9625 | 0.045776 | 0.027466 | 62.6862 | -59.7519 | 62.7869 | -59.6008 | -60.0677 | -59.8709 | -0.050354 | -0.086975 | -0.09613 | 0.082397 | 59.7565 | -0.25177 | 59.8068 | -0.20142 | -0.041199 | -0.07782 | 0.022888 | 0.10986 | -0.16022 | -0.35706 | -0.11902 | -0.31586 | 0.13275 | 122.4289 | 0.15106 | 122.5388 | 122.438 | 122.438 | 122.3877 | 122.3969 | -122.525 | -122.5159 | 122.3785 | 122.4976 | 59.7198 | 59.7382
842.7656 | 122.6028 | -59.7336 | 62.7457 | -0.018234 | -0.00022432 | 0.059889 | 0.09518 | -0.0023925 | -0.002713 | -0.002243 | -0.021667 | 0.0020764 | 0.063538 | 0.05464 | -0.014614 | 0.0029095 | -0.0016021 | 0.004578 | 62.6999 | -59.7702 | 62.6724 | -59.5871 | -59.9716 | 0.041199 | 0.022888 | 62.6862 | -59.7382 | 62.6129 | -59.8297 | -59.7977 | -59.5917 | -0.036621 | -0.045777 | -0.073243 | 0.14648 | 59.7748 | -0.23804 | 59.8114 | -0.20142 | -0.004577 | -0.05951 | -0.13275 | -0.09613 | 0.14191 | -0.064086 | 0.14648 | -0.059509 | 0.18311 | 122.4426 | -0.091553 | 122.3511 | 122.4701 | 122.4243 | 122.4335 | 122.4197 | -122.5159 | -122.4838 | 122.406 | 122.3465 | 59.7382 | 59.7565
843.7656 | 122.6212 | -59.7107 | 62.7594 | -0.010605 | 0.00020288 | 0.061171 | 0.09518 | -0.0036743 | -0.0035674 | -0.0018158 | -0.039978 | 0.00058097 | 0.064392 | 0.062972 | -0.016109 | 0.0018413 | -0.0013885 | -0.013733 | 62.7182 | -59.7885 | 62.6633 | -59.6191 | -59.9945 | 0.032043 | 0.013733 | 62.6953 | -59.761 | 62.7136 | -59.7427 | -59.8755 | -59.6603 | -0.07782 | -0.041198 | -0.09613 | 0.091552 | 59.7427 | -0.28381 | 59.8206 | -0.20599 | -0.050354 | -0.064087 | -0.045776 | -0.032044 | 0.050354 | -0.16479 | 0.10071 | -0.11444 | 0.16937 | 122.4518 | 0.01831 | 122.4747 | 122.5067 | 122.4564 | 122.4289 | 122.406 | -122.5479 | -122.5204 | 122.374 | 122.4243 | 59.697 | 59.7244
844.7656 | 122.6761 | -59.697 | 62.7686 | -0.06401 | 0.0036209 | 0.062025 | 0.095607 | -0.00025628 | -0.0014312 | -0.00032036 | 0.0088502 | 0.00079477 | 0.064179 | 0.053786 | -0.0144 | 0.0026959 | -0.0033111 | 0.064087 | 62.6633 | -59.7473 | 62.7502 | -59.5047 | -59.8984 | 0.10071 | 0.09613 | 62.6404 | -59.7198 | 62.7548 | -59.6786 | -59.8022 | -59.6054 | -0.050354 | -0.10529 | -0.018311 | 0.19226 | 59.7977 | -0.20142 | 59.848 | -0.15106 | -0.022889 | -0.12817 | -0.013733 | 0.01831 | 0.091552 | -0.10529 | 0.11444 | -0.082397 | 0.24261 | 122.4976 | 0.041199 | 122.4747 | 122.4106 | 122.3602 | 122.3602 | 122.3373 | -122.5159 | -122.4884 | 122.4472 | 122.4518 | 59.761 | 59.7931
845.7656 | 122.6166 | -59.7427 | 62.7319 | -0.10979 | 0.0012711 | 0.063094 | 0.095607 | -0.00046988 | -0.0003632 | -0.00053396 | -0.085754 | 0.0027174 | 0.065247 | 0.063185 | -0.012905 | 0.0016277 | 0.0024567 | 0.004578 | 62.6816 | -59.8709 | 62.5534 | -59.6375 | -59.9808 | -0.10986 | -0.11902 | 62.6266 | -59.7794 | 62.677 | -59.7885 | -59.9258 | -59.6832 | -0.12817 | -0.050354 | -0.17853 | 0.10529 | 59.6329 | -0.23804 | 59.761 | -0.10986 | -0.036621 | -0.10529 | -0.054932 | -0.045776 | 0.059509 | -0.18311 | 0.09613 | -0.14648 | 0.23346 | 122.4243 | -0.009155 | 122.4564 | 122.5525 | 122.406 | 122.4243 | 122.3694 | -122.6028 | -122.5113 | 122.2961 | 122.4197 | 59.7473 | 59.6237
846.7656 | 122.6074 | -59.697 | 62.7686 | -0.048752 | 0.0010575 | 0.060744 | 0.096461 | 0.0023071 | -0.0024994 | 0.00032044 | -0.04303 | 0.00229 | 0.066742 | 0.062545 | -0.01675 | 0.0014141 | -0.00096131 | 0.004578 | 62.7319 | -59.761 | 62.6816 | -59.6146 | -59.9854 | 0.036621 | 0 | 62.6816 | -59.729 | 62.709 | -59.7473 | -59.8663 | -59.6466 | -0.064087 | -0.036621 | -0.086975 | 0.082397 | 59.7336 | -0.28839 | 59.7977 | -0.22431 | -0.032044 | -0.086975 | -0.05951 | -0.050354 | 0.050354 | -0.16937 | 0.082398 | -0.13733 | 0.14648 | 122.4426 | -0.01831 | 122.438 | 122.493 | 122.4106 | 122.4289 | 122.3785 | -122.5296 | -122.4976 | 122.3785 | 122.406 | 59.7015 | 59.697
847.7656 | 122.5891 | -59.6832 | 62.7731 | 0.019913 | 0.0014847 | 0.06053 | 0.09518 | 0.0010253 | -0.0005768 | 0.00074764 | -0.027771 | 0.0016492 | 0.066315 | 0.05934 | -0.013973 | 0.0033367 | 0.00096129 | -0.004578 | 62.7228 | -59.761 | 62.6678 | -59.6146 | -59.9854 | 0.032043 | -0.009155 | 62.6953 | -59.7336 | 62.709 | -59.7473 | -59.8755 | -59.6466 | -0.077819 | -0.050354 | -0.10528 | 0.068665 | 59.7153 | -0.30212 | 59.7931 | -0.22431 | -0.050354 | -0.07782 | -0.064087 | -0.064086 | 0.036622 | -0.19226 | 0.086976 | -0.14191 | 0.14648 | 122.4289 | -0.013732 | 122.4426 | 122.4838 | 122.4289 | 122.406 | 122.3785 | -122.5342 | -122.5067 | 122.3511 | 122.3923 | 59.6786 | 59.6741
848.7656 | 122.5983 | -59.6924 | 62.7869 | -0.086899 | -0.00065152 | 0.061385 | 0.097102 | 0.0038025 | -0.0033538 | -0.0030976 | -0.030823 | 0.00079477 | 0.065674 | 0.062758 | -0.0144 | 0.0020551 | -0.00053411 | -0.004578 | 62.7182 | -59.7931 | 62.6495 | -59.6237 | -59.9945 | 0.027466 | 0.004578 | 62.6724 | -59.7565 | 62.7045 | -59.7519 | -59.8709 | -59.6558 | -0.10071 | -0.068664 | -0.13733 | 0.068665 | 59.7198 | -0.30212 | 59.8206 | -0.20142 | -0.064087 | -0.11444 | -0.082397 | -0.059509 | 0.036621 | -0.17853 | 0.10071 | -0.11444 | 0.16937 | 122.4426 | 0.004578 | 122.4609 | 122.5113 | 122.4289 | 122.4106 | 122.3648 | -122.58 | -122.5433 | 122.3419 | 122.3969 | 59.6878 | 59.697
849.7656 | 122.6212 | -59.6924 | 62.764 | -0.056381 | 0.0012711 | 0.061385 | 0.094539 | 0.0031617 | -0.0018586 | -0.0033112 | -0.039978 | 0.0014356 | 0.063751 | 0.06169 | -0.0144 | 0.0037641 | -0.00074771 | 0.004578 | 62.7365 | -59.8022 | 62.6587 | -59.6191 | -59.9991 | 0.018311 | 0.004578 | 62.6724 | -59.7565 | 62.7136 | -59.7427 | -59.8618 | -59.6603 | -0.10986 | -0.027466 | -0.10529 | 0.073242 | 59.7107 | -0.3067 | 59.8206 | -0.19684 | -0.064087 | -0.091553 | -0.050354 | -0.050354 | 0.032044 | -0.16937 | 0.096131 | -0.10529 | 0.1831 | 122.4609 | 0.013733 | 122.4701 | 122.5388 | 122.4289 | 122.4289 | 122.3648 | -122.5662 | -122.5204 | 122.3511 | 122.406 | 59.697 | 59.697
850.7656 | 122.7448 | -59.729 | 62.6953 | -0.12505 | -1.0718e-05 | 0.063521 | 0.096461 | 0.00081172 | -0.0024994 | -0.0018158 | -0.055237 | 0.0010084 | 0.065247 | 0.058058 | -0.015469 | 0.0031231 | -0.00053411 | -0.054932 | 62.6358 | -59.7931 | 62.6862 | -59.5779 | -59.9487 | -0.050354 | -0.013733 | 62.5763 | -59.7565 | 62.7777 | -59.6878 | -59.8114 | -59.5734 | -0.064087 | -0.059509 | -0.009155 | 0.15106 | 59.6787 | -0.21973 | 59.7427 | -0.15564 | -0.027466 | -0.11902 | 0.082398 | 0.041199 | 0.15564 | -0.082397 | 0.18311 | -0.054931 | 0.21515 | 122.4792 | 0.068665 | 122.5342 | 122.4289 | 122.3328 | 122.3648 | 122.3053 | -122.4884 | -122.4518 | 122.4152 | 122.5067 | 59.6741 | 59.7153
851.7656 | 122.5983 | -59.7153 | 62.764 | -0.018234 | -0.00065152 | 0.061385 | 0.093898 | 0.0031617 | -0.0050628 | -0.002884 | -0.04303 | -0.00070063 | 0.065674 | 0.054213 | -0.013546 | 0.0035503 | -0.00053411 | -0.027466 | 62.6999 | -59.7839 | 62.6541 | -59.6191 | -59.9762 | 0.027466 | 0.018311 | 62.645 | -59.7427 | 62.7182 | -59.7473 | -59.8526 | -59.6466 | -0.068665 | -0.064087 | -0.10986 | 0.09613 | 59.7427 | -0.26093 | 59.8114 | -0.19226 | -0.027466 | -0.11902 | -0.045776 | -0.032043 | 0.068665 | -0.13733 | 0.096131 | -0.10986 | 0.16479 | 122.4381 | -0.004577 | 122.4609 | 122.4838 | 122.3877 | 122.4152 | 122.3602 | -122.5479 | -122.5067 | 122.3694 | 122.4335 | 59.6878 | 59.7336
852.7656 | 122.6349 | -59.7107 | 62.7594 | -0.025863 | -0.00086512 | 0.061812 | 0.097316 | 0.00059812 | -0.0035674 | 0.00053404 | -0.018616 | 0.0020764 | 0.06482 | 0.059127 | -0.015896 | 0.0020551 | 0.0016021 | 0.004578 | 62.6999 | -59.7748 | 62.6633 | -59.6191 | -59.9899 | 0.032043 | 0.018311 | 62.6633 | -59.7427 | 62.709 | -59.7519 | -59.8618 | -59.6466 | -0.064087 | -0.059509 | -0.09613 | 0.091552 | 59.7427 | -0.27924 | 59.8068 | -0.21515 | -0.032044 | -0.09613 | -0.050354 | -0.041199 | 0.064087 | -0.15106 | 0.096131 | -0.11902 | 0.15564 | 122.438 | -0.009155 | 122.4518 | 122.4747 | 122.406 | 122.4106 | 122.374 | -122.5342 | -122.5021 | 122.374 | 122.4197 | 59.7153 | 59.729
853.7656 | 122.6761 | -59.7015 | 62.7457 | -0.10216 | 0.0014847 | 0.061598 | 0.093043 | 0.0038025 | -0.0014312 | -0.00096136 | -0.1712 | -0.00048703 | 0.064606 | 0.061049 | -0.018032 | 0.0037641 | -0.0013885 | 0.009155 | 62.6816 | -59.7885 | 62.6999 | -59.5734 | -59.967 | 0.009155 | 0.14648 | 62.6633 | -59.7565 | 62.7548 | -59.697 | -59.8434 | -59.6146 | -0.086975 | -0.064087 | -0.045777 | 0.12817 | 59.7107 | -0.2655 | 59.7977 | -0.17853 | -0.054932 | -0.082398 | 0.009155 | 0.004578 | 0.086975 | -0.14191 | 0.14191 | -0.086975 | 0.21515 | 122.4884 | 0.05951 | 122.5113 | 122.4701 | 122.4197 | 122.3831 | 122.3648 | -122.5342 | -122.5021 | 122.4014 | 122.4564 | 59.7107 | 59.848
854.7656 | 122.6715 | -59.697 | 62.7686 | -0.056381 | 0.0010575 | 0.063307 | 0.096034 | 0.0038025 | -0.0022858 | -0.0018158 | -0.030823 | 0.00036737 | 0.064392 | 0.060622 | -0.014828 | 0.0014141 | 0.0026703 | 0 | 62.7228 | -59.7702 | 62.6953 | -59.6008 | -59.967 | 0.027466 | 0.032043 | 62.6541 | -59.7748 | 62.7274 | -59.7107 | -59.8343 | -59.6054 | -0.073243 | -0.045777 | -0.073243 | 0.09613 | 59.7244 | -0.27008 | 59.7977 | -0.19684 | -0.07782 | -0.11444 | -0.041199 | -0.013733 | 0.091552 | -0.13733 | 0.16937 | -0.05951 | 0.16937 | 122.4655 | 0.064087 | 122.5021 | 122.493 | 122.4289 | 122.4197 | 122.3511 | -122.5388 | -122.5433 | 122.3923 | 122.4243 | 59.697 | 59.729
855.7656 | 122.6852 | -59.7198 | 62.7594 | -0.048752 | 0.00020288 | 0.061385 | 0.098384 | 0.0014527 | 0.000705 | 0.001175 | -0.036926 | 0.00015377 | 0.063324 | 0.05934 | -0.016964 | 0.0033367 | -0.0048065 | -0.009155 | 62.7045 | -59.8068 | 62.677 | -59.61 | -59.9625 | 0.027466 | 0.036621 | 62.6633 | -59.7656 | 62.7228 | -59.7198 | -59.8663 | -59.6237 | -0.086975 | -0.054931 | -0.082397 | 0.10986 | 59.7473 | -0.24261 | 59.8343 | -0.15564 | -0.045776 | -0.09613 | -0.036621 | 0 | 0.096131 | -0.14648 | 0.14191 | -0.10071 | 0.19684 | 122.4838 | 0.045776 | 122.4884 | 122.5113 | 122.4289 | 122.4243 | 122.3831 | -122.5662 | -122.525 | 122.3969 | 122.4426 | 59.7107 | 59.7565
856.7656 | 122.6532 | -59.7153 | 62.7502 | -0.056381 | 0.00084388 | 0.060103 | 0.095821 | 0.00017092 | 0.0009186 | -0.0020294 | -0.0064086 | -5.9826e-05 | 0.062897 | 0.058272 | -0.016323 | 0.00098693 | -0.00053411 | 0.009155 | 62.7228 | -59.7839 | 62.6678 | -59.61 | -59.9533 | 0.036621 | 0.027466 | 62.677 | -59.7519 | 62.7319 | -59.7198 | -59.8389 | -59.6054 | -0.068665 | -0.027466 | -0.082397 | 0.10529 | 59.7519 | -0.23804 | 59.8206 | -0.16937 | -0.036621 | -0.073242 | -0.01831 | -0.004578 | 0.10986 | -0.1236 | 0.14648 | -0.086975 | 0.17395 | 122.4518 | 0.032043 | 122.4838 | 122.5067 | 122.4289 | 122.438 | 122.3923 | -122.5342 | -122.5021 | 122.3831 | 122.4472 | 59.7244 | 59.7427
857.7656 | 122.6166 | -59.7061 | 62.8006 | -0.086899 | -1.0718e-05 | 0.061385 | 0.096248 | 0.0014527 | 0.0004914 | -0.0013886 | -0.0033568 | -0.00070063 | 0.065247 | 0.063185 | -0.014614 | -0.00093567 | -0.00032051 | -0.004578 | 62.7274 | -59.7794 | 62.6495 | -59.6191 | -59.9762 | 0.041199 | 0.004578 | 62.6633 | -59.7565 | 62.7045 | -59.7656 | -59.8526 | -59.6512 | -0.073242 | -0.073242 | -0.15106 | 0.086975 | 59.7473 | -0.27008 | 59.8206 | -0.19684 | -0.050354 | -0.13733 | -0.09613 | -0.059509 | 0.054932 | -0.14648 | 0.10529 | -0.09613 | 0.16022 | 122.4289 | -0.009155 | 122.4609 | 122.5067 | 122.4197 | 122.4335 | 122.3694 | -122.58 | -122.5571 | 122.3557 | 122.4106 | 59.7015 | 59.7107
858.7656 | 122.5983 | -59.7198 | 62.7869 | -0.10216 | -0.00065152 | 0.059676 | 0.093257 | 0.00059812 | -0.0033538 | -0.00032036 | -0.0094604 | 0.001222 | 0.06482 | 0.058272 | -0.015041 | 0.00077333 | 0.0016021 | 0.004578 | 62.7274 | -59.7794 | 62.6358 | -59.6329 | -59.9808 | 0.036621 | 0.018311 | 62.6907 | -59.7473 | 62.709 | -59.7382 | -59.8526 | -59.6329 | -0.059509 | -0.059509 | -0.15106 | 0.086975 | 59.7565 | -0.26092 | 59.816 | -0.20142 | -0.027465 | -0.09613 | -0.07782 | -0.01831 | 0.086975 | -0.13275 | 0.11444 | -0.10529 | 0.14648 | 122.4152 | 0.009155 | 122.4564 | 122.5067 | 122.438 | 122.4472 | 122.4106 | -122.5662 | -122.5342 | 122.3557 | 122.4289 | 59.7244 | 59.7382
859.7656 | 122.6532 | -59.7015 | 62.7686 | -0.079269 | 0.00084388 | 0.061385 | 0.097743 | -0.00025628 | -0.0029266 | -0.00053396 | -0.027771 | -0.00048703 | 0.065674 | 0.064253 | -0.017178 | 0.0031231 | -0.0026703 | 0.018311 | 62.7365 | -59.7656 | 62.6816 | -59.61 | -59.9625 | 0.036621 | 0.032043 | 62.6678 | -59.7473 | 62.7136 | -59.7198 | -59.8434 | -59.6146 | -0.064087 | -0.032044 | -0.086975 | 0.091553 | 59.7382 | -0.26093 | 59.8022 | -0.19684 | -0.045776 | -0.10071 | -0.054932 | -0.018311 | 0.086975 | -0.14191 | 0.13275 | -0.096131 | 0.15564 | 122.4472 | 0.027465 | 122.4609 | 122.5021 | 122.4152 | 122.438 | 122.3694 | -122.5342 | -122.5159 | 122.3831 | 122.4152 | 59.7198 | 59.7336
860.7656 | 122.6486 | -59.7015 | 62.7319 | -0.048752 | 0.0012711 | 0.061812 | 0.096889 | 0.0025207 | -0.001004 | -0.004593 | -0.021667 | -0.0015552 | 0.065033 | 0.05934 | -0.016323 | 0.0035503 | -0.0020295 | 0.027466 | 62.6953 | -59.7885 | 62.709 | -59.5734 | -60.022 | -0.15564 | 0.086975 | 62.6587 | -59.7382 | 62.7502 | -59.7336 | -59.8297 | -59.6008 | -0.086975 | -0.036622 | -0.022889 | 0.12817 | 59.5459 | -0.32044 | 59.6329 | -0.23346 | -0.036621 | -0.073243 | 0.01831 | -0.032044 | 0.10071 | -0.12817 | 0.13733 | -0.091553 | 0.21515 | 122.4976 | 0.004577 | 122.4884 | 122.4838 | 122.3969 | 122.3969 | 122.3602 | -122.5204 | -122.4701 | 122.4106 | 122.4518 | 59.729 | 59.7885
861.7656 | 122.6166 | -59.7198 | 62.7182 | -0.056381 | -1.0718e-05 | 0.062239 | 0.098384 | -0.00046988 | -0.0016448 | 0.00032044 | -0.058289 | 0.00015377 | 0.064392 | 0.063613 | -0.015041 | 0.0035503 | 0.0052337 | -0.009155 | 62.6907 | -59.7931 | 62.6724 | -59.6008 | -59.9945 | -0.027466 | 0.004578 | 62.6633 | -59.7198 | 62.7274 | -59.7565 | -59.8938 | -59.642 | -0.073242 | -0.027466 | -0.045777 | 0.11902 | 59.6924 | -0.27466 | 59.7656 | -0.20142 | 0 | -0.054932 | 0.009155 | -0.036621 | 0.07782 | -0.17395 | 0.07782 | -0.17395 | 0.19226 | 122.4655 | -0.036621 | 122.4472 | 122.4838 | 122.3831 | 122.4106 | 122.3831 | -122.5113 | -122.4381 | 122.3923 | 122.4472 | 59.7107 | 59.7244
862.7656 | 122.6715 | -59.7061 | 62.7457 | -0.033493 | 0.0012711 | 0.063307 | 0.096248 | 0.0025207 | -0.0033538 | -0.00096136 | -0.015564 | -0.00091423 | 0.06482 | 0.064467 | -0.01376 | 0.0020551 | 0.0039521 | 0.022888 | 62.6953 | -59.7702 | 62.5397 | -59.5322 | -59.8526 | 0.041199 | 0.059509 | 62.6587 | -59.761 | 62.7319 | -59.7198 | -59.848 | -59.6191 | -0.064087 | -0.050355 | -0.20599 | 0.17395 | 59.7473 | -0.14648 | 59.8114 | -0.082397 | -0.054931 | -0.086976 | -0.013733 | -0.013733 | 0.086975 | -0.14191 | 0.14191 | -0.086975 | 0.23804 | 122.3099 | 0.041198 | 122.493 | 122.4655 | 122.4197 | 122.4014 | 122.3648 | -122.5159 | -122.5067 | 122.2458 | 122.4381 | 59.729 | 59.7656
863.7656 | 122.644 | -59.7198 | 62.7457 | -0.041122 | 0.0012711 | 0.062666 | 0.096248 | -0.0030335 | 0.0032684 | 0.00053404 | 0.0057984 | 0.00036737 | 0.066315 | 0.062758 | -0.017178 | 0.0018413 | -0.0039521 | 0.009155 | 62.6862 | -59.7839 | 62.558 | -59.3948 | -59.9075 | 0.018311 | 0.045776 | 62.6633 | -59.7336 | 62.7365 | -59.7244 | -59.848 | -59.6329 | -0.064087 | -0.05951 | -0.18768 | 0.32501 | 59.7382 | -0.18768 | 59.8022 | -0.1236 | -0.013733 | -0.082398 | -0.009156 | -0.004577 | 0.086975 | -0.12817 | 0.10071 | -0.11444 | 0.3891 | 122.3419 | 0.009156 | 122.4701 | 122.4701 | 122.3969 | 122.406 | 122.3831 | -122.5296 | -122.4792 | 122.2778 | 122.4564 | 59.729 | 59.7656
864.7656 | 122.6349 | -59.697 | 62.7319 | -0.06401 | -0.0017197 | 0.061598 | 0.097102 | 0.0012391 | 0.0002778 | -0.0041656 | -0.033874 | 0.00036737 | 0.067383 | 0.056777 | -0.015255 | 0.0029095 | -0.00010671 | 0.009155 | 62.7136 | -59.7977 | 62.6907 | -59.5963 | -59.9442 | 0.036621 | 0.045776 | 62.6862 | -59.7336 | 62.7365 | -59.6741 | -59.8526 | -59.6146 | -0.10071 | -0.018311 | -0.041199 | 0.10071 | 59.7336 | -0.24719 | 59.8343 | -0.14648 | -0.036622 | -0.045777 | 0.004577 | 0.022888 | 0.082397 | -0.15564 | 0.11902 | -0.11902 | 0.20142 | 122.4884 | 0.05951 | 122.4701 | 122.5113 | 122.4197 | 122.4106 | 122.3831 | -122.5296 | -122.4655 | 122.3877 | 122.4335 | 59.7061 | 59.7427
865.7656 | 122.6303 | -59.7061 | 62.7594 | -0.086899 | 0.0023391 | 0.062453 | 0.096461 | 0.0020935 | -0.0020722 | -0.00053396 | 0.0088502 | 0.00015377 | 0.066101 | 0.062331 | -0.015469 | 0.0018413 | 0.0016021 | -0.009155 | 62.6999 | -59.7656 | 62.6862 | -59.5917 | -59.9533 | 0.022888 | 0.027466 | 62.6724 | -59.7244 | 62.7365 | -59.7061 | -59.8297 | -59.6191 | -0.059509 | -0.059509 | -0.073242 | 0.11444 | 59.729 | -0.24719 | 59.7885 | -0.18768 | -0.01831 | -0.086975 | -0.022888 | 0 | 0.086975 | -0.1236 | 0.10529 | -0.10529 | 0.17395 | 122.4518 | 0.01831 | 122.4609 | 122.4655 | 122.3969 | 122.406 | 122.3785 | -122.525 | -122.4838 | 122.3923 | 122.4426 | 59.697 | 59.7336
866.7656 | 122.6532 | -59.7061 | 62.7548 | -0.010605 | 0.0016983 | 0.062453 | 0.096034 | 0.0010253 | -0.0016448 | 0.00053404 | -0.015564 | -0.00048703 | 0.06482 | 0.060836 | -0.017178 | 0.00013253 | 0.0035247 | 0.009155 | 62.6999 | -59.7702 | 62.7228 | -59.7885 | -60.0952 | 0.10986 | 0.041199 | 62.6907 | -59.7198 | 62.7502 | -59.7198 | -59.8343 | -59.6146 | -0.064087 | -0.054932 | -0.032044 | -0.082397 | 59.816 | -0.3891 | 59.8801 | -0.32501 | -0.013733 | -0.064087 | -0.004578 | -0.013733 | 0.091553 | -0.12817 | 0.10529 | -0.11444 | -0.01831 | 122.493 | 0 | 122.4701 | 122.4701 | 122.4106 | 122.406 | 122.3969 | -122.525 | -122.4747 | 122.4289 | 122.4564 | 59.7153 | 59.7473
867.7656 | 122.644 | -59.7198 | 62.7502 | -0.025863 | -0.0019333 | 0.062239 | 0.096675 | 0.0018799 | -0.0007904 | 0.0024566 | -0.033874 | 0.00015377 | 0.065033 | 0.059127 | -0.0144 | 0.00013253 | 0.00096129 | -0.013733 | 62.6816 | -59.7839 | 62.6907 | -59.6008 | -59.9716 | -0.018311 | -0.027466 | 62.6587 | -59.7473 | 62.7228 | -59.7473 | -59.8755 | -59.6375 | -0.064087 | -0.068664 | -0.059509 | 0.11902 | 59.7015 | -0.25177 | 59.7656 | -0.18768 | -0.027465 | -0.091553 | -0.027466 | -0.027465 | 0.082398 | -0.15564 | 0.10986 | -0.12817 | 0.18311 | 122.4747 | 0 | 122.4701 | 122.4655 | 122.406 | 122.4014 | 122.3785 | -122.5342 | -122.4976 | 122.4106 | 122.4426 | 59.7061 | 59.6924
868.7656 | 122.6166 | -59.7015 | 62.7182 | -0.06401 | 0.00063028 | 0.063307 | 0.098811 | 0.0020935 | -0.0012176 | -0.00074776 | -0.021667 | -0.00027343 | 0.065247 | 0.057631 | -0.014187 | 0.0018413 | -0.0013885 | -0.013733 | 62.6999 | -59.7885 | 62.6862 | -59.5734 | -59.9762 | -0.004578 | -0.004578 | 62.645 | -59.7519 | 62.7136 | -59.7382 | -59.8846 | -59.6283 | -0.086975 | -0.018311 | -0.032044 | 0.12817 | 59.697 | -0.27466 | 59.7839 | -0.18768 | -0.050354 | -0.073243 | -0.004578 | -0.036621 | 0.073242 | -0.18311 | 0.1236 | -0.13275 | 0.21515 | 122.4747 | 0.013733 | 122.4655 | 122.4884 | 122.3969 | 122.4014 | 122.3465 | -122.5067 | -122.4701 | 122.3877 | 122.4152 | 59.6878 | 59.697
869.7656 | 122.5937 | -59.729 | 62.7182 | -0.07164 | 0.0012711 | 0.063948 | 0.095821 | 0.0046569 | -0.0012176 | -0.00053396 | -0.033874 | 0.0014356 | 0.064392 | 0.062331 | -0.015896 | 0.0041913 | 0.00010689 | -0.041199 | 62.6724 | -59.8022 | 62.6358 | -59.6329 | -60.0266 | -0.073242 | -0.091553 | 62.6404 | -59.7336 | 62.6678 | -59.7885 | -59.9304 | -59.6741 | -0.073242 | -0.045777 | -0.082398 | 0.09613 | 59.6558 | -0.29755 | 59.729 | -0.2243 | -0.004578 | -0.07782 | -0.050354 | -0.059509 | 0.054932 | -0.20142 | 0.05951 | -0.19684 | 0.16937 | 122.438 | -0.054931 | 122.4014 | 122.4747 | 122.374 | 122.4014 | 122.3694 | -122.5204 | -122.4518 | 122.3648 | 122.3969 | 59.6878 | 59.6375
870.8281 | 122.6486 | -59.6832 | 62.7502 | -0.041122 | 0.0012711 | 0.061598 | 0.095393 | 0.0014527 | -0.0016448 | -0.00032036 | 0.0088502 | -0.00027343 | 0.066315 | 0.056136 | -0.015896 | 0.0012005 | -0.00074771 | 0 | 62.709 | -59.7748 | 62.6724 | -59.5917 | -59.9579 | 0.041199 | 0.032043 | 62.6587 | -59.7153 | 62.7457 | -59.7198 | -59.8434 | -59.6146 | -0.091552 | -0.041199 | -0.07782 | 0.091553 | 59.7244 | -0.27466 | 59.816 | -0.18311 | -0.032043 | -0.091553 | -0.004577 | -0.036621 | 0.068665 | -0.16022 | 0.10071 | -0.12817 | 0.1831 | 122.4472 | -0.004578 | 122.4609 | 122.4838 | 122.374 | 122.3923 | 122.3419 | -122.525 | -122.4655 | 122.3557 | 122.4289 | 59.6832 | 59.7153
871.7656 | 122.6944 | -59.697 | 62.7457 | -0.033493 | -1.0718e-05 | 0.061812 | 0.096034 | 0.0038025 | -0.0024994 | -0.00010676 | -0.00030524 | 0.0014356 | 0.065674 | 0.067671 | -0.015469 | 0.0024823 | 0.00074769 | 0.009155 | 62.677 | -59.7839 | 62.709 | -59.5642 | -59.9533 | 0.032043 | 0.041199 | 62.6541 | -59.7748 | 62.7274 | -59.8938 | -59.8251 | -59.5047 | -0.086976 | -0.068665 | -0.036622 | 0.13275 | 59.729 | -0.25635 | 59.816 | -0.16937 | -0.07782 | -0.091553 | -0.018311 | -0.19684 | 0.19226 | -0.12817 | 0.27008 | -0.050354 | 0.21973 | 122.493 | -0.11902 | 122.5021 | 122.4609 | 122.4289 | 122.374 | 122.3511 | -122.5296 | -122.5204 | 122.406 | 122.4243 | 59.7061 | 59.7382
872.7656 | 122.6303 | -59.7015 | 62.7274 | -0.033493 | -0.00022432 | 0.061598 | 0.094752 | 0.0029479 | -0.0031402 | -0.0020294 | -0.030823 | 0.0027174 | 0.067169 | 0.064253 | -0.015469 | 0.0026959 | -0.0020295 | 0.013733 | 62.6953 | -59.7656 | 62.6953 | -59.5596 | -59.935 | 0.054932 | 0.054932 | 62.6587 | -59.7382 | 62.7548 | -59.7153 | -59.8434 | -59.6191 | -0.064087 | -0.032044 | -0.032044 | 0.14191 | 59.7565 | -0.23346 | 59.8206 | -0.16937 | -0.036621 | -0.068665 | 0.027466 | -0.013733 | 0.082397 | -0.14191 | 0.11902 | -0.10529 | 0.20599 | 122.4609 | 0.022888 | 122.493 | 122.4609 | 122.3969 | 122.3969 | 122.3602 | -122.493 | -122.4655 | 122.3969 | 122.4564 | 59.7153 | 59.7565
873.7656 | 122.6669 | -59.6924 | 62.7274 | 0.050431 | 0.00084388 | 0.06053 | 0.096675 | 0.0018799 | -0.0020722 | -0.0033112 | -0.024719 | 0.00058097 | 0.065247 | 0.063185 | -0.014187 | 0.0018413 | 0.00074769 | 0.027466 | 62.709 | -59.7702 | 62.7045 | -59.5688 | -59.967 | 0.013733 | 0.045776 | 62.6358 | -59.7382 | 62.7319 | -59.7244 | -59.8618 | -59.6191 | -0.07782 | -0.018311 | -0.022888 | 0.1236 | 59.7061 | -0.27466 | 59.7839 | -0.19684 | -0.045776 | -0.091553 | 0.004578 | -0.032043 | 0.073242 | -0.16937 | 0.11902 | -0.1236 | 0.20142 | 122.4747 | 0.013733 | 122.4701 | 122.4792 | 122.374 | 122.4014 | 122.3282 | -122.4976 | -122.4655 | 122.3969 | 122.4243 | 59.7198 | 59.7382
874.7656 | 122.6166 | -59.7153 | 62.7502 | -0.079269 | 0.0016983 | 0.061385 | 0.094325 | 0.00059812 | -0.0018586 | -0.0016022 | -0.033874 | 0.0014356 | 0.06546 | 0.06404 | -0.015041 | 0.0026959 | -0.00074771 | -0.018311 | 62.6495 | -59.7748 | 62.6678 | -59.6054 | -59.9991 | -0.036621 | -0.027466 | 62.6404 | -59.7519 | 62.6999 | -59.7702 | -59.8984 | -59.6466 | -0.059509 | -0.10071 | -0.082397 | 0.10986 | 59.6787 | -0.28381 | 59.7382 | -0.2243 | -0.036621 | -0.10986 | -0.050354 | -0.054932 | 0.068665 | -0.1831 | 0.10529 | -0.14648 | 0.16937 | 122.4426 | -0.018311 | 122.4518 | 122.4243 | 122.3923 | 122.3648 | 122.3557 | -122.525 | -122.5021 | 122.3831 | 122.4152 | 59.697 | 59.6878
875.7656 | 122.6028 | -59.7015 | 62.7228 | -0.086899 | -0.00065152 | 0.060744 | 0.098384 | 0.0014527 | 0.0002778 | 0.00010684 | -0.04303 | 0.00015377 | 0.06482 | 0.057845 | -0.015469 | 0.0033367 | -0.00074771 | -0.013733 | 62.6724 | -59.7702 | 62.677 | -59.6146 | -59.9899 | -0.032043 | -0.027466 | 62.6221 | -59.7565 | 62.7136 | -59.7748 | -59.903 | -59.642 | -0.068665 | -0.050354 | -0.045776 | 0.086975 | 59.6695 | -0.28839 | 59.7382 | -0.21973 | -0.054932 | -0.10071 | -0.009155 | -0.073242 | 0.059509 | -0.20142 | 0.11444 | -0.14648 | 0.15564 | 122.4472 | -0.01831 | 122.4701 | 122.4426 | 122.3785 | 122.374 | 122.3236 | -122.493 | -122.4792 | 122.3785 | 122.4152 | 59.6878 | 59.6741
876.7656 | 122.6257 | -59.6924 | 62.7457 | -0.10216 | 0.0025529 | 0.063307 | 0.096889 | 0.00081172 | -0.0016448 | -0.00053396 | -0.015564 | 0.0031446 | 0.065888 | 0.058486 | -0.013973 | 0.0014141 | 0.00074769 | -0.018311 | 62.677 | -59.7839 | 62.677 | -59.5871 | -59.9808 | -0.022888 | -0.018311 | 62.6678 | -59.7473 | 62.7136 | -59.761 | -59.8846 | -59.642 | -0.091553 | -0.068665 | -0.068665 | 0.10529 | 59.6695 | -0.28839 | 59.761 | -0.19684 | -0.054931 | -0.07782 | -0.032044 | -0.068664 | 0.050354 | -0.19226 | 0.10529 | -0.13733 | 0.19684 | 122.4609 | -0.013733 | 122.4609 | 122.4609 | 122.4152 | 122.3694 | 122.3602 | -122.5296 | -122.493 | 122.3694 | 122.406 | 59.6741 | 59.6741
877.7656 | 122.5937 | -59.7427 | 62.7274 | -0.094528 | 0.0010575 | 0.062453 | 0.09753 | -0.00046988 | -0.0037812 | -0.002243 | -0.018616 | 0.0010084 | 0.065247 | 0.062972 | -0.015041 | 0.00098693 | -0.0016021 | -0.054932 | 62.6816 | -59.7794 | 62.645 | -59.642 | -60.0311 | -0.068665 | -0.11444 | 62.645 | -59.7565 | 62.6724 | -59.8022 | -59.9396 | -59.6695 | -0.036621 | -0.045776 | -0.082398 | 0.10071 | 59.6741 | -0.28839 | 59.7107 | -0.25177 | -0.013733 | -0.082398 | -0.054932 | -0.059509 | 0.073242 | -0.19684 | 0.086975 | -0.1831 | 0.13733 | 122.4243 | -0.045776 | 122.4289 | 122.4609 | 122.4014 | 122.4243 | 122.3877 | -122.5067 | -122.4838 | 122.3877 | 122.4152 | 59.6878 | 59.6283
878.7656 | 122.6944 | -59.6786 | 62.7502 | -0.056381 | 0.0016983 | 0.06053 | 0.095607 | 0.00081172 | -0.0035674 | -0.001175 | -0.0094604 | 0.00036737 | 0.064606 | 0.059767 | -0.016323 | 0.0012005 | -0.0020295 | 0.022888 | 62.6862 | -59.7794 | 62.6999 | -59.5551 | -59.9487 | 0.018311 | 0.027466 | 62.6587 | -59.7565 | 62.7319 | -59.6558 | -59.8343 | -59.61 | -0.10071 | -0.064087 | -0.050354 | 0.1236 | 59.697 | -0.27008 | 59.7977 | -0.16937 | -0.07782 | -0.091553 | -0.01831 | 0.022888 | 0.068665 | -0.15564 | 0.14648 | -0.07782 | 0.2243 | 122.4792 | 0.10071 | 122.4884 | 122.4655 | 122.4152 | 122.3648 | 122.3373 | -122.5296 | -122.5067 | 122.3785 | 122.4106 | 59.7015 | 59.7061
879.7656 | 122.6486 | -59.6832 | 62.764 | -0.033493 | 0.0021255 | 0.06288 | 0.095393 | -0.0026063 | -0.0033538 | -0.002884 | -0.012512 | 0.001222 | 0.066742 | 0.060836 | -0.016537 | 0.0031231 | 0.0016021 | 0.013733 | 62.7045 | -59.7748 | 62.6816 | -59.5688 | -59.9533 | 0.018311 | 0.032043 | 62.6678 | -59.7107 | 62.6404 | -59.5688 | -59.816 | -59.6329 | -0.091552 | -0.059509 | -0.082397 | 0.11444 | 59.7015 | -0.27008 | 59.7931 | -0.17853 | -0.027465 | -0.09613 | -0.1236 | 0.11444 | 0.050354 | -0.13275 | 0.077819 | -0.10529 | 0.20599 | 122.4564 | 0.14191 | 122.3511 | 122.4792 | 122.3785 | 122.3877 | 122.3511 | -122.5388 | -122.4747 | 122.3648 | 122.3236 | 59.697 | 59.7153
880.7656 | 122.6257 | -59.6924 | 62.7457 | -0.16319 | -1.0718e-05 | 0.060744 | 0.096675 | 0.0020935 | -0.0039948 | -0.0026704 | -0.036926 | 0.00015377 | 0.06482 | 0.059554 | -0.015682 | 0.0018413 | 0.0033111 | -0.013733 | 62.677 | -59.7656 | 62.6953 | -59.5688 | -59.9625 | 0 | 0.022888 | 62.645 | -59.7473 | 62.7411 | -59.7244 | -59.8434 | -59.6146 | -0.073242 | -0.068665 | -0.050355 | 0.1236 | 59.6924 | -0.27008 | 59.7656 | -0.19684 | -0.054931 | -0.10071 | -0.004578 | -0.032043 | 0.07782 | -0.15106 | 0.13275 | -0.096131 | 0.19684 | 122.4609 | 0.022888 | 122.4884 | 122.4426 | 122.3923 | 122.3694 | 122.3373 | -122.5113 | -122.493 | 122.3877 | 122.4335 | 59.6786 | 59.7153
881.7656 | 122.612 | -59.7153 | 62.7274 | -0.086899 | 0.0014847 | 0.063094 | 0.096675 | 0.0014527 | -0.0016448 | -0.0035248 | -0.024719 | 0.0027174 | 0.063965 | 0.062331 | -0.015255 | 0.0018413 | 0.0018159 | -0.032043 | 62.6907 | -59.7656 | 62.677 | -59.6054 | -60.0037 | -0.036621 | -0.050354 | 62.6312 | -59.7382 | 62.6907 | -59.761 | -59.903 | -59.6649 | -0.050354 | -0.036621 | -0.050354 | 0.10986 | 59.6787 | -0.28839 | 59.729 | -0.23804 | -0.022888 | -0.09613 | -0.036621 | -0.045776 | 0.050354 | -0.18768 | 0.073242 | -0.16479 | 0.16022 | 122.4426 | -0.022888 | 122.4289 | 122.4564 | 122.3694 | 122.406 | 122.3465 | -122.493 | -122.4655 | 122.3923 | 122.406 | 59.6832 | 59.6649
882.7656 | 122.6166 | -59.7107 | 62.7686 | -0.056381 | 0.0034073 | 0.062025 | 0.09753 | 0.0029479 | 0.000705 | -0.0018158 | -0.015564 | -0.00070063 | 0.065674 | 0.056349 | -0.015255 | 0.0014141 | -0.00096131 | -0.022888 | 62.6816 | -59.7702 | 62.677 | -59.6054 | -60.0128 | -0.041199 | -0.036621 | 62.6541 | -59.7427 | 62.709 | -59.761 | -59.8938 | -59.642 | -0.05951 | -0.086975 | -0.091553 | 0.10529 | 59.6695 | -0.30212 | 59.729 | -0.24261 | -0.032044 | -0.11444 | -0.05951 | -0.050354 | 0.068664 | -0.18311 | 0.10071 | -0.15106 | 0.1648 | 122.4472 | -0.01831 | 122.4518 | 122.4518 | 122.3969 | 122.3923 | 122.3648 | -122.5388 | -122.5113 | 122.3877 | 122.4197 | 59.6878 | 59.6741
883.7656 | 122.6166 | -59.6924 | 62.7548 | -0.06401 | 0.0031937 | 0.062666 | 0.095821 | 0.0063659 | -0.0052764 | -0.00032036 | -0.039978 | 0.0010084 | 0.065033 | 0.06169 | -0.015896 | 0.0022687 | 0.00053409 | -0.013733 | 62.6953 | -59.7565 | 62.677 | -59.5871 | -59.9945 | -0.022888 | -0.027466 | 62.6312 | -59.7244 | 62.6953 | -59.761 | -59.8984 | -59.6603 | -0.064087 | -0.05951 | -0.07782 | 0.10529 | 59.6695 | -0.30212 | 59.7336 | -0.23804 | -0.032043 | -0.1236 | -0.05951 | -0.068664 | 0.032044 | -0.20599 | 0.064087 | -0.17395 | 0.16937 | 122.4335 | -0.036621 | 122.4197 | 122.4518 | 122.3557 | 122.3877 | 122.3236 | -122.5113 | -122.4792 | 122.3694 | 122.3877 | 59.6786 | 59.6649
884.7656 | 122.6028 | -59.6878 | 62.7365 | -0.056381 | -0.00065152 | 0.061598 | 0.096034 | -0.00089728 | -0.0033538 | 0.00010684 | -0.021667 | 0.001222 | 0.063751 | 0.064253 | -0.015469 | 0.0018413 | 0.0020295 | -0.013733 | 62.709 | -59.7794 | 62.6816 | -59.5825 | -59.9625 | -0.018311 | -0.018311 | 62.645 | -59.7427 | 62.7136 | -59.7565 | -59.8801 | -59.6237 | -0.091553 | -0.027466 | -0.054931 | 0.10528 | 59.6695 | -0.27466 | 59.761 | -0.1831 | -0.054932 | -0.091553 | -0.022888 | -0.068665 | 0.064087 | -0.19226 | 0.11902 | -0.13733 | 0.19684 | 122.4609 | -0.013733 | 122.4564 | 122.4884 | 122.3877 | 122.3969 | 122.3328 | -122.5159 | -122.4792 | 122.3694 | 122.4014 | 59.6741 | 59.6695
885.7656 | 122.6166 | -59.697 | 62.7411 | -0.041122 | 0.0010575 | 0.062025 | 0.096461 | 0.0067933 | -0.0001496 | -0.0020294 | -0.0094604 | 0.00079477 | 0.064392 | 0.06404 | -0.015469 | 0.0012005 | 0.0011749 | -0.032043 | 62.6724 | -59.7931 | 62.6862 | -59.5779 | -59.9762 | -0.018311 | -0.009155 | 62.6495 | -59.7427 | 62.7136 | -59.7382 | -59.8755 | -59.6375 | -0.096131 | -0.068665 | -0.054932 | 0.11902 | 59.6786 | -0.27924 | 59.7748 | -0.18311 | -0.045777 | -0.091553 | -0.027466 | -0.041199 | 0.059509 | -0.17853 | 0.10529 | -0.13275 | 0.21515 | 122.4792 | 0.004578 | 122.4564 | 122.4655 | 122.3923 | 122.3694 | 122.3465 | -122.5342 | -122.4838 | 122.3831 | 122.4106 | 59.6649 | 59.6878
886.7656 | 122.6578 | -59.6924 | 62.7274 | -0.094528 | 0.0021255 | 0.060957 | 0.094539 | -0.0021789 | -0.001004 | -0.003952 | -0.04303 | 0.001222 | 0.063965 | 0.063613 | -0.015469 | 0.0022687 | 0.0013885 | 0.004578 | 62.7045 | -59.7427 | 62.6953 | -59.5642 | -59.9396 | 0.032043 | 0.082397 | 62.6633 | -59.7565 | 62.7411 | -59.6558 | -59.8434 | -59.6237 | -0.050354 | -0.022888 | -0.032044 | 0.12817 | 59.7244 | -0.24719 | 59.7748 | -0.19684 | -0.064087 | -0.064087 | 0.013733 | 0.036621 | 0.068665 | -0.15106 | 0.13275 | -0.086975 | 0.17853 | 122.438 | 0.10071 | 122.4976 | 122.4472 | 122.4197 | 122.3969 | 122.3557 | -122.4701 | -122.4838 | 122.3877 | 122.4335 | 59.697 | 59.7748
887.7656 | 122.644 | -59.6924 | 62.7411 | -0.12505 | 0.0014847 | 0.062666 | 0.096461 | 0.0023071 | -0.0031402 | -0.00053396 | -0.024719 | 0.0010084 | 0.065247 | 0.057845 | -0.01675 | 0.0031231 | -0.0024567 | -0.018311 | 62.6816 | -59.761 | 62.7136 | -59.5734 | -59.967 | -0.004578 | 0.009155 | 62.6724 | -59.7153 | 62.7274 | -59.729 | -59.8663 | -59.6237 | -0.068664 | -0.059509 | -0.027466 | 0.11902 | 59.6878 | -0.27466 | 59.7565 | -0.20599 | -0.022888 | -0.068665 | -0.013733 | -0.036621 | 0.068665 | -0.17395 | 0.091553 | -0.15106 | 0.18768 | 122.4747 | -0.013733 | 122.4426 | 122.4426 | 122.3877 | 122.374 | 122.3648 | -122.5021 | -122.4564 | 122.406 | 122.4197 | 59.6741 | 59.7015
888.7656 | 122.6212 | -59.7107 | 62.7594 | -0.06401 | 0.0029801 | 0.061812 | 0.095821 | 0.0016663 | 0.0004914 | 0.00053404 | -0.033874 | -0.00027343 | 0.06546 | 0.056777 | -0.015896 | 0.0024823 | -0.0030975 | -0.045776 | 62.6678 | -59.8068 | 62.6587 | -59.6283 | -59.9899 | -0.054932 | -0.068665 | 62.645 | -59.761 | 62.677 | -59.7702 | -59.9075 | -59.6558 | -0.096131 | -0.091552 | -0.10071 | 0.082397 | 59.6558 | -0.27924 | 59.7519 | -0.1831 | -0.050354 | -0.11444 | -0.082397 | -0.05951 | 0.054931 | -0.19684 | 0.10528 | -0.14649 | 0.17853 | 122.4655 | -0.009156 | 122.438 | 122.4747 | 122.406 | 122.3785 | 122.3557 | -122.5662 | -122.5204 | 122.3694 | 122.3877 | 59.6649 | 59.642
889.7656 | 122.5983 | -59.7107 | 62.7594 | -0.07164 | 0.0010575 | 0.060957 | 0.097316 | 0.0070069 | -0.0014312 | -0.0024566 | -0.024719 | 0.001222 | 0.065888 | 0.063613 | -0.016323 | 0.0026959 | -0.00032051 | -0.032043 | 62.6999 | -59.7885 | 62.6587 | -59.6329 | -59.9991 | -0.041199 | -0.073242 | 62.6816 | -59.7336 | 62.6953 | -59.7519 | -59.8892 | -59.6649 | -0.07782 | -0.059509 | -0.10071 | 0.077819 | 59.6695 | -0.28839 | 59.7473 | -0.21057 | -0.022889 | -0.077819 | -0.064087 | -0.041199 | 0.045776 | -0.17853 | 0.068665 | -0.15564 | 0.15564 | 122.4472 | -0.01831 | 122.4289 | 122.4884 | 122.4152 | 122.4106 | 122.3923 | -122.5479 | -122.493 | 122.3694 | 122.406 | 59.6786 | 59.6375
890.7656 | 122.6028 | -59.697 | 62.7548 | -0.048752 | 0.0023391 | 0.064589 | 0.096889 | 0.00081172 | -0.0007904 | 0.0018158 | -0.04303 | -5.9826e-05 | 0.063965 | 0.060195 | -0.016537 | 0.0020551 | -0.00053411 | -0.032043 | 62.6999 | -59.7702 | 62.6587 | -59.6008 | -60.0082 | -0.041199 | -0.050354 | 62.6724 | -59.7565 | 62.6999 | -59.7656 | -59.8846 | -59.642 | -0.073243 | -0.054932 | -0.096131 | 0.09613 | 59.6558 | -0.31128 | 59.729 | -0.23804 | -0.05951 | -0.082398 | -0.054932 | -0.068665 | 0.054931 | -0.18768 | 0.11444 | -0.12817 | 0.16937 | 122.4289 | -0.009155 | 122.4564 | 122.4701 | 122.4289 | 122.3969 | 122.3694 | -122.525 | -122.5113 | 122.3557 | 122.3969 | 59.6649 | 59.6466
891.7656 | 122.731 | -59.729 | 62.709 | -0.094528 | 0.00041648 | 0.061171 | 0.095607 | 0.0027343 | -0.0012176 | -0.0016022 | -0.033874 | -0.002196 | 0.064179 | 0.064253 | -0.015041 | 0.0037641 | -0.0018157 | -0.073242 | 62.6724 | -59.8022 | 62.6083 | -59.6878 | -60.054 | -0.11444 | -0.16022 | 62.6495 | -59.7473 | 62.6495 | -59.8297 | -59.9487 | -59.6786 | -0.073242 | -0.036621 | -0.10071 | 0.041199 | 59.6146 | -0.32501 | 59.6878 | -0.25177 | -0.01831 | -0.059509 | -0.059509 | -0.10071 | 0.050354 | -0.21973 | 0.068664 | -0.20142 | 0.11444 | 122.4106 | -0.082398 | 122.3969 | 122.4747 | 122.3969 | 122.4014 | 122.3785 | -122.5113 | -122.4564 | 122.3373 | 122.3785 | 59.6558 | 59.5688
892.7656 | 122.6486 | -59.6512 | 62.7502 | -0.025863 | -0.0010787 | 0.061598 | 0.098384 | -0.0021789 | -0.0031402 | 0.00032044 | -0.033874 | 0.0014356 | 0.06482 | 0.057845 | -0.015469 | 0.00098693 | 0.0033111 | 0.009155 | 62.677 | -59.7839 | 62.7319 | -59.5688 | -59.903 | 0.045776 | 0.036621 | 62.6633 | -59.7244 | 62.7548 | -59.7153 | -59.8343 | -59.6008 | -0.13275 | -0.073242 | -0.01831 | 0.082397 | 59.697 | -0.25177 | 59.8297 | -0.11902 | -0.073242 | -0.086975 | 0.004578 | -0.064087 | 0.050354 | -0.18311 | 0.1236 | -0.10986 | 0.21515 | 122.5159 | 0.009155 | 122.4792 | 122.4609 | 122.3877 | 122.3282 | 122.3145 | -122.5342 | -122.4747 | 122.3831 | 122.406 | 59.6603 | 59.6878
893.7656 | 122.6303 | -59.697 | 62.7457 | -0.033493 | 0.00041648 | 0.062666 | 0.09753 | -0.00046988 | 0.0004914 | -0.00053396 | -0.039978 | 0.0016492 | 0.064606 | 0.056563 | -0.015682 | 0.0031231 | 0.0028839 | -0.009155 | 62.677 | -59.7656 | 62.6724 | -59.5825 | -59.9808 | -0.036621 | -0.036621 | 62.645 | -59.7382 | 62.709 | -59.7519 | -59.8709 | -59.6329 | -0.068665 | -0.068665 | -0.073243 | 0.11444 | 59.6603 | -0.28381 | 59.729 | -0.21515 | -0.041199 | -0.10071 | -0.036622 | -0.054932 | 0.064086 | -0.17395 | 0.10529 | -0.13275 | 0.1831 | 122.438 | -0.013733 | 122.4472 | 122.4426 | 122.3831 | 122.374 | 122.3419 | -122.5113 | -122.4838 | 122.3694 | 122.406 | 59.6878 | 59.6603
894.7656 | 122.5845 | -59.6924 | 62.7274 | -0.06401 | 0.00041648 | 0.06288 | 0.097102 | 0.00081172 | 0.0004914 | -0.001175 | -0.027771 | 0.00079477 | 0.065674 | 0.064467 | -0.016109 | 0.0020551 | 0.00032049 | -0.073242 | 62.6862 | -59.7748 | 62.6266 | -59.6695 | -60.0723 | -0.1236 | -0.15564 | 62.6724 | -59.7656 | 62.6587 | -59.8206 | -59.9442 | -59.6741 | -0.082397 | -0.041199 | -0.10071 | 0.022888 | 59.5688 | -0.37994 | 59.6512 | -0.29755 | -0.073242 | -0.054932 | -0.068665 | -0.12817 | 0.018311 | -0.25177 | 0.091553 | -0.17853 | 0.10529 | 122.4014 | -0.054932 | 122.4243 | 122.4609 | 122.438 | 122.3785 | 122.3648 | -122.5021 | -122.493 | 122.319 | 122.3511 | 59.6191 | 59.5367
895.7656 | 122.6074 | -59.7107 | 62.7319 | 0.16487 | -0.00022432 | 0.063521 | 0.096248 | -0.00025628 | -0.0035674 | -0.0018158 | -0.012512 | 0.0010084 | 0.067383 | 0.061904 | -0.016109 | 0.0020551 | -0.0016021 | -0.082397 | 62.709 | -59.7565 | 62.6312 | -59.6695 | -60.0861 | -0.11902 | -0.16937 | 62.6541 | -59.7656 | 62.6816 | -59.7839 | -59.9258 | -59.6603 | -0.045777 | -0.022889 | -0.10071 | 0.041198 | 59.5917 | -0.37537 | 59.6375 | -0.32959 | -0.054932 | -0.07782 | -0.050354 | -0.073243 | 0.050354 | -0.21515 | 0.10529 | -0.16022 | 0.086975 | 122.3877 | -0.018311 | 122.4472 | 122.4655 | 122.4197 | 122.4197 | 122.3648 | -122.4884 | -122.4976 | 122.3419 | 122.3923 | 59.6283 | 59.5413
896.7656 | 122.5708 | -59.6924 | 62.7411 | -0.033493 | 0.00063028 | 0.062666 | 0.096248 | 0.0020935 | -0.0024994 | -0.002243 | -0.024719 | 0.00015377 | 0.064179 | 0.061049 | -0.015041 | 0.0016277 | -0.00010671 | -0.068665 | 62.6953 | -59.7702 | 62.6312 | -59.6558 | -60.0449 | -0.11444 | -0.15106 | 62.677 | -59.7565 | 62.6678 | -59.8206 | -59.9396 | -59.6924 | -0.07782 | -0.045777 | -0.10986 | 0.036621 | 59.5779 | -0.35248 | 59.6558 | -0.27466 | -0.064087 | -0.064087 | -0.073242 | -0.12817 | 0 | -0.24719 | 0.064087 | -0.1831 | 0.11444 | 122.4014 | -0.064087 | 122.4243 | 122.4655 | 122.4335 | 122.3877 | 122.3694 | -122.5113 | -122.4976 | 122.3236 | 122.3602 | 59.6237 | 59.5413
897.7656 | 122.5708 | -59.7061 | 62.7548 | -0.07164 | 0.00063028 | 0.062239 | 0.097102 | 0.00017092 | -0.0014312 | -0.002243 | -0.030823 | -5.9826e-05 | 0.064392 | 0.058486 | -0.01376 | -8.1274e-05 | 0.00074769 | -0.091553 | 62.6862 | -59.7656 | 62.6358 | -59.6649 | -60.0311 | -0.10529 | -0.15106 | 62.6724 | -59.7473 | 62.6587 | -59.8206 | -59.935 | -59.6695 | -0.059509 | -0.068665 | -0.11902 | 0.041199 | 59.6008 | -0.32501 | 59.6603 | -0.2655 | -0.041198 | -0.082398 | -0.096131 | -0.11444 | 0.036621 | -0.22888 | 0.077819 | -0.18768 | 0.10071 | 122.4014 | -0.073243 | 122.406 | 122.4518 | 122.4197 | 122.3923 | 122.3785 | -122.5204 | -122.5021 | 122.3419 | 122.3648 | 59.6146 | 59.5551
898.7656 | 122.5754 | -59.7244 | 62.7502 | -0.06401 | 0.0023391 | 0.060744 | 0.097743 | 0.00081172 | -0.0012176 | 0.00074764 | -0.024719 | 0.00079477 | 0.063111 | 0.060836 | -0.015255 | 0.00013253 | -0.0011749 | -0.068665 | 62.7182 | -59.761 | 62.6221 | -59.6603 | -60.054 | -0.10529 | -0.16022 | 62.6953 | -59.7519 | 62.6678 | -59.8297 | -59.9487 | -59.6649 | -0.036621 | -0.032043 | -0.12817 | 0.064087 | 59.6191 | -0.32959 | 59.6558 | -0.29297 | -0.027466 | -0.054932 | -0.082397 | -0.10529 | 0.059509 | -0.2243 | 0.086975 | -0.19684 | 0.10071 | 122.3831 | -0.07782 | 122.4197 | 122.4792 | 122.4472 | 122.4426 | 122.4197 | -122.5113 | -122.5021 | 122.3465 | 122.3923 | 59.6558 | 59.5642
899.7656 | 122.6257 | -59.697 | 62.7594 | -0.10216 | -1.0718e-05 | 0.062239 | 0.097743 | -0.00025628 | -0.0035674 | -0.0018158 | -0.018616 | -0.00027343 | 0.06546 | 0.057631 | -0.014828 | -8.1274e-05 | -0.00032051 | -0.045776 | 62.6816 | -59.7427 | 62.677 | -59.5734 | -59.9854 | -0.050354 | -0.041199 | 62.6587 | -59.7519 | 62.7319 | -59.7427 | -59.8801 | -59.6375 | -0.045777 | -0.077819 | -0.082397 | 0.1236 | 59.6466 | -0.28839 | 59.6924 | -0.24262 | -0.054932 | -0.10071 | -0.027465 | -0.045777 | 0.059509 | -0.18311 | 0.11444 | -0.12817 | 0.16937 | 122.4197 | 0.009155 | 122.4838 | 122.4243 | 122.4106 | 122.3785 | 122.3557 | -122.5021 | -122.5113 | 122.374 | 122.4289 | 59.6512 | 59.6558
900.7656 | 122.5937 | -59.7107 | 62.764 | -0.094528 | 0.0012711 | 0.060957 | 0.096248 | 0.0014527 | -0.0020722 | -0.0013886 | -0.021667 | 0.001222 | 0.064606 | 0.067458 | -0.015255 | 0.0020551 | -0.0028839 | -0.036621 | 62.6953 | -59.7565 | 62.6724 | -59.5963 | -59.9716 | -0.045776 | -0.054932 | 62.6633 | -59.729 | 62.709 | -59.7153 | -59.8663 | -59.6375 | -0.045777 | -0.068665 | -0.091553 | 0.11444 | 59.6649 | -0.26093 | 59.7107 | -0.21515 | -0.018311 | -0.10071 | -0.054932 | -0.004578 | 0.073242 | -0.15564 | 0.091553 | -0.13733 | 0.16022 | 122.4289 | 0.013733 | 122.438 | 122.4518 | 122.3923 | 122.406 | 122.374 | -122.5204 | -122.493 | 122.3831 | 122.4197 | 59.6741 | 59.6558
901.7656 | 122.612 | -59.697 | 62.7319 | -0.056381 | 0.00084388 | 0.062666 | 0.096461 | 0.0018799 | -0.0024994 | -0.00032036 | -0.018616 | -0.00070063 | 0.06546 | 0.063613 | -0.015255 | 0.0014141 | 0.0011749 | -0.11444 | 62.6999 | -59.7748 | 62.6175 | -59.6558 | -60.0632 | -0.11444 | -0.15564 | 62.6312 | -59.761 | 62.6999 | -59.7839 | -59.903 | -59.642 | -0.07782 | -0.032044 | -0.11444 | 0.041198 | 59.5825 | -0.36621 | 59.6603 | -0.28839 | -0.064087 | -0.10071 | -0.032044 | -0.086976 | 0.054931 | -0.20599 | 0.11902 | -0.14191 | 0.11902 | 122.3923 | -0.022889 | 122.4609 | 122.4747 | 122.3923 | 122.3969 | 122.3282 | -122.5067 | -122.493 | 122.3145 | 122.3969 | 59.5825 | 59.5413
902.7656 | 122.6898 | -59.6878 | 62.7136 | -0.13267 | -0.00043792 | 0.062666 | 0.098811 | -0.00025628 | -0.0018586 | -0.0050202 | -0.018616 | 0.00015377 | 0.064179 | 0.057204 | -0.016323 | 0.0016277 | -0.00032051 | -0.10529 | 62.6862 | -59.7839 | 62.6633 | -59.6008 | -59.9945 | -0.10529 | -0.09613 | 62.645 | -59.7427 | 62.7411 | -59.6924 | -59.8343 | -59.5871 | -0.096131 | -0.027466 | -0.050354 | 0.086975 | 59.5825 | -0.3067 | 59.6786 | -0.21057 | -0.054932 | -0.068665 | 0.027466 | -0.004578 | 0.10071 | -0.14649 | 0.15564 | -0.091553 | 0.18311 | 122.4472 | 0.050354 | 122.4838 | 122.4701 | 122.3877 | 122.374 | 122.3328 | -122.4976 | -122.4564 | 122.3511 | 122.4289 | 59.5825 | 59.5917
903.7656 | 122.6761 | -59.6786 | 62.6999 | -0.094528 | -1.0718e-05 | 0.061598 | 0.095821 | 0.0035889 | -0.0007904 | -0.00096136 | -0.0064086 | -0.0017688 | 0.064179 | 0.067244 | -0.015469 | 0.0029095 | 0.00010689 | -0.11444 | 62.6633 | -59.7794 | 62.6495 | -59.6054 | -60.0082 | -0.09613 | -0.1236 | 62.645 | -59.7427 | 62.7548 | -59.7153 | -59.8297 | -59.5963 | -0.10071 | -0.036621 | -0.050354 | 0.073242 | 59.5825 | -0.32959 | 59.6832 | -0.22888 | -0.064087 | -0.054932 | 0.054932 | -0.036621 | 0.082398 | -0.15106 | 0.14648 | -0.086975 | 0.17395 | 122.4289 | 0.027466 | 122.4976 | 122.4426 | 122.3877 | 122.3419 | 122.3236 | -122.4792 | -122.4426 | 122.3282 | 122.4335 | 59.5642 | 59.5551
904.7656 | 122.6212 | -59.7061 | 62.7228 | -0.10979 | 0.0014847 | 0.059462 | 0.098384 | 0.00059812 | -0.0022858 | -0.0037384 | -0.046081 | -0.00048703 | 0.064179 | 0.061476 | -0.015682 | 0.00077333 | 0.0020295 | -0.10986 | 62.6953 | -59.7748 | 62.6221 | -59.6649 | -60.0403 | -0.10986 | -0.14648 | 62.6724 | -59.7565 | 62.6953 | -59.7702 | -59.9167 | -59.642 | -0.068664 | -0.027466 | -0.10071 | 0.041199 | 59.5963 | -0.33417 | 59.6649 | -0.2655 | -0.050354 | -0.050354 | -0.027466 | -0.064087 | 0.064087 | -0.21057 | 0.11444 | -0.16022 | 0.10986 | 122.3969 | -0.013733 | 122.4518 | 122.4701 | 122.4289 | 122.4014 | 122.3785 | -122.4976 | -122.4792 | 122.3282 | 122.4014 | 59.5963 | 59.5596
905.7656 | 122.612 | -59.7061 | 62.7411 | -0.094528 | 0.0012711 | 0.062239 | 0.09817 | 0.0014527 | 0.000705 | -0.0016022 | -0.046081 | 0.001222 | 0.066101 | 0.065749 | -0.015896 | 0.0033367 | -0.0024567 | -0.07782 | 62.709 | -59.7931 | 62.6175 | -59.642 | -60.0311 | -0.10529 | -0.15106 | 62.6816 | -59.7427 | 62.6862 | -59.7702 | -59.903 | -59.6603 | -0.086975 | -0.032044 | -0.1236 | 0.064087 | 59.6008 | -0.32501 | 59.6878 | -0.23804 | -0.036621 | -0.059509 | -0.054932 | -0.064087 | 0.045777 | -0.19684 | 0.082398 | -0.16022 | 0.15106 | 122.4106 | -0.027466 | 122.4289 | 122.5021 | 122.4243 | 122.4152 | 122.3877 | -122.5342 | -122.4838 | 122.3236 | 122.3923 | 59.6283 | 59.5551
906.7656 | 122.6715 | -59.697 | 62.7914 | -0.13267 | 0.00020288 | 0.062453 | 0.09817 | -0.0021789 | -0.0022858 | 0.00032044 | -0.06134 | 0.0014356 | 0.065033 | 0.058486 | -0.016109 | 0.0033367 | 0.0060883 | -0.068665 | 62.7274 | -59.7839 | 62.6266 | -59.6649 | -60.054 | -0.11444 | -0.18768 | 62.6724 | -59.761 | 62.7228 | -60.1273 | -59.8434 | -59.4589 | -0.086976 | -0.064087 | -0.16479 | 0.032043 | 59.5825 | -0.35706 | 59.6695 | -0.27008 | -0.064087 | -0.11902 | -0.068665 | -0.4303 | 0.23804 | -0.14649 | 0.30212 | -0.082398 | 0.11902 | 122.4106 | -0.36621 | 122.4838 | 122.5113 | 122.4335 | 122.4243 | 122.3694 | -122.5754 | -122.5525 | 122.3236 | 122.4197 | 59.6283 | 59.5093
907.7656 | 122.5388 | -59.7015 | 62.7777 | -0.025863 | 0.0021255 | 0.062025 | 0.098598 | 0.00059812 | -0.001004 | -0.0018158 | -0.055237 | -0.0015552 | 0.064606 | 0.062972 | -0.01675 | 0.0037641 | 0.0052337 | -0.064087 | 62.6907 | -59.7702 | 62.6358 | -59.6741 | -60.0677 | -0.11444 | -0.17853 | 62.677 | -59.7748 | 62.4619 | -59.6832 | -59.5779 | -59.3903 | -0.068665 | -0.086975 | -0.14191 | 0.027466 | 59.5871 | -0.36621 | 59.6558 | -0.29755 | -0.073242 | -0.10071 | -0.31586 | 0.01831 | 0.31128 | 0.1236 | 0.38452 | 0.19684 | 0.096131 | 122.406 | 0.091552 | 122.2366 | 122.4609 | 122.4518 | 122.3923 | 122.3785 | -122.5479 | -122.5525 | 122.3373 | 122.1634 | 59.6375 | 59.523
908.7656 | 122.612 | -59.7015 | 62.7365 | -0.12505 | 0.0012711 | 0.061385 | 0.099452 | 0.0016663 | -0.0003632 | -0.0016022 | -0.046081 | -0.00027343 | 0.065247 | 0.062758 | -0.0144 | 0.0020551 | 0.0011749 | -0.10529 | 62.6999 | -59.7702 | 62.6404 | -59.6558 | -60.0311 | -0.10529 | -0.16937 | 62.6495 | -59.7702 | 62.709 | -59.7656 | -59.8984 | -59.6283 | -0.068665 | -0.036621 | -0.09613 | 0.045776 | 59.5963 | -0.32959 | 59.6649 | -0.26093 | -0.068665 | -0.086975 | -0.027466 | -0.064087 | 0.073242 | -0.19684 | 0.14191 | -0.12817 | 0.11444 | 122.4106 | 0.004578 | 122.4792 | 122.4701 | 122.4197 | 122.4014 | 122.3511 | -122.5067 | -122.5067 | 122.3419 | 122.4106 | 59.5963 | 59.5322
909.7656 | 122.7036 | -59.6786 | 62.7228 | -0.11742 | -1.0718e-05 | 0.063094 | 0.098384 | -0.00068368 | -0.0022858 | -0.0030976 | -0.024719 | 0.00036737 | 0.065033 | 0.055922 | -0.015896 | 0.0050457 | -0.0060883 | -0.11902 | 62.6999 | -59.7748 | 62.6862 | -59.5871 | -60.0037 | -0.086975 | -0.11902 | 62.6358 | -59.729 | 62.7823 | -59.6695 | -59.8114 | -59.5734 | -0.09613 | -0.022888 | -0.036621 | 0.091553 | 59.5917 | -0.32501 | 59.6878 | -0.22888 | -0.050354 | -0.086975 | 0.05951 | 0.009155 | 0.10529 | -0.13275 | 0.15564 | -0.082397 | 0.18768 | 122.4609 | 0.059509 | 122.5113 | 122.4747 | 122.3648 | 122.3785 | 122.3145 | -122.4976 | -122.4518 | 122.3648 | 122.4609 | 59.5596 | 59.5596
910.7656 | 122.731 | -59.6603 | 62.7182 | -0.086899 | -1.0718e-05 | 0.062239 | 0.09817 | 0.00038452 | -0.001004 | -0.00032036 | -0.0064086 | -0.0013416 | 0.063965 | 0.065108 | -0.017178 | 0.0020551 | -0.00096131 | -0.091553 | 62.6907 | -59.7656 | 62.6862 | -59.5917 | -59.9762 | -0.09613 | -0.10071 | 62.645 | -59.7565 | 62.7777 | -59.6786 | -59.7977 | -59.5459 | -0.10529 | -0.027466 | -0.032044 | 0.068664 | 59.5642 | -0.31586 | 59.6695 | -0.21057 | -0.096131 | -0.073243 | 0.059509 | -0.018311 | 0.11444 | -0.13733 | 0.21057 | -0.041198 | 0.17395 | 122.4518 | 0.07782 | 122.5342 | 122.4564 | 122.4014 | 122.3511 | 122.3053 | -122.4838 | -122.4747 | 122.3465 | 122.438 | 59.5688 | 59.5596
911.7656 | 122.699 | -59.6649 | 62.7136 | -0.079269 | 0.00063028 | 0.063307 | 0.099025 | -0.00025628 | -0.0007904 | -0.00053396 | -0.052185 | 0.00079477 | 0.065033 | 0.06874 | -0.016109 | 0.0014141 | -0.0026703 | -0.11444 | 62.6999 | -59.7702 | 62.6724 | -59.6146 | -59.9899 | -0.082397 | -0.10529 | 62.6633 | -59.7061 | 62.7914 | -59.6832 | -59.8297 | -59.5551 | -0.10529 | -0.013733 | -0.041199 | 0.050354 | 59.5825 | -0.32501 | 59.6878 | -0.21973 | -0.041199 | -0.050354 | 0.07782 | -0.018311 | 0.10986 | -0.16479 | 0.15106 | -0.1236 | 0.15564 | 122.4426 | 0.022888 | 122.4976 | 122.4701 | 122.3694 | 122.3648 | 122.3282 | -122.4838 | -122.4197 | 122.3373 | 122.4564 | 59.5505 | 59.5596
912.7656 | 122.7448 | -59.6558 | 62.7182 | -0.048752 | 0.0012711 | 0.062666 | 0.096248 | 0.0038025 | -0.0022858 | -0.0037384 | -0.12543 | -0.0024096 | 0.062256 | 0.066176 | -0.016537 | 0.00098693 | 0.0037385 | -0.050354 | 62.6587 | -59.7427 | 62.7594 | -59.5139 | -59.9167 | -0.050354 | 0.10986 | 62.6129 | -59.697 | 62.8281 | -59.6237 | -59.7015 | -59.4955 | -0.086975 | -0.05951 | 0.041198 | 0.14191 | 59.6054 | -0.26093 | 59.6924 | -0.17395 | -0.041198 | -0.10529 | 0.10986 | 0.032044 | 0.16022 | -0.045776 | 0.20142 | -0.004578 | 0.22888 | 122.5021 | 0.073242 | 122.525 | 122.4014 | 122.3099 | 122.3145 | 122.2687 | -122.4609 | -122.4152 | 122.4152 | 122.4838 | 59.6054 | 59.7656
913.7656 | 122.6074 | -59.7198 | 62.7365 | -0.048752 | 0.0010575 | 0.062025 | 0.097316 | -0.0026063 | -0.0007904 | 0.00010684 | -0.049133 | -5.9826e-05 | 0.06546 | 0.067885 | -0.016537 | 0.0022687 | 0.00032049 | -0.11444 | 62.6999 | -59.7748 | 62.6358 | -59.6512 | -60.022 | -0.11902 | -0.17395 | 62.6907 | -59.7519 | 62.7228 | -59.7473 | -59.8938 | -59.6375 | -0.054931 | -0.036621 | -0.10071 | 0.068665 | 59.6008 | -0.30212 | 59.6558 | -0.24719 | -0.032043 | -0.045776 | -0.013733 | -0.027465 | 0.082398 | -0.17395 | 0.11444 | -0.14191 | 0.1236 | 122.4106 | 0.004578 | 122.4747 | 122.4747 | 122.4426 | 122.4197 | 122.4106 | -122.5113 | -122.4884 | 122.3557 | 122.4426 | 59.6054 | 59.5459
914.7656 | 122.6166 | -59.697 | 62.7548 | -0.094528 | 0.00041648 | 0.060957 | 0.098811 | -0.00089728 | -0.0033538 | -0.0030976 | -0.049133 | 0.00079477 | 0.063538 | 0.065108 | -0.015896 | 0.00098693 | 0.0020295 | -0.10986 | 62.7182 | -59.7839 | 62.645 | -59.6237 | -60.0357 | -0.10529 | -0.17395 | 62.6862 | -59.729 | 62.7182 | -59.7473 | -59.8892 | -59.6237 | -0.086976 | -0.036621 | -0.10986 | 0.073242 | 59.5917 | -0.33875 | 59.6786 | -0.25177 | -0.032044 | -0.068665 | -0.036621 | -0.050354 | 0.073242 | -0.19226 | 0.10529 | -0.16022 | 0.16022 | 122.4289 | -0.01831 | 122.4472 | 122.5021 | 122.4152 | 122.4152 | 122.3831 | -122.5388 | -122.4838 | 122.3419 | 122.4152 | 59.5871 | 59.523
915.7656 | 122.6898 | -59.6649 | 62.7228 | -0.10979 | -1.0718e-05 | 0.062239 | 0.098384 | 0.0042297 | -0.0033538 | -0.00053396 | -0.018616 | 0.0010084 | 0.060761 | 0.060622 | -0.015896 | 0.0018413 | -0.00074771 | -0.11902 | 62.6953 | -59.7656 | 62.6724 | -59.5917 | -59.9899 | -0.07782 | -0.10986 | 62.6587 | -59.7244 | 62.7823 | -59.6603 | -59.8206 | -59.5596 | -0.10071 | -0.027466 | -0.050354 | 0.073242 | 59.5871 | -0.32501 | 59.6878 | -0.2243 | -0.059509 | -0.064087 | 0.05951 | 0.004578 | 0.10529 | -0.15564 | 0.16479 | -0.096131 | 0.17395 | 122.438 | 0.064087 | 122.5067 | 122.4609 | 122.3831 | 122.3602 | 122.3236 | -122.4884 | -122.4472 | 122.3373 | 122.4472 | 59.5459 | 59.5551
916.7656 | 122.7127 | -59.6603 | 62.7182 | -0.06401 | -0.00065152 | 0.06288 | 0.097743 | -0.0017517 | -0.0001496 | -0.0035248 | -0.04303 | -5.9826e-05 | 0.063111 | 0.060408 | -0.015255 | 0.00055973 | 0.0016021 | -0.041199 | 62.645 | -59.7427 | 62.7502 | -59.5093 | -59.9075 | -0.022888 | -0.073242 | 62.6129 | -59.7656 | 62.796 | -59.5734 | -59.7748 | -59.5322 | -0.082398 | -0.073243 | 0.032043 | 0.15106 | 59.6375 | -0.24719 | 59.7198 | -0.1648 | -0.10529 | -0.10529 | 0.07782 | 0.086975 | 0.12817 | -0.11444 | 0.23346 | -0.009155 | 0.23346 | 122.493 | 0.19226 | 122.5616 | 122.3877 | 122.3785 | 122.3053 | 122.2733 | -122.4609 | -122.4838 | 122.4106 | 122.4564 | 59.6191 | 59.5871
917.7656 | 122.731 | -59.6329 | 62.709 | -0.16319 | 0.0010575 | 0.063734 | 0.094966 | 0.00059812 | -0.0005768 | -0.002243 | -0.039978 | 0.00015377 | 0.063324 | 0.062545 | -0.017605 | -0.0011493 | 0.00032049 | -0.073242 | 62.6495 | -59.7336 | 62.7457 | -59.5001 | -59.8984 | -0.032043 | -0.050354 | 62.645 | -59.7107 | 62.9059 | -59.7107 | -59.7794 | -59.5276 | -0.10071 | -0.059509 | 0.036622 | 0.13275 | 59.6008 | -0.2655 | 59.7015 | -0.16479 | -0.077819 | -0.064087 | 0.19684 | -0.077819 | 0.10529 | -0.14648 | 0.1831 | -0.068665 | 0.23346 | 122.4792 | 0 | 122.6166 | 122.3831 | 122.3557 | 122.2824 | 122.2778 | -122.4426 | -122.4197 | 122.3785 | 122.5388 | 59.5596 | 59.5825
918.7656 | 122.7036 | -59.61 | 62.7274 | -0.15556 | 0.0019119 | 0.06288 | 0.097316 | 0.0025207 | -0.0022858 | -0.00053396 | -0.024719 | -0.00027343 | 0.063324 | 0.05464 | -0.017391 | 0.00077333 | -0.0045929 | -0.045776 | 62.6907 | -59.729 | 62.7686 | -59.5184 | -59.903 | -0.027466 | -0.059509 | 62.645 | -59.6924 | 62.677 | -59.5642 | -59.5047 | -59.3216 | -0.11902 | -0.036621 | 0.041199 | 0.091552 | 59.5825 | -0.29297 | 59.7015 | -0.17395 | -0.082398 | -0.082398 | -0.050354 | 0.045776 | 0.28839 | 0.10529 | 0.37079 | 0.18768 | 0.21057 | 122.4976 | 0.12817 | 122.3694 | 122.4197 | 122.3373 | 122.3007 | 122.2549 | -122.4564 | -122.4197 | 122.3785 | 122.287 | 59.5642 | 59.5505
919.7656 | 122.7814 | -59.6695 | 62.7136 | -0.12505 | 0.0025529 | 0.063094 | 0.099239 | -0.0017517 | -0.0007904 | 0.00074764 | -0.06134 | -0.00070063 | 0.063111 | 0.062972 | -0.017178 | 0.0024823 | -0.0039521 | -0.068665 | 62.6816 | -59.7427 | 62.7319 | -59.5001 | -59.8984 | -0.045776 | -0.041199 | 62.645 | -59.7473 | 62.8326 | -59.6191 | -60.0266 | -59.642 | -0.073242 | -0.032043 | 0.018311 | 0.16937 | 59.6237 | -0.22888 | 59.697 | -0.15564 | -0.077819 | -0.068665 | 0.11902 | 0.050354 | 0.027466 | -0.35706 | 0.10529 | -0.27924 | 0.24262 | 122.4747 | 0.12817 | 122.58 | 122.4243 | 122.3923 | 122.3511 | 122.3145 | -122.4564 | -122.4609 | 122.4014 | 122.5021 | 59.6008 | 59.6283
920.7656 | 122.6532 | -59.6695 | 62.764 | -0.079269 | 0.0023391 | 0.06288 | 0.099239 | -0.00068368 | -0.0024994 | -0.003952 | -0.070496 | -5.9826e-05 | 0.064606 | 0.060836 | -0.017178 | 0.0018413 | -0.00074771 | -0.10986 | 62.7274 | -59.7519 | 62.6633 | -59.61 | -60.0082 | -0.10529 | -0.13733 | 62.6862 | -59.7198 | 62.764 | -59.7015 | -59.8434 | -59.5917 | -0.082397 | -0.036621 | -0.10071 | 0.05951 | 59.5642 | -0.33875 | 59.6466 | -0.25635 | -0.050354 | -0.07782 | 0 | -0.032043 | 0.07782 | -0.17395 | 0.12817 | -0.1236 | 0.14191 | 122.4152 | 0.018311 | 122.4838 | 122.4792 | 122.406 | 122.3969 | 122.3557 | -122.5159 | -122.4838 | 122.3328 | 122.4335 | 59.5596 | 59.5322
921.7656 | 122.7081 | -59.6512 | 62.7457 | -0.11742 | 0.0023391 | 0.063307 | 0.098384 | 0.0025207 | 0.0002778 | -0.0018158 | -0.067444 | -0.0013416 | 0.063324 | 0.062545 | -0.01675 | 0.0022687 | -0.0022431 | -0.073242 | 62.6999 | -59.7427 | 62.7365 | -59.5413 | -59.9167 | -0.054932 | -0.082397 | 62.6495 | -59.7061 | 62.8189 | -59.61 | -59.7656 | -59.5139 | -0.091553 | -0.045777 | -0.009156 | 0.10986 | 59.5963 | -0.2655 | 59.6878 | -0.17395 | -0.054932 | -0.096131 | 0.073242 | 0.041199 | 0.13733 | -0.11444 | 0.19226 | -0.059509 | 0.20142 | 122.4792 | 0.096131 | 122.525 | 122.4426 | 122.3557 | 122.3511 | 122.3007 | -122.4884 | -122.4518 | 122.3877 | 122.4701 | 59.5779 | 59.5688
922.7656 | 122.7219 | -59.6649 | 62.6999 | -0.13267 | 0.0016983 | 0.062453 | 0.095821 | -0.0034607 | -0.0024994 | -0.0026704 | -0.039978 | -5.9826e-05 | 0.064606 | 0.063185 | -0.018459 | 0.0018413 | -0.0016021 | -0.041199 | 62.6678 | -59.7198 | 62.7365 | -59.5093 | -59.848 | -0.004578 | -0.022888 | 62.6312 | -59.6832 | 62.8372 | -59.6054 | -59.7382 | -59.5001 | -0.054932 | -0.032043 | 0.036621 | 0.15564 | 59.6603 | -0.1831 | 59.7153 | -0.12817 | -0.018311 | -0.068664 | 0.13733 | 0.059509 | 0.1648 | -0.073242 | 0.18311 | -0.054931 | 0.21057 | 122.4564 | 0.07782 | 122.5204 | 122.3877 | 122.3145 | 122.3328 | 122.2961 | -122.4197 | -122.3831 | 122.4014 | 122.5021 | 59.6237 | 59.642
923.7656 | 122.7219 | -59.6466 | 62.7182 | -0.10216 | 0.0027665 | 0.063734 | 0.09817 | -0.00068368 | -0.0005768 | -0.0041656 | -0.052185 | -0.0017688 | 0.061615 | 0.059767 | -0.017391 | 0.00098693 | 0.0011749 | -0.041199 | 62.6724 | -59.6878 | 62.6678 | -59.697 | -59.697 | 0.10529 | -0.07782 | 62.6587 | -59.6649 | 62.8326 | -59.5917 | -59.7519 | -59.523 | -0.041199 | -0.045777 | -0.050354 | -0.050354 | 59.7519 | -0.050354 | 59.7931 | -0.009155 | -0.018311 | -0.05951 | 0.11444 | 0.054931 | 0.1236 | -0.10529 | 0.14191 | -0.086975 | -0.009155 | 122.3557 | 0.073242 | 122.4976 | 122.3602 | 122.3236 | 122.319 | 122.3053 | -122.406 | -122.3831 | 122.3145 | 122.4792 | 59.6054 | 59.5688
924.7656 | 122.7722 | -59.6466 | 62.7136 | -0.16319 | -0.00086512 | 0.06053 | 0.10009 | 0.00081172 | 0.0015594 | -0.00010676 | -0.027771 | -5.9826e-05 | 0.068878 | 0.057204 | -0.015469 | 0.0016277 | 0.00096129 | -0.032043 | 62.6724 | -59.7244 | 62.7548 | -59.5001 | -59.8846 | -0.027466 | -0.082397 | 62.6312 | -59.7382 | 62.8235 | -59.5551 | -59.7656 | -59.5184 | -0.07782 | -0.041199 | 0.041199 | 0.14648 | 59.6191 | -0.23804 | 59.697 | -0.16022 | -0.091553 | -0.082397 | 0.10986 | 0.091552 | 0.12817 | -0.11902 | 0.21973 | -0.027466 | 0.2243 | 122.4792 | 0.18311 | 122.5616 | 122.3969 | 122.3694 | 122.319 | 122.2778 | -122.438 | -122.4518 | 122.4014 | 122.4701 | 59.6146 | 59.5642
925.7656 | 122.7127 | -59.6191 | 62.7274 | -0.14793 | 0.00041648 | 0.064589 | 0.098811 | -0.0021789 | 6.4004e-05 | -0.0026704 | -0.064392 | -5.9826e-05 | 0.063111 | 0.064467 | -0.015682 | 0.0020551 | -0.00053411 | -0.059509 | 62.677 | -59.7382 | 62.7686 | -59.5001 | -59.9167 | -0.045776 | -0.054932 | 62.6587 | -59.6924 | 62.7182 | -59.5963 | -59.4772 | -59.2941 | -0.11902 | -0.050354 | 0.041199 | 0.11902 | 59.5734 | -0.29755 | 59.6924 | -0.17853 | -0.073242 | -0.068665 | -0.009155 | 0.022889 | 0.32501 | 0.14191 | 0.39825 | 0.21515 | 0.23804 | 122.5067 | 0.096131 | 122.4106 | 122.4152 | 122.3511 | 122.2961 | 122.2778 | -122.4655 | -122.4197 | 122.3877 | 122.3373 | 59.5596 | 59.5642
926.7656 | 122.7448 | -59.61 | 62.7594 | -0.056381 | -1.0718e-05 | 0.060957 | 0.096248 | -0.00025628 | -0.0003632 | -0.0018158 | 0.1004 | -0.003905 | 0.061188 | 0.060408 | -0.014614 | -8.1274e-05 | 0.0018159 | 0.036621 | 62.7045 | -59.6695 | 62.8464 | -59.3948 | -59.7794 | 0.1236 | 0.41657 | 62.7594 | -59.6375 | 62.8098 | -59.5001 | -59.6603 | -59.5047 | -0.05951 | -0.054931 | 0.086976 | 0.21515 | 59.7336 | -0.16937 | 59.7931 | -0.10986 | -0.027466 | 0 | 0.050354 | 0.10986 | 0.10529 | -0.050354 | 0.13275 | -0.022888 | 0.27466 | 122.5159 | 0.13733 | 122.4472 | 122.374 | 122.3969 | 122.3145 | 122.3694 | -122.4289 | -122.3969 | 122.4564 | 122.4197 | 59.6466 | 60.0266
927.7656 | 122.6257 | -59.6786 | 62.7686 | -0.13267 | 0.0012711 | 0.061171 | 0.098384 | -4.2682e-05 | -0.002713 | -0.003952 | -0.09491 | -0.002196 | 0.065674 | 0.070021 | -0.018459 | 0.0024823 | -0.0024567 | -0.091553 | 62.7228 | -59.7656 | 62.6816 | -59.61 | -59.9854 | -0.10529 | -0.15106 | 62.6999 | -59.7061 | 62.7777 | -59.7061 | -59.8572 | -59.5917 | -0.086975 | -0.045777 | -0.086975 | 0.068665 | 59.5734 | -0.3067 | 59.6603 | -0.21973 | -0.027466 | -0.068665 | 0.009155 | -0.027466 | 0.086975 | -0.17853 | 0.11444 | -0.15106 | 0.15564 | 122.4472 | 0 | 122.4838 | 122.4884 | 122.406 | 122.4014 | 122.3785 | -122.5342 | -122.4747 | 122.3602 | 122.4564 | 59.5871 | 59.5276
928.7656 | 122.7219 | -59.6603 | 62.7365 | -0.11742 | 0.00063028 | 0.062453 | 0.095821 | 0.0018799 | -0.0018586 | -0.001175 | -0.067444 | 0.0014356 | 0.063965 | 0.064894 | -0.018459 | 0.00055973 | -0.0020295 | -0.09613 | 62.709 | -59.7244 | 62.7228 | -59.5779 | -59.9579 | -0.086975 | -0.10986 | 62.677 | -59.6603 | 62.8372 | -59.642 | -59.7702 | -59.5276 | -0.064087 | -0.027466 | -0.013733 | 0.082397 | 59.5734 | -0.29755 | 59.6375 | -0.23346 | 0 | -0.059509 | 0.10071 | 0.01831 | 0.13275 | -0.10986 | 0.13275 | -0.10986 | 0.14648 | 122.4472 | 0.01831 | 122.4976 | 122.4335 | 122.3373 | 122.3694 | 122.3373 | -122.4609 | -122.3969 | 122.3831 | 122.4976 | 59.5642 | 59.5505
929.7656 | 122.7585 | -59.6146 | 62.7319 | -0.15556 | 0.0023391 | 0.062239 | 0.098598 | 0.0016663 | -0.0016448 | -0.0020294 | -0.039978 | -0.0026232 | 0.065033 | 0.066817 | -0.017818 | 0.00055973 | -0.0016021 | -0.068665 | 62.677 | -59.7336 | 62.7731 | -59.4772 | -59.8846 | -0.032043 | -0.054932 | 62.6587 | -59.6924 | 62.9745 | -59.6649 | -59.7748 | -59.5276 | -0.11902 | -0.054932 | 0.041198 | 0.13733 | 59.5825 | -0.27008 | 59.7015 | -0.15106 | -0.07782 | -0.073243 | 0.24261 | -0.050354 | 0.086975 | -0.16022 | 0.16479 | -0.082397 | 0.25635 | 122.5067 | 0.027466 | 122.6669 | 122.4106 | 122.3511 | 122.2916 | 122.2733 | -122.4655 | -122.4243 | 122.3877 | 122.5891 | 59.5459 | 59.5596
930.7656 | 122.6715 | -59.6466 | 62.677 | -0.079269 | 0.00041648 | 0.062453 | 0.09753 | 0.0012391 | 0.0002778 | -0.00074776 | -0.079651 | 0.00079477 | 0.063324 | 0.070021 | -0.01675 | 0.0018413 | -0.00032051 | -0.068665 | 62.6907 | -59.7336 | 62.764 | -59.5139 | -59.8984 | -0.027466 | -0.068665 | 62.645 | -59.6878 | 62.8647 | -59.6008 | -59.7382 | -59.4589 | -0.086976 | 0.013733 | 0.086975 | 0.13275 | 59.6191 | -0.25177 | 59.7061 | -0.16479 | -0.041199 | -0.032044 | 0.18768 | 0.045776 | 0.18768 | -0.091553 | 0.22888 | -0.050354 | 0.21973 | 122.4976 | 0.086975 | 122.5525 | 122.4243 | 122.3328 | 122.3373 | 122.2916 | -122.4106 | -122.3648 | 122.4106 | 122.5113 | 59.5779 | 59.5779
931.7656 | 122.7219 | -59.5917 | 62.7823 | -0.033493 | -0.00086512 | 0.061598 | 0.09817 | -0.0023925 | -0.0020722 | -0.00074776 | 0.011902 | -0.0019824 | 0.064392 | 0.064681 | -0.018246 | 0.00055973 | -0.0022431 | 0.041199 | 62.7502 | -59.6786 | 62.8418 | -59.3994 | -59.8114 | 0.10986 | 0.10529 | 62.709 | -59.6283 | 62.8601 | -59.5413 | -59.6832 | -59.4635 | -0.086975 | -0.032044 | 0.059509 | 0.19226 | 59.7015 | -0.21973 | 59.7885 | -0.13275 | -0.036621 | -0.073243 | 0.077819 | 0.050354 | 0.12817 | -0.091553 | 0.16479 | -0.054932 | 0.27924 | 122.5204 | 0.086975 | 122.4884 | 122.4289 | 122.3373 | 122.3419 | 122.3007 | -122.4609 | -122.4106 | 122.4335 | 122.4518 | 59.6329 | 59.697
932.7656 | 122.6898 | -59.6558 | 62.7731 | -0.10979 | 0.00041648 | 0.061598 | 0.098811 | 0.0023071 | -0.0012176 | -0.0020294 | -0.088806 | 0.00036737 | 0.064179 | 0.065749 | -0.017605 | 0.0020551 | 0.0030975 | -0.10071 | 62.7182 | -59.7382 | 62.7365 | -59.5459 | -59.9442 | -0.082397 | -0.10529 | 62.6724 | -59.697 | 62.8372 | -59.6329 | -59.7656 | -59.5184 | -0.082397 | -0.054931 | -0.036621 | 0.10986 | 59.5734 | -0.28839 | 59.6558 | -0.20599 | -0.041198 | -0.10071 | 0.064087 | 0.022888 | 0.13733 | -0.10986 | 0.17853 | -0.068665 | 0.19226 | 122.4747 | 0.064086 | 122.5342 | 122.4564 | 122.3694 | 122.374 | 122.3282 | -122.5113 | -122.4701 | 122.3923 | 122.493 | 59.5551 | 59.5505
933.7656 | 122.6807 | -59.6237 | 62.7319 | -0.07164 | 0.0012711 | 0.064162 | 0.099025 | -0.0017517 | 0.0013458 | -0.001175 | -0.06134 | 0.0020764 | 0.064606 | 0.061904 | -0.016537 | 0.0014141 | -0.00096131 | -0.10986 | 62.7365 | -59.729 | 62.709 | -59.5642 | -59.967 | -0.10071 | -0.14191 | 62.6907 | -59.7015 | 62.8143 | -59.6466 | -59.7885 | -59.5413 | -0.10529 | 0.004577 | -0.022889 | 0.059509 | 59.523 | -0.34332 | 59.6283 | -0.23804 | -0.07782 | -0.041199 | 0.082397 | -0.022888 | 0.082397 | -0.1648 | 0.16022 | -0.086975 | 0.1648 | 122.438 | 0.054932 | 122.5159 | 122.4655 | 122.3923 | 122.3602 | 122.3145 | -122.4609 | -122.4335 | 122.3328 | 122.438 | 59.5139 | 59.4818
934.7656 | 122.6303 | -59.6512 | 62.7869 | -0.23186 | 0.00041648 | 0.059676 | 0.099879 | 0.0033753 | -0.0014312 | -0.002243 | -0.082703 | 0.00015377 | 0.06546 | 0.059554 | -0.016964 | -0.00050847 | -0.0028839 | 0.15106 | 62.7594 | -59.7336 | 62.677 | -59.6054 | -59.9808 | -0.13733 | -0.1831 | 62.709 | -59.7244 | 62.7457 | -59.7244 | -59.8755 | -59.6054 | -0.082398 | -0.027466 | -0.10986 | 0.045776 | 59.5139 | -0.32959 | 59.5963 | -0.24719 | -0.073242 | -0.07782 | -0.041198 | -0.073242 | 0.045776 | -0.2243 | 0.11902 | -0.15106 | 0.12817 | 122.4106 | 0 | 122.4701 | 122.493 | 122.4335 | 122.4106 | 122.3602 | -122.5204 | -122.5113 | 122.3282 | 122.3969 | 59.8022 | 59.4681
935.7656 | 122.6349 | -59.6558 | 62.7731 | -0.094528 | 0.00084388 | 0.060957 | 0.099452 | 0.0010253 | -0.0012176 | -0.0026704 | -0.06134 | 0.0020764 | 0.06482 | 0.064894 | -0.01675 | 0.0039777 | 0.00074769 | -0.11444 | 62.7502 | -59.7382 | 62.6862 | -59.5825 | -59.9854 | -0.11444 | -0.16479 | 62.709 | -59.7061 | 62.7823 | -59.6786 | -59.8343 | -59.5596 | -0.082397 | -0.022888 | -0.086975 | 0.073242 | 59.5413 | -0.32959 | 59.6237 | -0.24719 | -0.050354 | -0.064087 | 0.009156 | -0.022888 | 0.096131 | -0.17853 | 0.14648 | -0.12817 | 0.15564 | 122.4243 | 0.027466 | 122.4884 | 122.4884 | 122.4152 | 122.406 | 122.3648 | -122.5113 | -122.4792 | 122.3419 | 122.4381 | 59.5413 | 59.491
936.7656 | 122.7173 | -59.5871 | 62.7869 | -0.06401 | 0.00020288 | 0.062239 | 0.096034 | -0.00046988 | 0.0002778 | -0.00032036 | 0.027161 | -0.00091423 | 0.065888 | 0.054854 | -0.016323 | 0.0020551 | -0.0022431 | 0.041199 | 62.7457 | -59.6649 | 62.8418 | -59.3903 | -59.7839 | 0.10529 | 0.086975 | 62.6907 | -59.6558 | 62.8876 | -59.5139 | -59.6558 | -59.4543 | -0.07782 | -0.041198 | 0.054932 | 0.19684 | 59.6924 | -0.19684 | 59.7702 | -0.11902 | -0.068665 | -0.09613 | 0.10071 | 0.073242 | 0.13275 | -0.068665 | 0.20142 | 0 | 0.27466 | 122.5067 | 0.14191 | 122.5433 | 122.4106 | 122.3465 | 122.3328 | 122.2778 | -122.4518 | -122.4426 | 122.4289 | 122.4747 | 59.6283 | 59.6741
937.7656 | 122.699 | -59.6375 | 62.7731 | -0.094528 | 0.0019119 | 0.063521 | 0.098384 | 0.0020935 | -0.0031402 | -0.0030976 | -0.085754 | -0.002196 | 0.065674 | 0.060836 | -0.0144 | 0.0022687 | -0.00032051 | -0.10071 | 62.7045 | -59.7244 | 62.7411 | -59.5459 | -59.9625 | -0.09613 | -0.11902 | 62.6816 | -59.7061 | 62.8418 | -59.6329 | -59.7565 | -59.4955 | -0.086975 | -0.068664 | -0.032043 | 0.091553 | 59.5413 | -0.32501 | 59.6283 | -0.23804 | -0.068665 | -0.091552 | 0.068665 | 0.004577 | 0.14191 | -0.11902 | 0.21057 | -0.050354 | 0.17853 | 122.4655 | 0.073242 | 122.5479 | 122.4289 | 122.3877 | 122.3419 | 122.319 | -122.4976 | -122.4792 | 122.3785 | 122.4792 | 59.5367 | 59.5184
938.7656 | 122.6761 | -59.6237 | 62.7548 | -0.094528 | 0.0021255 | 0.063307 | 0.098598 | 0.00017092 | -0.0012176 | -0.00032036 | -0.073547 | 0.0010084 | 0.064179 | 0.061049 | -0.017605 | 0.0014141 | -0.0033111 | -0.10529 | 62.7548 | -59.7244 | 62.7045 | -59.5688 | -59.9533 | -0.09613 | -0.13275 | 62.7136 | -59.697 | 62.8098 | -59.6237 | -59.7748 | -59.5322 | -0.10071 | 0 | -0.050354 | 0.054931 | 59.5276 | -0.32959 | 59.6283 | -0.22888 | -0.073242 | -0.041199 | 0.054931 | 0 | 0.091552 | -0.15106 | 0.16479 | -0.07782 | 0.15564 | 122.4289 | 0.073242 | 122.5067 | 122.4792 | 122.4106 | 122.3785 | 122.3373 | -122.4792 | -122.4518 | 122.3282 | 122.4335 | 59.5184 | 59.491
939.7656 | 122.6761 | -59.6649 | 62.7777 | -0.10979 | -0.0010787 | 0.063948 | 0.098811 | -0.0055969 | -0.0016448 | -0.00096136 | -0.073547 | 0.00036737 | 0.065674 | 0.057204 | -0.018673 | 0.0033367 | 0.00032049 | -0.10529 | 62.7594 | -59.7244 | 62.7045 | -59.5779 | -59.967 | -0.091553 | -0.15106 | 62.7228 | -59.6741 | 62.8098 | -59.6695 | -59.7885 | -59.5367 | -0.059509 | -0.018311 | -0.073242 | 0.086975 | 59.5734 | -0.30212 | 59.6329 | -0.24262 | -0.009155 | -0.054932 | 0.032043 | -0.004578 | 0.12817 | -0.1236 | 0.13733 | -0.11444 | 0.14648 | 122.4289 | 0.004577 | 122.4838 | 122.4838 | 122.3969 | 122.4243 | 122.3877 | -122.5021 | -122.4518 | 122.3694 | 122.4747 | 59.5596 | 59.5139
940.7656 | 122.6212 | -59.6512 | 62.7914 | -0.041122 | 0.0029801 | 0.063307 | 0.096248 | 0.0010253 | -0.0024994 | -0.00032036 | -0.097961 | 0.0014356 | 0.064606 | 0.056777 | -0.014187 | 0.0022687 | -0.00032051 | -0.24261 | 62.6862 | -59.7382 | 62.7136 | -59.6512 | -59.9854 | -0.09613 | -0.18768 | 62.7274 | -59.6786 | 62.7594 | -59.697 | -59.848 | -59.6054 | -0.086975 | -0.10529 | -0.07782 | 0 | 59.5551 | -0.33417 | 59.642 | -0.24719 | -0.027466 | -0.064087 | -0.032044 | -0.045776 | 0.045776 | -0.19684 | 0.073242 | -0.16937 | 0.086975 | 122.4518 | -0.01831 | 122.438 | 122.4243 | 122.406 | 122.3373 | 122.3785 | -122.5296 | -122.4701 | 122.3648 | 122.4106 | 59.4086 | 59.4635
941.7656 | 122.6761 | -59.6558 | 62.7914 | -0.10979 | 0.0021255 | 0.060316 | 0.099452 | -4.2682e-05 | -0.0018586 | 0.00032044 | -0.079651 | 0.00079477 | 0.066315 | 0.067244 | -0.016537 | 0.00055973 | -0.0024567 | -0.10529 | 62.7319 | -59.7336 | 62.6953 | -59.5734 | -59.9808 | -0.10986 | -0.15564 | 62.7182 | -59.6878 | 62.7823 | -59.6512 | -59.8206 | -59.5688 | -0.07782 | -0.059509 | -0.096131 | 0.082398 | 59.5459 | -0.32501 | 59.6237 | -0.24719 | -0.032043 | -0.073242 | -0.009155 | 0.004578 | 0.086975 | -0.16479 | 0.11902 | -0.13275 | 0.16022 | 122.4289 | 0.036621 | 122.4701 | 122.4655 | 122.406 | 122.3877 | 122.374 | -122.525 | -122.4792 | 122.3511 | 122.4381 | 59.5505 | 59.5001
942.7656 | 122.6212 | -59.6283 | 62.8006 | -0.10216 | 0.0010575 | 0.060957 | 0.098384 | 0.0046569 | -0.0012176 | -0.002243 | -0.046081 | 0.001222 | 0.066529 | 0.063399 | -0.016964 | 0.0033367 | -0.0018157 | -0.09613 | 62.7274 | -59.7427 | 62.6862 | -59.5688 | -59.967 | -0.10529 | -0.17853 | 62.7228 | -59.6878 | 62.7823 | -59.6695 | -59.8114 | -59.5642 | -0.11444 | -0.073242 | -0.11444 | 0.059509 | 59.523 | -0.33875 | 59.6375 | -0.2243 | -0.059509 | -0.07782 | -0.01831 | -0.041199 | 0.064087 | -0.1831 | 0.1236 | -0.1236 | 0.17395 | 122.4289 | 0.01831 | 122.4701 | 122.4701 | 122.4106 | 122.3557 | 122.3511 | -122.5433 | -122.4884 | 122.3145 | 122.4106 | 59.5322 | 59.4498
943.7656 | 122.7173 | -59.6054 | 62.7548 | -0.10216 | 0.00041648 | 0.062666 | 0.098811 | -4.2682e-05 | -0.0031402 | 0.00053404 | -0.070496 | 0.0010084 | 0.067383 | 0.063826 | -0.016109 | 0.0020551 | 0.0018159 | -0.091553 | 62.7274 | -59.7153 | 62.7319 | -59.523 | -59.9121 | -0.07782 | -0.11444 | 62.6862 | -59.6786 | 62.8281 | -59.5871 | -59.729 | -59.491 | -0.10986 | -0.027466 | -0.022888 | 0.082398 | 59.5276 | -0.3067 | 59.6375 | -0.19684 | -0.073242 | -0.068665 | 0.073242 | 0.018311 | 0.11444 | -0.1236 | 0.18768 | -0.050354 | 0.19226 | 122.4472 | 0.091553 | 122.5067 | 122.4426 | 122.3648 | 122.3328 | 122.2916 | -122.4701 | -122.4335 | 122.3373 | 122.4335 | 59.5139 | 59.491
944.7656 | 122.7264 | -59.6329 | 62.764 | -0.10979 | -1.0718e-05 | 0.061598 | 0.099239 | -0.0038879 | -0.001004 | 0.00032044 | -0.058289 | -0.00091423 | 0.063324 | 0.065322 | -0.017818 | 0.0024823 | -0.0041657 | -0.10529 | 62.7274 | -59.7015 | 62.7548 | -59.5367 | -59.9213 | -0.086975 | -0.11902 | 62.6999 | -59.6878 | 62.8693 | -59.6054 | -59.761 | -59.5093 | -0.068664 | -0.036621 | -0.009155 | 0.096131 | 59.5459 | -0.28839 | 59.6146 | -0.21973 | -0.054931 | -0.064087 | 0.10529 | 0.027466 | 0.1236 | -0.12817 | 0.17853 | -0.073242 | 0.16479 | 122.4564 | 0.082397 | 122.5571 | 122.4289 | 122.3877 | 122.3602 | 122.3328 | -122.4655 | -122.4518 | 122.3877 | 122.5021 | 59.5276 | 59.5139
945.7656 | 122.6944 | -59.6054 | 62.7777 | -0.14793 | -0.00065152 | 0.062025 | 0.096889 | -0.00068368 | -0.0018586 | -0.0024566 | -0.06134 | -0.0019824 | 0.064179 | 0.06639 | -0.017605 | 0.0044049 | -0.0011749 | -0.10071 | 62.7365 | -59.7061 | 62.7274 | -59.5276 | -59.9442 | -0.091553 | -0.12817 | 62.709 | -59.6832 | 62.8372 | -59.6191 | -59.7565 | -59.4955 | -0.10071 | -0.041199 | -0.050354 | 0.07782 | 59.5139 | -0.33875 | 59.6146 | -0.23804 | -0.07782 | -0.068665 | 0.059509 | -0.013733 | 0.10986 | -0.15106 | 0.18768 | -0.073242 | 0.17853 | 122.4335 | 0.064087 | 122.5204 | 122.4426 | 122.3923 | 122.3419 | 122.3145 | -122.4838 | -122.4609 | 122.3328 | 122.4426 | 59.5047 | 59.4772
946.7656 | 122.6944 | -59.6146 | 62.7731 | -0.1403 | 0.00041648 | 0.061812 | 0.099239 | 0.00059812 | -0.0001496 | -0.0013886 | -0.067444 | 0.0010084 | 0.063538 | 0.061904 | -0.016323 | 0.0039777 | -0.00010671 | -0.09613 | 62.7594 | -59.7336 | 62.7365 | -59.5459 | -59.9442 | -0.09613 | -0.14191 | 62.7228 | -59.6832 | 62.8555 | -59.61 | -59.7519 | -59.5139 | -0.11902 | -0.013733 | -0.036621 | 0.068665 | 59.5184 | -0.32959 | 59.6375 | -0.21057 | -0.068665 | -0.050354 | 0.082398 | 0.004578 | 0.10071 | -0.13733 | 0.16937 | -0.068664 | 0.18768 | 122.4701 | 0.073243 | 122.5388 | 122.493 | 122.406 | 122.374 | 122.3373 | -122.5067 | -122.4564 | 122.3511 | 122.4701 | 59.5184 | 59.4727
947.7656 | 122.6715 | -59.5917 | 62.8098 | -0.10979 | -0.00022432 | 0.060316 | 0.099239 | 0.0016663 | -0.0014312 | -0.003952 | -0.055237 | 0.00079477 | 0.064179 | 0.060836 | -0.016964 | 0.0033367 | -0.0011749 | -0.11444 | 62.7365 | -59.729 | 62.7319 | -59.5459 | -59.9579 | -0.10071 | -0.15106 | 62.6953 | -59.6741 | 62.8235 | -59.6329 | -59.7565 | -59.5001 | -0.13733 | -0.073242 | -0.077819 | 0.045777 | 59.491 | -0.36621 | 59.6283 | -0.22888 | -0.082397 | -0.11444 | 0.013733 | -0.041199 | 0.091553 | -0.16479 | 0.17395 | -0.082398 | 0.18311 | 122.4609 | 0.041198 | 122.4976 | 122.4655 | 122.3694 | 122.3282 | 122.287 | -122.5388 | -122.4838 | 122.3236 | 122.4152 | 59.4772 | 59.4406
948.7656 | 122.6898 | -59.6329 | 62.7777 | -0.018234 | 0.00063028 | 0.061812 | 0.098384 | -0.00089728 | -0.0022858 | -0.00053396 | -0.049133 | -0.00027343 | 0.06546 | 0.063399 | -0.018032 | 0.0029095 | -0.00053411 | -0.10529 | 62.7594 | -59.729 | 62.7274 | -59.5459 | -59.9579 | -0.09613 | -0.16022 | 62.709 | -59.6924 | 62.8189 | -59.6237 | -59.7702 | -59.523 | -0.09613 | -0.018311 | -0.050354 | 0.086976 | 59.5367 | -0.32501 | 59.6329 | -0.22888 | -0.059509 | -0.068665 | 0.041199 | 0.009156 | 0.10986 | -0.13733 | 0.16937 | -0.07782 | 0.18311 | 122.4564 | 0.068665 | 122.5113 | 122.4884 | 122.4014 | 122.3923 | 122.3419 | -122.5067 | -122.4701 | 122.3602 | 122.4518 | 59.5276 | 59.4727
949.7656 | 122.7814 | -59.6008 | 62.8006 | -0.14793 | 0.0019119 | 0.062666 | 0.099239 | 0.0027343 | -0.0016448 | -0.0020294 | -0.052185 | -0.00070063 | 0.065888 | 0.061904 | -0.018459 | 0.00098693 | -0.0039521 | -0.064087 | 62.7045 | -59.7015 | 62.8143 | -59.4635 | -59.8709 | -0.045776 | -0.086975 | 62.6907 | -59.6603 | 62.9654 | -59.6695 | -59.9487 | -59.4772 | -0.10071 | -0.09613 | 0.013733 | 0.13733 | 59.5551 | -0.27008 | 59.6558 | -0.16937 | -0.059509 | -0.10986 | 0.16479 | -0.068665 | 0.1236 | -0.3479 | 0.1831 | -0.28839 | 0.23804 | 122.5159 | -0.009156 | 122.6257 | 122.406 | 122.3511 | 122.3053 | 122.2916 | -122.5021 | -122.4609 | 122.4152 | 122.5662 | 59.5367 | 59.5139
950.7656 | 122.6578 | -59.6237 | 62.709 | -0.11742 | 0.0021255 | 0.061812 | 0.096889 | 0.0010253 | 0.0004914 | -0.0018158 | -0.055237 | 0.00036737 | 0.064179 | 0.065108 | -0.017818 | 0.0014141 | -0.0016021 | -0.068665 | 62.7319 | -59.7198 | 62.7823 | -59.4635 | -59.8434 | -0.027466 | -0.082397 | 62.6678 | -59.6283 | 62.8784 | -59.5734 | -59.6924 | -59.3491 | -0.096131 | 0.022889 | 0.073243 | 0.16022 | 59.5963 | -0.21973 | 59.6924 | -0.1236 | -0.004578 | -0.041198 | 0.16937 | 0.050354 | 0.27466 | -0.068665 | 0.27924 | -0.064087 | 0.25635 | 122.5021 | 0.054932 | 122.5067 | 122.4518 | 122.2961 | 122.3557 | 122.2916 | -122.4289 | -122.3373 | 122.406 | 122.5021 | 59.5551 | 59.5413
951.7656 | 122.6944 | -59.61 | 62.7777 | -0.12505 | -1.0718e-05 | 0.062239 | 0.096248 | 0.00059812 | -0.0014312 | -0.0037384 | 0.018005 | -0.00027343 | 0.062897 | 0.062545 | -0.014614 | 0.00098693 | 0.00074769 | -0.073242 | 62.7045 | -59.6558 | 62.8052 | -59.4315 | -59.8618 | -0.027466 | -0.073242 | 62.6862 | -59.6603 | 62.8555 | -59.5917 | -59.7198 | -59.4955 | -0.045777 | -0.073242 | 0.027466 | 0.17853 | 59.5825 | -0.25177 | 59.6283 | -0.20599 | -0.050354 | -0.091553 | 0.07782 | 0.01831 | 0.11444 | -0.10986 | 0.16479 | -0.05951 | 0.2243 | 122.4609 | 0.068664 | 122.5159 | 122.3602 | 122.3465 | 122.3145 | 122.2961 | -122.4335 | -122.438 | 122.4152 | 122.4655 | 59.5367 | 59.5367
952.7656 | 122.7036 | -59.6008 | 62.8052 | -0.11742 | 0.00084388 | 0.063094 | 0.09817 | 0.0031617 | -0.0007904 | -0.00074776 | -0.076599 | -0.00091423 | 0.063965 | 0.05934 | -0.0191 | 0.00098693 | 0.0016021 | -0.064087 | 62.7136 | -59.6878 | 62.7914 | -59.4772 | -59.8801 | -0.059509 | -0.059509 | 62.6999 | -59.6695 | 62.8738 | -59.5642 | -59.7198 | -59.4498 | -0.086975 | -0.091553 | -0.013733 | 0.1236 | 59.5413 | -0.27924 | 59.6283 | -0.19226 | -0.068665 | -0.10529 | 0.068664 | 0.036621 | 0.15106 | -0.11902 | 0.21973 | -0.050354 | 0.21057 | 122.4792 | 0.10529 | 122.5433 | 122.4014 | 122.3694 | 122.3145 | 122.3007 | -122.493 | -122.4747 | 122.3923 | 122.4747 | 59.5367 | 59.5413
953.7656 | 122.7219 | -59.5825 | 62.7823 | -0.07164 | 0.00084388 | 0.062239 | 0.098598 | -0.0034607 | -0.0005768 | -0.0041656 | -0.058289 | 0.0020764 | 0.062683 | 0.068526 | -0.01675 | 0.0026959 | -0.0033111 | -0.082397 | 62.7182 | -59.7015 | 62.7914 | -59.4864 | -59.8526 | -0.050354 | -0.086975 | 62.6907 | -59.6375 | 62.8922 | -59.5642 | -59.7107 | -59.4543 | -0.11902 | -0.064087 | 0.009155 | 0.096131 | 59.5322 | -0.27008 | 59.6512 | -0.15106 | -0.054931 | -0.091553 | 0.10986 | 0.018311 | 0.12817 | -0.12817 | 0.1831 | -0.073242 | 0.21515 | 122.493 | 0.073242 | 122.5296 | 122.4197 | 122.3282 | 122.3007 | 122.2733 | -122.4838 | -122.4197 | 122.374 | 122.4747 | 59.5001 | 59.4955
954.7656 | 122.6395 | -59.6191 | 62.8189 | -0.10979 | 0.00020288 | 0.059889 | 0.099025 | 0.0014527 | 0.0002778 | -0.002243 | -0.082703 | 0.0020764 | 0.062897 | 0.062758 | -0.017605 | 0.0029095 | 0.0018159 | -0.10529 | 62.7594 | -59.6832 | 62.7319 | -59.5734 | -59.9716 | -0.11902 | -0.17395 | 62.7502 | -59.6558 | 62.8189 | -59.6695 | -59.7931 | -59.5459 | -0.064087 | -0.05951 | -0.086975 | 0.045777 | 59.5001 | -0.35248 | 59.5642 | -0.28839 | -0.036621 | -0.068665 | 0 | -0.050354 | 0.073243 | -0.17395 | 0.10986 | -0.13733 | 0.10986 | 122.4152 | -0.013733 | 122.4747 | 122.4426 | 122.406 | 122.3785 | 122.3694 | -122.5021 | -122.4747 | 122.3511 | 122.4381 | 59.5139 | 59.4452
955.7656 | 122.6395 | -59.6237 | 62.8052 | -0.056381 | 0.00041648 | 0.062453 | 0.10031 | -0.00025628 | -0.002713 | -0.004593 | -0.070496 | 0.0016492 | 0.06482 | 0.059981 | -0.017605 | 0.0024823 | -0.0035247 | -0.10529 | 62.8098 | -59.6878 | 62.7136 | -59.5505 | -59.9487 | -0.11444 | -0.19226 | 62.7502 | -59.6695 | 62.8006 | -59.6695 | -59.7931 | -59.5413 | -0.064087 | 0.004577 | -0.091553 | 0.073242 | 59.5093 | -0.32501 | 59.5734 | -0.26093 | -0.045777 | -0.054932 | -0.004578 | -0.045777 | 0.082397 | -0.16937 | 0.12817 | -0.1236 | 0.13733 | 122.4014 | 0 | 122.4701 | 122.4976 | 122.4197 | 122.4335 | 122.374 | -122.493 | -122.4747 | 122.3373 | 122.4243 | 59.5184 | 59.4315
956.7656 | 122.7081 | -59.5963 | 62.764 | -0.056381 | -0.00065152 | 0.061598 | 0.098598 | -0.0013245 | 0.0009186 | 0.00032044 | -0.067444 | 0.00079477 | 0.064179 | 0.061049 | -0.014614 | 0.0024823 | -0.0013885 | -0.10986 | 62.7548 | -59.7061 | 62.7594 | -59.5139 | -59.8984 | -0.073242 | -0.13275 | 62.7045 | -59.6603 | 62.8738 | -59.5917 | -59.729 | -59.4864 | -0.10986 | -0.009155 | -0.004578 | 0.082397 | 59.523 | -0.30212 | 59.6329 | -0.19226 | -0.064087 | -0.059509 | 0.10986 | 0.004577 | 0.10986 | -0.13275 | 0.17395 | -0.068665 | 0.19226 | 122.4655 | 0.068664 | 122.5342 | 122.4609 | 122.3648 | 122.3511 | 122.3007 | -122.4701 | -122.4243 | 122.3557 | 122.4701 | 59.4864 | 59.4635
957.7656 | 122.7173 | -59.5642 | 62.7731 | -0.07164 | 0.0027665 | 0.062453 | 0.096889 | 0.0012391 | -0.0046356 | -0.00032036 | 0.079041 | 0.0016492 | 0.063538 | 0.059127 | -0.017605 | 0.0031231 | -0.0026703 | -0.045776 | 62.7228 | -59.6603 | 62.8052 | -59.4406 | -59.8343 | -0.032043 | -0.19684 | 62.645 | -59.6558 | 62.9242 | -59.5551 | -59.6832 | -59.4086 | -0.09613 | -0.050354 | 0.032044 | 0.1236 | 59.5322 | -0.27008 | 59.6283 | -0.17395 | -0.091553 | -0.12817 | 0.15106 | 0.009155 | 0.15564 | -0.11902 | 0.24719 | -0.027466 | 0.21973 | 122.4655 | 0.10071 | 122.58 | 122.3831 | 122.3007 | 122.287 | 122.2092 | -122.4335 | -122.4289 | 122.3694 | 122.4884 | 59.5184 | 59.3674
958.7656 | 122.7493 | -59.5825 | 62.8098 | -0.06401 | -1.0718e-05 | 0.062239 | 0.098598 | 0.0014527 | -0.0016448 | -0.0024566 | -0.033874 | -0.0013416 | 0.066101 | 0.060408 | -0.018246 | -0.00093567 | -0.0016021 | -0.059509 | 62.7457 | -59.7015 | 62.8281 | -59.4315 | -59.8343 | -0.045776 | -0.064087 | 62.7045 | -59.6375 | 63.0249 | -59.6191 | -59.729 | -59.4727 | -0.11902 | -0.064086 | 0.018311 | 0.15106 | 59.5367 | -0.25177 | 59.6558 | -0.13275 | -0.054931 | -0.10529 | 0.21515 | -0.036621 | 0.10986 | -0.14648 | 0.16479 | -0.091553 | 0.27008 | 122.5296 | 0.01831 | 122.6624 | 122.4472 | 122.3419 | 122.3282 | 122.287 | -122.5113 | -122.4472 | 122.4106 | 122.6074 | 59.523 | 59.5184
959.7656 | 122.7493 | -59.5596 | 62.7869 | -0.1403 | 0.00063028 | 0.063948 | 0.09817 | 0.00081172 | -0.0033538 | -0.00010676 | -0.049133 | 0.00058097 | 0.064606 | 0.057845 | -0.017178 | 0.0014141 | 0.00010689 | -0.082397 | 62.7548 | -59.6741 | 62.8281 | -59.4223 | -59.8572 | -0.041199 | -0.073242 | 62.6953 | -59.642 | 62.9242 | -59.7794 | -59.5596 | -59.3079 | -0.11444 | -0.032043 | 0.041199 | 0.13733 | 59.5184 | -0.29755 | 59.6329 | -0.18311 | -0.082398 | -0.091553 | 0.13733 | -0.21973 | 0.25177 | 0 | 0.33417 | 0.082398 | 0.25177 | 122.5021 | -0.13733 | 122.5662 | 122.4289 | 122.3373 | 122.3145 | 122.2549 | -122.4609 | -122.4289 | 122.3877 | 122.4838 | 59.4772 | 59.4864
960.7656 | 122.7264 | -59.5917 | 62.7502 | -0.11742 | -0.0010787 | 0.062239 | 0.10009 | 0.0010253 | -0.0005768 | 0.00032044 | -0.046081 | -0.00027343 | 0.064179 | 0.067031 | -0.018246 | 0.0014141 | 0.00096129 | -0.07782 | 62.7548 | -59.6695 | 62.8143 | -59.4543 | -59.8709 | -0.059509 | -0.07782 | 62.7228 | -59.6375 | 62.9013 | -59.5551 | -59.6878 | -59.4223 | -0.07782 | 0.004578 | 0.064087 | 0.13733 | 59.5322 | -0.27924 | 59.61 | -0.20142 | -0.045776 | -0.027466 | 0.15106 | 0.036621 | 0.16937 | -0.09613 | 0.21515 | -0.050354 | 0.21515 | 122.4838 | 0.082397 | 122.5388 | 122.4243 | 122.3602 | 122.3465 | 122.3145 | -122.4197 | -122.3877 | 122.406 | 122.493 | 59.5139 | 59.5139
961.7656 | 122.6578 | -59.5963 | 62.8143 | -0.06401 | -0.00086512 | 0.063734 | 0.099666 | 0.00059812 | -0.0031402 | 0.00074764 | -0.10101 | 0.00036737 | 0.06482 | 0.063826 | -0.01675 | 0.00055973 | -0.0011749 | -0.11444 | 62.8052 | -59.6878 | 62.7228 | -59.5505 | -59.9579 | -0.10529 | -0.18768 | 62.7502 | -59.6603 | 62.8326 | -59.642 | -59.8022 | -59.5322 | -0.091553 | -0.009155 | -0.091553 | 0.045776 | 59.491 | -0.36163 | 59.5825 | -0.27008 | -0.064087 | -0.064087 | 0.018311 | -0.045777 | 0.064086 | -0.20599 | 0.12817 | -0.14191 | 0.13733 | 122.4106 | 0.01831 | 122.493 | 122.493 | 122.4106 | 122.4014 | 122.3465 | -122.5021 | -122.4747 | 122.319 | 122.4289 | 59.4818 | 59.4086
962.7656 | 122.644 | -59.6008 | 62.8143 | -0.12505 | -0.00086512 | 0.06053 | 0.099239 | -0.0013245 | -0.0016448 | -0.00010676 | -0.067444 | 0.0020764 | 0.06482 | 0.067031 | -0.017818 | 0.0012005 | 0.00010689 | -0.091553 | 62.7914 | -59.7015 | 62.7228 | -59.5459 | -59.935 | -0.11444 | -0.19684 | 62.7594 | -59.6603 | 62.8189 | -59.6466 | -59.8022 | -59.5322 | -0.10071 | -0.022888 | -0.091553 | 0.054932 | 59.4864 | -0.33417 | 59.5871 | -0.23346 | -0.059509 | -0.054932 | 0.004578 | -0.045776 | 0.068664 | -0.20142 | 0.12817 | -0.14191 | 0.15564 | 122.4243 | 0.013733 | 122.4792 | 122.493 | 122.4197 | 122.3923 | 122.3602 | -122.5159 | -122.4747 | 122.3236 | 122.4197 | 59.5093 | 59.404
963.7656 | 122.6852 | -59.5871 | 62.7914 | -0.094528 | 0.00063028 | 0.06053 | 0.098598 | 0.0016663 | 0.0026276 | -0.002884 | -0.030823 | 0.00058097 | 0.062683 | 0.065108 | -0.017178 | 0.0026959 | 0.00053409 | -0.10071 | 62.7594 | -59.697 | 62.7869 | -59.4864 | -59.8938 | -0.068665 | -0.14191 | 62.7548 | -59.6191 | 62.8876 | -59.5642 | -59.7061 | -59.4589 | -0.10986 | -0.032044 | -0.004578 | 0.10071 | 59.5184 | -0.3067 | 59.6283 | -0.19684 | -0.032044 | -0.036621 | 0.09613 | 0.022888 | 0.12817 | -0.11902 | 0.16022 | -0.086975 | 0.21057 | 122.4838 | 0.054932 | 122.5067 | 122.4564 | 122.374 | 122.3465 | 122.3419 | -122.4884 | -122.4106 | 122.374 | 122.4747 | 59.4864 | 59.4452
964.7656 | 122.699 | -59.5871 | 62.796 | -0.094528 | 0.00084388 | 0.063521 | 0.096461 | -0.00089728 | -0.0014312 | -0.0033112 | 0.069885 | -0.00027343 | 0.063324 | 0.061049 | -0.019314 | 0.0014141 | 0.00096129 | -0.045776 | 62.7594 | -59.6466 | 62.8464 | -59.3948 | -60.1044 | -0.19226 | -0.073242 | 62.7411 | -59.6191 | 62.9242 | -59.5184 | -59.6695 | -59.4452 | -0.059509 | -0.036622 | 0.050354 | 0.19226 | 59.3948 | -0.51727 | 59.4543 | -0.45776 | -0.032044 | -0.054932 | 0.12817 | 0.068664 | 0.14191 | -0.082398 | 0.17395 | -0.050354 | 0.25177 | 122.493 | 0.10071 | 122.5433 | 122.406 | 122.3602 | 122.3465 | 122.3282 | -122.4426 | -122.4152 | 122.4335 | 122.5113 | 59.5413 | 59.5139
965.7656 | 122.7356 | -59.5413 | 62.8098 | -0.15556 | 0.0034073 | 0.062453 | 0.099025 | 0.0010253 | -0.002713 | -0.0033112 | -0.046081 | 0.00079477 | 0.065247 | 0.059767 | -0.01675 | 0.0022687 | 0.00074769 | -0.050354 | 62.7502 | -59.6649 | 62.851 | -59.4177 | -59.8206 | -0.041199 | -0.31128 | 62.6862 | -59.6466 | 62.9288 | -59.4864 | -59.7015 | -59.4131 | -0.1236 | -0.059509 | 0.041199 | 0.1236 | 59.5001 | -0.27924 | 59.6237 | -0.15564 | -0.10528 | -0.1236 | 0.11902 | 0.054932 | 0.12817 | -0.16022 | 0.23346 | -0.054932 | 0.24719 | 122.5159 | 0.16022 | 122.5754 | 122.4152 | 122.3328 | 122.2916 | 122.2275 | -122.4747 | -122.4564 | 122.3923 | 122.4701 | 59.491 | 59.23
966.7656 | 122.7173 | -59.5688 | 62.8235 | -0.094528 | -1.0718e-05 | 0.064375 | 0.097743 | 0.0014527 | -0.0007904 | 0.00032044 | -0.036926 | 0.0020764 | 0.061829 | 0.067671 | -0.015682 | 0.0033367 | -0.0048065 | -0.045776 | 62.7411 | -59.6603 | 62.8418 | -59.4269 | -59.816 | -0.027466 | -0.10071 | 62.7365 | -59.61 | 62.9517 | -59.3674 | -59.6786 | -59.4818 | -0.091552 | -0.082397 | 0.018311 | 0.14191 | 59.5413 | -0.24719 | 59.6329 | -0.15564 | -0.041198 | -0.086975 | 0.12817 | 0.20142 | 0.086975 | -0.10986 | 0.12817 | -0.068665 | 0.23346 | 122.5021 | 0.24261 | 122.5616 | 122.4014 | 122.3465 | 122.3099 | 122.3053 | -122.4838 | -122.4335 | 122.4106 | 122.5204 | 59.523 | 59.4681
967.7656 | 122.8088 | -59.6008 | 62.8098 | -0.16319 | 0.0021255 | 0.062239 | 0.099452 | 0.0014527 | 0.0015594 | -0.0016022 | -0.046081 | -0.00048703 | 0.062897 | 0.058486 | -0.017818 | 0.0024823 | -0.0022431 | -0.054932 | 62.7594 | -59.6466 | 62.8235 | -59.436 | -59.8251 | -0.041199 | -0.091553 | 62.7045 | -59.6146 | 62.9288 | -59.5688 | -59.9899 | -59.491 | -0.045776 | -0.050354 | 0.013733 | 0.1648 | 59.5596 | -0.2243 | 59.6054 | -0.17853 | -0.013733 | -0.10529 | 0.11902 | 0.032043 | 0.10986 | -0.3891 | 0.1236 | -0.37537 | 0.21057 | 122.4701 | 0.045776 | 122.5433 | 122.406 | 122.319 | 122.3602 | 122.3053 | -122.4564 | -122.4243 | 122.4243 | 122.5296 | 59.5459 | 59.5093
968.7656 | 122.6303 | -59.6054 | 62.8143 | -0.086899 | -1.0718e-05 | 0.062666 | 0.099452 | -0.00025628 | -0.0014312 | -0.0013886 | -0.067444 | -5.9826e-05 | 0.063751 | 0.066176 | -0.018673 | 0.0012005 | -0.0043793 | -0.09613 | 62.8006 | -59.6695 | 62.7457 | -59.5413 | -59.9304 | -0.10986 | -0.19226 | 62.7731 | -59.6741 | 62.8372 | -59.6283 | -59.7839 | -59.5139 | -0.064087 | -0.013733 | -0.068664 | 0.064087 | 59.4955 | -0.32501 | 59.5596 | -0.26093 | -0.068664 | -0.041199 | 0.022888 | -0.022888 | 0.091553 | -0.17853 | 0.16022 | -0.10986 | 0.12817 | 122.4152 | 0.045776 | 122.5113 | 122.4701 | 122.4472 | 122.406 | 122.3785 | -122.4838 | -122.4884 | 122.3511 | 122.4426 | 59.5093 | 59.4131
969.7656 | 122.6944 | -59.5688 | 62.8006 | -0.094528 | 0.00063028 | 0.062025 | 0.098384 | 0.0055115 | -0.0005768 | 0.00010684 | -0.049133 | 0.00036737 | 0.063965 | 0.062758 | -0.017605 | 0.0016277 | 0.00074769 | -0.091553 | 62.7869 | -59.6603 | 62.796 | -59.4635 | -59.8846 | -0.059509 | -0.11902 | 62.7182 | -59.6237 | 62.8922 | -59.5688 | -59.6924 | -59.436 | -0.091552 | -0.013733 | -0.004577 | 0.10529 | 59.5093 | -0.31586 | 59.6008 | -0.22431 | -0.054931 | -0.082397 | 0.091553 | 0 | 0.13275 | -0.1236 | 0.18768 | -0.068665 | 0.19684 | 122.4564 | 0.054931 | 122.5159 | 122.4472 | 122.3419 | 122.3557 | 122.287 | -122.4609 | -122.4243 | 122.3648 | 122.4609 | 59.4772 | 59.4498
970.7656 | 122.6944 | -59.5505 | 62.8006 | -0.07164 | -1.0718e-05 | 0.063094 | 0.098811 | 0.0020935 | -0.0022858 | -0.0020294 | -0.055237 | -0.001128 | 0.062683 | 0.056136 | -0.017391 | 0.0037641 | 0.0020295 | -0.10986 | 62.7869 | -59.7107 | 62.7914 | -59.4772 | -59.8755 | -0.068665 | -0.15564 | 62.7365 | -59.6512 | 62.9013 | -59.5688 | -59.7015 | -59.4589 | -0.16022 | -0.013733 | -0.009155 | 0.073242 | 59.4818 | -0.32501 | 59.642 | -0.16479 | -0.10071 | -0.064087 | 0.10071 | -0.018311 | 0.091553 | -0.15106 | 0.19226 | -0.050354 | 0.23346 | 122.5021 | 0.082397 | 122.5525 | 122.4976 | 122.3877 | 122.3373 | 122.287 | -122.5113 | -122.4518 | 122.3419 | 122.4518 | 59.4406 | 59.3948
971.7656 | 122.7081 | -59.5505 | 62.8189 | -0.13267 | -0.00065152 | 0.060744 | 0.098384 | 0.0018799 | -0.0020722 | -0.00053396 | -0.021667 | 0.00015377 | 0.064179 | 0.060408 | -0.018886 | 0.00098693 | -0.00010671 | -0.041199 | 62.7594 | -59.6558 | 62.8464 | -59.4223 | -59.8068 | -0.032043 | -0.086975 | 62.709 | -59.6146 | 62.883 | -59.5184 | -59.6603 | -59.4223 | -0.10529 | -0.05951 | 0.027466 | 0.12817 | 59.5184 | -0.25635 | 59.6237 | -0.15106 | -0.064087 | -0.10986 | 0.064087 | 0.032043 | 0.12817 | -0.10986 | 0.19226 | -0.045776 | 0.23346 | 122.5021 | 0.09613 | 122.4976 | 122.4152 | 122.3236 | 122.3099 | 122.2595 | -122.4747 | -122.4335 | 122.3969 | 122.4335 | 59.5093 | 59.4635
972.7656 | 122.7448 | -59.5779 | 62.7914 | -0.094528 | -0.00043792 | 0.063521 | 0.096889 | 0.0025207 | -0.0016448 | 0.00096124 | -0.036926 | 0.0010084 | 0.065247 | 0.070021 | -0.016964 | 0.00055973 | 0.00053409 | -0.059509 | 62.7731 | -59.6649 | 62.8372 | -59.4223 | -59.8343 | -0.045776 | -0.11444 | 62.7182 | -59.61 | 62.9288 | -59.5139 | -59.8434 | -59.5871 | -0.086975 | -0.018311 | 0.045776 | 0.15564 | 59.5322 | -0.25635 | 59.6191 | -0.16937 | -0.032043 | -0.073242 | 0.13733 | 0.064087 | -0.009155 | -0.2655 | 0.022888 | -0.23346 | 0.24262 | 122.5021 | 0.09613 | 122.5388 | 122.438 | 122.3282 | 122.3511 | 122.2961 | -122.4564 | -122.4014 | 122.4152 | 122.5067 | 59.5184 | 59.4635
973.7656 | 122.7219 | -59.5459 | 62.8098 | -0.10979 | 0.00020288 | 0.061812 | 0.098598 | 0.0016663 | -0.0050628 | -0.0048066 | -0.04303 | -0.00091423 | 0.062683 | 0.062331 | -0.0144 | 0.0022687 | -0.0022431 | -0.086975 | 62.764 | -59.6375 | 62.8326 | -59.4315 | -59.8434 | -0.050354 | -0.20599 | 62.7548 | -59.61 | 62.915 | -59.5413 | -59.6786 | -59.3948 | -0.091553 | -0.045776 | 0.022889 | 0.11444 | 59.4955 | -0.29755 | 59.5871 | -0.20599 | -0.064087 | -0.054931 | 0.10529 | 0.004577 | 0.15106 | -0.13275 | 0.21515 | -0.068665 | 0.20599 | 122.4701 | 0.068664 | 122.525 | 122.4014 | 122.3648 | 122.3099 | 122.3007 | -122.4472 | -122.4197 | 122.3785 | 122.4609 | 59.4589 | 59.3399
974.7656 | 122.7264 | -59.5551 | 62.8143 | -0.20134 | -0.00043792 | 0.062453 | 0.10031 | -0.0013245 | -0.0029266 | -0.0018158 | -0.055237 | 0.00058097 | 0.064392 | 0.057845 | -0.01675 | 0.0026959 | -0.0030975 | -0.091553 | 62.7914 | -59.6558 | 62.7869 | -59.4681 | -59.8709 | -0.082397 | -0.27924 | 62.7274 | -59.61 | 62.9242 | -59.5688 | -59.6924 | -59.4269 | -0.10071 | -0.022888 | -0.027466 | 0.086975 | 59.4727 | -0.31586 | 59.5734 | -0.21515 | -0.054931 | -0.086975 | 0.10986 | -0.013733 | 0.12817 | -0.13733 | 0.18311 | -0.082398 | 0.18768 | 122.4426 | 0.041198 | 122.5342 | 122.4472 | 122.3373 | 122.3465 | 122.2824 | -122.4701 | -122.4243 | 122.3419 | 122.4792 | 59.4635 | 59.2758
975.7656 | 122.5891 | -59.5596 | 62.8738 | -0.056381 | 0.0023391 | 0.060957 | 0.10009 | 0.00081172 | -0.0024994 | 0.00010684 | -0.082703 | -5.9826e-05 | 0.06482 | 0.067458 | -0.016537 | 0.0046185 | 0.0018159 | -0.07782 | 62.8189 | -59.6649 | 62.7594 | -59.5276 | -59.9487 | -0.11444 | -0.3891 | 62.7869 | -59.6283 | 62.8418 | -59.6237 | -59.7702 | -59.5139 | -0.10529 | -0.054931 | -0.11444 | 0.032043 | 59.4452 | -0.3891 | 59.5505 | -0.28381 | -0.068665 | -0.086975 | -0.032043 | -0.064087 | 0.045776 | -0.21057 | 0.11444 | -0.14191 | 0.13733 | 122.4243 | 0.004578 | 122.4701 | 122.4838 | 122.4152 | 122.3785 | 122.3465 | -122.5388 | -122.5021 | 122.319 | 122.4014 | 59.4818 | 59.1705
976.7656 | 122.6166 | -59.5779 | 62.8647 | -0.1403 | 0.0070389 | 0.064803 | 0.099452 | 0.0014527 | -0.0031402 | -0.0058746 | -0.073547 | 0.0027174 | 0.066101 | 0.063185 | -0.015896 | 0.0029095 | 0.00032049 | -0.36163 | 62.7548 | -59.7107 | 62.8098 | -59.5276 | -59.9579 | -0.10071 | -0.36163 | 62.8281 | -59.6146 | 62.8418 | -59.6512 | -59.7885 | -59.5505 | -0.13275 | -0.10986 | -0.054932 | 0.050354 | 59.4772 | -0.37994 | 59.61 | -0.24719 | -0.036621 | -0.036621 | -0.022888 | -0.073242 | 0.027466 | -0.21057 | 0.064087 | -0.17395 | 0.1831 | 122.5204 | -0.036621 | 122.4564 | 122.4655 | 122.4426 | 122.3328 | 122.406 | -122.5754 | -122.4792 | 122.3877 | 122.4197 | 59.2163 | 59.2163
977.7656 | 122.6532 | -59.5963 | 62.8281 | -0.11742 | -0.00043792 | 0.061171 | 0.099025 | 0.0023071 | -0.0012176 | -0.001175 | -0.064392 | 0.00058097 | 0.062897 | 0.063185 | -0.015469 | 0.00098693 | -0.0013885 | -0.10529 | 62.796 | -59.6741 | 62.7686 | -59.5276 | -59.9075 | -0.11902 | -0.33417 | 62.7777 | -59.642 | 62.8464 | -59.6191 | -59.7656 | -59.4955 | -0.07782 | -0.032043 | -0.059509 | 0.068664 | 59.4772 | -0.31128 | 59.5551 | -0.23346 | -0.045777 | -0.050354 | 0.018311 | -0.022889 | 0.10071 | -0.16937 | 0.14648 | -0.1236 | 0.14648 | 122.4426 | 0.022888 | 122.4884 | 122.4701 | 122.4197 | 122.3923 | 122.374 | -122.5021 | -122.4701 | 122.3648 | 122.4426 | 59.491 | 59.2621
978.7656 | 122.6944 | -59.5734 | 62.8189 | -0.13267 | -0.0012923 | 0.062025 | 0.099239 | 0.0010253 | -0.001004 | -0.0048066 | -0.04303 | -0.00048703 | 0.062683 | 0.059127 | -0.014828 | 0.0014141 | -0.0011749 | -0.082397 | 62.8189 | -59.6558 | 62.8098 | -59.4315 | -59.8434 | -0.07782 | -0.23346 | 62.7457 | -59.6191 | 62.9333 | -59.5184 | -59.6695 | -59.4177 | -0.082398 | 0 | -0.009156 | 0.14191 | 59.4955 | -0.27008 | 59.5779 | -0.18768 | -0.045777 | -0.073242 | 0.11444 | 0.054931 | 0.15564 | -0.096131 | 0.20142 | -0.050354 | 0.2243 | 122.4655 | 0.10071 | 122.5525 | 122.4747 | 122.3648 | 122.3923 | 122.319 | -122.4747 | -122.4381 | 122.3831 | 122.5067 | 59.491 | 59.3399
979.7656 | 122.7219 | -59.5367 | 62.8418 | -0.10979 | -0.00086512 | 0.062025 | 0.099239 | 0.0012391 | -0.0029266 | -0.0016022 | -0.039978 | 0.00058097 | 0.064179 | 0.058913 | -0.017391 | 0.0020551 | -0.0028839 | -0.11444 | 62.8098 | -59.6558 | 62.7914 | -59.4498 | -59.848 | -0.086975 | -0.31128 | 62.7777 | -59.5917 | 62.9242 | -59.5322 | -59.6741 | -59.4269 | -0.11902 | -0.032044 | -0.050354 | 0.086975 | 59.4498 | -0.31128 | 59.5688 | -0.19226 | -0.054932 | -0.064087 | 0.082397 | 0.004577 | 0.10986 | -0.13733 | 0.1648 | -0.082397 | 0.20599 | 122.4472 | 0.059509 | 122.5159 | 122.4655 | 122.3694 | 122.3465 | 122.3145 | -122.4976 | -122.4335 | 122.3282 | 122.4609 | 59.4223 | 59.2255
980.7656 | 122.7173 | -59.5551 | 62.8418 | -0.10979 | 0.00041648 | 0.064375 | 0.098384 | -0.0011109 | -0.0022858 | -0.0013886 | -0.052185 | -0.0013416 | 0.06247 | 0.062117 | -0.0191 | -0.00029487 | 0.0018159 | -0.10529 | 62.8006 | -59.6512 | 62.8052 | -59.4681 | -59.8572 | -0.082397 | -0.33875 | 62.7823 | -59.5871 | 62.9196 | -59.5459 | -59.6695 | -59.4177 | -0.09613 | -0.041199 | -0.036621 | 0.086975 | 59.4727 | -0.30212 | 59.5688 | -0.20599 | -0.032043 | -0.059509 | 0.07782 | 0.009156 | 0.13733 | -0.11444 | 0.16937 | -0.082398 | 0.1831 | 122.4564 | 0.041199 | 122.5067 | 122.4518 | 122.3694 | 122.3557 | 122.3373 | -122.493 | -122.4289 | 122.3602 | 122.4747 | 59.4498 | 59.2163
981.7656 | 122.699 | -59.5551 | 62.8464 | -0.079269 | -0.00065152 | 0.062453 | 0.099879 | 0.00017092 | -0.0037812 | -0.0013886 | -0.055237 | -0.00091423 | 0.062897 | 0.060195 | -0.018032 | 0.0026959 | -0.00010671 | -0.11902 | 62.8006 | -59.6375 | 62.7777 | -59.4818 | -59.8938 | -0.10071 | -0.35706 | 62.7869 | -59.6146 | 62.8876 | -59.5779 | -59.6924 | -59.4635 | -0.082397 | -0.045777 | -0.068665 | 0.073242 | 59.4543 | -0.33875 | 59.5367 | -0.25635 | -0.059509 | -0.05951 | 0.041198 | -0.022888 | 0.091553 | -0.13733 | 0.15106 | -0.07782 | 0.15564 | 122.4152 | 0.036621 | 122.5021 | 122.438 | 122.4014 | 122.3557 | 122.3419 | -122.4838 | -122.4609 | 122.3328 | 122.4426 | 59.436 | 59.198
982.7656 | 122.6166 | -59.5688 | 62.8601 | 0.088577 | -0.00065152 | 0.063734 | 0.10095 | 0.0018799 | -0.0012176 | -0.0018158 | -0.064392 | 0.0014356 | 0.065247 | 0.064253 | -0.017391 | 0.0020551 | -0.0013885 | -0.15564 | 62.8326 | -59.6466 | 62.7502 | -59.5505 | -59.9121 | -0.11902 | -0.40741 | 62.8143 | -59.6375 | 62.8372 | -59.6283 | -59.7839 | -59.5001 | -0.077819 | -0.027465 | -0.10986 | 0.018311 | 59.4498 | -0.34332 | 59.5276 | -0.2655 | -0.068664 | -0.045776 | -0.022888 | -0.059509 | 0.068665 | -0.21515 | 0.13733 | -0.14648 | 0.09613 | 122.3969 | 0.009155 | 122.4747 | 122.4792 | 122.4518 | 122.4014 | 122.3831 | -122.5067 | -122.4976 | 122.319 | 122.406 | 59.4131 | 59.1614
983.7656 | 122.5754 | -59.5917 | 62.8555 | 0.14961 | -0.0023605 | 0.06288 | 0.10073 | -0.00046988 | -0.0012176 | -0.001175 | -0.064392 | -0.00027343 | 0.065674 | 0.064894 | -0.017178 | 0.0026959 | 0.0030975 | -0.018311 | 62.8418 | -59.6603 | 62.7731 | -59.5047 | -59.9213 | -0.1236 | -0.44861 | 62.8326 | -59.6054 | 62.8326 | -59.6283 | -59.7794 | -59.5276 | -0.068664 | -0.013733 | -0.082398 | 0.086975 | 59.4681 | -0.32959 | 59.5367 | -0.26093 | -0.013733 | -0.022888 | -0.022888 | -0.036621 | 0.064087 | -0.18768 | 0.07782 | -0.17395 | 0.15564 | 122.4335 | -0.022888 | 122.4381 | 122.5021 | 122.4381 | 122.4335 | 122.4243 | -122.5159 | -122.4609 | 122.3648 | 122.4243 | 59.5734 | 59.1431
984.7656 | 122.6715 | -59.5642 | 62.8372 | -0.07164 | -1.0718e-05 | 0.060744 | 0.099239 | 0.0023071 | -0.0035674 | -0.001175 | -0.052185 | -0.00048703 | 0.063111 | 0.062972 | -0.017178 | 0.0020551 | 0.0026703 | -0.11444 | 62.8189 | -59.6375 | 62.7686 | -59.4955 | -59.8755 | -0.10529 | -0.3891 | 62.7823 | -59.61 | 62.8876 | -59.5917 | -59.7015 | -59.4635 | -0.073242 | -0.01831 | -0.068664 | 0.068665 | 59.4589 | -0.31128 | 59.5322 | -0.23804 | -0.045776 | -0.054931 | 0.050354 | -0.027466 | 0.10071 | -0.13733 | 0.14648 | -0.091553 | 0.14191 | 122.406 | 0.01831 | 122.4976 | 122.4564 | 122.3923 | 122.3831 | 122.3465 | -122.4747 | -122.4472 | 122.3328 | 122.4518 | 59.4498 | 59.1751
985.7656 | 122.7219 | -59.5139 | 62.8281 | -0.12505 | 0.0010575 | 0.063307 | 0.096248 | 0.0018799 | -0.0005768 | -0.0013886 | -0.0064086 | -0.001128 | 0.063538 | 0.062758 | -0.015255 | 0.0024823 | 0.0016021 | -0.054932 | 62.7823 | -59.6146 | 62.8693 | -59.4086 | -59.8022 | -0.027466 | -0.31586 | 62.7457 | -59.5779 | 62.8098 | -59.5276 | -59.3948 | -59.1888 | -0.10071 | -0.045776 | 0.041199 | 0.10529 | 59.4864 | -0.28839 | 59.5871 | -0.18768 | -0.064087 | -0.082397 | -0.018311 | -0.013733 | 0.32501 | 0.11902 | 0.3891 | 0.18311 | 0.20599 | 122.4838 | 0.050354 | 122.3877 | 122.3969 | 122.3236 | 122.2961 | 122.2595 | -122.4426 | -122.406 | 122.3831 | 122.3236 | 59.4589 | 59.198
986.7656 | 122.7402 | -59.491 | 62.8555 | -0.10216 | 0.00084388 | 0.061385 | 0.10052 | -0.00068368 | -0.0016448 | 0.00053404 | -0.024719 | 0.00036737 | 0.06247 | 0.055922 | -0.018246 | 0.0050457 | -0.0020295 | -0.054932 | 62.8052 | -59.6329 | 62.8784 | -59.3811 | -59.7839 | -0.027466 | -0.35706 | 62.7502 | -59.5734 | 62.915 | -59.2987 | -59.5459 | -59.4131 | -0.14191 | -0.050354 | 0.022888 | 0.10986 | 59.4635 | -0.29297 | 59.6054 | -0.15106 | -0.082397 | -0.10529 | 0.059509 | 0.19226 | 0.07782 | -0.054931 | 0.16022 | 0.027466 | 0.25177 | 122.5113 | 0.27466 | 122.4884 | 122.4381 | 122.3236 | 122.2961 | 122.2412 | -122.4884 | -122.4289 | 122.3694 | 122.406 | 59.436 | 59.1339
987.7656 | 122.7402 | -59.5184 | 62.8647 | -0.086899 | 0.0019119 | 0.062025 | 0.098598 | 0.00059812 | -0.0003632 | -0.0020294 | -0.012512 | -0.00070063 | 0.065033 | 0.060408 | -0.017605 | -0.00050847 | -0.00096131 | -0.082397 | 62.7777 | -59.6237 | 62.883 | -59.3765 | -59.7748 | -0.041199 | -0.43488 | 62.7457 | -59.5871 | 63.089 | -59.5367 | -59.6878 | -59.4269 | -0.10528 | -0.086975 | 0.018311 | 0.14191 | 59.4772 | -0.25635 | 59.5825 | -0.15106 | -0.068664 | -0.11902 | 0.2243 | -0.01831 | 0.091553 | -0.16937 | 0.16022 | -0.10071 | 0.24719 | 122.5067 | 0.050354 | 122.6761 | 122.4014 | 122.3328 | 122.2961 | 122.2641 | -122.4884 | -122.4518 | 122.4014 | 122.6074 | 59.436 | 59.0836
988.7656 | 122.7127 | -59.5139 | 62.8693 | -0.10979 | 0.0016983 | 0.063521 | 0.099239 | -0.0019653 | 0.0004914 | -0.00053396 | -0.052185 | 0.001222 | 0.06546 | 0.055495 | -0.01675 | 0.0031231 | -0.00010671 | -0.041199 | 62.7777 | -59.6283 | 62.8876 | -59.3628 | -59.7702 | -0.045776 | -0.42114 | 62.7731 | -59.6008 | 62.9379 | -59.4406 | -59.6512 | -59.3811 | -0.11444 | -0.091553 | 0.01831 | 0.15106 | 59.4681 | -0.25635 | 59.5825 | -0.14191 | -0.086975 | -0.096131 | 0.068664 | 0.073242 | 0.13275 | -0.13733 | 0.21973 | -0.050354 | 0.2655 | 122.5159 | 0.16022 | 122.5388 | 122.406 | 122.374 | 122.2916 | 122.287 | -122.4976 | -122.4701 | 122.4014 | 122.4518 | 59.4727 | 59.0927
989.7656 | 122.7081 | -59.5367 | 62.8418 | -0.1403 | -0.00086512 | 0.062025 | 0.098384 | 0.00081172 | -0.0033538 | -0.001175 | -0.04303 | -0.00070063 | 0.067597 | 0.064253 | -0.016323 | 0.0026959 | -0.0037383 | -0.10986 | 62.8235 | -59.642 | 62.8189 | -59.436 | -59.8389 | -0.091553 | -0.63171 | 62.8006 | -59.5779 | 62.9471 | -59.5276 | -59.6649 | -59.4131 | -0.10529 | -0.018311 | -0.022888 | 0.10071 | 59.4452 | -0.30212 | 59.5505 | -0.19684 | -0.041199 | -0.041199 | 0.10529 | 0.009155 | 0.1236 | -0.12817 | 0.16479 | -0.086975 | 0.20599 | 122.4609 | 0.050354 | 122.525 | 122.4655 | 122.3785 | 122.3602 | 122.3373 | -122.4838 | -122.4197 | 122.3557 | 122.4838 | 59.4269 | 58.905
990.7656 | 122.6944 | -59.5184 | 62.8693 | -0.11742 | 0.0010575 | 0.063521 | 0.10031 | -0.00025628 | -0.0024994 | -0.00053396 | -0.036926 | 0.001222 | 0.066101 | 0.057418 | -0.017391 | 0.0016277 | -0.00096131 | -0.10071 | 62.851 | -59.6054 | 62.8372 | -59.436 | -59.8343 | -0.07782 | -0.65002 | 62.8006 | -59.5734 | 62.9425 | -59.5093 | -59.642 | -59.3903 | -0.086975 | -0.018311 | -0.032044 | 0.082398 | 59.4406 | -0.31586 | 59.5276 | -0.22888 | -0.054931 | -0.068665 | 0.073242 | 0.009156 | 0.12817 | -0.1236 | 0.1831 | -0.068665 | 0.16937 | 122.4426 | 0.064087 | 122.5159 | 122.4564 | 122.374 | 122.3694 | 122.319 | -122.4747 | -122.4426 | 122.3557 | 122.4609 | 59.4177 | 58.8684
991.7656 | 122.7448 | -59.4681 | 62.8876 | -0.1403 | 0.0016983 | 0.06288 | 0.10137 | 0.0025207 | -0.0022858 | -0.002884 | 0.0057984 | 0.00079477 | 0.061829 | 0.061263 | -0.017391 | 0.00013253 | 0.0026703 | -0.050354 | 62.8372 | -59.5505 | 63.0753 | -59.2255 | -59.816 | -0.054932 | -0.66376 | 62.8326 | -59.5367 | 62.9974 | -59.4681 | -59.5642 | -59.3124 | -0.082397 | -0.050354 | 0.18768 | 0.24262 | 59.4131 | -0.3479 | 59.4955 | -0.2655 | -0.068664 | -0.054931 | 0.10986 | 0 | 0.15564 | -0.09613 | 0.2243 | -0.027466 | 0.32501 | 122.6257 | 0.068664 | 122.5342 | 122.3877 | 122.3694 | 122.3053 | 122.3007 | -122.438 | -122.4243 | 122.5433 | 122.4655 | 59.4177 | 58.8043
992.7656 | 122.6807 | -59.5047 | 62.8464 | -0.12505 | 0.0021255 | 0.060957 | 0.099666 | -0.0017517 | -0.0012176 | -0.0043792 | -0.0033568 | -0.00048703 | 0.063751 | 0.058058 | -0.01675 | -0.00029487 | 0.00010689 | -0.050354 | 62.8326 | -59.5688 | 62.8967 | -59.3262 | -59.7427 | -0.009155 | -0.62714 | 62.8006 | -59.5413 | 62.9608 | -59.4955 | -59.6146 | -59.3765 | -0.064087 | -0.013733 | 0.050354 | 0.17853 | 59.4955 | -0.23804 | 59.5596 | -0.17395 | -0.036621 | -0.045777 | 0.11444 | 0.009156 | 0.12817 | -0.10986 | 0.1648 | -0.073242 | 0.24262 | 122.4655 | 0.045777 | 122.5021 | 122.4014 | 122.3419 | 122.3373 | 122.3053 | -122.4152 | -122.3877 | 122.4014 | 122.4655 | 59.4543 | 58.8776
993.7656 | 122.6715 | -59.4772 | 62.8922 | -0.17082 | 0.00084388 | 0.061598 | 0.098384 | 0.0016663 | 0.0009186 | -0.0018158 | -0.00030524 | 0.00058097 | 0.06546 | 0.05934 | -0.017605 | 0.00077333 | -0.0039521 | -0.07782 | 62.8372 | -59.5596 | 62.9242 | -59.3079 | -59.729 | -0.009155 | -0.67749 | 62.8143 | -59.5184 | 62.9745 | -59.4864 | -59.6054 | -59.3491 | -0.082397 | -0.054932 | 0.032043 | 0.16937 | 59.4681 | -0.25177 | 59.5505 | -0.16937 | -0.041199 | -0.07782 | 0.082397 | -0.009155 | 0.12817 | -0.12817 | 0.16937 | -0.086975 | 0.25177 | 122.4838 | 0.032044 | 122.493 | 122.3969 | 122.3328 | 122.3145 | 122.2916 | -122.4518 | -122.4106 | 122.4014 | 122.4518 | 59.3994 | 58.7997
994.7656 | 122.6761 | -59.491 | 62.9105 | -0.12505 | -1.0718e-05 | 0.061385 | 0.097743 | -0.0023925 | 0.000705 | -0.00096136 | -0.027771 | -5.9826e-05 | 0.060974 | 0.056777 | -0.016537 | 0.0026959 | 0.00096129 | -0.073242 | 62.851 | -59.5322 | 62.9288 | -59.317 | -59.7336 | -0.009155 | -0.73242 | 62.8281 | -59.5093 | 62.97 | -59.4772 | -59.61 | -59.3765 | -0.041199 | -0.059509 | 0.018311 | 0.17395 | 59.4818 | -0.24262 | 59.523 | -0.20142 | -0.01831 | -0.082397 | 0.05951 | 0.013733 | 0.11444 | -0.11902 | 0.13275 | -0.10071 | 0.21515 | 122.4609 | 0.032043 | 122.4792 | 122.3831 | 122.3373 | 122.3419 | 122.319 | -122.4426 | -122.4197 | 122.4197 | 122.4609 | 59.4177 | 58.7585
995.7656 | 122.6715 | -59.4727 | 62.9333 | -0.14793 | 0.0025529 | 0.062453 | 0.099239 | -0.0019653 | -0.0031402 | -0.0016022 | 0.0057984 | -0.00070063 | 0.060547 | 0.061904 | -0.0191 | 0.0014141 | -0.0022431 | -0.059509 | 62.8555 | -59.5459 | 62.9196 | -59.3262 | -59.7382 | -0.032043 | -0.77362 | 62.8052 | -59.5276 | 62.97 | -59.4727 | -59.5871 | -59.3582 | -0.073242 | -0.07782 | -0.013733 | 0.14648 | 59.4406 | -0.2655 | 59.5139 | -0.19226 | -0.054932 | -0.12817 | 0.036621 | 0 | 0.11444 | -0.11444 | 0.16937 | -0.059509 | 0.21973 | 122.4655 | 0.054932 | 122.4976 | 122.4014 | 122.3328 | 122.3282 | 122.2778 | -122.4792 | -122.4609 | 122.3923 | 122.4426 | 59.4131 | 58.699
996.7656 | 122.7356 | -59.5001 | 62.883 | -0.12505 | 0.0023391 | 0.063094 | 0.099239 | 0.0018799 | -0.0037812 | 0.00053404 | -0.046081 | -0.00027343 | 0.065247 | 0.063613 | -0.020168 | 0.0012005 | -0.0018157 | -0.027466 | 62.8235 | -59.5642 | 62.9379 | -59.3262 | -59.7336 | -0.022888 | -0.68665 | 62.8006 | -59.5367 | 62.9883 | -59.4635 | -59.6008 | -59.3628 | -0.064087 | -0.05951 | 0.054931 | 0.17395 | 59.4772 | -0.23346 | 59.5413 | -0.16937 | -0.036621 | -0.082398 | 0.10529 | 0.036621 | 0.13733 | -0.10071 | 0.17395 | -0.064087 | 0.23804 | 122.5021 | 0.073242 | 122.525 | 122.3877 | 122.3373 | 122.3236 | 122.3007 | -122.4472 | -122.4197 | 122.438 | 122.4884 | 59.4727 | 58.8135
997.7656 | 122.7127 | -59.4681 | 62.8922 | -0.10979 | 0.0010575 | 0.062239 | 0.099239 | -0.00046988 | -0.0001496 | -0.00010676 | -0.015564 | 0.0016492 | 0.06247 | 0.06874 | -0.019955 | 0.00055973 | -0.0013885 | -0.050354 | 62.8281 | -59.5505 | 62.9379 | -59.3262 | -59.7244 | -0.018311 | -0.7782 | 62.8006 | -59.5505 | 62.9974 | -59.4498 | -59.5917 | -59.3445 | -0.082397 | -0.064087 | 0.045776 | 0.14191 | 59.4498 | -0.25635 | 59.5322 | -0.17395 | -0.082397 | -0.091553 | 0.10529 | 0.018311 | 0.1236 | -0.1236 | 0.20599 | -0.041199 | 0.2243 | 122.4884 | 0.10071 | 122.5479 | 122.3785 | 122.3511 | 122.2961 | 122.2687 | -122.4426 | -122.4426 | 122.406 | 122.4655 | 59.4177 | 58.6899
998.7656 | 122.6624 | -59.4955 | 62.915 | -0.086899 | 0.00063028 | 0.060103 | 0.09817 | -0.0028199 | -0.0039948 | -0.0065156 | -0.0094604 | -0.00027343 | 0.063324 | 0.061049 | -0.018032 | 0.00098693 | 0.0041657 | -0.068665 | 62.8555 | -59.5917 | 62.8372 | -59.2072 | -59.5734 | -0.064087 | -0.85144 | 62.796 | -59.5367 | 62.9288 | -59.4864 | -59.6237 | -59.3903 | -0.096131 | -0.059509 | -0.07782 | 0.28839 | 59.4315 | -0.07782 | 59.5276 | 0.018311 | -0.041199 | -0.11902 | 0.013733 | 0.009155 | 0.10529 | -0.12817 | 0.14648 | -0.086975 | 0.38452 | 122.4289 | 0.050354 | 122.4655 | 122.4472 | 122.3328 | 122.3511 | 122.2916 | -122.5067 | -122.4518 | 122.3328 | 122.4243 | 59.4269 | 58.6441
999.7656 | 122.6898 | -59.4772 | 62.9105 | -0.094528 | 0.00020288 | 0.063734 | 0.098811 | -4.2682e-05 | -0.0054902 | -0.0020294 | -0.018616 | -0.0013416 | 0.064606 | 0.055495 | -0.016537 | 0.00055973 | -0.00096131 | -0.073242 | 62.8693 | -59.5688 | 63.0249 | -59.2209 | -59.9579 | -0.073242 | -0.97961 | 62.8052 | -59.5322 | 62.9288 | -59.4818 | -59.6146 | -59.3719 | -0.091553 | -0.041198 | 0.11444 | 0.25635 | 59.404 | -0.48065 | 59.4955 | -0.3891 | -0.054932 | -0.10528 | 0.018311 | -0.004578 | 0.10529 | -0.13733 | 0.16022 | -0.082397 | 0.3479 | 122.5937 | 0.050354 | 122.4609 | 122.4381 | 122.3373 | 122.3465 | 122.2824 | -122.4792 | -122.4426 | 122.5021 | 122.406 | 59.404 | 58.4976
1000.7656 | 122.6852 | -59.4727 | 62.9333 | -0.079269 | 0.00084388 | 0.062025 | 0.097316 | -4.2682e-05 | -0.0020722 | -0.00096136 | 0.0027466 | 0.001222 | 0.062683 | 0.058913 | -0.017178 | 0.0026959 | -0.0041657 | -0.064087 | 62.8601 | -59.5779 | 63.0478 | -59.5276 | -59.8022 | -0.022888 | -0.98877 | 62.8418 | -59.5047 | 62.9608 | -59.4727 | -59.61 | -59.3719 | -0.10529 | -0.073243 | 0.11444 | -0.054932 | 59.4498 | -0.32959 | 59.5551 | -0.2243 | -0.032044 | -0.091553 | 0.027465 | 0 | 0.10071 | -0.13733 | 0.13275 | -0.10529 | 0.050354 | 122.6257 | 0.032044 | 122.4655 | 122.438 | 122.3465 | 122.3328 | 122.3145 | -122.5113 | -122.4381 | 122.5204 | 122.4335 | 59.4086 | 58.4839
1001.7656 | 122.6669 | -59.4406 | 62.9471 | -0.086899 | 0.0027665 | 0.060744 | 0.098598 | -0.0053833 | -0.0016448 | -0.0016022 | -0.024719 | 0.00015377 | 0.063965 | 0.065535 | -0.017818 | 0.00055973 | -0.0060883 | -0.07782 | 62.8693 | -59.5413 | 62.9608 | -59.5001 | -59.7519 | -0.004578 | -1.0208 | 62.851 | -59.5139 | 62.9745 | -59.4543 | -59.5779 | -59.3582 | -0.10071 | -0.07782 | 0.013732 | -0.059509 | 59.436 | -0.31128 | 59.5367 | -0.21057 | -0.073242 | -0.096131 | 0.027465 | -0.013733 | 0.082398 | -0.13733 | 0.15564 | -0.064087 | 0.041199 | 122.5021 | 0.059509 | 122.4884 | 122.4106 | 122.3648 | 122.3099 | 122.2916 | -122.4884 | -122.4609 | 122.4014 | 122.4152 | 59.3628 | 58.4198
1002.7656 | 122.6624 | -59.4452 | 62.97 | -0.11742 | 0.0014847 | 0.062239 | 0.10073 | -0.0038879 | -0.0054902 | -0.0016022 | -0.033874 | -0.00091423 | 0.061615 | 0.058058 | -0.017178 | 0.0018413 | -0.0018157 | -0.09613 | 62.8876 | -59.4955 | 63.0661 | -59.5139 | -59.7519 | -0.022888 | -1.0483 | 62.8693 | -59.523 | 62.9791 | -59.4543 | -59.5917 | -59.3536 | -0.050354 | -0.082398 | 0.09613 | -0.068665 | 59.4223 | -0.3067 | 59.4727 | -0.25635 | -0.07782 | -0.10071 | 0.009155 | -0.009156 | 0.091552 | -0.14649 | 0.16937 | -0.068665 | -0.018311 | 122.5616 | 0.068664 | 122.5021 | 122.3831 | 122.3923 | 122.3328 | 122.3145 | -122.4655 | -122.493 | 122.5113 | 122.4243 | 59.3491 | 58.3969
1003.7656 | 122.7036 | -59.4772 | 62.9059 | -0.13267 | 0.0010575 | 0.062453 | 0.096675 | 0.00059812 | -0.0020722 | -0.003952 | -0.049133 | -0.0017688 | 0.060974 | 0.056777 | -0.017605 | 0.0018413 | -0.0058747 | -0.054932 | 62.8464 | -59.5688 | 62.9288 | -59.3353 | -59.7198 | -0.050354 | -1.0803 | 62.8281 | -59.5322 | 62.97 | -59.491 | -59.6008 | -59.3582 | -0.091553 | -0.059509 | 0.022888 | 0.14191 | 59.4269 | -0.24262 | 59.5184 | -0.15106 | -0.054932 | -0.07782 | 0.064087 | -0.013733 | 0.11902 | -0.1236 | 0.17395 | -0.068664 | 0.23346 | 122.4976 | 0.041199 | 122.5021 | 122.4152 | 122.3602 | 122.3236 | 122.3053 | -122.4747 | -122.4381 | 122.406 | 122.4472 | 59.4223 | 58.3969
1004.7656 | 122.6532 | -59.4772 | 62.915 | -0.094528 | 0.00041648 | 0.060744 | 0.099452 | -4.2682e-05 | -0.0022858 | -0.00032036 | -0.049133 | 0.00036737 | 0.062042 | 0.061049 | -0.018886 | 0.0014141 | -0.0020295 | -0.054932 | 62.8555 | -59.5642 | 62.9105 | -59.3353 | -59.7427 | -0.032043 | -1.0986 | 62.8235 | -59.5551 | 62.9745 | -59.4864 | -59.6375 | -59.3811 | -0.086975 | -0.059509 | -0.004578 | 0.14191 | 59.4452 | -0.2655 | 59.5322 | -0.17853 | -0.07782 | -0.091553 | 0.059509 | -0.009155 | 0.09613 | -0.16022 | 0.17395 | -0.082397 | 0.22888 | 122.4747 | 0.068665 | 122.5296 | 122.4197 | 122.3785 | 122.3328 | 122.3007 | -122.4792 | -122.4701 | 122.3877 | 122.4518 | 59.4223 | 58.3786
1005.7656 | 122.7173 | -59.4589 | 62.9196 | -0.079269 | -0.00022432 | 0.06053 | 0.10052 | 0.0020935 | -0.0003632 | -0.0026704 | -0.018616 | -0.001128 | 0.063111 | 0.066817 | -0.01675 | 0.0016277 | -0.0013885 | -0.045776 | 62.8784 | -59.5413 | 62.8967 | -59.3399 | -59.7382 | 0.022888 | -1.0941 | 62.8281 | -59.5139 | 62.9837 | -59.4269 | -59.5551 | -59.3491 | -0.082398 | -0.041199 | -0.022888 | 0.11902 | 59.4818 | -0.27924 | 59.5642 | -0.19684 | -0.054932 | -0.091553 | 0.064087 | 0.032043 | 0.10986 | -0.096131 | 0.16479 | -0.041199 | 0.20142 | 122.4381 | 0.086975 | 122.4976 | 122.4197 | 122.3419 | 122.3373 | 122.287 | -122.4609 | -122.4335 | 122.3557 | 122.4426 | 59.4131 | 58.3649
1006.7656 | 122.6852 | -59.491 | 62.8922 | -0.11742 | 0.0021255 | 0.061812 | 0.099239 | -0.0038879 | -0.0018586 | -0.0054474 | -0.033874 | -5.9826e-05 | 0.064392 | 0.06169 | -0.016323 | 0.00098693 | -0.00096131 | -0.064087 | 62.883 | -59.5917 | 62.8876 | -59.3811 | -59.7519 | 0.009155 | -1.1124 | 62.8143 | -59.5596 | 62.9517 | -59.4727 | -59.5917 | -59.3628 | -0.10071 | -0.009155 | -0.004578 | 0.10986 | 59.5001 | -0.26093 | 59.6008 | -0.16022 | -0.068664 | -0.07782 | 0.059509 | 0.018311 | 0.12817 | -0.10071 | 0.19684 | -0.032044 | 0.21057 | 122.4792 | 0.086975 | 122.5113 | 122.4747 | 122.374 | 122.374 | 122.3053 | -122.4838 | -122.4518 | 122.3785 | 122.4426 | 59.4269 | 58.3786
1007.7656 | 122.6852 | -59.4818 | 62.9196 | -0.10216 | 0.0025529 | 0.06053 | 0.10073 | 0.0010253 | 0.0002778 | -0.002884 | -0.0033568 | -0.0024096 | 0.062683 | 0.062331 | -0.018032 | 0.0029095 | 0.00010689 | -0.068665 | 62.883 | -59.5688 | 62.9105 | -59.3536 | -59.729 | 0 | -1.1261 | 62.8555 | -59.5139 | 62.9929 | -59.4498 | -59.5825 | -59.3536 | -0.086975 | -0.036621 | -0.009156 | 0.12817 | 59.4818 | -0.24719 | 59.5688 | -0.16022 | -0.032043 | -0.064087 | 0.073242 | 0.032044 | 0.12817 | -0.10071 | 0.16022 | -0.068665 | 0.21515 | 122.4792 | 0.064087 | 122.5067 | 122.4518 | 122.3694 | 122.3648 | 122.3373 | -122.4884 | -122.4335 | 122.3923 | 122.4747 | 59.4131 | 58.3557
1008.7656 | 122.699 | -59.491 | 62.9242 | -0.094528 | 0.0016983 | 0.061385 | 0.099666 | -0.0036743 | -0.0035674 | -0.0048066 | -0.04303 | -0.00091423 | 0.064179 | 0.06639 | -0.01675 | -8.1274e-05 | 0.00074769 | -0.068665 | 62.8693 | -59.5917 | 62.8922 | -59.3719 | -59.761 | -0.004578 | -1.0117 | 62.8189 | -59.5459 | 62.9654 | -59.4772 | -59.6054 | -59.3719 | -0.10071 | -0.054931 | -0.032043 | 0.11902 | 59.4864 | -0.27008 | 59.5871 | -0.16937 | -0.054931 | -0.10529 | 0.041199 | 0.013733 | 0.11902 | -0.11444 | 0.17395 | -0.05951 | 0.21973 | 122.4838 | 0.068664 | 122.5113 | 122.4609 | 122.3648 | 122.3602 | 122.3099 | -122.5159 | -122.4701 | 122.3831 | 122.4564 | 59.4223 | 58.4793
1009.7656 | 122.6852 | -59.4452 | 62.9333 | -0.079269 | -0.00022432 | 0.060957 | 0.09753 | -0.0013245 | -0.0033538 | -0.0033112 | -0.033874 | 0.00079477 | 0.063324 | 0.066176 | -0.017605 | 0.00098693 | -0.0024567 | -0.086975 | 62.8738 | -59.5688 | 62.9059 | -59.3582 | -59.729 | -0.022888 | -1.1124 | 62.8555 | -59.491 | 63.002 | -59.4315 | -59.5734 | -59.3491 | -0.1236 | -0.05951 | -0.027466 | 0.086975 | 59.4223 | -0.28381 | 59.5459 | -0.16022 | -0.045777 | -0.07782 | 0.068664 | 0.013732 | 0.09613 | -0.12817 | 0.14191 | -0.082397 | 0.21057 | 122.4747 | 0.059509 | 122.493 | 122.4426 | 122.3465 | 122.319 | 122.3007 | -122.5021 | -122.4243 | 122.3511 | 122.4472 | 59.3582 | 58.3328
1010.7656 | 122.6624 | -59.4589 | 62.915 | -0.13267 | 0.00020288 | 0.061171 | 0.099025 | -0.0013245 | -0.0003632 | -0.0030976 | -0.055237 | -0.001128 | 0.061402 | 0.058913 | -0.017391 | 0.00013253 | 0.0041657 | -0.064087 | 62.883 | -59.5459 | 62.9196 | -59.3399 | -59.7519 | -0.036621 | -1.2131 | 62.8464 | -59.5047 | 62.9791 | -59.4543 | -59.5596 | -59.3491 | -0.086975 | -0.032043 | 0.004578 | 0.11902 | 59.4223 | -0.29297 | 59.5093 | -0.20599 | -0.045777 | -0.068664 | 0.064087 | 0.004577 | 0.10986 | -0.10071 | 0.15564 | -0.054931 | 0.20599 | 122.4655 | 0.050354 | 122.4838 | 122.4289 | 122.3511 | 122.3419 | 122.3053 | -122.4609 | -122.4197 | 122.3785 | 122.438 | 59.3948 | 58.2458
1011.7656 | 122.6532 | -59.4589 | 62.9196 | -0.13267 | 0.0014847 | 0.059889 | 0.10095 | 0.0014527 | 0.0002778 | -0.00096136 | -0.06134 | -0.00027343 | 0.064179 | 0.056563 | -0.018032 | -8.1274e-05 | -0.0037383 | -0.059509 | 62.8326 | -59.5551 | 62.9288 | -59.3353 | -59.7427 | -0.036621 | -1.2772 | 62.8235 | -59.5139 | 62.9974 | -59.4727 | -59.5825 | -59.3582 | -0.096131 | -0.086975 | 0.009155 | 0.1236 | 59.4223 | -0.28381 | 59.5184 | -0.18768 | -0.054932 | -0.096131 | 0.07782 | -0.013733 | 0.10071 | -0.1236 | 0.15564 | -0.068665 | 0.21973 | 122.4838 | 0.041199 | 122.5113 | 122.3877 | 122.3373 | 122.2916 | 122.2824 | -122.4747 | -122.4335 | 122.3877 | 122.4564 | 59.3994 | 58.1818
1012.7656 | 122.7127 | -59.4864 | 62.8876 | -0.13267 | 0.00041648 | 0.061812 | 0.098384 | -0.0026063 | -0.0031402 | -0.0013886 | -0.030823 | 0.001222 | 0.063965 | 0.056777 | -0.015682 | 0.0020551 | -0.00010671 | -0.050354 | 62.8647 | -59.5734 | 62.9196 | -59.3491 | -59.7382 | 0.004578 | -1.0483 | 62.851 | -59.5276 | 62.9654 | -59.4452 | -59.5642 | -59.3536 | -0.086975 | -0.022888 | 0.032044 | 0.13733 | 59.491 | -0.25177 | 59.5779 | -0.1648 | -0.041199 | -0.036621 | 0.07782 | 0.041199 | 0.13275 | -0.07782 | 0.17395 | -0.036621 | 0.2243 | 122.493 | 0.082398 | 122.493 | 122.438 | 122.3785 | 122.3511 | 122.3373 | -122.4609 | -122.4152 | 122.406 | 122.4518 | 59.436 | 58.4381
1013.7656 | 122.6852 | -59.4635 | 62.9196 | -0.10216 | -0.0015061 | 0.062025 | 0.10052 | -0.0026063 | -0.0033538 | 0.00053404 | -0.033874 | -0.0026232 | 0.061188 | 0.062331 | -0.01675 | 0.00034613 | -0.0041657 | -0.059509 | 62.9013 | -59.5276 | 62.915 | -59.3582 | -59.7244 | 0 | -1.0117 | 62.851 | -59.4955 | 62.9837 | -59.4406 | -59.5779 | -59.3399 | -0.064087 | -0.018311 | -0.004578 | 0.10529 | 59.4635 | -0.26093 | 59.5276 | -0.19684 | -0.032043 | -0.068665 | 0.064087 | 0.022888 | 0.1236 | -0.11444 | 0.15564 | -0.082398 | 0.16937 | 122.4426 | 0.054931 | 122.4792 | 122.4289 | 122.3465 | 122.3648 | 122.3145 | -122.4472 | -122.4152 | 122.3785 | 122.4472 | 59.404 | 58.4518
1014.7656 | 122.6898 | -59.4681 | 62.9471 | -0.13267 | 0.0019119 | 0.060744 | 0.09753 | -0.0036743 | -0.0033538 | -0.0013886 | -0.049133 | -0.002196 | 0.063751 | 0.063826 | -0.017391 | 0.0012005 | -0.0016021 | -0.059509 | 62.8784 | -59.5413 | 62.9059 | -59.3628 | -59.7427 | -0.004578 | -0.94757 | 62.8464 | -59.5322 | 62.9654 | -59.4315 | -59.5734 | -59.3582 | -0.073242 | -0.068665 | -0.041199 | 0.10529 | 59.4635 | -0.27466 | 59.5367 | -0.20142 | -0.064087 | -0.10071 | 0.01831 | 0.036621 | 0.10986 | -0.10528 | 0.17395 | -0.041198 | 0.17853 | 122.4472 | 0.10071 | 122.4976 | 122.4197 | 122.3785 | 122.3465 | 122.3145 | -122.4884 | -122.4792 | 122.374 | 122.4335 | 59.4086 | 58.5205
1015.7656 | 122.6898 | -59.491 | 62.9242 | 0.019913 | -0.00065152 | 0.063094 | 0.099025 | 0.0029479 | -0.0035674 | -0.002884 | -0.0033568 | -0.00091423 | 0.061615 | 0.056777 | -0.01675 | 0.0031231 | 0.00053409 | -0.14648 | 62.8464 | -59.5734 | 62.8693 | -59.404 | -59.7702 | -0.018311 | -0.97504 | 62.8006 | -59.5322 | 62.9471 | -59.4727 | -59.5871 | -59.3811 | -0.082397 | -0.077819 | -0.054931 | 0.086975 | 59.4727 | -0.27924 | 59.5551 | -0.19684 | -0.041199 | -0.1236 | 0.022889 | 0.018311 | 0.10986 | -0.09613 | 0.15106 | -0.054931 | 0.16937 | 122.4426 | 0.05951 | 122.4792 | 122.4197 | 122.3328 | 122.3373 | 122.2916 | -122.4976 | -122.4564 | 122.3602 | 122.4381 | 59.3445 | 58.5159
1016.7656 | 122.7081 | -59.523 | 62.9105 | -0.11742 | 0.0027665 | 0.060744 | 0.09753 | -0.0017517 | -0.0018586 | -0.0016022 | -0.055237 | 0.001222 | 0.065674 | 0.060622 | -0.016964 | 0.0039777 | 0.00053409 | -0.064087 | 62.8326 | -59.5734 | 62.8418 | -59.3948 | -59.7885 | -0.045776 | -1.0803 | 62.8189 | -59.5688 | 62.9379 | -59.491 | -59.61 | -59.3948 | -0.050354 | -0.077819 | -0.068664 | 0.12817 | 59.4772 | -0.2655 | 59.5276 | -0.21515 | -0.045777 | -0.091552 | 0.027466 | 0.032043 | 0.12817 | -0.086975 | 0.17395 | -0.041198 | 0.17853 | 122.4152 | 0.07782 | 122.5067 | 122.406 | 122.3877 | 122.3557 | 122.3419 | -122.4838 | -122.4792 | 122.3648 | 122.4609 | 59.4589 | 58.4427
1017.7656 | 122.6807 | -59.491 | 62.9791 | -0.07164 | -0.00065152 | 0.062666 | 0.10202 | -4.2682e-05 | -0.0022858 | -0.00053396 | -0.11017 | 0.00015377 | 0.062042 | 0.062331 | -0.01675 | 0.0016277 | -0.0035247 | -0.018311 | 62.9242 | -59.5779 | 62.9013 | -59.4131 | -59.7565 | -0.013733 | -0.97504 | 62.9105 | -59.5276 | 62.9562 | -59.4681 | -59.6283 | -59.3903 | -0.086975 | -0.054932 | -0.07782 | 0.07782 | 59.4772 | -0.2655 | 59.5642 | -0.17853 | -0.036621 | -0.068665 | -0.022888 | 0.022888 | 0.10071 | -0.13733 | 0.13733 | -0.10071 | 0.16479 | 122.4792 | 0.059509 | 122.4838 | 122.5021 | 122.438 | 122.4152 | 122.4014 | -122.5571 | -122.5067 | 122.3923 | 122.4472 | 59.4727 | 58.5159
1018.7656 | 122.6852 | -59.5047 | 62.915 | -0.14793 | 0.0010575 | 0.060744 | 0.10052 | -4.2682e-05 | 6.4004e-05 | 0.0018158 | -0.070496 | 0.0010084 | 0.065033 | 0.057631 | -0.017178 | 0.0026959 | -0.0018157 | -0.054932 | 62.8326 | -59.5596 | 62.9196 | -59.3262 | -59.7702 | -0.036621 | -0.84686 | 62.8235 | -59.5505 | 62.9745 | -59.4727 | -59.6191 | -59.3811 | -0.054931 | -0.082397 | 0.004578 | 0.17853 | 59.4681 | -0.2655 | 59.523 | -0.21057 | -0.045776 | -0.091553 | 0.059509 | 0.032044 | 0.1236 | -0.11444 | 0.16937 | -0.068665 | 0.23346 | 122.4792 | 0.07782 | 122.525 | 122.3923 | 122.374 | 122.3373 | 122.3282 | -122.4747 | -122.4655 | 122.4243 | 122.4792 | 59.4498 | 58.6578
1019.7656 | 122.699 | -59.5047 | 62.9059 | -0.07164 | 0.0023391 | 0.060957 | 0.099239 | -0.0026063 | -0.0031402 | -0.0013886 | -0.024719 | 0.001222 | 0.064179 | 0.057631 | -0.015896 | 0.0024823 | -0.0026703 | -0.050354 | 62.851 | -59.5688 | 62.8693 | -59.3674 | -59.7702 | -0.041199 | -0.78735 | 62.8235 | -59.5276 | 62.9654 | -59.4681 | -59.6054 | -59.3811 | -0.064087 | -0.054932 | -0.036621 | 0.13733 | 59.4635 | -0.2655 | 59.5276 | -0.20142 | -0.022888 | -0.082398 | 0.059509 | 0.036621 | 0.1236 | -0.10071 | 0.14648 | -0.07782 | 0.20142 | 122.4381 | 0.059509 | 122.493 | 122.4197 | 122.3511 | 122.3557 | 122.3282 | -122.4747 | -122.4335 | 122.374 | 122.4701 | 59.4543 | 58.7173
1020.7656 | 122.6807 | -59.5047 | 62.9242 | -0.094528 | 0.0023391 | 0.059248 | 0.097957 | 0.0018799 | 0.000705 | -0.002884 | -0.021667 | 0.00058097 | 0.063965 | 0.063399 | -0.017391 | 0.0022687 | -0.00053411 | 0.064087 | 62.883 | -59.5276 | 62.8647 | -59.3765 | -59.7885 | -0.054932 | -0.85144 | 62.8418 | -59.5596 | 62.9517 | -59.491 | -59.6008 | -59.3811 | -0.022888 | -0.041198 | -0.059509 | 0.12817 | 59.4498 | -0.28381 | 59.4727 | -0.26093 | -0.054931 | -0.082397 | 0.027466 | 0.013733 | 0.1236 | -0.09613 | 0.17853 | -0.041199 | 0.15106 | 122.3923 | 0.068664 | 122.5113 | 122.4106 | 122.4014 | 122.3877 | 122.3465 | -122.4518 | -122.4838 | 122.3694 | 122.4564 | 59.5688 | 58.6533
1021.7656 | 122.699 | -59.4864 | 62.915 | -0.12505 | -0.00022432 | 0.061385 | 0.09817 | 0.0010253 | -0.0018586 | -0.0041656 | -0.039978 | 0.0010084 | 0.06482 | 0.065535 | -0.018886 | 0.0020551 | -0.00096131 | -0.064087 | 62.8647 | -59.5596 | 63.0157 | -59.2346 | -59.9442 | -0.073242 | -0.92926 | 62.8464 | -59.5551 | 62.9562 | -59.4772 | -59.61 | -59.3765 | -0.073242 | -0.050354 | 0.10071 | 0.25177 | 59.4131 | -0.45776 | 59.4864 | -0.38452 | -0.068665 | -0.068664 | 0.041199 | 0.009155 | 0.10986 | -0.1236 | 0.17853 | -0.054931 | 0.32501 | 122.5754 | 0.07782 | 122.5113 | 122.4243 | 122.4014 | 122.3511 | 122.3328 | -122.4747 | -122.4701 | 122.5021 | 122.4426 | 59.4223 | 58.5571
1022.7656 | 122.6212 | -59.4406 | 62.9974 | -0.07164 | 0.0016983 | 0.059248 | 0.098384 | -0.0021789 | -0.0029266 | -0.0018158 | -0.091858 | 0.0010084 | 0.061402 | 0.06404 | -0.015896 | 0.0039777 | -0.00032051 | 0.17853 | 62.9837 | -59.5184 | 62.8418 | -59.4086 | -59.7473 | -0.027466 | -0.84228 | 62.9471 | -59.5139 | 62.9242 | -59.5047 | -59.642 | -59.3994 | -0.07782 | -0.013733 | -0.15564 | 0.032044 | 59.4131 | -0.3067 | 59.491 | -0.22888 | -0.073242 | -0.050354 | -0.073243 | -0.064087 | 0.041199 | -0.20142 | 0.11444 | -0.12817 | 0.10986 | 122.3602 | 0.009155 | 122.438 | 122.5021 | 122.4609 | 122.4243 | 122.3877 | -122.5159 | -122.5113 | 122.2824 | 122.3648 | 59.6191 | 58.5983
1023.7656 | 122.6715 | -59.4681 | 62.9013 | -0.12505 | 0.00041648 | 0.062239 | 0.09817 | -0.00068368 | -0.0035674 | -0.0013886 | -0.030823 | 0.00036737 | 0.065033 | 0.055068 | -0.016323 | 0.0012005 | -0.0041657 | -0.091553 | 62.8418 | -59.5505 | 62.8922 | -59.3765 | -59.7427 | -0.036621 | -0.97046 | 62.8372 | -59.5184 | 63.0524 | -59.3719 | -59.7153 | -59.4177 | -0.082397 | -0.059509 | -0.009155 | 0.091553 | 59.4315 | -0.27466 | 59.5139 | -0.19226 | -0.050354 | -0.064087 | 0.15106 | 0.096131 | 0.050354 | -0.24719 | 0.10071 | -0.19684 | 0.17395 | 122.4426 | 0.14648 | 122.5708 | 122.3923 | 122.3557 | 122.3099 | 122.3053 | -122.4518 | -122.4197 | 122.3602 | 122.5204 | 59.3765 | 58.4976
1024.7656 | 122.6761 | -59.4772 | 62.8922 | -0.13267 | -0.00065152 | 0.061171 | 0.09817 | -0.0030335 | -0.0005768 | -0.0018158 | -0.052185 | 0.00079477 | 0.065674 | 0.057418 | -0.018032 | 0.0018413 | 0.00010689 | -0.041199 | 62.8235 | -59.5779 | 62.9333 | -59.3353 | -59.7519 | -0.013733 | -0.99335 | 62.796 | -59.5276 | 62.9654 | -59.4772 | -59.6008 | -59.3765 | -0.10071 | -0.068665 | 0.041199 | 0.14191 | 59.4635 | -0.27466 | 59.5642 | -0.17395 | -0.050354 | -0.09613 | 0.073242 | 0 | 0.10071 | -0.1236 | 0.15106 | -0.073242 | 0.24262 | 122.5113 | 0.050354 | 122.493 | 122.4014 | 122.3236 | 122.3007 | 122.2733 | -122.4701 | -122.4197 | 122.4106 | 122.4426 | 59.436 | 58.4839
1025.7656 | 122.6624 | -59.5093 | 62.8922 | -0.094528 | -0.00065152 | 0.063307 | 0.098384 | -0.00089728 | -0.0012176 | -0.001175 | -0.046081 | 0.0018628 | 0.06482 | 0.060408 | -0.015041 | 0.00077333 | 0.00010689 | -0.082397 | 62.851 | -59.5596 | 62.9059 | -59.3582 | -59.7656 | -0.036621 | -1.0666 | 62.8189 | -59.5596 | 62.9562 | -59.4681 | -59.6146 | -59.3765 | -0.050354 | -0.041199 | 0.013733 | 0.15106 | 59.4727 | -0.25635 | 59.523 | -0.20599 | -0.050354 | -0.073242 | 0.064087 | 0.041198 | 0.13275 | -0.10529 | 0.18311 | -0.054932 | 0.20142 | 122.4655 | 0.091552 | 122.5159 | 122.4106 | 122.3785 | 122.3602 | 122.3282 | -122.4518 | -122.4518 | 122.4152 | 122.4655 | 59.4269 | 58.4427
1026.7656 | 122.699 | -59.4864 | 62.9288 | -0.086899 | 0.00084388 | 0.062453 | 0.098598 | -0.0026063 | -0.0005768 | -0.0013886 | -0.067444 | 0.0016492 | 0.063965 | 0.063185 | -0.01675 | 0.0020551 | 0.0020295 | -0.073242 | 62.8647 | -59.5505 | 62.9013 | -59.2804 | -59.5139 | 0.022888 | -1.0757 | 62.8372 | -59.5413 | 62.9562 | -59.4681 | -59.6146 | -59.3948 | -0.064087 | -0.064087 | -0.027466 | 0.20599 | 59.5093 | -0.027466 | 59.5734 | 0.036621 | -0.054932 | -0.091553 | 0.027466 | 0.01831 | 0.091553 | -0.12817 | 0.14649 | -0.073242 | 0.27008 | 122.4518 | 0.073242 | 122.4976 | 122.4152 | 122.3785 | 122.3511 | 122.3236 | -122.4792 | -122.4701 | 122.3877 | 122.4426 | 59.4131 | 58.4106
1027.7656 | 122.6166 | -59.5047 | 62.9562 | -0.018234 | 0.0023391 | 0.061812 | 0.10009 | -0.0017517 | -0.0059174 | 0.00010684 | -0.13458 | 0.0014356 | 0.062042 | 0.069808 | -0.017391 | 0.00034613 | -0.0018157 | -0.004578 | 62.9105 | -59.5642 | 62.8647 | -59.4269 | -59.7702 | 0 | -1.1124 | 62.9059 | -59.5322 | 62.9517 | -59.5047 | -59.6512 | -59.3857 | -0.059509 | -0.045777 | -0.091553 | 0.07782 | 59.5047 | -0.2655 | 59.5642 | -0.20599 | -0.027466 | -0.050354 | -0.004578 | 0 | 0.11902 | -0.14648 | 0.14648 | -0.11902 | 0.13733 | 122.4289 | 0.027466 | 122.4838 | 122.4747 | 122.4381 | 122.4152 | 122.4106 | -122.5204 | -122.4884 | 122.3694 | 122.4564 | 59.5001 | 58.3923
1028.7656 | 122.6761 | -59.4818 | 62.915 | -0.048752 | 0.0014847 | 0.061385 | 0.098384 | -0.0015381 | -0.0022858 | -0.001175 | -0.021667 | 0.00036737 | 0.063538 | 0.057845 | -0.016323 | -8.1274e-05 | 0.00010689 | -0.091553 | 62.8601 | -59.5642 | 62.9059 | -59.3582 | -59.7519 | -0.036621 | -1.2314 | 62.8189 | -59.523 | 62.9379 | -59.5413 | -59.6146 | -59.3582 | -0.082397 | -0.054932 | -0.009155 | 0.1236 | 59.4452 | -0.27008 | 59.5276 | -0.18768 | -0.041198 | -0.09613 | 0.022888 | -0.059509 | 0.1236 | -0.13275 | 0.16479 | -0.091553 | 0.20599 | 122.4701 | -0.018311 | 122.4609 | 122.4243 | 122.3419 | 122.3419 | 122.3007 | -122.4792 | -122.438 | 122.3877 | 122.4197 | 59.3903 | 58.2504
1029.7656 | 122.7127 | -59.4498 | 62.9379 | -0.086899 | -0.00065152 | 0.062025 | 0.099452 | -0.0034607 | -0.0003632 | -0.0013886 | -0.015564 | -0.00070063 | 0.065033 | 0.060622 | -0.017818 | 0.00034613 | 0.00074769 | -0.091553 | 62.8601 | -59.5505 | 62.9196 | -59.3399 | -59.7244 | -0.032043 | -1.3229 | 62.851 | -59.4955 | 62.9974 | -59.5001 | -59.3536 | -59.1614 | -0.10071 | -0.07782 | -0.01831 | 0.10986 | 59.4177 | -0.27466 | 59.5184 | -0.17395 | -0.045776 | -0.086975 | 0.05951 | -0.050354 | 0.28839 | 0.09613 | 0.33417 | 0.14191 | 0.21057 | 122.4701 | -0.004578 | 122.493 | 122.4106 | 122.3465 | 122.3099 | 122.3007 | -122.4884 | -122.4335 | 122.3694 | 122.4472 | 59.3582 | 58.1268
1030.7656 | 122.7081 | -59.4772 | 62.9059 | -0.12505 | 0.0014847 | 0.062453 | 0.10009 | 0.00059812 | -0.0016448 | -0.002243 | -0.06134 | -5.9826e-05 | 0.064179 | 0.057631 | -0.01675 | 0.0018413 | -0.0013885 | -0.050354 | 62.8555 | -59.5596 | 62.9379 | -59.317 | -59.7107 | -0.022888 | -1.3504 | 62.8235 | -59.5551 | 62.9974 | -59.4543 | -59.5871 | -59.3308 | -0.082397 | -0.050354 | 0.032043 | 0.16022 | 59.4543 | -0.23346 | 59.5367 | -0.15106 | -0.07782 | -0.082398 | 0.091553 | 0.022888 | 0.14648 | -0.10986 | 0.2243 | -0.032043 | 0.24261 | 122.4976 | 0.10071 | 122.5525 | 122.4152 | 122.3785 | 122.3328 | 122.3007 | -122.4655 | -122.4609 | 122.4152 | 122.4747 | 59.4269 | 58.1268
1031.7656 | 122.6761 | -59.4727 | 62.915 | -0.12505 | -0.00065152 | 0.062025 | 0.099879 | 0.0023071 | -0.0007904 | -0.0016022 | -0.070496 | -0.0030506 | 0.064179 | 0.069167 | -0.017605 | 0.0018413 | -0.00053411 | -0.054932 | 62.8693 | -59.5413 | 62.9471 | -59.2941 | -59.7107 | -0.027466 | -1.3962 | 62.8143 | -59.5276 | 63.002 | -59.4452 | -59.5642 | -59.3445 | -0.068665 | -0.045776 | 0.032044 | 0.17853 | 59.4452 | -0.23804 | 59.5139 | -0.16937 | -0.054932 | -0.10071 | 0.086975 | 0.027466 | 0.12817 | -0.091553 | 0.18311 | -0.036621 | 0.24719 | 122.4884 | 0.082398 | 122.5296 | 122.4106 | 122.3419 | 122.3419 | 122.287 | -122.4564 | -122.4426 | 122.4197 | 122.4747 | 59.4177 | 58.0765
1032.7656 | 122.6166 | -59.4543 | 63.0112 | -0.0029755 | 0.00084388 | 0.060316 | 0.10372 | -0.0034607 | -0.0039948 | 0.001175 | -0.079651 | 0.00079477 | 0.065033 | 0.060836 | -0.016537 | 0.0022687 | 0.0011749 | -0.022888 | 62.9517 | -59.5505 | 62.8876 | -59.3903 | -59.7519 | 0.004578 | -1.387 | 62.915 | -59.5184 | 62.9471 | -59.5001 | -59.6237 | -59.3903 | -0.09613 | -0.059509 | -0.1236 | 0.064087 | 59.4589 | -0.29755 | 59.5551 | -0.20142 | -0.064087 | -0.09613 | -0.064086 | -0.045776 | 0.064087 | -0.16937 | 0.12817 | -0.10528 | 0.16022 | 122.438 | 0.018311 | 122.4655 | 122.5021 | 122.4335 | 122.406 | 122.3694 | -122.5616 | -122.5296 | 122.3419 | 122.4014 | 59.4315 | 58.0673
1033.7656 | 122.7127 | -59.4635 | 62.9288 | -0.11742 | 0.0012711 | 0.058607 | 0.098384 | -4.2682e-05 | -0.0005768 | -0.0041656 | -0.00030524 | -0.001128 | 0.064606 | 0.061476 | -0.015682 | 0.0024823 | 0.00010689 | 0.059509 | 62.9013 | -59.5596 | 62.8784 | -59.3445 | -59.7519 | -0.036621 | -1.4786 | 62.8326 | -59.5505 | 62.9791 | -59.4589 | -59.5963 | -59.3582 | -0.09613 | -0.027466 | -0.050354 | 0.11902 | 59.4269 | -0.28839 | 59.523 | -0.19226 | -0.086975 | -0.09613 | 0.050354 | 0.004578 | 0.10529 | -0.13275 | 0.19226 | -0.045776 | 0.21515 | 122.438 | 0.091553 | 122.5296 | 122.4609 | 122.3831 | 122.3648 | 122.2961 | -122.4884 | -122.4792 | 122.3419 | 122.4426 | 59.523 | 57.9849
1034.7656 | 122.6944 | -59.4818 | 62.915 | -0.10216 | -0.00065152 | 0.060744 | 0.10052 | -0.0011109 | -0.0012176 | -0.0026704 | -0.036926 | -0.00027343 | 0.063538 | 0.054427 | -0.01675 | 0.00055973 | 0.00010689 | -0.073242 | 62.8738 | -59.5505 | 62.915 | -59.3857 | -59.7794 | -0.022888 | -1.4511 | 62.8052 | -59.5184 | 62.9654 | -59.4681 | -59.6191 | -59.3628 | -0.068664 | -0.041199 | 0 | 0.096131 | 59.4589 | -0.29755 | 59.5276 | -0.22888 | -0.036621 | -0.10986 | 0.050354 | 0.013733 | 0.11902 | -0.13733 | 0.15564 | -0.10071 | 0.1648 | 122.4655 | 0.050354 | 122.4838 | 122.4243 | 122.3236 | 122.3557 | 122.287 | -122.4655 | -122.4335 | 122.3969 | 122.4472 | 59.4086 | 58.0307
1035.7656 | 122.6944 | -59.4681 | 62.9105 | -0.10979 | -0.00043792 | 0.059889 | 0.09817 | -0.0062379 | -0.0052764 | -0.002243 | -0.033874 | -0.00048703 | 0.063538 | 0.056777 | -0.016537 | 0.0018413 | -0.0013885 | -0.064087 | 62.8601 | -59.5505 | 62.8326 | -59.4406 | -59.7336 | -0.045776 | -1.4008 | 62.8418 | -59.5322 | 62.9745 | -59.4727 | -59.5963 | -59.3536 | -0.082397 | -0.050354 | -0.077819 | 0.027466 | 59.4223 | -0.2655 | 59.5047 | -0.18311 | -0.064087 | -0.068664 | 0.064087 | -0.004577 | 0.11444 | -0.12817 | 0.17853 | -0.064086 | 0.10986 | 122.3831 | 0.05951 | 122.5067 | 122.4106 | 122.374 | 122.3282 | 122.3099 | -122.4609 | -122.4426 | 122.3007 | 122.4426 | 59.404 | 58.0673
1036.7656 | 122.6898 | -59.4864 | 62.9425 | -0.094528 | 0.00063028 | 0.061385 | 0.099239 | -0.0030335 | -0.0022858 | 0.00032044 | -0.027771 | 0.00015377 | 0.063111 | 0.064467 | -0.017391 | 0.0014141 | -0.0035247 | -0.086975 | 62.8738 | -59.5596 | 62.9059 | -59.1522 | -59.6008 | -0.11444 | -1.3962 | 62.8326 | -59.5367 | 62.9562 | -59.4589 | -59.6054 | -59.3582 | -0.073242 | -0.068665 | -0.036621 | 0.33417 | 59.3719 | -0.11444 | 59.4452 | -0.041199 | -0.050354 | -0.10986 | 0.013733 | 0.027466 | 0.12817 | -0.11902 | 0.17853 | -0.068665 | 0.40741 | 122.4655 | 0.07782 | 122.493 | 122.4335 | 122.3694 | 122.3602 | 122.319 | -122.5021 | -122.4792 | 122.3923 | 122.4426 | 59.3994 | 58.0902
1037.7656 | 122.6669 | -59.4772 | 62.8922 | -0.12505 | -1.0718e-05 | 0.06053 | 0.10095 | 0.00017092 | -0.0016448 | -0.00053396 | -0.064392 | 0.001222 | 0.068238 | 0.062331 | -0.018032 | 0.00077333 | -0.0033111 | -0.064087 | 62.8693 | -59.5505 | 62.9242 | -59.3308 | -59.7519 | -0.022888 | -1.4191 | 62.851 | -59.5001 | 62.9608 | -59.4727 | -59.6146 | -59.3811 | -0.073242 | -0.022888 | 0.032043 | 0.14648 | 59.4543 | -0.27466 | 59.5276 | -0.20142 | -0.022888 | -0.041199 | 0.068664 | 0.004578 | 0.09613 | -0.13733 | 0.11902 | -0.11444 | 0.21973 | 122.4747 | 0.027466 | 122.4609 | 122.4197 | 122.3511 | 122.3465 | 122.3282 | -122.4426 | -122.3923 | 122.4014 | 122.438 | 59.4131 | 58.0582
1038.7656 | 122.6624 | -59.4772 | 62.9196 | -0.12505 | 0.0016983 | 0.061171 | 0.098598 | 0.0023071 | 0.0002778 | -0.0024566 | -0.058289 | -0.0017688 | 0.061615 | 0.058058 | -0.01675 | 0.0033367 | -0.0024567 | -0.064087 | 62.8647 | -59.5734 | 62.9379 | -59.3216 | -59.7336 | -0.027466 | -1.3046 | 62.8372 | -59.5184 | 62.9837 | -59.4681 | -59.5917 | -59.3582 | -0.09613 | -0.054932 | 0.01831 | 0.15564 | 59.4498 | -0.25635 | 59.5459 | -0.16022 | -0.041199 | -0.082398 | 0.064087 | 0.009155 | 0.11902 | -0.11444 | 0.16022 | -0.073242 | 0.25177 | 122.5113 | 0.050354 | 122.5021 | 122.438 | 122.3557 | 122.3419 | 122.3145 | -122.493 | -122.4381 | 122.4152 | 122.4609 | 59.4131 | 58.1726
1039.7656 | 122.6715 | -59.491 | 62.9288 | -0.10216 | 0.0019119 | 0.06053 | 0.1018 | -0.0019653 | -0.0033538 | 0.00053404 | -0.018616 | -0.00070063 | 0.064606 | 0.058272 | -0.015896 | -0.00072207 | -0.0045929 | -0.10071 | 62.8738 | -59.5596 | 62.883 | -59.3765 | -59.7565 | -0.036621 | -1.4465 | 62.8372 | -59.5459 | 63.1348 | -59.6558 | -59.642 | -59.3903 | -0.068664 | -0.054932 | -0.045776 | 0.11444 | 59.4543 | -0.2655 | 59.523 | -0.19684 | -0.054931 | -0.091553 | 0.20599 | -0.1648 | 0.10071 | -0.15106 | 0.15564 | -0.096131 | 0.18311 | 122.4426 | -0.10986 | 122.6807 | 122.4335 | 122.3831 | 122.3648 | 122.3282 | -122.4884 | -122.4747 | 122.374 | 122.6257 | 59.3903 | 58.0444
1040.7656 | 122.6852 | -59.4681 | 62.9059 | -0.079269 | -0.0021469 | 0.063094 | 0.099666 | -0.0011109 | -0.0035674 | -0.00010676 | -0.024719 | -0.001128 | 0.063751 | 0.056349 | -0.017818 | 0.0037641 | 0.0016021 | -0.064087 | 62.8784 | -59.5734 | 62.8876 | -59.3719 | -59.761 | -0.018311 | -1.4832 | 62.8143 | -59.5184 | 62.9562 | -59.4543 | -59.5917 | -59.3674 | -0.10528 | -0.027466 | -0.018311 | 0.096131 | 59.4498 | -0.29297 | 59.5551 | -0.18768 | -0.050354 | -0.091553 | 0.050354 | 0.013733 | 0.10071 | -0.1236 | 0.15106 | -0.073242 | 0.20142 | 122.4609 | 0.064087 | 122.4747 | 122.4518 | 122.3328 | 122.3465 | 122.2824 | -122.4792 | -122.4243 | 122.3557 | 122.4243 | 59.404 | 57.9849
1041.7656 | 122.6715 | -59.4681 | 62.9333 | -0.041122 | 0.00084388 | 0.064375 | 0.099452 | -0.00089728 | -0.0020722 | -0.0024566 | -0.039978 | 0.00036737 | 0.065247 | 0.060622 | -0.017178 | -8.1274e-05 | -0.00032051 | -0.10071 | 62.8738 | -59.5642 | 62.9105 | -59.3903 | -59.7565 | -0.022888 | -1.4832 | 62.8235 | -59.5322 | 62.9745 | -59.4543 | -59.5871 | -59.3765 | -0.09613 | -0.05951 | -0.022889 | 0.07782 | 59.4452 | -0.28839 | 59.5413 | -0.19226 | -0.064087 | -0.10986 | 0.041198 | 0.013733 | 0.091553 | -0.11902 | 0.15564 | -0.054931 | 0.17395 | 122.4747 | 0.07782 | 122.5067 | 122.438 | 122.3557 | 122.3419 | 122.2916 | -122.4976 | -122.4655 | 122.3785 | 122.4426 | 59.3674 | 57.9849
1042.7656 | 122.6624 | -59.4818 | 62.915 | -0.06401 | 0.0027665 | 0.062239 | 0.098598 | -0.0011109 | -0.0014312 | -0.0013886 | -0.021667 | -0.0019824 | 0.063538 | 0.058058 | -0.018032 | -0.00029487 | 0.00032049 | -0.07782 | 62.8738 | -59.5642 | 62.8052 | -59.4086 | -59.7473 | -0.045776 | -1.5701 | 62.8372 | -59.5551 | 62.9654 | -59.4818 | -59.6054 | -59.3582 | -0.082397 | -0.041199 | -0.10986 | 0.073243 | 59.436 | -0.2655 | 59.5184 | -0.18311 | -0.073242 | -0.07782 | 0.050354 | 0 | 0.1236 | -0.1236 | 0.19684 | -0.050354 | 0.15564 | 122.3694 | 0.073242 | 122.5204 | 122.438 | 122.3923 | 122.3557 | 122.319 | -122.4792 | -122.4701 | 122.287 | 122.4472 | 59.404 | 57.9117
1043.7656 | 122.6761 | -59.4635 | 62.9333 | -0.15556 | 0.00041648 | 0.061598 | 0.10031 | 0.0023071 | -0.0018586 | -0.00096136 | 0.021057 | 0.00036737 | 0.062256 | 0.062545 | -0.018032 | 0.00013253 | -0.0011749 | -0.07782 | 62.8738 | -59.5505 | 62.915 | -59.3765 | -59.7382 | -0.027466 | -1.6525 | 62.8418 | -59.523 | 62.9745 | -59.491 | -59.61 | -59.3719 | -0.086975 | -0.05951 | -0.018311 | 0.086975 | 59.436 | -0.27466 | 59.523 | -0.18768 | -0.059509 | -0.091553 | 0.041198 | -0.027466 | 0.091553 | -0.14648 | 0.15106 | -0.086975 | 0.17395 | 122.4655 | 0.032043 | 122.4976 | 122.4243 | 122.3648 | 122.3373 | 122.3053 | -122.4838 | -122.4564 | 122.3785 | 122.438 | 59.3857 | 57.811
1044.7656 | 122.6898 | -59.4727 | 62.9013 | -0.094528 | 0.00084388 | 0.06288 | 0.10223 | 0.0046569 | -0.0016448 | -0.0037384 | -0.052185 | -0.0015552 | 0.066315 | 0.062972 | -0.017391 | 0.0016277 | -0.00010671 | -0.050354 | 62.8738 | -59.5551 | 62.9425 | -59.3079 | -59.7382 | -0.036621 | -1.6251 | 62.8143 | -59.5413 | 62.9929 | -59.4543 | -59.5917 | -59.3536 | -0.082398 | -0.027466 | 0.041199 | 0.16479 | 59.436 | -0.2655 | 59.5184 | -0.18311 | -0.068665 | -0.086975 | 0.091553 | 0.01831 | 0.11902 | -0.11902 | 0.18768 | -0.050354 | 0.24719 | 122.4976 | 0.086975 | 122.5342 | 122.4289 | 122.3557 | 122.3465 | 122.287 | -122.4564 | -122.4426 | 122.4152 | 122.4655 | 59.4223 | 57.8476
1045.7656 | 122.7127 | -59.4177 | 62.9562 | -0.15556 | 0.0036209 | 0.063094 | 0.10116 | 0.0031617 | -0.0018586 | -0.0026704 | -0.064392 | 0.00079477 | 0.065888 | 0.061263 | -0.0191 | 0.00077333 | 0.0016021 | -0.068665 | 62.8967 | -59.5047 | 62.9837 | -59.2621 | -59.6878 | -0.027466 | -1.6617 | 62.851 | -59.4772 | 63.0386 | -59.3948 | -59.5551 | -59.2987 | -0.086975 | -0.059509 | 0.027466 | 0.15564 | 59.3903 | -0.27008 | 59.4772 | -0.1831 | -0.059509 | -0.10529 | 0.082397 | 0.022889 | 0.11902 | -0.13733 | 0.17853 | -0.07782 | 0.24262 | 122.4884 | 0.082398 | 122.5159 | 122.4014 | 122.3282 | 122.3145 | 122.2687 | -122.4609 | -122.4335 | 122.4014 | 122.4564 | 59.3491 | 57.756
1046.7656 | 122.6715 | -59.4406 | 62.9471 | -0.07164 | 0.0019119 | 0.062025 | 0.099879 | 0.00017092 | 0.0022004 | -0.0016022 | -0.030823 | -0.00048703 | 0.06482 | 0.062117 | -0.015255 | 0.0020551 | -0.0039521 | -0.086975 | 62.9013 | -59.4955 | 62.97 | -59.2941 | -59.7107 | -0.036621 | -1.799 | 62.8967 | -59.5001 | 63.0157 | -59.4269 | -59.5551 | -59.3079 | -0.054931 | -0.045777 | 0.022888 | 0.14648 | 59.404 | -0.27008 | 59.4589 | -0.21515 | -0.059509 | -0.050354 | 0.068664 | 0.013733 | 0.13275 | -0.11444 | 0.19226 | -0.054932 | 0.20142 | 122.4655 | 0.073242 | 122.5159 | 122.3969 | 122.3969 | 122.3419 | 122.3373 | -122.4426 | -122.4472 | 122.4106 | 122.4564 | 59.3536 | 57.6416
1047.7656 | 122.6624 | -59.436 | 62.9562 | -0.12505 | -0.00065152 | 0.060103 | 0.10052 | -0.0041015 | -0.0012176 | -0.002884 | 0.10651 | -0.001128 | 0.064392 | 0.053786 | -0.016323 | 0.0024823 | -0.0028839 | -0.082397 | 62.9333 | -59.5139 | 62.9608 | -59.317 | -59.697 | -0.036621 | -1.9363 | 62.9059 | -59.4681 | 63.0157 | -59.436 | -59.5505 | -59.3079 | -0.07782 | -0.022888 | 0.004577 | 0.11902 | 59.3994 | -0.26093 | 59.4772 | -0.1831 | -0.032044 | -0.050354 | 0.059509 | 0 | 0.12817 | -0.11444 | 0.16022 | -0.082397 | 0.19684 | 122.4747 | 0.032044 | 122.4838 | 122.4472 | 122.374 | 122.3694 | 122.3419 | -122.4701 | -122.4243 | 122.3969 | 122.4518 | 59.3536 | 57.4997
1048.7656 | 122.6578 | -59.436 | 62.9745 | -0.13267 | 0.00020288 | 0.062666 | 0.099666 | -0.0047425 | -0.0024994 | -0.0035248 | -0.052185 | -0.00070063 | 0.063751 | 0.057418 | -0.018246 | 0.0014141 | -0.0028839 | -0.09613 | 62.9105 | -59.5184 | 62.9471 | -59.317 | -59.697 | -0.045776 | -1.8631 | 62.883 | -59.4955 | 63.0066 | -59.2163 | -59.4818 | -59.404 | -0.082398 | -0.064087 | -0.027465 | 0.11902 | 59.3903 | -0.26093 | 59.4727 | -0.17853 | -0.059509 | -0.091552 | 0.032044 | 0.21973 | 0.032043 | -0.045777 | 0.091552 | 0.013732 | 0.20142 | 122.4655 | 0.27923 | 122.5021 | 122.4289 | 122.3785 | 122.3465 | 122.319 | -122.493 | -122.4701 | 122.3831 | 122.4426 | 59.3399 | 57.5729
1049.7656 | 122.6715 | -59.436 | 62.9837 | -0.079269 | 0.0021255 | 0.062453 | 0.10095 | -0.00046988 | -0.0037812 | 0.00032044 | -0.052185 | 0.00015377 | 0.064606 | 0.06639 | -0.016964 | 0.0022687 | -0.0011749 | -0.09613 | 62.915 | -59.5001 | 62.9517 | -59.3033 | -59.697 | -0.054932 | -1.8997 | 62.9196 | -59.4864 | 63.0295 | -59.3903 | -59.5459 | -59.3033 | -0.064087 | -0.068665 | -0.032044 | 0.13275 | 59.3811 | -0.26093 | 59.4452 | -0.19684 | -0.050354 | -0.064087 | 0.045776 | 0.045776 | 0.13275 | -0.10986 | 0.18311 | -0.059509 | 0.19684 | 122.4518 | 0.09613 | 122.5159 | 122.4152 | 122.406 | 122.3511 | 122.3557 | -122.4838 | -122.4701 | 122.3877 | 122.4655 | 59.3399 | 57.5363
1050.7656 | 122.6944 | -59.4177 | 62.9745 | -0.14793 | 0.0014847 | 0.061598 | 0.10159 | -0.0015381 | -0.0037812 | -0.0024566 | -0.036926 | 0.0020764 | 0.064606 | 0.061049 | -0.016323 | 0.0012005 | 0.00053409 | -0.07782 | 62.9288 | -59.491 | 62.9837 | -59.2712 | -59.7015 | -0.045776 | -1.8997 | 62.8876 | -59.4727 | 63.0432 | -59.3994 | -59.5551 | -59.2987 | -0.073242 | -0.045776 | 0.009156 | 0.14648 | 59.3719 | -0.28381 | 59.4452 | -0.21057 | -0.054931 | -0.086975 | 0.068665 | 0.018311 | 0.11902 | -0.13733 | 0.17395 | -0.082398 | 0.21973 | 122.4747 | 0.073242 | 122.5159 | 122.4197 | 122.3602 | 122.3465 | 122.3053 | -122.4655 | -122.4472 | 122.4014 | 122.4609 | 59.3399 | 57.518
1051.7656 | 122.6944 | -59.4315 | 62.9654 | -0.10216 | 0.0010575 | 0.060316 | 0.099879 | -0.0023925 | 0.0004914 | -0.0018158 | -0.064392 | -0.001128 | 0.062256 | 0.055068 | -0.018886 | 0.0022687 | -0.0065155 | -0.054932 | 62.9242 | -59.4864 | 63.0112 | -59.2575 | -59.6603 | -0.041199 | -1.8723 | 62.8738 | -59.4681 | 63.0753 | -59.3628 | -59.5093 | -59.285 | -0.054931 | -0.041199 | 0.045776 | 0.17395 | 59.3903 | -0.22888 | 59.4452 | -0.17395 | -0.036621 | -0.091553 | 0.10986 | 0.068665 | 0.14648 | -0.077819 | 0.18311 | -0.041198 | 0.22888 | 122.4976 | 0.10529 | 122.5433 | 122.4106 | 122.3419 | 122.3557 | 122.3053 | -122.4518 | -122.4335 | 122.4426 | 122.5067 | 59.3765 | 57.5592
1052.7656 | 122.7402 | -59.404 | 62.9791 | -0.20134 | -0.00022432 | 0.062025 | 0.099452 | 0.0010253 | -0.0020722 | -0.00032036 | -0.09491 | -0.0013416 | 0.064179 | 0.057845 | -0.018459 | 0.0024823 | -0.0024567 | 0.027466 | 62.9013 | -59.4955 | 63.0157 | -59.2255 | -59.6191 | -0.059509 | -1.918 | 62.8784 | -59.4589 | 63.0981 | -59.3399 | -59.5047 | -59.2621 | -0.091552 | -0.07782 | 0.036621 | 0.17853 | 59.3445 | -0.21515 | 59.436 | -0.1236 | -0.054931 | -0.10071 | 0.11902 | 0.064087 | 0.14191 | -0.10071 | 0.19684 | -0.045777 | 0.27008 | 122.5113 | 0.11902 | 122.5571 | 122.3969 | 122.3373 | 122.3053 | 122.2824 | -122.4747 | -122.438 | 122.4197 | 122.5021 | 59.4315 | 57.486
1053.7656 | 122.6715 | -59.3948 | 63.0157 | -0.10216 | 0.00020288 | 0.062666 | 0.099452 | -0.0036743 | -0.0007904 | 0.0013886 | -0.021667 | -5.9826e-05 | 0.062897 | 0.060408 | -0.017391 | 0.00077333 | -0.0039521 | -0.091553 | 62.9242 | -59.4681 | 62.9929 | -59.285 | -59.6603 | -0.082397 | -2.0462 | 62.9379 | -59.4543 | 63.0524 | -59.3628 | -59.523 | -59.2758 | -0.073243 | -0.091553 | -0.022888 | 0.10986 | 59.3124 | -0.2655 | 59.3857 | -0.19226 | -0.05951 | -0.07782 | 0.036621 | 0.032043 | 0.11902 | -0.12817 | 0.17853 | -0.068664 | 0.18311 | 122.4609 | 0.091553 | 122.5067 | 122.3923 | 122.3923 | 122.319 | 122.3328 | -122.4838 | -122.4701 | 122.3877 | 122.4472 | 59.3033 | 57.3486
1054.7656 | 122.6761 | -59.3765 | 63.002 | -0.13267 | -0.00022432 | 0.061598 | 0.10137 | 0.00081172 | -0.0014312 | -0.002243 | -0.052185 | 0.00015377 | 0.061402 | 0.066817 | -0.018032 | 0.00098693 | -0.0054473 | -0.082397 | 62.9242 | -59.4772 | 63.0112 | -59.2438 | -59.6512 | -0.059509 | -2.0508 | 62.915 | -59.4406 | 63.0707 | -59.3674 | -59.5093 | -59.2667 | -0.10071 | -0.07782 | 0.009155 | 0.13275 | 59.317 | -0.27466 | 59.4177 | -0.17395 | -0.064087 | -0.086975 | 0.068665 | 0.009155 | 0.10986 | -0.13275 | 0.17395 | -0.068664 | 0.23346 | 122.4884 | 0.073242 | 122.5113 | 122.4014 | 122.3557 | 122.3007 | 122.2916 | -122.4792 | -122.4426 | 122.3877 | 122.4472 | 59.2941 | 57.3257
1055.7656 | 122.699 | -59.3765 | 62.9974 | -0.094528 | 0.00063028 | 0.062453 | 0.10052 | 0.00017092 | -0.0012176 | 0.00032044 | -0.046081 | 0.00079477 | 0.064179 | 0.064894 | -0.018459 | 0.0024823 | -0.0030975 | -0.073242 | 62.9242 | -59.4635 | 63.0157 | -59.2346 | -59.6558 | -0.064087 | -2.1881 | 62.9242 | -59.4452 | 63.0753 | -59.3582 | -59.491 | -59.2712 | -0.086975 | -0.073243 | 0.01831 | 0.14191 | 59.3124 | -0.27924 | 59.3994 | -0.19226 | -0.068664 | -0.073243 | 0.077819 | 0.018311 | 0.10529 | -0.11444 | 0.17395 | -0.045777 | 0.22888 | 122.4792 | 0.086975 | 122.5204 | 122.3877 | 122.3694 | 122.3007 | 122.3007 | -122.4609 | -122.4426 | 122.3923 | 122.4518 | 59.3033 | 57.1884
1056.7656 | 122.6898 | -59.3719 | 63.002 | -0.1403 | 0.0023391 | 0.062666 | 0.10073 | 0.0031617 | -0.0007904 | -0.00053396 | -0.073547 | -0.00048703 | 0.064179 | 0.058486 | -0.018673 | 0.0018413 | -0.0024567 | -0.073242 | 62.9471 | -59.4635 | 63.0478 | -59.2163 | -59.642 | -0.054932 | -2.1744 | 62.9242 | -59.4406 | 63.0753 | -59.3399 | -59.5139 | -59.2758 | -0.091553 | -0.054931 | 0.045777 | 0.15564 | 59.317 | -0.27008 | 59.4086 | -0.17853 | -0.068665 | -0.07782 | 0.073242 | 0.032043 | 0.09613 | -0.14191 | 0.16479 | -0.073242 | 0.24719 | 122.5113 | 0.10071 | 122.5159 | 122.4106 | 122.3648 | 122.319 | 122.2961 | -122.4655 | -122.4426 | 122.4197 | 122.4472 | 59.2987 | 57.1976
1057.7656 | 122.699 | -59.3674 | 63.002 | -0.11742 | 0.00020288 | 0.06288 | 0.10073 | -0.0015381 | -0.0033538 | -0.0024566 | -0.046081 | 0.0010084 | 0.065247 | 0.057845 | -0.017178 | 0.0020551 | -0.00096131 | -0.07782 | 62.9242 | -59.4864 | 63.0386 | -59.2072 | -59.6237 | -0.068665 | -2.1881 | 62.9288 | -59.4452 | 63.0753 | -59.3353 | -59.4772 | -59.2575 | -0.11902 | -0.07782 | 0.036621 | 0.16022 | 59.2987 | -0.25635 | 59.4177 | -0.13733 | -0.077819 | -0.073242 | 0.073242 | 0.032044 | 0.10986 | -0.10986 | 0.18768 | -0.032044 | 0.27924 | 122.525 | 0.10986 | 122.5204 | 122.4106 | 122.374 | 122.2916 | 122.2961 | -122.4884 | -122.4472 | 122.406 | 122.4426 | 59.2896 | 57.1793
1058.7656 | 122.699 | -59.3948 | 62.9929 | -0.048752 | 0.0012711 | 0.061598 | 0.098598 | -0.00046988 | -0.0029266 | -0.0024566 | -0.070496 | -0.00027343 | 0.060761 | 0.06938 | -0.018246 | 0.0014141 | -0.00053411 | -0.054932 | 62.9333 | -59.4818 | 63.1622 | -59.2804 | -59.6558 | -0.045776 | -2.1927 | 62.9059 | -59.4177 | 63.1165 | -59.3308 | -59.4635 | -59.2117 | -0.086976 | -0.059509 | 0.16937 | 0.11444 | 59.3491 | -0.26093 | 59.436 | -0.17395 | -0.022889 | -0.086975 | 0.1236 | 0.064086 | 0.1831 | -0.068665 | 0.20599 | -0.045776 | 0.20142 | 122.644 | 0.086975 | 122.5342 | 122.4152 | 122.3236 | 122.3282 | 122.3007 | -122.4747 | -122.4106 | 122.5571 | 122.5113 | 59.3399 | 57.2021
1059.7656 | 122.7264 | -59.4315 | 62.97 | -0.12505 | -1.0718e-05 | 0.061171 | 0.10052 | -0.0013245 | -0.0014312 | 0.00096124 | -0.11017 | 0.0010084 | 0.063538 | 0.057204 | -0.017178 | 0.0018413 | -0.00010671 | -0.059509 | 62.9288 | -59.4818 | 62.8464 | -59.1751 | -59.3719 | 0.004578 | -2.1652 | 62.8738 | -59.4635 | 63.0753 | -59.3399 | -59.523 | -59.2804 | -0.050354 | -0.041199 | -0.1236 | 0.25635 | 59.436 | 0.05951 | 59.4864 | 0.10986 | -0.032043 | -0.096131 | 0.10529 | 0.091553 | 0.15106 | -0.091552 | 0.1831 | -0.059509 | 0.3067 | 122.3282 | 0.1236 | 122.5388 | 122.4106 | 122.3373 | 122.3602 | 122.3053 | -122.4518 | -122.4335 | 122.2778 | 122.5067 | 59.3719 | 57.2662
1060.7656 | 122.6944 | -59.4131 | 62.9745 | -0.06401 | 0.00020288 | 0.062025 | 0.098811 | -0.0026063 | -0.0022858 | -0.00010676 | -0.021667 | 0.00079477 | 0.064179 | 0.060622 | -0.015682 | 0.0037641 | -0.00010671 | -0.086975 | 62.9013 | -59.5184 | 62.9654 | -59.2804 | -59.697 | -0.07782 | -2.2568 | 62.8738 | -59.491 | 63.0341 | -59.3857 | -59.5413 | -59.2941 | -0.10529 | -0.073242 | -0.009155 | 0.13275 | 59.3353 | -0.28381 | 59.4406 | -0.17853 | -0.07782 | -0.10071 | 0.05951 | 0.027466 | 0.11902 | -0.12817 | 0.19684 | -0.050354 | 0.23804 | 122.4838 | 0.10529 | 122.525 | 122.4197 | 122.3648 | 122.3145 | 122.287 | -122.493 | -122.4655 | 122.3785 | 122.4472 | 59.3262 | 57.1564
1061.7656 | 122.6761 | -59.3903 | 62.97 | -0.1403 | -0.00065152 | 0.061385 | 0.098811 | 0.00081172 | 0.0019866 | -0.0026704 | -0.030823 | 0.0014356 | 0.065674 | 0.065322 | -0.017178 | 0.0012005 | -0.0048065 | -0.082397 | 62.9288 | -59.5047 | 62.97 | -59.2621 | -59.6832 | -0.068665 | -2.3483 | 62.9242 | -59.4589 | 63.0341 | -59.3765 | -59.5322 | -59.2941 | -0.11444 | -0.041199 | 0 | 0.12817 | 59.3216 | -0.29297 | 59.436 | -0.17853 | -0.068664 | -0.045777 | 0.064087 | 0.013733 | 0.096131 | -0.14191 | 0.16479 | -0.073243 | 0.24262 | 122.4747 | 0.082397 | 122.493 | 122.4335 | 122.3831 | 122.319 | 122.3145 | -122.4747 | -122.4289 | 122.3602 | 122.4243 | 59.3079 | 57.0419
1062.7656 | 122.6761 | -59.4131 | 62.9608 | -0.094528 | 0.0010575 | 0.060957 | 0.10009 | -0.0011109 | -0.002713 | -0.00096136 | -0.039978 | -0.002196 | 0.064392 | 0.057631 | -0.016964 | 0.0014141 | -0.0045929 | -0.082397 | 62.915 | -59.4772 | 62.9974 | -59.2392 | -59.6832 | -0.07782 | -2.417 | 62.9105 | -59.4681 | 63.0569 | -59.3765 | -59.5276 | -59.285 | -0.064087 | -0.045776 | 0.036622 | 0.17395 | 59.3353 | -0.27008 | 59.3994 | -0.20599 | -0.054932 | -0.050354 | 0.096131 | 0.036621 | 0.12817 | -0.11444 | 0.18311 | -0.059509 | 0.23804 | 122.4747 | 0.091553 | 122.525 | 122.3923 | 122.3785 | 122.3282 | 122.3236 | -122.438 | -122.4289 | 122.4106 | 122.4701 | 59.3308 | 56.9962
1063.7656 | 122.6669 | -59.3994 | 62.9791 | -0.086899 | -1.0718e-05 | 0.062453 | 0.1018 | 0.0027343 | -0.0029266 | -0.00096136 | -0.049133 | -0.00027343 | 0.063538 | 0.06404 | -0.016109 | 0.0018413 | 0.00032049 | -0.086975 | 62.9333 | -59.4955 | 63.0112 | -59.2529 | -59.6649 | -0.09613 | -2.4353 | 62.9105 | -59.4635 | 63.0341 | -59.3491 | -59.5093 | -59.2804 | -0.09613 | -0.045776 | 0.032043 | 0.14648 | 59.3033 | -0.2655 | 59.3994 | -0.16937 | -0.064087 | -0.068665 | 0.054932 | 0.050354 | 0.11902 | -0.10986 | 0.1831 | -0.045776 | 0.24261 | 122.5067 | 0.11444 | 122.4976 | 122.4289 | 122.374 | 122.3328 | 122.3099 | -122.4747 | -122.4426 | 122.4106 | 122.4335 | 59.3124 | 56.9641
1064.7656 | 122.6852 | -59.3719 | 63.0203 | -0.11742 | -0.0010787 | 0.061385 | 0.10073 | 0.0018799 | -0.0014312 | 0.00053404 | -0.04303 | 0.00036737 | 0.064392 | 0.064467 | -0.016323 | 0.0022687 | 0.00074769 | -0.082397 | 62.9654 | -59.4406 | 63.0249 | -59.2117 | -59.6283 | -0.09613 | -2.3529 | 62.9288 | -59.4223 | 63.0936 | -59.3353 | -59.4772 | -59.2255 | -0.068665 | -0.054932 | 0.004577 | 0.16022 | 59.2758 | -0.25635 | 59.3445 | -0.18768 | -0.050354 | -0.091553 | 0.073242 | 0.036621 | 0.14648 | -0.10529 | 0.19684 | -0.054932 | 0.22888 | 122.4655 | 0.086975 | 122.5159 | 122.406 | 122.3511 | 122.3373 | 122.3007 | -122.4609 | -122.4426 | 122.3969 | 122.4655 | 59.2896 | 57.019
1065.7656 | 122.6486 | -59.3903 | 63.0569 | -0.10979 | 0.0025529 | 0.06288 | 0.10095 | -0.00025628 | 0.0002778 | -0.0030976 | -0.036926 | -5.9826e-05 | 0.065033 | 0.065749 | -0.016323 | 0.00013253 | 0.00053409 | -0.11444 | 62.9791 | -59.4269 | 63.0341 | -59.2484 | -59.6466 | -0.091553 | -2.4399 | 62.9974 | -59.3811 | 63.1027 | -59.3628 | -59.4543 | -59.2255 | -0.036621 | -0.07782 | -0.022888 | 0.14191 | 59.2987 | -0.25635 | 59.3353 | -0.21973 | 0.009155 | -0.059509 | 0.045776 | 0.027466 | 0.16479 | -0.064087 | 0.15564 | -0.073242 | 0.17853 | 122.4609 | 0.018311 | 122.4838 | 122.406 | 122.3785 | 122.3694 | 122.3877 | -122.4838 | -122.4381 | 122.4243 | 122.493 | 59.2758 | 56.9504
1066.7656 | 122.7356 | -59.3857 | 62.9929 | -0.23949 | 0.0012711 | 0.06053 | 0.099666 | 0.00081172 | 0.0004914 | -0.0016022 | -0.091858 | 0.0016492 | 0.062897 | 0.062758 | -0.015469 | 0.0031231 | -0.0026703 | -0.045776 | 62.9196 | -59.436 | 63.0157 | -59.2117 | -59.6512 | -0.11902 | -2.3621 | 62.8922 | -59.4406 | 63.0936 | -59.317 | -59.491 | -59.2438 | -0.050354 | -0.073242 | 0.022888 | 0.17395 | 59.2667 | -0.2655 | 59.317 | -0.21515 | -0.054932 | -0.10071 | 0.10071 | 0.068664 | 0.14191 | -0.10529 | 0.19684 | -0.050354 | 0.2243 | 122.4518 | 0.1236 | 122.5342 | 122.3557 | 122.3328 | 122.3053 | 122.2778 | -122.4289 | -122.4335 | 122.4014 | 122.4792 | 59.3399 | 57.0236
1067.7656 | 122.699 | -59.3994 | 62.9791 | -0.11742 | 0.0016983 | 0.061385 | 0.1018 | -0.00046988 | -0.0012176 | -0.00096136 | -0.049133 | 0.00079477 | 0.063111 | 0.05934 | -0.018246 | 0.0014141 | -0.0026703 | -0.091553 | 62.9105 | -59.4864 | 63.002 | -59.2346 | -59.6558 | -0.11902 | -2.4307 | 62.9059 | -59.436 | 63.0524 | -59.3674 | -59.5093 | -59.285 | -0.086975 | -0.068665 | 0.022888 | 0.16479 | 59.2804 | -0.25635 | 59.3674 | -0.16937 | -0.036621 | -0.073242 | 0.073242 | 0.032043 | 0.11444 | -0.10986 | 0.15106 | -0.073242 | 0.25177 | 122.4884 | 0.068664 | 122.4884 | 122.3969 | 122.3419 | 122.3099 | 122.3053 | -122.4655 | -122.4152 | 122.4014 | 122.4518 | 59.3079 | 56.9687
1068.7656 | 122.6486 | -59.404 | 62.9929 | -0.14793 | 0.00020288 | 0.061171 | 0.10031 | 0.00059812 | -0.0031402 | -0.0020294 | -0.015564 | -0.00027343 | 0.065033 | 0.060622 | -0.016109 | 0.00077333 | 0.0011749 | -0.11444 | 62.9288 | -59.5093 | 62.9517 | -59.2804 | -59.6741 | -0.11444 | -2.3666 | 62.9059 | -59.4681 | 63.0295 | -59.198 | -59.4589 | -59.3811 | -0.10528 | -0.064087 | -0.041199 | 0.1236 | 59.2896 | -0.27008 | 59.3948 | -0.1648 | -0.064087 | -0.086975 | 0.036621 | 0.20599 | 0.022888 | -0.054931 | 0.086975 | 0.009156 | 0.22888 | 122.4609 | 0.27008 | 122.4976 | 122.438 | 122.374 | 122.3328 | 122.3099 | -122.5021 | -122.4609 | 122.3557 | 122.4335 | 59.2896 | 57.0374
1069.7656 | 122.699 | -59.3765 | 62.9791 | -0.12505 | 0.00063028 | 0.060744 | 0.10073 | -0.0032471 | -0.0007904 | -0.002243 | -0.024719 | -0.00091423 | 0.064392 | 0.061263 | -0.017605 | -0.00029487 | -0.0016021 | -0.12817 | 62.9471 | -59.4818 | 62.9791 | -59.2804 | -59.6741 | -0.14191 | -2.3804 | 62.915 | -59.4543 | 63.0341 | -59.3674 | -59.3582 | -59.1568 | -0.10529 | -0.032043 | 0 | 0.09613 | 59.2346 | -0.29755 | 59.3399 | -0.19226 | -0.07782 | -0.064087 | 0.054932 | 0.009155 | 0.21973 | 0.018311 | 0.29755 | 0.096131 | 0.20142 | 122.4609 | 0.086975 | 122.4884 | 122.4289 | 122.3694 | 122.3236 | 122.2916 | -122.4609 | -122.4335 | 122.3557 | 122.4106 | 59.2484 | 56.9962
1070.7656 | 122.7631 | -59.404 | 63.0295 | -0.11742 | 0.00020288 | 0.062025 | 0.099666 | -0.0015381 | -0.0020722 | -0.0016022 | -0.04303 | 0.00015377 | 0.064606 | 0.060836 | -0.01675 | 0.00098693 | 0.00053409 | -0.11444 | 62.9425 | -59.4818 | 62.9745 | -59.2621 | -59.6786 | -0.15106 | -2.3346 | 62.9425 | -59.4543 | 63.0432 | -59.3674 | -59.5001 | -59.3811 | -0.07782 | -0.086975 | -0.054932 | 0.14191 | 59.2529 | -0.27466 | 59.3307 | -0.19684 | -0.050354 | -0.086975 | 0.013733 | 0.036621 | 0.022888 | -0.09613 | 0.073242 | -0.045776 | 0.21973 | 122.4564 | 0.086975 | 122.4976 | 122.4243 | 122.3969 | 122.3465 | 122.3465 | -122.5113 | -122.4838 | 122.3785 | 122.4472 | 59.2896 | 57.0694
1071.7656 | 122.6578 | -59.4131 | 62.9929 | -0.06401 | -0.00043792 | 0.060103 | 0.10031 | 0.0029479 | -0.0003632 | -0.00074776 | -0.030823 | -0.00048703 | 0.063538 | 0.059981 | -0.017605 | 0.0014141 | -0.00053411 | -0.1236 | 62.9425 | -59.4955 | 62.9517 | -59.2941 | -59.6924 | -0.14648 | -2.3621 | 62.9013 | -59.4498 | 63.0432 | -59.3903 | -59.5139 | -59.2941 | -0.082397 | -0.050354 | -0.041199 | 0.11902 | 59.2667 | -0.27924 | 59.3491 | -0.19684 | -0.036621 | -0.091553 | 0.050354 | 0.022888 | 0.11902 | -0.10071 | 0.15564 | -0.064087 | 0.20142 | 122.4472 | 0.059509 | 122.493 | 122.438 | 122.3511 | 122.3557 | 122.3145 | -122.4884 | -122.4426 | 122.3648 | 122.4564 | 59.2896 | 57.0511
1072.7656 | 122.699 | -59.404 | 62.9929 | -0.14793 | 0.00041648 | 0.063521 | 0.10223 | 0.0029479 | -0.0018586 | 0.00053404 | -0.055237 | -0.00070063 | 0.06482 | 0.061904 | -0.018886 | 0.0018413 | 0.00032049 | -0.082397 | 62.9196 | -59.4589 | 63.0203 | -59.2117 | -59.6329 | -0.16937 | -2.3758 | 62.9059 | -59.4131 | 63.0798 | -59.3536 | -59.4772 | -59.2575 | -0.054931 | -0.073242 | 0.027466 | 0.19226 | 59.2346 | -0.22888 | 59.2895 | -0.17395 | -0.009155 | -0.086975 | 0.086975 | 0.050354 | 0.14649 | -0.073242 | 0.15564 | -0.064087 | 0.24719 | 122.4792 | 0.059509 | 122.493 | 122.3785 | 122.319 | 122.3236 | 122.3099 | -122.4518 | -122.406 | 122.4243 | 122.4838 | 59.3216 | 57.0282
1073.7656 | 122.6852 | -59.3536 | 63.0341 | -0.094528 | 0.0010575 | 0.062239 | 0.10159 | -0.00068368 | -0.0001496 | -0.00010676 | -0.055237 | -0.0015552 | 0.064392 | 0.064894 | -0.01675 | 0.0022687 | 0.00074769 | -0.091553 | 62.9654 | -59.4269 | 63.0753 | -59.198 | -59.5917 | -0.19226 | -2.4857 | 62.9562 | -59.4223 | 63.121 | -59.2987 | -59.4635 | -59.2072 | -0.073242 | -0.068665 | 0.041198 | 0.15564 | 59.1614 | -0.23804 | 59.2346 | -0.1648 | -0.068664 | -0.07782 | 0.086975 | 0.054932 | 0.14648 | -0.10986 | 0.21515 | -0.041199 | 0.22888 | 122.5021 | 0.1236 | 122.5433 | 122.3923 | 122.3785 | 122.319 | 122.3099 | -122.4609 | -122.4564 | 122.4289 | 122.4747 | 59.2621 | 56.868
1074.7656 | 122.6669 | -59.3308 | 63.0707 | 0.080948 | 0.00084388 | 0.063948 | 0.099879 | 0.00081172 | -0.0022858 | -0.0018158 | -0.024719 | -0.0028368 | 0.062897 | 0.06639 | -0.016964 | 0.00034613 | -0.0037383 | -0.21057 | 63.0203 | -59.4131 | 63.0295 | -59.2392 | -59.6054 | -0.20599 | -2.5543 | 63.0066 | -59.3948 | 63.1119 | -59.2896 | -59.4498 | -59.2117 | -0.082397 | -0.050354 | -0.041199 | 0.091553 | 59.1248 | -0.27466 | 59.2072 | -0.19226 | -0.064086 | -0.064087 | 0.041198 | 0.041199 | 0.11902 | -0.11902 | 0.1831 | -0.054932 | 0.17395 | 122.4426 | 0.10528 | 122.5067 | 122.4335 | 122.4014 | 122.3511 | 122.3373 | -122.4838 | -122.4655 | 122.3602 | 122.4426 | 59.1202 | 56.7764
1075.7656 | 122.6486 | -59.3674 | 63.0432 | -0.086899 | -1.0718e-05 | 0.060957 | 0.10052 | -0.0017517 | -0.0014312 | -0.00096136 | -0.018616 | -0.00091423 | 0.063324 | 0.059981 | -0.018246 | 0.0018413 | 0.00096129 | 0.036621 | 63.0478 | -59.4131 | 63.0203 | -59.2438 | -59.6558 | -0.22888 | -2.5864 | 62.9745 | -59.4177 | 63.0936 | -59.285 | -59.4727 | -59.2346 | -0.045776 | 0.004578 | -0.022888 | 0.1236 | 59.1385 | -0.28839 | 59.1843 | -0.24262 | -0.050354 | -0.068665 | 0.050354 | 0.082398 | 0.13275 | -0.10529 | 0.18311 | -0.054931 | 0.16937 | 122.4335 | 0.13275 | 122.5113 | 122.4609 | 122.3923 | 122.4152 | 122.3419 | -122.4564 | -122.4609 | 122.3877 | 122.4609 | 59.404 | 56.781
1076.7656 | 122.6944 | -59.3536 | 63.0112 | -0.07164 | 0.0019119 | 0.06288 | 0.10073 | 0.0025207 | -0.0007904 | -0.00096136 | -0.046081 | -0.0017688 | 0.063324 | 0.062972 | -0.017391 | 0.00055973 | -0.0041657 | -0.1236 | 62.9562 | -59.4177 | 63.0112 | -59.2484 | -59.6603 | -0.2243 | -2.6321 | 62.9608 | -59.404 | 63.0753 | -59.3262 | -59.4772 | -59.2529 | -0.064087 | -0.054931 | 0 | 0.10529 | 59.1293 | -0.3067 | 59.1934 | -0.24261 | -0.050354 | -0.050354 | 0.064087 | 0.027466 | 0.10071 | -0.1236 | 0.15106 | -0.073242 | 0.16937 | 122.4289 | 0.07782 | 122.4792 | 122.374 | 122.3648 | 122.3099 | 122.3145 | -122.4289 | -122.4152 | 122.3648 | 122.4289 | 59.23 | 56.7215
1077.7656 | 122.6669 | -59.3308 | 63.0798 | -0.10216 | 0.00020288 | 0.063094 | 0.098811 | -0.0026063 | -0.0029266 | -0.0018158 | -0.018616 | 0.00036737 | 0.063965 | 0.065535 | -0.018246 | 0.00034613 | -0.00032051 | -0.1236 | 63.0432 | -59.4086 | 62.9929 | -59.2072 | -59.6237 | -0.27008 | -2.6642 | 62.9745 | -59.4086 | 63.1073 | -59.3124 | -59.4589 | -59.2072 | -0.077819 | -0.036621 | -0.086975 | 0.1236 | 59.0607 | -0.29297 | 59.1385 | -0.21515 | -0.077819 | -0.10529 | 0.027466 | 0.018311 | 0.1236 | -0.12817 | 0.20142 | -0.050354 | 0.20142 | 122.4014 | 0.09613 | 122.5159 | 122.4518 | 122.3831 | 122.374 | 122.3053 | -122.4884 | -122.4884 | 122.3236 | 122.4381 | 59.2072 | 56.6666
1078.7656 | 122.6532 | -59.3399 | 63.0661 | -0.11742 | 0.00041648 | 0.059676 | 0.099452 | -0.0026063 | -0.001004 | 0.001175 | -0.04303 | -0.00070063 | 0.062256 | 0.056136 | -0.017818 | 0.00077333 | -0.0016021 | -0.12817 | 63.002 | -59.4177 | 63.0707 | -59.3536 | -59.6466 | -0.25177 | -2.6047 | 62.97 | -59.3948 | 63.1027 | -59.2941 | -59.4589 | -59.2209 | -0.07782 | -0.064087 | 0.004578 | -0.013733 | 59.0881 | -0.3067 | 59.166 | -0.22888 | -0.054931 | -0.09613 | 0.036621 | 0.045777 | 0.11902 | -0.11902 | 0.17395 | -0.064087 | 0.064087 | 122.4884 | 0.10071 | 122.4976 | 122.4197 | 122.3648 | 122.3419 | 122.3099 | -122.4838 | -122.4609 | 122.4106 | 122.4426 | 59.2117 | 56.7352
1079.7656 | 122.6807 | -59.317 | 63.0569 | -0.12505 | 0.0014847 | 0.06288 | 0.099879 | -0.0015381 | -0.0018586 | -0.0016022 | -0.055237 | 0.00036737 | 0.065033 | 0.061049 | -0.018246 | 0.00077333 | -0.0033111 | -0.13733 | 62.9974 | -59.436 | 63.0524 | -59.198 | -59.6146 | -0.29755 | -2.6001 | 62.97 | -59.3765 | 63.1165 | -59.3033 | -59.4452 | -59.2026 | -0.11902 | -0.059509 | -0.004578 | 0.11902 | 59.0195 | -0.29755 | 59.1385 | -0.17853 | -0.059509 | -0.086975 | 0.059509 | 0.013733 | 0.11444 | -0.12817 | 0.17395 | -0.068664 | 0.23804 | 122.4884 | 0.073242 | 122.493 | 122.4335 | 122.3465 | 122.3145 | 122.287 | -122.493 | -122.4335 | 122.3694 | 122.4335 | 59.1797 | 56.7169
1080.7656 | 122.6807 | -59.3491 | 63.0615 | -0.11742 | -0.00043792 | 0.060957 | 0.10095 | 0.0016663 | -0.002713 | 0.00053404 | -0.058289 | -0.00091423 | 0.063965 | 0.06404 | -0.015896 | 0.0020551 | -0.0018157 | -0.11902 | 63.0066 | -59.4131 | 63.0524 | -59.1843 | -59.6191 | -0.3067 | -2.6871 | 62.9837 | -59.3811 | 63.1302 | -59.3079 | -59.4543 | -59.2072 | -0.064087 | -0.054931 | -0.009155 | 0.16479 | 59.0424 | -0.27008 | 59.1064 | -0.20599 | -0.032044 | -0.077819 | 0.068665 | 0.041199 | 0.14191 | -0.10529 | 0.17395 | -0.073242 | 0.22888 | 122.4655 | 0.073243 | 122.5113 | 122.4197 | 122.3648 | 122.3557 | 122.3328 | -122.4747 | -122.4426 | 122.4014 | 122.4792 | 59.23 | 56.662
1081.7656 | 122.7264 | -59.3353 | 63.0569 | -0.094528 | -1.0718e-05 | 0.062239 | 0.1018 | 0.00059812 | -0.0024994 | 0.00010684 | -0.046081 | -0.00027343 | 0.063324 | 0.055495 | -0.018246 | 0.0014141 | -0.0026703 | -0.082397 | 63.0157 | -59.4086 | 63.0615 | -59.198 | -59.5642 | -0.2655 | -2.655 | 62.9929 | -59.3811 | 63.1348 | -59.2484 | -59.4131 | -59.1797 | -0.073242 | -0.041199 | 0.004577 | 0.13733 | 59.0698 | -0.22888 | 59.1431 | -0.15564 | -0.045777 | -0.064087 | 0.07782 | 0.086975 | 0.15564 | -0.07782 | 0.20142 | -0.032043 | 0.21057 | 122.4701 | 0.13275 | 122.5159 | 122.4243 | 122.374 | 122.3511 | 122.3282 | -122.4655 | -122.4381 | 122.3969 | 122.4701 | 59.2529 | 56.6803
1082.7656 | 122.699 | -59.3353 | 63.0661 | -0.10216 | 0.0014847 | 0.061385 | 0.10159 | 0.0012391 | -0.0029266 | -0.00096136 | -0.024719 | -0.00027343 | 0.064392 | 0.067885 | -0.017818 | 0.00055973 | -0.0024567 | -0.11444 | 63.0112 | -59.4269 | 63.0524 | -59.1934 | -59.5688 | -0.30212 | -2.7603 | 62.9929 | -59.3674 | 63.1622 | -59.2392 | -59.404 | -59.166 | -0.091553 | -0.054932 | -0.013733 | 0.14191 | 59.0332 | -0.23346 | 59.1248 | -0.14191 | -0.032044 | -0.073242 | 0.09613 | 0.09613 | 0.16937 | -0.068665 | 0.20142 | -0.036621 | 0.23346 | 122.4792 | 0.12817 | 122.5296 | 122.438 | 122.3602 | 122.3465 | 122.3282 | -122.493 | -122.4335 | 122.3877 | 122.4976 | 59.2209 | 56.575
1083.7656 | 122.6944 | -59.3079 | 63.0753 | -0.079269 | 0.00041648 | 0.061385 | 0.10095 | -0.00046988 | -0.0018586 | -0.0041656 | -0.015564 | -0.00048703 | 0.06482 | 0.064467 | -0.017391 | 0.0022687 | -0.0035247 | -0.10529 | 63.0341 | -59.404 | 63.0936 | -59.1843 | -59.5596 | -0.31128 | -2.7924 | 63.0249 | -59.3399 | 63.1622 | -59.2255 | -59.3857 | -59.1705 | -0.096131 | -0.041198 | 0.018311 | 0.1236 | 58.9966 | -0.25177 | 59.0927 | -0.15564 | -0.032044 | -0.050354 | 0.086975 | 0.082397 | 0.13733 | -0.07782 | 0.16937 | -0.045776 | 0.21973 | 122.4976 | 0.11444 | 122.5021 | 122.4381 | 122.3648 | 122.3419 | 122.3328 | -122.4792 | -122.4152 | 122.4014 | 122.4701 | 59.2026 | 56.5155
1084.7656 | 122.7036 | -59.2941 | 63.1073 | -0.11742 | 0.0027665 | 0.059676 | 0.10052 | -0.00025628 | -0.0039948 | -0.002884 | -0.0064086 | 0.00079477 | 0.063324 | 0.062972 | -0.019741 | 0.0016277 | -0.0054473 | -0.10071 | 63.0615 | -59.404 | 63.0844 | -59.1751 | -59.5322 | -0.31128 | -2.8015 | 62.9929 | -59.3582 | 63.1622 | -59.2209 | -59.3903 | -59.1705 | -0.10986 | -0.045777 | -0.022888 | 0.11902 | 58.9828 | -0.23804 | 59.0927 | -0.12817 | -0.064087 | -0.11444 | 0.054931 | 0.073242 | 0.1236 | -0.096131 | 0.18768 | -0.032044 | 0.22888 | 122.4884 | 0.13733 | 122.5204 | 122.4655 | 122.3511 | 122.3557 | 122.287 | -122.5113 | -122.4655 | 122.3785 | 122.4564 | 59.1934 | 56.4926
1085.7656 | 122.699 | -59.2896 | 63.1302 | -0.094528 | 0.00020288 | 0.059889 | 0.1018 | 0.0014527 | -0.0012176 | -0.001175 | -0.033874 | 0.00079477 | 0.063111 | 0.062972 | -0.018246 | 0.0012005 | 0.00074769 | -0.1236 | 63.0524 | -59.3811 | 63.1027 | -59.1476 | -59.523 | -0.33417 | -2.8244 | 63.0249 | -59.3308 | 63.176 | -59.2072 | -59.3582 | -59.1568 | -0.091553 | -0.07782 | -0.027466 | 0.14191 | 58.9554 | -0.23346 | 59.0469 | -0.14191 | -0.041199 | -0.10529 | 0.045776 | 0.082398 | 0.13275 | -0.068664 | 0.17395 | -0.027465 | 0.23346 | 122.4838 | 0.1236 | 122.5067 | 122.4335 | 122.3557 | 122.3419 | 122.3145 | -122.5113 | -122.4609 | 122.3923 | 122.4655 | 59.166 | 56.4651
1086.7656 | 122.6715 | -59.317 | 63.1302 | -0.094528 | 0.0012711 | 0.060316 | 0.10031 | -0.0015381 | -0.0022858 | -0.0013886 | -0.06134 | -5.9826e-05 | 0.063324 | 0.069594 | -0.016964 | 0.0035503 | -0.0016021 | -0.15106 | 63.0661 | -59.3628 | 63.089 | -59.1522 | -59.5001 | -0.1831 | -2.9938 | 63.0386 | -59.3445 | 63.1256 | -59.2529 | -59.4086 | -59.1843 | -0.045776 | -0.064087 | -0.041199 | 0.16479 | 59.1339 | -0.1831 | 59.1797 | -0.13733 | -0.027465 | -0.091553 | -0.004578 | 0.064087 | 0.13275 | -0.091552 | 0.16022 | -0.064087 | 0.21057 | 122.4518 | 0.091552 | 122.4701 | 122.4289 | 122.3831 | 122.3831 | 122.3557 | -122.493 | -122.4747 | 122.406 | 122.4426 | 59.166 | 56.3232
1087.7656 | 122.6852 | -59.2438 | 63.1348 | -0.16319 | 0.0012711 | 0.06053 | 0.099879 | -0.0013245 | -0.002713 | -0.0020294 | -0.0033568 | -0.0015552 | 0.066315 | 0.062758 | -0.017178 | 0.0020551 | 0.0022431 | -0.15564 | 63.0936 | -59.3536 | 63.1165 | -59.1339 | -59.5413 | -0.37079 | -2.8885 | 63.0569 | -59.2896 | 63.1943 | -59.2255 | -59.3903 | -59.1476 | -0.10986 | -0.041199 | -0.018311 | 0.10986 | 58.873 | -0.29755 | 58.9828 | -0.18768 | -0.045777 | -0.07782 | 0.059509 | 0.01831 | 0.09613 | -0.14648 | 0.14191 | -0.10071 | 0.21973 | 122.4701 | 0.064087 | 122.4838 | 122.4472 | 122.3465 | 122.3373 | 122.3007 | -122.4884 | -122.4243 | 122.3602 | 122.438 | 59.0881 | 56.3553
1088.7656 | 122.7585 | -59.2392 | 63.1348 | -0.094528 | 0.00041648 | 0.062453 | 0.10116 | -4.2682e-05 | -0.0014312 | -0.002884 | -0.04303 | 0.00015377 | 0.063111 | 0.063399 | -0.017818 | -0.00072207 | -0.0026703 | -0.10071 | 63.0707 | -59.317 | 63.1622 | -59.0836 | -59.4772 | -0.29755 | -2.6917 | 63.0661 | -59.2987 | 63.2309 | -59.1248 | -59.2804 | -59.0881 | -0.07782 | -0.064087 | 0.027465 | 0.15564 | 58.9417 | -0.23804 | 59.0195 | -0.16022 | -0.059509 | -0.068665 | 0.09613 | 0.11444 | 0.15106 | -0.041199 | 0.21057 | 0.01831 | 0.23346 | 122.4792 | 0.17395 | 122.5296 | 122.3877 | 122.3648 | 122.3099 | 122.3053 | -122.4518 | -122.4335 | 122.4014 | 122.4701 | 59.1385 | 56.5475
1089.7656 | 122.731 | -59.2575 | 63.1393 | -0.079269 | 0.00084388 | 0.06053 | 0.10009 | -0.0036743 | -0.0016448 | -0.004593 | -0.033874 | -0.0013416 | 0.063111 | 0.05934 | -0.018032 | 0.0012005 | 0.00096129 | -0.10529 | 63.121 | -59.3308 | 63.1577 | -59.0836 | -59.4681 | -0.31128 | -2.7054 | 63.0569 | -59.2987 | 63.2309 | -59.1431 | -59.2987 | -59.0927 | -0.073243 | -0.01831 | 0.018311 | 0.17395 | 58.9462 | -0.21057 | 59.0195 | -0.13733 | -0.041199 | -0.082397 | 0.091553 | 0.11444 | 0.16479 | -0.041199 | 0.20599 | 0 | 0.24719 | 122.4884 | 0.15564 | 122.5296 | 122.4518 | 122.3557 | 122.3785 | 122.3145 | -122.4701 | -122.438 | 122.4152 | 122.4884 | 59.1522 | 56.5521
1090.7656 | 122.7402 | -59.23 | 63.1485 | -0.094528 | 0.00063028 | 0.061812 | 0.10031 | -0.00068368 | -0.0020722 | -0.0024566 | -0.024719 | -0.0013416 | 0.064179 | 0.062545 | -0.019314 | 0.0018413 | -0.0030975 | -0.10071 | 63.0707 | -59.3536 | 63.1622 | -59.0927 | -59.4498 | -0.28381 | -2.8152 | 63.0661 | -59.285 | 63.2401 | -59.1385 | -59.2987 | -59.079 | -0.1236 | -0.07782 | 0.013732 | 0.13733 | 58.9462 | -0.21973 | 59.0698 | -0.09613 | -0.054931 | -0.082398 | 0.091552 | 0.091553 | 0.15106 | -0.068664 | 0.20599 | -0.013733 | 0.26093 | 122.5159 | 0.14648 | 122.525 | 122.4243 | 122.3511 | 122.3007 | 122.2961 | -122.5021 | -122.4335 | 122.3923 | 122.4701 | 59.1293 | 56.4148
1091.7656 | 122.7264 | -59.2667 | 63.1485 | -0.048752 | 0.0016983 | 0.058394 | 0.10052 | 0.0010253 | -0.0035674 | -0.0026704 | -0.015564 | 0.00079477 | 0.066315 | 0.054854 | -0.018032 | 0.0029095 | 0.0011749 | -0.11902 | 63.089 | -59.3536 | 63.1622 | -59.0973 | -59.4772 | -0.33417 | -2.7512 | 63.0615 | -59.2987 | 63.2263 | -59.1385 | -59.3079 | -59.1019 | -0.086975 | -0.05951 | 0.013732 | 0.16937 | 58.9325 | -0.21057 | 59.0195 | -0.1236 | -0.032043 | -0.086976 | 0.077819 | 0.12817 | 0.16479 | -0.041198 | 0.19684 | -0.009155 | 0.25635 | 122.5159 | 0.16022 | 122.525 | 122.4426 | 122.3602 | 122.3557 | 122.3282 | -122.5021 | -122.4472 | 122.4289 | 122.493 | 59.1476 | 56.5155
1092.7656 | 122.731 | -59.2163 | 63.1348 | -0.10216 | -0.00043792 | 0.061171 | 0.10116 | 0.0031617 | -0.0012176 | 0.0016022 | -0.018616 | -5.9826e-05 | 0.062897 | 0.066817 | -0.016964 | -0.00072207 | -0.00096131 | -0.12817 | 63.1165 | -59.3308 | 63.1439 | -59.0973 | -59.4864 | -0.36163 | -2.5955 | 63.0524 | -59.3216 | 63.2446 | -59.1431 | -59.3079 | -59.0973 | -0.11444 | -0.018311 | 0.009155 | 0.11902 | 58.8547 | -0.27008 | 58.9691 | -0.15564 | -0.10528 | -0.082398 | 0.10986 | 0.073243 | 0.11902 | -0.091552 | 0.2243 | 0.013733 | 0.23346 | 122.4747 | 0.17853 | 122.5662 | 122.4472 | 122.374 | 122.3328 | 122.2687 | -122.4655 | -122.4564 | 122.3602 | 122.4609 | 59.0881 | 56.6208
1093.7656 | 122.6807 | -59.2484 | 63.1851 | -0.11742 | 0.00020288 | 0.060103 | 0.10116 | 0.0012391 | 0.0011322 | -0.00096136 | -0.14679 | 0.00036737 | 0.064179 | 0.066603 | -0.016964 | 0.0029095 | -0.0028839 | -0.14648 | 63.1027 | -59.3491 | 63.121 | -59.1064 | -59.2987 | -0.32044 | -2.6825 | 63.0569 | -59.3399 | 63.176 | -59.2072 | -59.3719 | -59.1431 | -0.10071 | -0.082398 | -0.064087 | 0.14191 | 58.9279 | -0.050354 | 59.0286 | 0.050354 | -0.091553 | -0.12817 | -0.009156 | 0.041199 | 0.10529 | -0.1236 | 0.19684 | -0.032043 | 0.24262 | 122.4701 | 0.13275 | 122.5159 | 122.4518 | 122.3969 | 122.3511 | 122.3053 | -122.5342 | -122.525 | 122.3694 | 122.4243 | 59.1019 | 56.5659
1094.7656 | 122.6761 | -59.2163 | 63.1805 | -0.12505 | 0.00020288 | 0.061171 | 0.10116 | 0.0046569 | -0.002713 | 0.00074764 | -0.039978 | -5.9826e-05 | 0.063965 | 0.05699 | -0.016323 | 0.00034613 | -0.0013885 | -0.16937 | 63.1073 | -59.3033 | 63.1668 | -59.0881 | -59.4727 | -0.50812 | -2.8473 | 63.1348 | -59.2667 | 63.208 | -59.1751 | -59.3674 | -59.1202 | -0.086975 | -0.073242 | -0.013733 | 0.12817 | 58.7082 | -0.25635 | 58.7952 | -0.16937 | -0.050354 | -0.045776 | 0.027466 | 0.041199 | 0.096131 | -0.15106 | 0.14648 | -0.10071 | 0.21515 | 122.4701 | 0.091553 | 122.4747 | 122.4106 | 122.4014 | 122.3236 | 122.3511 | -122.4838 | -122.4472 | 122.3831 | 122.4243 | 59.0469 | 56.369
1095.7656 | 122.731 | -59.1934 | 63.2034 | -0.13267 | 0.00020288 | 0.063734 | 0.099239 | -0.0019653 | -0.0042084 | -0.0035248 | -0.012512 | 0.0014356 | 0.063965 | 0.066176 | -0.018673 | 0.0014141 | 0.00010689 | -0.11902 | 63.1485 | -59.2804 | 63.2126 | -59.0103 | -59.3948 | -0.56763 | -2.8473 | 63.1119 | -59.2438 | 63.2904 | -59.0744 | -59.2392 | -59.0149 | -0.086976 | -0.054931 | 0.009155 | 0.18311 | 58.6258 | -0.20142 | 58.7128 | -0.11444 | -0.050354 | -0.091553 | 0.086975 | 0.11902 | 0.17853 | -0.045777 | 0.22888 | 0.004577 | 0.27008 | 122.493 | 0.16937 | 122.5342 | 122.4289 | 122.3557 | 122.3419 | 122.3053 | -122.4838 | -122.4472 | 122.406 | 122.4838 | 59.0744 | 56.3461
1096.7656 | 122.7173 | -59.1934 | 63.2217 | -0.10979 | 0.0021255 | 0.06288 | 0.10073 | -0.0023925 | -0.0029266 | -0.0026704 | -0.015564 | -0.00070063 | 0.063751 | 0.05699 | -0.016964 | 0.0016277 | -0.00010671 | -0.1236 | 63.176 | -59.2987 | 63.2263 | -59.0195 | -59.4177 | -0.59509 | -2.6917 | 63.1393 | -59.23 | 63.2996 | -59.0881 | -59.2484 | -59.024 | -0.10529 | -0.045777 | 0.004577 | 0.17395 | 58.5983 | -0.2243 | 58.7036 | -0.11902 | -0.036622 | -0.082398 | 0.07782 | 0.10529 | 0.16937 | -0.054932 | 0.20599 | -0.01831 | 0.27924 | 122.525 | 0.14191 | 122.5296 | 122.4747 | 122.3694 | 122.3694 | 122.3328 | -122.5204 | -122.4518 | 122.4197 | 122.493 | 59.0698 | 56.5018
1097.7656 | 122.7219 | -59.2072 | 63.208 | -0.094528 | -0.00022432 | 0.061385 | 0.10159 | -0.0019653 | -0.0012176 | -0.0018158 | -0.04303 | -0.00048703 | 0.063324 | 0.060195 | -0.018246 | 0.00055973 | -0.0026703 | -0.15564 | 63.1531 | -59.2941 | 63.1851 | -59.0698 | -59.4406 | -0.52643 | -2.6505 | 63.1027 | -59.2667 | 63.2675 | -59.1064 | -59.2804 | -59.0515 | -0.086975 | -0.054932 | -0.022888 | 0.13733 | 58.6807 | -0.23346 | 58.7677 | -0.14648 | -0.05951 | -0.10529 | 0.059509 | 0.10071 | 0.15564 | -0.073243 | 0.21515 | -0.013733 | 0.2243 | 122.4792 | 0.16022 | 122.5342 | 122.4472 | 122.3694 | 122.3602 | 122.3099 | -122.5021 | -122.4747 | 122.3923 | 122.4747 | 59.0515 | 56.5567
1098.7656 | 122.6074 | -59.2163 | 63.2492 | 0.096207 | 0.00084388 | 0.063094 | 0.10266 | 0.0018799 | -0.0012176 | -0.0016022 | -0.091858 | 0.00015377 | 0.063324 | 0.065108 | -0.017605 | 0.0033367 | 0.0013885 | -0.24261 | 63.2263 | -59.2987 | 63.1577 | -59.1248 | -59.523 | -0.59509 | -2.6917 | 63.176 | -59.2346 | 63.2034 | -59.1614 | -59.3536 | -59.1293 | -0.082397 | -0.022889 | -0.091553 | 0.091553 | 58.6212 | -0.3067 | 58.7036 | -0.2243 | -0.01831 | -0.073243 | -0.045777 | 0.054932 | 0.086976 | -0.13733 | 0.10529 | -0.11902 | 0.17395 | 122.4564 | 0.073242 | 122.438 | 122.525 | 122.4106 | 122.4426 | 122.3923 | -122.5479 | -122.4838 | 122.374 | 122.4197 | 58.9737 | 56.5247
1099.7656 | 122.6944 | -59.198 | 63.2172 | -0.07164 | -0.00065152 | 0.061385 | 0.10095 | -4.2682e-05 | -0.0020722 | -0.002243 | -0.0094604 | 0.0018628 | 0.063324 | 0.055922 | -0.017391 | 0.0024823 | 0.0018159 | -0.19684 | 63.1485 | -59.285 | 63.1805 | -59.0515 | -59.4452 | -0.60425 | -2.8107 | 63.1348 | -59.2484 | 63.2492 | -59.1248 | -59.2896 | -59.0561 | -0.086975 | -0.068664 | -0.036621 | 0.14648 | 58.5938 | -0.24719 | 58.6807 | -0.16022 | -0.050354 | -0.082397 | 0.032044 | 0.073242 | 0.14191 | -0.091553 | 0.19226 | -0.041199 | 0.23346 | 122.4655 | 0.1236 | 122.4976 | 122.4335 | 122.3831 | 122.3465 | 122.3328 | -122.5021 | -122.4655 | 122.3785 | 122.4472 | 59.0012 | 56.3873
1100.7656 | 122.6852 | -59.1797 | 63.208 | -0.1403 | 0.00063028 | 0.061598 | 0.10287 | 0.00081172 | -0.0014312 | -0.0020294 | -0.021667 | 0.00036737 | 0.064392 | 0.063185 | -0.017605 | 0.00055973 | -0.0013885 | -0.21973 | 63.121 | -59.2896 | 63.1714 | -59.0652 | -59.4772 | -0.66376 | -2.8107 | 63.1027 | -59.2621 | 63.2538 | -59.1476 | -59.3216 | -59.0973 | -0.10986 | -0.086975 | -0.036621 | 0.11444 | 58.5159 | -0.29755 | 58.6258 | -0.18768 | -0.082398 | -0.10529 | 0.045776 | 0.032043 | 0.082397 | -0.14191 | 0.16479 | -0.059509 | 0.2243 | 122.4609 | 0.11444 | 122.5159 | 122.4106 | 122.3648 | 122.3007 | 122.2824 | -122.4976 | -122.4701 | 122.3511 | 122.4335 | 58.96 | 56.369
1101.7656 | 122.6807 | -59.1843 | 63.2217 | -0.12505 | 0.00084388 | 0.06288 | 0.10052 | -0.0023925 | -0.0024994 | 0.00096124 | -0.076599 | -5.9826e-05 | 0.064392 | 0.060622 | -0.019527 | 0.0035503 | 0.0016021 | -0.20142 | 63.1485 | -59.2484 | 63.1989 | -59.0332 | -59.4635 | -0.67749 | -2.742 | 63.1302 | -59.2438 | 63.2492 | -59.1293 | -59.2987 | -59.0652 | -0.064087 | -0.073242 | -0.022888 | 0.15106 | 58.5068 | -0.27924 | 58.5709 | -0.21515 | -0.059509 | -0.091553 | 0.027466 | 0.054932 | 0.11902 | -0.11444 | 0.17853 | -0.054932 | 0.21515 | 122.4472 | 0.11444 | 122.493 | 122.3969 | 122.374 | 122.3328 | 122.3145 | -122.4701 | -122.4655 | 122.3831 | 122.4335 | 58.9828 | 56.4423
1102.7656 | 122.7127 | -59.2026 | 63.1897 | -0.033493 | -0.0019333 | 0.060957 | 0.10202 | -4.2682e-05 | -0.0035674 | -0.00010676 | -0.021667 | 0.00036737 | 0.062256 | 0.059127 | -0.016964 | 0.0024823 | -0.0030975 | -0.17395 | 63.1302 | -59.2896 | 63.1805 | -59.0469 | -59.4772 | -0.60883 | -2.8702 | 63.1256 | -59.2529 | 63.2446 | -59.1202 | -59.285 | -59.0607 | -0.086975 | -0.059509 | -0.009155 | 0.15564 | 58.5938 | -0.27466 | 58.6807 | -0.18768 | -0.050354 | -0.064087 | 0.054932 | 0.082398 | 0.14191 | -0.082397 | 0.19226 | -0.032043 | 0.24262 | 122.4701 | 0.13275 | 122.4976 | 122.4197 | 122.3785 | 122.3328 | 122.3282 | -122.4792 | -122.4426 | 122.3831 | 122.4472 | 59.0286 | 56.3324
1103.7656 | 122.6395 | -59.166 | 63.2584 | -0.079269 | -0.0010787 | 0.061385 | 0.10031 | 0.0020935 | -0.0003632 | -0.00096136 | -0.12238 | 0.00058097 | 0.064606 | 0.065749 | -0.018673 | 0.0026959 | 0.00032049 | -0.11902 | 63.2126 | -59.2712 | 63.208 | -59.0424 | -59.4177 | -0.68207 | -2.9068 | 63.1851 | -59.1934 | 63.2767 | -59.1156 | -59.3353 | -59.079 | -0.10529 | -0.045777 | -0.050354 | 0.1236 | 58.4839 | -0.25177 | 58.5892 | -0.14648 | -0.027465 | -0.073242 | 0.01831 | 0.050354 | 0.086976 | -0.16937 | 0.11444 | -0.14191 | 0.22888 | 122.4792 | 0.077819 | 122.4701 | 122.4838 | 122.3785 | 122.3785 | 122.3511 | -122.5296 | -122.4518 | 122.374 | 122.4426 | 59.0469 | 56.2592
1104.7656 | 122.7264 | -59.1568 | 63.2172 | -0.010605 | 0.00041648 | 0.062239 | 0.10116 | 0.00038452 | -0.0016448 | -0.0020294 | -0.0033568 | 0.00036737 | 0.064606 | 0.056349 | -0.017391 | 0.0020551 | -0.00096131 | -0.15564 | 63.1668 | -59.2758 | 63.2217 | -59.0103 | -59.404 | -0.63629 | -3.0258 | 63.1393 | -59.2392 | 63.3087 | -59.0744 | -59.2392 | -59.0286 | -0.11902 | -0.050354 | 0.004578 | 0.14648 | 58.5205 | -0.24719 | 58.6395 | -0.12817 | -0.082398 | -0.07782 | 0.091553 | 0.082397 | 0.12817 | -0.082398 | 0.21057 | 0 | 0.2655 | 122.4976 | 0.16479 | 122.5479 | 122.4426 | 122.3785 | 122.3236 | 122.2961 | -122.493 | -122.4564 | 122.3785 | 122.4655 | 59.0012 | 56.131
1105.7656 | 122.6669 | -59.1614 | 63.2492 | -0.12505 | -0.0010787 | 0.062453 | 0.10095 | -0.00025628 | -0.0012176 | -0.0026704 | -0.024719 | 0.001222 | 0.063111 | 0.055922 | -0.019314 | 0.0026959 | 0.0050201 | -0.054932 | 63.2217 | -59.2163 | 63.1805 | -59.0057 | -59.4543 | -0.80109 | -3.2181 | 63.1577 | -59.2163 | 63.2812 | -59.0836 | -59.2621 | -59.0652 | -0.054932 | -0.027466 | -0.068665 | 0.15564 | 58.3603 | -0.29297 | 58.4152 | -0.23804 | -0.054932 | -0.091553 | 0.032043 | 0.07782 | 0.09613 | -0.10071 | 0.15106 | -0.045776 | 0.21057 | 122.3969 | 0.13275 | 122.4976 | 122.4381 | 122.374 | 122.3831 | 122.319 | -122.4655 | -122.4655 | 122.3419 | 122.4426 | 59.1064 | 55.9433
1106.7656 | 122.6578 | -59.2026 | 63.2034 | -0.086899 | 0.0019119 | 0.061598 | 0.10095 | -4.2682e-05 | -0.0005768 | -0.0018158 | -0.030823 | -0.0013416 | 0.062256 | 0.062331 | -0.017605 | 0.00098693 | -0.0020295 | -0.20142 | 63.1531 | -59.2667 | 63.1302 | -58.8776 | -59.3033 | -0.77362 | -3.2455 | 63.1073 | -59.2712 | 63.2492 | -59.1431 | -59.2987 | -59.0744 | -0.064087 | -0.050354 | -0.073242 | 0.32501 | 58.429 | -0.10071 | 58.493 | -0.036621 | -0.068664 | -0.09613 | 0.045777 | 0.05951 | 0.12817 | -0.09613 | 0.19684 | -0.027466 | 0.3891 | 122.3969 | 0.12817 | 122.5204 | 122.4197 | 122.3785 | 122.3557 | 122.3099 | -122.4701 | -122.4747 | 122.3328 | 122.4518 | 59.0012 | 55.957
1107.7656 | 122.6852 | -59.1843 | 63.2034 | -0.041122 | 0.00063028 | 0.061171 | 0.1018 | 0.0010253 | -0.002713 | -0.001175 | -0.052185 | -0.001128 | 0.065674 | 0.061049 | -0.017391 | 0.0014141 | -0.00096131 | -0.17853 | 63.1531 | -59.2621 | 63.2355 | -59.0103 | -59.4498 | -0.74158 | -3.5431 | 63.1302 | -59.23 | 63.2675 | -59.111 | -59.3079 | -59.0607 | -0.07782 | -0.050354 | 0.032044 | 0.17395 | 58.4427 | -0.2655 | 58.5205 | -0.18768 | -0.045777 | -0.073242 | 0.064087 | 0.073242 | 0.1236 | -0.1236 | 0.16937 | -0.077819 | 0.25177 | 122.4976 | 0.11902 | 122.4976 | 122.4152 | 122.3602 | 122.3373 | 122.3145 | -122.4655 | -122.4335 | 122.4197 | 122.4518 | 59.0057 | 55.6412
1108.7656 | 122.6898 | -59.1293 | 63.2629 | -0.12505 | 0.00084388 | 0.062025 | 0.10159 | -0.0053833 | -0.0029266 | -0.0030976 | -0.036926 | 0.00015377 | 0.062042 | 0.060836 | -0.0191 | 0.0022687 | 0.0013885 | -0.09613 | 63.2172 | -59.2438 | 63.2812 | -58.9417 | -59.3399 | -0.72327 | -3.566 | 63.1577 | -59.1751 | 63.3224 | -59.024 | -59.2209 | -58.992 | -0.11444 | -0.045776 | 0.018311 | 0.18768 | 58.4061 | -0.21057 | 58.5205 | -0.096131 | -0.045777 | -0.10529 | 0.05951 | 0.10529 | 0.13733 | -0.091553 | 0.18311 | -0.045776 | 0.30212 | 122.525 | 0.15106 | 122.4976 | 122.4609 | 122.3328 | 122.3465 | 122.287 | -122.5067 | -122.438 | 122.4106 | 122.4518 | 59.0332 | 55.5634
1109.7656 | 122.6898 | -59.1843 | 63.2492 | -0.07164 | -0.00065152 | 0.060103 | 0.10073 | -0.0030335 | 0.0013458 | -0.0043792 | -0.036926 | -0.001128 | 0.06482 | 0.051436 | -0.019314 | 0.0029095 | -0.0013885 | -0.20142 | 63.1805 | -59.23 | 63.2172 | -59.0561 | -59.436 | -0.87433 | -3.8635 | 63.1622 | -59.2209 | 63.2721 | -59.0927 | -59.2712 | -59.0561 | -0.045777 | -0.068665 | -0.032044 | 0.12817 | 58.3099 | -0.25177 | 58.3557 | -0.20599 | -0.036621 | -0.086976 | 0.022888 | 0.091553 | 0.12817 | -0.086975 | 0.16479 | -0.050354 | 0.17395 | 122.4472 | 0.12817 | 122.493 | 122.4106 | 122.3831 | 122.3648 | 122.3465 | -122.4792 | -122.4701 | 122.4014 | 122.4564 | 58.9828 | 55.3207
1110.7656 | 122.6852 | -59.1248 | 63.2446 | -0.1403 | 0.0021255 | 0.060957 | 0.1018 | -0.0017517 | -0.0014312 | -0.00074776 | -0.046081 | -0.00091423 | 0.06482 | 0.062117 | -0.018886 | 0.0016277 | -0.0033111 | -0.21057 | 63.2126 | -59.2346 | 63.3957 | -59.0652 | -59.5184 | -1.0071 | -4.1519 | 63.1622 | -59.198 | 63.2858 | -59.079 | -59.2758 | -59.024 | -0.10986 | -0.032044 | 0.15106 | 0.059509 | 58.1177 | -0.39368 | 58.2275 | -0.28381 | -0.073242 | -0.082398 | 0.041199 | 0.045777 | 0.10071 | -0.15106 | 0.17395 | -0.07782 | 0.16937 | 122.6303 | 0.11902 | 122.4838 | 122.4472 | 122.3602 | 122.3373 | 122.287 | -122.4792 | -122.4426 | 122.5204 | 122.4106 | 58.9142 | 54.9728
1111.7656 | 122.6486 | -59.1614 | 63.2126 | -0.10216 | -0.00043792 | 0.062666 | 0.10159 | -0.0045289 | -0.001004 | -0.00053396 | -0.033874 | -0.0034778 | 0.061402 | 0.067031 | -0.016537 | 0.0016277 | -0.00096131 | -0.20142 | 63.1714 | -59.2575 | 63.2172 | -59.0195 | -59.4177 | -1.0071 | -3.9734 | 63.1897 | -59.1934 | 63.2584 | -59.0836 | -59.2987 | -59.0744 | -0.09613 | -0.041198 | 0.004578 | 0.14191 | 58.1543 | -0.25635 | 58.2504 | -0.16022 | -0.032043 | -0.022888 | 0.045777 | 0.07782 | 0.086975 | -0.13733 | 0.11902 | -0.10529 | 0.23804 | 122.4747 | 0.10986 | 122.4518 | 122.4289 | 122.3831 | 122.3328 | 122.3511 | -122.4701 | -122.406 | 122.3785 | 122.4197 | 58.96 | 55.188
1112.7656 | 122.6944 | -59.1568 | 63.2126 | -0.12505 | 0.0014847 | 0.061385 | 0.10052 | 0.0023071 | -0.0016448 | -0.00096136 | -0.033874 | -0.0017688 | 0.065674 | 0.060836 | -0.018673 | -0.0030719 | -0.00096131 | -0.21515 | 63.1577 | -59.2758 | 63.2172 | -59.024 | -59.4315 | -0.95673 | -4.0649 | 63.1668 | -59.23 | 63.4277 | -59.2804 | -59.3308 | -59.0652 | -0.11902 | -0.054931 | 0.004578 | 0.13275 | 58.2001 | -0.27466 | 58.3191 | -0.15564 | -0.073243 | -0.045776 | 0.21515 | -0.1236 | 0.091552 | -0.17395 | 0.16479 | -0.10071 | 0.25177 | 122.493 | -0.050354 | 122.6578 | 122.4335 | 122.3969 | 122.3145 | 122.3236 | -122.4884 | -122.4426 | 122.374 | 122.5845 | 58.9417 | 55.0919
1113.7656 | 122.6257 | -59.1476 | 63.3087 | -0.010605 | -0.00086512 | 0.061385 | 0.10266 | 0.0027343 | -0.0024994 | -0.0030976 | -0.091858 | 0.001222 | 0.063538 | 0.067885 | -0.0191 | 0.0035503 | -0.00053411 | -0.15564 | 63.2492 | -59.2758 | 63.1989 | -59.0469 | -59.4543 | -0.95673 | -4.1153 | 63.2309 | -59.1843 | 63.2584 | -59.1064 | -59.3216 | -59.0652 | -0.12817 | -0.059509 | -0.10986 | 0.10071 | 58.1909 | -0.3067 | 58.3191 | -0.17853 | -0.036621 | -0.07782 | -0.050354 | 0.041199 | 0.082397 | -0.17395 | 0.11902 | -0.13733 | 0.22888 | 122.4747 | 0.07782 | 122.4426 | 122.525 | 122.4152 | 122.3969 | 122.3785 | -122.5845 | -122.493 | 122.3465 | 122.406 | 58.992 | 55.0323
1114.7656 | 122.7127 | -59.1339 | 63.2263 | -0.086899 | 0.00084388 | 0.063734 | 0.10202 | 0.0040161 | -0.0020722 | -0.00096136 | -0.052185 | -0.0015552 | 0.063751 | 0.065108 | -0.018673 | 0.0024823 | -0.0035247 | -0.19226 | 63.1851 | -59.2438 | 63.2538 | -58.9462 | -59.3903 | -1.0803 | -4.1199 | 63.1531 | -59.2163 | 63.3224 | -59.0652 | -59.2392 | -59.0195 | -0.10986 | -0.041198 | 0.027466 | 0.18768 | 58.0536 | -0.25635 | 58.1635 | -0.14648 | -0.082398 | -0.073242 | 0.096131 | 0.068664 | 0.11444 | -0.10529 | 0.19684 | -0.022888 | 0.29755 | 122.4976 | 0.15106 | 122.5388 | 122.4289 | 122.3694 | 122.319 | 122.287 | -122.4701 | -122.4426 | 122.3877 | 122.4564 | 58.9416 | 55.014
1115.7656 | 122.6761 | -59.1705 | 63.2217 | -0.079269 | 0.00063028 | 0.06053 | 0.10009 | -0.0013245 | 6.4004e-05 | -0.001175 | -0.039978 | -0.0024096 | 0.065247 | 0.06639 | -0.019741 | 0.0026959 | -0.00032051 | -0.21515 | 63.1714 | -59.2621 | 63.208 | -58.9874 | -59.4223 | -1.1993 | -4.248 | 63.1622 | -59.2163 | 63.2858 | -59.1064 | -59.2987 | -59.0469 | -0.091553 | -0.050354 | -0.013733 | 0.18311 | 57.9712 | -0.25177 | 58.0627 | -0.16022 | -0.045777 | -0.05951 | 0.064087 | 0.064087 | 0.1236 | -0.12817 | 0.16937 | -0.082397 | 0.27466 | 122.4701 | 0.10986 | 122.5021 | 122.4335 | 122.3785 | 122.3419 | 122.3328 | -122.4838 | -122.4381 | 122.3785 | 122.4564 | 58.9554 | 54.9225
1116.7656 | 122.6807 | -59.1568 | 63.2584 | -0.10216 | -0.0012923 | 0.061812 | 0.099879 | -0.0026063 | -0.001004 | -0.0041656 | -0.0064086 | -0.00091423 | 0.064606 | 0.060195 | -0.016323 | 0.0029095 | 0.00032049 | -0.2243 | 63.1714 | -59.2346 | 63.208 | -59.0103 | -59.4269 | -1.236 | -4.3304 | 63.1897 | -59.1568 | 63.2812 | -59.1019 | -59.2667 | -59.0332 | -0.07782 | -0.086975 | -0.050354 | 0.14648 | 57.9208 | -0.27008 | 57.9987 | -0.19226 | 0 | -0.068665 | 0.022888 | 0.054931 | 0.1236 | -0.10986 | 0.1236 | -0.10986 | 0.2243 | 122.4426 | 0.054931 | 122.438 | 122.406 | 122.3465 | 122.3282 | 122.3465 | -122.493 | -122.4152 | 122.3648 | 122.438 | 58.9325 | 54.8264
1117.7656 | 122.7722 | -59.1614 | 63.2996 | -0.10979 | 0.00084388 | 0.062666 | 0.10095 | -0.00068368 | -0.0016448 | 0.00053404 | -0.039978 | 0.0014356 | 0.06247 | 0.060836 | -0.01675 | 0.0026959 | -0.0030975 | -0.23346 | 63.1943 | -59.2392 | 63.208 | -59.0149 | -59.436 | -1.2543 | -4.3304 | 63.1805 | -59.1797 | 63.295 | -59.0652 | -59.2712 | -59.0424 | -0.07782 | -0.10529 | -0.091553 | 0.14648 | 57.9071 | -0.27466 | 57.9849 | -0.19684 | -0.01831 | -0.11902 | -0.004578 | 0.09613 | 0.11902 | -0.10986 | 0.13733 | -0.091553 | 0.2243 | 122.4472 | 0.11444 | 122.4747 | 122.4335 | 122.3602 | 122.3557 | 122.3419 | -122.5388 | -122.4792 | 122.3694 | 122.4564 | 58.9279 | 54.8309
1118.7656 | 122.6807 | -59.1202 | 63.2812 | -0.086899 | 0.0012711 | 0.06053 | 0.10244 | 0.0033753 | -0.0022858 | -0.0013886 | -0.027771 | 0.00015377 | 0.06546 | 0.063826 | -0.018673 | 0.00077333 | 0.00010689 | -0.27008 | 63.2217 | -59.1705 | 63.2812 | -58.9417 | -59.3491 | -1.3916 | -4.4998 | 63.176 | -59.1751 | 63.3179 | -59.0469 | -59.2346 | -59.0012 | -0.050354 | -0.059509 | 0 | 0.17853 | 57.7286 | -0.22888 | 57.7789 | -0.17853 | -0.054932 | -0.10529 | 0.036621 | 0.073242 | 0.11902 | -0.11444 | 0.17395 | -0.059509 | 0.22888 | 122.4518 | 0.12817 | 122.493 | 122.3923 | 122.3511 | 122.3419 | 122.2961 | -122.4518 | -122.4564 | 122.4014 | 122.438 | 58.8501 | 54.6204
1119.7656 | 122.6761 | -59.1293 | 63.2401 | -0.16319 | -0.00065152 | 0.062666 | 0.10137 | 0.0029479 | -0.0024994 | -0.00032036 | -0.055237 | -0.00027343 | 0.063324 | 0.059981 | -0.017178 | 0.0014141 | 0.00010689 | -0.2655 | 63.1851 | -59.2392 | 63.2584 | -58.9554 | -59.4177 | -1.236 | -4.3808 | 63.1714 | -59.1797 | 63.3179 | -59.0515 | -59.2667 | -59.0286 | -0.10986 | -0.054931 | 0.018311 | 0.17395 | 57.8934 | -0.28839 | 58.0032 | -0.17853 | -0.050354 | -0.068664 | 0.07782 | 0.077819 | 0.10071 | -0.13733 | 0.15106 | -0.086976 | 0.28381 | 122.4976 | 0.12817 | 122.4976 | 122.4243 | 122.3511 | 122.3145 | 122.3007 | -122.4792 | -122.4197 | 122.3877 | 122.4472 | 58.8638 | 54.7485
1120.7656 | 122.6944 | -59.1385 | 63.2401 | -0.079269 | 0.0029801 | 0.062453 | 0.10009 | -0.00089728 | 0.000705 | 0.0024566 | -0.052185 | -0.0015552 | 0.064179 | 0.058913 | -0.017391 | 0.0012005 | -0.0043793 | -0.22888 | 63.1989 | -59.2117 | 63.2629 | -58.9279 | -59.3948 | -1.3 | -4.3625 | 63.1851 | -59.1843 | 63.3316 | -59.0515 | -59.2438 | -59.0057 | -0.073242 | -0.041198 | 0.022888 | 0.21057 | 57.8384 | -0.25635 | 57.9117 | -0.1831 | -0.045776 | -0.054931 | 0.091553 | 0.086975 | 0.13275 | -0.10529 | 0.17853 | -0.059509 | 0.28381 | 122.4747 | 0.13275 | 122.5159 | 122.4106 | 122.3694 | 122.3373 | 122.3236 | -122.4518 | -122.4243 | 122.4014 | 122.4701 | 58.9096 | 54.776
1121.7656 | 122.7448 | -59.1202 | 63.2492 | -0.10979 | 0.00020288 | 0.062453 | 0.10202 | 0.0031617 | -0.0014312 | -0.00096136 | -0.070496 | -5.9826e-05 | 0.06247 | 0.058913 | -0.024441 | 0.00055973 | -0.0011749 | -0.24719 | 63.1989 | -59.2438 | 63.2904 | -58.9417 | -59.3765 | -1.2726 | -4.39 | 63.176 | -59.1888 | 63.4872 | -59.0927 | -59.2575 | -58.9874 | -0.1236 | -0.050354 | 0.041198 | 0.17853 | 57.8476 | -0.25635 | 57.9712 | -0.13275 | -0.068665 | -0.073243 | 0.23804 | 0.027466 | 0.13275 | -0.13733 | 0.20142 | -0.068664 | 0.30212 | 122.5342 | 0.096131 | 122.6761 | 122.4426 | 122.3648 | 122.319 | 122.2961 | -122.493 | -122.4381 | 122.4106 | 122.6074 | 58.873 | 54.7302
1122.7656 | 122.7173 | -59.1019 | 63.2538 | -0.14793 | 0.0027665 | 0.062239 | 0.1033 | 0.00059812 | -0.0014312 | 0.0043792 | -0.079651 | 0.0010084 | 0.062683 | 0.064681 | -0.019741 | 0.0035503 | -0.0013885 | -0.27008 | 63.1577 | -59.2209 | 63.3224 | -58.9096 | -59.3491 | -1.4008 | -4.5731 | 63.1851 | -59.1614 | 63.3682 | -59.0057 | -59.23 | -58.96 | -0.11902 | -0.09613 | 0.068665 | 0.19226 | 57.7011 | -0.24719 | 57.8201 | -0.12817 | -0.059509 | -0.068664 | 0.11444 | 0.096131 | 0.14191 | -0.12817 | 0.20142 | -0.068665 | 0.31128 | 122.5433 | 0.15564 | 122.5296 | 122.3785 | 122.3465 | 122.2595 | 122.287 | -122.4747 | -122.4152 | 122.4243 | 122.4701 | 58.8318 | 54.5288
1123.7656 | 122.6898 | -59.1156 | 63.1989 | -0.13267 | 0.00041648 | 0.064162 | 0.099666 | -0.0043151 | -0.0016448 | -0.00032036 | -0.046081 | -5.9826e-05 | 0.062256 | 0.060408 | -0.016964 | 0.0026959 | 0.00053409 | -0.20142 | 63.1851 | -59.23 | 63.2767 | -58.9279 | -59.3994 | -1.3504 | -4.7424 | 63.1348 | -59.1705 | 63.3362 | -59.024 | -59.2209 | -59.0012 | -0.11444 | -0.013733 | 0.077819 | 0.18768 | 57.7652 | -0.28381 | 57.8796 | -0.16937 | -0.054931 | -0.064087 | 0.13733 | 0.091553 | 0.11444 | -0.10529 | 0.16937 | -0.050354 | 0.30212 | 122.5067 | 0.14648 | 122.5067 | 122.4152 | 122.3053 | 122.3007 | 122.2504 | -122.4289 | -122.3694 | 122.3923 | 122.4518 | 58.9142 | 54.3732
1124.7656 | 122.7127 | -59.1522 | 63.2217 | 0.012284 | 0.0012711 | 0.063307 | 0.10159 | 0.0040161 | 0.0013458 | -0.00010676 | -0.067444 | -0.00091423 | 0.063965 | 0.057204 | -0.017391 | 0.0024823 | -0.0020295 | -0.21057 | 63.1622 | -59.2346 | 63.2538 | -58.9645 | -59.4131 | -1.4557 | -4.6967 | 63.1622 | -59.2026 | 63.3224 | -59.0149 | -59.2438 | -59.0103 | -0.082397 | -0.05951 | 0.032043 | 0.18768 | 57.6965 | -0.26093 | 57.7789 | -0.17853 | -0.050354 | -0.05951 | 0.10071 | 0.13733 | 0.14191 | -0.091552 | 0.19226 | -0.041198 | 0.27008 | 122.4884 | 0.18768 | 122.525 | 122.3969 | 122.3648 | 122.3145 | 122.3145 | -122.4564 | -122.4243 | 122.406 | 122.4747 | 58.9417 | 54.4556
1125.7656 | 122.7127 | -59.166 | 63.1989 | -0.17082 | 0.0014847 | 0.065016 | 0.10052 | 0.0033753 | -0.0014312 | -0.0013886 | 0.033264 | -0.0017688 | 0.063538 | 0.069808 | -0.017605 | 0.0039777 | -0.00032051 | -0.17395 | 63.1302 | -59.2804 | 63.2401 | -58.9508 | -59.6558 | -1.5381 | -4.6692 | 63.1348 | -59.2163 | 63.3316 | -59.0515 | -59.2438 | -59.0103 | -0.11444 | -0.068665 | 0.041198 | 0.21515 | 57.6279 | -0.48981 | 57.7423 | -0.37537 | -0.050354 | -0.064087 | 0.13275 | 0.11444 | 0.15564 | -0.077819 | 0.20599 | -0.027465 | 0.32959 | 122.5204 | 0.1648 | 122.5479 | 122.4106 | 122.3511 | 122.2961 | 122.3007 | -122.4792 | -122.4152 | 122.406 | 122.4976 | 58.992 | 54.4968
1126.7656 | 122.7081 | -59.1797 | 63.1714 | -0.094528 | 0.0021255 | 0.062025 | 0.1033 | -0.00046988 | -0.0018586 | 0.0018158 | -0.09491 | -0.00027343 | 0.064179 | 0.061263 | -0.019955 | 0.0033367 | -0.0016021 | -0.20142 | 63.1439 | -59.2804 | 63.2263 | -58.9737 | -59.4406 | -1.4236 | -4.8294 | 63.1256 | -59.2255 | 63.3087 | -59.0561 | -59.3399 | -59.1751 | -0.10071 | -0.027466 | 0.054931 | 0.20599 | 57.756 | -0.26093 | 57.8568 | -0.16022 | -0.045777 | -0.045777 | 0.13733 | 0.1236 | 0.004577 | -0.16022 | 0.050354 | -0.11444 | 0.3067 | 122.5067 | 0.16937 | 122.5342 | 122.4243 | 122.3511 | 122.3236 | 122.3053 | -122.4518 | -122.3969 | 122.406 | 122.4884 | 58.9783 | 54.3503
1127.7656 | 122.6303 | -59.1751 | 63.2492 | -0.094528 | -1.0718e-05 | 0.061385 | 0.10266 | 0.00038452 | -0.0029266 | 0.00010684 | -0.091858 | 0.00058097 | 0.064179 | 0.065108 | -0.018459 | 0.0031231 | 0.00053409 | -0.2655 | 63.2263 | -59.2667 | 63.1531 | -59.079 | -59.5047 | -1.5656 | -4.9896 | 63.208 | -59.2163 | 63.2584 | -59.1248 | -59.3445 | -59.0881 | -0.091553 | -0.022889 | -0.096131 | 0.096131 | 57.6096 | -0.32959 | 57.7011 | -0.23804 | -0.041199 | -0.041199 | 0.009155 | 0.050354 | 0.086975 | -0.16937 | 0.12817 | -0.12817 | 0.18768 | 122.4197 | 0.091553 | 122.4747 | 122.493 | 122.4243 | 122.4014 | 122.3831 | -122.5159 | -122.4655 | 122.3282 | 122.4335 | 58.9096 | 54.1855
1128.7656 | 122.612 | -59.1705 | 63.2355 | -0.19371 | 0.00041648 | 0.062453 | 0.10437 | -0.0021789 | -0.0022858 | -0.00032036 | -0.11017 | 0.0027174 | 0.065247 | 0.064681 | -0.0191 | 0.00098693 | -0.0018157 | -0.21515 | 63.2126 | -59.2712 | 63.1348 | -59.079 | -59.5184 | -1.6479 | -4.9942 | 63.2126 | -59.2484 | 63.2446 | -59.1476 | -59.3628 | -59.0927 | -0.10071 | -0.022889 | -0.10071 | 0.091553 | 57.5226 | -0.3479 | 57.6233 | -0.24719 | -0.07782 | -0.022889 | 0.009155 | 0.022888 | 0.07782 | -0.19226 | 0.15564 | -0.11444 | 0.19226 | 122.406 | 0.10071 | 122.493 | 122.4838 | 122.4609 | 122.3831 | 122.3831 | -122.5067 | -122.4838 | 122.3053 | 122.4152 | 58.9554 | 54.1763
1129.7656 | 122.7173 | -59.1293 | 63.1989 | -0.12505 | 0.00063028 | 0.058607 | 0.10116 | 0.0033753 | 6.4004e-05 | 0.0018158 | -0.076599 | 0.0020764 | 0.064606 | 0.061904 | -0.016964 | 0.0035503 | 0.0011749 | -0.22888 | 63.1943 | -59.2621 | 63.1943 | -59.0057 | -59.4269 | -1.5289 | -5.3055 | 63.1302 | -59.2072 | 63.3179 | -59.0332 | -59.2575 | -59.0103 | -0.13275 | -0.004578 | -0.004578 | 0.1236 | 57.6004 | -0.29755 | 57.7332 | -0.16479 | -0.07782 | -0.068665 | 0.11902 | 0.09613 | 0.11902 | -0.12817 | 0.19684 | -0.050354 | 0.25635 | 122.4564 | 0.17395 | 122.525 | 122.4564 | 122.3373 | 122.3236 | 122.2595 | -122.4609 | -122.406 | 122.3236 | 122.4472 | 58.9005 | 53.8239
1130.7656 | 122.7036 | -59.1705 | 63.2172 | -0.12505 | -1.0718e-05 | 0.06053 | 0.1018 | -0.0017517 | -0.0005768 | 0.00010684 | -0.06134 | 0.0027174 | 0.064179 | 0.060195 | -0.017391 | 0.0039777 | 0.0011749 | -0.25635 | 63.1943 | -59.2941 | 63.1714 | -59.0195 | -59.4772 | -1.5701 | -5.7037 | 63.1622 | -59.2346 | 63.2858 | -59.0561 | -59.2712 | -59.0378 | -0.1236 | -0.022888 | -0.045776 | 0.15106 | 57.6004 | -0.3067 | 57.724 | -0.18311 | -0.064087 | -0.054932 | 0.068665 | 0.11444 | 0.13275 | -0.10071 | 0.19684 | -0.036621 | 0.27466 | 122.4655 | 0.17853 | 122.5204 | 122.4884 | 122.3969 | 122.3648 | 122.3328 | -122.5113 | -122.4518 | 122.3419 | 122.4564 | 58.9142 | 53.4668
1131.7656 | 122.6669 | -59.1751 | 63.2126 | -0.06401 | 0.0014847 | 0.063948 | 0.10351 | -0.00068368 | -0.0029266 | -0.0016022 | -0.070496 | -5.9826e-05 | 0.064606 | 0.066817 | -0.017818 | 0.0018413 | -0.0028839 | -0.26093 | 63.1851 | -59.2712 | 63.1348 | -59.0744 | -59.5276 | -1.5289 | -5.2963 | 63.1531 | -59.2529 | 63.2584 | -59.1248 | -59.3491 | -59.0744 | -0.09613 | -0.027465 | -0.077819 | 0.10071 | 57.6462 | -0.35248 | 57.7423 | -0.25635 | -0.07782 | -0.059509 | 0.045777 | 0.050354 | 0.10071 | -0.17395 | 0.17853 | -0.09613 | 0.19684 | 122.406 | 0.12817 | 122.5113 | 122.4564 | 122.406 | 122.3602 | 122.3282 | -122.4838 | -122.4655 | 122.3099 | 122.4335 | 58.9142 | 53.8788
1132.7656 | 122.6303 | -59.1705 | 63.2492 | -0.056381 | -0.00086512 | 0.061171 | 0.10266 | 0.0027343 | -0.0001496 | -0.0030976 | -0.067444 | 0.0014356 | 0.064606 | 0.063399 | -0.019527 | 0.0035503 | 0.00074769 | -0.28381 | 63.2217 | -59.2575 | 63.1485 | -59.079 | -59.4955 | -1.5793 | -5.3421 | 63.208 | -59.23 | 63.2767 | -59.1248 | -59.317 | -59.0607 | -0.086975 | -0.027466 | -0.10071 | 0.091553 | 57.5912 | -0.32501 | 57.6782 | -0.23804 | -0.05951 | -0.041199 | 0.027465 | 0.045776 | 0.10986 | -0.14648 | 0.16937 | -0.086975 | 0.17853 | 122.406 | 0.10529 | 122.5067 | 122.4792 | 122.4381 | 122.3923 | 122.3785 | -122.5067 | -122.4792 | 122.319 | 122.4472 | 58.8867 | 53.8284
1133.7656 | 122.6166 | -59.1568 | 63.2767 | -0.18608 | -0.00043792 | 0.061812 | 0.10266 | 0.0050843 | -0.0022858 | -0.001175 | -0.06134 | -5.9826e-05 | 0.063751 | 0.06404 | -0.018246 | 0.0026959 | -0.0028839 | -0.2655 | 63.2446 | -59.2667 | 63.1302 | -59.079 | -59.523 | -1.5884 | -5.365 | 63.1989 | -59.2438 | 63.2355 | -59.1293 | -59.3536 | -59.0881 | -0.10986 | -0.032043 | -0.14648 | 0.07782 | 57.5684 | -0.36621 | 57.6782 | -0.25635 | -0.086975 | -0.077819 | -0.041198 | 0.027466 | 0.068664 | -0.19684 | 0.15564 | -0.10986 | 0.18768 | 122.3969 | 0.11444 | 122.4792 | 122.5113 | 122.4426 | 122.4014 | 122.3557 | -122.5433 | -122.5204 | 122.287 | 122.3923 | 58.8913 | 53.7918
1134.7656 | 122.612 | -59.1888 | 63.2767 | -0.13267 | -0.00086512 | 0.062453 | 0.10223 | 0.0012391 | -0.0012176 | 0.0030976 | -0.085754 | 0.00036737 | 0.066315 | 0.058486 | -0.018032 | 0.0022687 | -0.0022431 | -0.21057 | 63.208 | -59.3033 | 63.1348 | -59.0927 | -59.5276 | -1.6022 | -4.7012 | 63.1805 | -59.23 | 63.2034 | -59.1751 | -59.404 | -59.1064 | -0.11444 | -0.068664 | -0.14191 | 0.096131 | 57.5867 | -0.33875 | 57.7011 | -0.2243 | -0.041199 | -0.09613 | -0.073242 | 0.013733 | 0.082398 | -0.21515 | 0.1236 | -0.17395 | 0.21057 | 122.4381 | 0.054932 | 122.4335 | 122.5113 | 122.4106 | 122.3969 | 122.3694 | -122.58 | -122.5067 | 122.3236 | 122.3923 | 58.9783 | 54.4876
1135.7656 | 122.5891 | -59.2117 | 63.2584 | -0.11742 | 0.0021255 | 0.061171 | 0.10287 | 0.00038452 | -0.004422 | -0.00053396 | -0.079651 | 0.00015377 | 0.066956 | 0.055495 | -0.017391 | 0.0050457 | -0.0011749 | -0.18768 | 63.2263 | -59.2575 | 63.1622 | -59.0424 | -59.491 | -1.6983 | -4.7333 | 63.1714 | -59.2484 | 63.2217 | -59.1293 | -59.3719 | -59.1064 | -0.045776 | -0.032044 | -0.096131 | 0.16937 | 57.5134 | -0.27924 | 57.5592 | -0.23346 | -0.036621 | -0.086975 | -0.036621 | 0.082398 | 0.10529 | -0.16022 | 0.14191 | -0.1236 | 0.21515 | 122.4197 | 0.11902 | 122.4701 | 122.4838 | 122.4197 | 122.438 | 122.3831 | -122.5159 | -122.5067 | 122.374 | 122.4335 | 59.024 | 54.4785
1136.8281 | 122.5937 | -59.198 | 63.2538 | -0.086899 | -0.0021469 | 0.061385 | 0.10415 | 0.0012391 | -0.001004 | 0.00032044 | -0.11017 | -0.00048703 | 0.06482 | 0.058913 | -0.019314 | 0.0029095 | -0.00010671 | -0.25177 | 63.2126 | -59.317 | 63.0936 | -59.1431 | -59.5459 | -1.9135 | -4.3579 | 63.1897 | -59.2255 | 63.1805 | -59.1385 | -59.3903 | -59.1293 | -0.11902 | -0.041199 | -0.16022 | 0.054932 | 57.2845 | -0.3479 | 57.4036 | -0.22888 | -0.027466 | -0.064087 | -0.073242 | 0.059509 | 0.068665 | -0.19226 | 0.096131 | -0.16479 | 0.17395 | 122.4106 | 0.086975 | 122.406 | 122.5296 | 122.4152 | 122.4106 | 122.3877 | -122.5708 | -122.4792 | 122.2916 | 122.3785 | 58.9462 | 54.8401
1137.7656 | 122.5891 | -59.1843 | 63.2629 | -0.12505 | -0.00043792 | 0.062666 | 0.10287 | 0.0027343 | -0.0033538 | -0.0041656 | -0.073547 | 0.0035718 | 0.066101 | 0.062758 | -0.018032 | 0.0014141 | 0.0011749 | -0.41199 | 63.1485 | -59.2804 | 63.1439 | -59.1431 | -59.5047 | -1.5244 | -4.8843 | 63.1805 | -59.2255 | 63.2172 | -59.166 | -59.3719 | -59.1064 | -0.096131 | -0.11444 | -0.11902 | 0.041199 | 57.6599 | -0.32043 | 57.756 | -0.2243 | -0.041199 | -0.082397 | -0.045776 | 0.01831 | 0.07782 | -0.18768 | 0.11902 | -0.14648 | 0.13733 | 122.4243 | 0.059509 | 122.4426 | 122.4289 | 122.406 | 122.3328 | 122.3648 | -122.5433 | -122.4884 | 122.3282 | 122.4014 | 58.7723 | 54.2999
1138.7656 | 122.5891 | -59.2163 | 63.2309 | -0.11742 | 0.0012711 | 0.063307 | 0.10565 | 0.0025207 | -0.0005768 | 0.00032044 | 0.051575 | 0.0018628 | 0.065033 | 0.064467 | -0.018459 | 0.0020551 | 0.0011749 | -0.28839 | 63.1897 | -59.2941 | 63.176 | -59.436 | -59.9167 | -1.4053 | -4.5502 | 63.1805 | -59.2392 | 63.2126 | -59.2026 | -59.4086 | -59.1248 | -0.077819 | -0.041199 | -0.054932 | -0.21973 | 57.811 | -0.70038 | 57.8888 | -0.62256 | -0.022888 | -0.050354 | -0.018311 | 0.013733 | 0.091553 | -0.19226 | 0.11444 | -0.16937 | -0.14191 | 122.4701 | 0.036621 | 122.4518 | 122.4838 | 122.4197 | 122.406 | 122.3969 | -122.525 | -122.4701 | 122.3923 | 122.4289 | 58.9279 | 54.6661
1139.7656 | 122.6212 | -59.2392 | 63.2217 | -0.07164 | 0.0019119 | 0.062025 | 0.10159 | 0.0025207 | -0.0016448 | -0.001175 | -0.04303 | 0.001222 | 0.066315 | 0.063826 | -0.018673 | 0.0024823 | -0.0016021 | -0.28839 | 63.1851 | -59.3262 | 63.0844 | -59.1339 | -59.5367 | -1.5793 | -4.0787 | 63.121 | -59.2758 | 63.1805 | -59.166 | -59.404 | -59.1202 | -0.086975 | -0.036621 | -0.13733 | 0.10529 | 57.6599 | -0.29755 | 57.7469 | -0.21057 | -0.036621 | -0.10071 | -0.041199 | 0.073242 | 0.11902 | -0.1648 | 0.15564 | -0.12817 | 0.19226 | 122.4106 | 0.10986 | 122.4564 | 122.5113 | 122.3969 | 122.4243 | 122.3602 | -122.5479 | -122.4976 | 122.3236 | 122.4197 | 58.9508 | 55.1605
1140.7656 | 122.5845 | -59.2575 | 63.1851 | -0.10979 | 0.0036209 | 0.063094 | 0.10372 | -0.00068368 | 0.0004914 | -0.002243 | -0.052185 | -0.0017688 | 0.064179 | 0.061049 | -0.018886 | 0.0020551 | -0.0028839 | -0.23804 | 63.1668 | -59.3308 | 63.0753 | -59.1339 | -59.5688 | -1.5152 | -4.1931 | 63.1531 | -59.2667 | 63.1393 | -59.2255 | -59.4589 | -59.1705 | -0.073243 | -0.018311 | -0.10986 | 0.1236 | 57.7423 | -0.31128 | 57.8156 | -0.23804 | -0.009156 | -0.032044 | -0.045777 | 0.032043 | 0.086975 | -0.20142 | 0.096131 | -0.19226 | 0.19684 | 122.406 | 0.041199 | 122.406 | 122.4976 | 122.4197 | 122.4243 | 122.4106 | -122.5159 | -122.4518 | 122.3328 | 122.3969 | 59.0195 | 55.0644
1141.7656 | 122.6166 | -59.2026 | 63.2309 | -0.06401 | 0.0021255 | 0.062025 | 0.10266 | 0.0029479 | -0.0003632 | -0.0013886 | -0.049133 | -0.0015552 | 0.064179 | 0.065535 | -0.016964 | 0.00098693 | 0.00053409 | -0.21515 | 63.1668 | -59.2987 | 63.176 | -59.0332 | -59.4772 | -1.5472 | -4.1656 | 63.1805 | -59.2529 | 63.2217 | -59.1156 | -59.3491 | -59.1064 | -0.09613 | -0.064087 | -0.054932 | 0.16937 | 57.6553 | -0.27466 | 57.7515 | -0.17853 | -0.050354 | -0.050354 | -0.009155 | 0.086975 | 0.096131 | -0.14648 | 0.14648 | -0.09613 | 0.2655 | 122.4747 | 0.13733 | 122.4747 | 122.4655 | 122.4335 | 122.3694 | 122.3831 | -122.5296 | -122.4838 | 122.3785 | 122.4243 | 58.9874 | 55.0369
1142.7656 | 122.6257 | -59.1934 | 63.2675 | -0.11742 | 0.0012711 | 0.060744 | 0.10415 | 0.0014527 | -0.0016448 | -0.0043792 | -0.039978 | 0.0016492 | 0.066529 | 0.06404 | -0.017818 | 0.0020551 | -0.0016021 | -0.24719 | 63.2126 | -59.2575 | 63.1805 | -59.0195 | -59.4543 | -1.5152 | -4.129 | 63.1805 | -59.2438 | 63.2401 | -59.1019 | -59.3216 | -59.0744 | -0.064087 | -0.054932 | -0.086975 | 0.17395 | 57.6782 | -0.26093 | 57.7423 | -0.19684 | -0.050354 | -0.086975 | -0.027466 | 0.091552 | 0.11902 | -0.12817 | 0.16937 | -0.07782 | 0.23804 | 122.438 | 0.14191 | 122.4838 | 122.4701 | 122.4243 | 122.406 | 122.374 | -122.525 | -122.5113 | 122.374 | 122.4335 | 58.9462 | 55.0644
1143.7656 | 122.6349 | -59.2026 | 63.2675 | -0.094528 | 0.00041648 | 0.060744 | 0.10223 | 0.0014527 | -0.0005768 | 0.00074764 | -0.076599 | 0.0010084 | 0.065674 | 0.064467 | -0.017178 | 0.0024823 | 0.0052337 | -0.32044 | 63.2401 | -59.2804 | 63.1027 | -59.1339 | -59.5551 | -1.712 | -4.216 | 63.176 | -59.2438 | 63.0936 | -59.5001 | -59.1522 | -58.8913 | -0.07782 | -0.027466 | -0.16479 | 0.068665 | 57.4905 | -0.35248 | 57.5684 | -0.27466 | -0.041198 | -0.091553 | -0.17395 | -0.29755 | 0.31128 | 0.050354 | 0.35248 | 0.091552 | 0.14649 | 122.3831 | -0.25635 | 122.3373 | 122.5204 | 122.4197 | 122.4426 | 122.3785 | -122.5479 | -122.5113 | 122.3053 | 122.2961 | 58.8821 | 54.9866
1144.7656 | 122.5708 | -59.2117 | 63.2401 | -0.10216 | -0.00043792 | 0.062239 | 0.10052 | 0.0052979 | -0.0020722 | -0.00010676 | -0.039978 | 0.00058097 | 0.064179 | 0.059554 | -0.017818 | 0.0026959 | -0.0022431 | -0.31586 | 63.1851 | -59.285 | 63.1073 | -59.111 | -59.5322 | -1.7715 | -4.1153 | 63.1805 | -59.2621 | 63.1622 | -59.1797 | -59.4177 | -59.1614 | -0.073242 | -0.054931 | -0.13275 | 0.10071 | 57.4402 | -0.32043 | 57.5134 | -0.24719 | -0.050354 | -0.059509 | -0.07782 | 0.032044 | 0.050354 | -0.20599 | 0.10071 | -0.15564 | 0.17395 | 122.3923 | 0.082398 | 122.4243 | 122.4701 | 122.4426 | 122.3969 | 122.3923 | -122.525 | -122.5021 | 122.319 | 122.374 | 58.8959 | 55.0964
1145.7656 | 122.58 | -59.1934 | 63.2812 | -0.079269 | 0.00063028 | 0.061171 | 0.10116 | -0.00089728 | -0.0024994 | -0.00010676 | -0.04303 | -5.9826e-05 | 0.065033 | 0.059767 | -0.018246 | 0.0044049 | -0.0013885 | -0.31586 | 63.1805 | -59.2667 | 63.1302 | -59.0836 | -59.5047 | -1.7624 | -4.0695 | 63.2126 | -59.2346 | 63.1943 | -59.166 | -59.3994 | -59.1248 | -0.073243 | -0.10071 | -0.15106 | 0.10986 | 57.431 | -0.31128 | 57.5043 | -0.23804 | -0.041199 | -0.068665 | -0.086975 | 0.027465 | 0.068664 | -0.20599 | 0.10986 | -0.16479 | 0.18311 | 122.3969 | 0.068664 | 122.4289 | 122.4472 | 122.4472 | 122.374 | 122.406 | -122.5479 | -122.5159 | 122.3236 | 122.3877 | 58.8776 | 55.1239
1146.7656 | 122.6028 | -59.2072 | 63.2492 | -0.06401 | 0.0012711 | 0.061598 | 0.1018 | -0.0023925 | -0.001004 | -0.002243 | -0.049133 | 0.0020764 | 0.065888 | 0.061476 | -0.017391 | 0.0016277 | 0.0024567 | -0.32959 | 63.2034 | -59.2712 | 63.1393 | -59.0652 | -59.491 | -1.6525 | -3.7445 | 63.1668 | -59.2346 | 63.1805 | -59.1568 | -59.3719 | -59.1248 | -0.064087 | -0.045777 | -0.10986 | 0.14191 | 57.5546 | -0.28381 | 57.6187 | -0.21973 | -0.027466 | -0.082398 | -0.068665 | 0.050354 | 0.082397 | -0.1648 | 0.10986 | -0.13733 | 0.20599 | 122.4106 | 0.07782 | 122.4152 | 122.4747 | 122.4014 | 122.4106 | 122.374 | -122.5204 | -122.4838 | 122.3465 | 122.3877 | 58.8776 | 55.4626
1147.7656 | 122.6028 | -59.1934 | 63.2675 | -0.10216 | 0.0029801 | 0.061812 | 0.10287 | -0.00089728 | -0.002713 | -0.00010676 | -0.049133 | 0.003999 | 0.064606 | 0.063826 | -0.019955 | 0.00098693 | -0.0026703 | -0.3067 | 63.2126 | -59.2804 | 63.1577 | -59.0607 | -59.5047 | -1.6754 | -3.6072 | 63.1622 | -59.2529 | 63.1989 | -59.1476 | -59.3628 | -59.1064 | -0.086976 | -0.054932 | -0.10986 | 0.13275 | 57.518 | -0.31128 | 57.605 | -0.2243 | -0.05951 | -0.10529 | -0.068664 | 0.045776 | 0.086975 | -0.16937 | 0.14648 | -0.10986 | 0.21973 | 122.4381 | 0.10529 | 122.4518 | 122.493 | 122.4152 | 122.406 | 122.3557 | -122.5479 | -122.5204 | 122.3511 | 122.3923 | 58.8867 | 55.5862
1148.7656 | 122.6486 | -59.1705 | 63.2538 | -0.06401 | 0.0014847 | 0.06053 | 0.10287 | 0.0044433 | -0.0029266 | -0.0033112 | -0.030823 | 0.0010084 | 0.062897 | 0.066817 | -0.019314 | 0.0024823 | -0.00032051 | -0.27924 | 63.2126 | -59.2621 | 63.2217 | -59.0286 | -59.4452 | -1.5839 | -3.035 | 63.1668 | -59.2484 | 63.2446 | -59.1019 | -59.3079 | -59.0698 | -0.091553 | -0.041199 | -0.032043 | 0.14191 | 57.5867 | -0.27466 | 57.6782 | -0.1831 | -0.07782 | -0.086975 | -0.009155 | 0.068664 | 0.10071 | -0.13733 | 0.17853 | -0.059509 | 0.23346 | 122.4838 | 0.14648 | 122.493 | 122.4747 | 122.4152 | 122.3831 | 122.3373 | -122.5159 | -122.5021 | 122.3923 | 122.4152 | 58.8913 | 56.1356
1149.7656 | 122.6715 | -59.1888 | 63.2584 | -0.06401 | -0.00043792 | 0.060744 | 0.10095 | 0.00059812 | -0.002713 | -0.0026704 | -0.015564 | 0.0018628 | 0.06546 | 0.061904 | -0.018886 | 0.0033367 | -0.00053411 | -0.27466 | 63.2034 | -59.2529 | 63.1851 | -59.0057 | -59.4406 | -1.6342 | -3.1219 | 63.1393 | -59.2621 | 63.2401 | -59.0744 | -59.2896 | -59.0561 | -0.064087 | -0.054932 | -0.073242 | 0.18311 | 57.5546 | -0.25177 | 57.6187 | -0.18768 | -0.073242 | -0.11902 | -0.018311 | 0.11444 | 0.13275 | -0.10071 | 0.20599 | -0.027466 | 0.24719 | 122.4381 | 0.18768 | 122.5021 | 122.4564 | 122.4014 | 122.3923 | 122.3282 | -122.5113 | -122.5204 | 122.374 | 122.4289 | 58.9142 | 56.0669
1150.7656 | 122.6257 | -59.198 | 63.2629 | -0.10979 | 0.0025529 | 0.062239 | 0.10372 | -4.2682e-05 | -0.0007904 | 0.00053404 | -0.055237 | 0.0016492 | 0.063751 | 0.05699 | -0.016964 | 0.0044049 | -0.0022431 | -0.33417 | 63.2034 | -59.285 | 63.1348 | -59.0652 | -59.5093 | -1.7212 | -3.1998 | 63.1851 | -59.2346 | 63.1714 | -59.1476 | -59.3857 | -59.1248 | -0.086975 | -0.059509 | -0.12817 | 0.13275 | 57.4768 | -0.31128 | 57.5638 | -0.2243 | -0.036621 | -0.077819 | -0.091552 | 0.050354 | 0.073242 | -0.18768 | 0.10986 | -0.15106 | 0.21973 | 122.4197 | 0.086975 | 122.406 | 122.4884 | 122.4197 | 122.4014 | 122.3831 | -122.5479 | -122.4976 | 122.3328 | 122.3694 | 58.8638 | 55.9982
1151.7656 | 122.6257 | -59.1888 | 63.2629 | -0.14793 | -0.0012923 | 0.062025 | 0.10287 | 0.0023071 | -0.0020722 | 0.00032044 | -0.015564 | -0.00027343 | 0.064392 | 0.059981 | -0.018032 | 0.0016277 | -0.0013885 | -0.34332 | 63.1989 | -59.2667 | 63.1577 | -59.0286 | -59.4818 | -1.7303 | -3.0487 | 63.176 | -59.2255 | 63.1989 | -59.1385 | -59.3536 | -59.1019 | -0.07782 | -0.064086 | -0.10529 | 0.16022 | 57.4585 | -0.29297 | 57.5363 | -0.21515 | -0.036621 | -0.086975 | -0.064086 | 0.050354 | 0.086975 | -0.16479 | 0.1236 | -0.12817 | 0.23804 | 122.4243 | 0.086975 | 122.4243 | 122.4655 | 122.4014 | 122.3877 | 122.3648 | -122.5296 | -122.4884 | 122.3465 | 122.3877 | 58.8455 | 56.1401
1152.7656 | 122.6486 | -59.198 | 63.2629 | -0.018234 | -1.0718e-05 | 0.062453 | 0.1033 | -0.0028199 | -0.0003632 | -0.0016022 | -0.030823 | 0.0010084 | 0.06247 | 0.065749 | -0.017178 | 0.00077333 | -0.00010671 | -0.33875 | 63.2217 | -59.285 | 63.1714 | -59.0195 | -59.4498 | -1.8173 | -2.7786 | 63.1805 | -59.2529 | 63.2309 | -59.1248 | -59.3399 | -59.079 | -0.086975 | -0.041198 | -0.091552 | 0.17853 | 57.3807 | -0.25177 | 57.4677 | -0.16479 | -0.054932 | -0.082397 | -0.032043 | 0.073242 | 0.11902 | -0.14191 | 0.17395 | -0.086975 | 0.2655 | 122.4564 | 0.12817 | 122.4838 | 122.5067 | 122.4335 | 122.4197 | 122.3785 | -122.5479 | -122.5159 | 122.3694 | 122.4289 | 58.8593 | 56.4194
1153.7656 | 122.6257 | -59.1614 | 63.2721 | -0.033493 | -1.0718e-05 | 0.063307 | 0.10223 | -4.2682e-05 | -0.0007904 | -0.0018158 | -0.039978 | 0.0025036 | 0.065674 | 0.062331 | -0.019527 | 0.0048321 | 0.00074769 | -0.3479 | 63.2172 | -59.2575 | 63.1805 | -59.0012 | -59.4406 | -1.8723 | -2.8198 | 63.1943 | -59.2117 | 63.2538 | -59.1019 | -59.317 | -59.079 | -0.09613 | -0.054932 | -0.091553 | 0.16022 | 57.2891 | -0.27924 | 57.3853 | -0.18311 | -0.050354 | -0.07782 | -0.018311 | 0.059509 | 0.082398 | -0.15564 | 0.13275 | -0.10529 | 0.25635 | 122.438 | 0.10986 | 122.4655 | 122.4747 | 122.406 | 122.3785 | 122.3557 | -122.5296 | -122.4838 | 122.3419 | 122.4152 | 58.8135 | 56.3416
1154.7656 | 122.6532 | -59.1751 | 63.2538 | -0.18608 | 0.0019119 | 0.060316 | 0.10372 | 0.0020935 | -0.0012176 | 0.00074764 | -0.0064086 | 0.00079477 | 0.064392 | 0.064467 | -0.018459 | 0.0014141 | -0.00032051 | -0.42114 | 63.1897 | -59.2209 | 63.1943 | -58.9874 | -59.404 | -1.8402 | -2.8427 | 63.208 | -59.2026 | 63.2584 | -59.0973 | -59.3216 | -59.0424 | -0.045776 | -0.064087 | -0.059509 | 0.18768 | 57.3349 | -0.22888 | 57.3807 | -0.18311 | -0.027466 | -0.045776 | 0.004578 | 0.07782 | 0.13275 | -0.14648 | 0.16022 | -0.11902 | 0.23346 | 122.4152 | 0.10529 | 122.4609 | 122.4106 | 122.4106 | 122.3648 | 122.3831 | -122.4747 | -122.4564 | 122.3694 | 122.4335 | 58.754 | 56.3324
1155.7656 | 122.6395 | -59.1568 | 63.295 | -0.10979 | 0.00063028 | 0.062239 | 0.10415 | 0.0016663 | -0.0014312 | -0.0043792 | -0.0064086 | 0.0014356 | 0.066956 | 0.063826 | -0.0191 | 0.0031231 | -0.00053411 | -0.36621 | 63.2584 | -59.2484 | 63.1805 | -59.0103 | -59.436 | -1.9409 | -3.0075 | 63.1851 | -59.2026 | 63.2309 | -59.0744 | -59.2987 | -59.0515 | -0.091553 | -0.036621 | -0.11444 | 0.14648 | 57.2159 | -0.27924 | 57.3074 | -0.18768 | -0.045777 | -0.10986 | -0.064087 | 0.082397 | 0.10529 | -0.14191 | 0.15106 | -0.09613 | 0.23804 | 122.4289 | 0.12817 | 122.4335 | 122.5067 | 122.3877 | 122.4152 | 122.3419 | -122.5433 | -122.4976 | 122.3373 | 122.3877 | 58.7906 | 56.1493
1156.7656 | 122.6486 | -59.1888 | 63.2675 | -0.048752 | -0.0025741 | 0.061171 | 0.10202 | 0.0033753 | 0.0002778 | -0.0020294 | 0.0057984 | 0.00015377 | 0.067169 | 0.061049 | -0.018673 | 0.0014141 | 0.0033111 | -0.36163 | 63.2538 | -59.2758 | 63.1531 | -59.0744 | -59.4315 | -1.973 | -2.7374 | 63.1897 | -59.23 | 63.2217 | -59.1202 | -59.317 | -59.1064 | -0.086975 | -0.013733 | -0.11444 | 0.11444 | 57.2159 | -0.24262 | 57.3029 | -0.15564 | -0.041199 | -0.07782 | -0.045776 | 0.068665 | 0.082398 | -0.12817 | 0.1236 | -0.086975 | 0.20142 | 122.4289 | 0.10986 | 122.4518 | 122.5296 | 122.4197 | 122.4426 | 122.3785 | -122.5433 | -122.4976 | 122.3419 | 122.4106 | 58.8272 | 56.4514
1157.7656 | 122.6486 | -59.1431 | 63.2721 | -0.086899 | 0.0025529 | 0.062239 | 0.10137 | 0.0027343 | -0.0016448 | -0.0018158 | -0.0094604 | 0.0010084 | 0.064392 | 0.060622 | -0.018032 | 0.0026959 | -0.0045929 | -0.34332 | 63.2172 | -59.285 | 63.1943 | -58.9645 | -59.4589 | -1.8311 | -2.8152 | 63.1897 | -59.2026 | 63.2401 | -59.1156 | -59.3262 | -59.079 | -0.14191 | -0.054932 | -0.07782 | 0.17853 | 57.312 | -0.31586 | 57.4539 | -0.17395 | -0.05951 | -0.082398 | -0.032044 | 0.027465 | 0.064087 | -0.18311 | 0.1236 | -0.1236 | 0.32043 | 122.4792 | 0.086975 | 122.4426 | 122.5021 | 122.3923 | 122.3602 | 122.3328 | -122.5571 | -122.4747 | 122.3373 | 122.3831 | 58.7997 | 56.3278
1158.7656 | 122.6395 | -59.1431 | 63.2904 | -0.094528 | 0.0019119 | 0.062666 | 0.10159 | 0.00081172 | -0.0005768 | -0.002243 | -0.030823 | -0.0013416 | 0.06482 | 0.063399 | -0.018886 | 0.0016277 | -0.0016021 | -0.36621 | 63.2538 | -59.2575 | 63.2034 | -58.992 | -59.4315 | -1.7761 | -3.0624 | 63.176 | -59.2392 | 63.2584 | -59.0927 | -59.2896 | -59.0607 | -0.11444 | -0.036621 | -0.086975 | 0.15106 | 57.3669 | -0.28839 | 57.4814 | -0.17395 | -0.096131 | -0.11444 | -0.032043 | 0.050354 | 0.082397 | -0.14649 | 0.17853 | -0.050354 | 0.2655 | 122.4609 | 0.14648 | 122.4976 | 122.5113 | 122.4152 | 122.3969 | 122.319 | -122.5479 | -122.5296 | 122.3465 | 122.4014 | 58.7769 | 56.0806
1159.7656 | 122.5845 | -59.1797 | 63.2401 | -0.086899 | -0.00065152 | 0.062239 | 0.10351 | 0.0046569 | -0.0024994 | -0.0013886 | -0.036926 | 0.0010084 | 0.06482 | 0.061476 | -0.018886 | 0.0022687 | -0.00053411 | -0.37079 | 63.2263 | -59.2575 | 63.1851 | -59.024 | -59.4452 | -1.6571 | -2.6184 | 63.1439 | -59.2255 | 63.2355 | -59.1064 | -59.4635 | -59.1888 | -0.07782 | -0.013733 | -0.054931 | 0.15564 | 57.5226 | -0.2655 | 57.6004 | -0.18768 | -0.045777 | -0.09613 | -0.004577 | 0.073242 | -0.009156 | -0.28381 | 0.036621 | -0.23804 | 0.23346 | 122.4426 | 0.11902 | 122.4609 | 122.4838 | 122.3694 | 122.406 | 122.3236 | -122.4976 | -122.4655 | 122.3648 | 122.4152 | 58.8089 | 56.5613
1160.7656 | 122.644 | -59.1705 | 63.2767 | 0.004654 | 0.00063028 | 0.063948 | 0.10159 | 0.0035889 | -0.0037812 | -0.0030976 | 0.0027466 | 0.0016492 | 0.06546 | 0.066817 | -0.017818 | 0.0029095 | 0.00096129 | -0.39368 | 63.2263 | -59.2529 | 63.176 | -59.0103 | -59.436 | -1.6937 | -2.4948 | 63.208 | -59.2072 | 63.2309 | -59.0836 | -59.2987 | -59.0607 | -0.082398 | -0.050354 | -0.10071 | 0.16022 | 57.4768 | -0.2655 | 57.5592 | -0.1831 | -0.036621 | -0.068664 | -0.045776 | 0.086975 | 0.10986 | -0.12817 | 0.14648 | -0.091553 | 0.24262 | 122.4289 | 0.1236 | 122.438 | 122.4792 | 122.4152 | 122.3969 | 122.3785 | -122.5296 | -122.4838 | 122.3465 | 122.4014 | 58.7769 | 56.6757
1161.7656 | 122.6486 | -59.1614 | 63.2996 | -0.033493 | -0.00043792 | 0.060316 | 0.10223 | -0.00068368 | -0.0018586 | -0.00096136 | 0.0088502 | 0.002931 | 0.066315 | 0.065535 | -0.017605 | 0.0014141 | -0.00032051 | -0.42114 | 63.2675 | -59.2117 | 63.1897 | -59.0103 | -59.404 | -1.7395 | -2.5909 | 63.2172 | -59.2026 | 63.2584 | -59.079 | -59.285 | -59.024 | -0.050354 | -0.032044 | -0.10986 | 0.15106 | 57.4219 | -0.24262 | 57.4722 | -0.19226 | -0.041199 | -0.082398 | -0.041199 | 0.082398 | 0.13733 | -0.1236 | 0.17853 | -0.082397 | 0.20142 | 122.4014 | 0.1236 | 122.4609 | 122.4792 | 122.4197 | 122.4289 | 122.3785 | -122.5113 | -122.5021 | 122.3511 | 122.4197 | 58.7402 | 56.5704
1162.7656 | 122.612 | -59.1751 | 63.3133 | -0.1403 | -0.00086512 | 0.058607 | 0.10244 | -0.0019653 | -0.0014312 | -0.00096136 | 0.036316 | 0.00036737 | 0.063751 | 0.059554 | -0.019314 | -8.1274e-05 | 0.0013885 | -0.35706 | 63.2446 | -59.2484 | 63.1531 | -59.0149 | -59.4589 | -1.7853 | -2.71 | 63.2172 | -59.1934 | 63.208 | -59.1248 | -59.317 | -59.0744 | -0.073242 | -0.068664 | -0.16022 | 0.16022 | 57.3898 | -0.28381 | 57.4631 | -0.21057 | -0.01831 | -0.09613 | -0.10529 | 0.050354 | 0.10071 | -0.14191 | 0.11902 | -0.1236 | 0.23346 | 122.4014 | 0.068664 | 122.4014 | 122.493 | 122.4106 | 122.4197 | 122.3923 | -122.5616 | -122.5067 | 122.3282 | 122.3831 | 58.8181 | 56.4651
1163.7656 | 122.6074 | -59.166 | 63.3316 | -0.041122 | -0.00086512 | 0.061385 | 0.10031 | -0.0049561 | -0.001004 | -0.0030976 | 0.021057 | 0.00229 | 0.065247 | 0.05934 | -0.017178 | 0.00013253 | 0.0018159 | -0.41657 | 63.2721 | -59.2346 | 63.0478 | -59.1202 | -59.3491 | -1.6067 | -2.8976 | 63.2217 | -59.1888 | 63.2309 | -59.0973 | -59.3033 | -59.0973 | -0.068664 | -0.059509 | -0.28381 | 0.045777 | 57.5592 | -0.18311 | 57.6279 | -0.11444 | -0.022888 | -0.10986 | -0.10071 | 0.068665 | 0.068665 | -0.13733 | 0.091553 | -0.11444 | 0.11444 | 122.2824 | 0.091553 | 122.4197 | 122.5067 | 122.4106 | 122.4381 | 122.3877 | -122.5662 | -122.5204 | 122.2137 | 122.3969 | 58.7494 | 56.2683
1164.7656 | 122.6349 | -59.1339 | 63.3224 | -0.10216 | -0.00043792 | 0.061598 | 0.10394 | 0.00059812 | 6.4004e-05 | -0.00053396 | -0.0094604 | 0.0016492 | 0.062042 | 0.057845 | -0.018246 | 0.0018413 | -0.0024567 | -0.42114 | 63.2492 | -59.2117 | 63.2217 | -58.9828 | -59.4131 | -1.5106 | -2.9617 | 63.2492 | -59.166 | 63.2858 | -59.0561 | -59.2712 | -59.0057 | -0.07782 | -0.073242 | -0.10071 | 0.15106 | 57.6233 | -0.27924 | 57.7011 | -0.20142 | -0.032044 | -0.073242 | -0.036621 | 0.07782 | 0.12817 | -0.13733 | 0.16022 | -0.10529 | 0.22888 | 122.4335 | 0.10986 | 122.4518 | 122.4609 | 122.4152 | 122.3831 | 122.3831 | -122.5342 | -122.4884 | 122.3557 | 122.4197 | 58.7128 | 56.1722
1165.7656 | 122.6669 | -59.166 | 63.3179 | -0.079269 | 0.0012711 | 0.060316 | 0.10458 | 0.0014527 | -0.0029266 | -0.0041656 | 0.0057984 | 0.00015377 | 0.064392 | 0.06404 | -0.01675 | 0.00013253 | 0.0016021 | -0.3891 | 63.2584 | -59.2529 | 63.176 | -59.0149 | -59.4269 | -1.4465 | -3.0167 | 63.2309 | -59.1888 | 63.2675 | -59.0881 | -59.2758 | -59.0332 | -0.086975 | -0.059509 | -0.14191 | 0.15106 | 57.7194 | -0.26093 | 57.8064 | -0.17395 | -0.022888 | -0.086975 | -0.050354 | 0.07782 | 0.13275 | -0.10986 | 0.15564 | -0.086975 | 0.23804 | 122.4289 | 0.10071 | 122.4564 | 122.5113 | 122.4197 | 122.4243 | 122.3969 | -122.5708 | -122.5067 | 122.3419 | 122.4335 | 58.7769 | 56.1493
1166.7656 | 122.6349 | -59.1339 | 63.3362 | -0.056381 | 0.00020288 | 0.061171 | 0.10287 | 0.0042297 | -0.0031402 | 0.00074764 | 0.0088502 | -0.00070063 | 0.064179 | 0.066603 | -0.018673 | 0.0024823 | 0.0020295 | -0.3891 | 63.2904 | -59.2117 | 63.1897 | -59.0057 | -59.404 | -1.4511 | -3.3417 | 63.2309 | -59.1797 | 63.2629 | -59.0515 | -59.2712 | -59.0378 | -0.07782 | -0.045777 | -0.14648 | 0.12817 | 57.6828 | -0.27008 | 57.7606 | -0.19226 | -0.045776 | -0.10529 | -0.073243 | 0.082397 | 0.09613 | -0.13733 | 0.14191 | -0.091553 | 0.20599 | 122.4014 | 0.12817 | 122.4426 | 122.5021 | 122.4106 | 122.4243 | 122.3648 | -122.5479 | -122.5159 | 122.3236 | 122.3969 | 58.7448 | 55.7922
1167.7656 | 122.5891 | -59.1614 | 63.3041 | -0.056381 | -0.00022432 | 0.062025 | 0.10287 | 0.0029479 | -0.0035674 | -0.0024566 | -0.0094604 | 0.00036737 | 0.063111 | 0.06169 | -0.018673 | 0.0014141 | -0.0020295 | -0.36163 | 63.2675 | -59.2346 | 63.1622 | -59.0469 | -59.4452 | -1.3596 | -3.1769 | 63.208 | -59.2117 | 63.2172 | -59.1019 | -59.3124 | -59.0652 | -0.073242 | -0.036621 | -0.14191 | 0.11444 | 57.8018 | -0.28381 | 57.8751 | -0.21057 | -0.050354 | -0.09613 | -0.086975 | 0.059509 | 0.09613 | -0.15106 | 0.14648 | -0.10071 | 0.18768 | 122.3969 | 0.10986 | 122.4289 | 122.5021 | 122.4197 | 122.4289 | 122.3694 | -122.5388 | -122.5159 | 122.3236 | 122.3785 | 58.7997 | 55.9845
1168.7656 | 122.6303 | -59.1476 | 63.3682 | -0.13267 | 0.0036209 | 0.059676 | 0.10137 | 0.0031617 | -0.0003632 | -0.00096136 | 0.014954 | 0.00015377 | 0.067383 | 0.056777 | -0.019527 | 0.00055973 | 0.0026703 | -0.3479 | 63.2904 | -59.1934 | 63.1943 | -59.0012 | -59.4315 | -1.2497 | -3.2089 | 63.2584 | -59.1614 | 63.2492 | -59.0927 | -59.317 | -59.0515 | -0.045776 | -0.07782 | -0.17395 | 0.14648 | 57.8979 | -0.28381 | 57.9437 | -0.23804 | -0.013733 | -0.10986 | -0.11902 | 0.054932 | 0.09613 | -0.16937 | 0.10986 | -0.15564 | 0.19226 | 122.3877 | 0.068665 | 122.4106 | 122.4838 | 122.4197 | 122.438 | 122.406 | -122.5616 | -122.5296 | 122.3419 | 122.3969 | 58.7997 | 55.9387
1169.7656 | 122.6349 | -59.1522 | 63.3316 | -0.079269 | 0.00041648 | 0.061385 | 0.1033 | 0.00017092 | -0.0016448 | -0.0020294 | 0.045471 | -0.001128 | 0.06247 | 0.058913 | -0.018032 | 0.00034613 | -0.00053411 | -0.33417 | 63.2309 | -59.2117 | 63.2263 | -58.9645 | -59.3765 | -1.0391 | -2.9755 | 63.2126 | -59.1705 | 63.2538 | -59.0652 | -59.2804 | -59.0607 | -0.059509 | -0.10071 | -0.10529 | 0.18768 | 58.1131 | -0.2243 | 58.1726 | -0.16479 | -0.01831 | -0.11902 | -0.07782 | 0.086975 | 0.091553 | -0.12817 | 0.10986 | -0.10986 | 0.24719 | 122.438 | 0.10529 | 122.4243 | 122.4426 | 122.3831 | 122.3831 | 122.3648 | -122.5433 | -122.5021 | 122.3785 | 122.406 | 58.8181 | 56.1768
1170.7656 | 122.6852 | -59.1339 | 63.3133 | -0.10216 | 0.0010575 | 0.061598 | 0.10095 | -0.0015381 | -0.0003632 | -0.0016022 | 0.045471 | -0.001128 | 0.066315 | 0.062972 | -0.019527 | -0.0011493 | -0.0011749 | -0.3479 | 63.2355 | -59.23 | 63.2584 | -58.9371 | -59.3582 | -1.03 | -2.9114 | 63.2263 | -59.1705 | 63.2721 | -59.0286 | -59.2117 | -59.0149 | -0.096131 | -0.077819 | -0.054931 | 0.19684 | 58.1039 | -0.2243 | 58.2001 | -0.12817 | -0.036621 | -0.086975 | -0.041198 | 0.10529 | 0.11902 | -0.07782 | 0.15564 | -0.041199 | 0.29297 | 122.4884 | 0.14191 | 122.4426 | 122.4655 | 122.3969 | 122.3694 | 122.3602 | -122.5433 | -122.4838 | 122.3923 | 122.406 | 58.786 | 56.2225
1171.7656 | 122.6028 | -59.1385 | 63.3408 | 0.035172 | 0.00020288 | 0.060744 | 0.10202 | 0.00038452 | -0.0018586 | -0.0026704 | 0.0088502 | -0.001128 | 0.065674 | 0.060836 | -0.018886 | 0.0014141 | 0.0013885 | -0.35248 | 63.3453 | -59.1843 | 63.1805 | -58.9828 | -59.4177 | -1.1444 | -3.4653 | 63.2767 | -59.1751 | 63.2675 | -59.0744 | -59.285 | -59.0332 | -0.045776 | 0.004578 | -0.16022 | 0.15564 | 57.9941 | -0.27924 | 58.0399 | -0.23346 | -0.036621 | -0.064087 | -0.073242 | 0.064087 | 0.10529 | -0.14648 | 0.14191 | -0.10986 | 0.20142 | 122.3648 | 0.10071 | 122.4426 | 122.5296 | 122.4518 | 122.4838 | 122.4152 | -122.525 | -122.5159 | 122.319 | 122.406 | 58.786 | 55.6732
1172.7656 | 122.6028 | -59.079 | 63.4232 | -0.025863 | -0.00043792 | 0.060744 | 0.1033 | 0.0020935 | -0.0054902 | -0.0052338 | 0.11871 | -0.0013416 | 0.06482 | 0.063399 | -0.018886 | 0.0016277 | -0.0039521 | -0.41657 | 63.3636 | -59.1293 | 63.2629 | -58.9462 | -59.3399 | -1.0849 | -4.2984 | 63.3316 | -59.1248 | 63.2858 | -59.0378 | -59.2575 | -59.024 | -0.050354 | -0.05951 | -0.16022 | 0.13275 | 57.9941 | -0.26093 | 58.0444 | -0.21057 | -0.045777 | -0.091553 | -0.13733 | 0.041198 | 0.054931 | -0.17853 | 0.10071 | -0.13275 | 0.18311 | 122.3923 | 0.086975 | 122.4106 | 122.493 | 122.4564 | 122.4426 | 122.4106 | -122.5525 | -122.5479 | 122.3419 | 122.3648 | 58.6624 | 54.7806
1173.7656 | 122.6761 | -58.992 | 63.4552 | -0.06401 | 0.0014847 | 0.060744 | 0.10266 | 0.00081172 | -0.0003632 | -0.0037384 | -0.0033568 | 0.001222 | 0.065247 | 0.061263 | -0.018673 | 0.0020551 | -0.0020295 | -0.40283 | 63.3774 | -59.1202 | 63.3087 | -58.9325 | -59.3399 | -1.0849 | -4.0237 | 63.3408 | -59.1019 | 63.3179 | -58.9874 | -59.2163 | -58.8867 | -0.12817 | -0.07782 | -0.14648 | 0.059509 | 57.9071 | -0.3479 | 58.0353 | -0.21973 | -0.10986 | -0.11444 | -0.13733 | 0.004577 | 0.10529 | -0.22431 | 0.21515 | -0.11444 | 0.18768 | 122.4289 | 0.11444 | 122.4197 | 122.4976 | 122.4426 | 122.3694 | 122.3328 | -122.5754 | -122.5571 | 122.3007 | 122.3099 | 58.5892 | 54.9683
1174.7656 | 122.6166 | -59.0332 | 63.4369 | -0.041122 | 0.0021255 | 0.061385 | 0.10244 | 0.0014527 | -0.0035674 | -0.0016022 | 0.018005 | -0.00091423 | 0.065033 | 0.055068 | -0.019527 | 0.0022687 | 0.0018159 | -0.3479 | 63.3636 | -59.0698 | 63.3499 | -58.8501 | -59.2712 | -1.0941 | -4.0649 | 63.3408 | -59.0836 | 63.3453 | -58.9691 | -59.1705 | -58.9279 | -0.036621 | -0.073243 | -0.086975 | 0.1831 | 57.9391 | -0.23804 | 57.9758 | -0.20142 | -0.050354 | -0.096131 | -0.091553 | 0.064087 | 0.10529 | -0.13733 | 0.15564 | -0.086975 | 0.21973 | 122.4197 | 0.11444 | 122.4289 | 122.4335 | 122.4243 | 122.3969 | 122.374 | -122.5067 | -122.5204 | 122.3831 | 122.3785 | 58.6853 | 54.9683
1175.7656 | 122.6257 | -59.0057 | 63.4644 | -0.041122 | 0.00041648 | 0.061171 | 0.1018 | 0.0012391 | -0.002713 | -0.003952 | 0.033264 | -0.002196 | 0.064392 | 0.058913 | -0.019527 | 0.00013253 | -0.0052337 | -0.35248 | 63.3408 | -59.0652 | 63.414 | -58.7997 | -59.2163 | -1.0941 | -3.9642 | 63.3362 | -59.024 | 63.4048 | -58.9005 | -59.1202 | -58.905 | -0.05951 | -0.1236 | -0.050354 | 0.20599 | 57.9117 | -0.21057 | 57.9712 | -0.15106 | -0.018311 | -0.12817 | -0.059509 | 0.10529 | 0.10071 | -0.11444 | 0.11902 | -0.09613 | 0.2655 | 122.4792 | 0.1236 | 122.4289 | 122.406 | 122.3602 | 122.3465 | 122.3419 | -122.5296 | -122.4884 | 122.4197 | 122.4106 | 58.6533 | 55.0415
1176.7656 | 122.699 | -58.9691 | 63.4048 | 0.37849 | -0.00086512 | 0.063521 | 0.10244 | 0.0063659 | 0.0013458 | -0.0037384 | 0.051575 | 0.00015377 | 0.067383 | 0.056349 | -0.019314 | 0.00098693 | -0.00096131 | -0.47607 | 63.3865 | -59.0881 | 63.4506 | -58.7402 | -59.2209 | -1.0757 | -4.01 | 63.3041 | -59.0378 | 63.4689 | -58.8135 | -59.0561 | -58.8135 | -0.11902 | -0.01831 | 0.045777 | 0.22888 | 57.8934 | -0.25177 | 58.0124 | -0.13275 | -0.068665 | -0.10071 | 0.064087 | 0.15564 | 0.15564 | -0.086975 | 0.2243 | -0.01831 | 0.3479 | 122.5388 | 0.2243 | 122.5067 | 122.4747 | 122.3419 | 122.3557 | 122.2733 | -122.493 | -122.4426 | 122.4197 | 122.438 | 58.493 | 54.9591
1177.7656 | 122.7264 | -59.024 | 63.3362 | -0.10216 | -0.0010787 | 0.061812 | 0.10394 | -0.0017517 | -0.0016448 | -0.002884 | -0.14069 | -5.9826e-05 | 0.061829 | 0.063613 | -0.019741 | 0.0024823 | 0.0022431 | -0.32044 | 63.3087 | -59.1064 | 63.4094 | -58.7952 | -58.7265 | -0.80566 | -3.8864 | 63.2538 | -59.0973 | 63.3911 | -58.8593 | -59.0652 | -58.8547 | -0.082397 | -0.027466 | 0.073242 | 0.22888 | 58.2184 | 0.29755 | 58.3008 | 0.37994 | -0.073242 | -0.082398 | 0.054931 | 0.16479 | 0.16937 | -0.041199 | 0.24262 | 0.032043 | 0.31128 | 122.5159 | 0.23804 | 122.4884 | 122.4152 | 122.3511 | 122.3328 | 122.2778 | -122.4426 | -122.4335 | 122.4335 | 122.4152 | 58.7036 | 55.1376
1178.7656 | 122.6212 | -59.0561 | 63.4048 | -0.086899 | 0.00063028 | 0.061385 | 0.10244 | -0.0015381 | -0.0039948 | -0.002884 | -0.021667 | -0.002196 | 0.062042 | 0.062758 | -0.020809 | 0.0022687 | 0.0011749 | -0.33875 | 63.3316 | -59.1248 | 63.3636 | -58.8501 | -59.2758 | -1.1078 | -4.216 | 63.2904 | -59.0927 | 63.3453 | -58.9737 | -59.1843 | -58.9508 | -0.068665 | -0.073242 | -0.041199 | 0.20599 | 57.9483 | -0.21973 | 58.017 | -0.15106 | -0.036621 | -0.11444 | -0.059509 | 0.082397 | 0.10529 | -0.12817 | 0.14191 | -0.091553 | 0.27466 | 122.4884 | 0.11902 | 122.438 | 122.4564 | 122.3831 | 122.3877 | 122.3465 | -122.5296 | -122.4976 | 122.4197 | 122.4014 | 58.7173 | 54.8401
1179.7656 | 122.6578 | -59.0698 | 63.3774 | -0.048752 | 0.0014847 | 0.063094 | 0.10223 | 0.0027343 | -0.0031402 | 0.00010684 | 0.0057984 | 0.00015377 | 0.065247 | 0.063613 | -0.018886 | 0.0022687 | 0.0013885 | -0.33875 | 63.2858 | -59.1248 | 63.3453 | -58.8638 | -59.285 | -1.1398 | -4.0924 | 63.2538 | -59.1202 | 63.3408 | -58.9508 | -59.1751 | -58.9005 | -0.054932 | -0.091552 | -0.032043 | 0.20599 | 57.93 | -0.21515 | 57.9849 | -0.16022 | -0.050354 | -0.1236 | -0.036621 | 0.11902 | 0.16937 | -0.10529 | 0.21973 | -0.054932 | 0.26093 | 122.4701 | 0.16937 | 122.4609 | 122.4106 | 122.374 | 122.3557 | 122.3236 | -122.5021 | -122.4976 | 122.4152 | 122.4106 | 58.7311 | 54.9774
1180.7656 | 122.6852 | -59.0515 | 63.3636 | -0.041122 | 0.0016983 | 0.061598 | 0.10351 | -0.00068368 | -0.0001496 | -0.00096136 | 0.0027466 | 0.001222 | 0.065247 | 0.062758 | -0.019741 | 0.0016277 | 0.00096129 | -0.31128 | 63.2858 | -59.1248 | 63.3682 | -58.8226 | -59.2529 | -1.03 | -4.4769 | 63.2721 | -59.1293 | 63.3682 | -58.9279 | -59.1385 | -58.9188 | -0.073242 | -0.077819 | 0.004578 | 0.22888 | 58.0215 | -0.20142 | 58.0948 | -0.12817 | -0.077819 | -0.091552 | 0.004578 | 0.1236 | 0.13275 | -0.086975 | 0.21057 | -0.009156 | 0.30212 | 122.493 | 0.20142 | 122.4976 | 122.4106 | 122.4014 | 122.3373 | 122.3236 | -122.4884 | -122.493 | 122.4197 | 122.4197 | 58.7402 | 54.5746
1181.7656 | 122.7173 | -59.0195 | 63.3774 | -0.033493 | 0.0016983 | 0.059462 | 0.10223 | 0.0016663 | -0.0005768 | -0.0041656 | 0.011902 | -0.0019824 | 0.064392 | 0.062758 | -0.018032 | -0.00072207 | -0.0011749 | -0.3067 | 63.2904 | -59.1156 | 63.3728 | -58.7997 | -59.2621 | -1.0437 | -4.6326 | 63.2858 | -59.1064 | 63.4094 | -58.9188 | -59.1064 | -58.8867 | -0.096131 | -0.086975 | -0.004577 | 0.21973 | 57.9758 | -0.24262 | 58.0719 | -0.14648 | -0.086975 | -0.091552 | 0.032044 | 0.10071 | 0.13275 | -0.086975 | 0.21973 | 0 | 0.31586 | 122.4884 | 0.18768 | 122.5159 | 122.406 | 122.3923 | 122.3099 | 122.3053 | -122.493 | -122.4838 | 122.3923 | 122.4289 | 58.7128 | 54.3869
1182.7656 | 122.731 | -59.0652 | 63.3499 | -0.094528 | 0.00063028 | 0.062239 | 0.10266 | 0.00081172 | 6.4004e-05 | -0.0020294 | 0.014954 | -0.00091423 | 0.063111 | 0.060836 | -0.018886 | 0.0018413 | -0.00032051 | -0.29297 | 63.2584 | -59.1476 | 63.3636 | -58.8455 | -59.2667 | -0.95215 | -4.2252 | 63.2446 | -59.1293 | 63.3911 | -58.9233 | -59.1156 | -58.9005 | -0.082397 | -0.091553 | 0.013732 | 0.21973 | 58.1131 | -0.20142 | 58.1955 | -0.11902 | -0.064086 | -0.10529 | 0.041198 | 0.14191 | 0.16479 | -0.050354 | 0.22888 | 0.013732 | 0.30212 | 122.5113 | 0.20599 | 122.5204 | 122.406 | 122.374 | 122.3236 | 122.3099 | -122.4976 | -122.4792 | 122.4289 | 122.4564 | 58.7723 | 54.8401
1183.7656 | 122.7585 | -59.0652 | 63.3224 | -0.094528 | -0.00065152 | 0.060957 | 0.10308 | -0.00046988 | -0.0029266 | -0.0024566 | 0.0088502 | -0.00027343 | 0.065247 | 0.057631 | -0.019314 | 0.00055973 | -0.00053411 | -0.32044 | 63.2309 | -59.1797 | 63.3408 | -58.8501 | -59.317 | -0.76904 | -4.0695 | 63.2172 | -59.1293 | 63.4048 | -58.9096 | -59.111 | -58.9096 | -0.11444 | -0.091553 | 0.01831 | 0.21515 | 58.2962 | -0.25177 | 58.4106 | -0.13733 | -0.064086 | -0.10529 | 0.082397 | 0.15564 | 0.15564 | -0.045776 | 0.21973 | 0.01831 | 0.32959 | 122.5204 | 0.21973 | 122.5342 | 122.4106 | 122.3465 | 122.2961 | 122.2824 | -122.5021 | -122.4518 | 122.406 | 122.4701 | 58.7448 | 54.9957
1184.7656 | 122.7402 | -59.0881 | 63.3133 | -0.094528 | -0.00043792 | 0.062025 | 0.10137 | -0.0011109 | -0.0029266 | -0.002884 | 0.0057984 | 0.00036737 | 0.063751 | 0.050795 | -0.017391 | 0.00055973 | -0.0018157 | -0.33417 | 63.2492 | -59.1522 | 63.3179 | -58.8547 | -59.2712 | -0.30212 | -4.3945 | 63.2217 | -59.1293 | 63.3865 | -58.8867 | -59.1522 | -58.8913 | -0.064087 | -0.064086 | 0.004578 | 0.23346 | 58.786 | -0.1831 | 58.8501 | -0.11902 | -0.041198 | -0.091552 | 0.073243 | 0.20142 | 0.19684 | -0.064087 | 0.23804 | -0.022889 | 0.29755 | 122.4701 | 0.24261 | 122.5159 | 122.4014 | 122.3511 | 122.3373 | 122.3099 | -122.4655 | -122.4426 | 122.406 | 122.4747 | 58.754 | 54.6936
1185.7656 | 122.7173 | -59.0744 | 63.3408 | -0.10216 | 0.00063028 | 0.061598 | 0.10223 | 0.0029479 | 0.0002778 | -0.004593 | -0.00030524 | -0.00091423 | 0.063111 | 0.060195 | -0.020168 | 0.0022687 | -0.0039521 | -0.31128 | 63.2904 | -59.1476 | 63.3774 | -58.8226 | -59.2712 | -0.14191 | -4.6875 | 63.2675 | -59.1064 | 63.3911 | -58.905 | -59.1522 | -58.8959 | -0.073242 | -0.050354 | 0.036621 | 0.25177 | 58.9325 | -0.19684 | 59.0057 | -0.1236 | -0.032043 | -0.073242 | 0.050354 | 0.16937 | 0.17853 | -0.07782 | 0.21057 | -0.045777 | 0.32501 | 122.525 | 0.20142 | 122.4976 | 122.438 | 122.374 | 122.3648 | 122.3419 | -122.4884 | -122.4472 | 122.4518 | 122.4655 | 58.7631 | 54.3869
1186.7656 | 122.7173 | -59.0698 | 63.3682 | -0.15556 | 0.0014847 | 0.061598 | 0.10202 | -0.0015381 | -0.0003632 | -0.0026704 | -0.0094604 | -0.0015552 | 0.063538 | 0.05934 | -0.0191 | 0.00013253 | -0.0022431 | -0.32044 | 63.2996 | -59.1568 | 63.382 | -58.8181 | -59.2621 | 0.091553 | -5.0903 | 63.295 | -59.1156 | 63.3865 | -58.8959 | -59.1248 | -58.9096 | -0.086975 | -0.068664 | 0.013733 | 0.25177 | 59.1614 | -0.19226 | 59.2484 | -0.10529 | -0.045777 | -0.073242 | 0.018311 | 0.17395 | 0.16022 | -0.054932 | 0.20599 | -0.009155 | 0.33875 | 122.5388 | 0.21973 | 122.5021 | 122.4564 | 122.4106 | 122.3694 | 122.3648 | -122.525 | -122.4838 | 122.4518 | 122.4564 | 58.7494 | 53.9795
1187.7656 | 122.7264 | -59.0286 | 63.3911 | -0.10216 | -0.0017197 | 0.062025 | 0.10351 | -0.00068368 | -0.0012176 | -0.001175 | -0.0094604 | 0.00079477 | 0.06482 | 0.058913 | -0.019527 | 0.00098693 | -0.0035247 | -0.31128 | 63.2904 | -59.0973 | 63.3957 | -58.8043 | -59.23 | 0.23804 | -5.3513 | 63.2721 | -59.1019 | 63.414 | -58.8684 | -59.0195 | -58.873 | -0.068665 | -0.10071 | 0.004578 | 0.2243 | 59.2667 | -0.20142 | 59.3353 | -0.13275 | -0.073243 | -0.11902 | 0.022888 | 0.16022 | 0.15564 | 0.009155 | 0.22888 | 0.082398 | 0.29297 | 122.493 | 0.23346 | 122.5159 | 122.3877 | 122.374 | 122.319 | 122.3007 | -122.4884 | -122.493 | 122.4243 | 122.4426 | 58.7173 | 53.6774
1188.7656 | 122.699 | -59.0378 | 63.3499 | -0.048752 | 0.0016983 | 0.063307 | 0.10351 | 0.0029479 | -0.0024994 | -0.0013886 | 0.0057984 | 0.00079477 | 0.063965 | 0.059554 | -0.018459 | 0.00055973 | -0.00053411 | -0.38452 | 63.2767 | -59.1431 | 63.4003 | -58.8181 | -59.2255 | 0.37079 | -5.4199 | 63.2629 | -59.0927 | 63.4369 | -58.8684 | -59.0927 | -58.8959 | -0.10528 | -0.073243 | 0.050354 | 0.21973 | 59.4086 | -0.18768 | 59.5139 | -0.082398 | -0.054931 | -0.086976 | 0.086975 | 0.16937 | 0.14191 | -0.054931 | 0.19684 | 0 | 0.32501 | 122.5433 | 0.2243 | 122.5296 | 122.4197 | 122.3557 | 122.3145 | 122.3007 | -122.493 | -122.4426 | 122.4381 | 122.4747 | 58.6533 | 53.6179
1189.7656 | 122.7356 | -59.0607 | 63.3408 | 0.05806 | 0.00063028 | 0.063948 | 0.10266 | 0.0029479 | 0.0022004 | -0.0037384 | -0.015564 | 0.00036737 | 0.064179 | 0.061476 | -0.020382 | 0.00013253 | -0.0045929 | -0.52643 | 63.3041 | -59.1522 | 63.4003 | -58.8181 | -59.2621 | 0.31128 | -5.5801 | 63.2538 | -59.079 | 63.4323 | -58.8913 | -59.1156 | -58.8821 | -0.091553 | -0.036621 | 0.05951 | 0.24262 | 59.3719 | -0.20142 | 59.4635 | -0.10986 | -0.01831 | -0.086975 | 0.091553 | 0.16937 | 0.17853 | -0.054932 | 0.19684 | -0.036622 | 0.33417 | 122.5525 | 0.18768 | 122.5113 | 122.4564 | 122.3328 | 122.3648 | 122.3145 | -122.493 | -122.4197 | 122.4609 | 122.493 | 58.5342 | 53.4805
1190.7656 | 122.7676 | -59.0057 | 63.3636 | -0.07164 | 0.0019119 | 0.060744 | 0.10202 | 0.00017092 | -0.0005768 | 0.00032044 | -0.00030524 | -0.00070063 | 0.065247 | 0.055495 | -0.019527 | 0.00055973 | -0.0033111 | -0.38452 | 63.3224 | -59.111 | 63.4094 | -58.8089 | -59.2163 | 0.027466 | -5.777 | 63.2996 | -59.0744 | 63.4689 | -58.8409 | -59.0332 | -58.8547 | -0.10529 | -0.041198 | 0.045777 | 0.19684 | 59.0332 | -0.21057 | 59.1385 | -0.10529 | -0.068665 | -0.064086 | 0.10529 | 0.1648 | 0.15106 | -0.027466 | 0.21973 | 0.041199 | 0.30212 | 122.5204 | 0.23346 | 122.5433 | 122.4335 | 122.374 | 122.3282 | 122.3053 | -122.4747 | -122.438 | 122.4152 | 122.4747 | 58.6212 | 53.2288
1191.7656 | 122.7356 | -59.0103 | 63.3636 | -0.06401 | 0.00041648 | 0.061171 | 0.10266 | 0.0018799 | -0.0020722 | 0.00096124 | -0.015564 | 0.0010084 | 0.063965 | 0.048018 | -0.018886 | 0.00055973 | -0.0011749 | -0.40741 | 63.3224 | -59.1248 | 63.3774 | -58.8043 | -59.2484 | 0.23346 | -5.777 | 63.3041 | -59.0652 | 63.4552 | -58.8501 | -59.0515 | -58.8455 | -0.11444 | -0.041198 | 0.013733 | 0.20599 | 59.2438 | -0.23804 | 59.3582 | -0.1236 | -0.054932 | -0.059509 | 0.091553 | 0.16022 | 0.16479 | -0.041199 | 0.21973 | 0.013733 | 0.32043 | 122.5021 | 0.21515 | 122.5204 | 122.4472 | 122.3694 | 122.3328 | 122.3145 | -122.4884 | -122.4289 | 122.3877 | 122.4655 | 58.6029 | 53.2333
1192.7656 | 122.6944 | -58.9828 | 63.4094 | -0.079269 | 0.00020288 | 0.061171 | 0.10394 | 0.00059812 | -0.0024994 | -0.00010676 | -0.021667 | -0.00091423 | 0.063324 | 0.063185 | -0.021023 | 0.0020551 | -0.00032051 | -0.37537 | 63.3591 | -59.0836 | 63.4369 | -58.7585 | -59.198 | -0.041199 | -6.0104 | 63.3087 | -59.0515 | 63.4689 | -58.8272 | -59.0515 | -58.873 | -0.10071 | -0.050354 | 0.027466 | 0.2243 | 58.9417 | -0.21515 | 59.0424 | -0.11444 | -0.068665 | -0.10071 | 0.059509 | 0.15564 | 0.10986 | -0.068665 | 0.17853 | 0 | 0.32501 | 122.5204 | 0.2243 | 122.5204 | 122.4426 | 122.3602 | 122.3419 | 122.2916 | -122.493 | -122.4609 | 122.4197 | 122.4518 | 58.6075 | 52.9724
1193.7656 | 122.7081 | -58.9645 | 63.4232 | -0.086899 | -0.00022432 | 0.060744 | 0.10287 | 0.0020935 | -0.0001496 | -0.0030976 | -0.024719 | 0.001222 | 0.064179 | 0.058913 | -0.020168 | 0.0018413 | -0.0011749 | -0.40741 | 63.3728 | -59.0698 | 63.4781 | -58.7265 | -59.166 | -0.050354 | -6.2805 | 63.3591 | -59.0332 | 63.5056 | -58.7906 | -59.024 | -58.8181 | -0.10528 | -0.050354 | 0.054931 | 0.23804 | 58.9142 | -0.20142 | 59.0195 | -0.096131 | -0.068664 | -0.064087 | 0.082397 | 0.17395 | 0.14649 | -0.059509 | 0.21515 | 0.009155 | 0.34332 | 122.5479 | 0.24262 | 122.5388 | 122.4426 | 122.3923 | 122.3373 | 122.3236 | -122.493 | -122.4564 | 122.4426 | 122.4701 | 58.5571 | 52.684
1194.7656 | 122.6486 | -58.9554 | 63.4689 | -0.079269 | 0.00020288 | 0.061171 | 0.10501 | 0.00081172 | -0.001004 | 0.0033112 | -0.13153 | 0.00079477 | 0.066956 | 0.063185 | -0.018246 | 0.0033367 | -0.0020295 | -0.42572 | 63.4186 | -59.0698 | 63.4094 | -58.7814 | -59.2529 | -0.19684 | -6.6513 | 63.3728 | -59.0469 | 63.4918 | -58.8684 | -59.0652 | -58.8181 | -0.11444 | -0.050354 | -0.059509 | 0.17395 | 58.7585 | -0.29755 | 58.873 | -0.18311 | -0.091553 | -0.09613 | 0.022888 | 0.086975 | 0.13733 | -0.10986 | 0.22888 | -0.018311 | 0.28839 | 122.4792 | 0.17853 | 122.5388 | 122.4884 | 122.4197 | 122.374 | 122.3282 | -122.5388 | -122.5159 | 122.3648 | 122.4472 | 58.5297 | 52.3041
1195.7656 | 122.7173 | -58.8959 | 63.4689 | -0.10979 | 0.0021255 | 0.060103 | 0.10095 | -0.0015381 | -0.0001496 | -0.004593 | 0.021057 | 0.001222 | 0.064392 | 0.057631 | -0.017818 | -8.1274e-05 | -0.0045929 | -0.43488 | 63.446 | -58.992 | 63.5605 | -58.6029 | -59.2392 | -0.50812 | -6.4224 | 63.3865 | -58.96 | 63.5742 | -58.7402 | -58.9828 | -58.7494 | -0.09613 | -0.022888 | 0.091553 | 0.29297 | 58.3878 | -0.34332 | 58.4839 | -0.24719 | -0.064087 | -0.082397 | 0.10529 | 0.15564 | 0.14648 | -0.086975 | 0.21057 | -0.022888 | 0.3891 | 122.5525 | 0.21973 | 122.5342 | 122.438 | 122.3465 | 122.3419 | 122.2824 | -122.4609 | -122.4289 | 122.4564 | 122.4701 | 58.461 | 52.4734
1196.7656 | 122.7264 | -58.9096 | 63.4781 | -0.048752 | 0.0014847 | 0.058394 | 0.10266 | 0.0014527 | -0.0018586 | 0.0020294 | 0.030212 | -0.0024096 | 0.068024 | 0.062972 | -0.019741 | 0.0020551 | -0.00010671 | -0.42114 | 63.4277 | -58.9874 | 63.7802 | -58.3282 | -59.3994 | -0.68207 | -6.6284 | 63.4048 | -58.9462 | 63.5742 | -58.699 | -58.9371 | -58.7311 | -0.07782 | -0.050354 | 0.30212 | 0.58136 | 58.2275 | -0.48981 | 58.3054 | -0.41199 | -0.036621 | -0.073242 | 0.096131 | 0.21057 | 0.17853 | -0.027466 | 0.21515 | 0.009155 | 0.65918 | 122.7676 | 0.24719 | 122.5204 | 122.4152 | 122.3511 | 122.3373 | 122.3145 | -122.4655 | -122.4243 | 122.6898 | 122.4838 | 58.4885 | 52.2812
1197.7656 | 122.7448 | -58.905 | 63.4781 | -0.10216 | 0.00020288 | 0.062025 | 0.10159 | -0.0017517 | -0.0016448 | 0.00053404 | 0.0027466 | -0.0013416 | 0.064392 | 0.060195 | -0.018886 | 0.0012005 | 0.0011749 | -0.46692 | 63.4415 | -58.9966 | 63.4781 | -58.7173 | -59.1431 | -0.47607 | -6.6559 | 63.414 | -58.9783 | 63.5788 | -58.7448 | -58.9508 | -58.7265 | -0.091553 | -0.036621 | 0 | 0.18768 | 58.429 | -0.23804 | 58.5205 | -0.14648 | -0.073242 | -0.064087 | 0.10071 | 0.16022 | 0.17853 | -0.045777 | 0.25177 | 0.027465 | 0.27924 | 122.4747 | 0.23346 | 122.5571 | 122.438 | 122.3923 | 122.3465 | 122.319 | -122.4747 | -122.4564 | 122.3831 | 122.4838 | 58.4381 | 52.2491
1198.7656 | 122.7036 | -58.9737 | 63.4369 | -0.079269 | -1.0718e-05 | 0.061385 | 0.10394 | 0.0012391 | -0.0016448 | -0.00053396 | -0.012512 | -0.00070063 | 0.066101 | 0.059554 | -0.018032 | 0.0020551 | -0.00053411 | -0.48523 | 63.3957 | -59.0332 | 63.4598 | -58.754 | -59.1843 | -0.42114 | -6.5186 | 63.3591 | -59.0012 | 63.5284 | -58.7631 | -58.9828 | -58.7631 | -0.059509 | -0.041199 | 0.022888 | 0.21973 | 58.5526 | -0.21057 | 58.6121 | -0.15106 | -0.027466 | -0.07782 | 0.091552 | 0.21057 | 0.21057 | -0.009155 | 0.23804 | 0.018311 | 0.27924 | 122.493 | 0.23804 | 122.5296 | 122.4289 | 122.3602 | 122.3694 | 122.3328 | -122.4701 | -122.4381 | 122.4335 | 122.5021 | 58.4885 | 52.4551
1199.7656 | 122.644 | -58.9462 | 63.4735 | -0.079269 | -0.00022432 | 0.060957 | 0.10607 | 0.0010253 | -0.0033538 | -0.0013886 | -0.10101 | 0.00058097 | 0.063324 | 0.063826 | -0.019955 | 0.00055973 | 0.0018159 | -0.44861 | 63.4277 | -59.0744 | 63.414 | -58.8226 | -59.2255 | 0.12817 | -6.9351 | 63.3957 | -58.9828 | 63.4735 | -58.8364 | -59.0836 | -58.8409 | -0.12817 | -0.045777 | -0.05951 | 0.1236 | 59.0744 | -0.27924 | 59.2026 | -0.15106 | -0.036621 | -0.07782 | 0 | 0.10986 | 0.10529 | -0.13733 | 0.14191 | -0.10071 | 0.25177 | 122.4884 | 0.14648 | 122.4564 | 122.5021 | 122.3785 | 122.374 | 122.3419 | -122.5479 | -122.4564 | 122.3602 | 122.4197 | 58.4976 | 52.0111
1200.7656 | 122.7081 | -58.9233 | 63.4827 | 0.004654 | 0.0012711 | 0.060957 | 0.10308 | 0.00017092 | -0.0018586 | -0.0041656 | -0.0094604 | 0.0010084 | 0.062897 | 0.059981 | -0.019314 | 0.00055973 | -0.00096131 | -0.49896 | 63.4003 | -59.0012 | 63.5422 | -58.6853 | -59.1156 | -0.2655 | -6.9672 | 63.4186 | -58.9508 | 63.5422 | -58.7311 | -58.9691 | -58.754 | -0.07782 | -0.082397 | 0.059509 | 0.23804 | 58.6578 | -0.19226 | 58.7357 | -0.11444 | -0.027466 | -0.064087 | 0.059509 | 0.19226 | 0.16937 | -0.045776 | 0.19684 | -0.01831 | 0.31586 | 122.5433 | 0.21973 | 122.493 | 122.4014 | 122.3694 | 122.3236 | 122.3419 | -122.4838 | -122.4335 | 122.4655 | 122.4655 | 58.4244 | 51.9562
1201.7656 | 122.7127 | -58.8821 | 63.501 | 0.004654 | 0.0029801 | 0.063521 | 0.10244 | 0.00017092 | -0.0020722 | -0.0026704 | 0.0027466 | -0.0043322 | 0.065247 | 0.065962 | -0.019527 | 0.0024823 | -0.0033111 | -0.75073 | 63.4323 | -58.9966 | 63.5422 | -58.6716 | -59.0927 | -0.54474 | -6.7795 | 63.414 | -58.9645 | 63.5788 | -58.7128 | -58.9371 | -58.7128 | -0.11444 | -0.068665 | 0.041198 | 0.21057 | 58.3374 | -0.21057 | 58.4518 | -0.09613 | -0.082398 | -0.086976 | 0.077819 | 0.16937 | 0.16937 | -0.054932 | 0.25177 | 0.027466 | 0.32501 | 122.5388 | 0.25177 | 122.5433 | 122.4289 | 122.3785 | 122.3145 | 122.2961 | -122.4976 | -122.4655 | 122.4243 | 122.4609 | 58.1314 | 52.1027
1202.7656 | 122.7219 | -58.8684 | 63.5239 | -0.048752 | -0.0062057 | 0.060103 | 0.10159 | 0.0016663 | -0.0005768 | -0.0033112 | 0.0057984 | 0.00036737 | 0.063751 | 0.05464 | -0.018246 | 0.00077333 | -0.00010671 | -0.26093 | 63.5422 | -58.9645 | 63.4689 | -58.6258 | -59.0515 | -0.62714 | -6.8436 | 63.4369 | -58.9371 | 63.588 | -58.699 | -58.9279 | -58.7082 | -0.096131 | 0.01831 | -0.054932 | 0.24262 | 58.2413 | -0.18311 | 58.3374 | -0.086975 | -0.068665 | -0.086975 | 0.064087 | 0.16937 | 0.16022 | -0.059509 | 0.22888 | 0.009156 | 0.33875 | 122.4335 | 0.23804 | 122.525 | 122.5067 | 122.374 | 122.4106 | 122.3053 | -122.4884 | -122.4609 | 122.3373 | 122.4564 | 58.6075 | 52.0248
1203.7656 | 122.7264 | -58.9005 | 63.4781 | -0.048752 | -0.00065152 | 0.06053 | 0.10266 | 0.0055115 | -0.0012176 | -0.0043792 | -0.00030524 | 0.00015377 | 0.063965 | 0.063399 | -0.018459 | 0.00055973 | -0.00074771 | -0.58136 | 63.4323 | -58.992 | 63.5605 | -58.6121 | -59.2209 | -0.76904 | -6.5048 | 63.3682 | -58.9554 | 63.5559 | -58.7265 | -58.9554 | -58.7173 | -0.091552 | -0.045776 | 0.082398 | 0.28839 | 58.1314 | -0.32043 | 58.223 | -0.22888 | -0.054931 | -0.10986 | 0.07782 | 0.17395 | 0.18311 | -0.054931 | 0.23804 | 0 | 0.37994 | 122.5525 | 0.22888 | 122.5113 | 122.4243 | 122.3236 | 122.3328 | 122.2687 | -122.4701 | -122.4335 | 122.4609 | 122.4564 | 58.3191 | 52.3956
1204.7656 | 122.6532 | -59.0012 | 63.4781 | -0.094528 | -0.0010787 | 0.06288 | 0.10437 | 0.0061523 | -0.0035674 | -0.002884 | -0.14984 | -5.9826e-05 | 0.065674 | 0.066176 | -0.018459 | -0.0011493 | -0.00053411 | -0.73242 | 63.3865 | -59.1019 | 63.3408 | -58.9462 | -59.3308 | -1.0574 | -6.7337 | 63.3591 | -59.0744 | 63.5834 | -58.9142 | -59.3033 | -58.9645 | -0.10071 | -0.091552 | -0.13733 | 0.054932 | 57.9437 | -0.32959 | 58.0444 | -0.22888 | -0.073242 | -0.11902 | 0.10529 | 0.086975 | 0.036621 | -0.30212 | 0.10986 | -0.22888 | 0.15564 | 122.4426 | 0.16022 | 122.6578 | 122.4884 | 122.4335 | 122.3877 | 122.3602 | -122.58 | -122.5525 | 122.3419 | 122.5845 | 58.2687 | 52.2675
1205.7656 | 122.7402 | -58.9325 | 63.4369 | -0.06401 | -0.00043792 | 0.062025 | 0.10308 | 0.0020935 | 0.0002778 | -0.0020294 | -0.1651 | -0.00027343 | 0.063965 | 0.057631 | -0.017391 | 0.0029095 | -0.0013885 | -0.63171 | 63.4048 | -59.0195 | 63.5056 | -58.667 | -58.7357 | -0.6958 | -6.1707 | 63.3453 | -59.0103 | 63.5284 | -58.7585 | -58.9645 | -58.7311 | -0.086975 | -0.032044 | 0.068664 | 0.2655 | 58.2367 | 0.19684 | 58.3237 | 0.28381 | -0.07782 | -0.091553 | 0.091552 | 0.17395 | 0.20142 | -0.032044 | 0.27924 | 0.045776 | 0.35248 | 122.525 | 0.25177 | 122.5388 | 122.4243 | 122.3557 | 122.3373 | 122.2778 | -122.4564 | -122.4472 | 122.438 | 122.4609 | 58.3008 | 52.7618
1206.7656 | 122.6898 | -58.8959 | 63.4598 | -0.056381 | 0.00020288 | 0.061598 | 0.10159 | 0.0016663 | -0.0029266 | -0.00053396 | -0.012512 | 0.00036737 | 0.064392 | 0.062758 | -0.021236 | 0.00077333 | -0.0054473 | -0.66834 | 63.4186 | -58.9966 | 63.5056 | -58.6899 | -59.1202 | -1.1536 | -6.4545 | 63.3865 | -58.9645 | 63.533 | -58.7357 | -58.9645 | -58.7311 | -0.10071 | -0.041199 | 0.045776 | 0.20599 | 57.7423 | -0.2243 | 57.843 | -0.1236 | -0.068665 | -0.073242 | 0.073242 | 0.16022 | 0.16479 | -0.068665 | 0.23346 | 0 | 0.3067 | 122.5021 | 0.22888 | 122.4976 | 122.4152 | 122.3511 | 122.3145 | 122.2824 | -122.4564 | -122.4243 | 122.4014 | 122.4289 | 58.2275 | 52.4414
1207.7656 | 122.6944 | -58.9325 | 63.446 | -0.07164 | 0.0010575 | 0.062239 | 0.10244 | 0.00059812 | -0.002713 | -0.00053396 | -0.012512 | -0.00091423 | 0.064392 | 0.062972 | -0.020168 | 0.00077333 | -0.0018157 | -0.71869 | 63.4232 | -59.0424 | 63.4689 | -58.7036 | -59.1339 | -0.97046 | -6.3126 | 63.3636 | -58.992 | 63.501 | -58.7585 | -58.992 | -58.7585 | -0.10986 | -0.022888 | 0.022888 | 0.22888 | 57.962 | -0.20142 | 58.0719 | -0.091553 | -0.059509 | -0.082398 | 0.054932 | 0.17395 | 0.17395 | -0.059509 | 0.23346 | 0 | 0.33875 | 122.5113 | 0.23346 | 122.493 | 122.4655 | 122.3557 | 122.3557 | 122.2961 | -122.4884 | -122.438 | 122.4014 | 122.4335 | 58.2138 | 52.6199
1208.7656 | 122.7219 | -58.9462 | 63.446 | -0.0029755 | -0.00065152 | 0.062239 | 0.10479 | 0.00081172 | -0.0024994 | 0.00032044 | -0.012512 | -0.00070063 | 0.064179 | 0.06169 | -0.019955 | 0.00077333 | -0.00053411 | -0.78735 | 63.3957 | -59.0332 | 63.4827 | -58.7173 | -59.1476 | -0.88348 | -6.5094 | 63.3728 | -58.992 | 63.5239 | -58.7769 | -58.9966 | -58.7677 | -0.086975 | -0.050354 | 0.036621 | 0.22888 | 58.0627 | -0.20142 | 58.1497 | -0.11444 | -0.045776 | -0.073242 | 0.07782 | 0.16937 | 0.17853 | -0.050354 | 0.2243 | -0.004578 | 0.31586 | 122.5159 | 0.21515 | 122.5159 | 122.4289 | 122.3648 | 122.3419 | 122.319 | -122.4792 | -122.438 | 122.4289 | 122.4701 | 58.1589 | 52.4368
1209.7656 | 122.5891 | -59.0103 | 63.4781 | -0.10979 | -0.00043792 | 0.061385 | 0.10458 | 0.0052979 | -0.001004 | -0.0013886 | -0.12848 | 0.0014356 | 0.065674 | 0.066603 | -0.019314 | 0.0016277 | 0.00010689 | -0.87891 | 63.4003 | -59.1064 | 63.3453 | -58.8913 | -59.3216 | -1.4053 | -6.8756 | 63.3911 | -59.0561 | 63.4048 | -58.9279 | -59.2072 | -58.9417 | -0.09613 | -0.077819 | -0.13275 | 0.11902 | 57.605 | -0.31128 | 57.7011 | -0.21515 | -0.045776 | -0.086975 | -0.073242 | 0.082398 | 0.068665 | -0.19684 | 0.11444 | -0.15106 | 0.21515 | 122.4518 | 0.12817 | 122.4609 | 122.5067 | 122.4472 | 122.4106 | 122.4014 | -122.5845 | -122.5342 | 122.3557 | 122.4152 | 58.1314 | 52.1347
1210.7656 | 122.7219 | -58.96 | 63.4506 | 0.10384 | -1.0718e-05 | 0.06288 | 0.10287 | 0.0014527 | -0.0016448 | -0.0013886 | 0.033264 | 0.00079477 | 0.066101 | 0.058272 | -0.020382 | 0.00055973 | 0.0013885 | -0.99792 | 63.4094 | -59.0652 | 63.4918 | -58.7036 | -59.1705 | -1.1124 | -6.5002 | 63.3362 | -58.9966 | 63.5284 | -58.7585 | -58.9966 | -58.7997 | -0.10529 | -0.041199 | 0.041198 | 0.25635 | 57.8476 | -0.21057 | 57.9529 | -0.10529 | -0.036621 | -0.11444 | 0.077819 | 0.20142 | 0.16022 | -0.036621 | 0.19684 | 0 | 0.36163 | 122.5571 | 0.23804 | 122.525 | 122.4747 | 122.3328 | 122.3694 | 122.2961 | -122.5159 | -122.4472 | 122.4518 | 122.4884 | 57.962 | 52.4597
1211.7656 | 122.7219 | -58.96 | 63.4232 | -0.079269 | -0.00065152 | 0.06053 | 0.10266 | 0.0014527 | -0.002713 | -0.0018158 | -0.0064086 | -0.00070063 | 0.063111 | 0.056563 | -0.018459 | 0.0012005 | -0.00096131 | -0.91553 | 63.3865 | -59.0469 | 63.446 | -58.7402 | -59.1705 | -1.3184 | -6.5277 | 63.3591 | -58.9874 | 63.5513 | -58.7677 | -58.9737 | -58.7631 | -0.086975 | -0.036621 | 0.022888 | 0.21973 | 57.6416 | -0.21057 | 57.7286 | -0.1236 | -0.027466 | -0.064087 | 0.12817 | 0.19226 | 0.19684 | -0.013733 | 0.2243 | 0.013733 | 0.3067 | 122.493 | 0.21973 | 122.5388 | 122.4335 | 122.3465 | 122.3465 | 122.319 | -122.4701 | -122.4106 | 122.406 | 122.5113 | 58.0444 | 52.4323
1212.7656 | 122.7036 | -58.9371 | 63.4735 | -0.1403 | 0.00084388 | 0.06053 | 0.10244 | -0.00089728 | -0.0003632 | -0.0026704 | -0.073547 | -0.0013416 | 0.063538 | 0.059127 | -0.018886 | 0.00034613 | -0.00096131 | -0.90637 | 63.4094 | -58.9874 | 63.4781 | -58.2458 | -58.9371 | -1.6571 | -6.6467 | 63.3591 | -58.9874 | 63.5422 | -58.7128 | -58.96 | -58.754 | -0.050354 | -0.064087 | 0.004577 | 0.69122 | 57.28 | 0 | 57.3303 | 0.050354 | -0.050354 | -0.11444 | 0.068664 | 0.2243 | 0.18311 | -0.022888 | 0.23346 | 0.027466 | 0.74158 | 122.4655 | 0.27466 | 122.5296 | 122.3969 | 122.3465 | 122.3465 | 122.2961 | -122.4609 | -122.4609 | 122.4152 | 122.4792 | 58.0307 | 52.2903
1213.7656 | 122.7036 | -58.9417 | 63.4689 | -0.10979 | 0.00063028 | 0.062025 | 0.10351 | -0.0011109 | -0.0022858 | -0.00010676 | -0.015564 | -0.0015552 | 0.064179 | 0.060622 | -0.018886 | 0.00055973 | -0.0028839 | -0.92468 | 63.4186 | -59.0103 | 63.501 | -58.7036 | -59.1064 | -1.7441 | -6.9168 | 63.3728 | -58.9874 | 63.5239 | -58.7585 | -58.9645 | -58.7814 | -0.068665 | -0.050354 | 0.032044 | 0.23804 | 57.1976 | -0.16479 | 57.2662 | -0.09613 | -0.045777 | -0.09613 | 0.054932 | 0.18311 | 0.16022 | -0.022889 | 0.20599 | 0.022888 | 0.3067 | 122.5113 | 0.22888 | 122.5113 | 122.4289 | 122.3602 | 122.3602 | 122.3145 | -122.4792 | -122.4564 | 122.4426 | 122.4655 | 58.017 | 52.0248
1214.7656 | 122.5662 | -58.9737 | 63.4918 | -0.10216 | 0.0023391 | 0.062239 | 0.10629 | 0.0046569 | -0.0007904 | -0.00053396 | -0.14374 | 0.00036737 | 0.066101 | 0.068526 | -0.021664 | 0.0022687 | -0.0022431 | -1.0803 | 63.4277 | -59.0469 | 63.3728 | -58.8867 | -59.3079 | -1.8494 | -7.1091 | 63.414 | -59.0195 | 63.4277 | -58.9325 | -59.1888 | -58.9233 | -0.073242 | -0.064087 | -0.11902 | 0.086975 | 57.1243 | -0.33417 | 57.1976 | -0.26093 | -0.045776 | -0.07782 | -0.064087 | 0.041199 | 0.050354 | -0.21515 | 0.09613 | -0.16937 | 0.16022 | 122.4197 | 0.086975 | 122.4472 | 122.4747 | 122.4335 | 122.4014 | 122.3877 | -122.5388 | -122.5113 | 122.3465 | 122.4014 | 57.8934 | 51.8646
1215.7656 | 122.7127 | -58.9233 | 63.446 | 0.012284 | 0.0010575 | 0.06053 | 0.10159 | 0.0046569 | -0.0020722 | -0.0041656 | 0.021057 | -0.0013416 | 0.062897 | 0.061476 | -0.0191 | 0.00013253 | -0.0011749 | -0.89722 | 63.4094 | -59.0057 | 63.5147 | -58.6945 | -59.1248 | -1.7395 | -7.0587 | 63.382 | -58.9508 | 63.5605 | -58.7265 | -58.9508 | -58.7814 | -0.082397 | -0.036621 | 0.068664 | 0.22888 | 57.1838 | -0.20142 | 57.2662 | -0.11902 | -0.027466 | -0.064087 | 0.11444 | 0.19684 | 0.14191 | -0.027466 | 0.16937 | 0 | 0.31128 | 122.5204 | 0.22431 | 122.5113 | 122.4152 | 122.3328 | 122.3328 | 122.3053 | -122.4518 | -122.3969 | 122.438 | 122.4838 | 58.0261 | 51.8646
1216.7656 | 122.7219 | -58.9508 | 63.4232 | -0.056381 | -0.0040695 | 0.059889 | 0.10202 | 0.00038452 | 0.0004914 | -0.00096136 | 0.014954 | -0.0028368 | 0.062683 | 0.06169 | -0.019955 | 0.0020551 | -0.00032051 | -0.49439 | 63.446 | -59.0561 | 63.4186 | -58.6761 | -59.1705 | -1.8539 | -6.7474 | 63.327 | -59.0286 | 63.5284 | -58.7631 | -59.024 | -58.7997 | -0.10529 | 0.022888 | -0.004578 | 0.27466 | 57.0969 | -0.21973 | 57.2021 | -0.11444 | -0.077819 | -0.096131 | 0.10528 | 0.18768 | 0.15106 | -0.073242 | 0.22888 | 0.004577 | 0.37994 | 122.4747 | 0.2655 | 122.5571 | 122.5021 | 122.3557 | 122.3969 | 122.2778 | -122.4792 | -122.4518 | 122.3694 | 122.4792 | 58.4564 | 52.2034
1217.7656 | 122.7448 | -58.96 | 63.4094 | -0.10979 | -0.00043792 | 0.060103 | 0.10501 | 0.00038452 | -0.0033538 | -0.00010676 | 0.0057984 | -0.00027343 | 0.065033 | 0.057204 | -0.019314 | 0.00013253 | -0.0028839 | -0.80109 | 63.4186 | -58.9828 | 63.446 | -58.7494 | -59.1751 | -1.9455 | -6.8848 | 63.3682 | -58.9874 | 63.5284 | -58.7357 | -59.0332 | -58.7677 | -0.022888 | 0.009155 | 0.036621 | 0.21057 | 57.0145 | -0.21515 | 57.0374 | -0.19226 | -0.027466 | -0.041199 | 0.11902 | 0.2243 | 0.19226 | -0.073242 | 0.21973 | -0.045776 | 0.23346 | 122.4289 | 0.25177 | 122.5159 | 122.4014 | 122.3557 | 122.3785 | 122.3282 | -122.3923 | -122.3969 | 122.406 | 122.4884 | 58.1589 | 52.0752
1218.7656 | 122.7219 | -58.9783 | 63.4323 | -0.07164 | -0.00065152 | 0.060744 | 0.10458 | 0.0016663 | -0.0016448 | -0.0026704 | 0.0027466 | 0.00079477 | 0.062897 | 0.057204 | -0.019955 | 0.0022687 | 0.0022431 | -0.87891 | 63.4094 | -59.0469 | 63.4232 | -58.7585 | -59.1797 | -1.8311 | -6.6833 | 63.3362 | -59.0195 | 63.501 | -58.7631 | -59.0012 | -58.7952 | -0.068665 | -0.022888 | -0.009155 | 0.21973 | 57.1472 | -0.20142 | 57.2159 | -0.13275 | -0.041199 | -0.09613 | 0.068665 | 0.21515 | 0.1831 | -0.022889 | 0.2243 | 0.01831 | 0.28839 | 122.4701 | 0.25635 | 122.5204 | 122.4564 | 122.3557 | 122.3877 | 122.3145 | -122.4792 | -122.4518 | 122.4014 | 122.4792 | 58.0994 | 52.2949
1219.7656 | 122.7081 | -58.9142 | 63.5056 | -0.06401 | -0.00043792 | 0.059676 | 0.10351 | -0.00046988 | -0.0007904 | -0.00010676 | -0.0094604 | -0.00027343 | 0.065033 | 0.065535 | -0.02145 | 0.0026959 | 0.00053409 | -0.8606 | 63.4003 | -59.0286 | 63.5056 | -58.6945 | -59.1385 | -1.8448 | -6.8344 | 63.3636 | -58.9691 | 63.533 | -58.7448 | -58.9691 | -58.7814 | -0.11444 | -0.10528 | 0 | 0.21973 | 57.0694 | -0.2243 | 57.1838 | -0.10986 | -0.054931 | -0.14191 | 0.027466 | 0.16937 | 0.13275 | -0.054931 | 0.18768 | 0 | 0.33417 | 122.5342 | 0.2243 | 122.5021 | 122.4289 | 122.3328 | 122.3145 | 122.2778 | -122.5342 | -122.4747 | 122.4197 | 122.4472 | 58.0536 | 52.0798
1220.7656 | 122.7219 | -58.8821 | 63.4964 | -0.056381 | 0.0025529 | 0.061812 | 0.10458 | 0.0012391 | -0.0022858 | -0.00074776 | -0.015564 | -0.0013416 | 0.063751 | 0.055922 | -0.02145 | 0.00034613 | -0.0022431 | -0.97961 | 63.4323 | -58.96 | 63.5284 | -58.6487 | -59.0698 | -2.1835 | -7.1274 | 63.414 | -58.9325 | 63.5834 | -58.7082 | -58.9462 | -58.7448 | -0.07782 | -0.064087 | 0.032043 | 0.23346 | 56.6986 | -0.18768 | 56.7764 | -0.10986 | -0.050354 | -0.082398 | 0.086975 | 0.17395 | 0.13733 | -0.064087 | 0.18768 | -0.013733 | 0.31128 | 122.4884 | 0.2243 | 122.5159 | 122.3923 | 122.3465 | 122.3145 | 122.2961 | -122.4564 | -122.4289 | 122.4106 | 122.4655 | 57.9025 | 51.7548
1221.7656 | 122.7173 | -58.8821 | 63.4918 | -0.041122 | 0.0014847 | 0.057967 | 0.10501 | -0.0028199 | -0.0024994 | -0.00053396 | -0.0033568 | -0.0019824 | 0.064179 | 0.057418 | -0.020809 | 0.0031231 | -0.0028839 | -0.737 | 63.501 | -58.9828 | 63.4827 | -58.6166 | -59.111 | -2.2659 | -7.3242 | 63.3911 | -58.9462 | 63.5651 | -58.7082 | -58.9508 | -58.7265 | -0.10071 | 0.009156 | -0.009155 | 0.2655 | 56.6162 | -0.22888 | 56.7169 | -0.12817 | -0.064087 | -0.10071 | 0.073242 | 0.17395 | 0.15564 | -0.068665 | 0.21973 | -0.004578 | 0.36621 | 122.4655 | 0.23804 | 122.5113 | 122.4838 | 122.3373 | 122.3831 | 122.2733 | -122.4747 | -122.438 | 122.3648 | 122.4472 | 58.1451 | 51.5579
1222.7656 | 122.7448 | -58.9005 | 63.4918 | -0.07164 | 0.0010575 | 0.060957 | 0.10458 | 0.0014527 | -0.0035674 | 0.002243 | -0.049133 | 0.0016492 | 0.062256 | 0.059554 | -0.019955 | -0.00029487 | 0.00010689 | -1.0803 | 63.4323 | -58.9828 | 63.382 | -58.96 | -59.1614 | -2.243 | -7.3975 | 63.3774 | -58.9554 | 63.5513 | -58.7219 | -58.9188 | -58.7173 | -0.082397 | -0.059509 | -0.10986 | -0.059509 | 56.6574 | -0.26093 | 56.7398 | -0.17853 | -0.054931 | -0.11444 | 0.05951 | 0.17853 | 0.18311 | -0.01831 | 0.23804 | 0.036621 | 0.022888 | 122.3648 | 0.23346 | 122.5067 | 122.4152 | 122.3328 | 122.3328 | 122.2778 | -122.4747 | -122.4472 | 122.2824 | 122.4518 | 57.8201 | 51.503
1223.7656 | 122.7264 | -58.9188 | 63.4827 | -0.10979 | 0.0019119 | 0.062666 | 0.10287 | -0.0011109 | -0.0029266 | -0.00096136 | 0.14313 | 0.0025036 | 0.065674 | 0.065108 | -0.020595 | 0.0026959 | -0.00074771 | -1.181 | 63.4048 | -59.0195 | 63.5101 | -58.6533 | -59.111 | -2.2202 | -7.5623 | 63.3957 | -59.0012 | 63.5468 | -58.7219 | -58.9508 | -58.7906 | -0.10071 | -0.07782 | 0.027466 | 0.2655 | 56.6986 | -0.19226 | 56.7993 | -0.091553 | -0.082398 | -0.086975 | 0.064087 | 0.19684 | 0.12817 | -0.032044 | 0.21057 | 0.050354 | 0.36621 | 122.5296 | 0.27924 | 122.5479 | 122.4243 | 122.3969 | 122.3236 | 122.3145 | -122.5021 | -122.4838 | 122.4289 | 122.4655 | 57.7377 | 51.3565
1224.7656 | 122.7219 | -58.905 | 63.4964 | -0.10216 | 0.0016983 | 0.061598 | 0.10543 | -0.0013245 | -0.0012176 | -0.002243 | -0.018616 | 0.00058097 | 0.06482 | 0.067031 | -0.019527 | 0.0024823 | -0.00010671 | -1.3092 | 63.414 | -59.0012 | 63.4918 | -58.7219 | -59.1385 | -2.6138 | -7.576 | 63.3911 | -58.9645 | 63.5605 | -58.7173 | -58.9508 | -58.7357 | -0.096131 | -0.082398 | -0.004578 | 0.1831 | 56.2912 | -0.23346 | 56.3873 | -0.13733 | -0.05951 | -0.10529 | 0.064087 | 0.18768 | 0.16937 | -0.045777 | 0.22888 | 0.013733 | 0.27924 | 122.493 | 0.24719 | 122.525 | 122.4152 | 122.3557 | 122.319 | 122.2961 | -122.4976 | -122.4609 | 122.3969 | 122.4655 | 57.5958 | 51.329
1225.7656 | 122.7173 | -58.8776 | 63.4964 | -0.094528 | -1.0718e-05 | 0.060103 | 0.10479 | -0.0011109 | -0.0012176 | -0.003952 | -0.012512 | -0.0015552 | 0.064179 | 0.056136 | -0.020595 | -0.00072207 | 0.00032049 | -1.3229 | 63.4277 | -59.0057 | 63.5056 | -58.6899 | -59.1202 | -2.6962 | -7.9605 | 63.4186 | -58.9508 | 63.5925 | -58.7128 | -58.9371 | -58.7082 | -0.12817 | -0.068665 | 0.009155 | 0.18768 | 56.1813 | -0.24262 | 56.3095 | -0.11444 | -0.073243 | -0.07782 | 0.09613 | 0.16479 | 0.16937 | -0.05951 | 0.24262 | 0.013733 | 0.31586 | 122.5113 | 0.23804 | 122.5433 | 122.4335 | 122.3694 | 122.3053 | 122.2961 | -122.5021 | -122.4472 | 122.3831 | 122.4701 | 57.5546 | 50.9171
1226.7656 | 122.6852 | -58.8959 | 63.4918 | -0.086899 | 0.00020288 | 0.059035 | 0.10437 | 0.0012391 | -0.0014312 | -0.002884 | -0.012512 | -0.0017688 | 0.065674 | 0.063826 | -0.0191 | 0.0020551 | -0.0018157 | -1.1032 | 63.4872 | -58.9554 | 63.5239 | -58.6029 | -59.1064 | -2.5909 | -8.139 | 63.414 | -58.9371 | 63.588 | -58.6761 | -58.9417 | -58.7173 | -0.059509 | -0.004577 | 0.032044 | 0.29297 | 56.3049 | -0.21057 | 56.3644 | -0.15106 | -0.041199 | -0.07782 | 0.096131 | 0.21973 | 0.17853 | -0.045776 | 0.21973 | -0.004577 | 0.35248 | 122.4792 | 0.26093 | 122.525 | 122.4426 | 122.3511 | 122.3831 | 122.3099 | -122.4472 | -122.4289 | 122.4197 | 122.4838 | 57.7927 | 50.7568
1227.7656 | 122.7173 | -58.9188 | 63.4735 | -0.07164 | 0.0010575 | 0.060957 | 0.10372 | -0.0058105 | -0.0016448 | 0.00074764 | -0.015564 | -0.00027343 | 0.062256 | 0.061476 | -0.021877 | 0.00034613 | 0.0030975 | -1.2039 | 63.4232 | -59.0149 | 63.4003 | -58.9554 | -59.23 | -2.3209 | -8.0566 | 63.382 | -58.9645 | 63.5468 | -58.7265 | -59.0149 | -58.7311 | -0.096131 | -0.050354 | -0.073242 | -0.036621 | 56.5979 | -0.31128 | 56.694 | -0.21515 | -0.045777 | -0.091553 | 0.073242 | 0.19226 | 0.18768 | -0.096131 | 0.23346 | -0.050354 | 0.05951 | 122.4152 | 0.23804 | 122.5113 | 122.4381 | 122.3465 | 122.3419 | 122.3007 | -122.4884 | -122.4381 | 122.319 | 122.4655 | 57.7148 | 50.8621
1228.7656 | 122.7219 | -58.8776 | 63.5056 | -0.12505 | 0.0012711 | 0.060103 | 0.10501 | -0.0015381 | -0.0020722 | -0.00032036 | 0.11566 | -0.00048703 | 0.063324 | 0.06169 | -0.019527 | 0.0022687 | -0.0050201 | -1.2955 | 63.4506 | -59.0103 | 63.5605 | -58.5983 | -59.0607 | -2.1927 | -8.0246 | 63.4781 | -58.9188 | 63.5422 | -58.6441 | -58.9554 | -58.7494 | -0.13275 | -0.054931 | 0.054932 | 0.27923 | 56.6849 | -0.18311 | 56.8176 | -0.050354 | -0.041199 | -0.027466 | 0.036621 | 0.23346 | 0.12817 | -0.07782 | 0.16937 | -0.036621 | 0.41199 | 122.5708 | 0.27466 | 122.4609 | 122.4609 | 122.3969 | 122.3282 | 122.3557 | -122.5159 | -122.4243 | 122.438 | 122.4197 | 57.5821 | 50.853
1229.7656 | 122.6898 | -58.9691 | 63.3774 | -0.12505 | -0.00065152 | 0.059035 | 0.10223 | 0.00017092 | -0.0001496 | -0.0026704 | -0.018616 | -0.00091423 | 0.066101 | 0.059127 | -0.02145 | 0.0012005 | -0.0030975 | -1.268 | 63.3728 | -59.0561 | 63.4552 | -58.699 | -59.1614 | -1.0941 | -7.6309 | 63.3316 | -59.0195 | 63.5468 | -58.4335 | -59.2484 | -59.0057 | -0.086975 | -0.004577 | 0.07782 | 0.27008 | 57.8751 | -0.19226 | 57.962 | -0.10529 | -0.050354 | -0.045776 | 0.16937 | 0.53558 | -0.036621 | -0.27924 | 0.013733 | -0.22888 | 0.35706 | 122.5113 | 0.58594 | 122.5662 | 122.4289 | 122.3511 | 122.3419 | 122.3007 | -122.4335 | -122.3969 | 122.4243 | 122.5159 | 57.7011 | 51.3382
1230.7656 | 122.7448 | -58.9737 | 63.4003 | -0.1403 | 0.00041648 | 0.057967 | 0.10394 | -0.0023925 | -0.0033538 | -0.0018158 | -0.018616 | -0.0019824 | 0.065247 | 0.058272 | -0.018459 | 0.00034613 | -0.00053411 | -1.1948 | 63.3545 | -59.0607 | 63.446 | -58.7082 | -59.166 | -1.1353 | -7.7225 | 63.3316 | -59.0012 | 63.533 | -58.7494 | -58.9645 | -58.786 | -0.086975 | -0.045777 | 0.045776 | 0.2655 | 57.8384 | -0.19226 | 57.9254 | -0.10529 | -0.027466 | -0.068665 | 0.13275 | 0.2243 | 0.18768 | 0.009155 | 0.21515 | 0.036621 | 0.35248 | 122.5067 | 0.25177 | 122.5342 | 122.4152 | 122.3328 | 122.3282 | 122.3053 | -122.4609 | -122.4014 | 122.4197 | 122.5067 | 57.7789 | 51.2512
1231.7656 | 122.699 | -58.9966 | 63.414 | -0.094528 | 0.0019119 | 0.063521 | 0.10415 | -0.00025628 | -0.0003632 | 0.00032044 | -0.012512 | 0.00058097 | 0.064392 | 0.058699 | -0.018886 | 0.0026959 | -0.0026703 | -1.1765 | 63.3453 | -59.0973 | 63.3499 | -58.8272 | -59.2758 | -1.3275 | -8.1665 | 63.3087 | -59.0515 | 63.4506 | -58.8455 | -59.079 | -58.8547 | -0.10071 | -0.068664 | -0.064086 | 0.16937 | 57.6691 | -0.27924 | 57.7698 | -0.17853 | -0.054932 | -0.10529 | 0.036622 | 0.15106 | 0.14191 | -0.082397 | 0.19684 | -0.027465 | 0.27008 | 122.4472 | 0.20599 | 122.5021 | 122.4426 | 122.3602 | 122.3419 | 122.3053 | -122.5113 | -122.4655 | 122.3465 | 122.4472 | 57.8201 | 50.8301
1232.7656 | 122.6898 | -59.0286 | 63.382 | -0.10216 | -1.0718e-05 | 0.060957 | 0.10501 | -0.0013245 | -0.0052764 | -0.00096136 | -0.030823 | -0.0013416 | 0.065674 | 0.062758 | -0.020595 | 0.00098693 | -0.0013885 | -1.2817 | 63.3224 | -59.0836 | 63.3545 | -58.8089 | -59.285 | -1.6754 | -8.1985 | 63.2996 | -59.0927 | 63.4323 | -58.8409 | -59.0836 | -58.8593 | -0.054932 | -0.059509 | -0.027466 | 0.21973 | 57.3532 | -0.25635 | 57.4081 | -0.20142 | -0.064087 | -0.082397 | 0.050354 | 0.18768 | 0.16937 | -0.054932 | 0.23346 | 0.009155 | 0.27466 | 122.438 | 0.25177 | 122.525 | 122.406 | 122.3923 | 122.3511 | 122.3282 | -122.4655 | -122.4747 | 122.3831 | 122.4609 | 57.7469 | 50.8301
1233.7656 | 122.644 | -58.9966 | 63.3408 | -0.10979 | -0.00043792 | 0.060103 | 0.10223 | 0.0016663 | -0.0003632 | -0.0024566 | -0.015564 | 0.0014356 | 0.065674 | 0.062117 | -0.020595 | 0.0016277 | -0.0045929 | -1.03 | 63.327 | -59.0881 | 63.4415 | -58.7219 | -59.198 | -0.94299 | -8.0338 | 63.3041 | -59.0607 | 63.4277 | -58.4839 | -59.1064 | -59.0195 | -0.091553 | -0.013733 | 0.10071 | 0.27466 | 58.0536 | -0.20142 | 58.1451 | -0.10986 | -0.064087 | -0.036621 | 0.086975 | 0.51269 | -0.022888 | -0.10986 | 0.041199 | -0.045776 | 0.36621 | 122.5296 | 0.57678 | 122.4884 | 122.4152 | 122.3648 | 122.3236 | 122.3007 | -122.4289 | -122.4014 | 122.438 | 122.4243 | 57.9666 | 50.9628
1234.7656 | 122.7539 | -58.9828 | 63.4232 | -0.1403 | 0.00041648 | 0.059248 | 0.10308 | -0.0038879 | -0.0020722 | -0.0026704 | -0.027771 | 0.00229 | 0.063751 | 0.05934 | -0.019955 | 0.0022687 | -0.00010671 | -1.0391 | 63.3453 | -59.0561 | 63.4323 | -58.7265 | -59.1614 | -1.1032 | -8.0246 | 63.3133 | -59.0332 | 63.5284 | -58.7448 | -58.9966 | -58.7814 | -0.073242 | -0.07782 | 0.009155 | 0.25635 | 57.8796 | -0.17853 | 57.9529 | -0.10529 | -0.050354 | -0.10986 | 0.10528 | 0.23804 | 0.20142 | -0.013733 | 0.25177 | 0.036621 | 0.32959 | 122.4884 | 0.28839 | 122.5616 | 122.4014 | 122.3465 | 122.3282 | 122.2961 | -122.4792 | -122.4564 | 122.4152 | 122.5113 | 57.9437 | 50.9583
1235.7656 | 122.7356 | -58.9783 | 63.3728 | -0.10979 | 0.00063028 | 0.062239 | 0.10458 | -0.0021789 | -0.0042084 | -0.0016022 | -0.0064086 | 0.001222 | 0.065888 | 0.065962 | -0.020809 | 0.00055973 | 0.0018159 | -1.1856 | 63.3316 | -59.0881 | 63.4094 | -58.7631 | -59.2209 | -1.2039 | -8.0383 | 63.3041 | -59.0332 | 63.4872 | -58.786 | -59.0286 | -58.8089 | -0.10986 | -0.041199 | 0.036621 | 0.21515 | 57.7744 | -0.24262 | 57.8842 | -0.13275 | -0.054932 | -0.068665 | 0.11444 | 0.19226 | 0.16937 | -0.050354 | 0.2243 | 0.004578 | 0.32501 | 122.4976 | 0.24719 | 122.5204 | 122.4197 | 122.3373 | 122.3099 | 122.2824 | -122.4609 | -122.406 | 122.3877 | 122.4655 | 57.7927 | 50.9399
1236.7656 | 122.7448 | -59.0012 | 63.4048 | -0.12505 | 0.0021255 | 0.060316 | 0.10543 | -4.2682e-05 | -0.0050628 | -0.0013886 | 0.0027466 | -0.00070063 | 0.062897 | 0.062972 | -0.02145 | 0.00055973 | -0.0022431 | -1.2543 | 63.3316 | -59.1156 | 63.3957 | -58.7769 | -59.2346 | -1.1993 | -8.2214 | 63.3133 | -59.0881 | 63.4827 | -58.8135 | -59.0515 | -58.7997 | -0.11444 | -0.073242 | -0.009155 | 0.22431 | 57.8018 | -0.23346 | 57.9163 | -0.11902 | -0.086975 | -0.091553 | 0.07782 | 0.18768 | 0.20142 | -0.050354 | 0.28839 | 0.036621 | 0.33875 | 122.5113 | 0.27466 | 122.5708 | 122.4472 | 122.4014 | 122.3328 | 122.3145 | -122.5204 | -122.493 | 122.3969 | 122.4838 | 57.7469 | 50.7797
1237.7656 | 122.7402 | -59.0607 | 63.3316 | -0.06401 | 0.00084388 | 0.060103 | 0.10394 | -0.00025628 | -0.0024994 | -0.00074776 | -0.027771 | -0.0013416 | 0.064392 | 0.064467 | -0.02145 | 0.0012005 | 0.0018159 | -1.1765 | 63.2904 | -59.1476 | 63.3224 | -58.8364 | -59.3033 | -0.99792 | -7.9559 | 63.2629 | -59.0973 | 63.3774 | -58.8776 | -59.1339 | -58.9005 | -0.086975 | -0.041199 | -0.009155 | 0.2243 | 58.0627 | -0.24262 | 58.1497 | -0.15564 | -0.036621 | -0.068665 | 0.045776 | 0.18311 | 0.16022 | -0.073242 | 0.19684 | -0.036621 | 0.31128 | 122.4701 | 0.21973 | 122.4747 | 122.438 | 122.3602 | 122.3511 | 122.3236 | -122.4792 | -122.4289 | 122.3831 | 122.438 | 57.8842 | 51.1047
1238.7656 | 122.6715 | -59.0607 | 63.3224 | -0.086899 | -0.00065152 | 0.062025 | 0.10565 | -0.0017517 | -0.0016448 | 0.00074764 | -0.033874 | -0.00027343 | 0.064179 | 0.068526 | -0.0191 | 0.00013253 | -0.0022431 | -1.2543 | 63.2858 | -59.1568 | 63.2355 | -58.96 | -59.3353 | -1.1307 | -8.1024 | 63.2584 | -59.1064 | 63.3774 | -58.9005 | -59.1843 | -58.9188 | -0.09613 | -0.036621 | -0.086975 | 0.10071 | 57.93 | -0.27466 | 58.0261 | -0.17853 | -0.045776 | -0.064087 | 0.054931 | 0.16022 | 0.14191 | -0.1236 | 0.18768 | -0.07782 | 0.19684 | 122.3923 | 0.20599 | 122.4838 | 122.4426 | 122.3648 | 122.3465 | 122.319 | -122.4792 | -122.4289 | 122.2961 | 122.438 | 57.8064 | 50.9583
1239.7656 | 122.6532 | -59.0378 | 63.3774 | -0.15556 | 0.0014847 | 0.059248 | 0.10437 | 0.00081172 | -0.0042084 | -0.0024566 | -0.033874 | -0.0017688 | 0.063965 | 0.065749 | -0.019955 | 0.00077333 | -0.0018157 | -1.355 | 63.2858 | -59.1339 | 63.327 | -58.8638 | -59.3308 | -0.83313 | -8.1482 | 63.2996 | -59.0652 | 63.4094 | -58.905 | -59.1339 | -58.9188 | -0.09613 | -0.091552 | -0.050354 | 0.17395 | 58.2047 | -0.29297 | 58.3008 | -0.19684 | -0.027466 | -0.077819 | 0.032044 | 0.13275 | 0.11902 | -0.09613 | 0.14648 | -0.068664 | 0.27008 | 122.4609 | 0.16022 | 122.4747 | 122.4197 | 122.3648 | 122.3236 | 122.3373 | -122.5113 | -122.4426 | 122.3648 | 122.4472 | 57.6828 | 50.8896
1240.7656 | 122.731 | -59.0515 | 63.3362 | -0.10979 | 0.0010575 | 0.060957 | 0.10351 | -0.0026063 | -0.0016448 | -0.0026704 | -0.024719 | -0.00091423 | 0.065674 | 0.063185 | -0.020382 | 0.00055973 | -0.0030975 | -1.2268 | 63.2767 | -59.1522 | 63.3408 | -58.8318 | -59.2941 | -0.37994 | -8.0246 | 63.2446 | -59.1522 | 63.4232 | -58.8272 | -59.0973 | -58.8913 | -0.10071 | -0.05951 | 0.004577 | 0.21973 | 58.6716 | -0.24261 | 58.7723 | -0.14191 | -0.10071 | -0.091553 | 0.086975 | 0.2243 | 0.16022 | -0.045776 | 0.26093 | 0.054932 | 0.32044 | 122.493 | 0.32501 | 122.5754 | 122.4289 | 122.3969 | 122.3282 | 122.2961 | -122.4884 | -122.4884 | 122.3923 | 122.4747 | 57.8247 | 51.0269
1241.7656 | 122.7127 | -59.0698 | 63.2858 | -0.086899 | -0.0010787 | 0.061598 | 0.10244 | -0.0030335 | -0.0031402 | 0.00053404 | -0.039978 | 0.00036737 | 0.063751 | 0.051863 | -0.018673 | 0.00013253 | -0.0037383 | -1.2268 | 63.2538 | -59.1843 | 63.3041 | -58.8501 | -59.3308 | -0.55389 | -7.8873 | 63.2355 | -59.1431 | 63.4048 | -58.873 | -59.1522 | -58.9188 | -0.11444 | -0.032044 | 0.01831 | 0.21973 | 58.5159 | -0.26093 | 58.6304 | -0.14648 | -0.073242 | -0.050354 | 0.11902 | 0.19684 | 0.15106 | -0.082398 | 0.2243 | -0.009156 | 0.33417 | 122.4884 | 0.27008 | 122.5479 | 122.438 | 122.3785 | 122.3236 | 122.3053 | -122.4701 | -122.4289 | 122.374 | 122.4747 | 57.843 | 51.1826
1242.7656 | 122.7219 | -59.0424 | 63.327 | -0.10979 | 0.00063028 | 0.060957 | 0.10565 | -0.0019653 | -0.0020722 | -0.00053396 | -0.024719 | 0.00079477 | 0.063111 | 0.06404 | -0.019955 | 0.00055973 | 0.00010689 | -1.3184 | 63.295 | -59.1568 | 63.3179 | -58.8364 | -59.3079 | -1.3321 | -8.432 | 63.2355 | -59.1202 | 63.4094 | -58.8593 | -59.1705 | -58.9142 | -0.11444 | -0.032043 | -0.009155 | 0.20599 | 57.7103 | -0.2655 | 57.8247 | -0.15106 | -0.07782 | -0.091552 | 0.082398 | 0.1831 | 0.12817 | -0.12817 | 0.20599 | -0.050354 | 0.32043 | 122.4747 | 0.26093 | 122.5296 | 122.4518 | 122.3557 | 122.3373 | 122.2778 | -122.4838 | -122.4472 | 122.3602 | 122.4518 | 57.724 | 50.6104
1243.7656 | 122.6852 | -59.0561 | 63.3591 | -0.14793 | 0.0010575 | 0.061598 | 0.10543 | -0.0032471 | -0.0016448 | -0.00074776 | -0.018616 | -0.0013416 | 0.066529 | 0.064681 | -0.021236 | 0.00077333 | -0.0033111 | -1.3641 | 63.3179 | -59.1431 | 63.327 | -58.8364 | -59.3216 | -0.88806 | -8.6975 | 63.2629 | -59.1202 | 63.4003 | -58.8547 | -59.1248 | -58.9096 | -0.086975 | -0.041199 | -0.032044 | 0.21973 | 58.168 | -0.2655 | 58.255 | -0.17853 | -0.064087 | -0.096131 | 0.041199 | 0.20142 | 0.14648 | -0.068665 | 0.21057 | -0.004578 | 0.3067 | 122.4701 | 0.2655 | 122.5204 | 122.4609 | 122.3831 | 122.374 | 122.319 | -122.5021 | -122.4792 | 122.3831 | 122.4564 | 57.692 | 50.3586
1244.7656 | 122.6944 | -59.0469 | 63.3545 | -0.10216 | 0.0012711 | 0.061171 | 0.10415 | -0.0011109 | -0.0024994 | -0.0030976 | -0.021667 | -0.00048703 | 0.063324 | 0.059554 | -0.018886 | 0.0029095 | -0.0028839 | -1.5335 | 63.3179 | -59.1339 | 63.3224 | -58.8318 | -59.2987 | -1.0254 | -8.6197 | 63.295 | -59.0744 | 63.414 | -58.8593 | -59.111 | -58.8913 | -0.086975 | -0.036621 | -0.032043 | 0.21515 | 58.0215 | -0.25177 | 58.1085 | -0.1648 | -0.027466 | -0.059509 | 0.059509 | 0.18768 | 0.15564 | -0.064087 | 0.18311 | -0.036621 | 0.30212 | 122.4564 | 0.21515 | 122.4884 | 122.4518 | 122.3694 | 122.3648 | 122.3419 | -122.4884 | -122.4289 | 122.3694 | 122.4609 | 57.5134 | 50.4272
1245.7656 | 122.6303 | -59.0881 | 63.3133 | -0.13267 | -0.00065152 | 0.061385 | 0.10458 | 0.0016663 | 0.001773 | -0.0030976 | -0.046081 | -0.00027343 | 0.064179 | 0.059767 | -0.019314 | 0.0014141 | -0.0054473 | -1.6525 | 63.2767 | -59.1476 | 63.3041 | -58.873 | -59.3445 | -0.96588 | -8.5968 | 63.2492 | -59.1293 | 63.2904 | -58.7311 | -59.024 | -58.9417 | -0.059509 | -0.036621 | -0.009155 | 0.21515 | 58.1223 | -0.25635 | 58.1818 | -0.19684 | -0.041198 | -0.064086 | -0.022888 | 0.35706 | 0.14648 | 0.064087 | 0.18768 | 0.10529 | 0.27466 | 122.4518 | 0.39825 | 122.4197 | 122.4243 | 122.3785 | 122.3648 | 122.3373 | -122.4609 | -122.4426 | 122.3923 | 122.3785 | 57.4356 | 50.4913
1246.7656 | 122.6715 | -59.0744 | 63.3316 | -0.10216 | 0.00063028 | 0.061812 | 0.10543 | -0.00068368 | -0.0016448 | -0.002243 | -0.052185 | 0.0014356 | 0.063111 | 0.06169 | -0.021664 | 0.00077333 | -0.00053411 | -1.5884 | 63.2721 | -59.1522 | 63.295 | -58.8867 | -59.3582 | -0.84686 | -8.4869 | 63.2492 | -59.1339 | 63.3591 | -58.9279 | -59.1751 | -58.9371 | -0.07782 | -0.059509 | -0.036621 | 0.18768 | 58.2275 | -0.28381 | 58.3054 | -0.20599 | -0.059509 | -0.082397 | 0.027466 | 0.14648 | 0.13733 | -0.10071 | 0.19684 | -0.041199 | 0.2655 | 122.4472 | 0.20599 | 122.493 | 122.4243 | 122.3831 | 122.3465 | 122.3236 | -122.4838 | -122.4655 | 122.3694 | 122.4335 | 57.486 | 50.5875
1247.7656 | 122.7081 | -59.0836 | 63.2904 | -0.079269 | 0.00063028 | 0.058394 | 0.10501 | -0.0038879 | -0.001004 | -0.00010676 | -0.036926 | -0.0028368 | 0.06546 | 0.063613 | -0.020382 | 0.00055973 | -0.0048065 | -1.7395 | 63.3041 | -59.1568 | 63.3087 | -58.8547 | -59.3399 | -0.51727 | -8.4137 | 63.2492 | -59.1476 | 63.3911 | -58.8913 | -59.0881 | -58.9142 | -0.073242 | 0.013733 | 0.018311 | 0.22888 | 58.5663 | -0.25635 | 58.6395 | -0.18311 | -0.064087 | -0.041198 | 0.10071 | 0.19226 | 0.16937 | -0.004578 | 0.23346 | 0.059509 | 0.30212 | 122.4655 | 0.25635 | 122.5388 | 122.4609 | 122.3969 | 122.3877 | 122.3328 | -122.4472 | -122.438 | 122.3923 | 122.4747 | 57.3441 | 50.6699
1248.7656 | 122.6761 | -59.0927 | 63.2904 | -0.1403 | 0.00020288 | 0.060744 | 0.10287 | 0.0023071 | -0.0022858 | -0.0030976 | -0.039978 | -0.00048703 | 0.064179 | 0.059554 | -0.019741 | 0.00098693 | -0.00032051 | -1.7212 | 63.2492 | -59.1614 | 63.2721 | -58.8638 | -59.3353 | -0.75989 | -8.5098 | 63.2309 | -59.1476 | 63.3591 | -58.905 | -59.1751 | -58.9371 | -0.068665 | -0.041198 | -0.01831 | 0.22888 | 58.3328 | -0.24262 | 58.4015 | -0.17395 | -0.054932 | -0.059509 | 0.068665 | 0.18768 | 0.15564 | -0.082398 | 0.21057 | -0.027466 | 0.29755 | 122.4335 | 0.24262 | 122.5067 | 122.4106 | 122.3785 | 122.3419 | 122.3236 | -122.4518 | -122.438 | 122.3648 | 122.4518 | 57.3715 | 50.5829
1249.7656 | 122.7036 | -59.1064 | 63.3087 | -0.048752 | -0.0010787 | 0.060103 | 0.10522 | 0.0014527 | -0.0012176 | -0.00053396 | -0.036926 | -0.00027343 | 0.065033 | 0.062117 | -0.020168 | 0.0026959 | 0.00010689 | -1.7944 | 63.2675 | -59.1751 | 63.2767 | -58.8821 | -59.3536 | -1.03 | -8.432 | 63.2355 | -59.166 | 63.3636 | -58.9188 | -59.1431 | -58.9371 | -0.068665 | -0.041199 | -0.032044 | 0.2243 | 58.0765 | -0.24719 | 58.1451 | -0.17853 | -0.05951 | -0.073242 | 0.054931 | 0.18768 | 0.16937 | -0.036621 | 0.22888 | 0.022889 | 0.29297 | 122.4518 | 0.24719 | 122.5296 | 122.4426 | 122.4014 | 122.374 | 122.3419 | -122.4838 | -122.4747 | 122.3831 | 122.4701 | 57.312 | 50.6744
1250.7656 | 122.6715 | -59.1248 | 63.3041 | -0.07164 | 0.00041648 | 0.062025 | 0.10394 | 0.0029479 | -0.0003632 | -0.0020294 | -0.033874 | 0.00015377 | 0.064392 | 0.062545 | -0.021023 | 0.0018413 | -0.0011749 | -1.9455 | 63.2309 | -59.2163 | 63.2309 | -58.9142 | -59.3857 | -1.2222 | -8.1161 | 63.208 | -59.1797 | 63.327 | -58.9417 | -59.1522 | -58.9554 | -0.091553 | -0.073242 | -0.073242 | 0.21057 | 57.9025 | -0.26093 | 57.9941 | -0.16937 | -0.054931 | -0.09613 | 0.022888 | 0.18311 | 0.16937 | -0.027466 | 0.2243 | 0.027465 | 0.30212 | 122.4472 | 0.23804 | 122.5067 | 122.4472 | 122.3877 | 122.3557 | 122.3328 | -122.5204 | -122.4838 | 122.3557 | 122.4518 | 57.1793 | 51.0086
1251.7656 | 122.7036 | -59.1293 | 63.2721 | -0.10979 | 0.00041648 | 0.061171 | 0.10458 | 0.0010253 | -0.0016448 | 0.00032044 | -0.021667 | -0.00027343 | 0.062256 | 0.058486 | -0.022091 | 0.00055973 | -0.0020295 | -2.3209 | 63.1989 | -59.2209 | 63.2309 | -58.9188 | -59.4086 | -1.7029 | -8.4686 | 63.2034 | -59.1751 | 63.3224 | -58.9508 | -59.2209 | -58.9874 | -0.091553 | -0.073242 | -0.041199 | 0.21057 | 57.4265 | -0.27924 | 57.518 | -0.18768 | -0.045777 | -0.068665 | 0.050354 | 0.17853 | 0.14191 | -0.091553 | 0.18768 | -0.045776 | 0.30212 | 122.4518 | 0.2243 | 122.4976 | 122.4197 | 122.3785 | 122.3282 | 122.3328 | -122.493 | -122.4472 | 122.3602 | 122.4518 | 56.8085 | 50.6607
1252.7656 | 122.6715 | -59.1431 | 63.2629 | -0.094528 | 0.00020288 | 0.062239 | 0.10351 | -0.0019653 | -0.0007904 | -0.00053396 | -0.052185 | -0.001128 | 0.063965 | 0.064253 | -0.019955 | 0.0012005 | -0.0041657 | -2.3346 | 63.2126 | -59.2255 | 63.2401 | -58.9233 | -59.4131 | -1.5198 | -8.3954 | 63.176 | -59.198 | 63.3087 | -58.9828 | -59.2484 | -58.9874 | -0.082398 | -0.050354 | -0.022888 | 0.21973 | 57.6233 | -0.27008 | 57.7057 | -0.18768 | -0.054932 | -0.086975 | 0.045777 | 0.16022 | 0.15564 | -0.10529 | 0.21057 | -0.050354 | 0.30212 | 122.4655 | 0.21515 | 122.5067 | 122.438 | 122.374 | 122.3557 | 122.319 | -122.4884 | -122.4609 | 122.3831 | 122.4518 | 56.8085 | 50.7477
1253.7656 | 122.6807 | -59.1614 | 63.2629 | -0.11742 | 0.00020288 | 0.061385 | 0.10629 | 0.0014527 | -0.0012176 | -0.002243 | -0.064392 | -0.0017688 | 0.065247 | 0.066817 | -0.021236 | 0.0039777 | -0.00010671 | -2.5269 | 63.1897 | -59.2529 | 63.2126 | -58.9371 | -59.4177 | -1.506 | -8.4229 | 63.2034 | -59.2209 | 63.295 | -58.9783 | -59.2667 | -59.0012 | -0.091553 | -0.073242 | -0.050354 | 0.2243 | 57.6553 | -0.25635 | 57.7469 | -0.16479 | -0.059509 | -0.059509 | 0.032044 | 0.18311 | 0.16022 | -0.10529 | 0.21973 | -0.045777 | 0.31586 | 122.4655 | 0.24262 | 122.5159 | 122.4426 | 122.4243 | 122.3511 | 122.3648 | -122.5159 | -122.4838 | 122.374 | 122.4564 | 56.6345 | 50.7385
1254.7656 | 122.7081 | -59.1431 | 63.2263 | -0.10216 | 0.00084388 | 0.061171 | 0.10394 | -0.00089728 | -0.0005768 | -0.0035248 | -0.024719 | -0.00048703 | 0.064179 | 0.068526 | -0.020168 | 0.00077333 | -0.0016021 | -2.6642 | 63.1989 | -59.2346 | 63.2446 | -58.9233 | -59.4086 | -1.3229 | -8.313 | 63.176 | -59.2072 | 63.3041 | -58.9462 | -59.2072 | -58.992 | -0.091553 | -0.027465 | 0.018311 | 0.21973 | 57.8201 | -0.2655 | 57.9117 | -0.17395 | -0.064087 | -0.050354 | 0.07782 | 0.19684 | 0.15106 | -0.064087 | 0.21515 | 0 | 0.31128 | 122.4792 | 0.26093 | 122.5113 | 122.4335 | 122.3831 | 122.3419 | 122.319 | -122.4609 | -122.4335 | 122.3877 | 122.4472 | 56.4789 | 50.8301
1255.7656 | 122.6807 | -59.0881 | 63.2812 | -0.094528 | 0.00084388 | 0.062239 | 0.10501 | -0.00046988 | -0.0003632 | -0.002243 | -0.024719 | -0.00048703 | 0.065247 | 0.05699 | -0.019314 | 0.0018413 | -0.0043793 | -2.8473 | 63.2172 | -59.2163 | 63.2492 | -58.8867 | -59.3536 | -1.9867 | -8.3679 | 63.1897 | -59.166 | 63.3591 | -58.9188 | -59.1568 | -58.9508 | -0.12817 | -0.064087 | -0.032043 | 0.20142 | 57.1014 | -0.2655 | 57.2296 | -0.13733 | -0.07782 | -0.091553 | 0.07782 | 0.16937 | 0.13733 | -0.068664 | 0.21515 | 0.009156 | 0.32959 | 122.4655 | 0.24719 | 122.525 | 122.4335 | 122.3557 | 122.3053 | 122.2778 | -122.4976 | -122.4472 | 122.3373 | 122.4472 | 56.2408 | 50.7202
1256.7656 | 122.7036 | -59.1797 | 63.1943 | -0.1403 | 0.00063028 | 0.061812 | 0.10415 | -4.2682e-05 | -0.0012176 | -0.0024566 | -0.021667 | -0.00048703 | 0.062683 | 0.057418 | -0.020382 | -0.0015765 | -0.00053411 | -2.6413 | 63.176 | -59.285 | 63.1943 | -58.9691 | -59.4223 | -1.2085 | -8.2031 | 63.121 | -59.2438 | 63.2675 | -58.9783 | -59.2484 | -59.0332 | -0.10529 | -0.018311 | 0 | 0.21057 | 57.9712 | -0.24262 | 58.0765 | -0.13733 | -0.064087 | -0.073242 | 0.073242 | 0.20142 | 0.14648 | -0.068665 | 0.21057 | -0.004578 | 0.31586 | 122.4792 | 0.2655 | 122.5113 | 122.4609 | 122.3648 | 122.3557 | 122.3007 | -122.4792 | -122.438 | 122.374 | 122.4472 | 56.5384 | 50.9766
1257.7656 | 122.7127 | -59.1202 | 63.2904 | -0.094528 | -0.00022432 | 0.06288 | 0.10501 | -0.00089728 | -0.0018586 | -0.001175 | -0.039978 | -0.00027343 | 0.063324 | 0.060408 | -0.021023 | 0.0026959 | -0.0024567 | -2.9892 | 63.2401 | -59.1934 | 63.2584 | -58.873 | -59.3582 | -1.8448 | -8.9493 | 63.2126 | -59.1888 | 63.3636 | -58.9188 | -59.1751 | -58.9462 | -0.073242 | -0.050354 | -0.032043 | 0.24719 | 57.2754 | -0.23804 | 57.3486 | -0.16479 | -0.068665 | -0.07782 | 0.073242 | 0.20142 | 0.17395 | -0.054932 | 0.24262 | 0.013733 | 0.32043 | 122.4518 | 0.27008 | 122.5525 | 122.4335 | 122.4014 | 122.3602 | 122.3328 | -122.4838 | -122.4792 | 122.3785 | 122.4838 | 56.131 | 50.1709
1258.7656 | 122.699 | -59.166 | 63.2217 | -0.11742 | -0.0019333 | 0.062453 | 0.10394 | 0.0020935 | -0.002713 | -0.0018158 | -0.021667 | -0.00091423 | 0.06482 | 0.059981 | -0.02145 | -8.1274e-05 | 0.0018159 | -3.0212 | 63.1943 | -59.2758 | 63.1989 | -58.9325 | -59.4223 | -1.68 | -8.4961 | 63.1439 | -59.2163 | 63.3087 | -58.9737 | -59.2438 | -58.992 | -0.10986 | -0.027466 | -0.022888 | 0.23346 | 57.486 | -0.25635 | 57.5958 | -0.14648 | -0.050354 | -0.07782 | 0.086975 | 0.19226 | 0.17395 | -0.077819 | 0.22431 | -0.027465 | 0.34332 | 122.4747 | 0.24262 | 122.525 | 122.4701 | 122.3602 | 122.3602 | 122.3099 | -122.4976 | -122.4381 | 122.3648 | 122.4747 | 56.1447 | 50.6699
1259.7656 | 122.6669 | -59.166 | 63.2538 | -0.10216 | -0.00043792 | 0.060103 | 0.10543 | -0.0011109 | -0.0012176 | -0.0035248 | -0.06134 | -0.0017688 | 0.063324 | 0.064253 | -0.020809 | 0.0012005 | 0.0018159 | -3.1311 | 63.1989 | -59.2438 | 63.3499 | -59.0195 | -59.523 | -1.7624 | -8.4732 | 63.1577 | -59.2163 | 63.2721 | -58.9966 | -59.2804 | -58.9966 | -0.077819 | -0.054931 | 0.096131 | 0.14648 | 57.4036 | -0.35706 | 57.4814 | -0.27924 | -0.050354 | -0.09613 | 0.018311 | 0.16937 | 0.16937 | -0.11444 | 0.21973 | -0.064087 | 0.2243 | 122.5937 | 0.21973 | 122.4884 | 122.4426 | 122.374 | 122.3648 | 122.3236 | -122.4976 | -122.4701 | 122.5159 | 122.4381 | 56.0349 | 50.6927
1260.7656 | 122.6578 | -59.1248 | 63.2584 | -0.041122 | 0.0012711 | 0.061171 | 0.10372 | 0.00038452 | -0.002713 | -0.0041656 | -0.021667 | 0.001222 | 0.064179 | 0.061049 | -0.019314 | -0.00029487 | -0.0011749 | -3.2639 | 63.1943 | -59.2621 | 63.3316 | -58.7906 | -59.5505 | -2.0004 | -8.6609 | 63.1485 | -59.2072 | 63.2812 | -58.992 | -59.2484 | -59.0103 | -0.13733 | -0.064087 | 0.073242 | 0.33417 | 57.1243 | -0.42572 | 57.2617 | -0.28839 | -0.082397 | -0.10986 | 0.022888 | 0.13275 | 0.11444 | -0.1236 | 0.19684 | -0.041199 | 0.4715 | 122.5937 | 0.21515 | 122.4884 | 122.4564 | 122.3557 | 122.319 | 122.2733 | -122.5204 | -122.4655 | 122.4564 | 122.406 | 55.8609 | 50.4639
1261.7656 | 122.7493 | -59.1019 | 63.2446 | -0.086899 | 0.0016983 | 0.062666 | 0.10501 | 0.00038452 | -0.0020722 | -0.0043792 | -0.021667 | -0.0024096 | 0.063751 | 0.061904 | -0.020595 | 0.00013253 | -0.0050201 | -3.0121 | 63.2172 | -59.2072 | 63.2904 | -58.8318 | -59.3262 | -1.5198 | -8.4045 | 63.1805 | -59.1751 | 63.3774 | -58.8776 | -59.1385 | -58.9188 | -0.10528 | -0.027466 | 0.045776 | 0.27008 | 57.5821 | -0.2243 | 57.6874 | -0.11902 | -0.073242 | -0.064087 | 0.13275 | 0.22431 | 0.18311 | -0.036621 | 0.25635 | 0.036621 | 0.37537 | 122.4976 | 0.29755 | 122.5525 | 122.4243 | 122.3557 | 122.319 | 122.2824 | -122.4518 | -122.4197 | 122.3923 | 122.4792 | 56.0898 | 50.6973
1262.7656 | 122.731 | -59.0744 | 63.2767 | -0.07164 | 0.00084388 | 0.060316 | 0.10543 | -0.00046988 | -0.0029266 | -0.0033112 | -0.0094604 | 0.00058097 | 0.06247 | 0.060195 | -0.02145 | -0.00093567 | -0.0028839 | -3.273 | 63.2309 | -59.2209 | 63.3179 | -58.8089 | -59.3124 | -2.2568 | -8.7936 | 63.1989 | -59.1522 | 63.4003 | -58.8547 | -59.111 | -58.905 | -0.14648 | -0.045776 | 0.041199 | 0.2655 | 56.8176 | -0.23804 | 56.9641 | -0.091553 | -0.07782 | -0.077819 | 0.1236 | 0.21973 | 0.16937 | -0.036621 | 0.24719 | 0.041199 | 0.41199 | 122.5388 | 0.29755 | 122.5525 | 122.4518 | 122.3511 | 122.3053 | 122.2733 | -122.4976 | -122.4289 | 122.3923 | 122.4747 | 55.8014 | 50.2808
1263.7656 | 122.7402 | -59.1385 | 63.2675 | -0.056381 | -0.00043792 | 0.060957 | 0.10266 | -0.0011109 | -0.0012176 | -0.002243 | -0.015564 | 0.001222 | 0.063538 | 0.055922 | -0.021023 | 0.0037641 | -0.0018157 | -3.4195 | 63.208 | -59.2163 | 63.2812 | -58.8272 | -59.3124 | -2.5543 | -8.8943 | 63.1897 | -59.1431 | 63.3774 | -58.873 | -59.1339 | -58.9371 | -0.07782 | -0.059509 | 0.013733 | 0.31128 | 56.5842 | -0.17395 | 56.662 | -0.09613 | -0.004577 | -0.07782 | 0.10986 | 0.2655 | 0.20142 | 0.004578 | 0.20599 | 0.009155 | 0.3891 | 122.4976 | 0.27008 | 122.5204 | 122.4243 | 122.3328 | 122.3465 | 122.3282 | -122.4838 | -122.4106 | 122.4197 | 122.5159 | 55.719 | 50.2441
1264.7656 | 122.7356 | -59.1202 | 63.2767 | -0.10979 | 0.0021255 | 0.059035 | 0.10479 | -0.0015381 | -0.0024994 | 0.00010684 | -0.024719 | -0.00070063 | 0.065888 | 0.05934 | -0.020168 | 0.0018413 | -0.0043793 | -3.2913 | 63.1714 | -59.2484 | 63.2767 | -58.8547 | -59.3262 | -2.1973 | -8.6014 | 63.1668 | -59.198 | 63.3636 | -58.8821 | -59.1522 | -58.9554 | -0.12817 | -0.10528 | 0 | 0.2655 | 56.9229 | -0.20599 | 57.0511 | -0.07782 | -0.07782 | -0.10986 | 0.086975 | 0.23804 | 0.1648 | -0.032044 | 0.24262 | 0.045776 | 0.39368 | 122.525 | 0.31586 | 122.5616 | 122.4197 | 122.3648 | 122.2916 | 122.287 | -122.525 | -122.4747 | 122.3969 | 122.4838 | 55.8289 | 50.5188
1265.7656 | 122.731 | -59.1476 | 63.2309 | -0.11742 | -0.00043792 | 0.059889 | 0.10501 | 0.0012391 | -0.0016448 | -0.0016022 | -0.046081 | -0.00048703 | 0.065033 | 0.054854 | -0.018886 | 0.0022687 | -0.00096131 | -3.273 | 63.1622 | -59.2712 | 63.2401 | -58.873 | -59.3582 | -1.7624 | -8.3862 | 63.1165 | -59.23 | 63.327 | -58.9096 | -59.2026 | -58.9783 | -0.1236 | -0.068665 | 0.009155 | 0.27466 | 57.3853 | -0.21057 | 57.5088 | -0.086975 | -0.082398 | -0.11444 | 0.09613 | 0.23804 | 0.16937 | -0.054932 | 0.25177 | 0.027466 | 0.39825 | 122.5113 | 0.32043 | 122.5571 | 122.4335 | 122.3465 | 122.3099 | 122.2641 | -122.5021 | -122.4609 | 122.3877 | 122.4747 | 55.8746 | 50.7614
1267.4062 | 122.731 | -59.1751 | 63.1989 | -0.11742 | 0.0012711 | 0.060316 | 0.10437 | 0.00038452 | -0.0014312 | -0.00074776 | -0.030823 | 0.00058097 | 0.063751 | 0.060195 | -0.019741 | 0.0022687 | -0.0011749 | -3.4561 | 63.1439 | -59.3033 | 63.1897 | -58.9508 | -59.436 | -2.3438 | -8.3313 | 63.1485 | -59.2529 | 63.2904 | -58.9828 | -59.2346 | -58.992 | -0.12817 | -0.054932 | -0.009156 | 0.2243 | 56.8314 | -0.26093 | 56.9595 | -0.13275 | -0.07782 | -0.050354 | 0.091552 | 0.19226 | 0.18311 | -0.059509 | 0.26093 | 0.018311 | 0.35248 | 122.493 | 0.27008 | 122.5433 | 122.4472 | 122.4014 | 122.319 | 122.3236 | -122.5021 | -122.4518 | 122.3648 | 122.4655 | 55.719 | 50.8438
1268.3125 | 122.6761 | -59.1614 | 63.2263 | -0.033493 | 0.0010575 | 0.062025 | 0.10629 | -0.0013245 | -0.0024994 | 0.00096124 | -0.027771 | -0.00070063 | 0.063751 | 0.05934 | -0.020168 | 0.0014141 | -0.0011749 | -3.5019 | 63.1668 | -59.23 | 63.2401 | -58.8821 | -59.3765 | -2.3895 | -8.3313 | 63.1668 | -59.23 | 63.2538 | -58.9874 | -59.2438 | -59.0469 | -0.068665 | -0.059509 | 0.013733 | 0.27924 | 56.7719 | -0.21515 | 56.8405 | -0.14648 | -0.068665 | -0.059509 | 0.027466 | 0.17395 | 0.11444 | -0.082397 | 0.18311 | -0.013732 | 0.3479 | 122.4701 | 0.24262 | 122.4838 | 122.3969 | 122.3969 | 122.3282 | 122.3282 | -122.4564 | -122.4564 | 122.4014 | 122.4152 | 55.6595 | 50.8301
1268.9219 | 122.6669 | -59.2163 | 63.1668 | -0.094528 | 0.00084388 | 0.061171 | 0.10543 | -0.0032471 | -0.0001496 | -0.001175 | -0.04303 | 0.001222 | 0.066742 | 0.060408 | -0.020382 | 0.00013253 | -0.0041657 | -3.5751 | 63.1439 | -59.2987 | 63.1393 | -58.9554 | -59.4635 | -2.3483 | -8.5602 | 63.1119 | -59.2529 | 63.2538 | -59.0286 | -59.2896 | -59.0515 | -0.082397 | -0.022888 | -0.027466 | 0.26093 | 56.868 | -0.24719 | 56.9504 | -0.16479 | -0.036621 | -0.054932 | 0.086975 | 0.18768 | 0.1648 | -0.073242 | 0.20142 | -0.036621 | 0.34332 | 122.438 | 0.22431 | 122.5067 | 122.4426 | 122.3648 | 122.3602 | 122.3282 | -122.4655 | -122.4197 | 122.3557 | 122.4701 | 55.6412 | 50.6561
1269.7656 | 122.6395 | -59.2163 | 63.1989 | -0.07164 | 0.00041648 | 0.061385 | 0.10522 | 0.0035889 | -0.0029266 | -0.00032036 | -0.033874 | -0.00048703 | 0.065674 | 0.063185 | -0.021023 | 0.0012005 | -0.0020295 | -3.653 | 63.1531 | -59.2804 | 63.208 | -58.9188 | -59.4131 | -2.2339 | -8.5052 | 63.1348 | -59.2804 | 63.2263 | -59.0149 | -59.2941 | -59.0652 | -0.064087 | -0.045777 | 0.009155 | 0.29755 | 56.9824 | -0.19684 | 57.0465 | -0.13275 | -0.064087 | -0.064087 | 0.027465 | 0.20142 | 0.15106 | -0.077819 | 0.21515 | -0.013732 | 0.36163 | 122.4884 | 0.2655 | 122.5067 | 122.4335 | 122.4152 | 122.3694 | 122.3511 | -122.4792 | -122.4792 | 122.4243 | 122.4426 | 55.5634 | 50.7111
1270.7812 | 122.5983 | -59.2346 | 63.2172 | -0.025863 | 0.0010575 | 0.062025 | 0.10437 | 0.0044433 | -0.0003632 | -0.0030976 | -0.09491 | -0.0017688 | 0.065674 | 0.067244 | -0.017818 | 0.0022687 | -0.0030975 | -3.8406 | 63.1805 | -59.3079 | 63.1073 | -59.0515 | -59.5093 | -2.4124 | -8.6151 | 63.1622 | -59.2896 | 63.1714 | -59.0881 | -59.3719 | -59.1339 | -0.073242 | -0.036621 | -0.10986 | 0.18311 | 56.8222 | -0.27466 | 56.8954 | -0.20142 | -0.054932 | -0.054932 | -0.045776 | 0.14648 | 0.10071 | -0.13733 | 0.15564 | -0.082397 | 0.25635 | 122.4152 | 0.20142 | 122.4609 | 122.4884 | 122.4518 | 122.4152 | 122.3969 | -122.525 | -122.5067 | 122.3419 | 122.406 | 55.394 | 50.6195
1271.7656 | 122.7036 | -59.198 | 63.176 | -0.079269 | -0.00086512 | 0.060744 | 0.10629 | 0.0014527 | -0.002713 | 0.0016022 | -0.0064086 | 0.00015377 | 0.065674 | 0.057845 | -0.020382 | 0.0016277 | -0.00032051 | -4.0146 | 63.1256 | -59.2941 | 63.208 | -58.9096 | -59.4177 | -2.6138 | -8.2947 | 63.0936 | -59.2255 | 63.2812 | -58.9783 | -59.2529 | -59.024 | -0.09613 | -0.050354 | 0.032044 | 0.28839 | 56.5842 | -0.21973 | 56.6803 | -0.1236 | -0.027466 | -0.082397 | 0.10529 | 0.21973 | 0.17395 | -0.054932 | 0.20142 | -0.027466 | 0.38452 | 122.5021 | 0.24719 | 122.5067 | 122.4197 | 122.319 | 122.3236 | 122.2916 | -122.4701 | -122.4014 | 122.406 | 122.4792 | 55.1834 | 50.9033
1272.7656 | 122.7264 | -59.2209 | 63.1851 | -0.094528 | 0.0016983 | 0.061385 | 0.10437 | 0.0059387 | -0.001004 | -0.0041656 | 0.0088502 | -0.0017688 | 0.062683 | 0.061904 | -0.018886 | 0.0012005 | -0.0011749 | -4.0421 | 63.1348 | -59.3079 | 63.1302 | -58.8043 | -59.436 | -2.2293 | -8.3542 | 63.0753 | -59.2941 | 63.2584 | -58.9966 | -59.2621 | -59.0515 | -0.086975 | -0.050354 | -0.054932 | 0.41656 | 56.9916 | -0.21515 | 57.0786 | -0.12817 | -0.073242 | -0.10986 | 0.073242 | 0.2243 | 0.16937 | -0.041199 | 0.24261 | 0.032043 | 0.50354 | 122.438 | 0.29755 | 122.5525 | 122.4426 | 122.3694 | 122.3557 | 122.2961 | -122.493 | -122.4792 | 122.3511 | 122.4792 | 55.1788 | 50.8667
1273.7656 | 122.7173 | -59.198 | 63.1805 | -0.07164 | 0.0027665 | 0.063094 | 0.10308 | -4.2682e-05 | -0.0001496 | 0.00096124 | -0.064392 | -0.00070063 | 0.06546 | 0.064681 | -0.020168 | 0.00098693 | -0.0033111 | -4.216 | 63.121 | -59.3079 | 63.0341 | -59.1248 | -59.2804 | -2.5543 | -8.4274 | 63.1073 | -59.2575 | 63.2767 | -58.9417 | -59.2712 | -59.0057 | -0.10986 | -0.059509 | -0.14648 | 0.073242 | 56.6437 | -0.082398 | 56.7535 | 0.027465 | -0.059509 | -0.073242 | 0.09613 | 0.25635 | 0.19226 | -0.073242 | 0.25177 | -0.013733 | 0.18311 | 122.3419 | 0.31586 | 122.5342 | 122.4289 | 122.3648 | 122.319 | 122.3053 | -122.4884 | -122.438 | 122.2321 | 122.4747 | 54.982 | 50.7706
1274.7656 | 122.7356 | -59.2438 | 63.1302 | -0.056381 | 0.00063028 | 0.062666 | 0.10672 | -0.00089728 | -0.0020722 | -0.0033112 | 0.0057984 | -0.00091423 | 0.064606 | 0.064467 | -0.020168 | 0.0016277 | -0.0018157 | -4.0054 | 63.0569 | -59.3582 | 63.4003 | -59.1614 | -59.8434 | -2.2751 | -8.1573 | 63.0295 | -59.3262 | 63.2172 | -59.0607 | -59.2804 | -59.0698 | -0.11444 | -0.073242 | 0.27008 | 0.082397 | 56.9687 | -0.59967 | 57.0831 | -0.48523 | -0.082398 | -0.10071 | 0.086975 | 0.18311 | 0.17395 | -0.036622 | 0.25635 | 0.045776 | 0.19684 | 122.7585 | 0.2655 | 122.5433 | 122.4152 | 122.3557 | 122.3007 | 122.2733 | -122.4884 | -122.4564 | 122.644 | 122.4609 | 55.2383 | 51.0864
1275.7656 | 122.6166 | -59.3033 | 63.121 | -0.11742 | 0.00041648 | 0.060744 | 0.1065 | 0.0025207 | -0.0007904 | 0.00074764 | -0.13458 | 0.0010084 | 0.064179 | 0.064894 | -0.019741 | 0.0014141 | -0.0024567 | -4.2618 | 63.1027 | -59.4086 | 63.0295 | -59.1019 | -59.6375 | -3.1174 | -8.226 | 63.0936 | -59.3811 | 63.1302 | -59.2026 | -59.4727 | -59.1934 | -0.10529 | -0.018311 | -0.091553 | 0.20142 | 56.1859 | -0.33417 | 56.2912 | -0.22888 | -0.07782 | -0.027466 | 0.009155 | 0.10071 | 0.10986 | -0.16937 | 0.18768 | -0.091552 | 0.3067 | 122.438 | 0.17853 | 122.5113 | 122.5113 | 122.4747 | 122.406 | 122.3969 | -122.5296 | -122.5021 | 122.3328 | 122.4335 | 55.0415 | 51.0773
1276.7656 | 122.6807 | -59.2758 | 63.1165 | -0.06401 | 0.0016983 | 0.061171 | 0.10522 | -0.0034607 | -0.0003632 | -0.002243 | -0.027771 | 0.00058097 | 0.062256 | 0.059981 | -0.018246 | 0.00098693 | 0.00053409 | -4.2572 | 63.0569 | -59.3719 | 63.1348 | -58.9874 | -59.5001 | -2.1835 | -8.1116 | 63.0341 | -59.3445 | 63.1714 | -59.0744 | -59.3582 | -59.1339 | -0.09613 | -0.059509 | 0.018311 | 0.28839 | 57.0923 | -0.2243 | 57.1884 | -0.12817 | -0.068664 | -0.082397 | 0.054932 | 0.20142 | 0.14191 | -0.082397 | 0.21057 | -0.013733 | 0.38452 | 122.5067 | 0.27008 | 122.5159 | 122.4289 | 122.3785 | 122.3328 | 122.3099 | -122.4884 | -122.4609 | 122.4106 | 122.4472 | 55.0186 | 51.1642
1277.7656 | 122.7173 | -59.2896 | 63.1348 | -0.11742 | 0.0014847 | 0.061385 | 0.10458 | -0.00046988 | 0.0002778 | -0.0024566 | -0.0094604 | -0.00070063 | 0.064179 | 0.061263 | -0.019741 | 0.0020551 | -0.0024567 | -4.3808 | 63.0524 | -59.3811 | 63.121 | -58.9828 | -59.491 | -2.4033 | -7.663 | 63.0157 | -59.3445 | 63.1622 | -59.079 | -59.3536 | -59.1522 | -0.091553 | -0.082398 | -0.013733 | 0.3067 | 56.8863 | -0.20142 | 56.9778 | -0.10986 | -0.054931 | -0.11902 | 0.027465 | 0.21057 | 0.13733 | -0.064087 | 0.19226 | -0.009156 | 0.39825 | 122.5021 | 0.2655 | 122.5067 | 122.4335 | 122.3602 | 122.3419 | 122.3053 | -122.5159 | -122.4792 | 122.4106 | 122.4518 | 54.9088 | 51.6266
1278.7656 | 122.6898 | -59.2667 | 63.1393 | -0.14793 | 0.0014847 | 0.061812 | 0.10437 | -4.2682e-05 | -0.0003632 | -0.002884 | -0.033874 | -0.00048703 | 0.065888 | 0.067458 | -0.022091 | -8.1274e-05 | -0.00053411 | -4.5868 | 63.0569 | -59.3765 | 63.1348 | -58.96 | -59.4772 | -2.0828 | -8.1299 | 63.0157 | -59.3491 | 63.1851 | -59.0698 | -59.3582 | -59.111 | -0.10986 | -0.082397 | -0.004577 | 0.3067 | 57.1838 | -0.21057 | 57.2937 | -0.10071 | -0.082397 | -0.1236 | 0.045777 | 0.19684 | 0.15564 | -0.091552 | 0.23804 | -0.009155 | 0.41656 | 122.5113 | 0.27924 | 122.5342 | 122.4335 | 122.3648 | 122.3236 | 122.2824 | -122.5159 | -122.4884 | 122.4014 | 122.4518 | 54.6799 | 51.1368
1279.7656 | 122.6852 | -59.285 | 63.1439 | -0.10216 | 0.0010575 | 0.061385 | 0.10437 | 0.0016663 | -0.002713 | -0.0016022 | -0.0064086 | 0.00058097 | 0.065033 | 0.065108 | -0.022091 | 0.0026959 | -0.00074771 | -4.7012 | 63.0844 | -59.3399 | 63.1714 | -58.9554 | -59.436 | -2.3987 | -8.1985 | 63.0615 | -59.3124 | 63.2126 | -59.0469 | -59.3079 | -59.1202 | -0.054932 | -0.059509 | 0.027466 | 0.32959 | 56.8863 | -0.15106 | 56.9412 | -0.09613 | -0.027466 | -0.082398 | 0.068664 | 0.23804 | 0.16479 | -0.022888 | 0.19226 | 0.004578 | 0.38452 | 122.5113 | 0.2655 | 122.525 | 122.4243 | 122.374 | 122.3694 | 122.3465 | -122.4838 | -122.4564 | 122.4564 | 122.4976 | 54.5837 | 51.0864
1280.7656 | 122.6532 | -59.3033 | 63.1577 | -0.094528 | 0.0019119 | 0.062025 | 0.10629 | -0.0017517 | -0.0024994 | -0.00053396 | -0.11932 | -0.00091423 | 0.06482 | 0.065108 | -0.020809 | 0.0014141 | -0.0011749 | -4.7791 | 63.1027 | -59.4131 | 63.089 | -59.0652 | -59.4955 | -2.6184 | -8.5739 | 63.0798 | -59.3399 | 63.1485 | -59.111 | -59.4131 | -59.1705 | -0.10986 | -0.054932 | -0.068665 | 0.23804 | 56.6849 | -0.19226 | 56.7947 | -0.082397 | -0.036621 | -0.07782 | -0.009155 | 0.19226 | 0.13275 | -0.10986 | 0.16937 | -0.073242 | 0.3479 | 122.5021 | 0.22888 | 122.4884 | 122.5159 | 122.4197 | 122.406 | 122.3831 | -122.5708 | -122.4976 | 122.3923 | 122.4518 | 54.5242 | 50.7294
1281.7656 | 122.7264 | -59.3124 | 63.1073 | -0.10979 | 0.0031937 | 0.061171 | 0.10394 | -0.0017517 | -0.002713 | -0.002243 | 0.018005 | 0.002931 | 0.064179 | 0.058913 | -0.019527 | 0.0024823 | -0.00053411 | -4.7379 | 63.0432 | -59.3811 | 63.121 | -58.9966 | -59.4955 | -2.7603 | -8.1161 | 63.0112 | -59.3491 | 63.1668 | -59.0652 | -59.3491 | -59.1431 | -0.068665 | -0.064087 | 0.013733 | 0.31586 | 56.5521 | -0.18311 | 56.6208 | -0.11444 | -0.036621 | -0.096131 | 0.059509 | 0.24719 | 0.16937 | -0.036621 | 0.20599 | 0 | 0.38452 | 122.5021 | 0.28381 | 122.5159 | 122.4243 | 122.3602 | 122.3557 | 122.3236 | -122.4884 | -122.4564 | 122.4335 | 122.4792 | 54.5746 | 51.1963
1282.7656 | 122.6257 | -59.3216 | 63.1439 | -0.079269 | 0.0014847 | 0.060744 | 0.10394 | 0.00017092 | -0.0016448 | -0.00074776 | -0.021667 | -0.001128 | 0.06482 | 0.059981 | -0.018459 | 0.0012005 | -0.0037383 | -4.6326 | 63.0707 | -59.3948 | 63.0981 | -59.0103 | -59.5093 | -2.6917 | -8.0063 | 63.0478 | -59.3491 | 63.121 | -59.1248 | -59.4177 | -59.1705 | -0.073242 | -0.073242 | -0.045776 | 0.31128 | 56.6299 | -0.18768 | 56.7032 | -0.11444 | -0.027466 | -0.09613 | -0.022888 | 0.19684 | 0.15106 | -0.096131 | 0.17853 | -0.068665 | 0.38452 | 122.493 | 0.2243 | 122.4701 | 122.4655 | 122.3969 | 122.3923 | 122.3694 | -122.5388 | -122.493 | 122.4197 | 122.4426 | 54.689 | 51.3153
1283.7656 | 122.6395 | -59.285 | 63.1622 | -0.094528 | 0.0027665 | 0.061171 | 0.10586 | 0.0020935 | -0.0016448 | -0.0041656 | -0.027771 | -0.00070063 | 0.064179 | 0.057204 | -0.019741 | -8.1274e-05 | 0.0013885 | -4.7791 | 63.0936 | -59.3308 | 63.1393 | -58.9554 | -59.4681 | -3.1403 | -8.226 | 63.0707 | -59.3033 | 63.1668 | -59.0881 | -59.3765 | -59.1248 | -0.045777 | -0.068664 | -0.022888 | 0.32959 | 56.1447 | -0.18311 | 56.1905 | -0.13733 | -0.018311 | -0.091552 | 0.004578 | 0.19684 | 0.16022 | -0.091553 | 0.17853 | -0.073242 | 0.37537 | 122.4701 | 0.21515 | 122.4701 | 122.4243 | 122.374 | 122.3785 | 122.3557 | -122.493 | -122.4655 | 122.4243 | 122.4518 | 54.5059 | 51.059
1284.7656 | 122.6349 | -59.2712 | 63.1851 | -0.07164 | 0.0031937 | 0.06288 | 0.10522 | 0.0014527 | -0.0016448 | -0.0018158 | -0.0094604 | -0.00070063 | 0.06247 | 0.058913 | -0.020168 | -0.00029487 | -0.00074771 | -4.985 | 63.1027 | -59.3353 | 63.1577 | -58.9508 | -59.4589 | -3.0533 | -8.1482 | 63.089 | -59.2941 | 63.1577 | -59.0836 | -59.3582 | -59.1293 | -0.064087 | -0.082398 | -0.027466 | 0.32043 | 56.218 | -0.18768 | 56.282 | -0.1236 | -0.022888 | -0.096131 | -0.027466 | 0.18768 | 0.14191 | -0.086975 | 0.16479 | -0.064087 | 0.38452 | 122.493 | 0.21057 | 122.4518 | 122.438 | 122.3831 | 122.374 | 122.3602 | -122.5204 | -122.4792 | 122.4289 | 122.4289 | 54.2862 | 51.123
1285.7656 | 122.7127 | -59.3399 | 63.0661 | -0.1403 | -0.00043792 | 0.062666 | 0.10607 | 0.0014527 | -0.0012176 | -0.00010676 | -0.076599 | -0.00048703 | 0.06546 | 0.066817 | -0.021664 | 0.0018413 | -0.0020295 | -5.0262 | 62.9974 | -59.491 | 63.002 | -59.1339 | -59.6466 | -2.417 | -8.0017 | 62.9791 | -59.4131 | 63.121 | -59.2026 | -59.4498 | -59.1568 | -0.15106 | -0.068664 | -0.064087 | 0.20599 | 56.9229 | -0.3067 | 57.074 | -0.15564 | -0.073242 | -0.086975 | 0.054932 | 0.13733 | 0.18311 | -0.10986 | 0.25635 | -0.036621 | 0.35706 | 122.493 | 0.21057 | 122.5342 | 122.4884 | 122.3923 | 122.3373 | 122.319 | -122.5571 | -122.4792 | 122.3419 | 122.4609 | 54.3137 | 51.3382
1286.7656 | 122.7036 | -59.3445 | 63.0844 | -0.07164 | -0.0015061 | 0.061598 | 0.10437 | 0.0029479 | -0.001004 | -0.002884 | -0.0064086 | 0.00058097 | 0.063751 | 0.071089 | -0.019741 | 0.0020551 | 0.00096129 | -4.9942 | 63.002 | -59.436 | 63.0707 | -59.0332 | -59.5184 | -2.0782 | -7.6584 | 62.9883 | -59.3719 | 63.1256 | -59.1339 | -59.3811 | -59.1843 | -0.091553 | -0.082398 | -0.013733 | 0.31128 | 57.2662 | -0.17395 | 57.3578 | -0.082398 | -0.027466 | -0.096131 | 0.041198 | 0.21057 | 0.16022 | -0.036622 | 0.18768 | -0.009156 | 0.40283 | 122.5067 | 0.23804 | 122.4976 | 122.438 | 122.3602 | 122.3465 | 122.3328 | -122.5204 | -122.4564 | 122.4152 | 122.4701 | 54.3503 | 51.6861
1287.7656 | 122.7402 | -59.2575 | 63.1348 | -0.1403 | -0.00022432 | 0.060744 | 0.10159 | 0.0020935 | -0.0014312 | -0.00010676 | 0.018005 | -0.00048703 | 0.064179 | 0.065108 | -0.021023 | 0.0012005 | 0.0011749 | -5.1041 | 63.0661 | -59.3582 | 63.1714 | -58.9005 | -59.4315 | -2.7145 | -7.9468 | 63.0569 | -59.2712 | 63.2584 | -59.1431 | -59.2712 | -59.0469 | -0.10071 | -0.068665 | 0.036621 | 0.35705 | 56.543 | -0.17395 | 56.6437 | -0.073243 | -0.013733 | -0.07782 | 0.1236 | 0.11444 | 0.21057 | -0.013733 | 0.2243 | 0 | 0.45776 | 122.5296 | 0.12817 | 122.5296 | 122.4243 | 122.3282 | 122.3236 | 122.3145 | -122.493 | -122.406 | 122.4289 | 122.5159 | 54.1534 | 51.3107
1288.7656 | 122.7127 | -59.2804 | 63.1119 | -0.033493 | 0.0029801 | 0.062666 | 0.1065 | 0.0023071 | -0.0012176 | -0.0020294 | 0.011902 | -0.001128 | 0.066742 | 0.058699 | -0.019955 | 0.0022687 | -0.0024567 | -5.159 | 63.0524 | -59.3948 | 63.1531 | -58.96 | -59.4772 | -2.1881 | -8.0841 | 63.0249 | -59.3445 | 63.1851 | -59.0836 | -59.3582 | -59.0973 | -0.11444 | -0.059509 | 0.041199 | 0.32044 | 57.0923 | -0.19684 | 57.2067 | -0.082398 | -0.064086 | -0.086975 | 0.073243 | 0.19684 | 0.18311 | -0.077819 | 0.24719 | -0.013733 | 0.43487 | 122.5479 | 0.26093 | 122.5296 | 122.4472 | 122.3694 | 122.3328 | 122.3053 | -122.5067 | -122.4564 | 122.4335 | 122.4655 | 54.1214 | 51.1963
1289.7656 | 122.6578 | -59.3262 | 63.1119 | -0.12505 | 0.0025529 | 0.061171 | 0.10522 | -4.2682e-05 | 0.0004914 | -0.002243 | -0.015564 | -0.00091423 | 0.06247 | 0.063826 | -0.0191 | 0.0018413 | 0.00032049 | -4.9576 | 63.0432 | -59.4086 | 63.0798 | -59.0286 | -59.5413 | -2.0096 | -7.695 | 63.0066 | -59.3857 | 63.1073 | -59.1568 | -59.4177 | -59.1843 | -0.082397 | -0.068664 | -0.032043 | 0.29755 | 57.3166 | -0.21515 | 57.399 | -0.13275 | -0.059509 | -0.10529 | -0.004577 | 0.16937 | 0.14191 | -0.091553 | 0.20142 | -0.032044 | 0.37994 | 122.4884 | 0.22888 | 122.493 | 122.4518 | 122.3923 | 122.3694 | 122.3328 | -122.5204 | -122.4976 | 122.406 | 122.4335 | 54.3686 | 51.6312
1290.7656 | 122.6166 | -59.3948 | 63.0432 | -0.13267 | 0.00063028 | 0.062239 | 0.108 | -0.00046988 | -0.0020722 | -0.00032036 | -0.12238 | 0.001222 | 0.066315 | 0.061476 | -0.020809 | 0.0022687 | 0.00096129 | -4.9805 | 63.0203 | -59.5001 | 62.9974 | -59.1202 | -59.6466 | -2.092 | -7.4478 | 62.9791 | -59.4223 | 63.0615 | -59.2438 | -59.5276 | -59.2667 | -0.10529 | -0.022888 | -0.045776 | 0.27466 | 57.3029 | -0.25177 | 57.4081 | -0.14648 | -0.027466 | -0.064087 | 0.01831 | 0.15106 | 0.12817 | -0.13275 | 0.15564 | -0.10529 | 0.37994 | 122.4976 | 0.17853 | 122.4838 | 122.5204 | 122.4014 | 122.4152 | 122.374 | -122.5433 | -122.4655 | 122.3923 | 122.4564 | 54.4144 | 51.947
1291.7656 | 122.7173 | -59.3948 | 63.0157 | -0.018234 | 0.00084388 | 0.060744 | 0.10672 | -0.0019653 | -0.0018586 | -0.0033112 | 0.027161 | -0.00091423 | 0.064179 | 0.051863 | -0.019741 | 0.0024823 | -0.0028839 | -5.2963 | 62.97 | -59.4406 | 63.0157 | -59.0286 | -59.5642 | -1.7075 | -7.5027 | 62.9288 | -59.436 | 63.0615 | -59.1614 | -59.4406 | -58.9874 | -0.045777 | -0.045776 | 0 | 0.36621 | 57.6874 | -0.16937 | 57.7332 | -0.1236 | -0.041199 | -0.086975 | 0.045776 | 0.23346 | 0.40741 | -0.045777 | 0.44861 | -0.004578 | 0.41199 | 122.4564 | 0.27466 | 122.4976 | 122.4106 | 122.3648 | 122.3648 | 122.3236 | -122.4564 | -122.4518 | 122.4106 | 122.4564 | 54.0985 | 51.8921
1292.7656 | 122.699 | -59.4269 | 62.9654 | -0.07164 | 0.0016983 | 0.059889 | 0.10437 | -0.00068368 | 6.4004e-05 | -0.0060882 | 0.033264 | -0.00091423 | 0.06482 | 0.056136 | -0.02145 | 0.0016277 | -0.0039521 | -5.1956 | 62.9059 | -59.5184 | 63.0066 | -59.0973 | -59.6054 | -1.7578 | -7.7271 | 62.8876 | -59.4635 | 63.0341 | -59.2209 | -59.4681 | -59.2575 | -0.091553 | -0.059509 | 0.041199 | 0.32959 | 57.6691 | -0.17853 | 57.7606 | -0.086975 | -0.036621 | -0.07782 | 0.068665 | 0.20599 | 0.16937 | -0.041199 | 0.20599 | -0.004578 | 0.42114 | 122.525 | 0.24262 | 122.4976 | 122.4243 | 122.3511 | 122.3328 | 122.3145 | -122.4838 | -122.4289 | 122.4335 | 122.4609 | 54.2313 | 51.6998
1293.7656 | 122.7173 | -59.5139 | 62.8647 | -0.079269 | -0.0036423 | 0.058607 | 0.10244 | -0.00025628 | -0.0012176 | -0.0037384 | 0.030212 | 0.0016492 | 0.064179 | 0.057418 | -0.019741 | 0.0026959 | -0.0013885 | -5.1682 | 62.8876 | -59.5688 | 62.8601 | -59.1248 | -59.7015 | -1.8036 | -7.3654 | 62.7777 | -59.5688 | 62.9471 | -59.3124 | -59.5596 | -59.3353 | -0.054932 | 0.022888 | -0.004578 | 0.3891 | 57.7103 | -0.18768 | 57.7652 | -0.13275 | -0.054932 | -0.086975 | 0.082398 | 0.20142 | 0.17853 | -0.045776 | 0.23346 | 0.009156 | 0.44403 | 122.4289 | 0.25635 | 122.5159 | 122.4564 | 122.3465 | 122.4014 | 122.2916 | -122.4335 | -122.4335 | 122.374 | 122.4609 | 54.3457 | 52.1484
1294.7656 | 122.7127 | -59.3903 | 63.0249 | -0.11742 | 0.0012711 | 0.060957 | 0.10437 | 0.0018799 | -0.0033538 | -0.0043792 | -0.1712 | 0.00015377 | 0.06247 | 0.057418 | -0.021236 | 0.0014141 | 0.0020295 | -5.1178 | 62.9333 | -59.4727 | 63.0615 | -59.1293 | -59.0332 | -1.1902 | -7.196 | 62.8922 | -59.4406 | 63.0707 | -59.1522 | -59.4131 | -59.198 | -0.082397 | -0.091552 | 0.036621 | 0.26093 | 58.2001 | 0.35706 | 58.2825 | 0.43945 | -0.050354 | -0.13275 | 0.045777 | 0.23804 | 0.19226 | -0.022888 | 0.24262 | 0.027466 | 0.34332 | 122.5342 | 0.28839 | 122.5113 | 122.406 | 122.3328 | 122.3236 | 122.2824 | -122.4976 | -122.4655 | 122.4518 | 122.4609 | 54.2725 | 52.1942
1295.7656 | 122.7768 | -59.4131 | 62.9562 | -0.048752 | 0.0021255 | 0.061598 | 0.10501 | 0.0020935 | -0.0031402 | -0.002243 | -0.0033568 | -0.00048703 | 0.063965 | 0.060195 | -0.020809 | -0.00029487 | -0.0077973 | -5.3925 | 62.9288 | -59.5093 | 63.0066 | -59.0607 | -59.6191 | -1.7258 | -7.402 | 62.8784 | -59.4772 | 63.3041 | -59.4589 | -59.7839 | -59.3903 | -0.09613 | -0.027466 | 0.050354 | 0.35248 | 57.6874 | -0.20599 | 57.7835 | -0.10986 | -0.064087 | -0.07782 | 0.3479 | -0.045776 | 0.022888 | -0.37079 | 0.086975 | -0.3067 | 0.44861 | 122.5159 | 0.018311 | 122.7814 | 122.438 | 122.3557 | 122.3419 | 122.2916 | -122.4655 | -122.4335 | 122.4197 | 122.7173 | 54.0207 | 52.0111
1296.7656 | 122.7081 | -59.436 | 62.9562 | 0.073319 | 0.00084388 | 0.064803 | 0.1065 | -0.00089728 | -0.0033538 | -0.0026704 | 0.0057984 | -0.00070063 | 0.063538 | 0.060622 | -0.020382 | 0.0020551 | -0.00032051 | -5.7541 | 62.8876 | -59.5642 | 62.9974 | -59.1156 | -59.6008 | -2.0004 | -7.338 | 62.8922 | -59.4818 | 63.0478 | -59.2163 | -59.4772 | -59.2529 | -0.12817 | -0.068665 | 0.041199 | 0.32043 | 57.4356 | -0.1648 | 57.5638 | -0.036621 | -0.045777 | -0.064087 | 0.091553 | 0.21973 | 0.1831 | -0.041199 | 0.22888 | 0.004578 | 0.44861 | 122.5616 | 0.2655 | 122.5296 | 122.4518 | 122.374 | 122.3236 | 122.3282 | -122.5204 | -122.4381 | 122.4335 | 122.4838 | 53.6819 | 52.0981
1297.7656 | 122.7036 | -59.4086 | 62.9608 | -0.07164 | -0.00043792 | 0.061812 | 0.10415 | -0.00068368 | -0.0012176 | 0.001175 | -0.039978 | -0.0013416 | 0.064179 | 0.059554 | -0.019955 | 0.00034613 | 0.0020295 | -5.3238 | 62.9379 | -59.5001 | 63.1256 | -58.6899 | -59.5367 | -2.211 | -7.338 | 62.9013 | -59.4635 | 63.0661 | -59.1888 | -59.4635 | -59.2484 | -0.091553 | -0.022888 | 0.1648 | 0.71869 | 57.1976 | -0.12817 | 57.2891 | -0.036621 | -0.054932 | -0.059509 | 0.10529 | 0.21973 | 0.16022 | -0.054932 | 0.21515 | 0 | 0.81024 | 122.6257 | 0.27466 | 122.5296 | 122.438 | 122.3648 | 122.3465 | 122.3099 | -122.4609 | -122.4243 | 122.5342 | 122.4747 | 54.0848 | 52.0706
1298.7656 | 122.7402 | -59.404 | 62.9745 | -0.094528 | 0.0014847 | 0.060744 | 0.10607 | 0.0016663 | -0.0035674 | -0.00032036 | 0.014954 | -0.00091423 | 0.06482 | 0.064253 | -0.028927 | -0.0032855 | 0.00032049 | -5.4428 | 62.9196 | -59.5047 | 63.0341 | -59.024 | -59.5825 | -2.1332 | -7.4753 | 62.915 | -59.4315 | 63.1714 | -59.491 | -59.5917 | -59.1934 | -0.10071 | -0.054931 | 0.05951 | 0.37994 | 57.2708 | -0.17853 | 57.3715 | -0.07782 | -0.027466 | -0.059509 | 0.19684 | -0.086975 | 0.21057 | -0.18768 | 0.23804 | -0.16022 | 0.48065 | 122.5388 | -0.059509 | 122.6028 | 122.4243 | 122.3465 | 122.3236 | 122.319 | -122.4792 | -122.406 | 122.4381 | 122.5754 | 53.9612 | 51.9287
1299.7656 | 122.7448 | -59.3536 | 63.0295 | -0.10979 | 0.0012711 | 0.059889 | 0.10607 | -0.00068368 | 0.0022004 | -0.0030976 | -0.0094604 | 0.00058097 | 0.064392 | 0.060408 | -0.020382 | -0.00029487 | 0.0037385 | -5.8823 | 62.9883 | -59.4131 | 63.0524 | -59.0149 | -59.5413 | -2.0737 | -7.6447 | 62.9425 | -59.3994 | 63.1348 | -59.1339 | -59.3719 | -59.1385 | -0.059509 | -0.041199 | 0.022888 | 0.33874 | 57.28 | -0.18768 | 57.3395 | -0.12817 | -0.045776 | -0.086975 | 0.10529 | 0.21973 | 0.21515 | -0.01831 | 0.26093 | 0.027466 | 0.39825 | 122.4655 | 0.2655 | 122.5342 | 122.4014 | 122.3419 | 122.3419 | 122.2961 | -122.4426 | -122.4289 | 122.406 | 122.4884 | 53.4714 | 51.709
1300.7656 | 122.7356 | -59.5047 | 62.8647 | -0.048752 | -0.0015061 | 0.061812 | 0.10543 | -0.00025628 | -0.0018586 | -0.0052338 | -0.012512 | -0.00048703 | 0.062897 | 0.060195 | -0.019741 | 0.0016277 | -0.0022431 | -5.7632 | 62.8418 | -59.6008 | 62.883 | -59.1843 | -59.7336 | -1.3321 | -7.5027 | 62.796 | -59.5734 | 62.9608 | -59.3033 | -59.5413 | -59.3353 | -0.09613 | -0.022888 | 0.018311 | 0.32043 | 58.1726 | -0.22888 | 58.2687 | -0.13275 | -0.068664 | -0.068664 | 0.09613 | 0.20142 | 0.16937 | -0.036621 | 0.23804 | 0.032043 | 0.41656 | 122.4838 | 0.27008 | 122.5342 | 122.4426 | 122.3694 | 122.3465 | 122.3007 | -122.4655 | -122.438 | 122.3877 | 122.4655 | 53.7415 | 52.002
1301.7656 | 122.6852 | -59.5596 | 62.8555 | -0.11742 | 0.0027665 | 0.060957 | 0.10372 | 0.00017092 | -0.0024994 | -0.00096136 | -0.036926 | -0.0024096 | 0.06482 | 0.061049 | -0.021023 | -8.1274e-05 | -0.0037383 | -5.8319 | 62.796 | -59.6741 | 62.7914 | -59.2941 | -59.8251 | -0.72784 | -7.196 | 62.7731 | -59.6375 | 62.8555 | -59.404 | -59.6603 | -59.4086 | -0.11444 | -0.059509 | -0.064087 | 0.2655 | 58.8318 | -0.2655 | 58.9462 | -0.15106 | -0.07782 | -0.082398 | 0 | 0.15564 | 0.15106 | -0.10071 | 0.22888 | -0.022888 | 0.37994 | 122.4655 | 0.23346 | 122.493 | 122.4701 | 122.4106 | 122.3557 | 122.3328 | -122.5296 | -122.493 | 122.3511 | 122.4152 | 53.7277 | 52.3636
1302.7656 | 122.731 | -59.5734 | 62.8189 | -0.1403 | -0.00043792 | 0.060744 | 0.10501 | -0.0028199 | -0.002713 | -0.0037384 | -0.015564 | 0.00015377 | 0.063324 | 0.055709 | -0.019741 | 0.00055973 | -0.00010671 | -5.3696 | 62.7777 | -59.6237 | 62.8555 | -59.2209 | -59.7565 | -1.6388 | -7.2006 | 62.7319 | -59.6237 | 62.9288 | -59.3216 | -59.5963 | -59.3719 | -0.050354 | -0.041199 | 0.036621 | 0.35248 | 57.9346 | -0.18311 | 57.9849 | -0.13275 | -0.050354 | -0.086975 | 0.10986 | 0.25177 | 0.20142 | -0.022888 | 0.25177 | 0.027466 | 0.40283 | 122.4792 | 0.30212 | 122.5525 | 122.4014 | 122.3557 | 122.3511 | 122.3053 | -122.4426 | -122.4426 | 122.4289 | 122.5021 | 54.2038 | 52.3727
1303.7656 | 122.7127 | -59.5688 | 62.7869 | -0.048752 | -0.00086512 | 0.060744 | 0.10693 | -0.0062379 | -0.0005768 | -0.0043792 | -0.0094604 | -0.00048703 | 0.060761 | 0.070876 | -0.020382 | -0.0017901 | -0.0041657 | -5.2963 | 62.7731 | -59.6649 | 62.8052 | -59.2575 | -59.7885 | -1.5472 | -7.3059 | 62.7274 | -59.6329 | 62.915 | -59.3445 | -59.5963 | -59.3719 | -0.09613 | -0.013733 | 0.018311 | 0.31128 | 58.0215 | -0.21973 | 58.1177 | -0.1236 | -0.064087 | -0.059509 | 0.12817 | 0.22431 | 0.19684 | -0.027465 | 0.26093 | 0.036622 | 0.40741 | 122.4701 | 0.28839 | 122.5479 | 122.438 | 122.3602 | 122.3419 | 122.2961 | -122.4518 | -122.4197 | 122.374 | 122.4838 | 54.2725 | 52.2629
1304.7656 | 122.731 | -59.5871 | 62.7777 | -0.07164 | 0.0010575 | 0.061812 | 0.10607 | 0.0012391 | -0.0035674 | -0.001175 | -0.0033568 | -0.0015552 | 0.06247 | 0.061263 | -0.022091 | 0.00077333 | 0.00053409 | -5.2963 | 62.7502 | -59.7061 | 62.7823 | -59.3079 | -59.8389 | -1.799 | -7.402 | 62.709 | -59.6558 | 62.8601 | -59.4086 | -59.6603 | -59.4269 | -0.11902 | -0.027466 | 0.004578 | 0.27924 | 57.7881 | -0.25177 | 57.9071 | -0.13275 | -0.068665 | -0.068665 | 0.082397 | 0.17853 | 0.16022 | -0.073242 | 0.22888 | -0.004577 | 0.39825 | 122.4884 | 0.24719 | 122.5159 | 122.4564 | 122.3648 | 122.3373 | 122.2961 | -122.4838 | -122.4335 | 122.3694 | 122.4472 | 54.2908 | 52.1851
1305.7656 | 122.6807 | -59.6237 | 62.7869 | -0.06401 | -0.00022432 | 0.061598 | 0.10565 | 0.0029479 | -0.0012176 | 0.00010684 | -0.018616 | -0.0015552 | 0.065033 | 0.066817 | -0.019955 | 0.0020551 | -0.0028839 | -5.3101 | 62.7457 | -59.7565 | 62.796 | -59.317 | -59.848 | -1.5839 | -7.6813 | 62.7411 | -59.642 | 62.8693 | -59.3765 | -59.6512 | -59.3994 | -0.13275 | -0.041198 | 0.009156 | 0.3067 | 58.0399 | -0.2243 | 58.1726 | -0.091552 | -0.018311 | -0.045776 | 0.082398 | 0.24719 | 0.2243 | -0.027466 | 0.24262 | -0.009155 | 0.43945 | 122.5525 | 0.2655 | 122.5113 | 122.5021 | 122.3831 | 122.3694 | 122.3648 | -122.5433 | -122.4289 | 122.4197 | 122.493 | 54.3137 | 51.9424
1306.7656 | 122.6349 | -60.9283 | 61.4182 | -0.14793 | 0.00041648 | 0.058821 | 0.10736 | 0.00059812 | -0.0042084 | -0.0024566 | -0.34821 | 0.77411 | 0.061402 | 0.068526 | -0.022091 | -0.0037129 | 0.78154 | -4.5273 | 61.4136 | -61.0703 | 61.409 | -60.6125 | -61.1572 | -1.0162 | -4.985 | 61.3083 | -60.8917 | 61.4365 | -60.5896 | -60.91 | 61.377 | -0.14191 | -0.004578 | -0.009155 | 0.31586 | 59.9121 | -0.22888 | 60.054 | -0.086976 | 0.036621 | -0.10986 | 0.01831 | 0.33875 | 122.3053 | 0.018311 | 122.2687 | -0.01831 | 0.45776 | 122.4792 | 0.30212 | 122.3282 | 122.4838 | 122.2 | 122.3419 | 122.2366 | -122.4884 | -122.3099 | 122.3373 | 122.3648 | 56.4011 | 55.9433
1307.7656 | 122.644 | -60.704 | 61.6013 | -0.079269 | 0.00020288 | 0.06053 | 0.10543 | -0.0023925 | -0.0016448 | -0.004593 | -0.33295 | 0.77133 | 0.063111 | 0.055922 | -0.023373 | -0.0041401 | 0.7794 | -4.5639 | 61.5372 | -60.8551 | 61.615 | -60.3745 | -60.9146 | -1.5289 | -4.9713 | 61.4319 | -60.6949 | 61.6196 | -60.379 | -60.7269 | 61.4594 | -0.15106 | -0.064087 | 0.013733 | 0.32959 | 59.1751 | -0.21057 | 59.3262 | -0.059509 | 0.009156 | -0.16937 | 0.018311 | 0.32501 | 122.1634 | -0.022888 | 122.1542 | -0.032044 | 0.48065 | 122.4701 | 0.31586 | 122.3145 | 122.3923 | 122.1268 | 122.2412 | 122.1359 | -122.4564 | -122.2961 | 122.319 | 122.3236 | 56.1401 | 55.7327
1308.7656 | 122.5754 | -60.7498 | 61.5555 | -0.14793 | 0.0010575 | 0.061171 | 0.10629 | 0.0010253 | -0.0024994 | -0.002243 | -0.35431 | 0.76685 | 0.060974 | 0.06639 | -0.022732 | -0.0017901 | 0.773 | -4.8248 | 61.4319 | -60.9146 | 61.496 | -60.4706 | -61.0382 | -1.8768 | -4.9576 | 61.3312 | -60.7773 | 61.5234 | -60.466 | -60.7681 | 61.1298 | -0.16479 | -0.1236 | -0.059509 | 0.27924 | 58.873 | -0.28839 | 59.0378 | -0.1236 | -0.027466 | -0.2243 | -0.032044 | 0.28381 | 121.8796 | -0.01831 | 121.907 | 0.009156 | 0.44403 | 122.4106 | 0.31128 | 122.3007 | 122.3465 | 122.1085 | 122.1817 | 122.081 | -122.4701 | -122.3328 | 122.2458 | 122.2733 | 55.925 | 55.7922
1309.7656 | 122.6486 | -60.6171 | 61.5875 | -0.079269 | 0.00020288 | 0.059248 | 0.10394 | -0.00068368 | 0.001773 | -0.0035248 | -0.19562 | 0.7536 | 0.062683 | 0.062545 | -0.02145 | -0.0045673 | 0.76787 | -4.7287 | 61.5555 | -60.8276 | 61.5417 | -60.3928 | -60.9329 | -1.0666 | -5.1956 | 61.4502 | -60.6903 | 61.5784 | -60.3882 | -60.6766 | 59.9945 | -0.21057 | -0.032043 | -0.045776 | 0.2243 | 59.5505 | -0.31586 | 59.761 | -0.10528 | -0.073243 | -0.13733 | -0.009155 | 0.22888 | 120.6116 | -0.05951 | 120.6848 | 0.013733 | 0.43488 | 122.3694 | 0.30212 | 122.2687 | 122.3831 | 122.1405 | 122.1725 | 122.0673 | -122.4152 | -122.2778 | 122.1588 | 122.1954 | 55.8884 | 55.4214
1310.7656 | 122.58 | -60.6949 | 61.5326 | -0.12505 | 0.00084388 | 0.058607 | 0.10458 | -0.00089728 | 0.0011322 | -0.003952 | -0.23529 | 0.74976 | 0.064392 | 0.05934 | -0.022304 | -0.0037129 | 0.76018 | -4.7791 | 61.4868 | -60.8826 | 61.4731 | -60.4385 | -60.997 | -1.5427 | -5.3009 | 61.3953 | -60.7315 | 61.4868 | -60.4614 | -60.759 | 59.9716 | -0.18768 | -0.045777 | -0.05951 | 0.25635 | 59.1522 | -0.30212 | 59.3399 | -0.11444 | -0.036621 | -0.13733 | -0.045777 | 0.23346 | 120.6665 | -0.064087 | 120.7031 | -0.027466 | 0.44403 | 122.3557 | 0.27008 | 122.2183 | 122.3694 | 122.1268 | 122.1817 | 122.0901 | -122.4152 | -122.2641 | 122.168 | 122.1817 | 55.9158 | 55.394
1311.7656 | 122.58 | -60.7178 | 61.5463 | -0.079269 | -0.00043792 | 0.060316 | 0.10415 | -0.00089728 | -0.0035674 | -0.0041656 | -0.25055 | 0.74677 | 0.064179 | 0.065108 | -0.022518 | -0.0024311 | 0.75932 | -4.5776 | 61.496 | -60.8276 | 61.4777 | -60.4523 | -60.9924 | -2.2797 | -5.3879 | 61.3953 | -60.704 | 61.496 | -60.466 | -60.7452 | 59.9579 | -0.10986 | -0.050354 | -0.068665 | 0.2655 | 58.4381 | -0.27466 | 58.548 | -0.16479 | 0.013732 | -0.15106 | -0.050354 | 0.25177 | 120.6757 | -0.027466 | 120.6619 | -0.041198 | 0.37537 | 122.3053 | 0.23804 | 122.2 | 122.3236 | 122.0993 | 122.2137 | 122.113 | -122.374 | -122.2504 | 122.1954 | 122.2137 | 56.1401 | 55.3299
1312.7656 | 122.5113 | -60.8093 | 61.4456 | -0.10979 | 0.00020288 | 0.061171 | 0.10522 | -0.0015381 | -0.0024994 | -0.0043792 | -0.23224 | 0.74869 | 0.064179 | 0.062545 | -0.021664 | -0.0030719 | 0.76125 | -4.834 | 61.4044 | -60.9192 | 61.5372 | -60.3516 | -61.2122 | -2.1149 | -5.4474 | 61.3083 | -60.8231 | 61.3815 | -60.5347 | -60.8368 | 60.4797 | -0.10986 | -0.041199 | 0.091552 | 0.45776 | 58.6945 | -0.40283 | 58.8043 | -0.29297 | -0.013733 | -0.13733 | -0.064087 | 0.27466 | 121.2891 | -0.027466 | 121.3028 | -0.013733 | 0.56763 | 122.4564 | 0.28839 | 122.2046 | 122.3236 | 122.1313 | 122.2137 | 122.1176 | -122.3648 | -122.2687 | 122.3465 | 122.1909 | 55.9753 | 55.3619
1313.7656 | 122.5113 | -60.7819 | 61.4502 | -0.13267 | 0.0016983 | 0.059676 | 0.1065 | -0.0032471 | -0.0007904 | -0.0016022 | -0.29327 | 0.73929 | 0.062042 | 0.059127 | -0.021877 | -0.0043537 | 0.75185 | -4.628 | 61.4182 | -60.9055 | 61.4044 | -60.4889 | -61.0062 | -1.4328 | -5.1498 | 61.3449 | -60.7681 | 61.3815 | -60.5347 | -60.7819 | 59.6283 | -0.1236 | -0.032043 | -0.045776 | 0.29297 | 59.3491 | -0.22431 | 59.4727 | -0.10071 | 0.013733 | -0.10529 | -0.068664 | 0.24719 | 120.4102 | 0 | 120.3964 | -0.013733 | 0.41656 | 122.3099 | 0.23346 | 122.1497 | 122.3236 | 122.113 | 122.2 | 122.1268 | -122.3557 | -122.2183 | 122.1863 | 122.1634 | 56.1539 | 55.632
1314.7656 | 122.4838 | -60.7315 | 61.496 | -0.12505 | 0.0016983 | 0.061812 | 0.10714 | -4.2682e-05 | 0.0002778 | -0.0016022 | -0.29938 | 0.74335 | 0.059906 | 0.053786 | -0.023373 | -0.0015765 | 0.75462 | -4.4952 | 61.4044 | -60.8551 | 61.4868 | -60.3973 | -60.9695 | -1.0849 | -5.0125 | 61.3403 | -60.704 | 61.4685 | -60.4523 | -60.7407 | 60.141 | -0.1236 | -0.091553 | -0.009156 | 0.33417 | 59.6466 | -0.23804 | 59.7702 | -0.11444 | 0.027465 | -0.15564 | -0.027466 | 0.27923 | 120.8725 | -0.009156 | 120.845 | -0.036621 | 0.45776 | 122.3419 | 0.25177 | 122.1725 | 122.2595 | 122.0444 | 122.1359 | 122.0718 | -122.3511 | -122.2 | 122.2183 | 122.2 | 56.2363 | 55.719
1315.7656 | 122.493 | -60.791 | 61.4227 | -0.094528 | 0.0016983 | 0.060316 | 0.10522 | -0.00046988 | -0.0022858 | -0.0020294 | -0.33295 | 0.73673 | 0.062897 | 0.058486 | -0.022091 | -0.0020039 | 0.74416 | -4.4586 | 61.377 | -60.9192 | 61.4136 | -60.4294 | -61.0153 | -1.5884 | -5.2322 | 61.2579 | -60.7636 | 61.3998 | -60.4889 | -60.8139 | 59.6191 | -0.12817 | -0.045776 | -0.009155 | 0.36163 | 59.2026 | -0.2243 | 59.3307 | -0.096131 | 0.027466 | -0.16479 | -0.022888 | 0.30212 | 120.4102 | -0.022888 | 120.3827 | -0.050354 | 0.48981 | 122.3328 | 0.27466 | 122.1634 | 122.2961 | 122.0215 | 122.168 | 122.049 | -122.3419 | -122.1863 | 122.2046 | 122.1909 | 56.3324 | 55.5588
1316.7656 | 122.4655 | -60.7407 | 61.4548 | -0.12505 | 0.0014847 | 0.058821 | 0.10607 | -0.0036743 | -0.0024994 | -0.002243 | -0.29327 | 0.73673 | 0.061829 | 0.056349 | -0.022518 | -0.0028583 | 0.74843 | -4.5593 | 61.4273 | -60.8551 | 61.3998 | -60.466 | -60.9787 | -2.4399 | -5.0995 | 61.322 | -60.7452 | 61.4227 | -60.4385 | -60.7544 | 60.1776 | -0.11444 | -0.027466 | -0.054932 | 0.27466 | 58.3008 | -0.23804 | 58.4152 | -0.1236 | -0.004577 | -0.13275 | -0.032044 | 0.30212 | 120.9183 | -0.013733 | 120.9229 | -0.009156 | 0.3891 | 122.2549 | 0.3067 | 122.168 | 122.2824 | 122.0673 | 122.168 | 122.0627 | -122.3099 | -122.2 | 122.1405 | 122.1634 | 56.1813 | 55.6412
1317.7656 | 122.4838 | -60.6857 | 61.5097 | -0.11742 | -0.0010787 | 0.060744 | 0.10543 | -0.00046988 | -0.0001496 | -0.0016022 | -0.31158 | 0.73117 | 0.063751 | 0.053359 | -0.0238 | -0.0020039 | 0.74266 | -4.9072 | 61.4731 | -60.8276 | 61.4273 | -60.379 | -60.9879 | -2.4261 | -5.2643 | 61.3495 | -60.7315 | 61.4548 | -60.4111 | -60.7224 | 59.7702 | -0.14191 | -0.036622 | -0.082398 | 0.3067 | 58.2596 | -0.30212 | 58.4015 | -0.16022 | -0.045776 | -0.16022 | -0.054932 | 0.27466 | 120.4559 | -0.036621 | 120.5017 | 0.009155 | 0.44861 | 122.2549 | 0.32043 | 122.1863 | 122.3007 | 122.081 | 122.1588 | 122.0352 | -122.3373 | -122.2412 | 122.113 | 122.1405 | 55.7785 | 55.4214
1318.7656 | 122.4609 | -60.6628 | 61.5326 | -0.12505 | -0.00086512 | 0.059676 | 0.10672 | -0.0028199 | -0.0048492 | -0.001175 | -0.31158 | 0.72946 | 0.061615 | 0.057631 | -0.024227 | -0.0032855 | 0.73775 | -5.0125 | 61.4548 | -60.8047 | 61.6104 | -60.5255 | -60.9467 | -2.6505 | -5.2643 | 61.3998 | -60.6537 | 61.496 | -60.3882 | -60.6812 | 59.7565 | -0.14191 | -0.07782 | 0.07782 | 0.13733 | 58.0124 | -0.28381 | 58.1543 | -0.14191 | 0.009155 | -0.13275 | -0.036621 | 0.27466 | 120.4193 | -0.01831 | 120.4102 | -0.027465 | 0.27924 | 122.4152 | 0.2655 | 122.1497 | 122.2595 | 122.0535 | 122.1176 | 122.0627 | -122.3373 | -122.1863 | 122.2733 | 122.1588 | 55.6503 | 55.3986
1319.7656 | 122.438 | -60.7086 | 61.5051 | -0.10216 | 0.0014847 | 0.060103 | 0.108 | -0.00025628 | -0.0012176 | 0.00096124 | -0.52826 | 0.71643 | 0.061829 | 0.07408 | -0.021023 | -0.00093567 | 0.7401 | -4.9026 | 61.4685 | -60.8826 | 61.441 | -60.4065 | -60.9558 | -1.2726 | -5.3375 | 61.3907 | -60.7086 | 61.5097 | -60.3973 | -60.7727 | 60.2005 | -0.17395 | -0.036621 | -0.064087 | 0.30212 | 59.436 | -0.24719 | 59.61 | -0.073243 | 0 | -0.11444 | 0.004578 | 0.31128 | 120.9091 | -0.064087 | 120.9091 | -0.064087 | 0.47607 | 122.3236 | 0.31128 | 122.2183 | 122.3511 | 122.0993 | 122.1771 | 122.0993 | -122.3877 | -122.2137 | 122.1497 | 122.2183 | 55.806 | 55.3711
1320.8281 | 122.5021 | -60.6262 | 61.4914 | -0.086899 | -1.0718e-05 | 0.061385 | 0.10736 | 0.00059812 | -0.0016448 | -0.00074776 | -0.3421 | 0.72797 | 0.06012 | 0.059554 | -0.024654 | -0.00050847 | 0.73882 | -5.1498 | 61.441 | -60.8047 | 61.6837 | -60.3012 | -60.965 | -1.4786 | -5.2231 | 61.377 | -60.64 | 61.5463 | -60.3058 | -60.6491 | 60.4385 | -0.17853 | -0.050354 | 0.19226 | 0.32501 | 59.1476 | -0.33874 | 59.3262 | -0.16022 | -0.013733 | -0.11444 | 0.054932 | 0.32044 | 121.0648 | -0.022888 | 121.0785 | -0.009155 | 0.50354 | 122.4884 | 0.33417 | 122.1863 | 122.2458 | 122.0169 | 122.0673 | 122.0032 | -122.2961 | -122.1313 | 122.3099 | 122.1725 | 55.4764 | 55.4031
1321.7656 | 122.5021 | -60.6949 | 61.4548 | -0.07164 | -0.0012923 | 0.05818 | 0.10415 | -0.0015381 | -0.0016448 | -0.0018158 | -0.29022 | 0.72369 | 0.063751 | 0.058699 | -0.022732 | -0.0015765 | 0.73006 | -4.6921 | 61.4319 | -60.8139 | 61.4914 | -60.3241 | -60.8917 | -0.9613 | -4.8523 | 61.3174 | -60.6949 | 61.4731 | -60.3424 | -60.5667 | 60.2142 | -0.11902 | -0.022888 | 0.036621 | 0.37079 | 59.7336 | -0.19684 | 59.8526 | -0.07782 | 0 | -0.13733 | 0.01831 | 0.35248 | 120.9091 | 0.12817 | 120.9091 | 0.12817 | 0.48981 | 122.3053 | 0.35248 | 122.168 | 122.2458 | 122.0123 | 122.1268 | 122.0123 | -122.2687 | -122.1497 | 122.1863 | 122.168 | 56.0028 | 55.8426
1322.7656 | 122.4426 | -60.6216 | 61.5509 | -0.12505 | 0.0027665 | 0.06053 | 0.10543 | 0.00038452 | 0.0009186 | -0.0013886 | -0.31158 | 0.72177 | 0.063324 | 0.063185 | -0.020595 | -0.0039265 | 0.73155 | -4.3396 | 61.5097 | -60.7269 | 61.6608 | -60.1547 | -61.0519 | -0.97961 | -4.9759 | 61.4136 | -60.6125 | 61.528 | -60.3149 | -60.6537 | 59.9899 | -0.10529 | -0.041198 | 0.10986 | 0.46692 | 59.642 | -0.4303 | 59.7473 | -0.32501 | 0.009155 | -0.13733 | -0.022888 | 0.3067 | 120.6116 | -0.032044 | 120.6024 | -0.041199 | 0.5722 | 122.3877 | 0.29755 | 122.1405 | 122.2366 | 122.0261 | 122.1313 | 122.0352 | -122.2778 | -122.1634 | 122.2824 | 122.1497 | 56.282 | 55.6458
1323.7656 | 122.4747 | -60.6354 | 61.5189 | -0.06401 | 0.00063028 | 0.061171 | 0.10672 | -0.0013245 | -0.0016448 | -0.0020294 | -0.31464 | 0.71985 | 0.059479 | 0.058699 | -0.02145 | -0.0020039 | 0.73283 | -3.8635 | 61.4639 | -60.7773 | 61.5051 | -60.3424 | -60.878 | -0.65918 | -4.4174 | 61.3724 | -60.6262 | 61.5326 | -60.3241 | -60.6216 | 59.9487 | -0.14191 | -0.054932 | -0.013733 | 0.29297 | 59.9762 | -0.24262 | 60.1181 | -0.10071 | 0.009155 | -0.14648 | 0.013733 | 0.31128 | 120.5841 | 0.013733 | 120.575 | 0.004578 | 0.43488 | 122.2824 | 0.30212 | 122.1588 | 122.2412 | 121.9986 | 122.0993 | 122.0078 | -122.2961 | -122.1451 | 122.1405 | 122.168 | 56.7719 | 56.218
1324.7656 | 122.4838 | -60.6628 | 61.4914 | -0.10979 | 0.0012711 | 0.061385 | 0.10437 | -0.0032471 | -0.0012176 | -0.003952 | -0.31158 | 0.71814 | 0.063965 | 0.056563 | -0.02145 | -0.0024311 | 0.72771 | -2.9388 | 61.4639 | -60.8276 | 61.4548 | -60.3653 | -60.8871 | -0.60425 | -4.5227 | 61.3403 | -60.6583 | 61.4822 | -60.3516 | -60.6583 | 60.1044 | -0.1648 | -0.027466 | -0.036621 | 0.29755 | 60.0586 | -0.2243 | 60.2234 | -0.059509 | 0.004578 | -0.15106 | -0.009155 | 0.31128 | 120.7672 | 0.004578 | 120.7626 | 0 | 0.46234 | 122.2824 | 0.3067 | 122.1405 | 122.2916 | 121.9986 | 122.1268 | 122.0032 | -122.319 | -122.1497 | 122.1176 | 122.1451 | 57.724 | 56.1401
1325.7656 | 122.4701 | -60.6491 | 61.4868 | -0.048752 | 0.0025529 | 0.059676 | 0.10714 | -4.2682e-05 | -0.0016448 | -0.0041656 | -0.3299 | 0.71451 | 0.062042 | 0.057204 | -0.025082 | -0.0028583 | 0.72621 | -3.4836 | 61.4502 | -60.8093 | 61.4868 | -60.3241 | -60.8688 | -0.24261 | -4.3991 | 61.3541 | -60.6308 | 61.4914 | -60.3333 | -60.6445 | 59.967 | -0.16022 | -0.036621 | 0 | 0.32501 | 60.4065 | -0.21973 | 60.5667 | -0.059509 | 0.018311 | -0.13275 | 0.004578 | 0.31586 | 120.6162 | 0.004578 | 120.5978 | -0.013733 | 0.48523 | 122.2961 | 0.29755 | 122.1222 | 122.2595 | 121.9849 | 122.0993 | 122.0032 | -122.2961 | -122.1176 | 122.1359 | 122.1405 | 57.1655 | 56.25
1326.7656 | 122.4472 | -60.672 | 61.4685 | -0.094528 | 0.0012711 | 0.059889 | 0.10415 | -0.0019653 | -0.0014312 | -0.0030976 | -0.3299 | 0.71344 | 0.061615 | 0.064467 | -0.023159 | -8.1274e-05 | 0.72322 | -3.1586 | 61.4319 | -60.8139 | 61.4777 | -60.3378 | -60.8826 | -0.21973 | -4.3121 | 61.3266 | -60.6583 | 61.4731 | -60.3287 | -60.6537 | 60.141 | -0.14191 | -0.036621 | 0.009155 | 0.33417 | 60.4523 | -0.21057 | 60.5942 | -0.068664 | 0.013733 | -0.14191 | 0.004577 | 0.34332 | 120.813 | 0.01831 | 120.7993 | 0.004577 | 0.47607 | 122.2916 | 0.32959 | 122.1313 | 122.2458 | 121.9849 | 122.1039 | 121.9986 | -122.2824 | -122.1268 | 122.1497 | 122.1451 | 57.5134 | 56.3599
1327.7656 | 122.4518 | -60.6125 | 61.5555 | -0.086899 | 0.00063028 | 0.061598 | 0.10629 | -0.00025628 | -0.0012176 | -0.00032036 | -0.32684 | 0.7113 | 0.063965 | 0.05699 | -0.020595 | -0.0032855 | 0.72408 | -3.6301 | 61.496 | -60.7315 | 61.5372 | -60.2692 | -60.8185 | -0.92926 | -4.7195 | 61.3998 | -60.5896 | 61.5463 | -60.2783 | -60.5759 | 60.1456 | -0.11902 | -0.059509 | -0.018311 | 0.34332 | 59.6832 | -0.20599 | 59.8022 | -0.086975 | 0.022888 | -0.15564 | -0.009155 | 0.33417 | 120.7581 | 0.036621 | 120.7352 | 0.013733 | 0.46234 | 122.2687 | 0.31128 | 122.1359 | 122.2275 | 121.9894 | 122.1085 | 122.0123 | -122.287 | -122.1451 | 122.1497 | 122.1588 | 56.9824 | 55.8929
1328.7656 | 122.3923 | -60.6262 | 61.5326 | 0.042801 | 0.00041648 | 0.060957 | 0.10629 | -0.0034607 | -0.0020722 | -0.002884 | -0.3421 | 0.71088 | 0.061188 | 0.059767 | -0.023159 | -0.0015765 | 0.72002 | -4.1611 | 61.4777 | -60.7956 | 61.4594 | -60.3378 | -60.8734 | -1.0345 | -5.0262 | 61.3861 | -60.6125 | 61.5005 | -60.347 | -60.6628 | 60.0723 | -0.16937 | -0.054932 | -0.073242 | 0.28839 | 59.5917 | -0.24719 | 59.761 | -0.07782 | 0.013733 | -0.14648 | -0.032044 | 0.27924 | 120.6985 | -0.036621 | 120.6848 | -0.050354 | 0.45776 | 122.2549 | 0.2655 | 122.113 | 122.2733 | 121.9986 | 122.1039 | 122.0123 | -122.3282 | -122.1451 | 122.0856 | 122.1268 | 56.4651 | 55.6
1329.7656 | 122.4243 | -60.7178 | 61.3998 | -0.079269 | 0.0014847 | 0.060316 | 0.10607 | -0.0011109 | 0.0004914 | -0.004593 | -0.336 | 0.70361 | 0.062256 | 0.061904 | -0.022091 | -0.0041401 | 0.71638 | -3.1769 | 61.3495 | -60.8459 | 61.4822 | -60.2783 | -60.8459 | -0.737 | -4.3808 | 61.29 | -60.6766 | 61.5967 | -60.0632 | -61.0062 | 59.0744 | -0.12817 | -0.050354 | 0.082398 | 0.43945 | 59.9808 | -0.12817 | 60.1089 | 0 | 0.041198 | -0.10986 | 0.19684 | 0.6546 | 119.7922 | -0.28839 | 119.751 | -0.32959 | 0.56763 | 122.3282 | 0.6134 | 122.2733 | 122.1954 | 121.9666 | 122.0673 | 122.0078 | -122.2458 | -122.0764 | 122.2 | 122.3145 | 57.5409 | 56.337
1330.7656 | 122.4472 | -60.6216 | 61.4639 | -0.056381 | -0.00043792 | 0.062666 | 0.10586 | 0.0010253 | -0.0037812 | -0.00074776 | -0.31158 | 0.70596 | 0.063324 | 0.058699 | -0.026577 | -0.0011493 | 0.7151 | -3.3188 | 61.441 | -60.7727 | 61.5234 | -60.2097 | -60.7864 | -0.54016 | -4.0924 | 61.3449 | -60.6354 | 61.4044 | -60.5026 | -60.5347 | 60.0403 | -0.15106 | -0.022888 | 0.059509 | 0.41199 | 60.0815 | -0.16479 | 60.2325 | -0.013733 | -0.013733 | -0.11902 | -0.059509 | 0.11902 | 120.6619 | 0.086975 | 120.6757 | 0.10071 | 0.56305 | 122.2961 | 0.13275 | 122.0398 | 122.2137 | 121.9803 | 122.0627 | 121.9666 | -122.2366 | -122.0993 | 122.1451 | 122.0261 | 57.3029 | 56.5292
1331.7656 | 122.4564 | -60.5942 | 61.5509 | -0.10216 | 0.0012711 | 0.060316 | 0.10736 | -0.00046988 | 0.0013458 | -0.0037384 | -0.33905 | 0.70319 | 0.06247 | 0.067244 | -0.020809 | -0.0020039 | 0.71425 | -3.1769 | 61.5051 | -60.704 | 61.6104 | -60.1501 | -60.7224 | -0.75531 | -4.1565 | 61.3998 | -60.5576 | 61.615 | -60.2463 | -60.5942 | 59.8022 | -0.10986 | -0.045776 | 0.05951 | 0.44403 | 59.8389 | -0.12817 | 59.9487 | -0.01831 | 0.036621 | -0.15106 | 0.064087 | 0.3479 | 120.3964 | 0 | 120.3598 | -0.036621 | 0.55389 | 122.3145 | 0.31128 | 122.1725 | 122.2092 | 121.9574 | 122.0993 | 121.994 | -122.2549 | -122.1085 | 122.2046 | 122.2092 | 57.4173 | 56.4377
1332.7656 | 122.4426 | -60.5942 | 61.5051 | -0.13267 | -0.0010787 | 0.061598 | 0.10501 | 0.00059812 | -0.002713 | -0.0020294 | -0.09491 | 0.70148 | 0.065033 | 0.059767 | -0.02145 | 0.00013253 | 0.71361 | -3.9047 | 61.4685 | -60.7361 | 61.5784 | -60.1776 | -60.7407 | -0.88806 | -4.0924 | 61.4227 | -60.5988 | 61.5326 | -60.2463 | -60.6033 | 60.1089 | -0.14191 | -0.036621 | 0.073242 | 0.41656 | 59.7061 | -0.14648 | 59.848 | -0.004578 | -0.004578 | -0.082398 | 0.027466 | 0.3479 | 120.7031 | -0.009156 | 120.7077 | -0.004578 | 0.55847 | 122.3145 | 0.35248 | 122.1313 | 122.2046 | 122.0215 | 122.0627 | 122.0169 | -122.2412 | -122.1039 | 122.1725 | 122.1268 | 56.6895 | 56.5018
1333.8125 | 122.3236 | -60.6766 | 61.5234 | -0.056381 | 0.0023391 | 0.058821 | 0.10394 | 0.00038452 | -0.0012176 | -0.0026704 | -0.35431 | 0.70169 | 0.062256 | 0.060622 | -0.022091 | -0.00093567 | 0.71062 | -2.9251 | 61.4731 | -60.8047 | 61.4639 | -60.3424 | -60.8871 | -0.59967 | -3.9688 | 61.3953 | -60.6583 | 61.377 | -60.4156 | -60.7315 | 60.1868 | -0.12817 | -0.050354 | -0.059509 | 0.33417 | 60.0769 | -0.21057 | 60.2051 | -0.082397 | 0.018311 | -0.12817 | -0.14648 | 0.26093 | 120.8633 | -0.054931 | 120.845 | -0.073242 | 0.46234 | 122.2687 | 0.24262 | 122.0352 | 122.2778 | 122.0535 | 122.1497 | 122.0718 | -122.3282 | -122.1817 | 122.1405 | 122.0535 | 57.7515 | 56.7078
1334.7656 | 122.3602 | -60.791 | 61.4273 | -0.07164 | 0.0029801 | 0.061812 | 0.10607 | 0.0025207 | -0.0005768 | -0.0018158 | -0.35736 | 0.69891 | 0.062897 | 0.053572 | -0.024013 | -0.0013629 | 0.7119 | -3.5294 | 61.3998 | -60.8597 | 61.3815 | -60.3882 | -60.9604 | -0.54932 | -4.248 | 61.3129 | -60.7224 | 61.3129 | -60.498 | -60.8231 | 60.2005 | -0.068664 | -0.027466 | -0.045776 | 0.40283 | 60.2417 | -0.16937 | 60.3104 | -0.10071 | 0.068665 | -0.11444 | -0.11444 | 0.29297 | 120.9915 | -0.032043 | 120.9229 | -0.10071 | 0.4715 | 122.2412 | 0.2243 | 122.0352 | 122.2595 | 122.0352 | 122.1909 | 122.1039 | -122.287 | -122.1497 | 122.1725 | 122.1039 | 57.2617 | 56.543
1335.7656 | 122.4472 | -60.5713 | 61.5326 | -0.094528 | 0.0027665 | 0.060744 | 0.10458 | 0.0018799 | -0.0018586 | -0.0016022 | -0.30243 | 0.69849 | 0.063751 | 0.05934 | -0.0238 | -0.0026447 | 0.71083 | -2.8473 | 61.4914 | -60.7132 | 61.5738 | -60.1959 | -60.7361 | -0.29755 | -4.1794 | 61.3907 | -60.5759 | 61.5967 | -60.2097 | -60.5164 | 60.0815 | -0.14191 | -0.041199 | 0.041199 | 0.37537 | 60.2737 | -0.16479 | 60.4157 | -0.022888 | -0.004578 | -0.14191 | 0.064087 | 0.36163 | 120.6528 | 0.054932 | 120.6573 | 0.05951 | 0.51727 | 122.287 | 0.36621 | 122.1725 | 122.2046 | 121.9666 | 122.0627 | 121.962 | -122.2458 | -122.1085 | 122.1451 | 122.168 | 57.724 | 56.3919
1336.8281 | 122.4197 | -60.6537 | 61.4594 | -0.10216 | 0.0012711 | 0.059889 | 0.10479 | -0.0017517 | -0.0020722 | 0.00010684 | -0.32074 | 0.69251 | 0.061615 | 0.058913 | -0.023159 | -0.0015765 | 0.70357 | -3.1769 | 61.3861 | -60.8002 | 61.496 | -60.2325 | -60.8093 | 0.068665 | -4.0375 | 61.3037 | -60.6674 | 61.4685 | -60.3241 | -60.64 | 59.729 | -0.14648 | -0.073243 | 0.036621 | 0.42114 | 60.7224 | -0.15564 | 60.8688 | -0.009155 | -0.013732 | -0.15564 | 0.009155 | 0.32959 | 120.3827 | 0.013733 | 120.3964 | 0.027465 | 0.56763 | 122.2961 | 0.34332 | 122.1359 | 122.1863 | 121.9711 | 122.0398 | 121.9574 | -122.2595 | -122.1268 | 122.1497 | 122.1222 | 57.4768 | 56.6162
1337.7656 | 122.374 | -60.6628 | 61.4914 | -0.094528 | -0.00043792 | 0.060103 | 0.10672 | 0.0018799 | -0.0007904 | -0.004593 | -0.3421 | 0.69037 | 0.063751 | 0.065535 | -0.024441 | -0.0030719 | 0.70015 | -2.3071 | 61.3953 | -60.7956 | 61.4822 | -60.2829 | -60.8139 | 0.21973 | -4.0466 | 61.322 | -60.6079 | 61.4502 | -60.347 | -60.6537 | 59.3719 | -0.13275 | -0.09613 | -0.009155 | 0.37994 | 60.8826 | -0.15106 | 61.0153 | -0.018311 | 0.054932 | -0.16937 | -0.041199 | 0.31586 | 120.0348 | 0.009155 | 119.9799 | -0.045777 | 0.51269 | 122.2778 | 0.26093 | 122.0581 | 122.1909 | 121.9299 | 122.0581 | 121.9849 | -122.287 | -122.0993 | 122.1451 | 122.113 | 58.3557 | 56.6162
1338.7656 | 122.4014 | -60.6628 | 61.4868 | -0.12505 | 0.00063028 | 0.06053 | 0.10693 | 0.00038452 | -0.0005768 | -0.0048066 | -0.3299 | 0.68994 | 0.063324 | 0.065962 | -0.022945 | -0.0043537 | 0.69951 | -2.7649 | 61.4548 | -60.8002 | 61.496 | -60.26 | -60.8093 | 0.16479 | -4.3808 | 61.3586 | -60.6308 | 61.4685 | -60.3424 | -60.6537 | 59.7519 | -0.13733 | -0.032043 | 0.009156 | 0.40283 | 60.8276 | -0.14648 | 60.965 | -0.009155 | 0.032044 | -0.12817 | -0.01831 | 0.32043 | 120.4147 | 0.009155 | 120.3827 | -0.022889 | 0.54016 | 122.2961 | 0.28839 | 122.0993 | 122.2549 | 121.9894 | 122.1176 | 122.0215 | -122.287 | -122.1176 | 122.1588 | 122.1313 | 57.8979 | 56.282
1339.7656 | 122.3602 | -60.6537 | 61.5143 | -0.10979 | -0.0012923 | 0.062453 | 0.10757 | 0.0055115 | -0.0016448 | -0.0035248 | -0.41534 | 0.68866 | 0.062683 | 0.067244 | -0.023586 | -0.00072207 | 0.69737 | -2.4811 | 61.4639 | -60.8276 | 61.4502 | -60.3378 | -60.9055 | -0.16479 | -4.5547 | 61.3495 | -60.6812 | 61.4777 | -60.3699 | -60.7086 | 59.2484 | -0.17395 | -0.050354 | -0.064087 | 0.31586 | 60.4889 | -0.25177 | 60.6628 | -0.07782 | -0.027465 | -0.16479 | -0.036621 | 0.28381 | 119.902 | -0.054931 | 119.9295 | -0.027466 | 0.48981 | 122.2778 | 0.31128 | 122.1588 | 122.2916 | 122.0306 | 122.1176 | 122.0032 | -122.3419 | -122.1954 | 122.1039 | 122.1313 | 58.1726 | 56.0989
1340.7656 | 122.374 | -60.6583 | 61.4868 | -0.048752 | 0.0038345 | 0.060957 | 0.10415 | 0.0020935 | -0.0016448 | -0.0013886 | -0.29327 | 0.6861 | 0.064392 | 0.06169 | -0.021236 | -0.0024311 | 0.6978 | -2.7191 | 61.4182 | -60.791 | 61.4685 | -60.3058 | -60.8551 | 0.32044 | -4.0924 | 61.3266 | -60.672 | 61.4456 | -60.3424 | -60.6857 | 59.3994 | -0.13275 | -0.068664 | -0.01831 | 0.35248 | 60.9787 | -0.19684 | 61.1115 | -0.064087 | -0.013733 | -0.16022 | -0.041198 | 0.31586 | 120.0577 | -0.027466 | 120.0714 | -0.013733 | 0.48523 | 122.2595 | 0.32959 | 122.1176 | 122.2092 | 121.9986 | 122.0764 | 121.9849 | -122.2778 | -122.1588 | 122.1268 | 122.1039 | 57.9391 | 56.5659
1341.7656 | 122.3053 | -60.6812 | 61.4822 | -0.11742 | 0.0019119 | 0.060957 | 0.108 | 0.00017092 | -0.0029266 | -0.0050202 | -0.336 | 0.68353 | 0.063751 | 0.06169 | -0.023586 | -0.0017901 | 0.69353 | -2.829 | 61.4685 | -60.8414 | 61.3495 | -60.379 | -60.9055 | 0.19226 | -4.2572 | 61.377 | -60.6857 | 61.3861 | -60.2005 | -60.9329 | 59.198 | -0.16022 | -0.013733 | -0.13275 | 0.30212 | 60.8734 | -0.22431 | 61.0336 | -0.064087 | -0.004578 | -0.10529 | -0.096131 | 0.48065 | 119.8791 | -0.25177 | 119.8837 | -0.24719 | 0.46234 | 122.1909 | 0.48523 | 122.0718 | 122.3099 | 122.0627 | 122.1497 | 122.0581 | -122.3236 | -122.168 | 122.0306 | 122.0673 | 57.8522 | 56.4239
1342.7656 | 122.4243 | -60.6903 | 61.3907 | 0.019913 | 0.0016983 | 0.061171 | 0.10693 | -0.00046988 | -0.0012176 | -0.0030976 | -0.27191 | 0.68268 | 0.062897 | 0.052504 | -0.021664 | -0.0024311 | 0.68947 | -2.5406 | 61.3358 | -60.8551 | 61.4365 | -60.3287 | -60.8414 | 0.95215 | -4.0054 | 61.2762 | -60.6949 | 61.4365 | -60.3607 | -60.6537 | 59.1705 | -0.16479 | -0.054932 | 0.045776 | 0.36163 | 61.6425 | -0.15106 | 61.8073 | 0.013733 | -0.004577 | -0.11444 | 0.045776 | 0.32959 | 119.8608 | 0.036621 | 119.8654 | 0.041198 | 0.52643 | 122.2916 | 0.33417 | 122.1313 | 122.1909 | 121.9711 | 122.0261 | 121.9666 | -122.2458 | -122.0856 | 122.1268 | 122.1268 | 58.1497 | 56.6849
1343.7656 | 122.3831 | -60.7636 | 61.3632 | -0.094528 | 0.0027665 | 0.060957 | 0.1065 | 0.0031617 | -0.001004 | -0.001175 | -0.31464 | 0.68054 | 0.06482 | 0.060195 | -0.022732 | -0.0039265 | 0.6884 | -2.623 | 61.2762 | -60.9329 | 61.3541 | -60.4248 | -60.9375 | 0.88348 | -3.9963 | 61.203 | -60.7636 | 61.322 | -60.4614 | -60.7819 | 59.0744 | -0.16937 | -0.086975 | -0.009155 | 0.33875 | 61.647 | -0.17395 | 61.8164 | -0.004578 | 0 | -0.16022 | -0.041199 | 0.30212 | 119.838 | -0.01831 | 119.838 | -0.01831 | 0.50812 | 122.287 | 0.30212 | 122.0856 | 122.2092 | 121.9666 | 122.0398 | 121.9666 | -122.2961 | -122.1268 | 122.1176 | 122.0856 | 58.1406 | 56.7673
1344.7656 | 122.3373 | -60.8322 | 61.3312 | -0.12505 | 0.0016983 | 0.059035 | 0.10821 | -0.0021789 | 6.4004e-05 | -0.0013886 | -0.4184 | 0.67948 | 0.063111 | 0.061904 | -0.023586 | 0.00034613 | 0.68755 | -2.3987 | 61.3037 | -60.9833 | 61.2213 | -60.585 | -61.116 | 0.8194 | -4.0329 | 61.235 | -60.8139 | 61.2442 | -60.6079 | -60.9329 | 59.0286 | -0.15106 | -0.027466 | -0.10986 | 0.24719 | 61.6516 | -0.28381 | 61.8027 | -0.13275 | 0.01831 | -0.096131 | -0.086975 | 0.2243 | 119.8608 | -0.10071 | 119.8425 | -0.11902 | 0.39825 | 122.2046 | 0.20599 | 122.0581 | 122.287 | 122.0489 | 122.1359 | 122.0673 | -122.3145 | -122.1451 | 122.0535 | 122.0764 | 58.4335 | 56.7993
1345.7656 | 122.3053 | -60.7407 | 61.4365 | -0.07164 | 0.00020288 | 0.057112 | 0.10586 | 0.0025207 | -0.0020722 | -0.002243 | -0.33905 | 0.68161 | 0.063324 | 0.065322 | -0.021236 | -0.0024311 | 0.69438 | -2.1744 | 61.4502 | -60.8459 | 61.2762 | -60.4568 | -60.9787 | 0.8194 | -3.891 | 61.2991 | -60.7315 | 61.3312 | -60.4889 | -60.8002 | 59.61 | -0.10529 | 0.013733 | -0.16022 | 0.28381 | 61.5601 | -0.23804 | 61.6653 | -0.13275 | 0.009156 | -0.13733 | -0.10529 | 0.25177 | 120.3506 | -0.059509 | 120.3415 | -0.068665 | 0.3891 | 122.1222 | 0.24261 | 122.0627 | 122.2961 | 122.0306 | 122.1909 | 122.0398 | -122.2824 | -122.168 | 122.0169 | 122.0718 | 58.5663 | 56.8497
1346.7656 | 122.2916 | -60.7544 | 61.3998 | -0.0029755 | 0.0010575 | 0.062239 | 0.10565 | -0.00025628 | -0.0031402 | -0.0030976 | -0.32074 | 0.67862 | 0.063965 | 0.062972 | -0.019527 | -0.0015765 | 0.69054 | -2.2751 | 61.3495 | -60.9329 | 61.2946 | -60.4568 | -61.0657 | 0.56763 | -4.1336 | 61.2488 | -60.7864 | 61.2671 | -60.5438 | -60.8643 | 59.6283 | -0.17853 | -0.050354 | -0.10529 | 0.29755 | 61.322 | -0.31128 | 61.5005 | -0.13275 | -0.032043 | -0.15106 | -0.13275 | 0.21057 | 120.3827 | -0.10986 | 120.4147 | -0.07782 | 0.47607 | 122.2275 | 0.24261 | 122.0535 | 122.2824 | 122.0352 | 122.1039 | 122.0032 | -122.3328 | -122.1863 | 122.049 | 122.0215 | 58.4793 | 56.6208
1347.7656 | 122.3282 | -60.704 | 61.4502 | -0.0029755 | 0.0023391 | 0.060957 | 0.10607 | -0.0011109 | -0.0039948 | -0.002243 | -0.3299 | 0.67606 | 0.063538 | 0.059127 | -0.021664 | -0.0026447 | 0.68776 | -2.1332 | 61.4227 | -60.8597 | 61.3266 | -60.4294 | -60.9695 | 0.62256 | -4.1931 | 61.3037 | -60.6995 | 61.3312 | -60.4523 | -60.7956 | 59.5459 | -0.15564 | -0.027466 | -0.1236 | 0.27466 | 61.3266 | -0.2655 | 61.4822 | -0.10986 | 0.004578 | -0.14648 | -0.11902 | 0.25177 | 120.2499 | -0.091552 | 120.2454 | -0.09613 | 0.4303 | 122.1863 | 0.24719 | 122.0306 | 122.2824 | 122.0032 | 122.1268 | 122.0078 | -122.3099 | -122.1497 | 122.0306 | 122.0352 | 58.5709 | 56.5109
1348.7656 | 122.3145 | -60.6674 | 61.4731 | -0.056381 | 0.0025529 | 0.059676 | 0.10501 | 0.0010253 | -0.0007904 | -0.004593 | -0.37567 | 0.67285 | 0.061615 | 0.064894 | -0.021236 | -0.00072207 | 0.68626 | -2.4902 | 61.4594 | -60.8231 | 61.3586 | -60.1822 | -60.7498 | 0.5127 | -4.1702 | 61.3541 | -60.6537 | 61.3632 | -60.4111 | -60.7498 | 59.1888 | -0.15564 | -0.013732 | -0.11444 | 0.48523 | 61.1801 | -0.082398 | 61.3358 | 0.073242 | 0.013732 | -0.11902 | -0.10986 | 0.25635 | 119.8563 | -0.082398 | 119.8425 | -0.09613 | 0.64087 | 122.1817 | 0.24262 | 122.0169 | 122.2824 | 122.0078 | 122.1268 | 122.0215 | -122.2961 | -122.1268 | 122.0261 | 122.0306 | 58.1772 | 56.4972
1349.7812 | 122.4335 | -60.6857 | 61.3907 | -0.12505 | 0.0014847 | 0.060103 | 0.10736 | 0.0029479 | -0.0046356 | -0.00010676 | -0.2597 | 0.67392 | 0.062897 | 0.062972 | -0.023586 | -0.0022175 | 0.68477 | -1.7349 | 61.3678 | -60.8414 | 61.4136 | -60.3378 | -60.8459 | -0.1236 | -3.7811 | 61.2579 | -60.672 | 61.4502 | -60.3241 | -60.6308 | 59.5963 | -0.15564 | -0.022888 | 0.022888 | 0.3479 | 60.5621 | -0.16022 | 60.7178 | -0.004577 | 0.013733 | -0.13275 | 0.059509 | 0.36163 | 120.282 | 0.054932 | 120.2682 | 0.041199 | 0.50354 | 122.2549 | 0.3479 | 122.1222 | 122.2092 | 121.9299 | 122.0535 | 121.9437 | -122.2321 | -122.0627 | 122.0993 | 122.1359 | 58.9508 | 56.9046
1350.7656 | 122.319 | -60.7132 | 61.4456 | -0.10979 | -1.0718e-05 | 0.060957 | 0.10757 | -0.00025628 | -0.0005768 | -0.0052338 | -0.29633 | 0.67307 | 0.06247 | 0.061049 | -0.024868 | -0.0030719 | 0.67986 | -1.6022 | 61.3632 | -60.8139 | 61.3998 | -60.3378 | -60.878 | 0.17395 | -3.6209 | 61.2717 | -60.6995 | 61.3632 | -60.4202 | -60.7361 | 59.4223 | -0.10071 | -0.082398 | -0.045777 | 0.37537 | 60.8871 | -0.16479 | 60.9879 | -0.064087 | 0.013733 | -0.17395 | -0.082398 | 0.29297 | 120.1355 | -0.022888 | 120.1218 | -0.036621 | 0.47607 | 122.2137 | 0.27924 | 122.0627 | 122.1771 | 121.9711 | 122.0764 | 121.9849 | -122.2595 | -122.1451 | 122.113 | 122.0764 | 59.111 | 57.0923
1351.7656 | 122.2458 | -60.6857 | 61.4822 | -0.06401 | 0.00041648 | 0.059035 | 0.10607 | 0.00038452 | -0.0016448 | 0.0030976 | -0.28412 | 0.67178 | 0.064392 | 0.059554 | -0.022732 | -0.00072207 | 0.67943 | -2.0096 | 61.409 | -60.7956 | 61.3495 | -60.3699 | -60.9192 | 0.045776 | -3.9185 | 61.3449 | -60.6628 | 61.3403 | -60.2051 | -60.8963 | 59.4543 | -0.10986 | -0.073242 | -0.13275 | 0.31586 | 60.7315 | -0.23346 | 60.8414 | -0.1236 | 0.022888 | -0.13733 | -0.14191 | 0.48065 | 120.1401 | -0.21057 | 120.1172 | -0.23346 | 0.42572 | 122.1451 | 0.45776 | 122.0032 | 122.2046 | 122.0078 | 122.0947 | 122.0306 | -122.2778 | -122.1451 | 122.0352 | 122.0261 | 58.6761 | 56.7673
1352.7656 | 122.3145 | -60.6537 | 61.5692 | -0.1403 | 0.00041648 | 0.061171 | 0.10714 | 0.0025207 | -0.0048492 | -0.0016022 | -0.30548 | 0.66986 | 0.064179 | 0.059127 | -0.024013 | -0.0020039 | 0.67772 | -2.4673 | 61.4502 | -60.7819 | 61.4182 | -60.3333 | -60.8688 | -0.19684 | -4.0604 | 61.3586 | -60.6354 | 61.3541 | -60.4385 | -60.7315 | 59.1385 | -0.12817 | -0.11902 | -0.15106 | 0.32043 | 60.4568 | -0.21515 | 60.585 | -0.086975 | 0.018311 | -0.21057 | -0.21515 | 0.21515 | 119.7922 | -0.077819 | 119.7739 | -0.09613 | 0.44861 | 122.2 | 0.19684 | 121.9894 | 122.2321 | 121.994 | 122.1039 | 122.0123 | -122.3511 | -122.2046 | 122.0718 | 122.0078 | 58.1863 | 56.5933
1353.7656 | 122.3099 | -60.6079 | 61.5921 | -0.06401 | -0.00043792 | 0.060957 | 0.10757 | -0.00025628 | -0.0007904 | -0.0018158 | -0.29022 | 0.66687 | 0.063538 | 0.058272 | -0.022732 | -0.00093567 | 0.67537 | -2.1286 | 61.4868 | -60.7315 | 61.4502 | -60.2692 | -60.8185 | 0.28839 | -4.1656 | 61.4136 | -60.5667 | 61.4227 | -60.3561 | -60.6628 | 59.3674 | -0.1236 | -0.10529 | -0.14191 | 0.33874 | 60.8963 | -0.21057 | 61.0199 | -0.086975 | 0.041199 | -0.17853 | -0.16937 | 0.25177 | 119.9753 | -0.054932 | 119.9341 | -0.096131 | 0.46234 | 122.1817 | 0.21057 | 121.9894 | 122.2183 | 121.9803 | 122.0947 | 122.0215 | -122.3236 | -122.1588 | 122.0581 | 122.0306 | 58.4793 | 56.4423
1354.8438 | 122.4243 | -60.5942 | 61.4685 | -0.10216 | 0.0012711 | 0.062025 | 0.108 | 0.0093567 | -0.0012176 | -0.0018158 | -0.30243 | 0.66773 | 0.063324 | 0.063613 | -0.022945 | -0.00050847 | 0.67516 | -1.7532 | 61.4365 | -60.7498 | 61.6562 | -60.2051 | -60.8963 | 0.8606 | -3.7582 | 61.3495 | -60.585 | 61.528 | -60.2875 | -60.5896 | 59.7336 | -0.15564 | -0.032044 | 0.18768 | 0.3891 | 61.4548 | -0.30212 | 61.6104 | -0.14648 | 0.009155 | -0.11902 | 0.059509 | 0.3067 | 120.3278 | 0.004577 | 120.3186 | -0.004578 | 0.54474 | 122.406 | 0.29755 | 122.113 | 122.1863 | 121.9345 | 122.0306 | 121.9437 | -122.2183 | -122.0535 | 122.2504 | 122.1222 | 58.8409 | 56.8359
1355.7656 | 122.2961 | -60.6171 | 61.5234 | -0.041122 | -0.00022432 | 0.057967 | 0.10714 | 0.0012391 | -0.0039948 | -0.0041656 | -0.41229 | 0.66516 | 0.061829 | 0.063613 | -0.02145 | -0.0024311 | 0.6758 | -1.7715 | 61.496 | -60.7498 | 61.409 | -60.3882 | -60.6171 | 0.80109 | -3.9597 | 61.3998 | -60.6308 | 61.3953 | -60.3882 | -60.7086 | 59.3262 | -0.13275 | -0.027465 | -0.11444 | 0.22888 | 61.4182 | 0 | 61.5509 | 0.13275 | -0.013733 | -0.1236 | -0.12817 | 0.22888 | 119.9432 | -0.091553 | 119.957 | -0.07782 | 0.36163 | 122.1588 | 0.24261 | 122.0261 | 122.2458 | 122.0306 | 122.113 | 122.0169 | -122.2733 | -122.1542 | 122.0261 | 122.0123 | 58.8455 | 56.6574
1356.7656 | 122.3053 | -60.64 | 61.496 | -0.041122 | 0.0021255 | 0.059676 | 0.10736 | 0.0027343 | -0.0003632 | -0.0060882 | -0.23224 | 0.66303 | 0.065033 | 0.063185 | -0.02145 | -0.00050847 | 0.67387 | -1.593 | 61.4365 | -60.759 | 61.4639 | -60.2371 | -60.7956 | 0.93842 | -3.4424 | 61.3495 | -60.6262 | 61.4182 | -60.3516 | -60.6537 | 59.5001 | -0.11902 | -0.05951 | -0.032044 | 0.40283 | 61.5784 | -0.15564 | 61.6974 | -0.036621 | 0.013733 | -0.14648 | -0.07782 | 0.28839 | 120.1401 | -0.013733 | 120.1263 | -0.027466 | 0.52185 | 122.2229 | 0.27466 | 122.0444 | 122.1954 | 121.9757 | 122.0764 | 121.9894 | -122.2549 | -122.1222 | 122.1039 | 122.0581 | 59.0469 | 57.1976
1357.7656 | 122.2229 | -60.7086 | 61.4227 | -0.06401 | -0.00043792 | 0.059889 | 0.1065 | -0.0015381 | -0.0018586 | -0.0035248 | -0.30548 | 0.66538 | 0.063751 | 0.060408 | -0.022945 | -0.0020039 | 0.67067 | -1.8677 | 61.4227 | -60.8597 | 61.3358 | -60.3745 | -60.9375 | 0.91095 | -3.6667 | 61.3129 | -60.6812 | 61.2671 | -60.2921 | -60.5804 | 59.6283 | -0.15106 | 0 | -0.086975 | 0.33417 | 61.6196 | -0.22888 | 61.7706 | -0.07782 | 0.027466 | -0.10986 | -0.15564 | 0.41656 | 120.3369 | 0.12817 | 120.3094 | 0.10071 | 0.48523 | 122.1954 | 0.3891 | 121.9482 | 122.2824 | 121.994 | 122.1313 | 122.0215 | -122.2824 | -122.1039 | 122.0444 | 121.9757 | 58.8409 | 57.0419
1358.7656 | 122.3465 | -60.6628 | 61.4685 | -0.094528 | -1.0718e-05 | 0.062239 | 0.10714 | 0.0025207 | -0.0035674 | -0.0013886 | -0.34515 | 0.66431 | 0.06247 | 0.061476 | -0.02145 | 0.00013253 | 0.67174 | -2.1057 | 61.4639 | -60.7956 | 61.3724 | -60.3653 | -60.8871 | 0.87891 | -3.8269 | 61.3312 | -60.6583 | 61.3815 | -60.4202 | -60.7269 | 59.5093 | -0.13275 | -0.004578 | -0.096131 | 0.29755 | 61.5417 | -0.2243 | 61.6745 | -0.091553 | 0.004578 | -0.13733 | -0.086975 | 0.24262 | 120.1721 | -0.064087 | 120.1675 | -0.068665 | 0.4303 | 122.168 | 0.23804 | 122.0398 | 122.2595 | 121.9894 | 122.1268 | 121.994 | -122.2641 | -122.1268 | 122.0352 | 122.0444 | 58.5571 | 56.8359
1359.7812 | 122.3236 | -60.585 | 61.5646 | -0.025863 | 0.00084388 | 0.059676 | 0.10629 | 0.0018799 | 6.4004e-05 | -0.002884 | -0.33295 | 0.65811 | 0.062897 | 0.057631 | -0.022945 | -0.0015765 | 0.6664 | -1.4511 | 61.5051 | -60.7178 | 61.4594 | -60.2692 | -60.7956 | 1.2405 | -3.6804 | 61.4456 | -60.5759 | 61.4822 | -60.3058 | -60.6262 | 59.1797 | -0.13275 | -0.059509 | -0.10529 | 0.31586 | 61.8256 | -0.21057 | 61.9583 | -0.07782 | 0.009155 | -0.11902 | -0.082397 | 0.27924 | 119.7647 | -0.041199 | 119.7556 | -0.050354 | 0.44861 | 122.1771 | 0.27008 | 122.0581 | 122.2229 | 122.0215 | 122.0901 | 122.0306 | -122.2824 | -122.1405 | 122.0444 | 122.0673 | 59.1339 | 56.9046
1360.7656 | 122.3099 | -60.5804 | 61.5509 | -0.086899 | -0.00043792 | 0.060103 | 0.10565 | 0.0014527 | -0.0005768 | -0.002884 | -0.34515 | 0.65961 | 0.062897 | 0.064894 | -0.022945 | 0.0014141 | 0.66853 | -1.6251 | 61.496 | -60.7544 | 61.4639 | -60.1822 | -60.7819 | 1.1581 | -3.685 | 61.4502 | -60.5896 | 61.5051 | -60.3058 | -60.6308 | 59.3857 | -0.17395 | -0.054931 | -0.086975 | 0.39825 | 61.7386 | -0.20142 | 61.9125 | -0.027465 | -0.009156 | -0.10071 | -0.045776 | 0.27466 | 119.9661 | -0.050354 | 119.9753 | -0.041198 | 0.57221 | 122.2183 | 0.28381 | 122.0947 | 122.2504 | 122.0398 | 122.0764 | 122.0306 | -122.3053 | -122.1405 | 122.0444 | 122.0856 | 58.9554 | 56.8954
1361.7656 | 122.3007 | -60.5392 | 61.5646 | -0.086899 | 0.0023391 | 0.060316 | 0.10586 | -0.0019653 | -0.0035674 | -0.0037384 | -0.24445 | 0.65662 | 0.064179 | 0.060836 | -0.021236 | -0.00072207 | 0.67216 | -1.4328 | 61.5189 | -60.6628 | 61.5234 | -60.1685 | -60.7178 | 0.9613 | -3.7125 | 61.4365 | -60.5301 | 61.5005 | -60.2646 | -60.5713 | 59.6603 | -0.1236 | -0.045776 | -0.041199 | 0.37079 | 61.5005 | -0.17853 | 61.6241 | -0.054931 | 0.009156 | -0.12817 | -0.064087 | 0.27466 | 120.1996 | -0.032043 | 120.1904 | -0.041199 | 0.49439 | 122.1863 | 0.2655 | 122.0306 | 122.1817 | 121.9666 | 122.0581 | 121.9757 | -122.2275 | -122.0947 | 122.0627 | 122.0398 | 59.1064 | 56.8268
1362.7656 | 122.2595 | -60.5621 | 61.5921 | -0.07164 | 0.0021255 | 0.060744 | 0.10586 | 0.0016663 | -0.0012176 | -0.002884 | -0.28107 | 0.65747 | 0.063751 | 0.062972 | -0.022732 | -0.00072207 | 0.66811 | -1.8448 | 61.5463 | -60.704 | 61.4594 | -60.2097 | -60.7864 | 1.181 | -3.6438 | 61.4456 | -60.5392 | 61.5372 | -60.1639 | -60.8276 | 59.5322 | -0.14191 | -0.045776 | -0.13275 | 0.35248 | 61.7432 | -0.2243 | 61.8851 | -0.082397 | 0.022888 | -0.14648 | -0.054932 | 0.39825 | 120.0943 | -0.2655 | 120.0714 | -0.28839 | 0.49438 | 122.1634 | 0.37537 | 122.0764 | 122.2504 | 121.9849 | 122.1085 | 122.0078 | -122.2961 | -122.1313 | 122.0215 | 122.0993 | 58.7173 | 56.9183
1363.7656 | 122.2 | -60.6171 | 61.5875 | -0.048752 | 0.00020288 | 0.060957 | 0.10522 | -0.0021789 | -0.0020722 | -0.0018158 | -0.29327 | 0.65769 | 0.063751 | 0.065535 | -0.022732 | -0.0032855 | 0.66661 | -1.1536 | 61.4777 | -60.7269 | 61.4136 | -60.2646 | -60.8047 | 1.7487 | -3.7079 | 61.4273 | -60.5804 | 61.4044 | -60.3882 | -60.6812 | 59.5642 | -0.10986 | -0.10986 | -0.17395 | 0.35248 | 62.3657 | -0.18768 | 62.4756 | -0.07782 | 0.036621 | -0.16022 | -0.18311 | 0.22888 | 120.1813 | -0.064087 | 120.1447 | -0.10071 | 0.46234 | 122.1405 | 0.19226 | 121.9849 | 122.2046 | 122.0078 | 122.0947 | 122.0444 | -122.3145 | -122.168 | 122.0306 | 122.0215 | 59.4635 | 56.9092
1364.7812 | 122.287 | -60.6308 | 61.5189 | -0.079269 | 0.00041648 | 0.058394 | 0.10479 | -0.00046988 | -0.0031402 | -0.002884 | -0.27496 | 0.65747 | 0.065247 | 0.06404 | -0.022732 | -0.0028583 | 0.6664 | -1.7303 | 61.4456 | -60.7636 | 61.3861 | -60.3195 | -60.8688 | 1.5518 | -3.6438 | 61.3953 | -60.6033 | 61.4365 | -60.5942 | -60.8276 | 59.6054 | -0.13275 | -0.073242 | -0.13275 | 0.31128 | 62.1826 | -0.23804 | 62.3154 | -0.10528 | 0.027465 | -0.1236 | -0.082398 | 0.036621 | 120.2362 | -0.19684 | 120.2087 | -0.2243 | 0.44403 | 122.1497 | 0.009156 | 122.0398 | 122.2092 | 121.9986 | 122.0764 | 122.0261 | -122.2824 | -122.1222 | 122.0169 | 122.0673 | 58.9005 | 56.987
1365.7656 | 122.2595 | -60.6812 | 61.4685 | -0.025863 | -0.00065152 | 0.059676 | 0.10842 | -0.0038879 | -0.0039948 | -0.0013886 | -0.29633 | 0.65192 | 0.062897 | 0.063826 | -0.023373 | -0.0013629 | 0.66255 | -1.4374 | 61.4365 | -60.7727 | 61.3541 | -60.4248 | -60.9192 | 1.8997 | -3.6942 | 61.3632 | -60.6445 | 61.2991 | -60.4614 | -60.7636 | 59.0973 | -0.091553 | -0.032044 | -0.11444 | 0.25635 | 62.5809 | -0.23804 | 62.6724 | -0.14648 | 0.036621 | -0.10529 | -0.16937 | 0.21973 | 119.7784 | -0.082398 | 119.7418 | -0.11902 | 0.3479 | 122.1268 | 0.1831 | 121.9437 | 122.2092 | 122.0078 | 122.1176 | 122.0444 | -122.2412 | -122.113 | 122.0352 | 121.9803 | 59.2438 | 56.987
1366.7812 | 122.3419 | -60.672 | 61.4548 | -0.086899 | 0.00084388 | 0.059462 | 0.10629 | 0.00081172 | -0.0016448 | -0.0052338 | -0.2475 | 0.65064 | 0.06247 | 0.055922 | -0.0238 | -0.0017901 | 0.66298 | -1.5427 | 61.3724 | -60.7956 | 61.3861 | -60.3104 | -60.8871 | 2.1515 | -3.6987 | 61.2854 | -60.6628 | 61.3678 | -60.4065 | -60.672 | 59.2529 | -0.1236 | -0.082398 | -0.068665 | 0.36163 | 62.8235 | -0.21515 | 62.9471 | -0.091553 | 0.009155 | -0.16937 | -0.086975 | 0.2655 | 119.9249 | 0 | 119.9158 | -0.009155 | 0.48523 | 122.1817 | 0.25635 | 122.0306 | 122.168 | 121.9482 | 122.0444 | 121.9574 | -122.2504 | -122.1176 | 122.0581 | 122.0398 | 59.1293 | 56.9733
1367.7656 | 122.2824 | -60.6995 | 61.4365 | -0.079269 | -0.00086512 | 0.061598 | 0.10714 | -0.0043151 | -0.0024994 | -0.004593 | -0.25055 | 0.65277 | 0.065674 | 0.064253 | -0.021877 | -0.0017901 | 0.65828 | -1.8173 | 61.3907 | -60.8551 | 61.2946 | -60.4019 | -60.965 | 2.1927 | -3.7399 | 61.2625 | -60.7178 | 61.2854 | -60.4935 | -60.7956 | 59.1019 | -0.15564 | -0.045776 | -0.14191 | 0.29755 | 62.8922 | -0.2655 | 63.0478 | -0.10986 | -0.01831 | -0.17395 | -0.15106 | 0.20599 | 119.8013 | -0.09613 | 119.8196 | -0.07782 | 0.45319 | 122.1497 | 0.2243 | 122.0032 | 122.2458 | 121.9803 | 122.0901 | 121.962 | -122.2916 | -122.1542 | 121.994 | 121.9849 | 58.8821 | 56.9595
1368.7656 | 122.287 | -60.6537 | 61.4548 | -0.086899 | 0.0010575 | 0.061171 | 0.10693 | 0.0018799 | -0.0039948 | 0.00010684 | -0.35736 | 0.65085 | 0.064392 | 0.061263 | -0.025936 | -0.0017901 | 0.65742 | -2.1469 | 61.4227 | -60.8002 | 61.3724 | -60.3287 | -60.9146 | 1.4877 | -3.5568 | 61.3312 | -60.6812 | 61.3724 | -60.4202 | -60.7498 | 59.2209 | -0.14648 | -0.032044 | -0.082398 | 0.32501 | 62.1414 | -0.26093 | 62.2879 | -0.11444 | -0.027465 | -0.1236 | -0.082398 | 0.23346 | 119.8746 | -0.09613 | 119.902 | -0.068665 | 0.4715 | 122.1725 | 0.26093 | 122.0535 | 122.2229 | 122.0123 | 122.0764 | 121.9849 | -122.2549 | -122.1359 | 122.0261 | 122.0261 | 58.5068 | 57.0969
1369.7812 | 122.3923 | -60.6171 | 61.4365 | -0.06401 | 0.00041648 | 0.060957 | 0.10458 | -0.0019653 | -0.0005768 | -0.0018158 | -0.21088 | 0.64572 | 0.061615 | 0.048445 | -0.023373 | -0.0024311 | 0.65614 | -1.9867 | 61.3815 | -60.7773 | 61.4868 | -60.141 | -60.7544 | 1.9455 | -3.035 | 61.3861 | -60.5438 | 61.4273 | -60.3012 | -60.5164 | 59.0927 | -0.16022 | -0.054931 | 0.050354 | 0.47607 | 62.5626 | -0.13733 | 62.7228 | 0.022888 | 0.073242 | -0.050354 | -0.009155 | 0.31586 | 119.7098 | 0.10071 | 119.6365 | 0.027466 | 0.63629 | 122.2641 | 0.24262 | 121.9711 | 122.1588 | 121.9299 | 121.9986 | 122.0032 | -122.2137 | -121.9803 | 122.1039 | 122.0444 | 58.6304 | 57.5821
1370.7656 | 122.3053 | -60.6766 | 61.4685 | -0.06401 | -0.0012923 | 0.059035 | 0.10586 | -0.00046988 | -0.0039948 | -0.00096136 | -0.27191 | 0.64679 | 0.062897 | 0.065535 | -0.021877 | -0.0047809 | 0.65657 | -1.9775 | 61.4227 | -60.7819 | 61.3724 | -60.3333 | -60.9009 | 1.7349 | -3.3463 | 61.3632 | -60.6171 | 61.4044 | -60.6033 | -60.9421 | 59.1431 | -0.10529 | -0.045777 | -0.096131 | 0.34332 | 62.4115 | -0.2243 | 62.5168 | -0.11902 | 0.05951 | -0.10529 | -0.064087 | 0.073242 | 119.8196 | -0.2655 | 119.7601 | -0.32501 | 0.44861 | 122.1542 | 0.013732 | 122.0215 | 122.2046 | 121.9803 | 122.0993 | 122.0398 | -122.2504 | -122.0856 | 122.0489 | 122.081 | 58.699 | 57.3303
1371.8438 | 122.4472 | -60.6354 | 61.4319 | -0.13267 | 0.0010575 | 0.061385 | 0.10757 | 0.0012391 | -0.0024994 | -0.00053396 | -0.31769 | 0.64572 | 0.062256 | 0.065322 | -0.022945 | 0.00098693 | 0.65379 | -1.973 | 61.3495 | -60.8047 | 61.4136 | -60.2783 | -60.8871 | 1.6113 | -3.4378 | 61.2534 | -60.6537 | 61.496 | -60.6125 | -60.5713 | 59.2667 | -0.16937 | -0.082398 | -0.018311 | 0.35706 | 62.2467 | -0.25177 | 62.4161 | -0.082397 | -0.018311 | -0.17853 | 0.064087 | 0.022888 | 119.902 | 0.064087 | 119.9203 | 0.082398 | 0.52643 | 122.2183 | 0.041199 | 122.1497 | 122.1542 | 121.907 | 121.9849 | 121.8887 | -122.2366 | -122.0856 | 122.0489 | 122.1313 | 58.6624 | 57.1976
1372.7656 | 122.2137 | -60.64 | 61.4777 | -0.07164 | 0.00041648 | 0.060103 | 0.10522 | -0.0017517 | -0.0035674 | -0.0026704 | -0.2597 | 0.64359 | 0.064392 | 0.061263 | -0.022945 | -0.0030719 | 0.65401 | -1.6708 | 61.441 | -60.8047 | 61.322 | -60.3333 | -60.91 | 1.4877 | -3.2639 | 61.3266 | -60.64 | 61.3541 | -60.4202 | -60.4797 | 59.3765 | -0.16479 | -0.036621 | -0.15564 | 0.3067 | 62.1277 | -0.27008 | 62.2925 | -0.10529 | 0 | -0.15106 | -0.1236 | 0.21973 | 120.0165 | 0.16022 | 120.0165 | 0.16022 | 0.4715 | 122.1268 | 0.21973 | 121.994 | 122.2458 | 121.9666 | 122.081 | 121.9666 | -122.2824 | -122.1176 | 121.962 | 121.994 | 58.9691 | 57.3761
1373.7656 | 122.3053 | -60.6445 | 61.5189 | -0.056381 | -0.00043792 | 0.061171 | 0.10693 | -0.0047425 | -0.0029266 | -0.0043792 | -0.28717 | 0.64401 | 0.064179 | 0.060622 | -0.021664 | -0.0015765 | 0.65742 | -1.4465 | 61.4182 | -60.7864 | 61.3312 | -60.3378 | -60.8917 | 1.2085 | -3.0808 | 61.3495 | -60.6491 | 61.3312 | -60.4065 | -60.7178 | 59.3353 | -0.14191 | -0.10071 | -0.18768 | 0.3067 | 61.853 | -0.24719 | 61.9949 | -0.10529 | -0.004578 | -0.16937 | -0.18768 | 0.23804 | 119.9799 | -0.073242 | 119.9844 | -0.068664 | 0.44861 | 122.1176 | 0.24262 | 121.9803 | 122.2046 | 121.9986 | 122.0627 | 121.994 | -122.3053 | -122.168 | 121.9757 | 121.9757 | 59.198 | 57.5638
1374.7656 | 122.3099 | -60.672 | 61.4273 | -0.10216 | 0.0012711 | 0.060744 | 0.10778 | 0.0025207 | -0.0042084 | 0.00074764 | -0.36957 | 0.64359 | 0.063538 | 0.062331 | -0.0238 | -0.0020039 | 0.65422 | -1.7532 | 61.4136 | -60.8459 | 61.3129 | -60.3699 | -60.965 | 0.88348 | -3.479 | 61.322 | -60.6491 | 61.3541 | -60.4568 | -60.7727 | 59.2575 | -0.17395 | -0.013733 | -0.11444 | 0.30212 | 61.5555 | -0.29297 | 61.7294 | -0.11902 | 0.022888 | -0.10529 | -0.073242 | 0.21515 | 119.9295 | -0.10071 | 119.9066 | -0.1236 | 0.47607 | 122.1588 | 0.19226 | 122.0032 | 122.2595 | 121.9711 | 122.0856 | 121.994 | -122.2733 | -122.0764 | 121.9849 | 122.0261 | 58.9188 | 57.193
1375.7656 | 122.3053 | -60.5804 | 61.5509 | -0.086899 | -0.00022432 | 0.060744 | 0.10607 | 0.00038452 | -0.002713 | 0.00053404 | -0.31464 | 0.64124 | 0.062256 | 0.06404 | -0.0238 | 0.00013253 | 0.65251 | -1.4557 | 61.496 | -60.7498 | 61.4182 | -60.2737 | -60.8322 | 1.0529 | -3.0716 | 61.3861 | -60.5988 | 61.4456 | -60.3241 | -60.6491 | 59.2896 | -0.16937 | -0.054931 | -0.13275 | 0.3067 | 61.6333 | -0.25177 | 61.8027 | -0.082397 | -0.018311 | -0.16479 | -0.10528 | 0.25635 | 119.87 | -0.068665 | 119.8883 | -0.050354 | 0.47607 | 122.168 | 0.27466 | 122.0444 | 122.2458 | 121.9849 | 122.0764 | 121.9666 | -122.3007 | -122.1497 | 121.9986 | 122.0261 | 59.1248 | 57.5089
1376.7656 | 122.3007 | -60.6125 | 61.4548 | -0.11742 | 0.0012711 | 0.063307 | 0.10821 | 0.00081172 | 0.0002778 | 0.001175 | -0.32074 | 0.64017 | 0.066315 | 0.05934 | -0.021023 | 0.00034613 | 0.64653 | -1.6022 | 61.4639 | -60.7864 | 61.3495 | -60.3195 | -60.91 | 0.79651 | -3.1174 | 61.377 | -60.6262 | 61.3998 | -60.4156 | -60.7178 | 59.1888 | -0.17395 | 0.009155 | -0.10529 | 0.29297 | 61.409 | -0.29755 | 61.5829 | -0.1236 | -0.013733 | -0.07782 | -0.054932 | 0.19684 | 119.8013 | -0.10529 | 119.8151 | -0.091552 | 0.46692 | 122.1359 | 0.21057 | 122.0261 | 122.2504 | 122.0032 | 122.0764 | 121.9894 | -122.2412 | -122.081 | 121.962 | 122.0123 | 59.0103 | 57.4951
1377.7656 | 122.2687 | -60.64 | 61.4822 | -0.048752 | -1.0718e-05 | 0.058821 | 0.1065 | -0.0034607 | -0.002713 | -0.0020294 | -0.2475 | 0.63611 | 0.06247 | 0.062331 | -0.024868 | -0.0022175 | 0.65102 | -1.4511 | 61.4594 | -60.7727 | 61.3815 | -60.2737 | -60.8459 | 1.3824 | -3.5797 | 61.3449 | -60.6308 | 61.3678 | -60.3882 | -60.6812 | 59.1293 | -0.13275 | -0.022888 | -0.10071 | 0.36621 | 62.0224 | -0.20599 | 62.1552 | -0.073242 | 0.009156 | -0.13733 | -0.11444 | 0.25177 | 119.7693 | -0.041198 | 119.7601 | -0.050354 | 0.49896 | 122.1542 | 0.24261 | 121.9986 | 122.2321 | 121.9757 | 122.0993 | 121.9849 | -122.2549 | -122.113 | 122.0215 | 122.0078 | 59.1888 | 57.0602
1378.7656 | 122.2687 | -60.6537 | 61.4548 | 0.10384 | -0.0015061 | 0.057753 | 0.10565 | 0.0018799 | -0.0033538 | -0.001175 | -0.26886 | 0.6406 | 0.063324 | 0.057418 | -0.02145 | -0.0022175 | 0.64546 | -1.4557 | 61.4594 | -60.791 | 61.322 | -60.3241 | -60.9192 | 1.3962 | -3.5706 | 61.3541 | -60.6354 | 61.3495 | -60.4156 | -60.7224 | 59.166 | -0.13733 | 0.004578 | -0.13275 | 0.32959 | 62.0499 | -0.2655 | 62.1872 | -0.12817 | 0.018311 | -0.10071 | -0.10529 | 0.23804 | 119.8196 | -0.068664 | 119.8013 | -0.086975 | 0.46692 | 122.113 | 0.21973 | 121.9849 | 122.2504 | 121.9894 | 122.113 | 122.0078 | -122.2458 | -122.0901 | 121.9757 | 122.0032 | 59.198 | 57.0831
1379.7656 | 122.3007 | -60.5713 | 61.5372 | -0.086899 | -1.0718e-05 | 0.060103 | 0.10693 | 0.0012391 | -0.001004 | 0.00074764 | -0.34821 | 0.63889 | 0.062897 | 0.059554 | -0.024013 | -0.00050847 | 0.64632 | -1.2085 | 61.4639 | -60.7315 | 61.4365 | -60.228 | -60.8459 | 1.3412 | -3.566 | 61.3586 | -60.5896 | 61.4548 | -60.3287 | -60.6537 | 59.198 | -0.16022 | -0.073242 | -0.10071 | 0.34332 | 61.9125 | -0.27466 | 62.0728 | -0.11444 | -0.018311 | -0.17853 | -0.082397 | 0.24262 | 119.7693 | -0.082398 | 119.7876 | -0.064087 | 0.50354 | 122.168 | 0.26093 | 122.0444 | 122.1954 | 121.9482 | 122.0352 | 121.9299 | -122.2687 | -122.1268 | 122.0078 | 122.0261 | 59.3628 | 57.0053
1380.7656 | 122.2458 | -60.5713 | 61.5601 | -0.033493 | 0.0012711 | 0.060103 | 0.10928 | -0.0011109 | -0.0046356 | -0.002884 | -0.21088 | 0.6359 | 0.065033 | 0.063826 | -0.022518 | -0.0011493 | 0.65251 | -1.4832 | 61.5372 | -60.6674 | 61.6058 | -60.2371 | -61.1023 | 1.2863 | -3.772 | 61.4227 | -60.5438 | 61.441 | -60.3378 | -60.6262 | 59.1797 | -0.09613 | -0.022889 | 0.045776 | 0.33417 | 61.8576 | -0.53101 | 61.9537 | -0.43488 | 0.027466 | -0.13733 | -0.11902 | 0.23346 | 119.751 | -0.054932 | 119.7235 | -0.082398 | 0.4303 | 122.2733 | 0.20599 | 121.9849 | 122.2046 | 121.9666 | 122.1085 | 121.994 | -122.2275 | -122.1039 | 122.1771 | 122.0123 | 59.0881 | 56.7993
1381.7656 | 122.2916 | -60.5713 | 61.5097 | -0.06401 | 0.0027665 | 0.059462 | 0.10842 | 0.00038452 | -0.0035674 | -0.00074776 | -0.3299 | 0.6359 | 0.061829 | 0.064253 | -0.024227 | -0.0024311 | 0.64888 | -1.1444 | 61.4868 | -60.7178 | 61.4044 | -60.2646 | -60.8688 | 1.8723 | -3.5934 | 61.3861 | -60.5896 | 61.4502 | -60.347 | -60.64 | 59.1843 | -0.14648 | -0.022889 | -0.10529 | 0.3067 | 62.4435 | -0.29755 | 62.59 | -0.15106 | -0.018311 | -0.1236 | -0.05951 | 0.2243 | 119.7556 | -0.068665 | 119.7739 | -0.050354 | 0.45319 | 122.1222 | 0.24262 | 122.0398 | 122.2046 | 121.9757 | 122.0581 | 121.9574 | -122.2275 | -122.0993 | 121.9757 | 122.0215 | 59.4269 | 56.9778
1382.7812 | 122.3648 | -60.5576 | 61.4639 | -0.086899 | -0.0023605 | 0.062239 | 0.10501 | 0.0031617 | -0.0014312 | -0.002884 | -0.21698 | 0.63291 | 0.061615 | 0.053359 | -0.022732 | -0.0028583 | 0.64525 | -1.1124 | 61.4365 | -60.7132 | 61.4227 | -60.2234 | -60.8139 | 1.6708 | -3.7628 | 61.3495 | -60.5804 | 61.4456 | -60.3378 | -60.4523 | 59.4635 | -0.15564 | -0.027466 | -0.041199 | 0.33417 | 62.2284 | -0.25635 | 62.384 | -0.10071 | -0.022888 | -0.11444 | -0.01831 | 0.21973 | 120.0211 | 0.10528 | 120.0439 | 0.12817 | 0.48981 | 122.1359 | 0.24261 | 122.0261 | 122.1497 | 121.9299 | 121.994 | 121.907 | -122.1771 | -122.0444 | 121.9803 | 122.0032 | 59.4452 | 56.7947
1383.7656 | 122.2916 | -60.585 | 61.5005 | -0.13267 | 0.0021255 | 0.06053 | 0.10907 | 0.0010253 | 0.0002778 | -0.0018158 | -0.35736 | 0.63526 | 0.063324 | 0.060836 | -0.024227 | 0.00055973 | 0.64397 | -1.474 | 61.4777 | -60.7361 | 61.4548 | -60.2051 | -60.8139 | 1.5701 | -3.7628 | 61.3678 | -60.6033 | 61.4319 | -60.498 | -60.6079 | 59.3719 | -0.15106 | -0.022888 | -0.045776 | 0.37994 | 62.1552 | -0.22888 | 62.3062 | -0.07782 | -0.018311 | -0.13275 | -0.068664 | 0.086975 | 119.957 | -0.022888 | 119.9753 | -0.004577 | 0.53101 | 122.1909 | 0.10529 | 122.0352 | 122.2137 | 121.9711 | 122.0627 | 121.9528 | -122.2366 | -122.1039 | 122.0398 | 122.0169 | 59.111 | 56.8222
1384.7656 | 122.3557 | -60.6674 | 61.5005 | -0.10216 | 0.0014847 | 0.062453 | 0.10928 | 0.0042297 | 6.4004e-05 | 0.00032044 | -0.35431 | 0.63333 | 0.061188 | 0.062545 | -0.024868 | -0.00050847 | 0.64162 | -1.886 | 61.4456 | -60.7727 | 61.3449 | -60.347 | -60.9329 | 1.2863 | -4.248 | 61.3678 | -60.64 | 61.3495 | -60.585 | -61.1298 | 58.8638 | -0.10529 | -0.054931 | -0.15564 | 0.32043 | 61.9537 | -0.2655 | 62.059 | -0.16022 | 0.027465 | -0.13275 | -0.15106 | 0.082397 | 119.5312 | -0.46234 | 119.5038 | -0.48981 | 0.42572 | 122.1176 | 0.054932 | 121.9894 | 122.2183 | 122.0078 | 122.113 | 122.0352 | -122.2733 | -122.1405 | 122.0123 | 122.0169 | 58.7814 | 56.4194
1385.7656 | 122.287 | -60.5942 | 61.5051 | -0.079269 | 0.0012711 | 0.062239 | 0.10629 | -0.0015381 | -0.0012176 | -0.0030976 | -0.23224 | 0.6312 | 0.064392 | 0.055922 | -0.022945 | -0.0015765 | 0.6414 | -1.4511 | 61.4456 | -60.7132 | 61.4685 | -60.1776 | -60.7498 | 1.4832 | -4.0329 | 61.3495 | -60.5759 | 61.4319 | -60.3378 | -60.5988 | 58.9645 | -0.11902 | -0.059509 | -0.036621 | 0.41656 | 62.0773 | -0.15564 | 62.1964 | -0.036621 | 0.01831 | -0.15564 | -0.073242 | 0.25635 | 119.5587 | -0.004578 | 119.5404 | -0.022888 | 0.53558 | 122.1817 | 0.23804 | 122.0078 | 122.1588 | 121.9254 | 122.0398 | 121.9437 | -122.2183 | -122.081 | 122.0627 | 122.0261 | 59.1431 | 56.5613
1386.7656 | 122.3419 | -60.5576 | 61.4639 | -0.10216 | 0.0014847 | 0.060957 | 0.10757 | 0.0027343 | -0.0003632 | -0.00032036 | -0.29938 | 0.6312 | 0.063751 | 0.062758 | -0.024227 | -0.00093567 | 0.64354 | -1.1261 | 61.441 | -60.7178 | 61.4456 | -60.228 | -60.8276 | 1.9363 | -3.9871 | 61.3266 | -60.5621 | 61.5005 | -60.3012 | -60.5988 | 59.3308 | -0.16022 | -0.022888 | -0.01831 | 0.32959 | 62.4939 | -0.27008 | 62.6541 | -0.10986 | -0.004578 | -0.13733 | 0.036621 | 0.25635 | 119.8883 | -0.041199 | 119.8929 | -0.036621 | 0.48981 | 122.1634 | 0.26093 | 122.0627 | 122.1588 | 121.8887 | 121.9986 | 121.8842 | -122.1817 | -122.0261 | 122.0032 | 122.0581 | 59.4315 | 56.5704
1387.7656 | 122.2961 | -60.5026 | 61.6104 | -0.079269 | 0.0025529 | 0.059676 | 0.1065 | 0.0055115 | -0.0007904 | -0.0035248 | -0.29938 | 0.63034 | 0.06247 | 0.067031 | -0.024868 | -0.00072207 | 0.64098 | -1.1078 | 61.6013 | -60.6445 | 61.4777 | -60.1776 | -60.7315 | 1.9547 | -3.7857 | 61.5005 | -60.4889 | 61.5051 | -60.2371 | -60.5576 | 59.2529 | -0.14191 | -0.009156 | -0.13275 | 0.32501 | 62.4573 | -0.22888 | 62.5992 | -0.086975 | 0.013733 | -0.10986 | -0.10529 | 0.2655 | 119.7556 | -0.054931 | 119.7418 | -0.068664 | 0.46692 | 122.1222 | 0.25177 | 121.994 | 122.2458 | 121.9894 | 122.1039 | 122.0032 | -122.2549 | -122.0993 | 121.9803 | 122.0078 | 59.3948 | 56.7169
1388.7656 | 122.2595 | -60.4935 | 61.6013 | -0.07164 | -0.00043792 | 0.059035 | 0.10629 | -4.2682e-05 | -0.0012176 | -0.0026704 | -0.2536 | 0.62735 | 0.065033 | 0.057204 | -0.021236 | -0.00029487 | 0.63564 | -1.0757 | 61.5601 | -60.6308 | 61.4502 | -60.1868 | -60.7636 | 1.6205 | -3.5568 | 61.5005 | -60.4935 | 61.4456 | -60.2829 | -60.6079 | 59.1797 | -0.13733 | -0.041198 | -0.15106 | 0.3067 | 62.114 | -0.27008 | 62.2513 | -0.13275 | 0 | -0.10071 | -0.15564 | 0.21057 | 119.6732 | -0.11444 | 119.6732 | -0.11444 | 0.44403 | 122.081 | 0.21057 | 121.9391 | 122.1909 | 121.994 | 122.0535 | 121.994 | -122.2321 | -122.0947 | 121.9437 | 121.9391 | 59.4177 | 56.9366
1389.7656 | 122.3007 | -60.5026 | 61.6562 | -0.025863 | -1.0718e-05 | 0.061598 | 0.1065 | 0.0018799 | -0.0039948 | -0.0024566 | -0.25665 | 0.62714 | 0.063965 | 0.05699 | -0.022518 | -0.0011493 | 0.63734 | -1.1673 | 61.5326 | -60.672 | 61.4685 | -60.1868 | -60.7681 | 1.1581 | -3.3005 | 61.4502 | -60.5209 | 61.4502 | -60.3012 | -60.5392 | 59.1019 | -0.16937 | -0.1236 | -0.18768 | 0.31586 | 61.6608 | -0.2655 | 61.8301 | -0.09613 | -0.01831 | -0.20599 | -0.20599 | 0.20142 | 119.6045 | -0.036621 | 119.6228 | -0.018311 | 0.48523 | 122.1405 | 0.21973 | 121.9711 | 122.2046 | 121.9711 | 122.0352 | 121.9528 | -122.3282 | -122.1771 | 121.9711 | 121.9528 | 59.3353 | 57.2021
1390.7656 | 122.2321 | -60.4568 | 61.6608 | -0.10979 | 0.00063028 | 0.059035 | 0.10607 | 0.0038025 | -0.0018586 | -0.0016022 | -0.2475 | 0.6265 | 0.06247 | 0.062331 | -0.022091 | -0.0015765 | 0.63243 | -0.89722 | 61.5784 | -60.5942 | 61.5463 | -60.0815 | -60.6491 | 1.0986 | -3.4882 | 61.4868 | -60.4614 | 61.5097 | -60.2371 | -60.5164 | 59.1248 | -0.13733 | -0.082398 | -0.11444 | 0.37537 | 61.5555 | -0.19226 | 61.6928 | -0.054932 | -0.004578 | -0.17395 | -0.15106 | 0.21973 | 119.5816 | -0.059509 | 119.5862 | -0.054931 | 0.5127 | 122.1405 | 0.2243 | 121.9711 | 122.1725 | 121.9482 | 122.0352 | 121.9437 | -122.2549 | -122.1222 | 122.0032 | 121.9666 | 59.5596 | 56.9687
1391.7656 | 122.2916 | -60.5026 | 61.5646 | -0.10979 | 0.00041648 | 0.060957 | 0.10714 | 0.0031617 | -0.0046356 | -0.00032036 | -0.32379 | 0.62479 | 0.063324 | 0.073653 | -0.024441 | -0.00050847 | 0.63307 | -1.268 | 61.528 | -60.6857 | 61.4639 | -60.2051 | -60.8047 | 1.181 | -3.566 | 61.4548 | -60.5026 | 61.4914 | -60.2966 | -60.5942 | 58.6853 | -0.1831 | -0.036621 | -0.10071 | 0.29755 | 61.6837 | -0.30212 | 61.8668 | -0.11902 | 0 | -0.10986 | -0.073242 | 0.20599 | 119.1879 | -0.091552 | 119.1879 | -0.091552 | 0.48065 | 122.1497 | 0.20599 | 121.994 | 122.2137 | 121.9574 | 122.0306 | 121.9574 | -122.2504 | -122.0673 | 121.9666 | 121.994 | 59.2346 | 56.9366
1392.7656 | 122.3236 | -60.5621 | 61.4822 | -0.041122 | 0.0019119 | 0.059248 | 0.10458 | -0.00046988 | -0.0022858 | -0.0026704 | -0.21698 | 0.62479 | 0.06247 | 0.061263 | -0.02145 | -0.0015765 | 0.63435 | -1.2451 | 61.4685 | -60.6857 | 61.5189 | -60.1135 | -60.6995 | 1.4648 | -3.0029 | 61.3586 | -60.5438 | 61.4777 | -60.2783 | -60.5484 | 58.8684 | -0.1236 | -0.013733 | 0.036621 | 0.44861 | 62.027 | -0.13733 | 62.1506 | -0.013733 | 0.018311 | -0.1236 | -0.004578 | 0.28381 | 119.4305 | 0.013733 | 119.4122 | -0.004578 | 0.5722 | 122.2046 | 0.2655 | 122.0215 | 122.1542 | 121.9025 | 122.0306 | 121.9208 | -122.168 | -122.0261 | 122.081 | 122.0398 | 59.317 | 57.5592
1393.7656 | 122.3648 | -60.4385 | 61.5829 | -0.094528 | 0.00020288 | 0.060316 | 0.10842 | 0.0016663 | -0.0022858 | -0.002243 | -0.24445 | 0.62329 | 0.062042 | 0.061476 | -0.022518 | -0.0013629 | 0.62923 | -1.5244 | 61.528 | -60.5621 | 61.6104 | -60.022 | -60.6171 | 1.5381 | -2.98 | 61.441 | -60.4385 | 61.5921 | -60.1501 | -60.4248 | 59.2163 | -0.1236 | -0.054932 | 0.027466 | 0.41656 | 61.9766 | -0.17853 | 62.1002 | -0.054931 | 0 | -0.14191 | 0.009155 | 0.28839 | 119.6548 | 0.013733 | 119.6548 | 0.013733 | 0.54016 | 122.1725 | 0.28839 | 122.0306 | 122.0901 | 121.8796 | 121.9666 | 121.8796 | -122.1451 | -122.0215 | 122.049 | 122.0306 | 58.9142 | 57.4585
1394.7656 | 122.2504 | -60.4385 | 61.6653 | -0.025863 | -1.0718e-05 | 0.06053 | 0.10736 | 0.0025207 | -0.0020722 | -0.0018158 | -0.36652 | 0.62308 | 0.061829 | 0.065749 | -0.025082 | -0.0020039 | 0.63115 | -1.3 | 61.5875 | -60.6033 | 61.5875 | -60.0677 | -60.6766 | 1.2772 | -3.1128 | 61.5234 | -60.4202 | 61.5829 | -60.2051 | -60.498 | 59.0973 | -0.16479 | -0.07782 | -0.07782 | 0.37079 | 61.7157 | -0.23804 | 61.8805 | -0.073242 | 0.018311 | -0.14191 | -0.082397 | 0.23346 | 119.5358 | -0.059509 | 119.5175 | -0.07782 | 0.53558 | 122.1909 | 0.21515 | 122.0032 | 122.1909 | 121.9437 | 122.0261 | 121.962 | -122.2687 | -122.0856 | 122.0261 | 122.0215 | 59.1385 | 57.3257
1395.7656 | 122.3328 | -60.4019 | 61.6928 | -0.079269 | 0.00063028 | 0.060316 | 0.10522 | 0.0031617 | -0.0016448 | -0.0020294 | -0.21088 | 0.62052 | 0.061829 | 0.057845 | -0.023586 | -0.0041401 | 0.63051 | -1.0117 | 61.5875 | -60.5164 | 61.6516 | -59.9762 | -60.5576 | 1.8082 | -3.0808 | 61.5189 | -60.3882 | 61.6196 | -60.0861 | -60.379 | 59.0881 | -0.11444 | -0.10529 | -0.041199 | 0.42572 | 62.2101 | -0.15564 | 62.3245 | -0.041199 | 0.013733 | -0.17395 | -0.073242 | 0.31586 | 119.4901 | 0.022889 | 119.4763 | 0.009156 | 0.54016 | 122.168 | 0.30212 | 122.0078 | 122.1039 | 121.907 | 121.9894 | 121.9208 | -122.2092 | -122.081 | 122.0535 | 122.0215 | 59.3903 | 57.3212
1396.7656 | 122.5296 | -60.347 | 61.7294 | -0.094528 | -0.00065152 | 0.061171 | 0.10565 | 0.0025207 | -0.0029266 | -0.0016022 | -0.22308 | 0.62094 | 0.064392 | 0.055709 | -0.023373 | -0.0020039 | 0.63115 | -1.3596 | 61.6104 | -60.5209 | 61.6653 | -59.9625 | -60.5576 | 1.1993 | -3.1311 | 61.4822 | -60.3699 | 61.6882 | -60.0494 | -60.3241 | 59.2941 | -0.17395 | -0.11902 | -0.064087 | 0.38452 | 61.5463 | -0.21057 | 61.7203 | -0.036621 | -0.022888 | -0.24719 | -0.041199 | 0.29755 | 119.6411 | 0.022888 | 119.664 | 0.045776 | 0.55847 | 122.1863 | 0.32043 | 122.0581 | 122.1313 | 121.8521 | 121.9574 | 121.8292 | -122.2504 | -122.0993 | 122.0123 | 122.0352 | 58.9874 | 57.2159
1397.7656 | 122.3511 | -60.3607 | 61.6653 | -0.033493 | 0.00084388 | 0.061812 | 0.10693 | 0.00038452 | -0.0031402 | -0.0035248 | -0.24139 | 0.62116 | 0.062256 | 0.055495 | -0.025295 | -0.0030719 | 0.62837 | -1.6663 | 61.615 | -60.5026 | 61.6974 | -60.2737 | -60.7269 | 0.89722 | -3.4653 | 61.5143 | -60.3745 | 61.6837 | -60.0677 | -60.3195 | 59.3353 | -0.14191 | -0.050354 | 0.032044 | 0.086975 | 61.2579 | -0.36621 | 61.3998 | -0.2243 | -0.013733 | -0.15106 | 0.018311 | 0.29297 | 119.696 | 0.041199 | 119.7098 | 0.054932 | 0.22888 | 122.2 | 0.3067 | 122.0581 | 122.1176 | 121.8887 | 121.9757 | 121.875 | -122.168 | -122.0398 | 122.0581 | 122.0444 | 58.6945 | 56.8954
1398.7656 | 122.2778 | -60.3882 | 61.702 | -0.086899 | 0.0012711 | 0.059035 | 0.10736 | 0.0027343 | -0.0042084 | -0.0026704 | -0.36346 | 0.61838 | 0.062897 | 0.069594 | -0.02615 | -0.0017901 | 0.62709 | -1.6708 | 61.6379 | -60.553 | 61.6791 | -60.0128 | -60.6125 | 1.0666 | -3.3646 | 61.5555 | -60.3745 | 61.6196 | -60.1547 | -60.4431 | 59.1431 | -0.16479 | -0.064087 | -0.022888 | 0.37537 | 61.4548 | -0.2243 | 61.6196 | -0.059509 | 0.013733 | -0.14648 | -0.082397 | 0.23346 | 119.5312 | -0.054931 | 119.5175 | -0.068664 | 0.54016 | 122.2321 | 0.21973 | 121.994 | 122.1909 | 121.9299 | 122.0261 | 121.9437 | -122.2549 | -122.0764 | 122.0673 | 122.0078 | 58.7173 | 57.0236
1399.7656 | 122.2275 | -60.4202 | 61.6699 | -0.094528 | 0.00041648 | 0.062239 | 0.10949 | 0.00017092 | -0.0003632 | -0.00010676 | -0.23529 | 0.6171 | 0.066101 | 0.065749 | -0.0238 | 0.00034613 | 0.62901 | -1.4053 | 61.615 | -60.5804 | 61.5005 | -60.3195 | -61.1572 | 0.41199 | -3.5248 | 61.5555 | -60.4019 | 61.5784 | -60.26 | -60.5438 | 58.8043 | -0.16022 | -0.054932 | -0.16937 | 0.10071 | 60.8322 | -0.737 | 60.9924 | -0.57678 | 0.01831 | -0.11444 | -0.091553 | 0.16022 | 119.2245 | -0.1236 | 119.2062 | -0.14191 | 0.26093 | 122.081 | 0.14191 | 121.9803 | 122.1954 | 121.9574 | 122.0352 | 121.9757 | -122.2504 | -122.0718 | 121.9208 | 121.9986 | 59.0149 | 56.8954
1400.8125 | 122.3053 | -60.379 | 61.6837 | -0.13267 | 0.00063028 | 0.06053 | 0.10543 | -0.0015381 | -0.0012176 | -0.00010676 | -0.25055 | 0.61688 | 0.06247 | 0.056563 | -0.023159 | 0.00055973 | 0.62474 | -1.7532 | 61.6058 | -60.5255 | 61.615 | -60.0037 | -60.5988 | 0.25635 | -3.5522 | 61.5463 | -60.3561 | 61.5829 | -60.1044 | -60.4019 | 58.8867 | -0.14648 | -0.07782 | -0.068665 | 0.37537 | 60.6354 | -0.21973 | 60.7819 | -0.073242 | 0.022888 | -0.13733 | -0.10071 | 0.27466 | 119.2657 | -0.022889 | 119.2429 | -0.045777 | 0.52185 | 122.1405 | 0.25177 | 121.9391 | 122.1313 | 121.9025 | 121.9849 | 121.9254 | -122.2092 | -122.0398 | 121.994 | 121.962 | 58.6258 | 56.8268
1401.7969 | 122.3099 | -60.3058 | 61.7111 | -0.086899 | -0.00043792 | 0.060744 | 0.10586 | 0.0027343 | -0.0022858 | -0.0016022 | -0.24139 | 0.61646 | 0.062042 | 0.056777 | -0.022732 | -0.0026447 | 0.62901 | -2.0416 | 61.6699 | -60.466 | 61.7065 | -59.903 | -60.4935 | 0.36621 | -3.4012 | 61.5784 | -60.3241 | 61.6837 | -60.0586 | -60.3378 | 59.0286 | -0.16022 | -0.041199 | -0.004578 | 0.40283 | 60.672 | -0.18768 | 60.8322 | -0.027466 | -0.018311 | -0.13275 | -0.027466 | 0.24719 | 119.3344 | -0.032044 | 119.3527 | -0.013733 | 0.56305 | 122.1725 | 0.2655 | 122.0078 | 122.1359 | 121.9025 | 121.9757 | 121.8842 | -122.1771 | -122.0352 | 122.0123 | 121.9894 | 58.2642 | 56.9046
1402.8594 | 122.287 | -60.3333 | 61.7065 | -0.086899 | -0.00086512 | 0.060957 | 0.10672 | 0.00059812 | -0.0024994 | 0.00074764 | -0.22614 | 0.61325 | 0.062042 | 0.059767 | -0.023373 | -0.0013629 | 0.62816 | -1.506 | 61.6608 | -60.4523 | 61.702 | -59.9167 | -60.5072 | 0.4715 | -3.2684 | 61.5738 | -60.3424 | 61.6699 | -60.0677 | -60.3561 | 58.9279 | -0.11902 | -0.045776 | -0.004578 | 0.41656 | 60.8047 | -0.17395 | 60.9238 | -0.054931 | -0.009155 | -0.13275 | -0.036621 | 0.2655 | 119.2612 | -0.022888 | 119.2703 | -0.013733 | 0.53558 | 122.1542 | 0.27466 | 122.0123 | 122.113 | 121.9162 | 121.994 | 121.907 | -122.1588 | -122.049 | 122.0352 | 122.0032 | 58.8272 | 57.0648
1403.7656 | 122.3282 | -60.3561 | 61.6837 | -0.079269 | 0.0010575 | 0.059676 | 0.10437 | -0.0013245 | -0.0020722 | -0.0013886 | -0.22308 | 0.61517 | 0.058838 | 0.057204 | -0.022945 | -0.00029487 | 0.61983 | -1.5106 | 61.6333 | -60.4935 | 61.6425 | -59.9991 | -60.5759 | 0.32501 | -3.2959 | 61.5189 | -60.3699 | 61.6745 | -60.0815 | -60.3607 | 58.7631 | -0.13733 | -0.050354 | -0.041199 | 0.35706 | 60.6812 | -0.21973 | 60.8185 | -0.082398 | -0.013733 | -0.1648 | -0.009155 | 0.27466 | 119.1193 | -0.004578 | 119.133 | 0.009155 | 0.49438 | 122.1359 | 0.28839 | 122.0444 | 122.1268 | 121.8887 | 121.9894 | 121.875 | -122.1771 | -122.0535 | 121.9986 | 122.0306 | 58.8455 | 57.0602
1404.7812 | 122.3053 | -60.2829 | 61.7157 | -0.07164 | -0.00022432 | 0.061812 | 0.10714 | -0.0019653 | -0.0012176 | -0.002243 | -0.40619 | 0.61197 | 0.061829 | 0.06169 | -0.025082 | -0.00072207 | 0.61983 | -1.6525 | 61.6837 | -60.4477 | 61.7661 | -59.935 | -60.0311 | 0.44861 | -3.3463 | 61.5463 | -60.3058 | 61.702 | -59.9899 | -60.2692 | 58.667 | -0.16479 | -0.032043 | 0.050354 | 0.3479 | 60.7315 | 0.25177 | 60.8963 | 0.41656 | -0.022888 | -0.16937 | -0.013733 | 0.29297 | 118.9499 | 0.013733 | 118.9728 | 0.036621 | 0.5127 | 122.2137 | 0.31586 | 122.0078 | 122.1313 | 121.8521 | 121.9666 | 121.8292 | -122.1634 | -122.0215 | 122.049 | 121.9849 | 58.6304 | 56.9366
1405.7656 | 122.3419 | -58.9233 | 63.0753 | -0.10216 | 0.0031937 | 0.058821 | 0.10714 | 0.0014527 | -0.001004 | -0.0035248 | -0.024719 | -0.0051868 | 0.064392 | 0.05934 | -0.019527 | 0.0033367 | 0.00010689 | -2.7008 | 63.0203 | -59.1064 | 63.0661 | -58.6212 | -59.2117 | -1.3229 | -6.6284 | 63.0203 | -59.0424 | 63.121 | -58.8501 | -59.0652 | -58.7997 | -0.1831 | -0.054931 | -0.009155 | 0.30212 | 57.6004 | -0.28839 | 57.7835 | -0.10529 | -0.11902 | -0.054931 | 0.045777 | 0.073242 | 0.1236 | -0.14191 | 0.24261 | -0.022889 | 0.48523 | 122.1725 | 0.19226 | 122.1634 | 122.1268 | 122.0627 | 121.9437 | 121.9437 | -122.1817 | -122.1176 | 121.9894 | 122.0444 | 56.2225 | 52.2949
1406.7656 | 122.2641 | -58.9691 | 63.1348 | -0.048752 | 0.0012711 | 0.05818 | 0.1065 | -4.2682e-05 | -0.002713 | -0.0048066 | -0.027771 | -0.002196 | 0.06247 | 0.065322 | -0.018459 | -0.00029487 | 0.0039521 | -2.33 | 63.1531 | -59.0744 | 63.0615 | -58.6349 | -59.2804 | -0.97961 | -6.6467 | 63.0844 | -59.0744 | 63.0524 | -58.8547 | -58.8226 | -53.1097 | -0.10529 | 0.01831 | -0.073243 | 0.33417 | 57.9895 | -0.31128 | 58.0948 | -0.20599 | -0.10529 | -0.050354 | -0.082398 | 0.11444 | 5.8594 | 0.14648 | 5.9647 | 0.25177 | 0.43945 | 122.1359 | 0.21973 | 122.1268 | 122.2275 | 122.1588 | 122.1222 | 122.0535 | -122.2092 | -122.2092 | 122.0306 | 122.0215 | 56.6391 | 52.3224
1407.7812 | 122.3007 | -58.9371 | 63.1668 | -0.086899 | -0.00086512 | 0.057753 | 0.10629 | -0.0034607 | -0.0050628 | -0.00010676 | -0.030823 | -0.0034778 | 0.064179 | 0.062331 | -0.019741 | -0.00029487 | 0.0045929 | -2.6184 | 63.1348 | -59.079 | 63.0844 | -58.6166 | -59.2026 | -1.2177 | -6.8573 | 63.1485 | -59.0195 | 63.1485 | -58.8593 | -59.0378 | -58.3923 | -0.14191 | -0.032043 | -0.082397 | 0.32043 | 57.7194 | -0.2655 | 57.8613 | -0.1236 | -0.082397 | -0.01831 | -0.01831 | 0.07782 | 0.54474 | -0.10071 | 0.62714 | -0.018311 | 0.46234 | 122.1634 | 0.16022 | 122.168 | 122.2137 | 122.168 | 122.0718 | 122.0856 | -122.2458 | -122.1863 | 122.0215 | 122.0856 | 56.3187 | 52.0798
1408.7656 | 122.5204 | -58.8959 | 63.1622 | -0.094528 | 0.0010575 | 0.060744 | 0.10693 | -0.0026063 | 6.4004e-05 | -0.0037384 | 0.014954 | -0.005614 | 0.064179 | 0.055281 | -0.020595 | 0.0033367 | 0.00010689 | -2.6413 | 63.0981 | -59.0836 | 63.176 | -58.5114 | -59.1156 | -1.0437 | -6.5277 | 63.0707 | -59.0012 | 63.2584 | -58.7357 | -58.6853 | -58.4885 | -0.18768 | -0.064086 | 0.013733 | 0.38452 | 57.8522 | -0.21973 | 58.0399 | -0.032044 | -0.10529 | -0.091552 | 0.096131 | 0.16022 | 0.40741 | 0.21057 | 0.5127 | 0.31586 | 0.5722 | 122.2595 | 0.2655 | 122.2595 | 122.1817 | 122.0718 | 121.994 | 121.9666 | -122.2458 | -122.1634 | 122.0718 | 122.1542 | 56.2546 | 52.3682
1409.7656 | 122.3785 | -59.0057 | 63.1165 | -0.079269 | 0.0010575 | 0.060957 | 0.10714 | 0.0023071 | -0.0022858 | -0.00074776 | -0.046081 | -0.002196 | 0.063965 | 0.064467 | -0.019314 | 0.0012005 | 0.0028839 | -2.6733 | 63.0661 | -59.1431 | 63.0981 | -58.7952 | -59.2667 | -1.1353 | -6.2393 | 63.0386 | -59.0652 | 63.1393 | -58.8684 | -59.0057 | -57.3029 | -0.13733 | -0.050354 | -0.01831 | 0.21057 | 57.8705 | -0.26093 | 58.0078 | -0.1236 | -0.05951 | -0.07782 | 0.022888 | 0.13733 | 1.7029 | 0 | 1.7624 | 0.05951 | 0.3479 | 122.2412 | 0.19684 | 122.2046 | 122.2092 | 122.1039 | 122.0718 | 122.0444 | -122.2595 | -122.1817 | 122.1039 | 122.1451 | 56.3324 | 52.7664
1410.7656 | 122.3831 | -59.024 | 63.0981 | -0.079269 | 0.00084388 | 0.061171 | 0.10864 | 0.0023071 | -0.0001496 | -0.00096136 | -0.027771 | -0.0047594 | 0.066529 | 0.06404 | -0.020809 | 0.0012005 | 0.0016021 | -2.3758 | 63.0478 | -59.1385 | 63.121 | -58.6212 | -59.1797 | -1.0483 | -6.2119 | 63.0615 | -59.0836 | 63.1439 | -58.8409 | -59.079 | -58.8272 | -0.11444 | -0.050354 | 0.022888 | 0.40283 | 57.9758 | -0.15564 | 58.0902 | -0.041198 | -0.059509 | -0.036622 | 0.045776 | 0.18311 | 0.19684 | -0.054931 | 0.25635 | 0.004578 | 0.51727 | 122.2595 | 0.24262 | 122.2275 | 122.1863 | 122.1451 | 122.0718 | 122.0856 | -122.2366 | -122.1817 | 122.1451 | 122.168 | 56.6483 | 52.8122
1411.7656 | 122.4197 | -59.0561 | 63.0661 | -0.11742 | -0.00065152 | 0.060744 | 0.108 | -0.00068368 | -0.0003632 | 0.00053404 | -0.015564 | -0.0024096 | 0.062256 | 0.059767 | -0.022091 | -0.0013629 | -0.00096131 | -2.8336 | 63.0157 | -59.1888 | 63.0432 | -58.7082 | -59.2987 | -1.5244 | -6.0654 | 63.0112 | -59.1156 | 63.2446 | -59.0103 | -59.2026 | -58.9783 | -0.13275 | -0.050354 | -0.022888 | 0.3479 | 57.5317 | -0.24262 | 57.6645 | -0.10986 | -0.05951 | -0.054932 | 0.17853 | 0.045776 | 0.07782 | -0.14648 | 0.13733 | -0.086975 | 0.48065 | 122.2321 | 0.10529 | 122.3602 | 122.2046 | 122.1268 | 122.0718 | 122.0673 | -122.2549 | -122.1817 | 122.0993 | 122.3007 | 56.2225 | 52.9907
1412.7656 | 122.3511 | -59.0332 | 63.1165 | -0.07164 | 0.0010575 | 0.05818 | 0.10736 | 0.00059812 | -0.0035674 | -0.0048066 | -0.046081 | -0.0036914 | 0.064392 | 0.060408 | -0.022732 | 0.00098693 | 0.0028839 | -2.7603 | 63.0798 | -59.1797 | 63.0844 | -58.6716 | -59.2392 | -1.5564 | -5.8502 | 63.0569 | -59.079 | 63.0936 | -58.9005 | -59.1064 | -58.6761 | -0.14648 | -0.036621 | -0.032043 | 0.36163 | 57.4768 | -0.20599 | 57.6233 | -0.05951 | -0.045776 | -0.059509 | -0.022888 | 0.13275 | 0.35706 | -0.073242 | 0.40283 | -0.027466 | 0.50812 | 122.2641 | 0.17853 | 122.1725 | 122.2595 | 122.1359 | 122.113 | 122.0901 | -122.2961 | -122.1954 | 122.1176 | 122.1268 | 56.2729 | 53.183
1413.7656 | 122.4197 | -59.0561 | 63.0753 | -0.079269 | -1.0718e-05 | 0.062239 | 0.10949 | 0.0023071 | -0.0005768 | -0.0030976 | -0.021667 | -0.0032642 | 0.062256 | 0.058058 | -0.022304 | 0.00077333 | 0.0043793 | -2.4994 | 63.0524 | -59.1888 | 63.0157 | -58.7311 | -59.317 | -1.9043 | -5.8044 | 62.9929 | -59.1156 | 63.0981 | -58.9371 | -59.1614 | -58.9279 | -0.13275 | -0.022888 | -0.059509 | 0.32501 | 57.1518 | -0.26093 | 57.2845 | -0.12817 | -0.05951 | -0.082397 | 0.022889 | 0.11902 | 0.12817 | -0.10529 | 0.18768 | -0.045776 | 0.45776 | 122.2046 | 0.17853 | 122.2137 | 122.2412 | 122.1085 | 122.1085 | 122.049 | -122.2641 | -122.1909 | 122.0718 | 122.1542 | 56.5567 | 53.2516
1414.7656 | 122.4335 | -59.0469 | 63.1073 | -0.094528 | -0.0012923 | 0.061385 | 0.10693 | -0.00025628 | -0.0012176 | -0.0016022 | -0.030823 | -0.0017688 | 0.06482 | 0.059554 | -0.022304 | 0.0024823 | -0.00074771 | -2.7557 | 63.0569 | -59.1705 | 63.1348 | -58.5022 | -59.2712 | -1.9775 | -5.8502 | 63.0066 | -59.1293 | 63.1302 | -58.9096 | -59.1431 | -58.8272 | -0.1236 | -0.050354 | 0.027466 | 0.54474 | 57.0694 | -0.2243 | 57.193 | -0.10071 | -0.082397 | -0.10071 | 0.022888 | 0.13733 | 0.21973 | -0.09613 | 0.30212 | -0.013733 | 0.66833 | 122.3053 | 0.21973 | 122.2595 | 122.2275 | 122.1359 | 122.1039 | 122.0535 | -122.2778 | -122.2366 | 122.1817 | 122.1771 | 56.2912 | 53.1967
1415.7656 | 122.4243 | -59.1019 | 63.0569 | -0.079269 | 0.00084388 | 0.061598 | 0.10714 | 0.0029479 | -0.0033538 | -0.00010676 | -0.039978 | -0.0043322 | 0.063751 | 0.063185 | -0.021236 | 0.0033367 | 0.0041657 | -2.8107 | 63.0066 | -59.2484 | 63.0066 | -58.7585 | -59.2804 | -2.1698 | -5.896 | 63.0203 | -59.1522 | 63.1027 | -58.9783 | -59.1843 | -59.1248 | -0.14648 | -0.050354 | -0.050354 | 0.34332 | 56.9321 | -0.17853 | 57.0786 | -0.032044 | -0.050354 | -0.036621 | 0.045776 | 0.1236 | -0.022888 | -0.082397 | 0.027466 | -0.032043 | 0.48981 | 122.2549 | 0.17395 | 122.2549 | 122.2549 | 122.1725 | 122.1085 | 122.1222 | -122.3053 | -122.2092 | 122.1085 | 122.2046 | 56.2912 | 53.2059
1416.7656 | 122.4655 | -59.0149 | 63.1119 | -0.086899 | 0.00084388 | 0.061598 | 0.10778 | 0.0025207 | -0.0024994 | -0.0016022 | -0.0064086 | -0.00091423 | 0.062897 | 0.059981 | -0.020809 | 0.0026959 | 0.00053409 | -2.6276 | 63.0844 | -59.1522 | 63.1851 | -58.5892 | -59.1522 | -1.9638 | -5.8502 | 63.0341 | -59.0652 | 63.2126 | -58.7631 | -59.1248 | -58.8684 | -0.13733 | -0.027465 | 0.073243 | 0.42572 | 57.0511 | -0.13733 | 57.1884 | 0 | -0.050354 | -0.077819 | 0.10071 | 0.25177 | 0.14648 | -0.10986 | 0.19684 | -0.059509 | 0.56305 | 122.3373 | 0.30212 | 122.2778 | 122.2366 | 122.0993 | 122.0993 | 122.049 | -122.2641 | -122.1771 | 122.2 | 122.2275 | 56.3873 | 53.1647
1417.7656 | 122.3099 | -59.0881 | 63.1256 | -0.07164 | 0.0016983 | 0.060957 | 0.10992 | -4.2682e-05 | -0.0050628 | -0.00096136 | -0.052185 | -0.0024096 | 0.065247 | 0.05699 | -0.02145 | 0.0022687 | -0.00096131 | -2.5681 | 63.1073 | -59.2026 | 63.0249 | -58.7677 | -59.3216 | -2.1378 | -5.8273 | 63.0936 | -59.1614 | 62.9471 | -58.9828 | -59.1339 | -58.9691 | -0.11444 | -0.01831 | -0.10071 | 0.32044 | 56.9504 | -0.23346 | 57.0648 | -0.11902 | -0.073242 | -0.032043 | -0.17853 | 0.10529 | 0.11902 | -0.045776 | 0.19226 | 0.027466 | 0.43488 | 122.2275 | 0.17853 | 122.1085 | 122.3099 | 122.2549 | 122.1954 | 122.1817 | -122.3282 | -122.287 | 122.113 | 122.0352 | 56.5201 | 53.2608
1418.7656 | 122.4747 | -59.024 | 63.1256 | -0.033493 | 0.0051163 | 0.057326 | 0.10736 | -0.0030335 | -0.0033538 | -0.0037384 | -0.012512 | -0.0013416 | 0.062683 | 0.060836 | -0.022091 | 0.0029095 | -0.0016021 | -2.4445 | 63.1531 | -59.1293 | 63.0981 | -58.6166 | -59.1522 | -1.8723 | -5.6992 | 63.0295 | -59.0744 | 63.1943 | -58.8364 | -59.0698 | -58.7494 | -0.10529 | 0.027466 | -0.027465 | 0.40741 | 57.1518 | -0.12817 | 57.2571 | -0.022889 | -0.050354 | -0.09613 | 0.068665 | 0.18768 | 0.27466 | -0.045776 | 0.32501 | 0.004578 | 0.5127 | 122.2275 | 0.23804 | 122.2687 | 122.2824 | 122.1039 | 122.1771 | 122.0535 | -122.2549 | -122.2 | 122.1222 | 122.2183 | 56.5796 | 53.3249
1419.7656 | 122.4426 | -59.0652 | 63.0707 | -0.11742 | 0.0014847 | 0.06053 | 0.10907 | 0.0010253 | -0.001004 | -0.00010676 | -0.036926 | -0.001128 | 0.063965 | 0.061476 | -0.022304 | -8.1274e-05 | 0.0020295 | -2.7512 | 63.0066 | -59.2438 | 63.0707 | -58.7219 | -59.3308 | -1.7258 | -5.658 | 62.9837 | -59.1431 | 63.1027 | -58.96 | -59.2072 | -59.0378 | -0.17853 | -0.064087 | 0 | 0.34332 | 57.3395 | -0.2655 | 57.518 | -0.086976 | -0.077819 | -0.086975 | 0.032043 | 0.10529 | 0.027466 | -0.14191 | 0.10528 | -0.064087 | 0.52185 | 122.3145 | 0.1831 | 122.2458 | 122.2504 | 122.1268 | 122.0718 | 122.049 | -122.3145 | -122.2137 | 122.1359 | 122.168 | 56.3141 | 53.4073
1420.7656 | 122.4747 | -59.0836 | 63.0707 | -0.048752 | 0.00063028 | 0.060316 | 0.108 | -0.0015381 | -0.0018586 | -0.0018158 | -0.04303 | -0.0045458 | 0.063538 | 0.056777 | -0.021023 | 0.0031231 | 0.00032049 | -2.5589 | 63.0203 | -59.2346 | 63.0341 | -58.7769 | -59.3353 | -1.387 | -5.4977 | 62.9974 | -59.1522 | 63.0981 | -58.9417 | -59.166 | -58.8547 | -0.15106 | -0.050354 | -0.036621 | 0.3067 | 57.6965 | -0.25177 | 57.8476 | -0.10071 | -0.068665 | -0.073242 | 0.027466 | 0.14191 | 0.22888 | -0.082398 | 0.29755 | -0.013733 | 0.45776 | 122.2687 | 0.21057 | 122.2504 | 122.2549 | 122.1497 | 122.1039 | 122.081 | -122.3053 | -122.2229 | 122.1176 | 122.1817 | 56.5247 | 53.5858
1421.7656 | 122.4289 | -59.0744 | 63.0707 | -0.11742 | -0.00043792 | 0.061812 | 0.10928 | 0.0020935 | 0.000705 | -0.001175 | -0.058289 | -0.0032642 | 0.062042 | 0.057631 | -0.022518 | 0.0014141 | 0.0028839 | -2.8427 | 63.0432 | -59.2438 | 63.0707 | -58.754 | -59.3353 | -2.005 | -5.6992 | 63.0112 | -59.1522 | 63.1119 | -58.9645 | -59.1843 | -58.8318 | -0.16937 | -0.027466 | 0 | 0.32043 | 57.0694 | -0.26093 | 57.2388 | -0.091553 | -0.07782 | -0.05951 | 0.041198 | 0.10986 | 0.24262 | -0.10986 | 0.32044 | -0.032043 | 0.48981 | 122.3145 | 0.18768 | 122.2641 | 122.287 | 122.1634 | 122.1176 | 122.0856 | -122.3145 | -122.2229 | 122.1451 | 122.1863 | 56.2317 | 53.3752
1422.7656 | 122.4518 | -59.024 | 63.1256 | -0.1403 | 0.00084388 | 0.060103 | 0.108 | 0.0042297 | -0.0024994 | -0.001175 | -0.027771 | -0.003905 | 0.062256 | 0.062117 | -0.02145 | 0.0014141 | 0.00074769 | -2.7191 | 63.0798 | -59.1797 | 63.1073 | -58.6945 | -59.2667 | -2.1194 | -5.5115 | 63.0661 | -59.079 | 63.1897 | -58.8638 | -59.1064 | -58.8089 | -0.15564 | -0.045776 | -0.01831 | 0.32959 | 56.9046 | -0.24262 | 57.0602 | -0.086976 | -0.054931 | -0.059509 | 0.064087 | 0.16022 | 0.21515 | -0.082397 | 0.27008 | -0.027466 | 0.48523 | 122.287 | 0.21515 | 122.2687 | 122.2595 | 122.1451 | 122.1039 | 122.0901 | -122.3053 | -122.2046 | 122.1313 | 122.2137 | 56.3049 | 53.5126
1423.7656 | 122.438 | -59.079 | 63.0798 | -0.17082 | -0.00022432 | 0.060957 | 0.10757 | 0.0029479 | -0.0007904 | -0.0020294 | -0.067444 | -0.0043322 | 0.060547 | 0.061263 | -0.022732 | 0.0020551 | 0.0052337 | -2.6505 | 63.0295 | -59.2255 | 63.0981 | -58.7128 | -59.285 | -2.0737 | -5.6534 | 63.0295 | -59.0927 | 63.1485 | -58.9645 | -59.3445 | -59.5825 | -0.14649 | -0.050354 | 0.018311 | 0.36621 | 57.0053 | -0.20599 | 57.1518 | -0.059509 | -0.013733 | -0.050354 | 0.068665 | 0.11444 | -0.50354 | -0.2655 | -0.48981 | -0.25177 | 0.5127 | 122.3236 | 0.12817 | 122.2412 | 122.2549 | 122.1222 | 122.1085 | 122.1085 | -122.3053 | -122.1725 | 122.1771 | 122.2275 | 56.4285 | 53.4256
1424.7656 | 122.4609 | -59.0881 | 63.0981 | -0.11742 | 0.00063028 | 0.061812 | 0.10778 | 0.0010253 | -0.0001496 | 0.00096124 | -0.024719 | -0.0045458 | 0.061402 | 0.058699 | -0.022518 | 0.0014141 | 0.00032049 | -2.7557 | 63.0341 | -59.2438 | 63.0295 | -58.7494 | -59.3399 | -2.1103 | -5.6671 | 63.0295 | -59.1385 | 63.1256 | -58.9462 | -59.1751 | -58.96 | -0.15564 | -0.064087 | -0.068665 | 0.33875 | 56.9778 | -0.25177 | 57.1335 | -0.096131 | -0.050354 | -0.068665 | 0.027465 | 0.14191 | 0.12817 | -0.086975 | 0.17853 | -0.036621 | 0.49438 | 122.2733 | 0.19226 | 122.2641 | 122.2778 | 122.168 | 122.1222 | 122.1176 | -122.3419 | -122.2366 | 122.1176 | 122.2137 | 56.3324 | 53.421
1425.7656 | 122.5067 | -59.0881 | 63.0753 | -0.11742 | 0.0012711 | 0.062666 | 0.10885 | 0.0040161 | -0.0012176 | -0.0035248 | -0.10712 | -0.003905 | 0.062256 | 0.062331 | -0.0238 | 0.0026959 | 0.00074769 | -2.4628 | 62.9929 | -59.2758 | 63.0478 | -58.9783 | -59.2392 | -1.9318 | -5.6946 | 62.9791 | -59.1751 | 63.1622 | -58.9417 | -59.1568 | -58.6761 | -0.18768 | -0.082397 | -0.027465 | 0.10986 | 57.1564 | -0.15106 | 57.3441 | 0.036621 | -0.086975 | -0.09613 | 0.086975 | 0.14648 | 0.41199 | -0.068664 | 0.49896 | 0.018311 | 0.29755 | 122.3236 | 0.23346 | 122.3373 | 122.2687 | 122.1542 | 122.081 | 122.0673 | -122.3511 | -122.2504 | 122.1359 | 122.2504 | 56.6254 | 53.3936
1426.7656 | 122.4884 | -59.0561 | 63.089 | -0.079269 | 0.0019119 | 0.06053 | 0.11035 | -0.00068368 | -0.0022858 | 0.00096124 | -0.091858 | -0.0034778 | 0.065247 | 0.061049 | -0.022304 | 0.0024823 | 0.0018159 | -2.8381 | 63.0661 | -59.2392 | 63.1348 | -58.6761 | -59.2987 | -2.417 | -5.864 | 63.0203 | -59.1248 | 63.1805 | -58.9417 | -59.1293 | -58.8638 | -0.18311 | -0.022888 | 0.045777 | 0.37994 | 56.6391 | -0.24262 | 56.8222 | -0.059509 | -0.068665 | -0.068664 | 0.091553 | 0.11444 | 0.19226 | -0.073242 | 0.26093 | -0.004577 | 0.56305 | 122.374 | 0.18311 | 122.3053 | 122.3053 | 122.1451 | 122.1222 | 122.0764 | -122.3282 | -122.2137 | 122.1909 | 122.2366 | 56.218 | 53.1921
1427.7656 | 122.5296 | -59.0607 | 63.1073 | -0.11742 | 0.0027665 | 0.059676 | 0.10714 | -0.0013245 | -0.0035674 | -0.0026704 | -0.018616 | -0.003905 | 0.064179 | 0.058058 | -0.021236 | 0.0016277 | 0.00053409 | -3.0487 | 63.0753 | -59.2072 | 63.1165 | -58.6899 | -59.2667 | -2.2018 | -5.8594 | 63.0249 | -59.1385 | 63.2034 | -58.8776 | -59.0973 | -58.9142 | -0.14648 | -0.032044 | 0.009155 | 0.37079 | 56.8588 | -0.20599 | 57.0053 | -0.05951 | -0.07782 | -0.082398 | 0.09613 | 0.18311 | 0.14648 | -0.036621 | 0.2243 | 0.041199 | 0.51727 | 122.3236 | 0.26093 | 122.3419 | 122.2824 | 122.1634 | 122.1359 | 122.0856 | -122.3145 | -122.2458 | 122.1771 | 122.2641 | 56.012 | 53.2013
1428.7656 | 122.4472 | -59.079 | 63.1119 | -0.12505 | 0.0016983 | 0.060103 | 0.10501 | -0.0028199 | -0.0033538 | -0.002884 | -0.058289 | -0.0036914 | 0.065674 | 0.056136 | -0.02145 | 0.0016277 | 0.0043793 | -2.8748 | 63.0798 | -59.23 | 63.1027 | -58.7219 | -59.3216 | -2.3438 | -5.8731 | 63.0615 | -59.1293 | 63.1577 | -58.9508 | -59.1568 | -58.9645 | -0.15106 | -0.032043 | -0.009155 | 0.35705 | 56.7352 | -0.24262 | 56.8863 | -0.091552 | -0.050354 | -0.050354 | 0.045777 | 0.12817 | 0.11444 | -0.07782 | 0.16479 | -0.027466 | 0.50812 | 122.3328 | 0.17853 | 122.287 | 122.3099 | 122.1909 | 122.1588 | 122.1405 | -122.3419 | -122.2412 | 122.1817 | 122.2366 | 56.2042 | 53.2059
1429.7656 | 122.4655 | -59.079 | 63.0844 | -0.1403 | 0.0012711 | 0.060957 | 0.10778 | 0.0048705 | -0.0012176 | -0.001175 | -0.082703 | -0.0032642 | 0.06247 | 0.061049 | -0.021877 | 0.0029095 | 0.0016021 | -2.7466 | 63.0203 | -59.23 | 63.1302 | -58.6899 | -59.3124 | -2.1881 | -5.7678 | 63.0341 | -59.1156 | 63.1897 | -58.9142 | -59.1751 | -58.8913 | -0.15106 | -0.064087 | 0.045776 | 0.3891 | 56.8909 | -0.23346 | 57.0419 | -0.082397 | -0.036622 | -0.050354 | 0.10529 | 0.16479 | 0.18768 | -0.096131 | 0.22431 | -0.059509 | 0.54016 | 122.3602 | 0.20142 | 122.3053 | 122.2504 | 122.1497 | 122.0993 | 122.113 | -122.3145 | -122.2 | 122.2092 | 122.2687 | 56.3324 | 53.3112
1430.7656 | 122.5067 | -59.0561 | 63.0753 | -0.10979 | 0.00063028 | 0.062453 | 0.10907 | 0.0012391 | -0.0014312 | 0.00074764 | -0.079651 | -0.0028368 | 0.06247 | 0.059767 | -0.02145 | 0.0018413 | 0.0011749 | -3.4058 | 63.0661 | -59.2117 | 63.1302 | -58.699 | -59.3033 | -2.5314 | -6.1157 | 63.0066 | -59.1568 | 63.1989 | -58.905 | -59.1568 | -58.905 | -0.15564 | -0.009155 | 0.054932 | 0.35706 | 56.5247 | -0.24719 | 56.6803 | -0.091553 | -0.10071 | -0.068664 | 0.1236 | 0.15106 | 0.15106 | -0.10071 | 0.25177 | 0 | 0.5127 | 122.3419 | 0.25177 | 122.3557 | 122.2778 | 122.1634 | 122.1222 | 122.0627 | -122.287 | -122.2321 | 122.1863 | 122.2549 | 55.6503 | 52.9404
1431.7656 | 122.4884 | -59.0698 | 63.0981 | -0.16319 | -1.0718e-05 | 0.060744 | 0.108 | -0.00068368 | -0.0020722 | -0.0018158 | -0.067444 | -0.003905 | 0.062683 | 0.06404 | -0.021236 | 0.00055973 | 0.0030975 | -3.3371 | 63.0432 | -59.2758 | 63.0936 | -58.7082 | -59.3033 | -2.211 | -6.0928 | 63.0203 | -59.1476 | 63.1851 | -58.9142 | -59.1614 | -58.9828 | -0.20599 | -0.054932 | -0.004578 | 0.36163 | 56.8588 | -0.23346 | 57.0648 | -0.027466 | -0.07782 | -0.07782 | 0.086975 | 0.15564 | 0.086975 | -0.091553 | 0.16479 | -0.013733 | 0.56763 | 122.3694 | 0.23346 | 122.3328 | 122.319 | 122.168 | 122.113 | 122.0901 | -122.374 | -122.2458 | 122.1634 | 122.2549 | 55.7327 | 52.977
1432.7656 | 122.5067 | -59.0378 | 63.1485 | 0.065689 | 0.0025529 | 0.062239 | 0.10736 | 0.0012391 | -0.0018586 | -0.00053396 | -0.018616 | -0.0032642 | 0.06012 | 0.058913 | -0.022091 | 0.00098693 | 0.00074769 | -3.4195 | 63.0798 | -59.2209 | 63.2034 | -58.6258 | -59.2346 | -2.3209 | -6.0059 | 63.0615 | -59.0927 | 63.2217 | -58.8318 | -59.0652 | -58.8181 | -0.1831 | -0.068665 | 0.054931 | 0.41199 | 56.7169 | -0.19684 | 56.9 | -0.013733 | -0.054931 | -0.086976 | 0.073242 | 0.20599 | 0.21973 | -0.027466 | 0.27466 | 0.027465 | 0.59509 | 122.4243 | 0.26093 | 122.3145 | 122.3007 | 122.1542 | 122.1176 | 122.0993 | -122.3694 | -122.2412 | 122.2412 | 122.2595 | 55.6183 | 53.0319
1433.7812 | 122.5433 | -59.0012 | 63.1851 | -0.1403 | -0.0027877 | 0.059676 | 0.10586 | -0.00089728 | -0.0022858 | -0.0018158 | -0.015564 | -0.0051868 | 0.061615 | 0.064681 | -0.022945 | 0.0016277 | -0.0028839 | -2.7374 | 63.0936 | -59.1843 | 63.2172 | -58.5892 | -59.1797 | -2.3804 | -5.9463 | 63.0936 | -59.0561 | 63.2904 | -58.7769 | -59.0103 | -58.7814 | -0.18311 | -0.091553 | 0.032043 | 0.41199 | 56.6208 | -0.17853 | 56.8039 | 0.004578 | -0.054931 | -0.091553 | 0.10529 | 0.22431 | 0.21973 | -0.009155 | 0.27466 | 0.045776 | 0.59509 | 122.4014 | 0.27924 | 122.3465 | 122.2778 | 122.1497 | 122.0947 | 122.0947 | -122.3694 | -122.2412 | 122.2183 | 122.2916 | 56.2637 | 53.0548
1434.7656 | 122.5021 | -59.0424 | 63.1668 | -0.086899 | 0.0010575 | 0.060744 | 0.108 | 0.0020935 | -0.0024994 | -0.0024566 | -0.00030524 | -0.002196 | 0.063538 | 0.062545 | -0.021023 | 0.00013253 | 0.0056611 | -2.7191 | 63.1256 | -59.1797 | 63.1577 | -58.6395 | -59.2438 | -2.5497 | -6.015 | 63.0844 | -59.0927 | 63.2584 | -58.8501 | -59.0698 | -58.8409 | -0.13733 | -0.041199 | -0.009155 | 0.40283 | 56.4926 | -0.20142 | 56.6299 | -0.064087 | -0.050354 | -0.082397 | 0.091553 | 0.19226 | 0.20142 | -0.027466 | 0.25177 | 0.022888 | 0.54016 | 122.3373 | 0.24261 | 122.3511 | 122.3053 | 122.1771 | 122.168 | 122.1268 | -122.3465 | -122.2595 | 122.2 | 122.3007 | 56.3232 | 53.0273
1435.8438 | 122.5296 | -59.0286 | 63.1805 | -0.07164 | 0.00063028 | 0.061598 | 0.108 | 0.00059812 | -0.0035674 | -0.00010676 | -0.015564 | -0.003905 | 0.062256 | 0.061049 | -0.021664 | 0.0014141 | -0.00053411 | -2.9297 | 63.1439 | -59.1568 | 63.1943 | -58.6029 | -59.2026 | -2.6505 | -5.9052 | 63.1073 | -59.0652 | 63.2858 | -58.8181 | -59.0378 | -58.8043 | -0.12817 | -0.036621 | 0.013733 | 0.42572 | 56.3782 | -0.17395 | 56.5063 | -0.045777 | -0.036622 | -0.073242 | 0.10529 | 0.21057 | 0.2243 | -0.009156 | 0.26093 | 0.027466 | 0.55389 | 122.3511 | 0.24719 | 122.3511 | 122.3007 | 122.1725 | 122.1725 | 122.1359 | -122.3373 | -122.2458 | 122.2229 | 122.3145 | 56.0989 | 53.1235
1436.7812 | 122.5204 | -59.0881 | 63.1027 | -0.10979 | -0.00022432 | 0.06288 | 0.10778 | 0.0025207 | -0.001004 | -0.0035248 | -0.12543 | -0.0024096 | 0.064392 | 0.062117 | -0.02145 | 0.0039777 | 0.00032049 | -2.9984 | 63.0661 | -59.2667 | 63.0844 | -58.7677 | -59.3811 | -2.504 | -6.0333 | 63.0386 | -59.1431 | 63.1943 | -58.9645 | -59.1934 | -58.8913 | -0.17853 | -0.036621 | -0.01831 | 0.32044 | 56.5842 | -0.29297 | 56.7627 | -0.11444 | -0.054931 | -0.064087 | 0.091553 | 0.1236 | 0.19684 | -0.10529 | 0.25177 | -0.050354 | 0.49896 | 122.3511 | 0.17853 | 122.3373 | 122.3328 | 122.1817 | 122.1542 | 122.1268 | -122.3694 | -122.2458 | 122.1725 | 122.2824 | 56.0898 | 53.0548
1437.875 | 122.5342 | -59.0561 | 63.1485 | -0.13267 | -0.00043792 | 0.059676 | 0.10864 | 0.0025207 | -0.0016448 | -0.0035248 | -0.049133 | -0.0030506 | 0.061829 | 0.061263 | -0.019527 | 0.0016277 | 0.0018159 | -3.0579 | 63.1073 | -59.2072 | 63.176 | -58.6624 | -59.2392 | -2.536 | -5.9601 | 63.0615 | -59.1064 | 63.2309 | -58.8821 | -59.0973 | -58.9279 | -0.15106 | -0.041199 | 0.027465 | 0.39368 | 56.5201 | -0.18311 | 56.6711 | -0.032044 | -0.050354 | -0.086976 | 0.082397 | 0.17395 | 0.12817 | -0.041199 | 0.17853 | 0.009155 | 0.54474 | 122.3831 | 0.2243 | 122.3373 | 122.3145 | 122.168 | 122.1634 | 122.1176 | -122.3557 | -122.2549 | 122.2321 | 122.287 | 55.9982 | 53.096
1438.7969 | 122.4655 | -59.079 | 63.1027 | -0.10979 | 0.0023391 | 0.06053 | 0.10885 | 0.0010253 | -0.0007904 | -0.0013886 | -0.033874 | -0.0034778 | 0.063751 | 0.059554 | -0.0238 | 0.0014141 | 0.0022431 | -2.7512 | 63.0798 | -59.2163 | 63.1485 | -58.6533 | -59.2529 | -2.2751 | -5.7495 | 63.089 | -59.111 | 63.1668 | -58.9279 | -59.1568 | -58.992 | -0.13733 | -0.022888 | 0.045777 | 0.42572 | 56.8039 | -0.17395 | 56.9412 | -0.036621 | -0.032044 | -0.013733 | 0.064087 | 0.15106 | 0.086975 | -0.07782 | 0.11902 | -0.045776 | 0.56305 | 122.3648 | 0.18311 | 122.2778 | 122.2961 | 122.2 | 122.1588 | 122.168 | -122.319 | -122.2137 | 122.2275 | 122.2458 | 56.3278 | 53.3295
1439.7656 | 122.4335 | -59.0836 | 63.1531 | -0.1403 | -1.0718e-05 | 0.060103 | 0.10821 | 0.0018799 | 6.4004e-05 | -0.001175 | -0.14374 | -0.00070063 | 0.06546 | 0.064253 | -0.022304 | 0.0029095 | -0.0013885 | -2.6505 | 63.1073 | -59.2575 | 63.0066 | -58.8089 | -59.3994 | -2.5681 | -5.7724 | 63.1027 | -59.1614 | 63.1393 | -59.0378 | -59.2621 | -58.9874 | -0.17395 | -0.045776 | -0.14648 | 0.27466 | 56.5155 | -0.31586 | 56.6895 | -0.14191 | -0.07782 | -0.050354 | -0.013733 | 0.045776 | 0.09613 | -0.17853 | 0.17395 | -0.10071 | 0.44861 | 122.2641 | 0.1236 | 122.3007 | 122.3648 | 122.2641 | 122.1909 | 122.1863 | -122.4106 | -122.3145 | 122.0901 | 122.2229 | 56.4331 | 53.3112
1440.7656 | 122.5067 | -59.024 | 63.1989 | -0.094528 | 0.00063028 | 0.059676 | 0.10757 | -0.00068368 | -0.0020722 | -0.0024566 | 0.0027466 | -0.0017688 | 0.062897 | 0.05464 | -0.022518 | 0.00077333 | -0.0013885 | -2.9114 | 63.1531 | -59.1431 | 63.1577 | -58.6441 | -59.2438 | -2.8656 | -6.0425 | 63.1256 | -59.0744 | 63.2401 | -58.8776 | -59.0744 | -58.786 | -0.11902 | -0.045777 | -0.041199 | 0.37994 | 56.1584 | -0.21973 | 56.2775 | -0.10071 | -0.050354 | -0.073243 | 0.041198 | 0.14648 | 0.23804 | -0.050354 | 0.28839 | 0 | 0.49896 | 122.3007 | 0.19684 | 122.3145 | 122.2961 | 122.2 | 122.1771 | 122.1497 | -122.3419 | -122.2733 | 122.1817 | 122.2641 | 56.1127 | 52.9816
1441.8281 | 122.4884 | -59.0515 | 63.1668 | -0.06401 | -0.00043792 | 0.060744 | 0.10607 | -4.2682e-05 | -0.0031402 | -0.0030976 | 0.0088502 | -0.003905 | 0.062897 | 0.065962 | -0.022518 | -8.1274e-05 | 0.00032049 | -3.1036 | 63.1439 | -59.2163 | 63.121 | -58.6853 | -59.2941 | -2.8244 | -6.0287 | 63.1073 | -59.0973 | 63.2034 | -58.8867 | -59.111 | -58.8547 | -0.1648 | -0.022888 | -0.045776 | 0.36621 | 56.2271 | -0.24261 | 56.3919 | -0.077819 | -0.045776 | -0.059509 | 0.036621 | 0.16479 | 0.19684 | -0.059509 | 0.24262 | -0.013733 | 0.53101 | 122.3373 | 0.21057 | 122.3007 | 122.3602 | 122.2046 | 122.1954 | 122.1588 | -122.3831 | -122.2641 | 122.1725 | 122.2549 | 55.9479 | 53.0228
1442.7812 | 122.4243 | -59.0836 | 63.2126 | -0.07164 | 0.0021255 | 0.060316 | 0.10714 | 0.0016663 | -0.0033538 | -0.0026704 | -0.015564 | -0.0024096 | 0.062897 | 0.060622 | -0.021877 | 0.0012005 | 0.0022431 | -2.6917 | 63.1439 | -59.2026 | 63.1348 | -58.6716 | -59.2575 | -2.5818 | -6.0699 | 63.121 | -59.1064 | 63.1439 | -58.9691 | -59.2026 | -57.1426 | -0.11902 | -0.068664 | -0.077819 | 0.41199 | 56.5018 | -0.17395 | 56.6208 | -0.054931 | -0.022888 | -0.091552 | -0.068664 | 0.11444 | 1.9409 | -0.11902 | 1.9638 | -0.096131 | 0.53101 | 122.3373 | 0.13733 | 122.2504 | 122.3465 | 122.2275 | 122.2275 | 122.2046 | -122.4152 | -122.319 | 122.2183 | 122.2275 | 56.3919 | 53.0136
1443.8281 | 122.5433 | -59.0424 | 63.1485 | -0.06401 | 0.00041648 | 0.061385 | 0.10607 | 0.00081172 | 6.4004e-05 | -0.0033112 | -0.00030524 | -0.001128 | 0.063751 | 0.058272 | -0.0238 | 0.0024823 | 0.0016021 | -2.6962 | 63.1119 | -59.2209 | 63.1577 | -58.6441 | -59.2529 | -2.2614 | -5.864 | 63.0707 | -59.0973 | 63.2172 | -58.8821 | -59.1614 | -58.9783 | -0.17853 | -0.036622 | 0.009155 | 0.39825 | 56.781 | -0.21057 | 56.9595 | -0.032044 | -0.054932 | -0.07782 | 0.068664 | 0.16022 | 0.064087 | -0.11902 | 0.11902 | -0.064087 | 0.57678 | 122.3785 | 0.21515 | 122.3145 | 122.3328 | 122.168 | 122.1542 | 122.113 | -122.3694 | -122.2458 | 122.2 | 122.2595 | 56.3461 | 53.1784
1444.7656 | 122.5845 | -59.0607 | 63.1714 | -0.13267 | 0.0012711 | 0.062025 | 0.10821 | -0.0011109 | -0.0018586 | -0.0037384 | -0.091858 | -0.0043322 | 0.061829 | 0.06169 | -0.021877 | 0.00077333 | 0.0045929 | -2.7008 | 63.1165 | -59.2072 | 63.1943 | -58.6212 | -59.2804 | -2.5131 | -5.8868 | 63.0798 | -59.0744 | 63.2675 | -58.8776 | -59.3857 | -58.992 | -0.14648 | -0.054932 | 0.022888 | 0.43945 | 56.5475 | -0.21973 | 56.694 | -0.073243 | -0.013733 | -0.091553 | 0.09613 | 0.18311 | 0.068665 | -0.32501 | 0.082398 | -0.31128 | 0.58594 | 122.4014 | 0.19684 | 122.3419 | 122.3236 | 122.1542 | 122.1771 | 122.1405 | -122.3785 | -122.2458 | 122.2549 | 122.3282 | 56.3599 | 53.1738
1445.8281 | 122.4701 | -59.024 | 63.1577 | -0.10216 | 0.00041648 | 0.061171 | 0.10907 | 0.0018799 | 0.0009186 | -0.0026704 | -0.046081 | -0.0024096 | 0.063965 | 0.063613 | -0.021877 | 0.0018413 | -0.0013885 | -3.0945 | 63.1622 | -59.1888 | 63.1805 | -58.6304 | -59.2758 | -2.6093 | -6.015 | 63.1073 | -59.111 | 63.2217 | -58.9142 | -59.1385 | -58.9233 | -0.16479 | 0.004577 | 0.022888 | 0.39368 | 56.4148 | -0.25177 | 56.5796 | -0.086975 | -0.086975 | -0.050354 | 0.064087 | 0.10986 | 0.10071 | -0.11444 | 0.18768 | -0.027466 | 0.55847 | 122.3694 | 0.19684 | 122.3328 | 122.3511 | 122.2183 | 122.1863 | 122.1313 | -122.3465 | -122.2687 | 122.2046 | 122.2458 | 55.9296 | 53.009
1446.7656 | 122.5479 | -58.9508 | 63.1989 | -0.11742 | 0.0049027 | 0.060103 | 0.10864 | 0.0052979 | -0.0020722 | 0.0018158 | -0.079651 | -0.0028368 | 0.060761 | 0.06639 | -0.022304 | 0.0026959 | 0.0011749 | -2.7237 | 63.1805 | -59.1431 | 63.295 | -58.3603 | -59.1064 | -2.8152 | -5.8228 | 63.1577 | -59.0469 | 63.3179 | -58.8089 | -59.0561 | -58.7219 | -0.19226 | -0.018311 | 0.09613 | 0.59052 | 56.1356 | -0.15564 | 56.3278 | 0.036621 | -0.09613 | -0.041199 | 0.11902 | 0.14191 | 0.22888 | -0.10529 | 0.32501 | -0.009155 | 0.78278 | 122.438 | 0.23804 | 122.3648 | 122.3236 | 122.2046 | 122.1313 | 122.1085 | -122.3419 | -122.2458 | 122.2458 | 122.2687 | 56.2271 | 53.1281
1447.8438 | 122.4518 | -58.9874 | 63.2858 | -0.056381 | 0.00020288 | 0.060316 | 0.10885 | -0.0021789 | -0.0016448 | -0.0013886 | -0.073547 | -0.0028368 | 0.06482 | 0.061263 | -0.023373 | 0.0018413 | 0.0041657 | -2.7512 | 63.2767 | -59.1431 | 63.1805 | -58.6578 | -59.2484 | -2.5131 | -5.9692 | 63.2584 | -59.0424 | 63.2584 | -58.8913 | -59.1156 | -58.873 | -0.15564 | -0.009156 | -0.10529 | 0.32959 | 56.4743 | -0.26093 | 56.6299 | -0.10529 | -0.054931 | -0.027466 | -0.027466 | 0.096131 | 0.11444 | -0.12817 | 0.16937 | -0.073243 | 0.48523 | 122.3236 | 0.15106 | 122.3007 | 122.4197 | 122.3007 | 122.2641 | 122.2458 | -122.4289 | -122.3282 | 122.168 | 122.2458 | 56.2363 | 53.0182
1448.7656 | 122.5342 | -59.0515 | 63.1348 | -0.14793 | 0.00041648 | 0.062239 | 0.10885 | -0.00068368 | -0.0018586 | -0.001175 | -0.097961 | -0.0049732 | 0.065033 | 0.056349 | -0.023159 | 0.0012005 | 0.0026703 | -2.948 | 63.1165 | -59.198 | 63.1805 | -58.6441 | -59.2758 | -2.6184 | -6.1615 | 63.1165 | -59.0927 | 63.2767 | -58.9096 | -59.2255 | -59.0103 | -0.14648 | -0.018311 | 0.045776 | 0.40741 | 56.4331 | -0.2243 | 56.5796 | -0.07782 | -0.041198 | -0.018311 | 0.14191 | 0.14191 | 0.041199 | -0.17395 | 0.082397 | -0.13275 | 0.55389 | 122.3785 | 0.1831 | 122.3694 | 122.3145 | 122.2092 | 122.168 | 122.168 | -122.3328 | -122.2275 | 122.2321 | 122.3282 | 56.1035 | 52.89
1449.8281 | 122.5388 | -59.0378 | 63.1622 | -0.14793 | 0.00041648 | 0.059676 | 0.10672 | -4.2682e-05 | -0.0022858 | 0.00032044 | 0.018005 | -0.0036914 | 0.06482 | 0.055922 | -0.019955 | 0.0024823 | 0.0020295 | -3.4195 | 63.121 | -59.2438 | 63.1348 | -58.7036 | -59.317 | -2.6276 | -6.1981 | 63.0798 | -59.1431 | 63.2217 | -58.905 | -59.1339 | -58.873 | -0.20599 | -0.041198 | -0.027465 | 0.33417 | 56.4102 | -0.27924 | 56.6162 | -0.073243 | -0.10528 | -0.082397 | 0.05951 | 0.13275 | 0.1648 | -0.09613 | 0.27008 | 0.009155 | 0.54016 | 122.3785 | 0.23804 | 122.3648 | 122.3648 | 122.2229 | 122.1588 | 122.1176 | -122.406 | -122.3053 | 122.1725 | 122.2595 | 55.6183 | 52.8397
1450.7656 | 122.4289 | -59.0469 | 63.1714 | -0.1403 | 0.00084388 | 0.062666 | 0.10928 | 0.0014527 | -0.0014312 | -0.0018158 | -0.11932 | -0.002196 | 0.062042 | 0.062331 | -0.02145 | 0.0037641 | 0.00053409 | -2.9709 | 63.1851 | -59.23 | 63.0936 | -58.7494 | -59.3994 | -2.948 | -6.2393 | 63.1439 | -59.0973 | 63.1989 | -58.9828 | -59.2255 | -59.0057 | -0.18311 | 0.013733 | -0.07782 | 0.29755 | 56.0989 | -0.35248 | 56.282 | -0.16937 | -0.050354 | -0.027466 | 0.027466 | 0.064087 | 0.041199 | -0.17853 | 0.091553 | -0.12817 | 0.48065 | 122.3236 | 0.11444 | 122.2961 | 122.4152 | 122.2412 | 122.2321 | 122.1909 | -122.4014 | -122.2687 | 122.1405 | 122.2458 | 56.0761 | 52.8076
1451.8281 | 122.4655 | -59.0103 | 63.2446 | -0.12505 | -0.00065152 | 0.062666 | 0.11077 | 0.00038452 | -0.0005768 | 0.00032044 | -0.097961 | -0.00070063 | 0.064606 | 0.060408 | -0.022091 | 0.0026959 | 0.0060883 | -3.2043 | 63.1943 | -59.1888 | 63.089 | -58.7402 | -59.3445 | -2.8107 | -6.1432 | 63.176 | -59.1019 | 63.2401 | -58.9371 | -59.2026 | -58.9737 | -0.17853 | -0.050354 | -0.15564 | 0.27008 | 56.1996 | -0.33417 | 56.3782 | -0.15564 | -0.091553 | -0.068665 | -0.004578 | 0.073242 | 0.036621 | -0.19226 | 0.12817 | -0.10071 | 0.44861 | 122.2778 | 0.1648 | 122.3419 | 122.3831 | 122.2778 | 122.2046 | 122.1863 | -122.4335 | -122.3465 | 122.0993 | 122.2504 | 55.806 | 52.8671
1452.7656 | 122.5616 | -58.9554 | 63.2446 | -0.079269 | -0.00086512 | 0.060957 | 0.10714 | -0.00068368 | -0.0033538 | -0.0018158 | 0.039368 | -0.0041186 | 0.063111 | 0.058913 | -0.019741 | -0.00093567 | 0.0018159 | -2.9663 | 63.1668 | -59.111 | 63.2126 | -58.5846 | -59.1843 | -2.6184 | -6.0699 | 63.1668 | -59.0469 | 63.3499 | -58.7631 | -58.9554 | -58.6395 | -0.15564 | -0.07782 | -0.032044 | 0.37079 | 56.337 | -0.22888 | 56.4926 | -0.073242 | -0.091553 | -0.07782 | 0.10529 | 0.19226 | 0.31586 | 0 | 0.40741 | 0.091553 | 0.52643 | 122.3236 | 0.28381 | 122.3969 | 122.2778 | 122.2137 | 122.1222 | 122.1222 | -122.3557 | -122.2916 | 122.168 | 122.3053 | 55.9891 | 52.8854
1453.7656 | 122.3969 | -59.0424 | 63.2584 | -0.10216 | 0.0014847 | 0.062666 | 0.10907 | 0.0040161 | -0.0029266 | 0.00032044 | -0.12238 | -0.0041186 | 0.061402 | 0.06404 | -0.022945 | 0.0016277 | 0.00053409 | -2.948 | 63.1943 | -59.1934 | 63.1531 | -58.6945 | -59.3353 | -2.9022 | -6.395 | 63.1851 | -59.0881 | 63.1989 | -58.9828 | -59.2117 | -58.9005 | -0.15106 | -0.064087 | -0.10529 | 0.3479 | 56.1401 | -0.29297 | 56.2912 | -0.14191 | -0.045777 | -0.073242 | -0.059509 | 0.059509 | 0.14191 | -0.16937 | 0.18768 | -0.1236 | 0.49896 | 122.3465 | 0.10529 | 122.287 | 122.3877 | 122.2733 | 122.2366 | 122.2275 | -122.4518 | -122.3465 | 122.1954 | 122.2412 | 56.0944 | 52.6474
1454.7656 | 122.5388 | -58.96 | 63.2309 | -0.14793 | 0.0012711 | 0.062453 | 0.10821 | -0.00025628 | 0.001773 | -0.0018158 | -0.064392 | -0.0043322 | 0.063965 | 0.064253 | -0.022091 | 0.0014141 | 0.0013885 | -3.1403 | 63.1714 | -59.1339 | 63.0981 | -58.4564 | -58.9279 | -3.0212 | -6.0791 | 63.1668 | -59.024 | 63.3499 | -58.8272 | -59.0515 | -58.7814 | -0.17395 | -0.059509 | -0.13275 | 0.50354 | 55.9387 | 0.032044 | 56.1127 | 0.20599 | -0.064087 | -0.064087 | 0.11902 | 0.13275 | 0.17853 | -0.091553 | 0.24262 | -0.027466 | 0.67749 | 122.2321 | 0.19684 | 122.374 | 122.3053 | 122.1909 | 122.1313 | 122.1268 | -122.3648 | -122.2549 | 122.0581 | 122.3099 | 55.8197 | 52.8809
1455.8281 | 122.5388 | -58.9737 | 63.2172 | -0.12505 | 0.0021255 | 0.060744 | 0.10757 | -0.0015381 | -0.0029266 | -0.0033112 | -0.067444 | -0.002196 | 0.064179 | 0.059127 | -0.023159 | 0.0018413 | 0.0033111 | -3.067 | 63.2172 | -59.1248 | 63.2401 | -58.6304 | -59.1797 | -2.8244 | -6.3263 | 63.1668 | -59.0195 | 63.3362 | -58.8135 | -59.0744 | -58.8638 | -0.15106 | 0 | 0.022888 | 0.34332 | 56.1493 | -0.20599 | 56.3004 | -0.054931 | -0.045776 | -0.050354 | 0.11902 | 0.16022 | 0.10986 | -0.10071 | 0.15564 | -0.054932 | 0.49439 | 122.3648 | 0.20599 | 122.3557 | 122.3419 | 122.1863 | 122.1909 | 122.1405 | -122.3419 | -122.2366 | 122.2137 | 122.3099 | 55.9067 | 52.6474
1456.7656 | 122.493 | -58.9966 | 63.2401 | -0.094528 | 0.0023391 | 0.06053 | 0.10992 | 0.0033753 | -0.0033538 | -0.001175 | -0.082703 | -0.0017688 | 0.064606 | 0.059127 | -0.020809 | 0.0029095 | 0.0013885 | -3.0762 | 63.2309 | -59.1705 | 63.1531 | -58.667 | -59.3033 | -3.0075 | -6.3126 | 63.1577 | -59.0561 | 63.2858 | -58.8959 | -59.1202 | -58.8181 | -0.17395 | -0.009155 | -0.086975 | 0.32959 | 55.9891 | -0.3067 | 56.163 | -0.13275 | -0.059509 | -0.082397 | 0.045777 | 0.10071 | 0.17853 | -0.1236 | 0.23804 | -0.064087 | 0.50354 | 122.3236 | 0.16022 | 122.3419 | 122.4014 | 122.2137 | 122.2275 | 122.1542 | -122.4106 | -122.2961 | 122.1497 | 122.2824 | 55.9204 | 52.684
1457.7656 | 122.4976 | -58.9737 | 63.2538 | -0.086899 | 0.0025529 | 0.05818 | 0.10821 | 0.0010253 | -0.0029266 | -0.002884 | 0.027161 | -0.005614 | 0.061615 | 0.057845 | -0.022732 | 0.0014141 | 0.00010689 | -3.4241 | 63.208 | -59.1202 | 63.1805 | -58.6029 | -59.2392 | -3.0579 | -6.134 | 63.1851 | -59.0424 | 63.2904 | -58.8593 | -59.0515 | -58.7997 | -0.14648 | -0.045776 | -0.073242 | 0.37079 | 55.9158 | -0.2655 | 56.0623 | -0.11902 | -0.068664 | -0.068664 | 0.036621 | 0.11444 | 0.17395 | -0.07782 | 0.24261 | -0.009156 | 0.51727 | 122.3007 | 0.1831 | 122.3328 | 122.3282 | 122.2275 | 122.1817 | 122.1588 | -122.374 | -122.2961 | 122.1542 | 122.2641 | 55.5496 | 52.8397
1458.7656 | 122.4655 | -59.079 | 63.1989 | -0.094528 | -0.0012923 | 0.063521 | 0.10864 | 0.0014527 | -0.0048492 | -0.001175 | -0.10101 | -0.00091423 | 0.063751 | 0.062972 | -0.021877 | 0.0022687 | 0.0020295 | -3.0396 | 63.1714 | -59.2392 | 63.1027 | -58.7631 | -59.3857 | -3.4332 | -6.3538 | 63.1577 | -59.1156 | 63.208 | -58.9645 | -59.2163 | -58.8867 | -0.16022 | -0.027466 | -0.096131 | 0.31586 | 55.6458 | -0.3067 | 55.806 | -0.14648 | -0.036622 | -0.041199 | 0.009155 | 0.11444 | 0.19226 | -0.13733 | 0.22888 | -0.10071 | 0.47607 | 122.3419 | 0.15106 | 122.3236 | 122.4106 | 122.2733 | 122.2504 | 122.2366 | -122.4381 | -122.3145 | 122.1817 | 122.287 | 56.0394 | 52.7252
1459.7656 | 122.4472 | -59.0515 | 63.2126 | -0.10216 | 0.00063028 | 0.06288 | 0.10949 | 0.0063659 | -0.002713 | -0.00096136 | -0.10101 | -0.002196 | 0.063751 | 0.066817 | -0.021664 | 0.0031231 | 0.00074769 | -3.2181 | 63.2126 | -59.2072 | 63.0249 | -58.4152 | -59.111 | -3.3051 | -6.2988 | 63.1989 | -59.111 | 63.176 | -59.0057 | -59.2621 | -58.9828 | -0.15564 | 0 | -0.18768 | 0.63629 | 55.7465 | -0.059509 | 55.9021 | 0.09613 | -0.059509 | -0.013732 | -0.036621 | 0.045777 | 0.068665 | -0.21057 | 0.12817 | -0.15106 | 0.79193 | 122.2321 | 0.10529 | 122.287 | 122.4197 | 122.3099 | 122.2641 | 122.2504 | -122.4197 | -122.3236 | 122.0764 | 122.2275 | 55.8334 | 52.7527
1460.7656 | 122.4335 | -59.0378 | 63.2629 | -0.12505 | 0.0012711 | 0.059889 | 0.10864 | 0.0020935 | -0.0012176 | 0.0020294 | 0.097351 | -0.0019824 | 0.062042 | 0.064681 | -0.019955 | 0.0026959 | 0.00032049 | -3.5843 | 63.2401 | -59.2026 | 63.089 | -58.7494 | -59.8114 | -3.7445 | -6.1615 | 63.2309 | -59.0836 | 63.2309 | -58.9691 | -59.2346 | -58.9233 | -0.16479 | -0.022888 | -0.17395 | 0.28839 | 55.2933 | -0.77362 | 55.4581 | -0.60882 | -0.045776 | -0.032043 | -0.032043 | 0.068665 | 0.11444 | -0.19684 | 0.16022 | -0.15106 | 0.45319 | 122.2916 | 0.11444 | 122.3145 | 122.4426 | 122.3145 | 122.2778 | 122.2687 | -122.4655 | -122.3465 | 122.1268 | 122.2687 | 55.4535 | 52.8763
1461.7656 | 122.5433 | -59.0057 | 63.2034 | -0.1403 | -0.0017197 | 0.061812 | 0.108 | -0.0013245 | -0.0037812 | 0.00053404 | -0.06134 | -0.0015552 | 0.063965 | 0.064894 | -0.021236 | 0.0031231 | 0.00010689 | -3.6438 | 63.1943 | -59.1705 | 63.1577 | -58.6624 | -59.3033 | -3.891 | -5.9692 | 63.1393 | -59.1019 | 63.2721 | -58.8684 | -59.1156 | -58.8089 | -0.16479 | -0.009155 | -0.045776 | 0.34332 | 55.1147 | -0.29755 | 55.2795 | -0.13275 | -0.096131 | -0.064087 | 0.068665 | 0.13733 | 0.19684 | -0.10986 | 0.29297 | -0.013733 | 0.50812 | 122.3282 | 0.23346 | 122.374 | 122.3648 | 122.2412 | 122.2 | 122.1451 | -122.374 | -122.3053 | 122.1634 | 122.2778 | 55.3619 | 53.0365
1462.7656 | 122.4976 | -59.0195 | 63.2034 | -0.15556 | 0.0014847 | 0.059676 | 0.10864 | 0.0027343 | -0.0018586 | -0.0016022 | 0.033264 | -0.0047594 | 0.063111 | 0.056777 | -0.020595 | 0.00013253 | -0.0011749 | -3.3646 | 63.2492 | -59.1202 | 63.1989 | -58.6212 | -59.2575 | -3.598 | -5.8594 | 63.1622 | -59.0607 | 63.2675 | -58.8959 | -59.1019 | -58.8272 | -0.10071 | 0.045777 | -0.004577 | 0.39825 | 55.4214 | -0.23804 | 55.5222 | -0.13733 | -0.041199 | -0.041199 | 0.064087 | 0.1236 | 0.19226 | -0.082398 | 0.23346 | -0.041199 | 0.49896 | 122.319 | 0.16479 | 122.3282 | 122.3694 | 122.2229 | 122.2687 | 122.1817 | -122.3236 | -122.2641 | 122.2183 | 122.287 | 55.6549 | 53.1601
1463.7656 | 122.4472 | -59.0286 | 63.2538 | -0.10979 | 0.00041648 | 0.060744 | 0.11035 | 0.0014527 | -0.0029266 | -0.002243 | -0.097961 | -0.0024096 | 0.063538 | 0.06404 | -0.021664 | 0.0031231 | 0.0043793 | -3.0762 | 63.2309 | -59.1705 | 63.1256 | -58.7082 | -59.3399 | -3.5385 | -6.2668 | 63.2172 | -59.0607 | 63.2584 | -58.9371 | -59.1614 | -58.6807 | -0.14191 | -0.022888 | -0.12817 | 0.32043 | 55.4901 | -0.31128 | 55.632 | -0.16937 | -0.032044 | -0.036621 | 0.004578 | 0.091552 | 0.3479 | -0.13275 | 0.37994 | -0.10071 | 0.46234 | 122.2961 | 0.1236 | 122.319 | 122.4014 | 122.2778 | 122.2595 | 122.2458 | -122.4243 | -122.3145 | 122.1542 | 122.287 | 55.9525 | 52.7618
1464.7656 | 122.5525 | -58.9371 | 63.2629 | -0.094528 | -0.00022432 | 0.059462 | 0.10907 | -0.00025628 | -0.0014312 | 0.001175 | -0.079651 | -0.002196 | 0.063538 | 0.061904 | -0.02145 | 0.0039777 | 0.0011749 | -3.2776 | 63.2675 | -59.1156 | 63.2263 | -58.6121 | -59.2529 | -3.6896 | -5.9784 | 63.2217 | -59.0149 | 63.3636 | -58.8409 | -59.0652 | -58.7814 | -0.17853 | 0.004578 | -0.036621 | 0.32501 | 55.2475 | -0.31586 | 55.426 | -0.13733 | -0.07782 | -0.041198 | 0.10071 | 0.096131 | 0.15564 | -0.12817 | 0.23346 | -0.050354 | 0.50354 | 122.3419 | 0.17395 | 122.3785 | 122.3831 | 122.2366 | 122.2046 | 122.1588 | -122.3785 | -122.2778 | 122.1634 | 122.3007 | 55.6595 | 52.9587
1465.7656 | 122.5616 | -58.9325 | 63.295 | -0.13267 | 0.00063028 | 0.059676 | 0.10907 | -0.00068368 | 0.000705 | -0.0052338 | 0.057678 | -0.0036914 | 0.062897 | 0.05934 | -0.021023 | 0.0029095 | 0.0041657 | -3.1403 | 63.2355 | -59.1019 | 63.2996 | -58.5068 | -59.3399 | -4.0512 | -5.9463 | 63.2309 | -58.9691 | 63.4186 | -58.7723 | -58.992 | -58.7265 | -0.16937 | -0.059509 | 0.004578 | 0.42572 | 54.8813 | -0.40741 | 55.0507 | -0.23804 | -0.036621 | -0.064087 | 0.1236 | 0.16022 | 0.20599 | -0.059509 | 0.24262 | -0.022888 | 0.59509 | 122.4014 | 0.19684 | 122.3877 | 122.3373 | 122.2 | 122.168 | 122.1634 | -122.3969 | -122.2641 | 122.2321 | 122.3511 | 55.7922 | 52.9861
1466.7656 | 122.4655 | -58.9966 | 63.2904 | -0.086899 | -0.00022432 | 0.062239 | 0.11142 | -0.00046988 | -0.0022858 | 0.00096124 | -0.088806 | -0.0028368 | 0.064179 | 0.064894 | -0.022091 | 0.0029095 | 0.0022431 | -2.9022 | 63.295 | -59.1431 | 63.1714 | -58.6624 | -59.2896 | -3.5522 | -5.777 | 63.2584 | -59.0424 | 63.2812 | -58.9188 | -59.1751 | -58.8593 | -0.14648 | 0.004578 | -0.11902 | 0.33417 | 55.4443 | -0.29297 | 55.5908 | -0.14649 | -0.045776 | -0.032043 | -0.009155 | 0.07782 | 0.13733 | -0.17853 | 0.1831 | -0.13275 | 0.48065 | 122.3145 | 0.1236 | 122.3236 | 122.438 | 122.3007 | 122.2916 | 122.2549 | -122.4335 | -122.3328 | 122.168 | 122.2778 | 56.0944 | 53.2196
1467.7656 | 122.5571 | -58.9508 | 63.2904 | -0.094528 | -0.0010787 | 0.061385 | 0.108 | 0.0042297 | -0.0024994 | -0.001175 | -0.076599 | -0.0041186 | 0.065674 | 0.063613 | -0.023373 | 0.0022687 | -0.00096131 | -2.8931 | 63.2858 | -59.1385 | 63.2217 | -58.6212 | -59.2392 | -3.4744 | -5.7999 | 63.2217 | -59.0103 | 63.3453 | -58.8409 | -59.0561 | -58.786 | -0.18768 | -0.004577 | -0.068664 | 0.32959 | 55.4764 | -0.28839 | 55.6641 | -0.10071 | -0.059509 | -0.068664 | 0.054932 | 0.10986 | 0.16479 | -0.10529 | 0.2243 | -0.045776 | 0.51727 | 122.3602 | 0.16937 | 122.3557 | 122.4243 | 122.2321 | 122.2366 | 122.1725 | -122.4289 | -122.3007 | 122.1725 | 122.2961 | 56.0577 | 53.1509
1468.7656 | 122.4564 | -58.9783 | 63.2996 | -0.10979 | 0.0012711 | 0.059889 | 0.10864 | 0.0027343 | -0.0018586 | -0.0035248 | -0.091858 | -0.0028368 | 0.063751 | 0.062545 | -0.022518 | 0.0026959 | 0.0011749 | -2.8564 | 63.2996 | -59.1431 | 63.1622 | -58.6807 | -59.2804 | -3.4927 | -5.5939 | 63.2538 | -59.0149 | 63.2812 | -58.9233 | -59.1385 | -58.8501 | -0.16479 | 0 | -0.13733 | 0.29755 | 55.4855 | -0.30213 | 55.6503 | -0.13733 | -0.036622 | -0.045777 | -0.018311 | 0.054931 | 0.12817 | -0.16022 | 0.16479 | -0.1236 | 0.46234 | 122.3053 | 0.091553 | 122.2961 | 122.4426 | 122.2687 | 122.2778 | 122.2321 | -122.4426 | -122.3145 | 122.1405 | 122.2595 | 56.1218 | 53.3844
1469.7656 | 122.58 | -58.9005 | 63.2996 | -0.11742 | -1.0718e-05 | 0.061171 | 0.10693 | -0.0013245 | 0.0013458 | -0.0018158 | -0.039978 | -0.0017688 | 0.061615 | 0.060408 | -0.021877 | 0.0018413 | 0.0024567 | -2.8473 | 63.2446 | -59.0744 | 63.2996 | -58.5342 | -59.1568 | -3.3966 | -5.6854 | 63.2355 | -58.9966 | 63.4323 | -58.8547 | -59.0378 | -58.7311 | -0.17395 | -0.054932 | 0 | 0.36621 | 55.5038 | -0.25635 | 55.6778 | -0.082397 | -0.09613 | -0.064087 | 0.13275 | 0.045777 | 0.16937 | -0.13733 | 0.2655 | -0.041199 | 0.54016 | 122.374 | 0.14191 | 122.4289 | 122.319 | 122.2321 | 122.1451 | 122.1359 | -122.374 | -122.2961 | 122.2 | 122.3328 | 56.0532 | 53.215
1470.7656 | 122.5159 | -58.9188 | 63.3087 | -0.11742 | 0.00063028 | 0.060316 | 0.10992 | 0.0038025 | -0.0033538 | -0.001175 | -0.052185 | -0.0043322 | 0.06247 | 0.05934 | -0.022518 | 0.0020551 | -0.00096131 | -3.273 | 63.327 | -59.0836 | 63.2446 | -58.5892 | -59.2346 | -3.772 | -5.7083 | 63.2629 | -58.96 | 63.3682 | -58.8409 | -59.0561 | -58.4885 | -0.16479 | 0.01831 | -0.064087 | 0.32959 | 55.1468 | -0.31586 | 55.3116 | -0.15106 | -0.041199 | -0.045777 | 0.059509 | 0.07782 | 0.4303 | -0.13733 | 0.4715 | -0.09613 | 0.49439 | 122.3282 | 0.11902 | 122.3282 | 122.4106 | 122.2229 | 122.2458 | 122.1817 | -122.3923 | -122.2687 | 122.1634 | 122.287 | 55.6458 | 53.2104
1471.7656 | 122.5113 | -58.9508 | 63.2996 | -0.10216 | 0.0014847 | 0.061171 | 0.10842 | 0.00017092 | -0.0005768 | -0.002243 | 0.027161 | -0.0028368 | 0.06247 | 0.055281 | -0.022091 | 0.0031231 | 0.0050201 | -3.2364 | 63.2492 | -59.0607 | 63.2538 | -58.5617 | -59.2117 | -3.685 | -5.4153 | 63.2355 | -59.0057 | 63.3224 | -58.8409 | -59.0424 | -58.7723 | -0.10986 | -0.050354 | -0.045777 | 0.3891 | 55.2658 | -0.26093 | 55.3757 | -0.15106 | -0.054931 | -0.064087 | 0.022888 | 0.10986 | 0.17853 | -0.091552 | 0.23346 | -0.036621 | 0.49896 | 122.3145 | 0.1648 | 122.3282 | 122.3099 | 122.2412 | 122.2 | 122.1863 | -122.3602 | -122.3053 | 122.2046 | 122.2733 | 55.7144 | 53.5355
1472.8438 | 122.4792 | -58.9691 | 63.3545 | -0.06401 | 0.0012711 | 0.059676 | 0.10821 | 0.0027343 | -0.0029266 | 0.00074764 | -0.067444 | -0.0019824 | 0.062256 | 0.05934 | -0.023373 | 0.0029095 | -0.0011749 | -3.3371 | 63.3224 | -59.0973 | 63.2492 | -58.6075 | -59.2026 | -3.9185 | -5.4108 | 63.2858 | -59.0149 | 63.3316 | -58.8318 | -59.0927 | -58.8089 | -0.12817 | -0.032043 | -0.10529 | 0.36163 | 55.0507 | -0.23346 | 55.1788 | -0.10529 | -0.045777 | -0.068664 | -0.022888 | 0.13733 | 0.16022 | -0.1236 | 0.20599 | -0.077819 | 0.48981 | 122.3465 | 0.18311 | 122.3465 | 122.4197 | 122.3007 | 122.2916 | 122.2549 | -122.4518 | -122.3694 | 122.2183 | 122.3007 | 55.632 | 53.5583
1473.7656 | 122.5571 | -58.9737 | 63.2629 | -0.1403 | 0.0010575 | 0.061385 | 0.11013 | -4.2682e-05 | -0.002713 | -0.0035248 | -0.015564 | -0.003905 | 0.06012 | 0.063399 | -0.022091 | 0.0016277 | 0.0028839 | -3.3005 | 63.2446 | -59.0927 | 63.2721 | -58.5434 | -59.1843 | -3.7857 | -5.3375 | 63.2172 | -59.0195 | 63.3728 | -58.8181 | -59.0332 | -58.7769 | -0.11902 | -0.01831 | 0.009156 | 0.4303 | 55.188 | -0.21057 | 55.307 | -0.091553 | -0.045776 | -0.045776 | 0.10986 | 0.15564 | 0.19684 | -0.059509 | 0.24262 | -0.013733 | 0.54932 | 122.3648 | 0.20142 | 122.3923 | 122.3373 | 122.2366 | 122.2183 | 122.1909 | -122.3557 | -122.2824 | 122.2458 | 122.3465 | 55.6732 | 53.6362
1474.8281 | 122.4976 | -58.7952 | 63.4598 | -0.11742 | 0.0025529 | 0.061598 | 0.10885 | -0.0013245 | -0.0016448 | -0.0018158 | 0.014954 | -0.0017688 | 0.063965 | 0.057418 | -0.022732 | 0.0029095 | 0.0018159 | -3.1036 | 63.4323 | -58.9005 | 63.4552 | -58.3466 | -58.9874 | -3.7674 | -5.2094 | 63.3957 | -58.8455 | 63.4827 | -58.7036 | -58.8821 | -58.6853 | -0.10529 | -0.027466 | -0.004578 | 0.44861 | 55.0278 | -0.19226 | 55.1331 | -0.086975 | -0.050354 | -0.064087 | 0.022888 | 0.091553 | 0.10986 | -0.086975 | 0.16022 | -0.036621 | 0.55389 | 122.3557 | 0.14191 | 122.3282 | 122.3328 | 122.2412 | 122.2275 | 122.1909 | -122.3602 | -122.3053 | 122.2504 | 122.2778 | 55.6915 | 53.5858
1475.7656 | 122.5433 | -58.873 | 63.3865 | -0.056381 | -0.00022432 | 0.061385 | 0.11056 | 0.0038025 | -0.0016448 | -0.0035248 | -0.067444 | -0.00048703 | 0.063965 | 0.06404 | -0.023373 | 0.0022687 | 0.0041657 | -3.2272 | 63.3636 | -59.0378 | 63.3087 | -58.5068 | -59.1568 | -4.0604 | -5.3467 | 63.3179 | -58.9279 | 63.4506 | -58.754 | -58.9462 | -58.7036 | -0.1648 | -0.022889 | -0.07782 | 0.36621 | 54.8126 | -0.28381 | 54.9774 | -0.11902 | -0.054931 | -0.068665 | 0.064087 | 0.11902 | 0.16937 | -0.073242 | 0.2243 | -0.018311 | 0.53101 | 122.3465 | 0.17395 | 122.3785 | 122.4014 | 122.2458 | 122.2366 | 122.1909 | -122.4243 | -122.3145 | 122.1817 | 122.3236 | 55.6458 | 53.5263
1476.8281 | 122.6028 | -58.7494 | 63.4964 | -0.14793 | 0.0021255 | 0.061385 | 0.108 | 0.0010253 | -0.0003632 | -0.0013886 | 0.027161 | -0.0032642 | 0.063965 | 0.050795 | -0.021664 | 0.0018413 | 0.0013885 | -2.916 | 63.4827 | -58.905 | 63.4323 | -58.3191 | -59.0057 | -3.9276 | -5.1407 | 63.4186 | -58.786 | 63.5376 | -58.6487 | -58.8409 | -58.461 | -0.15564 | -0.013733 | -0.064087 | 0.4303 | 54.8218 | -0.25635 | 54.9774 | -0.10071 | -0.036621 | -0.07782 | 0.041199 | 0.10071 | 0.28839 | -0.091552 | 0.32501 | -0.054931 | 0.58594 | 122.3373 | 0.13733 | 122.3236 | 122.3877 | 122.2046 | 122.2321 | 122.168 | -122.4014 | -122.2824 | 122.1817 | 122.287 | 55.8334 | 53.6087
1477.7656 | 122.5616 | -58.3099 | 63.9313 | -0.12505 | -0.00065152 | 0.059462 | 0.10586 | -4.2682e-05 | -0.0016448 | -0.00096136 | 0.033264 | -0.0030506 | 0.062256 | 0.056136 | -0.023373 | 0.0020551 | 0.0030975 | -3.067 | 63.8809 | -58.4381 | 63.8351 | -57.7148 | -58.5846 | -3.8361 | -5.0629 | 63.8306 | -58.3878 | 63.9816 | -58.168 | -58.374 | -58.1497 | -0.12817 | -0.050354 | -0.09613 | 0.59509 | 54.4739 | -0.27466 | 54.6021 | -0.14648 | -0.077819 | -0.10071 | 0.050354 | 0.14191 | 0.16022 | -0.064086 | 0.23804 | 0.013733 | 0.72327 | 122.2733 | 0.21973 | 122.3694 | 122.319 | 122.2183 | 122.1909 | 122.1405 | -122.3694 | -122.319 | 122.1451 | 122.2916 | 55.2429 | 53.2471
1478.8281 | 122.4472 | -57.8476 | 64.3845 | -0.079269 | -0.0015061 | 0.06053 | 0.10885 | -0.00068368 | 0.0011322 | -0.0018158 | 0.0057984 | -0.0026232 | 0.063324 | 0.059981 | -0.024227 | 0.00077333 | 0.0020295 | -2.8244 | 64.3433 | -58.0124 | 64.3387 | -57.0053 | -58.1268 | -3.7537 | -4.8477 | 64.3112 | -57.9254 | 64.4119 | -57.7194 | -57.7789 | -57.5226 | -0.1648 | -0.041198 | -0.045776 | 0.84228 | 54.0939 | -0.27924 | 54.2587 | -0.11444 | -0.07782 | -0.073242 | 0.027466 | 0.12817 | 0.32501 | 0.068664 | 0.40283 | 0.14648 | 1.0071 | 122.3511 | 0.20599 | 122.3373 | 122.3557 | 122.2366 | 122.1909 | 122.1588 | -122.3969 | -122.3099 | 122.1863 | 122.2595 | 55.0232 | 52.9999
1479.7656 | 122.5296 | -57.9391 | 64.3204 | -0.11742 | 0.00041648 | 0.06053 | 0.10842 | -0.0019653 | -0.001004 | -0.0020294 | -0.00030524 | -0.002196 | 0.060761 | 0.054 | -0.022945 | 0.0031231 | 0.0013885 | -2.6413 | 64.2609 | -58.0902 | 64.2288 | -57.1838 | -58.1863 | -3.653 | -4.8981 | 64.2563 | -58.0032 | 64.3387 | -57.8156 | -58.017 | -57.7744 | -0.15106 | -0.05951 | -0.091553 | 0.75531 | 54.2862 | -0.24719 | 54.4373 | -0.09613 | -0.064087 | -0.064087 | 0.01831 | 0.1236 | 0.1648 | -0.07782 | 0.22888 | -0.013733 | 0.90637 | 122.319 | 0.18768 | 122.3419 | 122.3511 | 122.2595 | 122.2 | 122.1954 | -122.4106 | -122.3236 | 122.168 | 122.2778 | 55.2979 | 53.0411
1480.8281 | 122.6212 | -57.5363 | 64.7369 | -0.07164 | 0.00063028 | 0.061598 | 0.11035 | -0.00046988 | -0.0046356 | -0.0016022 | -0.015564 | -0.003905 | 0.061188 | 0.064253 | -0.023159 | 0.00098693 | 0.0045929 | -2.6642 | 64.6317 | -57.7194 | 64.6545 | -56.5933 | -57.8339 | -3.4424 | -4.9988 | 64.6133 | -57.6279 | 64.7415 | -57.4539 | -57.6508 | -57.3807 | -0.1831 | -0.10528 | -0.082397 | 0.94299 | 54.0939 | -0.29755 | 54.277 | -0.11444 | -0.091553 | -0.1236 | 0.004578 | 0.082398 | 0.15564 | -0.11444 | 0.24719 | -0.022888 | 1.1261 | 122.374 | 0.17395 | 122.3694 | 122.3511 | 122.2412 | 122.168 | 122.1497 | -122.4564 | -122.3648 | 122.1909 | 122.2778 | 54.8721 | 52.5375
1481.7656 | 122.5296 | -57.4219 | 64.8193 | -0.10216 | 0.0025529 | 0.061598 | 0.10821 | -0.0017517 | 0.0004914 | -0.0013886 | -0.055237 | -0.002196 | 0.061188 | 0.056777 | -0.021664 | 0.0041913 | 0.0030975 | -2.4261 | 64.7415 | -57.5958 | 64.8285 | -56.3461 | -57.692 | -3.1219 | -4.9255 | 64.7232 | -57.4951 | 64.9017 | -57.3074 | -57.5134 | -57.2479 | -0.17395 | -0.07782 | 0.009155 | 1.0757 | 54.2999 | -0.27008 | 54.4739 | -0.096131 | -0.073242 | -0.09613 | 0.082397 | 0.11444 | 0.17395 | -0.091553 | 0.24719 | -0.018311 | 1.2497 | 122.4243 | 0.18768 | 122.3969 | 122.3373 | 122.2183 | 122.1634 | 122.1451 | -122.4152 | -122.3145 | 122.2504 | 122.3236 | 54.9957 | 52.4963
1482.8438 | 122.4518 | -57.5043 | 64.8102 | -0.033493 | -0.00065152 | 0.060103 | 0.11099 | -0.0038879 | -0.0016448 | -0.00074776 | -0.067444 | -0.0062548 | 0.061402 | 0.059767 | -0.023586 | 0.0018413 | 0.00053409 | -2.2476 | 64.801 | -57.637 | 64.6866 | -56.5155 | -57.7789 | -2.9663 | -4.6463 | 64.7919 | -57.5043 | 64.7232 | -57.4173 | -57.6553 | -57.4539 | -0.13275 | -0.009156 | -0.1236 | 0.98877 | 54.538 | -0.27466 | 54.6707 | -0.14191 | 0 | -0.018311 | -0.086975 | 0.086975 | 0.050354 | -0.15106 | 0.050354 | -0.15106 | 1.1215 | 122.3236 | 0.086975 | 122.2275 | 122.438 | 122.2961 | 122.3053 | 122.2961 | -122.4472 | -122.3145 | 122.1909 | 122.2275 | 55.2567 | 52.858
1483.7656 | 122.5616 | -57.3944 | 64.8376 | -0.086899 | 0.00041648 | 0.063094 | 0.10714 | 0.0016663 | -0.002713 | -0.0013886 | -0.06134 | -0.003905 | 0.062683 | 0.058486 | -0.023586 | 0.0022687 | 0.00010689 | -2.2476 | 64.8331 | -57.5317 | 64.8788 | -56.2637 | -57.6416 | -2.9434 | -4.8981 | 64.7919 | -57.4493 | 64.92 | -57.28 | -57.4768 | -57.2205 | -0.13733 | -0.004577 | 0.041199 | 1.1307 | 54.451 | -0.24719 | 54.5883 | -0.10986 | -0.054932 | -0.045776 | 0.082398 | 0.11444 | 0.17395 | -0.082398 | 0.22888 | -0.027466 | 1.268 | 122.4106 | 0.16937 | 122.3694 | 122.3648 | 122.2412 | 122.2275 | 122.1863 | -122.3694 | -122.287 | 122.2733 | 122.3145 | 55.1468 | 52.4963
1484.8281 | 122.5708 | -56.8817 | 65.3687 | -0.10979 | 0.0016983 | 0.061171 | 0.11013 | 0.0040161 | -0.0033538 | -0.0018158 | 0.021057 | -0.003905 | 0.060974 | 0.058272 | -0.021664 | 0.0016277 | 0.0050201 | -1.9775 | 65.3183 | -57.0419 | 65.387 | -55.5359 | -57.4265 | -3.1403 | -4.7653 | 65.3046 | -56.955 | 65.4694 | -56.7535 | -56.9504 | -56.7123 | -0.16022 | -0.050354 | 0.018311 | 1.3458 | 53.7415 | -0.54474 | 53.9017 | -0.38452 | -0.073242 | -0.064087 | 0.10071 | 0.12817 | 0.16937 | -0.068664 | 0.24262 | 0.004578 | 1.506 | 122.4289 | 0.20142 | 122.4243 | 122.3602 | 122.2595 | 122.2 | 122.1863 | -122.4106 | -122.3236 | 122.2687 | 122.3511 | 54.9042 | 52.1164
1485.7656 | 122.525 | -57.2662 | 64.9933 | -0.10216 | 0.00084388 | 0.062666 | 0.10821 | 0.00038452 | 0.000705 | -0.0024566 | -0.030823 | -0.0028368 | 0.061829 | 0.064253 | -0.022518 | -0.00029487 | -0.00074771 | -1.9501 | 65.0299 | -57.3349 | 65.0345 | -56.1218 | -57.486 | -3.0258 | -4.7104 | 64.9567 | -57.3029 | 65.0528 | -57.1335 | -57.3395 | -57.0557 | -0.068665 | 0.036621 | 0.041199 | 1.1444 | 54.2404 | -0.21973 | 54.3091 | -0.15106 | -0.036621 | -0.036621 | 0.059509 | 0.13275 | 0.21057 | -0.073243 | 0.24719 | -0.036622 | 1.2131 | 122.3694 | 0.16937 | 122.3557 | 122.3648 | 122.2595 | 122.2961 | 122.2229 | -122.3282 | -122.2961 | 122.3007 | 122.319 | 55.3162 | 52.5558
1486.8281 | 122.5662 | -56.3828 | 65.8218 | -0.094528 | 0.00084388 | 0.06288 | 0.10778 | -0.0015381 | -0.0018586 | -0.00010676 | -0.064392 | -0.0045458 | 0.062256 | 0.064681 | -0.021664 | 0.0014141 | 0.00053409 | -1.387 | 65.7944 | -56.5475 | 65.8768 | -54.9774 | -56.6437 | -2.6871 | -4.4083 | 65.7944 | -56.4789 | 65.95 | -56.2592 | -56.4835 | -56.2271 | -0.16479 | -0.027465 | 0.054932 | 1.4053 | 53.6957 | -0.26093 | 53.8605 | -0.096131 | -0.096131 | -0.027465 | 0.12817 | 0.1236 | 0.15564 | -0.10071 | 0.25177 | -0.004577 | 1.5701 | 122.4243 | 0.21973 | 122.4289 | 122.3419 | 122.2733 | 122.1771 | 122.1771 | -122.3694 | -122.3007 | 122.2595 | 122.3328 | 54.9957 | 51.9745
1487.7656 | 122.5891 | -57.2708 | 64.9933 | -0.086899 | 0.0021255 | 0.061171 | 0.10949 | -0.0019653 | -0.0033538 | -0.0024566 | 0.018005 | -0.0019824 | 0.062256 | 0.058913 | -0.022945 | -8.1274e-05 | 0.00032049 | -1.7578 | 64.9704 | -57.4356 | 64.9612 | -56.2088 | -57.4997 | -2.8702 | -4.5959 | 64.9338 | -57.3257 | 65.0574 | -57.1198 | -57.3395 | -57.1014 | -0.1648 | -0.022888 | -0.032043 | 1.062 | 54.4006 | -0.22888 | 54.5654 | -0.064087 | -0.054932 | -0.059509 | 0.064087 | 0.15106 | 0.16937 | -0.068665 | 0.22431 | -0.013733 | 1.2268 | 122.3969 | 0.20599 | 122.3831 | 122.406 | 122.2595 | 122.2412 | 122.2046 | -122.4289 | -122.319 | 122.2321 | 122.3282 | 55.513 | 52.6749
1488.8281 | 122.5433 | -57.2433 | 65.0528 | -0.20134 | 0.0025529 | 0.060744 | 0.10778 | -0.0030335 | -0.0012176 | -0.0020294 | -0.021667 | -0.002196 | 0.064392 | 0.064894 | -0.022091 | 0.0022687 | -0.00096131 | -1.4511 | 65.1306 | -57.2388 | 65.1306 | -56.0669 | -57.3349 | -2.71 | -4.2938 | 65.126 | -57.1243 | 65.0574 | -57.1426 | -57.3624 | -57.106 | 0.004577 | 0.07782 | 0.07782 | 1.1765 | 54.5334 | -0.091553 | 54.5288 | -0.09613 | 0.11902 | 0.073243 | 0.004578 | 0.10071 | 0.13733 | -0.11902 | 0.018311 | -0.23804 | 1.1719 | 122.3694 | -0.01831 | 122.1817 | 122.3694 | 122.2504 | 122.374 | 122.3694 | -122.2916 | -122.1771 | 122.374 | 122.3007 | 55.7922 | 52.9495
1489.7656 | 122.5159 | -57.1289 | 65.1398 | -0.13267 | 0.0021255 | 0.060957 | 0.10949 | -0.0030335 | -0.001004 | -0.0026704 | -0.049133 | -0.0030506 | 0.062683 | 0.055068 | -0.022304 | 0.00077333 | -0.0018157 | -1.6159 | 65.0986 | -57.2479 | 65.0894 | -55.925 | -57.4219 | -2.8656 | -4.3716 | 65.0711 | -57.1838 | 65.1581 | -57.0557 | -57.2525 | -56.9962 | -0.11902 | -0.041199 | -0.050354 | 1.2039 | 54.2633 | -0.29297 | 54.3823 | -0.17395 | -0.054932 | -0.068665 | 0.01831 | 0.073242 | 0.13275 | -0.1236 | 0.18768 | -0.068664 | 1.3229 | 122.3373 | 0.12817 | 122.3419 | 122.3465 | 122.2549 | 122.2275 | 122.2 | -122.3877 | -122.3236 | 122.2183 | 122.287 | 55.513 | 52.7573
1490.8281 | 122.5708 | -56.9366 | 65.3458 | -0.12505 | 0.00063028 | 0.062025 | 0.10778 | -0.0011109 | 6.4004e-05 | 0.00032044 | -0.0064086 | -0.0043322 | 0.061402 | 0.061476 | -0.022945 | 0.0020551 | 0.0013885 | -1.5427 | 65.3091 | -57.0328 | 65.3229 | -55.632 | -57.1564 | -2.7878 | -4.2068 | 65.2679 | -56.9412 | 65.4007 | -56.813 | -57.0053 | -56.7581 | -0.09613 | -0.036621 | -0.022888 | 1.3046 | 54.1489 | -0.21973 | 54.245 | -0.1236 | -0.004577 | -0.07782 | 0.054932 | 0.1236 | 0.17853 | -0.068664 | 0.1831 | -0.064087 | 1.4008 | 122.3557 | 0.12817 | 122.3419 | 122.3419 | 122.2092 | 122.2458 | 122.2046 | -122.3785 | -122.287 | 122.2595 | 122.3373 | 55.394 | 52.7298
1491.7656 | 122.5433 | -56.9916 | 65.2634 | -0.24712 | 0.0025529 | 0.060103 | 0.11013 | 0.0010253 | -0.0020722 | -0.0020294 | -0.012512 | -0.002196 | 0.063751 | 0.062117 | -0.021023 | 0.0018413 | -0.0020295 | -1.4923 | 65.2679 | -57.1381 | 65.2405 | -55.7465 | -57.2433 | -2.6276 | -4.3808 | 65.2084 | -57.0282 | 65.3275 | -56.8726 | -57.0969 | -56.8314 | -0.14648 | 0.004577 | -0.022888 | 1.2451 | 54.364 | -0.25177 | 54.5105 | -0.10529 | -0.036621 | -0.054932 | 0.064087 | 0.11902 | 0.16022 | -0.10529 | 0.19684 | -0.068665 | 1.3916 | 122.3785 | 0.15564 | 122.3557 | 122.406 | 122.2366 | 122.2595 | 122.2 | -122.4014 | -122.2916 | 122.2321 | 122.319 | 55.4993 | 52.6108
1492.8438 | 122.4518 | -57.5455 | 64.7827 | -0.10216 | -0.0017197 | 0.060316 | 0.10971 | 0.0023071 | -0.0018586 | -0.0024566 | 0.014954 | -0.00027343 | 0.063965 | 0.063185 | -0.02145 | 0.0020551 | -0.00032051 | -1.7624 | 64.7415 | -57.7011 | 64.6362 | -56.6254 | -57.8384 | -2.8061 | -4.5227 | 64.7507 | -57.5821 | 64.7049 | -57.4493 | -57.7194 | -57.4905 | -0.15564 | -0.041199 | -0.14648 | 0.9201 | 54.7394 | -0.29297 | 54.895 | -0.13733 | -0.036621 | -0.032044 | -0.07782 | 0.09613 | 0.054931 | -0.17395 | 0.091552 | -0.13733 | 1.0757 | 122.3373 | 0.13275 | 122.287 | 122.4426 | 122.3328 | 122.287 | 122.2961 | -122.4838 | -122.3648 | 122.1817 | 122.2504 | 55.7831 | 53.0228
1493.7656 | 122.5571 | -57.1655 | 65.0711 | -0.094528 | -0.0010787 | 0.061385 | 0.108 | 0.0029479 | -0.0033538 | -0.00053396 | -0.064392 | -0.003905 | 0.06247 | 0.069167 | -0.024013 | 0.00077333 | 0.0013885 | -1.7303 | 65.0299 | -57.3303 | 65.1031 | -55.9662 | -57.4127 | -2.6642 | -4.4586 | 65.007 | -57.2342 | 65.1443 | -57.0419 | -57.2708 | -57.0099 | -0.1648 | -0.041199 | 0.032043 | 1.1993 | 54.5013 | -0.24719 | 54.6661 | -0.082398 | -0.068665 | -0.064087 | 0.073242 | 0.1236 | 0.15564 | -0.10529 | 0.2243 | -0.036621 | 1.3641 | 122.4335 | 0.19226 | 122.3785 | 122.3602 | 122.2412 | 122.1954 | 122.1725 | -122.4014 | -122.3053 | 122.2687 | 122.3099 | 55.4352 | 52.7069
1494.8281 | 122.5479 | -57.1014 | 65.1627 | -0.11742 | 0.0021255 | 0.060744 | 0.10907 | -0.0015381 | -0.0022858 | -0.0024566 | -0.12848 | -0.0036914 | 0.061829 | 0.05934 | -0.020168 | 0.0029095 | -0.0041657 | -1.8127 | 65.1306 | -57.2479 | 65.1215 | -55.9982 | -57.0969 | -2.5772 | -4.4861 | 65.094 | -57.1564 | 65.1993 | -56.9962 | -57.2113 | -56.9641 | -0.14649 | -0.032044 | -0.041199 | 1.1032 | 54.5242 | 0.004577 | 54.6707 | 0.15106 | -0.054932 | -0.068665 | 0.036621 | 0.10528 | 0.13733 | -0.10986 | 0.19226 | -0.054932 | 1.2497 | 122.3694 | 0.16022 | 122.3557 | 122.3785 | 122.2504 | 122.2321 | 122.1954 | -122.4106 | -122.319 | 122.2229 | 122.3007 | 55.2887 | 52.6154
1495.7656 | 122.5525 | -56.6254 | 65.6296 | -0.11742 | 0.00020288 | 0.060744 | 0.10907 | -0.0019653 | -0.0012176 | 0.00053404 | -0.082703 | -0.003905 | 0.060974 | 0.062117 | -0.024441 | 0.0026959 | 0.0033111 | -1.7853 | 65.6296 | -56.8039 | 65.5884 | -55.3986 | -56.9138 | -2.5726 | -4.3808 | 65.5884 | -56.6803 | 65.712 | -56.5201 | -56.7215 | -56.4468 | -0.17853 | 0 | -0.041199 | 1.2268 | 54.0527 | -0.28839 | 54.2313 | -0.10986 | -0.054932 | -0.041199 | 0.082397 | 0.10529 | 0.17853 | -0.096131 | 0.23346 | -0.041199 | 1.4053 | 122.3923 | 0.16022 | 122.3923 | 122.4335 | 122.2687 | 122.2549 | 122.2137 | -122.4335 | -122.3099 | 122.2137 | 122.3373 | 54.8401 | 52.2446
1496.8281 | 122.5159 | -56.4102 | 65.8356 | -0.15556 | 0.0012711 | 0.06053 | 0.10949 | -0.0015381 | -0.0022858 | 0.00074764 | -0.055237 | -0.0043322 | 0.061615 | 0.061263 | -0.021023 | -0.00029487 | 0.0013885 | -1.7212 | 65.7623 | -56.6071 | 65.8127 | -55.1926 | -56.6849 | -2.5223 | -4.39 | 65.7394 | -56.5063 | 65.8951 | -56.3095 | -56.5018 | -56.2729 | -0.19684 | -0.073242 | -0.022888 | 1.2177 | 53.8879 | -0.27466 | 54.0848 | -0.077819 | -0.096131 | -0.09613 | 0.05951 | 0.10071 | 0.13733 | -0.091553 | 0.23346 | 0.004578 | 1.4145 | 122.4197 | 0.19684 | 122.4014 | 122.3694 | 122.2458 | 122.1725 | 122.1497 | -122.4426 | -122.3419 | 122.2229 | 122.3053 | 54.689 | 52.0203
1497.7656 | 122.5754 | -56.6528 | 65.5701 | -0.10979 | 0.00041648 | 0.061598 | 0.11077 | 0.0025207 | -0.0033538 | -0.002884 | -0.064392 | -0.0030506 | 0.059479 | 0.063399 | -0.023586 | 0.0014141 | 0.0011749 | -1.7166 | 65.5472 | -56.8039 | 65.6296 | -55.5084 | -56.9046 | -2.5314 | -4.5822 | 65.5289 | -56.6666 | 65.6891 | -56.5063 | -56.7444 | -56.4743 | -0.15106 | -0.022888 | 0.05951 | 1.1444 | 54.1214 | -0.25177 | 54.2725 | -0.10071 | -0.013733 | -0.041198 | 0.11902 | 0.14648 | 0.17853 | -0.091553 | 0.19226 | -0.07782 | 1.2955 | 122.4335 | 0.16022 | 122.3557 | 122.3511 | 122.1954 | 122.2 | 122.1817 | -122.374 | -122.2366 | 122.2824 | 122.3419 | 54.9362 | 52.0706
1498.8281 | 122.5525 | -56.3095 | 65.9592 | -0.27 | -0.00043792 | 0.061598 | 0.10821 | 0.00038452 | -0.0022858 | -0.0020294 | -0.018616 | -0.0034778 | 0.06247 | 0.057418 | -0.023586 | 0.00098693 | 0.0056611 | -1.5244 | 65.9317 | -56.4514 | 65.9225 | -55.0278 | -56.5842 | -2.3987 | -4.5502 | 65.8768 | -56.3782 | 65.9912 | -56.2042 | -56.4148 | -56.1768 | -0.14191 | -0.027465 | -0.036621 | 1.2817 | 53.9108 | -0.27466 | 54.0527 | -0.13275 | -0.068665 | -0.082397 | 0.032044 | 0.10528 | 0.13275 | -0.10529 | 0.20142 | -0.036621 | 1.4236 | 122.374 | 0.17395 | 122.3694 | 122.3831 | 122.2549 | 122.2412 | 122.1863 | -122.4106 | -122.3373 | 122.2321 | 122.3007 | 54.7852 | 51.7593
1499.7656 | 122.5708 | -57.2983 | 64.9521 | -0.041122 | -0.00065152 | 0.061812 | 0.10778 | -0.0013245 | -0.0022858 | -0.0018158 | -0.039978 | -0.0036914 | 0.064179 | 0.06404 | -0.021664 | 0.0024823 | -0.00074771 | -1.8356 | 65.0391 | -57.3669 | 64.9933 | -56.1493 | -57.4997 | -2.7466 | -4.866 | 64.9338 | -57.3349 | 64.9933 | -57.2433 | -57.4036 | -57.1701 | -0.068664 | 0.086975 | 0.041199 | 1.149 | 54.5517 | -0.20142 | 54.6204 | -0.13275 | -0.036621 | -0.01831 | 0.041199 | 0.054932 | 0.12817 | -0.10529 | 0.16479 | -0.068664 | 1.2177 | 122.3602 | 0.091553 | 122.3282 | 122.406 | 122.2687 | 122.3373 | 122.2321 | -122.319 | -122.287 | 122.2916 | 122.2916 | 55.4626 | 52.4323
1500.8281 | 122.5571 | -56.5979 | 65.6296 | -0.13267 | 0.0019119 | 0.061598 | 0.10778 | -0.00025628 | 6.4004e-05 | 0.00010684 | -0.073547 | -0.0036914 | 0.062256 | 0.067885 | -0.022945 | 0.00098693 | 0.0013885 | -1.7166 | 65.625 | -56.7169 | 65.7166 | -55.3345 | -56.813 | -2.5452 | -4.6921 | 65.5975 | -56.6025 | 65.7578 | -56.4789 | -56.7032 | -56.4331 | -0.11902 | -0.004578 | 0.086975 | 1.2634 | 54.0527 | -0.21515 | 54.1718 | -0.09613 | -0.004578 | -0.032044 | 0.12817 | 0.11902 | 0.1648 | -0.10529 | 0.16937 | -0.10071 | 1.3824 | 122.4335 | 0.1236 | 122.3602 | 122.3419 | 122.2 | 122.2229 | 122.1954 | -122.3465 | -122.2321 | 122.3145 | 122.3557 | 54.8813 | 51.9058
1501.7656 | 122.5754 | -55.8701 | 66.3757 | -0.10979 | 0.00084388 | 0.062453 | 0.10971 | -0.00025628 | -0.002713 | -0.00053396 | -0.088806 | -0.0030506 | 0.062683 | 0.065322 | -0.023159 | 0.0048321 | -0.00074771 | -1.5381 | 66.2842 | -56.0532 | 66.3666 | -54.5609 | -56.1676 | -2.4765 | -4.5639 | 66.3391 | -55.9067 | 66.4764 | -55.7648 | -55.957 | -55.6961 | -0.18311 | -0.091552 | -0.009155 | 1.3092 | 53.3936 | -0.29755 | 53.5767 | -0.11444 | -0.036621 | -0.036621 | 0.10071 | 0.10528 | 0.17395 | -0.086975 | 0.21057 | -0.050354 | 1.4923 | 122.4197 | 0.14191 | 122.3831 | 122.3373 | 122.2458 | 122.1542 | 122.2092 | -122.4289 | -122.2824 | 122.2366 | 122.3465 | 54.332 | 51.3062
1502.8281 | 122.4747 | -56.6528 | 65.6754 | -0.048752 | 0.00041648 | 0.06288 | 0.10949 | -0.0038879 | -0.0031402 | -0.0043792 | -0.058289 | -0.0013416 | 0.060761 | 0.059767 | -0.021023 | 0.00077333 | 0.0013885 | -1.8494 | 65.6479 | -56.7719 | 65.5609 | -55.632 | -56.9046 | -2.742 | -4.7928 | 65.6479 | -56.6299 | 65.6982 | -56.5018 | -56.7764 | -56.5247 | -0.11902 | -0.027466 | -0.11444 | 1.0208 | 53.9108 | -0.25177 | 54.0298 | -0.13275 | 0.022888 | -0.027466 | 0.022888 | 0.15106 | 0.12817 | -0.1236 | 0.10529 | -0.14648 | 1.1398 | 122.3328 | 0.12817 | 122.3282 | 122.4197 | 122.2778 | 122.3007 | 122.3007 | -122.4472 | -122.3053 | 122.2137 | 122.3511 | 54.8035 | 51.86
1503.7656 | 122.6166 | -56.8863 | 65.3503 | -0.16319 | 0.0025529 | 0.06288 | 0.10971 | 0.0029479 | -0.002713 | -0.003952 | 0.014954 | -0.0034778 | 0.063538 | 0.054 | -0.022732 | 0.0014141 | -0.0011749 | -2.0004 | 65.2954 | -57.0557 | 65.4739 | -55.9525 | -57.3395 | -2.9297 | -5.0034 | 65.3549 | -56.8954 | 65.5151 | -56.7078 | -56.9458 | -56.7123 | -0.16937 | -0.054932 | 0.1236 | 0.93384 | 53.9566 | -0.45319 | 54.126 | -0.28381 | -0.009155 | 0.004577 | 0.16479 | 0.17853 | 0.17395 | -0.059509 | 0.18311 | -0.050354 | 1.1032 | 122.5296 | 0.18768 | 122.4106 | 122.3511 | 122.2504 | 122.1817 | 122.2412 | -122.406 | -122.2458 | 122.3602 | 122.4014 | 54.8859 | 51.8829
1504.8281 | 122.5479 | -55.8334 | 66.4627 | -0.13267 | 0.00020288 | 0.063521 | 0.10629 | 0.0040161 | -0.0020722 | -0.0026704 | -0.036926 | -0.002196 | 0.063751 | 0.059767 | -0.023373 | 0.00077333 | -0.00053411 | -1.7853 | 66.3803 | -55.9616 | 66.4032 | -54.6249 | -56.0898 | -2.8519 | -4.6326 | 66.4078 | -55.8609 | 66.4673 | -55.7465 | -55.9296 | -55.687 | -0.12817 | -0.082398 | -0.05951 | 1.2085 | 52.9816 | -0.25635 | 53.1097 | -0.12817 | -0.027466 | -0.054932 | 0.004577 | 0.086975 | 0.14648 | -0.09613 | 0.17395 | -0.068664 | 1.3367 | 122.3648 | 0.11444 | 122.3282 | 122.3419 | 122.2687 | 122.2137 | 122.2412 | -122.4243 | -122.3236 | 122.2366 | 122.3007 | 54.0482 | 51.2009
1505.7656 | 122.6212 | -55.8289 | 66.4215 | -0.086899 | 0.00020288 | 0.05818 | 0.10885 | 0.0035889 | -0.0029266 | -0.0033112 | 0.014954 | -0.0043322 | 0.064392 | 0.064681 | -0.022304 | 0.00098693 | -0.00053411 | -1.5472 | 66.806 | -55.5496 | 66.8289 | -54.1077 | -55.7327 | -2.5864 | -4.6509 | 66.5314 | -55.7968 | 66.4536 | -55.6732 | -55.8517 | -55.6229 | 0.27923 | 0.38452 | 0.40741 | 1.7212 | 53.2425 | 0.09613 | 52.9633 | -0.1831 | 0.032043 | 0.10986 | 0.032043 | 0.15564 | 0.20599 | -0.022889 | 0.17395 | -0.054932 | 1.442 | 122.3785 | 0.1236 | 122.2504 | 122.3557 | 122.3282 | 122.6349 | 122.3602 | -121.9711 | -122.2183 | 122.6578 | 122.2824 | 54.2816 | 51.178
1506.8281 | 122.4838 | -55.3986 | 66.925 | -0.07164 | 0.0023391 | 0.061171 | 0.1127 | 0.0027343 | -0.0016448 | -0.0020294 | -0.14679 | -0.0024096 | 0.063538 | 0.066603 | -0.024013 | 0.0046185 | 0.0013885 | -1.5884 | 66.9205 | -55.4901 | 66.8243 | -54.1718 | -55.7281 | -2.536 | -4.6738 | 66.8793 | -55.4626 | 66.8335 | -55.4123 | -55.5908 | -55.3024 | -0.091552 | -0.004578 | -0.10071 | 1.2268 | 52.8625 | -0.32959 | 52.9541 | -0.23804 | -0.064086 | -0.045777 | -0.091553 | -0.013732 | 0.096131 | -0.19226 | 0.16022 | -0.12817 | 1.3184 | 122.3145 | 0.050354 | 122.2961 | 122.4106 | 122.3419 | 122.319 | 122.2778 | -122.4152 | -122.3877 | 122.2229 | 122.2321 | 53.8101 | 50.7248
1507.7656 | 122.5342 | -55.0369 | 67.2363 | -0.07164 | 0.0012711 | 0.062666 | 0.10757 | -0.0028199 | -0.0029266 | -0.0013886 | -0.033874 | -0.0024096 | 0.063751 | 0.05934 | -0.024013 | 0.00098693 | 0.0035247 | -1.2955 | 67.2043 | -55.1605 | 67.2134 | -53.6087 | -55.2475 | -2.5314 | -4.5273 | 67.2043 | -55.0873 | 67.2546 | -54.9591 | -55.1102 | -54.8813 | -0.1236 | -0.032043 | -0.022888 | 1.4282 | 52.5055 | -0.21057 | 52.6291 | -0.086976 | -0.050354 | -0.032043 | 0.018311 | 0.07782 | 0.15564 | -0.073242 | 0.20599 | -0.022888 | 1.5518 | 122.374 | 0.12817 | 122.3419 | 122.3648 | 122.2916 | 122.2412 | 122.2412 | -122.3969 | -122.3236 | 122.2504 | 122.2916 | 53.7415 | 50.5096
1508.8281 | 122.5891 | -55.7785 | 66.4444 | -0.12505 | 0.0010575 | 0.059889 | 0.11142 | 0.00017092 | -0.0037812 | -0.0013886 | -0.018616 | -0.002196 | 0.06247 | 0.057204 | -0.021664 | 0.0016277 | 0.0050201 | -1.2726 | 66.4764 | -55.9387 | 66.3849 | -54.7714 | -56.0303 | -2.6733 | -4.5181 | 66.33 | -55.9021 | 66.5451 | -55.6274 | -55.8563 | -55.6229 | -0.16022 | 0.032043 | -0.059509 | 1.0071 | 53.1052 | -0.25177 | 53.2654 | -0.091552 | -0.1236 | -0.11444 | 0.10071 | 0.15106 | 0.15564 | -0.07782 | 0.27924 | 0.045777 | 1.1673 | 122.3236 | 0.27466 | 122.4472 | 122.4152 | 122.2321 | 122.2549 | 122.1085 | -122.3831 | -122.3465 | 122.1634 | 122.3236 | 54.5059 | 51.2604
1509.7656 | 122.5708 | -56.25 | 66.0324 | -0.12505 | 0.0029801 | 0.059462 | 0.10778 | -0.0013245 | -0.0012176 | -0.0016022 | -0.04303 | -0.0026232 | 0.063538 | 0.061904 | -0.0238 | 0.00077333 | 0.0020295 | -1.5747 | 65.9637 | -56.4011 | 66.0233 | -55.2429 | -56.5155 | -2.7237 | -4.7653 | 65.918 | -56.3095 | 66.0782 | -56.1493 | -56.3232 | -56.0898 | -0.15106 | -0.068665 | -0.009156 | 1.0071 | 53.5263 | -0.2655 | 53.6774 | -0.11444 | -0.059509 | -0.11444 | 0.045776 | 0.10071 | 0.16022 | -0.073242 | 0.21973 | -0.013733 | 1.1581 | 122.4243 | 0.16022 | 122.3877 | 122.3648 | 122.2275 | 122.2137 | 122.168 | -122.4335 | -122.3419 | 122.2733 | 122.3282 | 54.6753 | 51.4847
1510.8281 | 122.5845 | -57.0877 | 65.1718 | -0.10979 | 0.0010575 | 0.060103 | 0.1112 | -4.2682e-05 | -0.0012176 | 0.0016022 | -0.073547 | -0.0028368 | 0.063324 | 0.058058 | -0.024227 | 0.0031231 | 0.0039521 | -1.9089 | 65.1031 | -57.2571 | 65.1352 | -56.5933 | -57.4081 | -2.9022 | -5.0446 | 65.0528 | -57.2113 | 65.2496 | -57.0007 | -57.2159 | -56.9321 | -0.16937 | -0.068665 | -0.036621 | 0.49439 | 54.1855 | -0.32043 | 54.3549 | -0.15106 | -0.1236 | -0.11902 | 0.07782 | 0.086976 | 0.15564 | -0.12817 | 0.27924 | -0.004577 | 0.66376 | 122.3923 | 0.21057 | 122.4609 | 122.3602 | 122.2641 | 122.1909 | 122.1405 | -122.4289 | -122.3831 | 122.2229 | 122.3373 | 55.1788 | 52.0432
1511.7656 | 122.5937 | -56.7352 | 65.5197 | -0.13267 | -0.00022432 | 0.063094 | 0.10907 | -0.0011109 | -0.0039948 | -0.0024566 | -0.058289 | -0.0041186 | 0.063538 | 0.063613 | -0.024227 | -0.00093567 | -0.0011749 | -1.8082 | 65.4648 | -56.8863 | 65.538 | -56.2546 | -57.0465 | -2.7054 | -4.8294 | 65.4236 | -56.7993 | 65.625 | -56.6254 | -56.8314 | -56.5659 | -0.15106 | -0.054931 | 0.018311 | 0.48065 | 54.0298 | -0.31128 | 54.1809 | -0.16022 | -0.064087 | -0.09613 | 0.10529 | 0.10986 | 0.16937 | -0.096131 | 0.23346 | -0.032044 | 0.63171 | 122.4243 | 0.17395 | 122.4243 | 122.3511 | 122.2229 | 122.2 | 122.1588 | -122.406 | -122.319 | 122.2733 | 122.3602 | 54.9271 | 51.9058
1512.8438 | 122.5021 | -56.8817 | 65.4373 | -0.041122 | 0.00063028 | 0.063094 | 0.10992 | -0.0019653 | 0.002414 | -0.0026704 | -0.10406 | -0.0019824 | 0.063965 | 0.061263 | -0.025722 | 0.0024823 | 0.0028839 | -1.9135 | 65.4922 | -56.9687 | 65.4236 | -56.1447 | -57.0694 | -2.8107 | -4.8935 | 65.4739 | -56.8588 | 65.4373 | -56.7673 | -57.019 | -56.7581 | -0.086975 | 0.054932 | -0.013733 | 0.737 | 54.071 | -0.18768 | 54.158 | -0.10071 | 0.022888 | 0.036621 | 0 | 0.11444 | 0.1236 | -0.13733 | 0.10071 | -0.16022 | 0.82397 | 122.3923 | 0.091553 | 122.2961 | 122.4609 | 122.3328 | 122.374 | 122.3557 | -122.406 | -122.2961 | 122.3053 | 122.319 | 54.9683 | 51.9882
1513.7656 | 122.5754 | -57.193 | 65.0803 | -0.17845 | -0.00022432 | 0.060316 | 0.10821 | 0.0018799 | -0.0014312 | -0.001175 | -0.039978 | -0.0026232 | 0.061829 | 0.057631 | -0.022732 | 0.0012005 | 0.0030975 | -2.0645 | 65.0848 | -57.2845 | 65.0986 | -56.7856 | -57.4127 | -2.8473 | -5.0812 | 65.0253 | -57.2479 | 65.1535 | -57.0511 | -57.2662 | -57.0282 | -0.091553 | 0.004578 | 0.018311 | 0.40741 | 54.3457 | -0.21973 | 54.4373 | -0.12817 | -0.054932 | -0.054931 | 0.073242 | 0.14191 | 0.16479 | -0.073242 | 0.21973 | -0.01831 | 0.49896 | 122.3831 | 0.19684 | 122.4014 | 122.3694 | 122.2733 | 122.2778 | 122.2183 | -122.3648 | -122.3282 | 122.2916 | 122.3465 | 55.1285 | 52.1118
1514.8281 | 122.58 | -56.5247 | 65.7394 | -0.12505 | -0.00086512 | 0.061812 | 0.11056 | -0.00025628 | -0.0014312 | -0.0016022 | -0.091858 | -0.0030506 | 0.064179 | 0.05934 | -0.023373 | 0.0018413 | -0.00010671 | -2.0782 | 65.7166 | -56.6895 | 65.7028 | -56.2683 | -56.8405 | -2.8839 | -4.8935 | 65.7074 | -56.6162 | 65.8218 | -56.3965 | -56.6162 | -56.3416 | -0.16479 | -0.022888 | -0.036621 | 0.25635 | 53.6407 | -0.31586 | 53.8055 | -0.15106 | -0.091553 | -0.032044 | 0.082397 | 0.12817 | 0.18311 | -0.091553 | 0.27466 | 0 | 0.42114 | 122.3923 | 0.21973 | 122.438 | 122.406 | 122.3236 | 122.2412 | 122.2321 | -122.4289 | -122.3557 | 122.2275 | 122.3465 | 54.4464 | 51.6312
1515.7656 | 122.5616 | -57.399 | 64.8926 | -0.094528 | 0.00020288 | 0.06053 | 0.11099 | 0.0029479 | -0.0022858 | -0.001175 | -0.097961 | -0.0054004 | 0.064392 | 0.060408 | -0.021023 | 0.0020551 | 0.0013885 | -2.3621 | 64.888 | -57.55 | 64.8376 | -57.0923 | -57.6599 | -2.829 | -5.1178 | 64.8743 | -57.4219 | 64.9658 | -57.2571 | -57.5043 | -57.2388 | -0.15106 | -0.004578 | -0.054932 | 0.3067 | 54.57 | -0.26093 | 54.7211 | -0.10986 | -0.022888 | -0.01831 | 0.073242 | 0.14191 | 0.16022 | -0.10529 | 0.1831 | -0.082397 | 0.45776 | 122.3877 | 0.16479 | 122.3877 | 122.438 | 122.2961 | 122.287 | 122.2733 | -122.4426 | -122.3145 | 122.2366 | 122.3648 | 55.0369 | 52.2812
1516.7656 | 122.6303 | -57.1518 | 65.0894 | -0.079269 | -0.00043792 | 0.061385 | 0.10949 | -4.2682e-05 | -0.0012176 | -0.00096136 | -0.070496 | -0.002196 | 0.065674 | 0.059981 | -0.022732 | 0.0026959 | 0.0016021 | -2.1698 | 65.0803 | -57.2891 | 65.094 | -56.8359 | -57.3898 | -2.7786 | -5.0949 | 65.0436 | -57.1976 | 65.2359 | -56.987 | -57.2021 | -56.9458 | -0.13733 | -0.009156 | 0.004577 | 0.31586 | 54.3732 | -0.23804 | 54.5105 | -0.10071 | -0.045777 | -0.045777 | 0.14648 | 0.16479 | 0.20599 | -0.050354 | 0.25177 | -0.004577 | 0.45319 | 122.3831 | 0.21057 | 122.4335 | 122.3694 | 122.2412 | 122.2321 | 122.1954 | -122.3785 | -122.287 | 122.2458 | 122.3877 | 54.982 | 52.0569
1517.8438 | 122.5113 | -56.6895 | 65.625 | -0.033493 | 0.0016983 | 0.06053 | 0.1112 | -0.0023925 | -0.0012176 | -0.002243 | -0.064392 | -0.001128 | 0.063111 | 0.061476 | -0.023586 | 0.0020551 | -0.0022431 | -2.1606 | 65.657 | -56.8085 | 65.5243 | -56.4514 | -56.9504 | -2.8152 | -4.985 | 65.6113 | -56.7032 | 65.6067 | -56.5613 | -56.8222 | -56.5475 | -0.11902 | 0.032043 | -0.10071 | 0.23804 | 53.8742 | -0.26093 | 53.9932 | -0.14191 | -0.013733 | -0.013733 | -0.018311 | 0.12817 | 0.14191 | -0.13275 | 0.15564 | -0.11902 | 0.35706 | 122.3328 | 0.14191 | 122.3099 | 122.4655 | 122.3145 | 122.3465 | 122.3007 | -122.4335 | -122.3282 | 122.2137 | 122.2961 | 54.5288 | 51.7044
1518.7656 | 122.5662 | -56.8542 | 65.4144 | -0.14793 | 0.0029801 | 0.061812 | 0.10949 | 0.0020935 | -0.0016448 | -0.00074776 | -0.0064086 | -0.0054004 | 0.063538 | 0.055495 | -0.022091 | 0.0016277 | -0.00053411 | -2.2064 | 65.3732 | -57.0053 | 65.4327 | -56.5018 | -57.106 | -2.9205 | -4.9805 | 65.3275 | -56.9229 | 65.4739 | -56.7261 | -56.9321 | -56.694 | -0.15106 | -0.041199 | 0.01831 | 0.35248 | 53.9337 | -0.25177 | 54.0848 | -0.10071 | -0.068665 | -0.086975 | 0.059509 | 0.12817 | 0.16022 | -0.07782 | 0.22888 | -0.009155 | 0.50354 | 122.438 | 0.19684 | 122.3969 | 122.3785 | 122.2504 | 122.2275 | 122.1817 | -122.4197 | -122.3373 | 122.287 | 122.3282 | 54.6478 | 51.8738
1519.8281 | 122.5754 | -56.2088 | 66.0736 | -0.1403 | -0.00022432 | 0.061385 | 0.10821 | -0.0013245 | -0.0012176 | -0.002243 | -0.046081 | -0.0017688 | 0.064606 | 0.06639 | -0.022518 | 0.0016277 | -0.00053411 | -1.9958 | 66.0278 | -56.3461 | 66.0416 | -55.8655 | -56.4606 | -2.8244 | -4.9393 | 66.0004 | -56.2592 | 66.1194 | -56.0761 | -56.3004 | -56.0623 | -0.13733 | -0.045776 | -0.032043 | 0.34332 | 53.3844 | -0.25177 | 53.5217 | -0.11444 | -0.050354 | -0.073242 | 0.045777 | 0.13275 | 0.14648 | -0.091553 | 0.19684 | -0.041199 | 0.48065 | 122.3877 | 0.1831 | 122.3785 | 122.374 | 122.2595 | 122.2366 | 122.2092 | -122.4197 | -122.3328 | 122.2504 | 122.3282 | 54.213 | 51.2695
1520.7656 | 122.5891 | -56.662 | 65.6113 | -0.086899 | 0.0023391 | 0.06053 | 0.10842 | 0.0035889 | -0.0018586 | -0.0030976 | 0.021057 | -0.0028368 | 0.063538 | 0.061049 | -0.023586 | 0.0022687 | -0.0020295 | -2.0279 | 65.5701 | -56.8085 | 65.5701 | -56.3736 | -56.9321 | -2.8427 | -5.0949 | 65.538 | -56.7444 | 65.6662 | -56.4972 | -56.7032 | -56.4926 | -0.14648 | -0.041199 | -0.041199 | 0.28839 | 53.8193 | -0.27008 | 53.9658 | -0.1236 | -0.082398 | -0.073242 | 0.054932 | 0.1648 | 0.16937 | -0.041199 | 0.25177 | 0.041199 | 0.43488 | 122.3785 | 0.24719 | 122.4106 | 122.3785 | 122.2824 | 122.2321 | 122.2 | -122.4197 | -122.3557 | 122.2321 | 122.3282 | 54.6341 | 51.5671
1521.8281 | 122.5754 | -56.4789 | 65.8173 | -0.14793 | 0.0023391 | 0.060957 | 0.11056 | -0.0011109 | -0.0024994 | -0.0016022 | -0.0033568 | -0.0045458 | 0.063111 | 0.058699 | -0.025082 | 0.0018413 | 0.0024567 | -2.1927 | 65.7532 | -56.6345 | 65.7303 | -56.2317 | -56.7535 | -2.9572 | -5.2551 | 65.7303 | -56.543 | 65.8356 | -56.3644 | -56.5933 | -56.3507 | -0.15564 | -0.064087 | -0.086975 | 0.24719 | 53.5217 | -0.27466 | 53.6774 | -0.11902 | -0.064087 | -0.086975 | 0.01831 | 0.11444 | 0.12817 | -0.11444 | 0.19226 | -0.050354 | 0.40283 | 122.3648 | 0.17853 | 122.3785 | 122.3877 | 122.2733 | 122.2321 | 122.2092 | -122.4518 | -122.3602 | 122.2092 | 122.3145 | 54.2862 | 51.2238
1522.7656 | 122.5937 | -55.687 | 66.568 | -0.17082 | -0.00065152 | 0.062239 | 0.11056 | 0.0063659 | -0.0003632 | -0.0043792 | -0.039978 | -0.0047594 | 0.062042 | 0.05934 | -0.025722 | 0.0022687 | -0.00096131 | -2.0142 | 66.5359 | -55.8655 | 66.5817 | -55.3619 | -55.9662 | -2.6459 | -5.0125 | 66.4856 | -55.7556 | 66.6595 | -55.5634 | -55.7877 | -55.5313 | -0.17853 | -0.032043 | 0.013733 | 0.32501 | 53.0411 | -0.27924 | 53.2196 | -0.10071 | -0.068664 | -0.082397 | 0.091553 | 0.1236 | 0.15564 | -0.10071 | 0.2243 | -0.032044 | 0.50354 | 122.4472 | 0.19226 | 122.4152 | 122.4014 | 122.2412 | 122.2229 | 122.1725 | -122.4335 | -122.3236 | 122.2687 | 122.3465 | 53.6728 | 50.6744
1523.8281 | 122.5662 | -54.7256 | 67.5385 | -0.11742 | 0.0025529 | 0.063094 | 0.10907 | -0.00025628 | -0.001004 | -0.0054474 | -0.055237 | -0.0041186 | 0.061829 | 0.065108 | -0.024868 | 0.0014141 | -0.0013885 | -1.8951 | 67.5156 | -54.8355 | 67.543 | -54.3961 | -54.9774 | -2.3254 | -4.7791 | 67.4973 | -54.744 | 67.6437 | -54.5837 | -54.8355 | -54.5792 | -0.10986 | -0.022888 | 0.004578 | 0.32959 | 52.4002 | -0.25177 | 52.5101 | -0.14191 | -0.018311 | -0.041199 | 0.10529 | 0.14191 | 0.14648 | -0.10986 | 0.16479 | -0.091552 | 0.43945 | 122.3785 | 0.16022 | 122.3877 | 122.3511 | 122.2412 | 122.2412 | 122.2229 | -122.374 | -122.2824 | 122.2687 | 122.3694 | 52.8305 | 49.9466
1524.7656 | 122.5708 | -54.4556 | 67.8131 | -0.079269 | 0.00084388 | 0.064162 | 0.10885 | -0.0036743 | -0.002713 | -0.003952 | -0.012512 | -0.0045458 | 0.062683 | 0.060836 | -0.024441 | 0.0018413 | 0.00096129 | -1.7349 | 67.8177 | -54.6249 | 67.7902 | -54.1855 | -54.7028 | -2.2797 | -4.8065 | 67.7719 | -54.5151 | 67.8909 | -54.2953 | -54.5288 | -54.2953 | -0.16937 | 0.004578 | -0.022888 | 0.27008 | 52.1759 | -0.24719 | 52.3453 | -0.07782 | -0.05951 | -0.041198 | 0.07782 | 0.16022 | 0.16022 | -0.073243 | 0.21973 | -0.013733 | 0.43945 | 122.4152 | 0.21973 | 122.406 | 122.4426 | 122.287 | 122.2733 | 122.2275 | -122.438 | -122.3282 | 122.2458 | 122.3465 | 52.7206 | 49.649
1525.8281 | 122.5616 | -53.9749 | 68.3166 | -0.1403 | -0.0019333 | 0.061812 | 0.10757 | -0.00025628 | 0.0002778 | -0.0016022 | -0.030823 | -0.0019824 | 0.063751 | 0.061049 | -0.021877 | 0.00098693 | 0.0013885 | -1.5244 | 68.2571 | -54.1122 | 68.1244 | -53.7689 | -54.2267 | -2.1927 | -4.8477 | 68.2388 | -54.0161 | 68.3395 | -53.8559 | -54.0848 | -53.8422 | -0.13733 | -0.059509 | -0.19226 | 0.20599 | 51.7822 | -0.25177 | 51.9196 | -0.11444 | -0.041198 | -0.077819 | 0.022889 | 0.11902 | 0.13275 | -0.10986 | 0.17395 | -0.068665 | 0.34332 | 122.2366 | 0.16022 | 122.3557 | 122.3694 | 122.2549 | 122.2321 | 122.2137 | -122.4289 | -122.3328 | 122.0993 | 122.3145 | 52.4506 | 49.1272
1526.7656 | 122.5571 | -55.2841 | 66.9891 | -0.1403 | 0.0019119 | 0.060957 | 0.11056 | 0.00017092 | -0.0035674 | 0.00032044 | -0.049133 | -0.005614 | 0.062683 | 0.062972 | -0.024227 | 0.0018413 | -0.0026703 | -1.8585 | 67.0029 | -55.3802 | 67.0349 | -54.9179 | -55.513 | -2.3941 | -5.0217 | 66.9525 | -55.3162 | 67.0441 | -55.1697 | -55.3986 | -55.1559 | -0.09613 | 0.013733 | 0.045776 | 0.36621 | 52.89 | -0.22888 | 52.9861 | -0.13275 | -0.032043 | -0.036621 | 0.054931 | 0.11444 | 0.12817 | -0.11444 | 0.16022 | -0.082398 | 0.46234 | 122.4152 | 0.14648 | 122.3602 | 122.3831 | 122.2687 | 122.287 | 122.2366 | -122.3694 | -122.3053 | 122.319 | 122.3282 | 53.4256 | 50.2625
1527.8438 | 122.5067 | -54.8492 | 67.4835 | -0.048752 | 0.00041648 | 0.062666 | 0.10907 | 0.00059812 | -0.0012176 | -0.00032036 | -0.12238 | -0.0026232 | 0.065033 | 0.068526 | -0.023159 | 0.00034613 | 0.00010689 | -1.6846 | 67.5201 | -54.9408 | 67.4194 | -54.5654 | -55.0781 | -2.3895 | -5.2094 | 67.4881 | -54.8721 | 67.4698 | -54.7485 | -55.0049 | -54.7348 | -0.091553 | 0.036621 | -0.064087 | 0.28381 | 52.4597 | -0.22888 | 52.5513 | -0.13733 | -0.022888 | 0.004577 | -0.013733 | 0.10071 | 0.11444 | -0.15564 | 0.13733 | -0.13275 | 0.37537 | 122.3602 | 0.1236 | 122.3419 | 122.4609 | 122.3602 | 122.3694 | 122.3373 | -122.4243 | -122.3557 | 122.2687 | 122.319 | 53.1647 | 49.6399
1528.7656 | 122.4838 | -54.9866 | 67.3645 | -0.086899 | -0.00043792 | 0.061171 | 0.1127 | 0.0048705 | -0.0020722 | -0.00010676 | -0.11932 | -0.0028368 | 0.062256 | 0.058058 | -0.023159 | 0.0026959 | 0.0016021 | -1.886 | 67.3508 | -55.1056 | 67.2729 | -54.6936 | -55.2612 | -2.6184 | -5.3146 | 67.3462 | -55.0095 | 67.2821 | -54.9316 | -55.22 | -54.9316 | -0.11902 | -0.013733 | -0.091553 | 0.29297 | 52.3682 | -0.27466 | 52.4872 | -0.15564 | -0.022888 | -0.018311 | -0.082398 | 0.054931 | 0.054931 | -0.23346 | 0.077819 | -0.21057 | 0.41199 | 122.3785 | 0.077819 | 122.2916 | 122.4564 | 122.3557 | 122.3373 | 122.3328 | -122.4701 | -122.374 | 122.2595 | 122.2687 | 53.1006 | 49.6719
1529.8281 | 122.6303 | -54.0939 | 68.1702 | -0.07164 | 0.0012711 | 0.061171 | 0.10971 | -0.0034607 | -0.0018586 | -0.002884 | -0.0033568 | -0.0045458 | 0.060974 | 0.063613 | -0.022304 | -0.0017901 | 0.0026703 | -1.5106 | 68.129 | -54.2587 | 68.1976 | -53.6591 | -54.2999 | -2.3071 | -5.0446 | 68.1152 | -54.1351 | 68.3578 | -53.9886 | -54.1443 | -53.9062 | -0.16479 | -0.041199 | 0.027466 | 0.43487 | 51.7868 | -0.20599 | 51.9516 | -0.041199 | -0.041199 | -0.054932 | 0.18768 | 0.10529 | 0.18768 | -0.050354 | 0.22888 | -0.009155 | 0.59967 | 122.4564 | 0.14648 | 122.493 | 122.3877 | 122.2504 | 122.2229 | 122.2092 | -122.4289 | -122.3053 | 122.2916 | 122.4518 | 52.5833 | 49.0494
1530.7656 | 122.5983 | -53.2837 | 68.9896 | -0.10979 | 0.0016983 | 0.062239 | 0.10971 | 0.00059812 | 0.0004914 | -0.0033112 | -0.04303 | -0.0034778 | 0.062042 | 0.064894 | -0.022732 | 0.0020551 | 0.00010689 | -1.4832 | 68.9026 | -53.4576 | 68.9529 | -52.8488 | -53.5767 | -2.3575 | -4.9026 | 68.8614 | -53.3707 | 69.072 | -53.1784 | -53.3798 | -53.1647 | -0.17395 | -0.086975 | -0.036621 | 0.43487 | 50.9262 | -0.29297 | 51.1002 | -0.11902 | -0.086976 | -0.12817 | 0.082397 | 0.10528 | 0.11902 | -0.096131 | 0.20599 | -0.009155 | 0.60883 | 122.4106 | 0.19226 | 122.4426 | 122.3602 | 122.2321 | 122.1863 | 122.1451 | -122.4472 | -122.3602 | 122.2366 | 122.3557 | 51.8005 | 48.381
1531.8281 | 122.5845 | -54.9774 | 67.3096 | -0.10216 | -0.00086512 | 0.063521 | 0.11013 | 0.00038452 | -0.0020722 | -0.0030976 | 0.011902 | -0.0030506 | 0.061402 | 0.060836 | -0.024227 | 0.0014141 | 0.00053409 | -1.8997 | 67.218 | -55.1559 | 67.2501 | -54.5563 | -55.2292 | -2.623 | -4.9622 | 67.2043 | -55.0552 | 67.392 | -54.7943 | -55.014 | -54.7989 | -0.17853 | -0.091552 | -0.059509 | 0.42114 | 52.3544 | -0.25177 | 52.533 | -0.073242 | -0.07782 | -0.10528 | 0.082398 | 0.18311 | 0.17853 | -0.036621 | 0.25635 | 0.041199 | 0.59967 | 122.406 | 0.26093 | 122.4472 | 122.374 | 122.2595 | 122.1954 | 122.1817 | -122.4655 | -122.3648 | 122.2275 | 122.3694 | 53.0777 | 50.0153
1532.7656 | 122.5433 | -53.0594 | 69.191 | -0.10979 | 0.0014847 | 0.062025 | 0.10971 | 0.00038452 | -0.0012176 | -0.0013886 | -0.04303 | -0.0017688 | 0.064392 | 0.059981 | -0.025082 | 0.0014141 | 0.00053409 | -1.4465 | 69.1315 | -53.2196 | 69.1589 | -52.6566 | -53.389 | -2.5818 | -4.5868 | 69.1269 | -53.1372 | 69.2825 | -52.9221 | -53.1921 | -52.9358 | -0.16022 | -0.059509 | -0.032043 | 0.40283 | 50.4776 | -0.32959 | 50.6378 | -0.16937 | -0.07782 | -0.064087 | 0.091553 | 0.13733 | 0.1236 | -0.13275 | 0.20142 | -0.054932 | 0.56305 | 122.3785 | 0.21515 | 122.4197 | 122.3511 | 122.2641 | 122.1909 | 122.1863 | -122.4106 | -122.3282 | 122.2183 | 122.3419 | 51.6129 | 48.4726
1533.8438 | 122.5296 | -53.1738 | 69.1681 | -0.07164 | 0.00020288 | 0.063094 | 0.11013 | -0.0021789 | -0.0035674 | -0.00074776 | -0.11322 | -0.002196 | 0.065033 | 0.063399 | -0.024013 | 0.0031231 | -0.00053411 | -1.4832 | 69.0216 | -53.4531 | 69.0399 | -52.7161 | -53.4943 | -2.4811 | -4.7424 | 69.0399 | -53.2745 | 69.1864 | -53.0594 | -53.3066 | -53.0502 | -0.27924 | -0.14648 | -0.12817 | 0.45776 | 50.6927 | -0.32043 | 50.972 | -0.041199 | -0.10071 | -0.12817 | 0.01831 | 0.11444 | 0.1236 | -0.13275 | 0.2243 | -0.032044 | 0.737 | 122.493 | 0.21515 | 122.4609 | 122.4747 | 122.3145 | 122.1954 | 122.2137 | -122.6212 | -122.4426 | 122.2137 | 122.3602 | 51.6907 | 48.4314
1534.7656 | 122.5754 | -53.1738 | 69.0903 | -0.1403 | -1.0718e-05 | 0.061171 | 0.10971 | 0.00059812 | 0.0011322 | -0.0018158 | -0.021667 | -0.0045458 | 0.06482 | 0.05934 | -0.023159 | 0.0029095 | 0.0026703 | -1.2543 | 69.1772 | -53.1967 | 69.0994 | -52.6382 | -53.4302 | -2.3254 | -4.541 | 69.0903 | -53.1921 | 69.1864 | -53.0319 | -53.2883 | -53.0548 | -0.022888 | 0.086975 | 0.009155 | 0.53558 | 50.8484 | -0.25635 | 50.8713 | -0.23346 | -0.018311 | 0 | 0.09613 | 0.14191 | 0.11902 | -0.11444 | 0.13733 | -0.09613 | 0.55847 | 122.2961 | 0.16022 | 122.3785 | 122.374 | 122.2824 | 122.3511 | 122.2641 | -122.287 | -122.2824 | 122.2733 | 122.3602 | 51.9196 | 48.6328
1535.8281 | 122.644 | -53.2059 | 69.072 | -0.10216 | -0.0015061 | 0.062453 | 0.11077 | 0.0035889 | -0.0031402 | -0.0013886 | -0.058289 | -0.0017688 | 0.063751 | 0.059127 | -0.024654 | 0.00077333 | 0.0050201 | -1.1765 | 69.1315 | -53.2608 | 69.1635 | -52.5238 | -53.3432 | -2.1698 | -4.6555 | 69.0308 | -53.2471 | 69.2825 | -53.1097 | -53.3661 | -53.096 | -0.054931 | 0.05951 | 0.091553 | 0.68207 | 51.0361 | -0.13733 | 51.091 | -0.082398 | -0.041198 | -0.041198 | 0.21057 | 0.096131 | 0.10986 | -0.16022 | 0.15106 | -0.11902 | 0.737 | 122.4243 | 0.13733 | 122.5296 | 122.3923 | 122.2778 | 122.3373 | 122.2366 | -122.3328 | -122.319 | 122.3694 | 122.4884 | 52.0294 | 48.5504
1536.7656 | 122.5891 | -53.5355 | 68.7195 | -0.26237 | 0.00041648 | 0.062025 | 0.108 | 0.0023071 | 0.000705 | 0.002243 | -0.052185 | -0.0034778 | 0.061402 | 0.060622 | -0.024868 | 0.00034613 | -0.00010671 | -1.4969 | 68.6096 | -53.7689 | 68.7012 | -52.6932 | -53.8101 | -2.4536 | -4.6326 | 68.6508 | -53.6087 | 68.8065 | -53.389 | -53.6453 | -53.4164 | -0.23346 | -0.10986 | -0.01831 | 0.84228 | 51.0818 | -0.27466 | 51.3153 | -0.041199 | -0.073243 | -0.068664 | 0.086976 | 0.14648 | 0.11902 | -0.10986 | 0.19226 | -0.036621 | 1.0757 | 122.4701 | 0.21973 | 122.4152 | 122.3785 | 122.2595 | 122.1451 | 122.1863 | -122.4884 | -122.3282 | 122.2366 | 122.3419 | 52.0386 | 48.9029
1537.8281 | 122.6028 | -52.5604 | 69.7266 | -0.11742 | 0.0010575 | 0.061385 | 0.10885 | 0.0038025 | -0.0020722 | 0.00010684 | -0.049133 | -0.0062548 | 0.062042 | 0.064467 | -0.022518 | 0.0014141 | -0.00096131 | -1.2268 | 69.6854 | -52.6794 | 69.7037 | -51.6403 | -52.8351 | -2.2659 | -4.4037 | 69.6671 | -52.6108 | 69.809 | -52.4002 | -52.6611 | -52.4048 | -0.11902 | -0.041198 | -0.022888 | 0.9201 | 50.2945 | -0.27466 | 50.4135 | -0.15564 | -0.050354 | -0.059509 | 0.082398 | 0.16022 | 0.15564 | -0.10071 | 0.20599 | -0.050354 | 1.0391 | 122.3831 | 0.21057 | 122.4197 | 122.3648 | 122.2778 | 122.2458 | 122.2275 | -122.406 | -122.3373 | 122.2641 | 122.3694 | 51.3336 | 48.1567
1538.7656 | 122.4976 | -51.8326 | 70.491 | -0.033493 | -0.0023605 | 0.061598 | 0.11013 | -0.0041015 | -0.0050628 | -0.0018158 | -0.06134 | -0.001128 | 0.063751 | 0.061263 | -0.023373 | 0.0012005 | -0.0013885 | -0.98419 | 70.5368 | -51.9424 | 70.4086 | -50.6973 | -52.1027 | -2.2751 | -4.4678 | 70.5002 | -51.8555 | 70.4773 | -51.741 | -51.9928 | -51.7639 | -0.10986 | 0.045776 | -0.082398 | 1.1353 | 49.5575 | -0.27008 | 49.6674 | -0.16022 | -0.022888 | 0.009155 | -0.013733 | 0.091553 | 0.068665 | -0.16022 | 0.091553 | -0.13733 | 1.2451 | 122.3511 | 0.11444 | 122.3328 | 122.4792 | 122.3557 | 122.3694 | 122.3328 | -122.4335 | -122.3465 | 122.2412 | 122.3099 | 50.8484 | 47.3648
1539.8281 | 122.6028 | -52.1988 | 70.0882 | -0.033493 | -0.0012923 | 0.060744 | 0.11035 | 0.00081172 | -0.0039948 | -0.002884 | -0.12848 | -0.0015552 | 0.060974 | 0.059981 | -0.024654 | 0.00055973 | 0.0022431 | -0.97504 | 69.9921 | -52.4277 | 70.0333 | -50.9033 | -52.0248 | -2.3987 | -4.1885 | 69.9646 | -52.2766 | 70.1752 | -51.9699 | -52.2263 | -52.0798 | -0.22888 | -0.096131 | -0.054932 | 1.2955 | 49.8001 | 0.17395 | 50.029 | 0.40283 | -0.077819 | -0.1236 | 0.086975 | 0.22888 | 0.11902 | -0.027465 | 0.19684 | 0.050354 | 1.5244 | 122.4609 | 0.3067 | 122.4518 | 122.4197 | 122.2412 | 122.1909 | 122.1634 | -122.5159 | -122.3648 | 122.2321 | 122.374 | 51.2238 | 48.0103
1540.7656 | 122.6257 | -52.9861 | 69.2825 | -0.094528 | 0.0012711 | 0.060744 | 0.10672 | -0.0019653 | -0.0005768 | -0.0020294 | -0.0064086 | -0.0019824 | 0.062897 | 0.059981 | -0.024868 | 0.0012005 | 0.0028839 | -1.2543 | 69.2688 | -53.1281 | 69.223 | -51.9836 | -53.334 | -2.5452 | -4.509 | 69.1772 | -53.0685 | 69.3329 | -52.8534 | -53.0777 | -52.8625 | -0.14191 | -0.013733 | -0.05951 | 1.0025 | 50.441 | -0.3479 | 50.5829 | -0.20599 | -0.082397 | -0.10529 | 0.050354 | 0.13275 | 0.1236 | -0.091553 | 0.20599 | -0.009156 | 1.1444 | 122.3511 | 0.21515 | 122.4014 | 122.3969 | 122.2458 | 122.2549 | 122.1634 | -122.4106 | -122.3511 | 122.2092 | 122.319 | 51.7319 | 48.4772
1541.8281 | 122.5616 | -51.8738 | 70.3903 | -0.15556 | 0.00063028 | 0.062025 | 0.10714 | -0.0013245 | -0.004422 | -0.00032036 | -0.049133 | -0.0032642 | 0.065033 | 0.063399 | -0.02615 | 0.00077333 | -0.0011749 | -1.1078 | 70.2576 | -52.1072 | 70.3171 | -50.7385 | -52.24 | -2.298 | -4.1748 | 70.2988 | -51.9791 | 70.4727 | -51.7639 | -51.9974 | -51.7776 | -0.23346 | -0.13275 | -0.073242 | 1.1353 | 49.5758 | -0.36621 | 49.8093 | -0.13275 | -0.10529 | -0.091553 | 0.082397 | 0.10986 | 0.09613 | -0.1236 | 0.20142 | -0.01831 | 1.3687 | 122.4243 | 0.21515 | 122.4518 | 122.3648 | 122.2778 | 122.1313 | 122.1725 | -122.4976 | -122.3694 | 122.1909 | 122.3465 | 50.766 | 47.699
1542.7656 | 122.4747 | -51.4297 | 70.9534 | -0.048752 | 0.0010575 | 0.061385 | 0.10971 | 0.0010253 | -0.0048492 | -0.0033112 | -0.049133 | -0.0026232 | 0.063111 | 0.060622 | -0.025509 | 0.0022687 | 0.0013885 | -1.1124 | 70.9717 | -51.5167 | 70.8206 | -50.0656 | -51.6861 | -2.2293 | -4.1656 | 70.9167 | -51.4252 | 70.7336 | -51.3245 | -51.5305 | -51.3107 | -0.086975 | 0.018311 | -0.13275 | 1.3641 | 49.2004 | -0.25635 | 49.2874 | -0.16937 | 0.004578 | -0.036621 | -0.21973 | 0.10529 | 0.11902 | -0.10071 | 0.11444 | -0.10529 | 1.4511 | 122.3373 | 0.10071 | 122.1588 | 122.4884 | 122.3419 | 122.4014 | 122.3465 | -122.4701 | -122.3785 | 122.2504 | 122.1634 | 50.3174 | 47.2641
1543.8438 | 122.5616 | -51.6357 | 70.6879 | -0.086899 | 0.00084388 | 0.063521 | 0.11077 | 0.0057251 | -0.002713 | 0.0016022 | -0.11017 | -0.002196 | 0.065888 | 0.07173 | -0.024868 | 0.0033367 | 0.0045929 | -0.99792 | 70.7977 | -51.6861 | 70.7291 | -50.1617 | -51.7548 | -1.8723 | -4.1473 | 70.7703 | -51.59 | 70.6879 | -51.5717 | -51.8188 | -51.5808 | -0.050354 | 0.10986 | 0.041199 | 1.474 | 49.7635 | -0.11902 | 49.8138 | -0.068665 | 0.045776 | 0.082398 | 0 | 0.064087 | 0.054931 | -0.18311 | 0.009155 | -0.22888 | 1.5244 | 122.4152 | 0.018311 | 122.2778 | 122.4838 | 122.3602 | 122.4335 | 122.406 | -122.374 | -122.2778 | 122.3648 | 122.3236 | 50.6378 | 47.4884
1544.7656 | 122.5937 | -51.9104 | 70.372 | -0.11742 | -0.00022432 | 0.061812 | 0.10949 | 0.00081172 | -0.0001496 | 0.00053404 | -0.039978 | -0.0032642 | 0.060333 | 0.062117 | -0.026363 | 0.00077333 | 0.0011749 | -1.0849 | 70.1019 | -52.2583 | 70.1981 | -50.6058 | -52.2995 | -1.9272 | -4.2801 | 70.2805 | -51.9653 | 70.4269 | -51.8097 | -52.0752 | -51.8234 | -0.3479 | -0.27008 | -0.17395 | 1.3046 | 49.9832 | -0.3891 | 50.3311 | -0.041199 | -0.054932 | -0.091552 | 0.054932 | 0.10071 | 0.086975 | -0.16479 | 0.14191 | -0.10986 | 1.6525 | 122.4564 | 0.15564 | 122.3923 | 122.3602 | 122.2458 | 122.0123 | 122.1909 | -122.6303 | -122.3373 | 122.1085 | 122.3373 | 50.8255 | 47.6303
1545.8281 | 122.5754 | -52.5055 | 69.7998 | -0.10979 | 0.0038345 | 0.063094 | 0.11206 | -0.00025628 | -0.0018586 | -0.0020294 | -0.024719 | -0.0032642 | 0.064179 | 0.062758 | -0.022945 | 0.00013253 | 0.0024567 | -1.3367 | 69.7037 | -52.6978 | 69.7678 | -51.1322 | -52.7435 | -2.1423 | -4.6417 | 69.722 | -52.5513 | 69.8135 | -52.4002 | -52.6062 | -52.3956 | -0.19226 | -0.096131 | -0.032044 | 1.3733 | 50.3632 | -0.23804 | 50.5554 | -0.045776 | -0.045777 | -0.07782 | 0.013733 | 0.10529 | 0.10986 | -0.10071 | 0.15564 | -0.054931 | 1.5656 | 122.4655 | 0.15106 | 122.3648 | 122.4014 | 122.2733 | 122.2092 | 122.2275 | -122.4976 | -122.3511 | 122.2733 | 122.319 | 51.1688 | 47.8638
1546.7656 | 122.6166 | -52.9816 | 69.3054 | -0.10216 | -0.00086512 | 0.061385 | 0.10971 | -4.2682e-05 | -0.0020722 | -0.0033112 | -0.088806 | -0.0017688 | 0.064606 | 0.062331 | -0.025082 | 0.0016277 | 0.0013885 | -1.5656 | 69.0765 | -53.302 | 69.31 | -51.9974 | -52.8625 | -2.536 | -4.5822 | 69.2093 | -53.0823 | 69.3695 | -52.803 | -53.0365 | -52.8351 | -0.32044 | -0.22888 | 0.004578 | 0.98419 | 50.4456 | 0.11902 | 50.766 | 0.43945 | -0.10071 | -0.09613 | 0.064087 | 0.17853 | 0.14648 | -0.054932 | 0.24719 | 0.045776 | 1.3046 | 122.612 | 0.27923 | 122.4518 | 122.3785 | 122.2916 | 122.0581 | 122.1909 | -122.6074 | -122.3877 | 122.2916 | 122.3511 | 51.416 | 48.3994
1547.8281 | 122.5616 | -53.0731 | 69.2322 | -0.11742 | 0.0027665 | 0.063094 | 0.10928 | 0.0029479 | -0.0029266 | -0.00010676 | -0.052185 | -0.0032642 | 0.062897 | 0.058913 | -0.024227 | 0.0022687 | 0.0024567 | -1.4923 | 69.1956 | -53.2425 | 69.191 | -52.5604 | -53.3432 | -2.5177 | -4.7928 | 69.1681 | -53.1143 | 69.2734 | -52.9587 | -53.1876 | -52.9449 | -0.16937 | -0.036621 | -0.041199 | 0.5127 | 50.5554 | -0.27008 | 50.7248 | -0.10071 | -0.041199 | -0.064087 | 0.041198 | 0.11444 | 0.12817 | -0.11444 | 0.16937 | -0.073242 | 0.68207 | 122.4335 | 0.15564 | 122.3877 | 122.4381 | 122.2824 | 122.2687 | 122.2412 | -122.4747 | -122.3465 | 122.2641 | 122.3465 | 51.5808 | 48.2803
1548.7656 | 122.5937 | -54.0115 | 68.2892 | -0.079269 | 0.00020288 | 0.062666 | 0.11013 | 0.0010253 | -0.0012176 | -0.0026704 | -0.033874 | -0.0024096 | 0.06482 | 0.055068 | -0.024868 | 0.0018413 | -0.00096131 | -1.6617 | 68.3075 | -54.0802 | 68.3624 | -53.4164 | -54.2267 | -2.5818 | -4.9438 | 68.2114 | -54.0665 | 68.3533 | -53.8742 | -54.1306 | -53.8696 | -0.068664 | 0.01831 | 0.073242 | 0.59509 | 51.4297 | -0.21515 | 51.4984 | -0.14649 | -0.054931 | -0.07782 | 0.064086 | 0.13733 | 0.14191 | -0.11902 | 0.19684 | -0.064087 | 0.66376 | 122.4426 | 0.19226 | 122.4197 | 122.3877 | 122.2778 | 122.319 | 122.2229 | -122.3694 | -122.3557 | 122.374 | 122.3648 | 52.3499 | 49.0677
1549.8281 | 122.6486 | -52.858 | 69.4382 | -0.079269 | 0.0012711 | 0.062666 | 0.10885 | 0.0031617 | -0.0016448 | -0.001175 | -0.0064086 | -0.0049732 | 0.064179 | 0.055922 | -0.025295 | 0.00013253 | 0.0018159 | -1.4648 | 69.3832 | -53.0228 | 69.429 | -51.8051 | -53.1006 | -2.2156 | -4.66 | 69.3787 | -52.9129 | 69.5114 | -52.6611 | -52.8992 | -52.7069 | -0.16479 | -0.054931 | -0.009155 | 1.0529 | 50.6424 | -0.24262 | 50.8072 | -0.07782 | -0.054932 | -0.059509 | 0.073243 | 0.19684 | 0.15106 | -0.041199 | 0.20599 | 0.013733 | 1.2177 | 122.4518 | 0.25177 | 122.4243 | 122.406 | 122.2916 | 122.2412 | 122.2366 | -122.4609 | -122.3511 | 122.287 | 122.3694 | 51.3931 | 48.1979
1550.7656 | 122.5616 | -52.0615 | 70.2301 | -0.10979 | 0.0016983 | 0.064162 | 0.11013 | 0.0018799 | -0.0014312 | -0.002243 | -0.052185 | -0.0051868 | 0.061829 | 0.059981 | -0.024654 | 0.00077333 | 0.0022431 | -1.6937 | 70.2118 | -52.1805 | 70.1202 | -50.8255 | -52.4231 | -2.2614 | -4.4769 | 70.134 | -52.1439 | 70.3033 | -51.9653 | -52.1896 | -51.9516 | -0.11902 | -0.018311 | -0.10986 | 1.236 | 49.8001 | -0.36163 | 49.9191 | -0.24262 | -0.082398 | -0.096131 | 0.073242 | 0.09613 | 0.10986 | -0.12817 | 0.19226 | -0.045776 | 1.355 | 122.3007 | 0.17853 | 122.4472 | 122.3923 | 122.2778 | 122.2733 | 122.1954 | -122.4106 | -122.374 | 122.1817 | 122.3648 | 50.3677 | 47.5845
1551.8281 | 122.5479 | -51.6724 | 70.6329 | -0.10979 | 0.0014847 | 0.062666 | 0.11077 | 0.0040161 | -0.0024994 | -0.002243 | -0.033874 | -0.0013416 | 0.062897 | 0.061049 | -0.0238 | 0.0024823 | 0.0020295 | -1.4923 | 70.6329 | -51.7822 | 70.6696 | -50.1755 | -51.8555 | -2.0416 | -4.422 | 70.6238 | -51.6632 | 70.6604 | -51.5671 | -51.7868 | -51.5442 | -0.10986 | 0 | 0.036621 | 1.4969 | 49.6307 | -0.18311 | 49.7406 | -0.073242 | 0.009155 | -0.009156 | 0.027465 | 0.10528 | 0.12817 | -0.11444 | 0.11902 | -0.1236 | 1.6068 | 122.4518 | 0.09613 | 122.3236 | 122.4152 | 122.287 | 122.3053 | 122.2961 | -122.4152 | -122.2961 | 122.3419 | 122.3328 | 50.1801 | 47.2504
1552.7656 | 122.5937 | -51.6678 | 70.5963 | -0.018234 | 0.0021255 | 0.064375 | 0.11013 | -0.00068368 | -0.0016448 | -0.0037384 | -0.027771 | -0.0034778 | 0.063965 | 0.065962 | -0.026577 | 0.0018413 | -0.00032051 | -1.9501 | 70.5826 | -51.828 | 70.6741 | -50.2441 | -51.8143 | -2.0279 | -4.2938 | 70.6558 | -51.6129 | 70.7199 | -51.5259 | -51.7593 | -51.5533 | -0.16022 | -0.013732 | 0.07782 | 1.4236 | 49.6399 | -0.14648 | 49.8001 | 0.013733 | 0.054932 | 0.05951 | 0.1236 | 0.14191 | 0.11444 | -0.091552 | 0.059509 | -0.14648 | 1.5839 | 122.5021 | 0.086975 | 122.3328 | 122.4106 | 122.2687 | 122.2504 | 122.3236 | -122.4243 | -122.2092 | 122.3419 | 122.3877 | 49.7177 | 47.374
1553.8281 | 122.58 | -51.6129 | 70.7062 | -0.25475 | 0.0012711 | 0.06288 | 0.11013 | -0.0017517 | -0.0014312 | -0.001175 | 0.0027466 | -0.0024096 | 0.064179 | 0.054 | -0.025082 | 0.0024823 | 0.00074769 | -1.4282 | 70.7382 | -51.6815 | 70.7382 | -50.1892 | -51.8097 | -1.9547 | -4.4952 | 70.752 | -51.5854 | 70.7336 | -51.503 | -51.7364 | -51.5213 | -0.068665 | 0.032043 | 0.032043 | 1.4236 | 49.6582 | -0.19684 | 49.7269 | -0.12817 | 0.027466 | 0.045776 | 0.027466 | 0.10986 | 0.091553 | -0.1236 | 0.064087 | -0.15106 | 1.4923 | 122.4197 | 0.082397 | 122.319 | 122.4197 | 122.3373 | 122.3511 | 122.3648 | -122.3877 | -122.2916 | 122.3511 | 122.3465 | 50.1846 | 47.1176
1554.7656 | 122.5433 | -52.0477 | 70.2713 | -0.079269 | 0.0016983 | 0.062239 | 0.10842 | 0.00038452 | -0.0018586 | 0.00053404 | -0.027771 | -0.0045458 | 0.065033 | 0.06404 | -0.025509 | 0.0014141 | 0.00053409 | -1.506 | 70.2164 | -52.2125 | 70.2301 | -51.0544 | -52.3132 | -1.8265 | -4.3716 | 70.166 | -52.1255 | 70.2896 | -51.9058 | -52.1576 | -51.947 | -0.1648 | -0.054931 | -0.041198 | 0.99335 | 50.2213 | -0.2655 | 50.386 | -0.10071 | -0.07782 | -0.10528 | 0.018311 | 0.14191 | 0.10071 | -0.10986 | 0.17853 | -0.032044 | 1.1581 | 122.4426 | 0.21973 | 122.4152 | 122.4289 | 122.2916 | 122.2641 | 122.2137 | -122.4838 | -122.3969 | 122.2778 | 122.3373 | 50.5417 | 47.6761
1555.8281 | 122.612 | -51.6724 | 70.6512 | -0.12505 | -0.00043792 | 0.061812 | 0.10885 | 0.0023071 | -0.0018586 | -0.0018158 | -0.018616 | -0.0041186 | 0.064606 | 0.054213 | -0.024441 | 0.0022687 | 0.00010689 | -1.5152 | 70.6146 | -51.8234 | 70.61 | -50.8804 | -51.9287 | -1.767 | -4.216 | 70.4269 | -51.86 | 70.6879 | -51.4938 | -51.7227 | -51.503 | -0.15106 | -0.036621 | -0.041199 | 0.79193 | 49.9054 | -0.25635 | 50.0565 | -0.10529 | -0.18768 | -0.2243 | 0.036621 | 0.17853 | 0.16937 | -0.050354 | 0.35705 | 0.13733 | 0.94299 | 122.4335 | 0.36621 | 122.5479 | 122.438 | 122.287 | 122.287 | 122.0993 | -122.4747 | -122.5113 | 122.2824 | 122.3602 | 50.1572 | 47.4564
1556.7656 | 122.6074 | -51.796 | 70.4819 | -0.10216 | -1.0718e-05 | 0.061598 | 0.11184 | 0.0023071 | -0.0024994 | -0.0018158 | -0.015564 | -0.0043322 | 0.061829 | 0.061904 | -0.028072 | 0.0024823 | -0.00010671 | -1.5656 | 70.2576 | -52.1118 | 70.4086 | -50.9445 | -52.1164 | -1.8311 | -4.0237 | 70.3903 | -51.8967 | 70.5688 | -51.6266 | -51.8692 | -51.6861 | -0.31586 | -0.2243 | -0.073243 | 0.85144 | 49.9649 | -0.32043 | 50.2808 | -0.004578 | -0.10071 | -0.091553 | 0.086975 | 0.16937 | 0.10986 | -0.073243 | 0.21057 | 0.027465 | 1.1673 | 122.5204 | 0.27008 | 122.4655 | 122.3694 | 122.287 | 122.0535 | 122.1863 | -122.5937 | -122.3785 | 122.2046 | 122.3648 | 50.2304 | 47.7722
1557.8281 | 122.5754 | -51.7731 | 70.5322 | -0.11742 | -0.0019333 | 0.059889 | 0.1112 | 0.0029479 | -0.0024994 | -0.0016022 | -0.021667 | -0.0019824 | 0.061402 | 0.059127 | -0.025295 | 0.0022687 | 0.0013885 | -1.5289 | 70.4681 | -51.9836 | 70.4498 | -50.6516 | -52.1164 | -1.8402 | -4.184 | 70.4269 | -51.8509 | 70.5597 | -51.6586 | -51.8784 | -51.6495 | -0.21057 | -0.064087 | -0.082398 | 1.1215 | 49.9329 | -0.34332 | 50.1434 | -0.13275 | -0.07782 | -0.10529 | 0.027465 | 0.11444 | 0.1236 | -0.10529 | 0.20142 | -0.027466 | 1.3321 | 122.4335 | 0.19226 | 122.4106 | 122.4518 | 122.2778 | 122.2412 | 122.2 | -122.5159 | -122.3831 | 122.2229 | 122.3328 | 50.2441 | 47.5891
1558.7656 | 122.5662 | -50.5508 | 71.7682 | -0.16319 | 0.0029801 | 0.061385 | 0.10928 | -4.2682e-05 | -0.0037812 | -0.001175 | -0.039978 | -0.0024096 | 0.062683 | 0.057845 | -0.024441 | 0.0039777 | 0.0024567 | -1.442 | 71.6492 | -50.7523 | 71.5439 | -49.3561 | -50.9949 | -1.6434 | -3.7582 | 71.5897 | -50.6653 | 71.7499 | -50.473 | -50.7294 | -50.4593 | -0.20142 | -0.11902 | -0.2243 | 1.1948 | 48.9075 | -0.44403 | 49.1089 | -0.24262 | -0.11444 | -0.17853 | -0.01831 | 0.07782 | 0.091552 | -0.17853 | 0.20599 | -0.064087 | 1.3962 | 122.2961 | 0.19226 | 122.4152 | 122.4014 | 122.2549 | 122.2 | 122.1405 | -122.5204 | -122.4335 | 122.0947 | 122.3007 | 49.1089 | 46.7926
1559.8281 | 122.5708 | -51.1002 | 71.2051 | -0.086899 | -0.0012923 | 0.061598 | 0.10885 | 0.0012391 | -0.002713 | -0.00010676 | -0.052185 | -0.0041186 | 0.062256 | 0.059554 | -0.024868 | 0.00098693 | 0.0037385 | -1.6754 | 71.1777 | -51.2329 | 71.1227 | -49.8917 | -51.4343 | -1.5884 | -4.0375 | 71.1456 | -51.1688 | 71.2143 | -50.9857 | -51.2283 | -51.0086 | -0.13275 | -0.027466 | -0.082397 | 1.2085 | 49.5117 | -0.33417 | 49.6445 | -0.20142 | -0.068664 | -0.059509 | 0.009155 | 0.11444 | 0.091553 | -0.12817 | 0.16022 | -0.05951 | 1.3412 | 122.3557 | 0.18311 | 122.3831 | 122.4106 | 122.3145 | 122.2778 | 122.2458 | -122.438 | -122.374 | 122.2229 | 122.3145 | 49.4247 | 47.0627
1560.7656 | 122.5662 | -51.7502 | 70.5276 | -0.12505 | 0.0016983 | 0.062453 | 0.108 | -0.0017517 | -0.0039948 | -0.0024566 | -0.024719 | -0.0041186 | 0.064392 | 0.055495 | -0.02615 | 0.0041913 | -0.0011749 | -1.6388 | 70.4178 | -51.9791 | 70.4407 | -50.4456 | -52.0981 | -1.7853 | -4.0054 | 70.4681 | -51.8509 | 70.5139 | -51.7044 | -51.8463 | -51.6449 | -0.22888 | -0.10986 | -0.086975 | 1.3046 | 49.9649 | -0.3479 | 50.1938 | -0.11902 | -0.10071 | -0.059509 | -0.013733 | 0.045776 | 0.10529 | -0.09613 | 0.20599 | 0.004578 | 1.5335 | 122.4197 | 0.14648 | 122.3648 | 122.3969 | 122.319 | 122.168 | 122.2183 | -122.5067 | -122.3785 | 122.1909 | 122.2641 | 50.1114 | 47.7448
1561.8281 | 122.6303 | -52.1118 | 70.1843 | -0.15556 | 0.00041648 | 0.061812 | 0.11099 | -4.2682e-05 | -0.0033538 | -0.0041656 | -0.036926 | -0.0036914 | 0.063751 | 0.060622 | -0.023373 | 0.0012005 | 0.00074769 | -1.6296 | 70.2118 | -52.1988 | 70.2072 | -51.2878 | -52.3361 | -1.8311 | -4.0833 | 70.1523 | -52.1576 | 70.2667 | -51.947 | -52.1988 | -52.0065 | -0.086976 | 0.027466 | 0.022888 | 0.82397 | 50.2808 | -0.22431 | 50.3677 | -0.13733 | -0.045777 | -0.032043 | 0.082398 | 0.16479 | 0.10528 | -0.086976 | 0.15106 | -0.041199 | 0.91095 | 122.406 | 0.21057 | 122.4243 | 122.4106 | 122.3099 | 122.3236 | 122.2641 | -122.3831 | -122.3419 | 122.319 | 122.3785 | 50.4822 | 48.0286
1562.7656 | 122.5571 | -51.9379 | 70.3857 | -0.056381 | 0.00084388 | 0.062666 | 0.11142 | -0.0021789 | -0.0014312 | -0.0035248 | -0.10406 | -0.00027343 | 0.063751 | 0.064681 | -0.022945 | 0.0035503 | -0.0039521 | -1.5472 | 70.3857 | -52.0889 | 70.2667 | -51.2375 | -52.272 | -1.9409 | -4.0329 | 70.3857 | -52.002 | 70.3491 | -51.8692 | -52.1301 | -51.8967 | -0.15106 | 0 | -0.11902 | 0.70038 | 49.9969 | -0.33417 | 50.148 | -0.18311 | -0.064087 | 0 | -0.036621 | 0.068664 | 0.041199 | -0.19226 | 0.10529 | -0.12817 | 0.85144 | 122.3557 | 0.13275 | 122.3511 | 122.4747 | 122.3877 | 122.3236 | 122.3236 | -122.4747 | -122.3877 | 122.2046 | 122.287 | 50.3906 | 47.905
1563.8281 | 122.5754 | -52.4963 | 69.8227 | -0.10979 | 0.00041648 | 0.062239 | 0.10949 | 0.0052979 | -0.0016448 | -0.001175 | -0.018616 | -0.0026232 | 0.061829 | 0.060408 | -0.024227 | 0.00034613 | -0.00074771 | -1.8311 | 69.754 | -52.6566 | 69.754 | -51.6769 | -52.803 | -1.9775 | -4.2709 | 69.7632 | -52.5375 | 69.8318 | -52.359 | -52.6154 | -52.3865 | -0.16022 | -0.068665 | -0.068665 | 0.8194 | 50.5188 | -0.3067 | 50.679 | -0.14649 | -0.041199 | -0.059509 | 0.009155 | 0.13733 | 0.10986 | -0.11902 | 0.15106 | -0.077819 | 0.97961 | 122.4106 | 0.17853 | 122.3694 | 122.4106 | 122.3007 | 122.2504 | 122.2595 | -122.4792 | -122.3602 | 122.2504 | 122.3282 | 50.6653 | 48.2254
1564.7656 | 122.6212 | -51.9287 | 70.3674 | -0.094528 | -0.00065152 | 0.058394 | 0.1112 | -0.00046988 | 0.000705 | -0.0016022 | -0.021667 | -0.0047594 | 0.063751 | 0.058272 | -0.024654 | 0.0020551 | -0.0026703 | -1.8173 | 70.3217 | -52.0798 | 70.3766 | -51.0086 | -52.1576 | -2.0782 | -4.3259 | 70.2988 | -52.0111 | 70.4727 | -51.7502 | -52.002 | -51.8097 | -0.15106 | -0.045777 | 0.009155 | 0.9201 | 49.8505 | -0.22888 | 50.0015 | -0.07782 | -0.082397 | -0.068665 | 0.10529 | 0.17853 | 0.11902 | -0.073242 | 0.20142 | 0.009155 | 1.0712 | 122.4564 | 0.26093 | 122.4838 | 122.4014 | 122.3099 | 122.2504 | 122.2275 | -122.4472 | -122.3785 | 122.3053 | 122.4014 | 50.1114 | 47.6028
1565.8281 | 122.6303 | -51.4893 | 70.7062 | -0.094528 | 0.00063028 | 0.064162 | 0.11227 | -4.2682e-05 | -0.0020722 | -0.001175 | -0.067444 | -0.0028368 | 0.06247 | 0.065108 | -0.025295 | 0.0018413 | -0.00096131 | -1.3229 | 71.283 | -51.1093 | 71.3699 | -50.1389 | -51.2054 | -1.6205 | -4.0146 | 71.3242 | -50.9674 | 71.2006 | -51.3748 | -51.6632 | -51.535 | 0.37994 | 0.57678 | 0.66376 | 1.3504 | 49.8688 | 0.28381 | 49.4888 | -0.09613 | 0.52185 | 0.61798 | 0.49439 | 0.11444 | -0.045776 | -0.17395 | -0.56763 | -0.6958 | 0.97046 | 122.4792 | -0.40741 | 122.168 | 122.3923 | 122.2916 | 122.7722 | 122.8134 | -121.8155 | -121.6736 | 122.8592 | 122.6898 | 50.1663 | 47.4747
1566.7656 | 122.5616 | -50.56 | 71.7453 | -0.12505 | 0.0016983 | 0.062453 | 0.10928 | 0.0025207 | -0.0018586 | -0.00032036 | -0.024719 | -0.0036914 | 0.063111 | 0.055709 | -0.02615 | 0.0031231 | 0.00032049 | -1.3641 | 71.6949 | -50.7294 | 71.6492 | -49.7726 | -50.853 | -1.4099 | -4.1061 | 71.7178 | -50.6424 | 71.7773 | -50.4456 | -50.6744 | -50.4593 | -0.16937 | -0.050354 | -0.09613 | 0.78735 | 49.1501 | -0.29297 | 49.3195 | -0.1236 | -0.082397 | -0.027466 | 0.032044 | 0.11444 | 0.10071 | -0.11444 | 0.1831 | -0.032043 | 0.95673 | 122.3785 | 0.19684 | 122.4197 | 122.4243 | 122.3602 | 122.2549 | 122.2778 | -122.4747 | -122.3877 | 122.2092 | 122.3373 | 49.1959 | 46.4539
1567.8281 | 122.4792 | -51.1826 | 71.2006 | -0.086899 | 0.0021255 | 0.061812 | 0.11312 | -0.0011109 | -0.0029266 | -0.0037384 | -0.036926 | -0.0019824 | 0.061402 | 0.060836 | -0.024868 | 0.0022687 | 0.0020295 | -1.4282 | 71.1365 | -51.3062 | 71.0449 | -50.2487 | -51.4664 | -1.3 | -4.1336 | 71.0815 | -51.2512 | 71.1456 | -51.0864 | -51.3336 | -51.1139 | -0.1236 | -0.064087 | -0.15564 | 0.93384 | 49.8825 | -0.28381 | 50.0061 | -0.16022 | -0.068665 | -0.11902 | -0.054932 | 0.09613 | 0.068664 | -0.15106 | 0.13733 | -0.082397 | 1.0574 | 122.3511 | 0.16479 | 122.3969 | 122.4426 | 122.3328 | 122.319 | 122.2641 | -122.5067 | -122.4518 | 122.2275 | 122.3282 | 49.7543 | 47.0489
1568.7656 | 122.5891 | -51.1002 | 71.1365 | -0.018234 | 0.00041648 | 0.062239 | 0.11142 | -0.0021789 | -0.0033538 | -0.0033112 | 0.0027466 | -0.003905 | 0.063111 | 0.060195 | -0.028072 | 0.00098693 | 0.0013885 | -1.5656 | 71.0175 | -51.3657 | 71.1548 | -49.7635 | -51.3474 | -1.3962 | -3.9825 | 71.077 | -51.178 | 71.3058 | -50.9262 | -51.1551 | -50.9949 | -0.2655 | -0.11902 | 0.01831 | 1.3367 | 49.704 | -0.24719 | 49.9695 | 0.018311 | -0.07782 | -0.05951 | 0.16937 | 0.17395 | 0.10529 | -0.054931 | 0.18311 | 0.022889 | 1.6022 | 122.5204 | 0.25177 | 122.4838 | 122.3831 | 122.2549 | 122.1176 | 122.1771 | -122.5021 | -122.3145 | 122.2549 | 122.406 | 49.5346 | 47.1176
1569.8281 | 122.6257 | -50.9033 | 71.3791 | -0.086899 | 0.00020288 | 0.061385 | 0.10992 | 0.00081172 | -0.0035674 | -0.0024566 | -0.0094604 | -0.0034778 | 0.061615 | 0.055281 | -0.0238 | 0.0018413 | 0.00053409 | -1.4877 | 71.2418 | -51.1505 | 71.3104 | -49.617 | -51.2009 | -1.1856 | -3.8086 | 71.2784 | -51.0086 | 71.4844 | -50.6744 | -51.0223 | -50.7751 | -0.24719 | -0.13733 | -0.068664 | 1.2863 | 49.7177 | -0.29755 | 49.9649 | -0.050354 | -0.10529 | -0.10071 | 0.10529 | 0.22888 | 0.12817 | -0.11902 | 0.23346 | -0.013733 | 1.5335 | 122.4609 | 0.33417 | 122.493 | 122.3923 | 122.287 | 122.1451 | 122.1817 | -122.5296 | -122.3877 | 122.2137 | 122.3877 | 49.4156 | 47.0947
1570.7656 | 122.6166 | -51.2421 | 71.077 | -0.11742 | 0.0012711 | 0.062239 | 0.10971 | -4.2682e-05 | -0.0033538 | -0.0033112 | -0.021667 | -0.0013416 | 0.065033 | 0.059767 | -0.025722 | 0.0012005 | 0.0033111 | -1.7075 | 70.9808 | -51.4755 | 70.9396 | -49.7681 | -51.5717 | -1.3596 | -4.0283 | 70.9259 | -51.3611 | 71.1182 | -51.1139 | -51.3107 | -51.1185 | -0.23346 | -0.09613 | -0.13733 | 1.474 | 49.8825 | -0.32959 | 50.116 | -0.09613 | -0.11902 | -0.15106 | 0.041199 | 0.12817 | 0.1236 | -0.068665 | 0.24262 | 0.050354 | 1.7075 | 122.4152 | 0.24719 | 122.4792 | 122.4564 | 122.287 | 122.2229 | 122.168 | -122.5525 | -122.438 | 122.1817 | 122.3602 | 49.5346 | 47.2137
1571.8281 | 122.612 | -50.1709 | 72.1436 | -0.086899 | 0.00063028 | 0.063948 | 0.11013 | -0.0013245 | -0.002713 | -0.002243 | -0.055237 | -0.0015552 | 0.061615 | 0.05699 | -0.024654 | 0.0037641 | 0.0050201 | -1.4877 | 72.2351 | -50.1892 | 72.1939 | -48.8022 | -50.3586 | -1.4008 | -3.8223 | 72.084 | -50.2167 | 72.1619 | -50.0565 | -50.2853 | -50.0748 | -0.018311 | 0.091552 | 0.050354 | 1.3687 | 48.7701 | -0.18768 | 48.7885 | -0.16937 | -0.045777 | -0.05951 | 0.01831 | 0.11444 | 0.09613 | -0.11444 | 0.14191 | -0.068664 | 1.387 | 122.3831 | 0.16022 | 122.3785 | 122.4243 | 122.3007 | 122.406 | 122.2549 | -122.3328 | -122.3602 | 122.3648 | 122.3328 | 48.6832 | 46.3486
1572.7656 | 122.4792 | -49.3515 | 73.0133 | -0.07164 | -0.00043792 | 0.062666 | 0.1127 | 0.0074341 | -0.0029266 | -0.00010676 | -0.14374 | -0.0049732 | 0.063965 | 0.067031 | -0.026363 | 0.0037641 | 0.0016021 | -1.3733 | 72.9172 | -49.5712 | 72.8531 | -47.9507 | -49.704 | -1.3779 | -3.8361 | 72.9721 | -49.411 | 72.9584 | -49.3469 | -49.5712 | -49.3332 | -0.21973 | -0.096131 | -0.16022 | 1.4008 | 47.9736 | -0.35248 | 48.1934 | -0.13275 | -0.05951 | -0.041199 | -0.054932 | 0.004577 | 0.01831 | -0.21973 | 0.07782 | -0.16022 | 1.6205 | 122.4243 | 0.064087 | 122.3694 | 122.4884 | 122.3831 | 122.2687 | 122.3236 | -122.5845 | -122.4243 | 122.2046 | 122.3099 | 47.9782 | 45.5154
1573.7656 | 122.5891 | -50.3174 | 71.9788 | -0.10979 | 0.0010575 | 0.06053 | 0.10928 | -0.0011109 | -0.0012176 | -0.002243 | -0.0064086 | -0.0047594 | 0.063538 | 0.056349 | -0.024227 | 0.0024823 | 0.00032049 | -1.5976 | 71.8277 | -50.5737 | 71.8369 | -48.8754 | -50.647 | -1.3229 | -3.9642 | 71.8735 | -50.4089 | 72.0291 | -50.1892 | -50.3952 | -50.1801 | -0.25635 | -0.15106 | -0.14191 | 1.442 | 48.9944 | -0.32959 | 49.2508 | -0.073243 | -0.091553 | -0.10529 | 0.050354 | 0.12817 | 0.13733 | -0.07782 | 0.22888 | 0.013733 | 1.6983 | 122.4106 | 0.21973 | 122.4381 | 122.4014 | 122.2824 | 122.1451 | 122.1909 | -122.5525 | -122.3877 | 122.1542 | 122.3465 | 48.7198 | 46.3531
1574.8281 | 122.4976 | -50.386 | 71.9971 | -0.056381 | 0.0016983 | 0.059462 | 0.11077 | -0.0017517 | -0.0022858 | -0.00074776 | -0.06134 | -0.005614 | 0.063965 | 0.062545 | -0.023159 | 0.0012005 | 0.0041657 | -1.8814 | 71.8826 | -50.5325 | 71.8826 | -49.054 | -50.6332 | -1.6571 | -4.0375 | 71.9513 | -50.4044 | 71.9467 | -50.322 | -50.5692 | -50.3494 | -0.14649 | -0.11444 | -0.11444 | 1.3321 | 48.7289 | -0.24719 | 48.8754 | -0.10071 | -0.018311 | -0.045776 | -0.050354 | 0.064087 | 0.036621 | -0.18311 | 0.054932 | -0.16479 | 1.4786 | 122.4152 | 0.082398 | 122.3511 | 122.4152 | 122.3557 | 122.2687 | 122.3373 | -122.5296 | -122.4014 | 122.2687 | 122.3328 | 48.5046 | 46.3486
1575.7656 | 122.6349 | -51.5396 | 70.8069 | -0.10216 | -0.00022432 | 0.062666 | 0.10864 | -0.0034607 | -0.002713 | -0.0018158 | -0.0064086 | -0.0045458 | 0.06247 | 0.056349 | -0.023159 | 0.00077333 | 0.0020295 | -1.9363 | 70.9946 | -51.4206 | 70.6787 | -50.6561 | -51.8829 | -1.9318 | -4.4952 | 70.6512 | -51.6541 | 70.816 | -51.3428 | -51.6129 | -51.384 | 0.11902 | 0.18768 | -0.12817 | 0.88348 | 49.6078 | -0.34332 | 49.4888 | -0.46234 | -0.11444 | -0.15564 | 0.009155 | 0.19684 | 0.15564 | -0.073242 | 0.27008 | 0.041199 | 0.76446 | 122.0993 | 0.31128 | 122.4701 | 122.4152 | 122.3053 | 122.5342 | 122.1909 | -122.2275 | -122.4609 | 122.2183 | 122.3557 | 49.6033 | 47.0444
1576.8281 | 122.644 | -51.6403 | 70.6375 | -0.06401 | -0.00086512 | 0.061812 | 0.11077 | 0.00059812 | -0.0005768 | -0.0024566 | 0.0088502 | -0.003905 | 0.062683 | 0.060408 | -0.023159 | 0.00098693 | -0.0035247 | -1.8265 | 70.6833 | -51.741 | 70.7062 | -50.5096 | -51.7776 | -1.5244 | -4.1473 | 70.6375 | -51.6815 | 70.7108 | -51.5167 | -51.7364 | -51.5396 | -0.10071 | 0.045777 | 0.068665 | 1.1307 | 50.116 | -0.13733 | 50.2167 | -0.036621 | -0.041199 | 0 | 0.073242 | 0.1236 | 0.10071 | -0.09613 | 0.14191 | -0.054931 | 1.2314 | 122.4472 | 0.16479 | 122.3923 | 122.4243 | 122.319 | 122.3236 | 122.2778 | -122.3785 | -122.319 | 122.3465 | 122.3511 | 49.8138 | 47.493
1577.7656 | 122.5388 | -51.4481 | 70.9396 | -0.07164 | 0.0010575 | 0.062453 | 0.11035 | -0.0013245 | -0.0012176 | -0.0030976 | -0.11017 | -0.0028368 | 0.064179 | 0.062117 | -0.025295 | 0.0029095 | 0.00074769 | -1.8906 | 70.9625 | -51.5213 | 70.816 | -50.5188 | -51.7136 | -1.5152 | -4.4083 | 70.8618 | -51.4893 | 70.8618 | -51.3702 | -51.6037 | -51.3657 | -0.073242 | 0.022888 | -0.1236 | 0.92926 | 49.9329 | -0.2655 | 50.0061 | -0.19226 | -0.041199 | -0.07782 | -0.07782 | 0.07782 | 0.082397 | -0.15564 | 0.1236 | -0.11444 | 1.0025 | 122.3373 | 0.11902 | 122.3511 | 122.4838 | 122.3511 | 122.4106 | 122.3099 | -122.4609 | -122.4289 | 122.2641 | 122.3099 | 49.5575 | 47.0398
1578.8281 | 122.5571 | -52.0477 | 70.2942 | -0.10216 | -1.0718e-05 | 0.063307 | 0.10992 | -0.0034607 | -0.0037812 | -0.0013886 | -0.018616 | -0.0028368 | 0.064606 | 0.061476 | -0.025295 | 0.0014141 | -0.0011749 | -1.8814 | 70.2026 | -52.2263 | 70.2347 | -51.2054 | -52.272 | -1.4877 | -4.422 | 70.1935 | -52.0981 | 70.3125 | -51.8967 | -52.1347 | -51.9196 | -0.17853 | -0.091552 | -0.059509 | 0.84228 | 50.56 | -0.22431 | 50.7385 | -0.045777 | -0.050354 | -0.10071 | 0.018311 | 0.15106 | 0.12817 | -0.086976 | 0.17853 | -0.036622 | 1.0208 | 122.4609 | 0.20142 | 122.4106 | 122.4289 | 122.2916 | 122.2504 | 122.2412 | -122.5204 | -122.3923 | 122.2824 | 122.3602 | 50.1663 | 47.6257
1579.7656 | 122.6257 | -52.7252 | 69.6075 | -0.13267 | 0.00084388 | 0.062025 | 0.10864 | -0.0036743 | -0.0022858 | -0.0035248 | -0.00030524 | -0.0041186 | 0.06247 | 0.056563 | -0.027004 | 0.00055973 | 0.00053409 | -1.9684 | 69.6396 | -52.7618 | 69.6487 | -51.9058 | -52.8763 | -1.5289 | -4.5364 | 69.5938 | -52.684 | 69.6167 | -52.6154 | -52.8351 | -52.6245 | -0.036621 | 0.032043 | 0.041199 | 0.8194 | 51.1963 | -0.15106 | 51.2329 | -0.11444 | 0.041199 | -0.013733 | 0.009155 | 0.10986 | 0.10071 | -0.10986 | 0.059509 | -0.15106 | 0.85602 | 122.4106 | 0.068665 | 122.3007 | 122.4014 | 122.2778 | 122.3648 | 122.319 | -122.3694 | -122.2916 | 122.374 | 122.3419 | 50.7568 | 48.1888
1580.8281 | 122.4976 | -52.4094 | 69.9783 | -0.11742 | -0.00022432 | 0.059676 | 0.10928 | 0.0014527 | -0.0035674 | -0.0035248 | -0.070496 | -0.0015552 | 0.063965 | 0.059554 | -0.024441 | 0.0035503 | 0.0048065 | -1.9501 | 69.9966 | -52.5375 | 69.8318 | -51.7364 | -52.6703 | -1.4236 | -4.5364 | 69.9417 | -52.4048 | 69.9051 | -52.3407 | -52.5833 | -52.3224 | -0.12817 | 0.01831 | -0.14649 | 0.67291 | 50.9857 | -0.26093 | 51.1139 | -0.13275 | 0.004578 | -0.036622 | -0.073243 | 0.068665 | 0.086975 | -0.17395 | 0.082397 | -0.17853 | 0.80109 | 122.3694 | 0.064087 | 122.3099 | 122.5342 | 122.3465 | 122.406 | 122.3511 | -122.5159 | -122.3831 | 122.2412 | 122.3145 | 50.4593 | 47.8729
1581.7656 | 122.5021 | -51.9882 | 70.4361 | -0.0029755 | -0.0023605 | 0.057539 | 0.11142 | 0.00059812 | -0.0014312 | -0.002884 | -0.058289 | -0.0036914 | 0.063538 | 0.064681 | -0.026577 | -0.00050847 | 0.0035247 | -1.886 | 70.4224 | -52.0615 | 70.2209 | -51.1505 | -52.1988 | -1.3092 | -4.5502 | 70.372 | -52.0248 | 70.2988 | -51.8875 | -52.1301 | -51.8829 | -0.073242 | -0.013733 | -0.21515 | 0.83771 | 50.679 | -0.21057 | 50.7523 | -0.13733 | -0.036621 | -0.064087 | -0.13733 | 0.10071 | 0.10528 | -0.14191 | 0.14191 | -0.10529 | 0.91095 | 122.2824 | 0.13733 | 122.3236 | 122.4838 | 122.3969 | 122.4106 | 122.3602 | -122.4976 | -122.4609 | 122.2092 | 122.287 | 50.1022 | 47.438
1582.8281 | 122.6212 | -51.6541 | 70.665 | -0.1403 | 0.00063028 | 0.063094 | 0.11013 | 0.0035889 | -0.0031402 | -0.002243 | -0.00030524 | -0.0047594 | 0.060761 | 0.054 | -0.024441 | -0.0011493 | 0.0039521 | -2.005 | 70.6375 | -51.8005 | 70.5826 | -50.4684 | -51.9058 | -1.2497 | -4.4266 | 70.6238 | -51.6998 | 70.7199 | -51.503 | -51.7319 | -51.535 | -0.14648 | -0.027466 | -0.082397 | 1.1856 | 50.4044 | -0.25177 | 50.5508 | -0.10529 | -0.045776 | -0.041199 | 0.054932 | 0.15106 | 0.11902 | -0.07782 | 0.16479 | -0.032044 | 1.3321 | 122.3831 | 0.19684 | 122.4197 | 122.438 | 122.3236 | 122.2916 | 122.2778 | -122.4655 | -122.3648 | 122.2366 | 122.374 | 49.649 | 47.2275
1583.7656 | 122.5204 | -51.4481 | 70.9351 | -0.06401 | 0.0010575 | 0.061385 | 0.11035 | -0.0028199 | -0.0018586 | -0.0018158 | -0.033874 | -0.0028368 | 0.063538 | 0.06404 | -0.026363 | 0.0012005 | 0.0022431 | -1.8311 | 70.9076 | -51.535 | 70.8481 | -50.5692 | -51.6953 | -1.2131 | -4.4312 | 70.8801 | -51.4755 | 70.8847 | -51.3519 | -51.5991 | -51.4069 | -0.086975 | -0.027466 | -0.086976 | 0.87891 | 50.235 | -0.24719 | 50.322 | -0.16022 | -0.027466 | -0.054932 | -0.050354 | 0.09613 | 0.041199 | -0.15106 | 0.068665 | -0.1236 | 0.96588 | 122.3831 | 0.1236 | 122.3602 | 122.4426 | 122.3557 | 122.3557 | 122.3282 | -122.4701 | -122.4106 | 122.2961 | 122.3328 | 49.617 | 47.0169
1584.8281 | 122.5388 | -50.9354 | 71.4432 | -0.10216 | -0.00022432 | 0.062453 | 0.1112 | -0.00068368 | -0.0035674 | -0.00053396 | -0.10101 | -0.003905 | 0.063538 | 0.064681 | -0.026577 | 0.0026959 | 0.00096129 | -1.7532 | 71.5347 | -50.9674 | 71.315 | -49.9374 | -51.2466 | -1.2634 | -4.3808 | 71.3608 | -51.0132 | 71.3882 | -50.8255 | -51.0681 | -50.8301 | -0.032043 | 0.091553 | -0.12817 | 0.99793 | 49.6719 | -0.31128 | 49.704 | -0.27924 | -0.07782 | -0.082397 | -0.054931 | 0.10986 | 0.10529 | -0.13275 | 0.18311 | -0.054931 | 1.03 | 122.2824 | 0.18768 | 122.4014 | 122.5021 | 122.374 | 122.4701 | 122.2961 | -122.4106 | -122.4564 | 122.2504 | 122.3236 | 49.1821 | 46.5546
1585.7656 | 122.5708 | -50.9033 | 71.4661 | -0.10216 | 0.0025529 | 0.059889 | 0.10992 | 0.00081172 | -0.0022858 | -0.004593 | -0.0094604 | -0.0019824 | 0.063751 | 0.053572 | -0.025722 | 0.0029095 | -0.0013885 | -1.4557 | 71.4066 | -51.0086 | 71.4203 | -49.2783 | -51.0773 | -0.75989 | -4.1656 | 71.4157 | -50.8987 | 71.4523 | -50.7477 | -50.9995 | -50.7889 | -0.10529 | -0.059509 | -0.045776 | 1.6251 | 50.1434 | -0.17395 | 50.2487 | -0.068665 | 0.004577 | -0.050354 | -0.013732 | 0.15564 | 0.11444 | -0.096131 | 0.10986 | -0.10071 | 1.7303 | 122.4289 | 0.15106 | 122.3511 | 122.4152 | 122.3145 | 122.3099 | 122.319 | -122.4747 | -122.3648 | 122.3236 | 122.3557 | 49.4476 | 46.7377
1586.8281 | 122.5616 | -51.5121 | 70.871 | -0.086899 | 0.0019119 | 0.06053 | 0.11163 | 0.00038452 | -0.0024994 | -0.0024566 | -0.10101 | -0.0019824 | 0.063538 | 0.05934 | -0.025082 | 0.0039777 | 0.0026703 | -1.5701 | 70.8939 | -51.59 | 70.7474 | -50.3036 | -51.8097 | -1.0941 | -4.4586 | 70.7932 | -51.59 | 70.8481 | -51.416 | -51.6632 | -51.4069 | -0.07782 | 0.022888 | -0.1236 | 1.2085 | 50.4181 | -0.29755 | 50.4959 | -0.21973 | -0.07782 | -0.07782 | -0.022889 | 0.09613 | 0.10529 | -0.15106 | 0.18311 | -0.073242 | 1.2863 | 122.3373 | 0.17395 | 122.438 | 122.4838 | 122.3831 | 122.406 | 122.3053 | -122.4609 | -122.4609 | 122.2595 | 122.3602 | 49.942 | 47.0535
1587.7656 | 122.5616 | -50.3952 | 71.9696 | -0.056381 | 0.0016983 | 0.060744 | 0.11398 | 0.00081172 | -0.0037812 | -0.00053396 | -0.064392 | -0.00048703 | 0.065888 | 0.059554 | -0.024868 | -8.1274e-05 | 0.0016021 | -1.5335 | 71.8643 | -50.6378 | 71.8002 | -49.0311 | -50.7202 | -0.78735 | -4.1245 | 71.8506 | -50.5188 | 71.9559 | -50.2762 | -50.5234 | -50.2853 | -0.24261 | -0.10529 | -0.16937 | 1.3641 | 49.6078 | -0.32501 | 49.8505 | -0.082398 | -0.1236 | -0.11902 | -0.013732 | 0.11902 | 0.10986 | -0.12817 | 0.23346 | -0.004577 | 1.6067 | 122.438 | 0.24262 | 122.4747 | 122.5021 | 122.3694 | 122.2595 | 122.2458 | -122.6074 | -122.4884 | 122.1954 | 122.3511 | 48.8617 | 46.2708
1588.7656 | 122.5159 | -52.2079 | 70.1752 | -0.10979 | 0.00020288 | 0.060957 | 0.10971 | -0.0013245 | -0.0039948 | -0.0035248 | -0.012512 | -0.0024096 | 0.063751 | 0.06169 | -0.026577 | -8.1274e-05 | 0.0043793 | -1.5884 | 70.1569 | -52.3499 | 70.0104 | -50.9995 | -52.4826 | -0.90179 | -4.5456 | 70.134 | -52.2537 | 70.1248 | -52.2629 | -52.3682 | -52.0981 | -0.14191 | -0.018311 | -0.1648 | 1.2085 | 51.3062 | -0.27466 | 51.4481 | -0.13275 | -0.045776 | -0.041199 | -0.050354 | -0.054931 | 0.10986 | -0.16022 | 0.15564 | -0.11444 | 1.3504 | 122.3602 | -0.009155 | 122.3785 | 122.5067 | 122.3877 | 122.3648 | 122.3419 | -122.525 | -122.4289 | 122.2183 | 122.3328 | 50.6195 | 47.6624
1589.8281 | 122.6303 | -50.0153 | 72.2946 | -0.10979 | 0.00084388 | 0.060744 | 0.10971 | 0.0042297 | -0.0029266 | -0.0035248 | 0.033264 | -0.0019824 | 0.06546 | 0.060195 | -0.024441 | 0.0014141 | 0.0018159 | -1.5289 | 72.2076 | -50.2167 | 72.2214 | -48.2162 | -50.3036 | -0.58594 | -4.2297 | 72.1619 | -50.1572 | 72.345 | -49.8596 | -50.0702 | -49.8459 | -0.20142 | -0.086975 | -0.073242 | 1.799 | 49.4293 | -0.28839 | 49.6307 | -0.086975 | -0.14191 | -0.13275 | 0.050354 | 0.15564 | 0.16937 | -0.054931 | 0.31128 | 0.086976 | 2.0004 | 122.4381 | 0.29755 | 122.5021 | 122.4243 | 122.319 | 122.2229 | 122.1771 | -122.5113 | -122.4518 | 122.2366 | 122.3602 | 48.4863 | 45.7855
1590.7656 | 122.5845 | -50.6195 | 71.7499 | -0.0029755 | 0.0014847 | 0.062239 | 0.11227 | -4.2682e-05 | -0.0003632 | 0.00053404 | -0.079651 | -0.0017688 | 0.064606 | 0.057204 | -0.026791 | 0.0031231 | 0.00010689 | -1.6983 | 71.6675 | -50.7843 | 71.5759 | -49.2188 | -50.972 | -0.78278 | -4.541 | 71.6263 | -50.7111 | 71.6904 | -50.5463 | -50.7843 | -50.5234 | -0.16479 | -0.082398 | -0.17395 | 1.4008 | 49.8367 | -0.35248 | 50.0015 | -0.18768 | -0.091553 | -0.1236 | -0.059509 | 0.073242 | 0.096131 | -0.16479 | 0.18768 | -0.073242 | 1.5656 | 122.3602 | 0.1648 | 122.4014 | 122.4518 | 122.3373 | 122.287 | 122.2458 | -122.5342 | -122.4609 | 122.1954 | 122.3099 | 48.9212 | 46.0785
1591.8281 | 122.5616 | -49.7223 | 72.6334 | -0.018234 | -0.00086512 | 0.061598 | 0.11013 | 0.0025207 | -0.0024994 | -0.00053396 | -0.091858 | -0.0013416 | 0.065674 | 0.063613 | -0.026577 | 0.0067547 | 0.0011749 | -1.6067 | 72.6929 | -49.7818 | 72.6013 | -47.8409 | -49.9741 | -0.63629 | -4.4495 | 72.6471 | -49.7269 | 72.5784 | -49.6628 | -49.7635 | -49.585 | -0.059509 | 0.059509 | -0.032044 | 1.8814 | 49.086 | -0.25177 | 49.1455 | -0.19226 | -0.004578 | 0.013733 | -0.054932 | 0.059509 | 0.13733 | -0.041199 | 0.14191 | -0.036621 | 1.9409 | 122.3831 | 0.064087 | 122.3053 | 122.4747 | 122.374 | 122.4152 | 122.3694 | -122.4152 | -122.3602 | 122.3236 | 122.3007 | 48.1155 | 45.2728
1592.7656 | 122.5479 | -49.3652 | 73.0316 | -0.06401 | 0.0014847 | 0.061385 | 0.11334 | 0.0018799 | -0.0014312 | -0.0033112 | -0.046081 | -0.0028368 | 0.064392 | 0.061263 | -0.025936 | 0.0018413 | 0.0024567 | -1.5289 | 73.0545 | -49.4431 | 72.9172 | -47.0261 | -49.6353 | -0.65918 | -4.3854 | 73.0133 | -49.3652 | 72.9904 | -49.2737 | -49.4934 | -49.3057 | -0.07782 | 0.022888 | -0.11444 | 2.3392 | 48.7061 | -0.27008 | 48.7839 | -0.19226 | 0 | -0.01831 | -0.041199 | 0.091552 | 0.059509 | -0.12817 | 0.059509 | -0.12817 | 2.417 | 122.3602 | 0.091552 | 122.3557 | 122.4976 | 122.3785 | 122.4197 | 122.3785 | -122.4747 | -122.3969 | 122.2824 | 122.3557 | 47.8363 | 44.9799
1593.8281 | 122.5433 | -49.5575 | 72.8027 | -0.056381 | 0.0010575 | 0.060957 | 0.11035 | 0.0025207 | -0.0035674 | -0.00096136 | -0.030823 | -0.002196 | 0.063965 | 0.058486 | -0.025295 | 0.00034613 | -0.0013885 | -1.6113 | 72.6791 | -49.7955 | 72.6425 | -47.1588 | -49.9466 | -0.78278 | -4.3488 | 72.7158 | -49.6582 | 72.8165 | -49.4705 | -49.704 | -49.4705 | -0.23804 | -0.1236 | -0.16022 | 2.3987 | 48.7747 | -0.3891 | 49.0128 | -0.15106 | -0.10071 | -0.086975 | 0.013733 | 0.086975 | 0.086975 | -0.14648 | 0.18768 | -0.045776 | 2.6367 | 122.438 | 0.18768 | 122.4747 | 122.4747 | 122.374 | 122.2366 | 122.2733 | -122.5983 | -122.4609 | 122.2 | 122.374 | 47.9462 | 45.2087
1594.7656 | 122.525 | -49.6216 | 72.7844 | -0.056381 | 0.0031937 | 0.063734 | 0.11099 | 0.0029479 | -0.0031402 | 0.00010684 | -0.018616 | -0.0024096 | 0.06546 | 0.056563 | -0.024654 | 0.0018413 | 0.0077973 | -1.4694 | 72.7203 | -49.8001 | 72.5876 | -47.3007 | -49.9191 | -0.7782 | -4.3854 | 72.6974 | -49.6811 | 72.6562 | -49.5804 | -49.8184 | -49.5804 | -0.17853 | -0.064087 | -0.19684 | 2.3209 | 48.8434 | -0.29755 | 49.0219 | -0.11902 | -0.059509 | -0.086975 | -0.12817 | 0.041199 | 0.041199 | -0.19684 | 0.10071 | -0.13733 | 2.4994 | 122.3877 | 0.10071 | 122.3373 | 122.5204 | 122.3785 | 122.3419 | 122.319 | -122.5845 | -122.4655 | 122.2092 | 122.2778 | 48.1522 | 45.2362
1595.8281 | 122.5708 | -48.9349 | 73.4436 | -0.041122 | 0.0044755 | 0.064162 | 0.11142 | 0.0012391 | -0.0031402 | -0.002884 | -0.064392 | -0.0017688 | 0.062897 | 0.060836 | -0.028286 | 0.0037641 | 0.0028839 | -1.474 | 73.4299 | -49.0356 | 73.3246 | -46.5683 | -49.2004 | -0.5722 | -4.2068 | 73.3978 | -48.9532 | 73.4116 | -48.8342 | -49.0677 | -48.8571 | -0.10071 | -0.013733 | -0.11902 | 2.3666 | 48.3627 | -0.2655 | 48.4634 | -0.16479 | -0.01831 | -0.045777 | -0.032044 | 0.10071 | 0.07782 | -0.13275 | 0.09613 | -0.11444 | 2.4673 | 122.3602 | 0.11902 | 122.3648 | 122.4655 | 122.3511 | 122.3648 | 122.3328 | -122.4792 | -122.3969 | 122.2595 | 122.3465 | 47.4609 | 44.7281
1596.7656 | 122.5113 | -49.6857 | 72.7066 | -0.025863 | 0.00041648 | 0.062453 | 0.10949 | 0.0027343 | -0.0050628 | -0.003952 | -0.052185 | -0.0017688 | 0.063538 | 0.061263 | -0.02615 | 0.0026959 | 0.00074769 | -1.5656 | 72.7203 | -49.8184 | 72.5372 | -47.525 | -49.9832 | -0.77362 | -4.4403 | 72.6471 | -49.736 | 72.5967 | -49.6307 | -49.8596 | -49.6445 | -0.13275 | 0.013733 | -0.16937 | 2.1606 | 48.912 | -0.29755 | 49.0448 | -0.16479 | -0.050354 | -0.059509 | -0.10986 | 0.054932 | 0.041199 | -0.17395 | 0.091553 | -0.1236 | 2.2934 | 122.3557 | 0.10529 | 122.3328 | 122.5388 | 122.3831 | 122.406 | 122.3328 | -122.525 | -122.4426 | 122.2229 | 122.2824 | 48.1201 | 45.2454
1597.8281 | 122.5296 | -49.8001 | 72.5967 | -0.1403 | 0.00041648 | 0.062453 | 0.1127 | -0.00068368 | -0.0031402 | 0.00053404 | -0.070496 | -0.0028368 | 0.063965 | 0.062117 | -0.026577 | 0.0022687 | 0.0018159 | -1.6617 | 72.5372 | -49.9878 | 72.377 | -47.7173 | -50.1709 | -0.78735 | -4.6051 | 72.5143 | -49.8734 | 72.5281 | -49.7726 | -49.9969 | -49.736 | -0.18768 | -0.05951 | -0.21973 | 2.0828 | 49.0128 | -0.37079 | 49.2004 | -0.1831 | -0.073242 | -0.082398 | -0.068665 | 0.027466 | 0.064087 | -0.19684 | 0.13733 | -0.1236 | 2.2705 | 122.3648 | 0.10071 | 122.4014 | 122.525 | 122.3877 | 122.3373 | 122.3145 | -122.5845 | -122.4701 | 122.1771 | 122.3282 | 48.1384 | 45.195
1598.7656 | 122.5708 | -49.1821 | 73.1689 | -0.056381 | 0.0010575 | 0.06288 | 0.11184 | 0.0035889 | -0.001004 | -0.0033112 | -0.058289 | -0.0034778 | 0.066742 | 0.059127 | -0.025082 | 0.0022687 | 0.0033111 | -1.3962 | 73.1964 | -49.3149 | 73.0957 | -47.0764 | -49.4705 | -0.56763 | -4.184 | 73.1186 | -49.2188 | 73.1689 | -49.086 | -49.3423 | -49.1089 | -0.13275 | 0.027466 | -0.073242 | 2.1057 | 48.6145 | -0.28839 | 48.7473 | -0.15564 | -0.036621 | -0.050354 | 0 | 0.09613 | 0.073242 | -0.16022 | 0.10986 | -0.1236 | 2.2385 | 122.4106 | 0.13275 | 122.3877 | 122.5113 | 122.3373 | 122.3785 | 122.3007 | -122.4838 | -122.3877 | 122.2778 | 122.3511 | 47.7859 | 44.9982
1599.8281 | 122.5571 | -49.4202 | 72.9904 | -0.041122 | -1.0718e-05 | 0.063734 | 0.11056 | -4.2682e-05 | 6.4004e-05 | -0.0052338 | -0.027771 | -0.0028368 | 0.062042 | 0.062972 | -0.025722 | 0.0018413 | -0.0016021 | -1.4328 | 72.995 | -49.5117 | 72.8348 | -47.2733 | -49.7086 | -0.59967 | -4.3762 | 72.8943 | -49.4705 | 72.9172 | -49.3286 | -49.5529 | -49.3378 | -0.091553 | 0.004578 | -0.15564 | 2.1469 | 48.8205 | -0.28839 | 48.912 | -0.19684 | -0.050354 | -0.09613 | -0.073242 | 0.091553 | 0.082397 | -0.13275 | 0.13275 | -0.082397 | 2.2385 | 122.3465 | 0.14191 | 122.3877 | 122.5067 | 122.3648 | 122.4152 | 122.3145 | -122.5021 | -122.4609 | 122.2549 | 122.3373 | 47.9874 | 45.0439
1600.7656 | 122.58 | -49.205 | 73.1735 | -0.041122 | 0.00063028 | 0.062666 | 0.11013 | 0.0040161 | -0.001004 | -0.00053396 | -0.052185 | -0.0030506 | 0.063751 | 0.065535 | -0.025722 | -8.1274e-05 | 0.0013885 | -1.4877 | 72.9858 | -49.4659 | 72.9675 | -46.8063 | -49.5621 | -0.54016 | -4.4815 | 73.0225 | -49.3103 | 73.2056 | -49.1409 | -49.3332 | -49.0814 | -0.26093 | -0.18768 | -0.20599 | 2.3987 | 48.6649 | -0.35706 | 48.9258 | -0.096131 | -0.10529 | -0.15106 | 0.032043 | 0.064087 | 0.1236 | -0.12817 | 0.22888 | -0.022888 | 2.6596 | 122.4335 | 0.16937 | 122.5159 | 122.4518 | 122.3328 | 122.1909 | 122.2275 | -122.6395 | -122.4838 | 122.1725 | 122.4106 | 47.7173 | 44.7235
1601.8281 | 122.5754 | -48.381 | 73.9746 | -0.048752 | 0.00063028 | 0.061598 | 0.11163 | 0.00081172 | -0.0039948 | 0.00053404 | -0.06134 | -0.0013416 | 0.064392 | 0.061904 | -0.024013 | 0.0050457 | 0.0033111 | -1.3229 | 73.8693 | -48.5916 | 73.819 | -45.6665 | -48.6328 | -0.44403 | -4.1794 | 73.8831 | -48.4406 | 73.9792 | -48.2941 | -48.5504 | -48.3032 | -0.21057 | -0.10528 | -0.15564 | 2.7145 | 47.937 | -0.25177 | 48.1476 | -0.041198 | -0.05951 | -0.091552 | 0.004578 | 0.086975 | 0.077819 | -0.16937 | 0.13733 | -0.10986 | 2.9251 | 122.4106 | 0.14648 | 122.4197 | 122.4609 | 122.3236 | 122.2504 | 122.2641 | -122.5662 | -122.4152 | 122.2 | 122.3602 | 47.0581 | 44.2017
1602.7656 | 122.5525 | -48.3856 | 74.0158 | -0.07164 | 0.0021255 | 0.065443 | 0.1127 | -0.0011109 | -0.002713 | -0.0026704 | -0.046081 | -0.0054004 | 0.065033 | 0.055068 | -0.026791 | 0.00055973 | -0.0024567 | -1.3046 | 73.7778 | -48.7152 | 73.6862 | -45.9732 | -48.8297 | -0.35706 | -4.1016 | 73.8327 | -48.5458 | 73.9151 | -48.2803 | -48.5321 | -48.2712 | -0.32959 | -0.23804 | -0.32959 | 2.4124 | 48.0286 | -0.44403 | 48.3582 | -0.11444 | -0.16022 | -0.18311 | -0.10071 | 0.10529 | 0.11444 | -0.14648 | 0.27466 | 0.013733 | 2.742 | 122.4014 | 0.2655 | 122.4609 | 122.493 | 122.3785 | 122.1634 | 122.2183 | -122.731 | -122.5616 | 122.0718 | 122.3007 | 47.081 | 44.2841
1603.8281 | 122.5296 | -50.5554 | 71.8369 | -0.048752 | 0.0023391 | 0.062666 | 0.11184 | 0.0027343 | -0.0003632 | 0.00074764 | -0.058289 | -0.0017688 | 0.062897 | 0.05934 | -0.026363 | 0.0029095 | 0.0022431 | -1.8265 | 71.8231 | -50.6836 | 71.6904 | -49.0997 | -50.8621 | -0.64087 | -4.8111 | 71.7453 | -50.6012 | 71.7453 | -50.473 | -50.7477 | -50.5005 | -0.12817 | -0.013733 | -0.14648 | 1.4557 | 49.9146 | -0.3067 | 50.0427 | -0.17853 | -0.045776 | -0.091553 | -0.091553 | 0.082398 | 0.054932 | -0.19226 | 0.10071 | -0.14648 | 1.5839 | 122.374 | 0.12817 | 122.3465 | 122.5067 | 122.3465 | 122.3785 | 122.3007 | -122.5204 | -122.438 | 122.2458 | 122.3007 | 48.7289 | 45.7443
1604.7656 | 122.5708 | -51.5625 | 70.784 | -0.094528 | 0.00084388 | 0.06288 | 0.11142 | 0.0035889 | -0.0014312 | -0.001175 | -0.064392 | -0.0047594 | 0.065247 | 0.055281 | -0.02615 | 0.0022687 | 0.00096129 | -2.0645 | 70.7108 | -51.7822 | 70.6421 | -50.4272 | -51.8875 | -0.62256 | -4.9805 | 70.7199 | -51.6495 | 70.752 | -51.5167 | -51.7502 | -51.4984 | -0.21973 | -0.073243 | -0.14191 | 1.1353 | 50.9399 | -0.32501 | 51.1597 | -0.10529 | -0.086975 | -0.064087 | -0.032044 | 0.045776 | 0.064087 | -0.18768 | 0.15106 | -0.10071 | 1.355 | 122.4243 | 0.13275 | 122.4014 | 122.493 | 122.3694 | 122.2733 | 122.2824 | -122.5662 | -122.4335 | 122.2046 | 122.3145 | 49.498 | 46.582
1605.8281 | 122.5571 | -51.535 | 70.8572 | -0.12505 | 0.00084388 | 0.062025 | 0.11099 | 0.0016663 | -0.0024994 | -0.001175 | -0.055237 | -0.0036914 | 0.063538 | 0.067458 | -0.02615 | -0.0017901 | 0.0018159 | -2.0874 | 70.9442 | -51.5442 | 70.697 | -50.2533 | -51.8646 | -0.64087 | -5.2185 | 70.7794 | -51.59 | 70.9808 | -51.5854 | -51.8143 | -51.4893 | -0.009155 | 0.086975 | -0.16022 | 1.2817 | 50.8942 | -0.32959 | 50.9033 | -0.32043 | -0.054932 | -0.07782 | 0.1236 | -0.050354 | 0.045776 | -0.27924 | 0.10071 | -0.2243 | 1.2909 | 122.2412 | 0.004578 | 122.5708 | 122.4884 | 122.3694 | 122.4792 | 122.3145 | -122.4014 | -122.4472 | 122.2321 | 122.5159 | 49.4476 | 46.3165
1606.7656 | 122.525 | -50.5783 | 71.7773 | -0.07164 | -0.0015061 | 0.063094 | 0.11334 | -4.2682e-05 | -0.0020722 | -0.0013886 | -0.033874 | -0.001128 | 0.063111 | 0.060622 | -0.027218 | -0.00029487 | 0.0020295 | -1.9409 | 71.5897 | -50.9079 | 71.5485 | -49.205 | -51.0086 | -0.53558 | -4.7836 | 71.6217 | -50.7156 | 71.7499 | -50.528 | -50.766 | -50.5371 | -0.32959 | -0.18768 | -0.22888 | 1.3733 | 50.0427 | -0.4303 | 50.3723 | -0.10071 | -0.13733 | -0.15564 | -0.027466 | 0.050354 | 0.041199 | -0.18768 | 0.17853 | -0.050354 | 1.7029 | 122.4564 | 0.18768 | 122.4655 | 122.4976 | 122.3373 | 122.168 | 122.2 | -122.6852 | -122.493 | 122.1268 | 122.3282 | 48.6374 | 45.7947
1607.8281 | 122.493 | -49.2462 | 73.1735 | -0.10979 | 0.0010575 | 0.065016 | 0.11142 | 0.00017092 | -0.0012176 | -0.001175 | -0.1712 | -0.0054004 | 0.063538 | 0.058058 | -0.027431 | 0.00098693 | 0.0033111 | -1.5244 | 73.0545 | -49.4476 | 72.9675 | -46.962 | -49.5895 | -0.28839 | -4.2801 | 73.1094 | -49.2737 | 73.0774 | -49.1821 | -49.4064 | -49.1547 | -0.20142 | -0.11902 | -0.20599 | 2.2842 | 48.9578 | -0.34332 | 49.1592 | -0.14191 | -0.027466 | -0.064087 | -0.09613 | 0.064087 | 0.091553 | -0.16022 | 0.11902 | -0.13275 | 2.4857 | 122.4152 | 0.091553 | 122.3511 | 122.5021 | 122.3831 | 122.3007 | 122.3557 | -122.6212 | -122.4472 | 122.2137 | 122.3236 | 47.7219 | 44.9661
1608.7656 | 122.5021 | -50.0565 | 72.2809 | -0.12505 | -0.0017197 | 0.061171 | 0.11184 | 0.0018799 | -0.0020722 | -0.00010676 | -0.039978 | -0.0034778 | 0.065033 | 0.067458 | -0.025936 | 0.00077333 | 0.0028839 | -1.6891 | 72.3038 | -50.1938 | 72.1573 | -48.4314 | -50.386 | -0.3479 | -4.7333 | 72.226 | -50.116 | 72.2443 | -50.0244 | -50.2808 | -50.0153 | -0.13733 | 0.022888 | -0.1236 | 1.6251 | 49.7086 | -0.32959 | 49.8459 | -0.19226 | -0.059509 | -0.054932 | -0.036621 | 0.032044 | 0.041199 | -0.2243 | 0.10071 | -0.1648 | 1.7624 | 122.3511 | 0.091553 | 122.3602 | 122.4976 | 122.3419 | 122.3602 | 122.2824 | -122.4747 | -122.3969 | 122.2137 | 122.3007 | 48.3673 | 45.3232
1609.8281 | 122.6395 | -48.8617 | 73.4344 | -0.1403 | 0.0031937 | 0.065016 | 0.10885 | 0.0025207 | -0.0042084 | -0.001175 | 0.027161 | -0.0019824 | 0.061402 | 0.058913 | -0.027431 | 0.00013253 | -0.00074771 | -1.6754 | 73.3292 | -49.054 | 73.407 | -46.5179 | -49.205 | -0.16479 | -4.4266 | 73.3521 | -48.9441 | 73.4802 | -48.7885 | -48.9944 | -48.7656 | -0.19226 | -0.10529 | -0.027466 | 2.3438 | 48.6969 | -0.34332 | 48.8892 | -0.15106 | -0.082398 | -0.082397 | 0.045777 | 0.073242 | 0.09613 | -0.13275 | 0.17853 | -0.050354 | 2.536 | 122.4609 | 0.15564 | 122.4243 | 122.3831 | 122.2961 | 122.1909 | 122.2137 | -122.4884 | -122.3785 | 122.2687 | 122.3419 | 47.1863 | 44.4351
1610.7656 | 122.493 | -49.4934 | 72.8622 | -0.10979 | -0.00043792 | 0.06288 | 0.11206 | -0.0013245 | -0.0052764 | -0.0013886 | -0.049133 | -0.002196 | 0.061615 | 0.058272 | -0.025936 | 0.00077333 | 0.0035247 | -1.6342 | 72.7982 | -49.6857 | 72.7478 | -47.58 | -49.8276 | -0.16937 | -4.6738 | 72.7936 | -49.5758 | 72.7478 | -49.4934 | -49.7269 | -49.4614 | -0.19226 | -0.064087 | -0.11444 | 1.9135 | 49.324 | -0.33417 | 49.5163 | -0.14191 | -0.082398 | -0.068665 | -0.11444 | 0 | 0.032043 | -0.23346 | 0.11444 | -0.15106 | 2.1057 | 122.4335 | 0.082398 | 122.3236 | 122.4838 | 122.3694 | 122.2916 | 122.287 | -122.5479 | -122.4381 | 122.2412 | 122.2412 | 47.8592 | 44.8196
1611.8281 | 122.5662 | -49.3698 | 72.995 | -0.07164 | 0.00020288 | 0.063734 | 0.1112 | -0.0013245 | -0.0037812 | -0.001175 | -0.036926 | -0.0017688 | 0.063538 | 0.060836 | -0.024654 | 0.0039777 | 0.0069427 | -1.7441 | 73.233 | -49.2691 | 72.9263 | -47.0123 | -49.6582 | -0.29297 | -4.9072 | 72.9721 | -49.4019 | 72.9813 | -49.3011 | -49.5438 | -49.2645 | 0.10071 | 0.23804 | -0.068664 | 2.3575 | 49.0768 | -0.28839 | 48.9761 | -0.3891 | -0.032043 | -0.022888 | -0.013733 | 0.068665 | 0.10529 | -0.17395 | 0.13733 | -0.14191 | 2.2568 | 122.1954 | 0.10071 | 122.3831 | 122.5021 | 122.374 | 122.6028 | 122.3419 | -122.2641 | -122.3969 | 122.2961 | 122.3511 | 47.6257 | 44.4626
1612.7656 | 122.5113 | -49.6078 | 72.7982 | -0.10979 | 0.00041648 | 0.065443 | 0.11056 | 0.0025207 | -0.0024994 | 0.00074764 | -0.064392 | -0.0017688 | 0.06546 | 0.057845 | -0.027004 | 0.0022687 | -0.0022431 | -1.8173 | 72.7432 | -49.7406 | 72.6059 | -47.2824 | -49.9512 | -0.28839 | -4.8843 | 72.6883 | -49.6399 | 72.7386 | -49.5621 | -49.7818 | -49.5438 | -0.13275 | -0.054932 | -0.19226 | 2.3254 | 49.3195 | -0.34332 | 49.4522 | -0.21057 | -0.032044 | -0.10986 | -0.05951 | 0.045776 | 0.064087 | -0.17395 | 0.096131 | -0.14191 | 2.4582 | 122.3465 | 0.07782 | 122.3785 | 122.4838 | 122.3282 | 122.3511 | 122.2961 | -122.5388 | -122.4381 | 122.2137 | 122.3465 | 47.7905 | 44.7235
1613.8281 | 122.6578 | -49.8642 | 72.4136 | -0.18608 | 0.0014847 | 0.06288 | 0.10885 | 0.00038452 | -0.0048492 | -0.0037384 | -0.0094604 | -0.0032642 | 0.061402 | 0.05934 | -0.024227 | -0.00072207 | -0.0016021 | -2.1011 | 72.2717 | -50.1617 | 72.3679 | -47.5067 | -50.1709 | -0.19684 | -5.0491 | 72.3267 | -49.9649 | 72.5098 | -49.7406 | -49.9695 | -49.7177 | -0.29755 | -0.14191 | -0.045776 | 2.3575 | 49.6674 | -0.3067 | 49.9649 | -0.009155 | -0.10071 | -0.086975 | 0.096131 | 0.1236 | 0.14648 | -0.10529 | 0.24719 | -0.004577 | 2.655 | 122.5296 | 0.2243 | 122.4747 | 122.4335 | 122.2916 | 122.1359 | 122.1909 | -122.5754 | -122.3785 | 122.2321 | 122.374 | 47.7631 | 44.8151
1614.7656 | 122.525 | -49.6628 | 72.7432 | -0.079269 | 0.0014847 | 0.062666 | 0.11184 | -0.00068368 | -0.0037812 | 0.00074764 | -0.049133 | -0.001128 | 0.061402 | 0.061904 | -0.025509 | 0.0018413 | 0.0026703 | -2.1103 | 72.7386 | -49.7635 | 72.5693 | -47.2504 | -50.0107 | -0.37079 | -5.1727 | 72.6974 | -49.7131 | 72.6379 | -49.5392 | -50.2396 | -49.8138 | -0.10071 | -0.004578 | -0.17395 | 2.4124 | 49.292 | -0.3479 | 49.3927 | -0.24719 | -0.050354 | -0.045776 | -0.10529 | 0.1236 | -0.15106 | -0.57678 | -0.10071 | -0.52643 | 2.5131 | 122.3328 | 0.17395 | 122.3511 | 122.5021 | 122.4106 | 122.4014 | 122.3602 | -122.5067 | -122.4564 | 122.2321 | 122.3007 | 47.5525 | 44.4901
1615.8281 | 122.5983 | -49.4522 | 72.8439 | -0.10979 | -0.00022432 | 0.063948 | 0.11227 | -0.0011109 | -0.0003632 | -0.001175 | -0.04303 | -0.0019824 | 0.064606 | 0.059554 | -0.027004 | 0.0031231 | 0.00096129 | -1.9958 | 73.2788 | -49.2096 | 73.2056 | -46.6461 | -49.3378 | -0.19226 | -5.246 | 73.0911 | -49.292 | 72.8897 | -49.4293 | -49.617 | -49.3607 | 0.24261 | 0.43488 | 0.36163 | 2.8061 | 49.2599 | 0.11444 | 49.0173 | -0.12817 | 0.16022 | 0.24719 | 0.045776 | 0.022888 | 0.091552 | -0.16479 | -0.068665 | -0.32501 | 2.5635 | 122.4152 | -0.13733 | 122.1817 | 122.4884 | 122.3831 | 122.731 | 122.5433 | -122.0535 | -122.1359 | 122.6578 | 122.3419 | 47.4564 | 44.2062
1616.7656 | 122.6852 | -48.0972 | 74.2081 | -0.1403 | 0.00084388 | 0.065657 | 0.11227 | 0.0046569 | -0.0014312 | -0.0013886 | 0.018005 | -0.0036914 | 0.064392 | 0.059127 | -0.027431 | 0.0031231 | 0.0035247 | -1.7578 | 74.2264 | -48.2117 | 74.1806 | -45.5154 | -48.4131 | 0.013733 | -4.7287 | 74.1348 | -48.1842 | 74.3088 | -47.9095 | -48.4955 | -48.1201 | -0.11444 | 0.01831 | -0.027466 | 2.5818 | 48.111 | -0.31586 | 48.2254 | -0.20142 | -0.086975 | -0.073242 | 0.10071 | 0.18768 | -0.022888 | -0.39825 | 0.064087 | -0.31128 | 2.6962 | 122.3923 | 0.27466 | 122.493 | 122.438 | 122.319 | 122.3236 | 122.2321 | -122.4197 | -122.3923 | 122.2778 | 122.406 | 46.3394 | 43.3685
1617.8281 | 122.5113 | -48.5458 | 73.8327 | -0.0029755 | 0.0014847 | 0.06053 | 0.11056 | -0.00025628 | -0.0001496 | -0.00096136 | -0.055237 | -0.00027343 | 0.066101 | 0.060622 | -0.027004 | 0.00055973 | 0.0013885 | -1.9638 | 73.7961 | -48.7106 | 73.6633 | -45.7855 | -48.8983 | -0.12817 | -4.9438 | 73.8052 | -48.6099 | 73.7595 | -48.4863 | -48.7518 | -48.4909 | -0.16479 | -0.036621 | -0.16937 | 2.7603 | 48.4177 | -0.35248 | 48.5825 | -0.18768 | -0.064087 | -0.027466 | -0.073243 | 0.059509 | 0.054931 | -0.20599 | 0.11902 | -0.14191 | 2.9251 | 122.374 | 0.1236 | 122.3694 | 122.5067 | 122.4152 | 122.3419 | 122.3511 | -122.5433 | -122.4426 | 122.2092 | 122.3053 | 46.582 | 43.602
1618.7656 | 122.5113 | -54.3503 | 68.0099 | -0.079269 | 0.00063028 | 0.061812 | 0.1127 | -0.0023925 | -0.0042084 | 0.0020294 | -0.09491 | -0.0019824 | 0.061829 | 0.061476 | -0.027645 | 0.0022687 | 0.0030975 | -3.1403 | 67.955 | -54.5288 | 67.5888 | -53.6041 | -54.2908 | -0.62714 | -6.2622 | 67.9367 | -54.4327 | 67.9321 | -54.2999 | -54.5654 | -54.2725 | -0.17853 | -0.054932 | -0.42114 | 0.74616 | 53.7231 | 0.05951 | 53.9017 | 0.23804 | -0.082397 | -0.073242 | -0.07782 | 0.050354 | 0.07782 | -0.21515 | 0.16022 | -0.13275 | 0.92468 | 122.1176 | 0.13275 | 122.3648 | 122.4838 | 122.3694 | 122.3053 | 122.287 | -122.5388 | -122.4426 | 121.9391 | 122.2824 | 51.21 | 48.0881
1619.8438 | 122.493 | -53.9932 | 68.399 | -0.094528 | 0.0012711 | 0.062666 | 0.11206 | 0.0023071 | -0.0020722 | -0.00032036 | -0.04303 | -0.0019824 | 0.063324 | 0.059767 | -0.025295 | 0.0020551 | 0.0011749 | -2.8519 | 68.3762 | -54.1306 | 68.2434 | -52.6886 | -54.3365 | -0.69122 | -6.2759 | 68.3258 | -54.039 | 68.3304 | -53.8788 | -54.5563 | -54.1306 | -0.13733 | -0.022888 | -0.15564 | 1.3046 | 53.302 | -0.34332 | 53.4393 | -0.20599 | -0.045776 | -0.073242 | -0.068665 | 0.11444 | -0.13733 | -0.56305 | -0.091553 | -0.51727 | 1.442 | 122.374 | 0.16022 | 122.3694 | 122.5067 | 122.3648 | 122.3694 | 122.319 | -122.5296 | -122.438 | 122.2366 | 122.3236 | 51.1414 | 47.7173
1620.7656 | 122.5708 | -52.6749 | 69.7266 | -0.15556 | 0.0021255 | 0.06288 | 0.11184 | 0.0042297 | -0.0029266 | -0.0013886 | -0.073547 | -0.0036914 | 0.062256 | 0.068526 | -0.023586 | 0.0016277 | 0.00096129 | -2.6688 | 69.6075 | -52.8854 | 69.4656 | -51.6495 | -53.1006 | -0.37994 | -6.0837 | 69.6121 | -52.7481 | 69.7083 | -52.5146 | -52.9861 | -52.6978 | -0.21057 | -0.11902 | -0.26093 | 1.0254 | 52.2949 | -0.42572 | 52.5055 | -0.21515 | -0.073242 | -0.11444 | -0.01831 | 0.16022 | -0.022888 | -0.31128 | 0.050354 | -0.23804 | 1.236 | 122.3511 | 0.23346 | 122.4564 | 122.493 | 122.3602 | 122.2824 | 122.287 | -122.612 | -122.4747 | 122.1405 | 122.3831 | 50.0061 | 46.5912
1621.8281 | 122.5433 | -54.2496 | 68.1244 | -0.086899 | -1.0718e-05 | 0.061171 | 0.11163 | 0.0018799 | -0.0033538 | -0.00096136 | -0.036926 | -0.0019824 | 0.064606 | 0.06169 | -0.026577 | 0.00034613 | 0.0022431 | -3.0304 | 68.1564 | -54.3549 | 68.0191 | -53.2242 | -54.5563 | -0.70496 | -6.5231 | 68.0374 | -54.364 | 68.0557 | -54.1992 | -54.4281 | -54.1443 | -0.10529 | 0.032043 | -0.10529 | 1.0254 | 53.5446 | -0.3067 | 53.6499 | -0.20142 | -0.11444 | -0.086975 | -0.068665 | 0.050354 | 0.10529 | -0.17853 | 0.21973 | -0.064087 | 1.1307 | 122.374 | 0.16479 | 122.4197 | 122.5113 | 122.4014 | 122.406 | 122.287 | -122.4792 | -122.4884 | 122.2687 | 122.3053 | 51.2192 | 47.7264
1622.7656 | 122.5433 | -54.3182 | 68.0374 | -0.20134 | -0.0017197 | 0.058607 | 0.1127 | 0.0023071 | -0.0003632 | -0.00074776 | -0.06134 | -0.0030506 | 0.06247 | 0.058272 | -0.026791 | 0.0012005 | 0.00074769 | -2.8061 | 68.0283 | -54.5151 | 67.8314 | -53.183 | -54.7211 | -0.70953 | -6.5598 | 67.9688 | -54.4189 | 67.9688 | -54.3045 | -54.5334 | -54.2267 | -0.19684 | -0.009156 | -0.20599 | 1.1353 | 53.6087 | -0.40283 | 53.8055 | -0.20599 | -0.10071 | -0.068665 | -0.068665 | 0.013733 | 0.091552 | -0.21515 | 0.19226 | -0.11444 | 1.3321 | 122.3465 | 0.11444 | 122.3877 | 122.5433 | 122.3877 | 122.3465 | 122.287 | -122.5525 | -122.4564 | 122.1497 | 122.287 | 51.5121 | 47.7585
1623.8281 | 122.5754 | -54.2404 | 68.0923 | -0.1403 | -0.0010787 | 0.061812 | 0.1127 | -0.0013245 | -0.0007904 | -0.00032036 | -0.04303 | -0.0028368 | 0.062897 | 0.062331 | -0.026363 | 0.0014141 | 0.00074769 | -2.9343 | 68.0878 | -54.3961 | 67.9733 | -53.2974 | -54.5792 | -0.73242 | -6.4041 | 68.0374 | -54.2953 | 68.1244 | -54.1306 | -54.3686 | -54.1122 | -0.15564 | -0.004577 | -0.11902 | 0.94299 | 53.508 | -0.33875 | 53.6636 | -0.18311 | -0.054932 | -0.054931 | 0.032044 | 0.10986 | 0.12817 | -0.12817 | 0.18311 | -0.073242 | 1.0986 | 122.3694 | 0.1648 | 122.4197 | 122.4838 | 122.3328 | 122.3282 | 122.2778 | -122.4884 | -122.3877 | 122.2137 | 122.3648 | 51.3062 | 47.8363
1624.7656 | 122.6303 | -54.0344 | 68.3075 | -0.11742 | 0.0010575 | 0.063521 | 0.10949 | -0.00046988 | -0.0035674 | -0.00053396 | 0.0088502 | -0.0028368 | 0.061188 | 0.056563 | -0.025082 | -0.0015765 | 0.0016021 | -2.9114 | 68.2159 | -54.1672 | 68.2343 | -53.0869 | -54.2953 | -0.65002 | -6.2988 | 68.2205 | -54.1031 | 68.3441 | -53.8605 | -54.1077 | -53.8605 | -0.13275 | -0.091553 | -0.073242 | 0.94757 | 53.3844 | -0.26093 | 53.5172 | -0.12817 | -0.068664 | -0.086975 | 0.036621 | 0.17395 | 0.17395 | -0.073242 | 0.24261 | -0.004578 | 1.0803 | 122.4014 | 0.24261 | 122.4472 | 122.3831 | 122.3236 | 122.2504 | 122.2549 | -122.4747 | -122.4106 | 122.2687 | 122.3785 | 51.123 | 47.7356
1625.8281 | 122.6303 | -53.7643 | 68.5364 | -0.23949 | 0.0034073 | 0.061385 | 0.11013 | 0.0025207 | 0.000705 | 0.00074764 | -0.012512 | -0.0028368 | 0.061188 | 0.063399 | -0.027218 | 0.00013253 | 0.0013885 | -2.8793 | 68.454 | -53.9246 | 68.5547 | -52.7573 | -53.9795 | -0.52643 | -6.1752 | 68.486 | -53.7964 | 68.6005 | -53.627 | -53.8513 | -53.6224 | -0.16022 | -0.082398 | 0.01831 | 1.0071 | 53.2379 | -0.21515 | 53.3981 | -0.054931 | -0.032044 | -0.050354 | 0.064087 | 0.13733 | 0.14191 | -0.086975 | 0.17395 | -0.054931 | 1.1673 | 122.4792 | 0.16937 | 122.3969 | 122.3785 | 122.2824 | 122.2183 | 122.2504 | -122.4609 | -122.3328 | 122.319 | 122.3648 | 50.885 | 47.5891
1626.7656 | 122.5479 | -52.4185 | 69.9417 | -0.0029755 | 0.0012711 | 0.061812 | 0.11291 | 0.0029479 | -0.0037812 | 0.00010684 | -0.091858 | -0.0024096 | 0.064179 | 0.060836 | -0.025509 | 0.0018413 | 0.00010689 | -2.5635 | 69.9326 | -52.6016 | 69.8181 | -51.4938 | -52.7573 | -0.21057 | -6.0745 | 69.9463 | -52.4277 | 69.9097 | -52.3407 | -52.6062 | -52.359 | -0.18311 | -0.009155 | -0.1236 | 0.92468 | 52.2079 | -0.33875 | 52.3911 | -0.15564 | -0.009155 | 0.004578 | -0.032043 | 0.07782 | 0.059509 | -0.18768 | 0.068664 | -0.17853 | 1.1078 | 122.4197 | 0.086975 | 122.3373 | 122.5342 | 122.374 | 122.3511 | 122.3648 | -122.5433 | -122.3694 | 122.2366 | 122.3282 | 49.855 | 46.344
1627.8281 | 122.5983 | -53.627 | 68.6737 | -0.1403 | 0.00063028 | 0.06053 | 0.11013 | 0.00059812 | -0.0039948 | -0.00096136 | 0.011902 | -0.0019824 | 0.061615 | 0.059767 | -0.024227 | -0.00029487 | 0.00074769 | -2.623 | 68.9941 | -53.4531 | 68.8889 | -52.2675 | -53.7231 | -0.70953 | -6.6376 | 68.605 | -53.7369 | 68.6691 | -53.5492 | -53.7781 | -53.5217 | 0.17395 | 0.32044 | 0.21515 | 1.3596 | 52.9175 | -0.096131 | 52.7435 | -0.27008 | -0.10986 | -0.068664 | -0.004578 | 0.07782 | 0.10529 | -0.15106 | 0.21515 | -0.041199 | 1.1856 | 122.3419 | 0.18768 | 122.406 | 122.4472 | 122.3419 | 122.6212 | 122.2321 | -122.1268 | -122.4106 | 122.5159 | 122.2961 | 51.004 | 46.9894
1628.7656 | 122.6303 | -52.4963 | 69.7815 | -0.13267 | 0.0019119 | 0.063307 | 0.11099 | 0.0016663 | -0.0024994 | -0.00074776 | -0.070496 | -0.0051868 | 0.064606 | 0.057204 | -0.027645 | 0.0031231 | -0.0016021 | -2.4857 | 69.7723 | -52.6749 | 69.7357 | -51.5625 | -52.8305 | -0.66834 | -6.3309 | 69.7083 | -52.6108 | 69.8547 | -52.4002 | -52.6291 | -52.359 | -0.17853 | -0.009155 | -0.045776 | 0.93384 | 51.828 | -0.33417 | 52.0065 | -0.15564 | -0.11444 | -0.073242 | 0.073242 | 0.09613 | 0.13733 | -0.13275 | 0.25177 | -0.01831 | 1.1124 | 122.4106 | 0.21057 | 122.4655 | 122.4472 | 122.319 | 122.2687 | 122.2046 | -122.4564 | -122.3923 | 122.2321 | 122.3511 | 50.0107 | 46.1655
1629.8438 | 122.6166 | -51.3199 | 70.9854 | -0.086899 | 0.0012711 | 0.061171 | 0.11035 | -0.0030335 | -0.0016448 | -0.0016022 | 0.21332 | -0.005614 | 0.064179 | 0.058486 | -0.025509 | 0.0014141 | -0.00053411 | -2.2522 | 70.7153 | -51.6815 | 70.8801 | -50.2899 | -51.6357 | -0.16022 | -6.1386 | 70.8755 | -51.4481 | 71.0587 | -51.1826 | -51.4114 | -51.1917 | -0.36163 | -0.27008 | -0.10529 | 1.03 | 51.1597 | -0.31586 | 51.5213 | 0.045777 | -0.12817 | -0.10986 | 0.073242 | 0.13733 | 0.12817 | -0.091553 | 0.25635 | 0.036621 | 1.3916 | 122.5616 | 0.2655 | 122.5067 | 122.3969 | 122.3236 | 122.0352 | 122.1954 | -122.6669 | -122.4335 | 122.2 | 122.3785 | 49.0677 | 45.1813
1630.7656 | 122.5571 | -51.6953 | 70.7062 | -0.056381 | 0.0010575 | 0.060744 | 0.11227 | -0.00068368 | -0.0012176 | -0.00074776 | -0.097961 | -0.0041186 | 0.061188 | 0.062331 | -0.026791 | -0.00093567 | -0.00053411 | -2.3849 | 70.546 | -51.9287 | 70.459 | -50.7935 | -52.1667 | -0.44861 | -6.2576 | 70.5643 | -51.8097 | 70.7657 | -51.6312 | -52.0065 | -51.6953 | -0.23346 | -0.16022 | -0.24719 | 0.90179 | 51.2466 | -0.4715 | 51.4801 | -0.23804 | -0.11444 | -0.14191 | 0.059509 | 0.064086 | 0 | -0.31128 | 0.11444 | -0.19684 | 1.1353 | 122.3877 | 0.17853 | 122.5754 | 122.4747 | 122.374 | 122.2412 | 122.2595 | -122.6349 | -122.5159 | 122.1542 | 122.4609 | 49.3103 | 45.4376
1631.8281 | 122.5159 | -50.7019 | 71.6812 | -0.10216 | -1.0718e-05 | 0.063094 | 0.11184 | 0.00017092 | -0.0020722 | -0.00032036 | -0.10712 | -0.0028368 | 0.067169 | 0.061476 | -0.024868 | 0.0029095 | 0.0035247 | -2.0966 | 71.6675 | -50.8438 | 71.521 | -49.53 | -51.0544 | -0.1831 | -6.2347 | 71.6263 | -50.7568 | 71.5988 | -50.5646 | -50.9491 | -50.679 | -0.14191 | -0.013733 | -0.16022 | 1.1719 | 50.5188 | -0.35248 | 50.6607 | -0.21057 | -0.054932 | -0.054931 | -0.082397 | 0.13733 | 0.022888 | -0.24719 | 0.07782 | -0.19226 | 1.3138 | 122.3648 | 0.19226 | 122.3557 | 122.5113 | 122.3831 | 122.3694 | 122.3282 | -122.525 | -122.438 | 122.2229 | 122.3007 | 48.6053 | 44.4672
1632.7656 | 122.58 | -50.4822 | 71.8826 | -0.079269 | -0.00065152 | 0.061385 | 0.11184 | -0.00046988 | -0.0005768 | -0.0033112 | -0.082703 | -0.0028368 | 0.066315 | 0.068526 | -0.025295 | 0.0022687 | 0.0039521 | -2.0691 | 71.8735 | -50.647 | 71.7041 | -49.324 | -50.8621 | -0.2243 | -5.9784 | 71.8185 | -50.528 | 71.8552 | -50.4044 | -50.6516 | -50.3906 | -0.1648 | -0.009155 | -0.17853 | 1.1581 | 50.2579 | -0.37994 | 50.4227 | -0.21515 | -0.045776 | -0.064087 | -0.027465 | 0.07782 | 0.091553 | -0.16937 | 0.13733 | -0.1236 | 1.3229 | 122.3511 | 0.1236 | 122.3831 | 122.5204 | 122.3465 | 122.3557 | 122.3007 | -122.5296 | -122.4106 | 122.1863 | 122.3373 | 48.4131 | 44.5038
1633.8281 | 122.6074 | -51.0681 | 71.2555 | -0.11742 | 0.00084388 | 0.063307 | 0.108 | -0.00046988 | 0.0009186 | -0.0035248 | -0.021667 | -0.002196 | 0.062683 | 0.05934 | -0.025936 | 0.00034613 | 0.0030975 | -2.1835 | 71.0358 | -51.3886 | 71.0541 | -50.2716 | -51.4847 | -0.25635 | -6.2531 | 71.022 | -51.3062 | 71.1273 | -50.9445 | -51.1963 | -50.885 | -0.32044 | -0.21973 | -0.20142 | 0.79651 | 50.8118 | -0.41656 | 51.1322 | -0.09613 | -0.23804 | -0.23346 | -0.12817 | 0.1236 | 0.1831 | -0.12817 | 0.42114 | 0.10986 | 1.1169 | 122.4426 | 0.36163 | 122.4335 | 122.4243 | 122.3282 | 122.1039 | 122.0901 | -122.644 | -122.5616 | 122.1222 | 122.1954 | 48.8846 | 44.8151
1634.7656 | 122.6303 | -51.4435 | 70.8618 | -0.1403 | 0.0019119 | 0.062239 | 0.11483 | 0.0048705 | 6.4004e-05 | -0.005661 | 0.0027466 | -0.0047594 | 0.063111 | 0.058913 | -0.027645 | 0.00098693 | -0.00074771 | -2.1744 | 70.8389 | -51.622 | 70.9351 | -50.2853 | -51.7731 | -0.42572 | -6.2439 | 70.7611 | -51.4984 | 70.9396 | -51.329 | -51.5671 | -51.2924 | -0.17853 | -0.022888 | 0.073243 | 1.1581 | 51.0178 | -0.32959 | 51.1963 | -0.15106 | -0.054932 | -0.10071 | 0.07782 | 0.11444 | 0.15106 | -0.1236 | 0.20599 | -0.068665 | 1.3367 | 122.5571 | 0.16937 | 122.438 | 122.4609 | 122.2595 | 122.2824 | 122.2046 | -122.4838 | -122.3602 | 122.3785 | 122.3831 | 49.2691 | 45.1996
1635.8281 | 122.6349 | -51.4114 | 70.871 | -0.1403 | 0.0010575 | 0.063521 | 0.11099 | 0.0029479 | -0.0033538 | -0.00010676 | -0.033874 | -0.0036914 | 0.063111 | 0.060195 | -0.02615 | 0.0022687 | 0.00032049 | -2.2156 | 70.7565 | -51.6449 | 70.8847 | -50.4776 | -51.6815 | -0.36163 | -6.2988 | 70.8252 | -51.4847 | 70.9717 | -51.3107 | -51.5259 | -51.2924 | -0.23346 | -0.11444 | 0.013733 | 0.93384 | 51.0498 | -0.27008 | 51.2833 | -0.036622 | -0.073242 | -0.045777 | 0.10071 | 0.10071 | 0.11902 | -0.11444 | 0.19226 | -0.041199 | 1.1673 | 122.5296 | 0.17395 | 122.4564 | 122.4014 | 122.3099 | 122.168 | 122.2366 | -122.5159 | -122.3557 | 122.2961 | 122.3831 | 49.1959 | 45.1126
1636.7656 | 122.5479 | -51.5717 | 70.8389 | -0.11742 | 0.0021255 | 0.063094 | 0.11184 | 0.0012391 | -0.0003632 | -0.00010676 | -0.12848 | -0.0030506 | 0.061615 | 0.058486 | -0.02615 | 0.0022687 | -0.00053411 | -2.1011 | 70.5505 | -51.9424 | 70.4361 | -51.1185 | -52.1484 | -0.4303 | -6.3492 | 70.5093 | -51.8509 | 70.7794 | -51.4893 | -51.7136 | -51.4252 | -0.37079 | -0.28839 | -0.40283 | 0.45319 | 51.1414 | -0.57678 | 51.5121 | -0.20599 | -0.27924 | -0.32959 | -0.059509 | 0.082397 | 0.14648 | -0.14191 | 0.42572 | 0.13733 | 0.82398 | 122.3785 | 0.36163 | 122.6303 | 122.493 | 122.3602 | 122.1222 | 122.081 | -122.7814 | -122.6898 | 122.0078 | 122.3511 | 49.4705 | 45.2225
1637.8281 | 122.5479 | -50.5646 | 71.7957 | -0.041122 | 0.0019119 | 0.063094 | 0.11312 | 0.0012391 | -0.0029266 | -0.00096136 | -0.082703 | -0.0034778 | 0.061402 | 0.063185 | -0.028286 | 0.0026959 | 0.00074769 | -1.8951 | 71.7728 | -50.7019 | 71.7133 | -49.6582 | -50.8484 | -0.25635 | -6.189 | 71.727 | -50.6287 | 71.7911 | -50.5096 | -50.7385 | -50.5051 | -0.13733 | -0.022888 | -0.082397 | 0.90637 | 50.3082 | -0.28381 | 50.4456 | -0.14648 | -0.064087 | -0.068664 | -0.004577 | 0.054931 | 0.059509 | -0.17395 | 0.1236 | -0.10986 | 1.0437 | 122.4152 | 0.11902 | 122.4197 | 122.4747 | 122.3557 | 122.3373 | 122.2916 | -122.4976 | -122.4243 | 122.2778 | 122.3557 | 48.6694 | 44.3756
1638.7656 | 122.5067 | -52.6337 | 69.7357 | -0.094528 | 0.00041648 | 0.06053 | 0.11419 | 0.0029479 | -0.0067718 | -0.00074776 | -0.067444 | -0.001128 | 0.06247 | 0.057631 | -0.026363 | 0.0029095 | 0.0020295 | -2.298 | 69.7906 | -52.6978 | 69.8685 | -51.828 | -53.0182 | -0.46234 | -6.8069 | 69.7815 | -52.6337 | 69.722 | -52.6016 | -52.8488 | -52.5742 | -0.064087 | 0.054931 | 0.13275 | 0.80566 | 52.1713 | -0.38452 | 52.2354 | -0.32043 | 0 | 0.045776 | -0.013733 | 0.032043 | 0.059509 | -0.21515 | 0.059509 | -0.21515 | 0.86975 | 122.5662 | 0.032043 | 122.3557 | 122.4884 | 122.4152 | 122.4243 | 122.4152 | -122.4335 | -122.3694 | 122.5021 | 122.3557 | 50.3357 | 45.8267
1639.8281 | 122.612 | -51.9791 | 70.2896 | -0.094528 | -0.0015061 | 0.060744 | 0.11035 | 0.00017092 | -0.004422 | -0.002243 | 0.039368 | -0.0045458 | 0.062897 | 0.051436 | -0.026577 | 0.00013253 | 0.00010689 | -1.9089 | 70.3537 | -52.0798 | 70.4224 | -50.7935 | -52.1118 | -0.09613 | -6.3446 | 70.3308 | -51.9699 | 70.5185 | -51.503 | -52.3315 | -52.066 | -0.10071 | 0.064087 | 0.13275 | 1.1856 | 51.8829 | -0.13275 | 51.9836 | -0.032043 | 0.009155 | 0.041199 | 0.22888 | 0.47607 | -0.086975 | -0.35248 | -0.09613 | -0.36163 | 1.2863 | 122.5021 | 0.46692 | 122.4884 | 122.4335 | 122.3007 | 122.3328 | 122.3099 | -122.3694 | -122.2595 | 122.4014 | 122.4976 | 50.0702 | 45.6345
1640.7812 | 122.5571 | -50.2579 | 72.084 | -0.15556 | 0.0029801 | 0.062453 | 0.11013 | -0.0015381 | -0.0029266 | -0.0026704 | -0.00030524 | -0.0043322 | 0.062897 | 0.058058 | -0.027218 | -0.00029487 | 0.00096129 | -1.7761 | 72.0566 | -50.3906 | 72.0062 | -49.1043 | -50.4913 | 0.12817 | -5.9189 | 72.0291 | -50.2945 | 72.0657 | -50.1892 | -50.3769 | -50.1846 | -0.13275 | -0.027465 | -0.077819 | 1.1536 | 50.386 | -0.23346 | 50.5188 | -0.10071 | -0.036621 | -0.054931 | -0.01831 | 0.068665 | 0.073243 | -0.11902 | 0.10986 | -0.082397 | 1.2863 | 122.3969 | 0.10529 | 122.3602 | 122.4472 | 122.3236 | 122.3145 | 122.287 | -122.4747 | -122.3785 | 122.2641 | 122.3236 | 48.4818 | 44.339
1641.8281 | 122.5571 | -51.0086 | 71.3837 | -0.010605 | 0.0016983 | 0.062453 | 0.1127 | -0.0015381 | -0.0042084 | -0.00074776 | -0.085754 | -0.0024096 | 0.063324 | 0.067031 | -0.026577 | 0.0020551 | 0.00074769 | -1.9043 | 71.2326 | -51.2558 | 71.2418 | -50.0519 | -51.3062 | -0.07782 | -6.2759 | 71.2967 | -51.0956 | 71.3425 | -50.9445 | -51.178 | -50.9583 | -0.24719 | -0.15106 | -0.14191 | 0.95673 | 50.9308 | -0.29755 | 51.178 | -0.050354 | -0.086975 | -0.086975 | -0.041199 | 0.064087 | 0.050354 | -0.16937 | 0.13733 | -0.082398 | 1.2039 | 122.4976 | 0.15106 | 122.438 | 122.4884 | 122.3923 | 122.2412 | 122.3053 | -122.6395 | -122.4792 | 122.2504 | 122.3511 | 49.1043 | 44.7327
1642.7656 | 122.5113 | -50.7523 | 71.608 | -0.086899 | 0.0010575 | 0.060744 | 0.11206 | -0.0015381 | -0.001004 | -0.0030976 | -0.085754 | -0.0017688 | 0.062897 | 0.064467 | -0.027431 | 0.00077333 | 0.0058747 | -1.8631 | 71.5851 | -50.9079 | 71.489 | -49.7681 | -51.0544 | -0.050354 | -6.2164 | 71.5485 | -50.8301 | 71.5668 | -50.7248 | -50.9354 | -50.6744 | -0.15564 | -0.022888 | -0.11902 | 0.98419 | 50.7019 | -0.30212 | 50.8575 | -0.14648 | -0.07782 | -0.059509 | -0.041199 | 0.027466 | 0.07782 | -0.18311 | 0.15564 | -0.10529 | 1.1398 | 122.3969 | 0.10529 | 122.3969 | 122.493 | 122.3785 | 122.3373 | 122.3007 | -122.5159 | -122.438 | 122.2412 | 122.319 | 48.8892 | 44.5358
1643.7656 | 122.525 | -50.0519 | 72.3633 | -0.094528 | -0.0010787 | 0.062666 | 0.1127 | -0.00068368 | -0.001004 | -0.0020294 | -0.079651 | -0.0049732 | 0.062256 | 0.063185 | -0.0285 | 0.00077333 | 0.0011749 | -1.8494 | 72.3221 | -50.1572 | 72.2443 | -49.0402 | -50.3082 | 0.19684 | -6.2164 | 72.3129 | -50.0931 | 72.3221 | -49.9786 | -50.1938 | -49.9558 | -0.10529 | -0.041198 | -0.11902 | 1.0117 | 50.2487 | -0.25635 | 50.354 | -0.15106 | -0.041199 | -0.050354 | -0.041198 | 0.073242 | 0.09613 | -0.14191 | 0.13733 | -0.10071 | 1.1169 | 122.4014 | 0.11444 | 122.4152 | 122.4792 | 122.406 | 122.374 | 122.3648 | -122.5204 | -122.4564 | 122.2961 | 122.374 | 48.2025 | 43.8354
1644.7656 | 122.5754 | -50.3174 | 72.0612 | -0.079269 | -0.0017197 | 0.059889 | 0.11227 | -0.00046988 | -0.0046356 | -0.0020294 | -0.052185 | -0.0015552 | 0.062683 | 0.058699 | -0.023586 | 0.0014141 | 0.0013885 | -2.0508 | 71.6263 | -50.8347 | 71.608 | -49.7177 | -50.9399 | 0.086975 | -6.4087 | 71.8826 | -50.473 | 71.9925 | -50.2853 | -50.5051 | -50.2029 | -0.51727 | -0.43487 | -0.45319 | 0.59967 | 50.4044 | -0.62256 | 50.9216 | -0.10528 | -0.15564 | -0.17853 | -0.068664 | 0.032044 | 0.11444 | -0.18768 | 0.27008 | -0.032044 | 1.1169 | 122.4426 | 0.18768 | 122.4655 | 122.4609 | 122.3557 | 121.9437 | 122.2 | -122.8958 | -122.5342 | 121.9254 | 122.3099 | 48.2666 | 43.9087
1645.8281 | 122.6715 | -50.5188 | 71.8002 | -0.13267 | 0.00041648 | 0.06288 | 0.11248 | 0.0027343 | -0.0022858 | -0.0024566 | 0.0057984 | -0.002196 | 0.063965 | 0.058913 | -0.025722 | 0.0024823 | 0.0018159 | -1.973 | 71.7133 | -50.679 | 71.7773 | -49.2279 | -50.7935 | 0 | -6.395 | 71.7133 | -50.5783 | 71.846 | -50.3998 | -50.6332 | -50.3952 | -0.16022 | -0.086975 | -0.022888 | 1.2909 | 50.5188 | -0.27466 | 50.679 | -0.11444 | -0.059509 | -0.086975 | 0.045776 | 0.11902 | 0.1236 | -0.11444 | 0.1831 | -0.054932 | 1.4511 | 122.4564 | 0.17853 | 122.4243 | 122.3923 | 122.2916 | 122.2321 | 122.2321 | -122.4792 | -122.3785 | 122.2961 | 122.3648 | 48.5458 | 44.1238
1646.7656 | 122.5708 | -51.8829 | 70.4819 | -0.10979 | 0.00020288 | 0.062025 | 0.11206 | 0.0048705 | -0.0035674 | 0.00053404 | -0.06134 | -0.0030506 | 0.064392 | 0.062117 | -0.0285 | 0.00098693 | 0.0045929 | -2.243 | 70.4086 | -52.0981 | 70.2896 | -51.0086 | -52.2766 | -0.1831 | -6.7566 | 70.3995 | -51.9562 | 70.459 | -51.8372 | -52.066 | -51.8097 | -0.21515 | -0.073243 | -0.19226 | 0.87433 | 51.6998 | -0.39368 | 51.915 | -0.17853 | -0.073242 | -0.082398 | -0.022889 | 0.045777 | 0.073243 | -0.1831 | 0.14648 | -0.10986 | 1.0895 | 122.3877 | 0.11902 | 122.4152 | 122.5067 | 122.3557 | 122.2916 | 122.2824 | -122.58 | -122.438 | 122.1725 | 122.3419 | 49.6399 | 45.1263
1647.8281 | 122.58 | -51.8646 | 70.5002 | -0.10979 | 0.0016983 | 0.066084 | 0.11312 | 0.0033753 | -0.0024994 | -0.002884 | 0.027161 | -0.0026232 | 0.063324 | 0.060408 | -0.026791 | 0.0020551 | 0.0020295 | -2.0508 | 70.4041 | -52.0935 | 70.3857 | -50.8438 | -52.4139 | -0.13733 | -6.7795 | 70.4773 | -51.9012 | 70.5093 | -51.7776 | -52.0111 | -51.7502 | -0.22888 | -0.09613 | -0.11444 | 1.0208 | 51.7273 | -0.54932 | 51.9562 | -0.32043 | -0.036621 | -0.022888 | 0.009155 | 0.086975 | 0.11444 | -0.14648 | 0.15106 | -0.10986 | 1.2497 | 122.4792 | 0.1236 | 122.4106 | 122.4976 | 122.3785 | 122.2687 | 122.3419 | -122.5937 | -122.4014 | 122.2504 | 122.374 | 49.8138 | 45.0851
1648.7656 | 122.5067 | -51.9379 | 70.4498 | -0.086899 | 0.0023391 | 0.063521 | 0.1127 | 0.0018799 | -0.0012176 | -0.002243 | -0.076599 | -0.0034778 | 0.061188 | 0.062331 | -0.024868 | 0.0024823 | 0.0052337 | -2.1606 | 70.4224 | -52.0844 | 70.2988 | -50.9125 | -52.2491 | -0.21973 | -6.9763 | 70.3949 | -52.0157 | 70.3903 | -51.8967 | -52.1439 | -51.8738 | -0.14648 | -0.027466 | -0.15106 | 1.0254 | 51.7181 | -0.31128 | 51.8646 | -0.1648 | -0.07782 | -0.054932 | -0.059509 | 0.041199 | 0.064087 | -0.20599 | 0.14191 | -0.12817 | 1.1719 | 122.3831 | 0.11902 | 122.406 | 122.5067 | 122.4106 | 122.3602 | 122.3328 | -122.5342 | -122.4655 | 122.2366 | 122.3282 | 49.7772 | 44.9615
1649.8281 | 122.6349 | -51.2833 | 71.0037 | -0.12505 | -0.0025741 | 0.063521 | 0.11291 | -0.0023925 | -0.0018586 | 0.00032044 | -0.027771 | -0.0019824 | 0.062256 | 0.065749 | -0.027004 | 0.0016277 | 0.0020295 | -2.0233 | 70.9808 | -51.503 | 70.9305 | -50.3036 | -51.6357 | -0.004578 | -6.8344 | 70.9076 | -51.4206 | 71.109 | -51.1826 | -51.4069 | -51.1459 | -0.21973 | -0.022888 | -0.073242 | 0.97961 | 51.2787 | -0.35248 | 51.4984 | -0.13275 | -0.13733 | -0.09613 | 0.10529 | 0.10071 | 0.13733 | -0.1236 | 0.27466 | 0.013733 | 1.1993 | 122.4335 | 0.23804 | 122.5296 | 122.4838 | 122.3282 | 122.2641 | 122.1909 | -122.5067 | -122.4243 | 122.2137 | 122.3923 | 49.2599 | 44.4489
1650.7656 | 122.5159 | -51.2466 | 71.1731 | -0.086899 | -0.00022432 | 0.063094 | 0.1127 | 0.0027343 | -0.0003632 | -0.0026704 | -0.085754 | -0.00091423 | 0.064606 | 0.061904 | -0.025722 | 0.0039777 | 0.0016021 | -1.918 | 71.0449 | -51.4297 | 70.9854 | -50.1663 | -51.5854 | -0.045776 | -6.7978 | 71.0632 | -51.2787 | 71.0907 | -51.1963 | -51.4297 | -51.1642 | -0.18311 | -0.12817 | -0.18768 | 1.0803 | 51.2009 | -0.33875 | 51.384 | -0.15564 | -0.032044 | -0.10986 | -0.082398 | 0.050354 | 0.082397 | -0.18311 | 0.11444 | -0.15106 | 1.2634 | 122.4152 | 0.082398 | 122.3694 | 122.4747 | 122.3419 | 122.2916 | 122.3099 | -122.6028 | -122.4518 | 122.2321 | 122.3373 | 49.3286 | 44.4489
1651.8281 | 122.5296 | -50.6836 | 71.6995 | -0.033493 | 0.00063028 | 0.063521 | 0.11142 | 0.0010253 | -0.0022858 | -0.00032036 | -0.073547 | -0.0028368 | 0.06247 | 0.06404 | -0.027004 | 0.0022687 | 0.0035247 | -1.7532 | 71.5988 | -50.9079 | 71.5027 | -49.5667 | -51.0635 | 0.009155 | -6.8115 | 71.5988 | -50.8255 | 71.6354 | -50.6104 | -50.8804 | -50.6149 | -0.2243 | -0.10071 | -0.19684 | 1.1169 | 50.6927 | -0.37994 | 50.9171 | -0.15564 | -0.14191 | -0.10071 | -0.064087 | 0.073242 | 0.068665 | -0.19684 | 0.21057 | -0.054932 | 1.3412 | 122.4106 | 0.21515 | 122.4609 | 122.5067 | 122.4243 | 122.2824 | 122.2824 | -122.6074 | -122.525 | 122.1863 | 122.319 | 48.9304 | 43.8721
1652.7656 | 122.5433 | -51.8829 | 70.4865 | -0.079269 | -1.0718e-05 | 0.061385 | 0.1112 | 0.00059812 | -0.0039948 | -0.00074776 | -0.085754 | -0.0036914 | 0.064179 | 0.064681 | -0.024227 | 0.00077333 | -0.0013885 | -1.9638 | 70.5093 | -51.9836 | 70.3766 | -50.7614 | -52.1622 | -0.21973 | -7.1182 | 70.4498 | -51.9287 | 70.5414 | -51.7364 | -52.0752 | -51.8417 | -0.10071 | 0.022888 | -0.10986 | 1.1215 | 51.6632 | -0.27923 | 51.7639 | -0.17853 | -0.045776 | -0.036621 | 0.054932 | 0.14649 | 0.041199 | -0.19226 | 0.086975 | -0.14648 | 1.2222 | 122.3602 | 0.19226 | 122.4701 | 122.493 | 122.3785 | 122.3923 | 122.3328 | -122.4701 | -122.4152 | 122.2595 | 122.4243 | 49.9191 | 44.7647
1653.8281 | 122.5204 | -53.334 | 69.0399 | -0.14793 | 0.0019119 | 0.060957 | 0.11163 | -0.0017517 | -0.0024994 | -0.003952 | -0.085754 | -0.0032642 | 0.063965 | 0.066176 | -0.025722 | 0.00013253 | 0.0033111 | -2.0096 | 69.0948 | -53.389 | 68.9301 | -52.3315 | -53.6911 | -0.20142 | -7.7545 | 68.9484 | -53.4164 | 68.9896 | -53.27 | -53.5126 | -53.2516 | -0.054932 | 0.054932 | -0.10986 | 1.0025 | 53.1326 | -0.35706 | 53.1876 | -0.30212 | -0.082398 | -0.091553 | -0.050354 | 0.064087 | 0.082397 | -0.17853 | 0.16479 | -0.09613 | 1.0574 | 122.319 | 0.14648 | 122.406 | 122.4838 | 122.3648 | 122.4289 | 122.2824 | -122.4289 | -122.4564 | 122.2641 | 122.3236 | 51.3245 | 45.5795
1654.7656 | 122.5616 | -53.8376 | 68.5089 | -0.10216 | -0.00043792 | 0.061385 | 0.11355 | 0.0023071 | -0.0042084 | -0.005661 | -0.070496 | -0.0024096 | 0.063751 | 0.059127 | -0.027218 | 0.0022687 | 0.0033111 | -2.0279 | 68.4814 | -54.0161 | 68.3624 | -53.0228 | -54.1763 | -0.1831 | -7.8232 | 68.4036 | -53.9566 | 68.4357 | -53.8147 | -54.0344 | -53.7552 | -0.17853 | -0.027466 | -0.14648 | 0.81482 | 53.6545 | -0.33875 | 53.833 | -0.16022 | -0.11902 | -0.10529 | -0.073242 | 0.022888 | 0.082397 | -0.19684 | 0.20142 | -0.07782 | 0.99335 | 122.3785 | 0.14191 | 122.3923 | 122.4976 | 122.3602 | 122.319 | 122.2412 | -122.525 | -122.4655 | 122.2 | 122.2733 | 51.8097 | 46.0144
1655.8281 | 122.5571 | -53.92 | 68.4723 | -0.048752 | 0.0010575 | 0.063307 | 0.11291 | 0.0016663 | -0.0005768 | -0.0024566 | -0.082703 | -0.0017688 | 0.064392 | 0.057631 | -0.027218 | 0.0039777 | -0.0030975 | -2.1423 | 68.4265 | -54.0665 | 68.3166 | -53.2471 | -54.213 | -0.091553 | -7.8552 | 68.4036 | -53.9932 | 68.4311 | -53.8605 | -54.071 | -53.7827 | -0.14648 | -0.045776 | -0.15564 | 0.67291 | 53.8284 | -0.29297 | 53.9749 | -0.14648 | -0.073242 | -0.068665 | -0.041199 | 0.059509 | 0.13733 | -0.15106 | 0.21057 | -0.07782 | 0.8194 | 122.3831 | 0.13275 | 122.4243 | 122.493 | 122.3969 | 122.3465 | 122.3236 | -122.5388 | -122.4655 | 122.2366 | 122.3511 | 51.7776 | 46.0648
1656.7656 | 122.5296 | -52.7985 | 69.6259 | -0.10216 | 0.0021255 | 0.06288 | 0.11291 | 0.0027343 | -0.0024994 | 0.00032044 | -0.058289 | 0.00036737 | 0.065674 | 0.057204 | -0.026363 | 0.00077333 | 0.0035247 | -1.9775 | 69.7083 | -52.7664 | 69.4794 | -52.0065 | -53.0411 | 0.073242 | -7.7683 | 69.6167 | -52.7664 | 69.548 | -52.7573 | -52.977 | -52.684 | 0.032044 | 0.082398 | -0.14648 | 0.79193 | 52.8717 | -0.24262 | 52.8397 | -0.27466 | 0.032044 | -0.009155 | -0.077819 | 0.041199 | 0.11444 | -0.17853 | 0.082397 | -0.21057 | 0.75989 | 122.2458 | 0.009155 | 122.3145 | 122.4747 | 122.3831 | 122.5067 | 122.4152 | -122.3923 | -122.3923 | 122.2778 | 122.3465 | 50.8209 | 45.0302
1657.8281 | 122.5433 | -53.9749 | 68.3899 | -0.048752 | 0.0034073 | 0.06053 | 0.11035 | -0.00025628 | -0.0005768 | -0.0033112 | -0.033874 | -0.0032642 | 0.063965 | 0.060836 | -0.02615 | 0.00077333 | 0.0043793 | -1.973 | 68.4402 | -54.0756 | 68.2388 | -53.1692 | -54.3228 | -0.16022 | -8.2214 | 68.3395 | -54.0207 | 68.367 | -53.9154 | -54.1534 | -53.8879 | -0.10071 | 0.050354 | -0.15106 | 0.80567 | 53.8147 | -0.3479 | 53.9154 | -0.24719 | -0.045776 | -0.050354 | -0.022889 | 0.05951 | 0.086976 | -0.17853 | 0.13275 | -0.13275 | 0.90637 | 122.3145 | 0.10529 | 122.3877 | 122.5159 | 122.3602 | 122.4152 | 122.3145 | -122.4655 | -122.4106 | 122.2137 | 122.3419 | 52.002 | 45.7535
1658.7656 | 122.6303 | -53.389 | 68.9346 | -0.10979 | 0.00063028 | 0.062666 | 0.1127 | -0.00068368 | -0.0014312 | -0.00074776 | -0.049133 | -0.001128 | 0.063965 | 0.061904 | -0.027004 | -8.1274e-05 | 0.0048065 | -1.7166 | 68.9941 | -53.508 | 68.8431 | -52.7481 | -53.714 | 0.041199 | -8.0246 | 68.9529 | -53.4164 | 68.9392 | -53.3478 | -53.5812 | -53.2837 | -0.11902 | 0.05951 | -0.091552 | 0.64087 | 53.4302 | -0.32501 | 53.5492 | -0.20599 | -0.027466 | 0.018311 | 0.004578 | 0.041199 | 0.10529 | -0.19226 | 0.13275 | -0.16479 | 0.75989 | 122.3511 | 0.068665 | 122.3557 | 122.5021 | 122.3694 | 122.3831 | 122.3419 | -122.4426 | -122.3511 | 122.2321 | 122.3282 | 51.6724 | 45.3644
1659.8281 | 122.6349 | -53.5721 | 68.7515 | -0.056381 | 0.00020288 | 0.062453 | 0.10885 | 0.0031617 | -0.0029266 | -0.0048066 | -0.012512 | -0.0036914 | 0.065033 | 0.062117 | -0.027218 | 0.0024823 | 0.0018159 | -1.6571 | 68.7927 | -53.7369 | 68.6737 | -52.8076 | -53.8284 | 0.15564 | -7.7774 | 68.7332 | -53.6591 | 68.779 | -53.4805 | -53.7048 | -53.4531 | -0.16479 | 0.041199 | -0.07782 | 0.76447 | 53.7277 | -0.25635 | 53.8925 | -0.091553 | -0.086975 | -0.018311 | 0.027466 | 0.091553 | 0.11902 | -0.13275 | 0.20599 | -0.045776 | 0.92926 | 122.4106 | 0.17853 | 122.4381 | 122.5296 | 122.3923 | 122.3648 | 122.3053 | -122.4884 | -122.4106 | 122.2458 | 122.3511 | 51.915 | 45.7947
1660.7656 | 122.5159 | -53.0914 | 69.31 | -0.079269 | 0.0010575 | 0.061598 | 0.11206 | 0.0035889 | -0.001004 | -0.0033112 | -0.049133 | -0.0036914 | 0.064392 | 0.05934 | -0.02615 | 0.00077333 | 0.0030975 | -1.6708 | 69.2505 | -53.2288 | 69.136 | -52.3361 | -53.4302 | 0.1831 | -7.8049 | 69.2322 | -53.1555 | 69.2139 | -53.0182 | -53.3066 | -53.0045 | -0.13733 | -0.05951 | -0.17395 | 0.75531 | 53.2745 | -0.33875 | 53.4119 | -0.20142 | -0.064087 | -0.07782 | -0.096131 | 0.073243 | 0.086975 | -0.21515 | 0.15106 | -0.15106 | 0.89264 | 122.3648 | 0.13733 | 122.3694 | 122.4792 | 122.3877 | 122.3419 | 122.3236 | -122.5388 | -122.4655 | 122.2275 | 122.3053 | 51.4206 | 45.2866
1661.8281 | 122.6074 | -54.1489 | 68.1976 | -0.10979 | -0.00065152 | 0.064589 | 0.11312 | -4.2682e-05 | -0.0037812 | -0.0035248 | -0.015564 | -0.00091423 | 0.064179 | 0.063613 | -0.026577 | 0.00034613 | 0.0011749 | -1.9226 | 68.2205 | -54.2679 | 68.0878 | -53.3752 | -54.4556 | 0.082397 | -7.9788 | 68.129 | -54.213 | 68.2159 | -54.0573 | -54.2679 | -54.0298 | -0.11902 | 0.022888 | -0.10986 | 0.77362 | 54.2313 | -0.3067 | 54.3503 | -0.18768 | -0.064087 | -0.068665 | 0.01831 | 0.091553 | 0.11902 | -0.11902 | 0.18311 | -0.054931 | 0.89264 | 122.3557 | 0.15564 | 122.4289 | 122.4884 | 122.3419 | 122.3694 | 122.2778 | -122.4655 | -122.4106 | 122.2366 | 122.3648 | 52.2263 | 46.17
1662.7656 | 122.5204 | -51.4664 | 70.9305 | -0.07164 | 0.00020288 | 0.063094 | 0.11377 | 0.0031617 | -0.0020722 | -0.002243 | -0.049133 | -0.00048703 | 0.063965 | 0.060195 | -0.027004 | 0.0029095 | -0.0022431 | -1.5839 | 70.8847 | -51.6357 | 70.784 | -50.6607 | -51.7822 | 0.49896 | -7.2693 | 70.8618 | -51.5305 | 70.8527 | -51.4343 | -51.6632 | -51.3931 | -0.16937 | -0.045776 | -0.14648 | 0.80566 | 51.9653 | -0.31586 | 52.1347 | -0.14648 | -0.064087 | -0.068665 | -0.07782 | 0.032044 | 0.073243 | -0.19684 | 0.13733 | -0.13275 | 0.97504 | 122.4197 | 0.096131 | 122.3831 | 122.5204 | 122.3923 | 122.3511 | 122.3282 | -122.5662 | -122.4609 | 122.2504 | 122.319 | 49.8825 | 44.1971
1663.8281 | 122.5479 | -52.597 | 69.7952 | -0.07164 | -1.0718e-05 | 0.060957 | 0.10928 | 0.0018799 | -0.0035674 | -0.003952 | -0.046081 | -0.0034778 | 0.063538 | 0.065749 | -0.026577 | 0.0016277 | 0.00096129 | -2.005 | 69.7037 | -52.771 | 69.6259 | -51.7273 | -53.0045 | 0.12817 | -7.6447 | 69.722 | -52.652 | 69.7266 | -52.4689 | -52.803 | -52.5192 | -0.17395 | -0.091553 | -0.16937 | 0.86975 | 52.7252 | -0.40741 | 52.8992 | -0.23346 | -0.054932 | -0.073242 | -0.068665 | 0.12817 | 0.07782 | -0.20599 | 0.13275 | -0.15106 | 1.0437 | 122.3969 | 0.18311 | 122.3785 | 122.4747 | 122.374 | 122.3007 | 122.319 | -122.5662 | -122.4472 | 122.2229 | 122.3236 | 50.592 | 44.9524
1664.7656 | 122.5342 | -52.8671 | 69.516 | -0.086899 | 0.00084388 | 0.060957 | 0.11099 | 0.00059812 | -0.0024994 | -0.00032036 | -0.04303 | -0.001128 | 0.062897 | 0.062117 | -0.027645 | 0.0012005 | 0.0020295 | -1.8402 | 69.4016 | -53.1052 | 69.3512 | -52.0706 | -53.1921 | 0.045776 | -7.695 | 69.4656 | -52.9266 | 69.4519 | -52.7435 | -53.0502 | -52.7893 | -0.23804 | -0.11444 | -0.16479 | 0.79651 | 52.9129 | -0.32501 | 53.1509 | -0.086975 | -0.05951 | -0.050354 | -0.064087 | 0.1236 | 0.077819 | -0.18311 | 0.13733 | -0.1236 | 1.0345 | 122.4564 | 0.18311 | 122.3785 | 122.5067 | 122.3923 | 122.2687 | 122.3328 | -122.6212 | -122.4426 | 122.2183 | 122.319 | 51.0269 | 45.1721
1665.8281 | 122.5616 | -52.8809 | 69.5023 | -0.12505 | 0.0014847 | 0.061171 | 0.11227 | 0.00081172 | -0.0016448 | -0.002243 | -0.04303 | -0.00027343 | 0.065247 | 0.05934 | -0.025295 | 0.0012005 | -0.0018157 | -1.8173 | 69.4748 | -53.0319 | 69.3192 | -51.8692 | -53.215 | 0 | -7.5668 | 69.4199 | -52.9266 | 69.4382 | -52.803 | -53.0411 | -52.771 | -0.15106 | -0.027466 | -0.1831 | 1.0117 | 52.8809 | -0.33417 | 53.0319 | -0.18311 | -0.045777 | -0.082397 | -0.064087 | 0.077819 | 0.10986 | -0.16022 | 0.15564 | -0.11444 | 1.1627 | 122.3511 | 0.1236 | 122.3648 | 122.5067 | 122.3465 | 122.3557 | 122.3007 | -122.5342 | -122.4289 | 122.2 | 122.319 | 51.0635 | 45.314
1666.7656 | 122.5479 | -51.8051 | 70.5917 | -0.16319 | 0.00020288 | 0.061598 | 0.11291 | -0.0013245 | 0.0002778 | 0.00053404 | -0.046081 | -0.0028368 | 0.061829 | 0.057204 | -0.02615 | 0.0016277 | 0.0067291 | -1.6388 | 70.4681 | -52.0203 | 70.4132 | -50.6836 | -52.1301 | 0.082397 | -7.457 | 70.5551 | -51.8188 | 70.5551 | -51.7639 | -51.9745 | -51.7227 | -0.21515 | -0.1236 | -0.17853 | 1.1215 | 51.8875 | -0.32501 | 52.1027 | -0.10986 | -0.013733 | -0.036621 | -0.036621 | 0.041199 | 0.082398 | -0.16937 | 0.096131 | -0.15564 | 1.3367 | 122.4335 | 0.054932 | 122.374 | 122.4884 | 122.374 | 122.2733 | 122.3602 | -122.612 | -122.4106 | 122.2183 | 122.3602 | 50.1663 | 44.3481
1667.8281 | 122.5616 | -51.4618 | 70.9076 | -0.15556 | -1.0718e-05 | 0.061598 | 0.11142 | 0.0010253 | -0.0007904 | -0.001175 | -0.036926 | -0.0017688 | 0.064179 | 0.063185 | -0.026363 | 0.00098693 | -0.00053411 | -1.6067 | 70.9396 | -51.5625 | 70.8481 | -50.3952 | -51.7044 | 0.009155 | -7.4799 | 71.0037 | -51.3565 | 70.8572 | -51.4481 | -51.6724 | -51.3977 | -0.10071 | 0.032043 | -0.05951 | 1.0666 | 51.4709 | -0.24262 | 51.5717 | -0.14191 | 0.10529 | 0.09613 | -0.050354 | 0.013733 | 0.064087 | -0.21057 | -0.041199 | -0.31586 | 1.1673 | 122.4106 | -0.091553 | 122.2137 | 122.5021 | 122.3602 | 122.4014 | 122.4655 | -122.4701 | -122.2641 | 122.3099 | 122.319 | 49.855 | 43.9819
1668.7656 | 122.5525 | -52.5558 | 69.8181 | -0.018234 | 0.0016983 | 0.060103 | 0.11184 | -0.0019653 | -0.0035674 | -0.002884 | -0.046081 | -0.0019824 | 0.063111 | 0.071303 | -0.025936 | 0.0022687 | 0.0043793 | -1.5976 | 69.7998 | -52.7115 | 69.6899 | -51.535 | -52.8854 | -0.12817 | -7.814 | 69.7815 | -52.6062 | 69.7632 | -52.4872 | -52.7206 | -52.4643 | -0.15564 | -0.01831 | -0.12817 | 1.0208 | 52.4277 | -0.32959 | 52.5833 | -0.17395 | -0.050354 | -0.036621 | -0.054931 | 0.068664 | 0.091553 | -0.16479 | 0.14191 | -0.11444 | 1.1765 | 122.4014 | 0.11902 | 122.3694 | 122.5113 | 122.3877 | 122.3557 | 122.3373 | -122.5296 | -122.4243 | 122.2458 | 122.319 | 50.9583 | 44.7418
1669.8281 | 122.6395 | -53.1097 | 69.1681 | -0.17082 | 0.00041648 | 0.060957 | 0.10928 | 0.0010253 | -0.0035674 | -0.0018158 | -0.039978 | -0.0049732 | 0.062897 | 0.060836 | -0.027004 | 0.0012005 | 0.0039521 | -1.6251 | 69.1818 | -53.2471 | 69.1544 | -52.3361 | -53.4073 | 0.004578 | -7.6584 | 69.1177 | -53.1738 | 69.2734 | -52.9541 | -53.1738 | -52.9587 | -0.13733 | 0.013733 | -0.013733 | 0.77362 | 53.1143 | -0.29755 | 53.2516 | -0.16022 | -0.064087 | -0.050354 | 0.10528 | 0.15564 | 0.15106 | -0.064087 | 0.21515 | 0 | 0.91095 | 122.4014 | 0.21973 | 122.4472 | 122.4289 | 122.2916 | 122.2916 | 122.2275 | -122.4152 | -122.3419 | 122.2641 | 122.3831 | 51.4847 | 45.4514
1670.7656 | 122.4976 | -51.6769 | 70.752 | -0.10979 | 0.0012711 | 0.060103 | 0.11312 | 0.0052979 | -0.0029266 | -0.0035248 | -0.070496 | -0.0028368 | 0.063324 | 0.058913 | -0.026791 | 0.0016277 | 0.0020295 | -1.4099 | 70.7062 | -51.8234 | 70.5231 | -50.8942 | -52.0798 | 0.28381 | -7.8003 | 70.6192 | -51.7822 | 70.6146 | -51.6357 | -51.8829 | -51.59 | -0.14648 | -0.045776 | -0.22888 | 0.78278 | 51.9608 | -0.40283 | 52.1072 | -0.25635 | -0.10529 | -0.13275 | -0.13733 | 0.041199 | 0.086975 | -0.20599 | 0.19226 | -0.10071 | 0.92926 | 122.3465 | 0.14648 | 122.3969 | 122.5296 | 122.4014 | 122.3831 | 122.2961 | -122.5754 | -122.5342 | 122.2 | 122.2916 | 50.267 | 43.8766
1671.8281 | 122.6212 | -53.1738 | 69.1681 | -0.07164 | -0.0010787 | 0.060744 | 0.11206 | -0.0023925 | -0.0007904 | -0.002884 | -0.049133 | -0.0017688 | 0.063965 | 0.059127 | -0.025722 | 0.00098693 | 0.0039521 | -1.5701 | 69.2734 | -53.2242 | 69.0262 | -52.5146 | -53.5172 | 0.032043 | -8.0978 | 69.0903 | -53.27 | 69.1635 | -53.0869 | -53.3157 | -53.0457 | -0.050354 | 0.10528 | -0.14191 | 0.65918 | 53.2059 | -0.34332 | 53.2562 | -0.29297 | -0.09613 | -0.07782 | -0.004578 | 0.086975 | 0.12817 | -0.14191 | 0.2243 | -0.045777 | 0.70953 | 122.2504 | 0.18311 | 122.4335 | 122.4976 | 122.3602 | 122.4472 | 122.2641 | -122.3923 | -122.438 | 122.2 | 122.3373 | 51.6037 | 45.076
1672.7656 | 122.5204 | -53.2883 | 69.0537 | -0.13267 | -0.0010787 | 0.062453 | 0.11291 | -0.0015381 | -0.0005768 | -0.0018158 | -0.073547 | -5.9826e-05 | 0.065247 | 0.056777 | -0.027004 | 0.0037641 | 0.00010689 | -1.5335 | 69.104 | -53.4393 | 68.7607 | -52.2354 | -53.2974 | 0.19226 | -8.107 | 69.0765 | -53.3203 | 69.0445 | -53.2242 | -53.5034 | -53.2425 | -0.15106 | 0.050354 | -0.29297 | 1.0529 | 53.4805 | -0.009155 | 53.6316 | 0.14191 | -0.032043 | 0.022888 | -0.009155 | 0.064087 | 0.045776 | -0.21515 | 0.077819 | -0.18311 | 1.2039 | 122.2 | 0.09613 | 122.3648 | 122.5433 | 122.3969 | 122.3923 | 122.3648 | -122.493 | -122.374 | 122.049 | 122.3328 | 51.7548 | 45.1813
1673.8281 | 122.5204 | -52.7435 | 69.6579 | -0.11742 | 0.0025529 | 0.062453 | 0.1127 | -0.00068368 | -0.0039948 | -0.0016022 | -0.058289 | -0.0032642 | 0.064179 | 0.061263 | -0.025295 | 0.00077333 | 0.00032049 | -1.6479 | 69.5801 | -52.8809 | 69.4839 | -51.8326 | -53.1509 | 0.41199 | -7.9697 | 69.5709 | -52.8305 | 69.5755 | -52.7252 | -52.9404 | -52.652 | -0.13733 | -0.07782 | -0.17395 | 0.91095 | 53.1555 | -0.40741 | 53.2928 | -0.27008 | -0.086975 | -0.086975 | -0.082398 | 0.01831 | 0.091552 | -0.19684 | 0.17853 | -0.10986 | 1.0483 | 122.3648 | 0.10529 | 122.406 | 122.4609 | 122.4014 | 122.3236 | 122.3145 | -122.5388 | -122.4884 | 122.2275 | 122.319 | 51.0956 | 44.7739
1674.7656 | 122.5525 | -52.8854 | 69.5389 | -0.094528 | 0.0010575 | 0.063094 | 0.1127 | 0.0035889 | -0.0020722 | -0.0043792 | -0.049133 | -0.0026232 | 0.06247 | 0.064681 | -0.028713 | 0.0024823 | -0.0041657 | -1.3687 | 69.5206 | -53.0045 | 69.397 | -51.828 | -53.183 | 0.44403 | -7.8506 | 69.4427 | -52.9495 | 69.4336 | -52.8351 | -53.0777 | -52.7939 | -0.11902 | -0.01831 | -0.14191 | 1.0574 | 53.3295 | -0.29755 | 53.4485 | -0.17853 | -0.064087 | -0.09613 | -0.10528 | 0.050354 | 0.091553 | -0.19226 | 0.15564 | -0.12817 | 1.1765 | 122.4014 | 0.11444 | 122.3831 | 122.525 | 122.3923 | 122.406 | 122.3282 | -122.5433 | -122.4884 | 122.2824 | 122.319 | 51.5167 | 45.0348
1675.8281 | 122.5708 | -52.9953 | 69.3878 | -0.079269 | 0.00084388 | 0.061385 | 0.11355 | 0.0033753 | -0.0007904 | -0.00074776 | -0.04303 | -0.0036914 | 0.064179 | 0.060836 | -0.026791 | 0.0026959 | -0.00032051 | -1.4694 | 69.4473 | -53.0914 | 69.2459 | -52.1164 | -53.2654 | 0.58594 | -7.7362 | 69.3283 | -53.0502 | 69.3466 | -52.858 | -53.1509 | -52.8992 | -0.096131 | 0.05951 | -0.14191 | 0.87891 | 53.5812 | -0.27008 | 53.6774 | -0.17395 | -0.054932 | -0.059509 | -0.041198 | 0.13733 | 0.09613 | -0.15564 | 0.15106 | -0.10071 | 0.97504 | 122.3373 | 0.19226 | 122.3969 | 122.5388 | 122.3785 | 122.4426 | 122.3236 | -122.4792 | -122.438 | 122.2412 | 122.3419 | 51.5259 | 45.2591
1676.7656 | 122.5204 | -53.0594 | 69.3375 | -0.086899 | 0.00020288 | 0.061812 | 0.11206 | 0.0029479 | -0.004422 | -0.0018158 | -0.039978 | -0.0019824 | 0.06546 | 0.057204 | -0.025722 | 0.0029095 | -0.00053411 | -1.4465 | 69.3878 | -53.1235 | 69.1589 | -52.1301 | -53.4119 | 0.42114 | -8.0246 | 69.3146 | -53.1097 | 69.2642 | -52.8809 | -53.6224 | -53.2013 | -0.064087 | 0.050354 | -0.17853 | 0.92926 | 53.4805 | -0.35248 | 53.5446 | -0.28839 | -0.050354 | -0.022888 | -0.073242 | 0.17853 | -0.14191 | -0.56305 | -0.091553 | -0.5127 | 0.99335 | 122.2824 | 0.22888 | 122.374 | 122.5113 | 122.4243 | 122.4472 | 122.374 | -122.4609 | -122.4472 | 122.2183 | 122.3236 | 51.6129 | 45.0348
1677.8281 | 122.5616 | -53.0914 | 69.2734 | -0.14793 | 0.00063028 | 0.061812 | 0.11334 | 0.0029479 | -0.002713 | 0.001175 | -0.039978 | -0.0032642 | 0.064392 | 0.062758 | -0.025295 | 0.0029095 | 0.0037385 | -1.5335 | 69.3466 | -53.2013 | 69.0628 | -52.1805 | -53.5126 | 0.35248 | -8.3313 | 69.2276 | -53.1647 | 69.2459 | -53.009 | -53.2654 | -53.0045 | -0.10986 | 0.073243 | -0.21057 | 0.91095 | 53.4439 | -0.42114 | 53.5538 | -0.31128 | -0.073242 | -0.045776 | -0.027465 | 0.082398 | 0.086975 | -0.17395 | 0.16022 | -0.10071 | 1.0208 | 122.2641 | 0.15564 | 122.4106 | 122.5479 | 122.3923 | 122.4381 | 122.319 | -122.4747 | -122.438 | 122.1542 | 122.3373 | 51.5579 | 44.7601
1678.7656 | 122.5021 | -53.6957 | 68.7012 | -0.086899 | 0.0010575 | 0.06288 | 0.11142 | 0.0044433 | -0.0029266 | -0.0018158 | -0.064392 | -0.0026232 | 0.062042 | 0.063399 | -0.02615 | 0.0020551 | -0.00053411 | -1.5976 | 68.7149 | -53.7781 | 68.6005 | -52.7252 | -53.9658 | 0.33875 | -8.4686 | 68.7195 | -53.7003 | 68.6462 | -53.6499 | -53.8834 | -53.6362 | -0.082397 | 0.013733 | -0.10071 | 0.97046 | 54.0344 | -0.27008 | 54.1168 | -0.18768 | -0.004577 | 0.01831 | -0.054932 | 0.045777 | 0.05951 | -0.18768 | 0.064087 | -0.18311 | 1.0529 | 122.3785 | 0.050354 | 122.3465 | 122.493 | 122.4197 | 122.4106 | 122.4152 | -122.4792 | -122.4014 | 122.2961 | 122.3419 | 52.0981 | 45.2271
1679.8281 | 122.612 | -53.4119 | 68.8751 | -0.16319 | -0.0010787 | 0.061812 | 0.1127 | 0.00059812 | -0.0031402 | -0.0026704 | -0.012512 | -0.0024096 | 0.06247 | 0.055709 | -0.027859 | 0.0037641 | 0.0011749 | -1.5106 | 68.866 | -53.6041 | 68.8614 | -52.3315 | -53.6865 | 0.32501 | -8.2397 | 68.8202 | -53.4988 | 68.8385 | -53.1692 | -53.2562 | -53.0777 | -0.19226 | -0.009155 | -0.013733 | 1.0803 | 53.7369 | -0.27466 | 53.9291 | -0.082397 | -0.086975 | -0.054932 | -0.036621 | 0.24262 | 0.33417 | 0.15564 | 0.42114 | 0.24261 | 1.2726 | 122.4655 | 0.32959 | 122.3373 | 122.4701 | 122.319 | 122.2778 | 122.2321 | -122.4792 | -122.374 | 122.2733 | 122.2504 | 51.9012 | 45.1721
1680.7656 | 122.5067 | -53.2242 | 69.2047 | -0.056381 | 0.0021255 | 0.061385 | 0.11377 | -0.0028199 | 6.4004e-05 | -0.0026704 | -0.067444 | -0.0015552 | 0.062683 | 0.062117 | -0.027218 | 0.0050457 | -0.0033111 | -1.4282 | 69.1269 | -53.4164 | 69.0399 | -52.0477 | -53.5263 | 0.25635 | -8.3908 | 69.1406 | -53.2379 | 69.0811 | -53.1509 | -53.421 | -53.1235 | -0.19226 | -0.07782 | -0.16479 | 1.1765 | 53.4805 | -0.30212 | 53.6728 | -0.10986 | -0.013733 | -0.064087 | -0.1236 | 0.073242 | 0.10071 | -0.19684 | 0.11444 | -0.18311 | 1.3687 | 122.4564 | 0.086975 | 122.319 | 122.5433 | 122.3785 | 122.3511 | 122.3648 | -122.6212 | -122.4426 | 122.2641 | 122.3053 | 51.796 | 44.8334
1681.8281 | 122.5754 | -52.7573 | 69.6075 | -0.07164 | 0.00020288 | 0.063307 | 0.11099 | 0.0031617 | -0.0022858 | -0.0026704 | -0.070496 | -0.0032642 | 0.063538 | 0.060195 | -0.026363 | 0.0018413 | -0.00053411 | -1.4832 | 69.5938 | -52.8763 | 69.5114 | -51.6861 | -53.0411 | -0.29755 | -8.1757 | 69.5938 | -52.8076 | 69.5801 | -52.6794 | -52.9312 | -52.652 | -0.11902 | -0.013733 | -0.09613 | 1.0712 | 52.4597 | -0.28381 | 52.5787 | -0.16479 | -0.050354 | -0.013733 | -0.027466 | 0.07782 | 0.10529 | -0.17395 | 0.15564 | -0.1236 | 1.1902 | 122.3877 | 0.12817 | 122.3877 | 122.4701 | 122.4014 | 122.3511 | 122.3511 | -122.4838 | -122.4152 | 122.2687 | 122.3373 | 51.2741 | 44.5816
1682.7656 | 122.5342 | -53.2791 | 69.104 | -0.086899 | 0.0012711 | 0.062453 | 0.10992 | 0.0027343 | -0.002713 | -0.00074776 | -0.052185 | -0.0032642 | 0.064392 | 0.062331 | -0.026791 | 0.0020551 | 0.0026703 | -1.4877 | 69.1406 | -53.3752 | 69.0537 | -52.1713 | -53.4851 | 0.28381 | -8.2535 | 69.0857 | -53.3157 | 69.0353 | -53.2242 | -53.4622 | -53.1921 | -0.09613 | 0.036621 | -0.050354 | 1.1078 | 53.5629 | -0.20599 | 53.6591 | -0.10986 | -0.036621 | -0.018311 | -0.068665 | 0.054932 | 0.086975 | -0.1831 | 0.1236 | -0.14648 | 1.2039 | 122.4289 | 0.091553 | 122.3511 | 122.5159 | 122.4014 | 122.4197 | 122.3648 | -122.4792 | -122.4197 | 122.3328 | 122.3145 | 51.7914 | 45.0256
1683.8281 | 122.525 | -53.27 | 69.104 | -0.056381 | 0.0019119 | 0.063307 | 0.11227 | -0.00046988 | -0.0031402 | -0.001175 | -0.046081 | -0.0041186 | 0.068238 | 0.060195 | -0.025509 | 0.0012005 | 0.0024567 | -1.5244 | 69.1498 | -53.389 | 68.9438 | -52.6382 | -53.6179 | 0.16479 | -8.6288 | 68.9987 | -53.3707 | 69.0491 | -53.183 | -53.5538 | -53.2288 | -0.11902 | 0.045776 | -0.16022 | 0.63171 | 53.4348 | -0.3479 | 53.5538 | -0.22888 | -0.10071 | -0.10529 | -0.054932 | 0.086975 | 0.041198 | -0.28381 | 0.14191 | -0.18311 | 0.75073 | 122.3328 | 0.18768 | 122.4197 | 122.5388 | 122.3694 | 122.4197 | 122.2687 | -122.493 | -122.4747 | 122.2137 | 122.319 | 51.7456 | 44.6411
1684.7656 | 122.5479 | -53.3615 | 69.0262 | -0.36919 | 0.00020288 | 0.056898 | 0.11142 | 0.0012391 | -0.0031402 | -0.0026704 | -0.049133 | -0.0024096 | 0.065888 | 0.058272 | -0.026577 | 0.0012005 | 0.0050201 | -1.2131 | 69.0353 | -53.4531 | 68.8889 | -52.327 | -53.627 | 0.28381 | -8.4091 | 69.0033 | -53.389 | 68.9713 | -53.3157 | -53.5767 | -53.27 | -0.091553 | 0.009155 | -0.13733 | 1.0345 | 53.6453 | -0.2655 | 53.7369 | -0.17395 | -0.027466 | -0.022888 | -0.054932 | 0.045776 | 0.091553 | -0.21515 | 0.11902 | -0.18768 | 1.1261 | 122.3419 | 0.073242 | 122.3602 | 122.4884 | 122.3923 | 122.3969 | 122.3648 | -122.4792 | -122.4152 | 122.2504 | 122.3328 | 52.1484 | 44.9524
1685.8281 | 122.6257 | -52.8214 | 69.5389 | -0.10216 | 0.00020288 | 0.06288 | 0.11377 | 0.0014527 | 0.0004914 | -0.0026704 | -0.021667 | -0.0030506 | 0.063324 | 0.062972 | -0.028927 | 0.0014141 | 0.0052337 | -1.4694 | 69.5297 | -52.9816 | 69.4107 | -52.0432 | -53.1601 | 0.54932 | -8.0475 | 69.4702 | -52.8946 | 69.548 | -52.7298 | -52.9587 | -52.7069 | -0.16022 | -0.009155 | -0.12817 | 0.7782 | 53.3707 | -0.33874 | 53.5309 | -0.17853 | -0.073242 | -0.068664 | 0.009156 | 0.091553 | 0.11444 | -0.13733 | 0.18768 | -0.064087 | 0.93841 | 122.3923 | 0.1648 | 122.4426 | 122.5113 | 122.3648 | 122.3511 | 122.2916 | -122.5204 | -122.4335 | 122.2321 | 122.3694 | 51.3519 | 44.7739
1686.7656 | 122.5433 | -55.0552 | 67.3416 | -0.06401 | 0.00041648 | 0.06053 | 0.11377 | 0.0040161 | -0.002713 | -0.002884 | -0.064392 | -0.003905 | 0.062042 | 0.056136 | -0.026577 | 0.00055973 | -0.00074771 | -1.5015 | 67.3004 | -55.2155 | 67.1814 | -54.483 | -55.3894 | 0.37994 | -8.638 | 67.2775 | -55.1147 | 67.2638 | -55.0095 | -55.2338 | -54.9591 | -0.16022 | -0.041199 | -0.16022 | 0.5722 | 55.4352 | -0.33417 | 55.5954 | -0.17395 | -0.059509 | -0.064087 | -0.07782 | 0.045777 | 0.096131 | -0.17853 | 0.15564 | -0.11902 | 0.73242 | 122.3969 | 0.10529 | 122.3785 | 122.5159 | 122.3923 | 122.3557 | 122.3328 | -122.5571 | -122.4564 | 122.2366 | 122.319 | 53.5538 | 46.4172
1687.8281 | 122.5891 | -54.1397 | 68.2434 | -0.13267 | -0.00065152 | 0.061812 | 0.11398 | 0.0044433 | -0.0018586 | -0.0026704 | -0.049133 | 0.0010084 | 0.061402 | 0.062972 | -0.027431 | 0.0012005 | 0.00096129 | -1.4465 | 68.1747 | -54.332 | 68.0145 | -53.6957 | -54.5151 | 0.43945 | -8.4641 | 68.1198 | -54.2404 | 68.2388 | -54.0161 | -54.2175 | -54.0115 | -0.19226 | -0.068664 | -0.22888 | 0.44403 | 54.5792 | -0.37537 | 54.7714 | -0.18311 | -0.10071 | -0.1236 | -0.004577 | 0.1236 | 0.12817 | -0.07782 | 0.22888 | 0.022888 | 0.63629 | 122.3465 | 0.2243 | 122.4792 | 122.5067 | 122.3602 | 122.3145 | 122.2595 | -122.5754 | -122.4838 | 122.1542 | 122.3785 | 52.6932 | 45.6757
1688.7656 | 122.5296 | -53.5858 | 68.8248 | -0.07164 | 0.00041648 | 0.061385 | 0.11248 | 0.0025207 | -0.0003632 | -0.003952 | -0.06134 | -0.002196 | 0.063111 | 0.06169 | -0.028286 | 0.00077333 | 0.0037385 | -1.4236 | 68.8019 | -53.6911 | 68.7012 | -52.652 | -53.8742 | 0.48523 | -8.1161 | 68.7744 | -53.6133 | 68.7607 | -53.4988 | -53.7506 | -53.4805 | -0.10529 | -0.022888 | -0.1236 | 0.93384 | 54.071 | -0.28839 | 54.1763 | -0.18311 | -0.027466 | -0.050354 | -0.064087 | 0.086975 | 0.10528 | -0.1648 | 0.13275 | -0.13733 | 1.0391 | 122.3923 | 0.11444 | 122.374 | 122.493 | 122.3877 | 122.3877 | 122.3602 | -122.5159 | -122.438 | 122.287 | 122.3465 | 52.1622 | 45.4697
1689.8281 | 122.5571 | -53.9017 | 68.5135 | -0.14793 | 0.00020288 | 0.061385 | 0.11441 | 0.0059387 | -0.0020722 | -0.001175 | -0.049133 | -0.003905 | 0.062683 | 0.057845 | -0.0238 | -0.0034991 | -0.00074771 | -1.4511 | 68.4814 | -54.0482 | 68.3075 | -53.508 | -54.277 | 0.3891 | -8.2993 | 68.454 | -53.9566 | 68.5776 | -53.9612 | -54.1672 | -53.801 | -0.14649 | -0.032044 | -0.20599 | 0.39368 | 54.2908 | -0.37537 | 54.4373 | -0.22888 | -0.054932 | -0.05951 | 0.064087 | -0.05951 | 0.10071 | -0.2655 | 0.15564 | -0.21057 | 0.54016 | 122.3557 | -0.004578 | 122.5342 | 122.5296 | 122.4106 | 122.3831 | 122.3557 | -122.5616 | -122.4701 | 122.2092 | 122.4792 | 52.4506 | 45.6024
1690.7656 | 122.5342 | -53.7048 | 68.692 | -0.06401 | 0.00063028 | 0.059889 | 0.10907 | 0.0012391 | -0.0029266 | -0.0018158 | -0.033874 | -0.0017688 | 0.064606 | 0.059127 | -0.025295 | 0.0033367 | -0.0028839 | -1.5747 | 68.5181 | -54.0527 | 68.2755 | -53.2974 | -54.1122 | 0.44403 | -8.1894 | 68.5822 | -53.7735 | 68.6142 | -53.6179 | -53.8742 | -53.5858 | -0.3479 | -0.17395 | -0.41657 | 0.40741 | 54.1489 | -0.40741 | 54.4968 | -0.05951 | -0.068665 | -0.10986 | -0.07782 | 0.086975 | 0.11902 | -0.16937 | 0.18768 | -0.10071 | 0.75531 | 122.3282 | 0.15564 | 122.3877 | 122.5708 | 122.3557 | 122.2229 | 122.287 | -122.7448 | -122.4655 | 121.9803 | 122.319 | 52.1301 | 45.5154
1691.8281 | 122.5479 | -53.2837 | 69.1544 | 0.073319 | -0.00065152 | 0.059889 | 0.11227 | 0.0025207 | -0.0029266 | -0.002884 | -0.027771 | -0.0026232 | 0.065033 | 0.063613 | -0.027859 | -0.00072207 | 0.0033111 | -1.3779 | 69.2139 | -53.334 | 69.0537 | -52.24 | -53.5172 | 0.2655 | -8.2535 | 69.1452 | -53.2516 | 69.0674 | -53.2059 | -53.4393 | -53.1692 | -0.050354 | 0.059509 | -0.10071 | 1.0437 | 53.5492 | -0.23346 | 53.5995 | -0.18311 | 0.032043 | -0.009155 | -0.086975 | 0.077819 | 0.11444 | -0.15564 | 0.082398 | -0.18768 | 1.0941 | 122.3877 | 0.045776 | 122.319 | 122.5479 | 122.3969 | 122.4976 | 122.4289 | -122.4884 | -122.406 | 122.3373 | 122.3511 | 51.9058 | 45.0302
1692.7656 | 122.6395 | -53.7552 | 68.6005 | 0.10384 | 0.0027665 | 0.062453 | 0.10971 | -0.0028199 | -0.0035674 | -0.0050202 | 0.088196 | -0.0026232 | 0.063111 | 0.055281 | -0.025295 | -0.00029487 | -0.00032051 | -1.5839 | 68.7012 | -53.7186 | 68.4998 | -52.8168 | -54.0207 | 0.11444 | -8.3817 | 68.573 | -53.7506 | 68.6325 | -53.5767 | -53.8239 | -53.5995 | 0.036621 | 0.10071 | -0.10071 | 0.93842 | 53.8696 | -0.2655 | 53.833 | -0.30212 | 0.004578 | -0.027466 | 0.032043 | 0.17853 | 0.15564 | -0.068665 | 0.15106 | -0.073243 | 0.90179 | 122.2183 | 0.17395 | 122.3831 | 122.4197 | 122.3236 | 122.4564 | 122.3282 | -122.319 | -122.3511 | 122.2549 | 122.3877 | 52.1713 | 45.3735
1693.8281 | 122.6532 | -54.4647 | 67.8497 | -0.17845 | -0.0021469 | 0.063734 | 0.11099 | 0.00038452 | -0.0020722 | -0.00032036 | -0.046081 | -0.0036914 | 0.065033 | 0.063399 | -0.028072 | 0.0026959 | 0.0030975 | -1.7258 | 67.8497 | -54.6295 | 67.8726 | -53.8788 | -54.657 | -0.14648 | -8.8852 | 67.8726 | -54.4693 | 67.9184 | -54.3274 | -54.5746 | -54.2908 | -0.16479 | 0 | 0.022889 | 0.58594 | 54.3182 | -0.19226 | 54.483 | -0.027465 | -0.004577 | 0.022889 | 0.068665 | 0.13733 | 0.17395 | -0.10986 | 0.17853 | -0.10529 | 0.75073 | 122.5021 | 0.14191 | 122.3877 | 122.4792 | 122.3419 | 122.3145 | 122.3373 | -122.4792 | -122.319 | 122.3373 | 122.3831 | 52.739 | 45.5795
1694.7656 | 122.6212 | -53.7048 | 68.6508 | -0.06401 | 0.00063028 | 0.062239 | 0.11526 | -0.0032471 | -0.0024994 | -0.00032036 | -0.052185 | -0.0032642 | 0.06247 | 0.059554 | -0.027859 | 0.0012005 | 0.0024567 | -1.561 | 68.6874 | -53.7964 | 68.6188 | -53.0182 | -53.9612 | 0.086975 | -8.6472 | 68.66 | -53.7186 | 68.6874 | -53.5492 | -53.8193 | -53.5446 | -0.091553 | 0.036621 | -0.032044 | 0.68665 | 53.7918 | -0.25635 | 53.8834 | -0.16479 | -0.013733 | 0.009155 | 0.036621 | 0.15564 | 0.16022 | -0.11444 | 0.17395 | -0.10071 | 0.7782 | 122.4152 | 0.16937 | 122.406 | 122.4838 | 122.3785 | 122.3923 | 122.3648 | -122.4472 | -122.3694 | 122.3236 | 122.3923 | 52.1439 | 45.0577
1695.8281 | 122.5525 | -54.158 | 68.2159 | -0.1403 | 0.00063028 | 0.061385 | 0.11184 | 0.0020935 | -0.0054902 | -0.002243 | -0.046081 | -0.0041186 | 0.063965 | 0.060622 | -0.025722 | -0.00029487 | 0.0022431 | -1.7349 | 68.1793 | -54.3274 | 68.0328 | -53.5309 | -54.5563 | -0.022888 | -8.8669 | 68.1519 | -54.2313 | 68.161 | -54.0802 | -54.3365 | -54.039 | -0.16937 | -0.036621 | -0.1831 | 0.62714 | 54.1351 | -0.39825 | 54.3045 | -0.22888 | -0.073242 | -0.064087 | -0.054931 | 0.07782 | 0.11902 | -0.17853 | 0.19226 | -0.10529 | 0.79651 | 122.3602 | 0.15106 | 122.3923 | 122.5067 | 122.3831 | 122.3373 | 122.3099 | -122.5433 | -122.4472 | 122.1909 | 122.319 | 52.4231 | 45.2911
1696.7656 | 122.5525 | -53.7918 | 68.5547 | -0.15556 | 0.00041648 | 0.062453 | 0.11377 | 0.0038025 | -0.0046356 | -0.002884 | -0.070496 | -0.0024096 | 0.061188 | 0.06169 | -0.028072 | 0.0014141 | 0.0011749 | -1.561 | 68.5959 | -53.8971 | 68.5181 | -53.0823 | -54.039 | 0.10071 | -8.5968 | 68.5684 | -53.833 | 68.5638 | -53.714 | -53.9978 | -53.7277 | -0.10529 | 0.041199 | -0.036621 | 0.70953 | 53.8925 | -0.24719 | 53.9978 | -0.14191 | -0.041199 | 0.013733 | 0.009156 | 0.07782 | 0.064087 | -0.20599 | 0.10529 | -0.16479 | 0.81482 | 122.4152 | 0.11902 | 122.3969 | 122.493 | 122.4014 | 122.3877 | 122.3602 | -122.4518 | -122.3877 | 122.3099 | 122.3557 | 52.2308 | 45.195
1697.8281 | 122.5571 | -54.1077 | 68.28 | -0.15556 | 0.00020288 | 0.060103 | 0.11377 | 0.00081172 | -0.0024994 | -0.0016022 | -0.055237 | -0.0030506 | 0.063751 | 0.059767 | -0.025509 | 0.00013253 | 0.0024567 | -1.4786 | 68.3212 | -54.1946 | 68.1793 | -53.4576 | -54.4052 | 0.40741 | -8.6334 | 68.2709 | -54.1306 | 68.2388 | -54.0344 | -54.2953 | -54.0253 | -0.086975 | 0.041199 | -0.10071 | 0.65002 | 54.5151 | -0.29755 | 54.6021 | -0.21057 | -0.022888 | -0.009155 | -0.041198 | 0.073242 | 0.082397 | -0.18768 | 0.10528 | -0.1648 | 0.737 | 122.374 | 0.09613 | 122.3694 | 122.5159 | 122.4014 | 122.4289 | 122.3785 | -122.4747 | -122.4106 | 122.287 | 122.3465 | 52.6291 | 45.4742
1698.7656 | 122.5433 | -53.5034 | 68.8568 | -0.10216 | 0.0019119 | 0.060744 | 0.11377 | 0.0044433 | -0.0020722 | -0.0024566 | -0.079651 | -0.0013416 | 0.063751 | 0.061904 | -0.027218 | 0.0029095 | 0.00074769 | -1.561 | 68.9621 | -53.5721 | 68.6508 | -52.9404 | -53.9154 | 0.44861 | -8.3038 | 68.8614 | -53.5034 | 68.8889 | -53.3798 | -53.6957 | -53.4622 | -0.068665 | 0.10528 | -0.20599 | 0.56305 | 53.952 | -0.41199 | 54.0207 | -0.34332 | 0 | 0.004577 | 0.032043 | 0.1236 | 0.041199 | -0.19226 | 0.041199 | -0.19226 | 0.63171 | 122.2229 | 0.1236 | 122.3923 | 122.5342 | 122.3648 | 122.4655 | 122.3648 | -122.4289 | -122.3602 | 122.1542 | 122.3923 | 51.9424 | 45.1996
1699.8281 | 122.4976 | -53.9017 | 68.4906 | -0.06401 | -0.0012923 | 0.06288 | 0.11206 | 0.00081172 | -0.0029266 | -0.003952 | -0.021667 | -0.0026232 | 0.062683 | 0.058699 | -0.02615 | -0.00029487 | 0.0067291 | -1.5564 | 68.4677 | -54.0619 | 68.3075 | -53.2516 | -54.1763 | 0.25177 | -8.5922 | 68.4402 | -53.9658 | 68.4311 | -53.7964 | -54.0436 | -53.7872 | -0.16022 | -0.022889 | -0.18311 | 0.65002 | 54.1534 | -0.27466 | 54.3137 | -0.11444 | -0.064087 | -0.050354 | -0.05951 | 0.10528 | 0.11444 | -0.14191 | 0.17853 | -0.07782 | 0.81024 | 122.3694 | 0.16937 | 122.3969 | 122.5296 | 122.406 | 122.3694 | 122.3419 | -122.5525 | -122.4564 | 122.2092 | 122.3328 | 52.3453 | 45.3094
1700.7656 | 122.5433 | -53.8742 | 68.5638 | -0.10216 | 0.0014847 | 0.060744 | 0.11291 | -0.00089728 | -0.0042084 | -0.002884 | -0.067444 | -0.0032642 | 0.063111 | 0.055068 | -0.025295 | 0.0018413 | 0.0011749 | -1.6159 | 68.573 | -53.9337 | 68.4677 | -53.3615 | -54.1031 | 0.15564 | -8.6014 | 68.5638 | -53.8239 | 68.4952 | -53.7598 | -54.071 | -53.7872 | -0.059509 | 0.009155 | -0.096131 | 0.5127 | 54.0298 | -0.22888 | 54.0894 | -0.16937 | 0.050354 | 0 | -0.068665 | 0.11444 | 0.086976 | -0.19684 | 0.036622 | -0.24719 | 0.5722 | 122.4014 | 0.064087 | 122.319 | 122.5067 | 122.3877 | 122.4472 | 122.4381 | -122.4976 | -122.3877 | 122.3419 | 122.3694 | 52.2583 | 45.2728
1701.8281 | 122.525 | -54.2633 | 68.1198 | -0.010605 | -0.0015061 | 0.061385 | 0.11312 | -0.00089728 | -0.0014312 | -0.002884 | -0.073547 | -0.0017688 | 0.064179 | 0.06169 | -0.025082 | 0.0022687 | 0.0033111 | -1.6663 | 68.2251 | -54.3274 | 68.042 | -53.6407 | -54.5288 | 0.1831 | -8.9035 | 68.161 | -54.2084 | 68.0878 | -54.1901 | -54.4693 | -54.1672 | -0.064087 | 0.10529 | -0.07782 | 0.62256 | 54.4464 | -0.2655 | 54.5105 | -0.20142 | 0.054932 | 0.041199 | -0.032043 | 0.073243 | 0.096131 | -0.20599 | 0.041199 | -0.26093 | 0.68665 | 122.3694 | 0.018311 | 122.2961 | 122.5525 | 122.3694 | 122.4884 | 122.4243 | -122.4472 | -122.3282 | 122.3053 | 122.3511 | 52.597 | 45.3598
1702.7656 | 122.5204 | -53.5812 | 68.8065 | -0.13267 | 0.0012711 | 0.063094 | 0.11355 | 0.00038452 | -0.0024994 | -0.0020294 | -0.064392 | -0.0036914 | 0.064179 | 0.050368 | -0.028072 | 0.00055973 | 0.0026703 | -1.6296 | 68.7653 | -53.7598 | 68.6874 | -52.9083 | -53.8788 | 0.48065 | -8.6838 | 68.8065 | -53.6179 | 68.7927 | -53.4714 | -53.7369 | -53.4897 | -0.17853 | -0.041199 | -0.11902 | 0.67291 | 54.0619 | -0.29755 | 54.2404 | -0.11902 | -0.036621 | 0 | -0.013733 | 0.10986 | 0.091553 | -0.15564 | 0.12817 | -0.11902 | 0.85144 | 122.4472 | 0.14648 | 122.4106 | 122.525 | 122.4243 | 122.3465 | 122.3877 | -122.5662 | -122.4243 | 122.2687 | 122.374 | 51.9516 | 44.8975
1703.8281 | 122.5754 | -53.9703 | 68.3853 | -0.14793 | 0.0012711 | 0.06053 | 0.11441 | 0.0027343 | -0.0031402 | -0.001175 | -0.024719 | -0.0043322 | 0.065033 | 0.060408 | -0.027218 | 0.00034613 | 0.0037385 | -1.7715 | 68.4082 | -54.1214 | 68.2617 | -53.4531 | -54.2908 | 0.24261 | -8.931 | 68.3258 | -54.0619 | 68.3395 | -53.8879 | -54.1397 | -53.8696 | -0.15106 | 0.022888 | -0.1236 | 0.51727 | 54.213 | -0.32043 | 54.364 | -0.16937 | -0.091553 | -0.059509 | -0.045776 | 0.082398 | 0.10071 | -0.16937 | 0.19226 | -0.077819 | 0.66833 | 122.3831 | 0.17395 | 122.4014 | 122.5296 | 122.3877 | 122.3785 | 122.2961 | -122.5067 | -122.4472 | 122.2321 | 122.3099 | 52.1988 | 45.0394
1704.7656 | 122.5479 | -55.0369 | 67.3599 | -0.11742 | -0.0010787 | 0.06053 | 0.11355 | -0.00068368 | -0.0018586 | -0.0013886 | -0.052185 | -0.00027343 | 0.063965 | 0.056777 | -0.025509 | 0.0029095 | 0.0016021 | -1.9684 | 67.3965 | -55.1102 | 67.2455 | -54.538 | -55.3528 | 0.086975 | -9.4894 | 67.3096 | -55.0827 | 67.2775 | -54.8538 | -55.2795 | -54.9774 | -0.073242 | 0.036621 | -0.11444 | 0.49896 | 55.1239 | -0.31586 | 55.1971 | -0.24262 | -0.045777 | -0.050354 | -0.082397 | 0.1831 | 0.059509 | -0.24262 | 0.10529 | -0.19684 | 0.5722 | 122.3557 | 0.22888 | 122.3602 | 122.5067 | 122.3923 | 122.4335 | 122.3465 | -122.4701 | -122.4426 | 122.2824 | 122.3145 | 53.0685 | 45.5475
1705.8281 | 122.5479 | -54.9637 | 67.4149 | -0.10979 | 0.00063028 | 0.062666 | 0.11184 | 0.0065795 | -0.0050628 | -0.00074776 | -0.012512 | -0.0019824 | 0.062683 | 0.064894 | -0.027431 | 0.0024823 | 0.0026703 | -1.9089 | 67.3691 | -55.1651 | 67.5201 | -54.3823 | -55.4169 | 0.59509 | -9.2926 | 67.4057 | -55.0003 | 67.3737 | -54.8904 | -55.1605 | -54.8584 | -0.20142 | -0.045776 | 0.10529 | 0.58136 | 55.5588 | -0.45319 | 55.7602 | -0.25177 | -0.036621 | -0.009155 | -0.041199 | 0.073242 | 0.10529 | -0.19684 | 0.14191 | -0.16022 | 0.78278 | 122.6852 | 0.10986 | 122.374 | 122.5342 | 122.406 | 122.3328 | 122.3694 | -122.58 | -122.4152 | 122.4838 | 122.3373 | 53.0548 | 45.6711
1706.7656 | 122.4884 | -53.9108 | 68.4814 | -0.10979 | -0.00022432 | 0.06053 | 0.11163 | 0.0025207 | -0.004422 | -0.0018158 | -0.04303 | -0.0019824 | 0.063324 | 0.057845 | -0.02914 | 0.00055973 | 0.00053409 | -1.6571 | 68.4036 | -54.1168 | 68.1976 | -53.5263 | -54.332 | 0.82398 | -8.963 | 68.3945 | -54.007 | 68.4448 | -53.8925 | -54.039 | -53.7689 | -0.20599 | -0.07782 | -0.28381 | 0.38452 | 54.7348 | -0.42114 | 54.9408 | -0.21515 | -0.09613 | -0.086975 | -0.036621 | 0.018311 | 0.14191 | -0.12817 | 0.23804 | -0.032043 | 0.59052 | 122.3145 | 0.11444 | 122.4518 | 122.5204 | 122.4014 | 122.3145 | 122.3053 | -122.5983 | -122.4884 | 122.1085 | 122.3557 | 52.2537 | 44.9478
1707.8281 | 122.5388 | -54.7989 | 67.6071 | -0.07164 | -0.0010787 | 0.061171 | 0.11377 | -0.0019653 | -0.0003632 | 0.0026702 | -0.10101 | -0.0017688 | 0.064179 | 0.063185 | -0.028072 | 0.00034613 | 0.0039521 | -1.7624 | 67.7032 | -54.8721 | 67.1768 | -54.3411 | -54.7302 | 0.78278 | -9.0042 | 67.5476 | -54.8447 | 67.5247 | -54.6799 | -54.9866 | -54.6936 | -0.073242 | 0.09613 | -0.4303 | 0.45776 | 55.5817 | 0.068664 | 55.6549 | 0.14191 | -0.045777 | -0.05951 | -0.082398 | 0.11902 | 0.10529 | -0.18768 | 0.15106 | -0.14191 | 0.53101 | 122.0489 | 0.16479 | 122.3694 | 122.5754 | 122.3923 | 122.5021 | 122.3465 | -122.4792 | -122.4518 | 121.9757 | 122.3236 | 53.0365 | 45.7947
1708.7656 | 122.6166 | -54.8813 | 67.4698 | -0.07164 | -0.00043792 | 0.059676 | 0.11312 | 0.0010253 | -0.0018586 | -0.0013886 | -0.021667 | -0.0045458 | 0.065674 | 0.061263 | -0.025509 | 0.0022687 | 0.0016021 | -1.7944 | 67.5385 | -54.9637 | 67.4377 | -54.4922 | -55.1331 | 0.40741 | -8.9859 | 67.5064 | -54.8401 | 67.5247 | -54.7165 | -54.9637 | -54.7073 | -0.082397 | 0.068664 | -0.032044 | 0.3891 | 55.2887 | -0.25177 | 55.3711 | -0.16937 | 0.041199 | 0.036621 | 0.054931 | 0.16479 | 0.17395 | -0.082397 | 0.13275 | -0.1236 | 0.4715 | 122.4014 | 0.1236 | 122.3648 | 122.5021 | 122.3465 | 122.4197 | 122.3877 | -122.4335 | -122.3099 | 122.319 | 122.406 | 53.0869 | 45.8954
1709.8281 | 122.6395 | -54.4876 | 67.8177 | -0.17082 | 0.0021255 | 0.063094 | 0.11035 | 0.0018799 | -0.0005768 | -0.002243 | -0.00030524 | -0.0034778 | 0.062683 | 0.055495 | -0.027645 | 0.0014141 | -0.0013885 | -1.8677 | 67.7216 | -54.689 | 67.7994 | -54.0024 | -54.7897 | 0.75531 | -8.7021 | 67.7628 | -54.5288 | 67.9184 | -54.2953 | -54.5609 | -54.3137 | -0.20142 | -0.09613 | -0.018311 | 0.48523 | 55.2429 | -0.30212 | 55.4443 | -0.10071 | -0.041199 | -0.054932 | 0.10071 | 0.19226 | 0.17395 | -0.073242 | 0.21515 | -0.032043 | 0.68665 | 122.4884 | 0.23346 | 122.4472 | 122.4106 | 122.2916 | 122.2092 | 122.2504 | -122.5067 | -122.3465 | 122.287 | 122.406 | 52.6199 | 45.7855
1710.7656 | 122.6669 | -54.982 | 67.2958 | -0.094528 | -1.0718e-05 | 0.061385 | 0.1112 | 0.0025207 | 0.000705 | -0.0033112 | 0.097351 | -0.0045458 | 0.063538 | 0.052931 | -0.027218 | -0.0020039 | 0.0024567 | -1.8448 | 67.2684 | -55.1743 | 67.2821 | -54.5517 | -55.2063 | 0.73242 | -8.7158 | 67.2638 | -55.0552 | 67.4057 | -54.7623 | -55.0095 | -54.8126 | -0.19226 | -0.027465 | -0.013733 | 0.4303 | 55.7144 | -0.2243 | 55.9067 | -0.032044 | -0.073242 | -0.032043 | 0.10986 | 0.21973 | 0.16937 | -0.027465 | 0.24262 | 0.045777 | 0.62256 | 122.4564 | 0.29297 | 122.4609 | 122.4426 | 122.319 | 122.2504 | 122.2458 | -122.4701 | -122.3511 | 122.2641 | 122.3877 | 53.1372 | 46.2662
1711.8281 | 122.6257 | -54.8172 | 67.5247 | -0.10216 | 0.00084388 | 0.060957 | 0.11227 | -0.0015381 | -0.0014312 | -0.0033112 | -0.021667 | -0.0041186 | 0.064179 | 0.064253 | -0.027645 | 0.0039777 | -0.0022431 | -1.8723 | 67.4469 | -54.9957 | 67.424 | -54.3869 | -55.0232 | 0.69122 | -8.8165 | 67.4561 | -54.8309 | 67.6025 | -54.6066 | -54.8859 | -54.6066 | -0.17853 | -0.07782 | -0.10071 | 0.4303 | 55.5084 | -0.20599 | 55.687 | -0.027465 | -0.013733 | -0.068664 | 0.07782 | 0.21057 | 0.21057 | -0.068664 | 0.22431 | -0.054931 | 0.60883 | 122.4197 | 0.22431 | 122.4335 | 122.4426 | 122.287 | 122.2641 | 122.2733 | -122.5204 | -122.3557 | 122.2412 | 122.4197 | 52.9449 | 46.0007
1712.7656 | 122.6074 | -54.5334 | 67.7856 | -0.06401 | -0.00065152 | 0.062239 | 0.11248 | -4.2682e-05 | -0.0024994 | -0.00074776 | -0.039978 | -0.0034778 | 0.060974 | 0.061263 | -0.029781 | 0.0026959 | 0.0043793 | -1.8036 | 67.8543 | -54.6433 | 67.7719 | -54.1397 | -54.8538 | 0.59967 | -9.0637 | 67.7444 | -54.6295 | 67.8223 | -54.4052 | -54.6661 | -54.4006 | -0.10986 | 0.068664 | -0.013733 | 0.39368 | 55.1331 | -0.32044 | 55.2429 | -0.21057 | -0.096131 | -0.041199 | 0.036621 | 0.12817 | 0.13275 | -0.13275 | 0.22888 | -0.036621 | 0.50354 | 122.4152 | 0.22431 | 122.4518 | 122.4976 | 122.374 | 122.3877 | 122.2778 | -122.4289 | -122.4152 | 122.3053 | 122.3557 | 52.7298 | 45.4697
1713.8281 | 122.6166 | -54.9179 | 67.4103 | -0.12505 | 0.00020288 | 0.060316 | 0.11291 | 0.0027343 | -0.0035674 | -0.004593 | 0.024109 | -0.001128 | 0.063111 | 0.052718 | -0.027004 | 0.00098693 | -0.00010671 | -2.0416 | 67.3279 | -55.1422 | 67.3004 | -54.5792 | -55.2383 | 0.55847 | -9.2102 | 67.305 | -55.0049 | 67.4332 | -54.7852 | -55.014 | -54.776 | -0.2243 | -0.082397 | -0.10986 | 0.33874 | 55.4764 | -0.32043 | 55.7007 | -0.09613 | -0.086975 | -0.10529 | 0.022889 | 0.13275 | 0.14191 | -0.09613 | 0.22888 | -0.009155 | 0.56305 | 122.4426 | 0.21973 | 122.4381 | 122.4701 | 122.3099 | 122.2458 | 122.2229 | -122.5525 | -122.4152 | 122.2183 | 122.3511 | 52.8763 | 45.7077
1714.7656 | 122.6303 | -54.5883 | 67.7399 | -0.1403 | -0.00086512 | 0.061812 | 0.11334 | -0.00046988 | -0.0007904 | 0.001175 | -0.088806 | -0.0017688 | 0.062683 | 0.067031 | -0.0285 | 0.0018413 | 0.00053409 | -2.0187 | 67.7994 | -54.6753 | 67.7216 | -54.1351 | -54.8492 | 0.58136 | -9.0271 | 67.749 | -54.6204 | 67.7948 | -54.4235 | -54.6982 | -54.4281 | -0.086975 | 0.059509 | -0.01831 | 0.45319 | 55.1697 | -0.26093 | 55.2567 | -0.17395 | -0.032043 | 0.009155 | 0.054932 | 0.16479 | 0.16022 | -0.10986 | 0.19226 | -0.07782 | 0.54016 | 122.3969 | 0.19684 | 122.4152 | 122.4747 | 122.3694 | 122.3877 | 122.3373 | -122.4152 | -122.3602 | 122.3099 | 122.3831 | 52.5696 | 45.5612
1715.8281 | 122.6532 | -54.2908 | 68.0054 | -0.094528 | 0.00084388 | 0.061598 | 0.11377 | 0.0012391 | -0.0033538 | -0.002884 | -0.058289 | -0.0036914 | 0.062042 | 0.064467 | -0.029781 | 0.0022687 | 0.0030975 | -1.9089 | 67.9825 | -54.4785 | 67.9596 | -53.8055 | -54.6158 | 0.74158 | -8.7845 | 67.9459 | -54.364 | 68.1061 | -54.1214 | -54.4006 | -54.1214 | -0.18768 | -0.022888 | -0.045776 | 0.48523 | 55.0323 | -0.32501 | 55.22 | -0.13733 | -0.073243 | -0.059509 | 0.10071 | 0.16937 | 0.16937 | -0.10986 | 0.24262 | -0.036621 | 0.67291 | 122.438 | 0.24262 | 122.4701 | 122.4609 | 122.3099 | 122.2733 | 122.2366 | -122.4838 | -122.3694 | 122.2504 | 122.3969 | 52.3819 | 45.5063
1716.7656 | 122.5388 | -54.6295 | 67.7628 | -0.07164 | -0.00022432 | 0.06053 | 0.11419 | 0.00081172 | -0.0014312 | -0.002884 | -0.091858 | -0.002196 | 0.063751 | 0.06404 | -0.026363 | 0.0031231 | 0.0037385 | -2.0737 | 67.7994 | -54.7302 | 67.662 | -54.1534 | -54.9133 | 0.66834 | -8.5327 | 67.7673 | -54.6661 | 67.7444 | -54.483 | -54.7714 | -54.4922 | -0.10071 | 0.036621 | -0.10071 | 0.47608 | 55.2979 | -0.28381 | 55.3986 | -0.18311 | -0.036621 | 0.004578 | -0.01831 | 0.14648 | 0.13733 | -0.14191 | 0.17395 | -0.10529 | 0.57678 | 122.3923 | 0.18311 | 122.4106 | 122.5296 | 122.4335 | 122.4289 | 122.3969 | -122.493 | -122.4289 | 122.2916 | 122.374 | 52.5558 | 46.0968
1717.8281 | 122.6715 | -54.5197 | 67.7902 | -0.15556 | 0.00041648 | 0.063094 | 0.1159 | 0.0042297 | 0.002414 | -0.0030976 | -0.018616 | -0.003905 | 0.063111 | 0.064467 | -0.028713 | 0.0026959 | 0.0016021 | -1.918 | 67.836 | -54.6112 | 67.9779 | -53.9154 | -54.8538 | 0.70038 | -6.6284 | 67.7444 | -54.57 | 67.8955 | -54.3228 | -54.6066 | -54.332 | -0.091553 | 0.045777 | 0.18768 | 0.60425 | 55.22 | -0.33417 | 55.3116 | -0.24262 | -0.050354 | -0.045776 | 0.10529 | 0.19684 | 0.18768 | -0.086975 | 0.23804 | -0.036621 | 0.6958 | 122.5891 | 0.24719 | 122.4655 | 122.4472 | 122.3145 | 122.3557 | 122.2641 | -122.4014 | -122.3602 | 122.4976 | 122.4152 | 52.6016 | 47.8912
1718.7656 | 122.612 | -54.1992 | 68.1519 | -0.24712 | 0.00084388 | 0.061385 | 0.11569 | 0.0042297 | -0.0007904 | -0.003952 | -0.079651 | -0.0041186 | 0.06482 | 0.064253 | -0.027645 | 0.0024823 | 0.0013885 | -1.9958 | 68.1839 | -54.3228 | 68.0878 | -53.6087 | -54.4876 | 0.83771 | -9.0271 | 68.1381 | -54.2358 | 68.1793 | -54.0344 | -54.3274 | -54.0482 | -0.1236 | 0.032044 | -0.064086 | 0.59051 | 55.0369 | -0.28839 | 55.1605 | -0.16479 | -0.036621 | -0.013732 | 0.027466 | 0.16479 | 0.15106 | -0.12817 | 0.18768 | -0.091553 | 0.71411 | 122.4106 | 0.20142 | 122.4152 | 122.5067 | 122.374 | 122.3831 | 122.3373 | -122.4747 | -122.3877 | 122.287 | 122.3785 | 52.2034 | 45.1721
1719.7656 | 122.6166 | -53.627 | 68.7012 | -0.10979 | 0.0019119 | 0.062025 | 0.11441 | -0.00025628 | -0.0046356 | -0.0020294 | -0.064392 | -0.003905 | 0.063751 | 0.062545 | -0.026577 | 0.0020551 | -0.00074771 | -2.1011 | 68.7332 | -53.7598 | 68.6325 | -52.9999 | -53.9108 | 0.62256 | -5.928 | 68.7149 | -53.6636 | 68.7561 | -53.4485 | -53.8055 | -53.54 | -0.13275 | 0.032043 | -0.068665 | 0.62714 | 54.2496 | -0.28381 | 54.3823 | -0.15106 | -0.036621 | 0.013733 | 0.054932 | 0.17853 | 0.086975 | -0.17853 | 0.1236 | -0.14191 | 0.75989 | 122.3923 | 0.21515 | 122.4197 | 122.493 | 122.3785 | 122.3602 | 122.3419 | -122.4609 | -122.3648 | 122.2595 | 122.3831 | 51.5259 | 47.699
1720.8438 | 122.5204 | -54.4235 | 67.9871 | -0.06401 | -0.00065152 | 0.061171 | 0.11377 | -0.0021789 | -0.0037812 | -0.004593 | -0.0094604 | -0.0051868 | 0.064179 | 0.059127 | -0.02615 | -0.0020039 | 0.00074769 | -2.1927 | 68.0237 | -54.4785 | 67.8223 | -53.9017 | -54.7302 | 0.64087 | -8.1985 | 67.923 | -54.4647 | 68.0603 | -54.2358 | -54.8767 | -54.5242 | -0.054932 | 0.036621 | -0.16479 | 0.52185 | 55.0644 | -0.3067 | 55.1193 | -0.25177 | -0.041199 | -0.064087 | 0.073242 | 0.18768 | -0.10071 | -0.45319 | -0.059509 | -0.41199 | 0.57678 | 122.3007 | 0.22888 | 122.525 | 122.5021 | 122.3877 | 122.4472 | 122.3465 | -122.4655 | -122.4518 | 122.2458 | 122.4838 | 52.2308 | 46.225
1721.7656 | 122.6212 | -54.2725 | 68.0695 | -0.07164 | -0.0012923 | 0.061171 | 0.11419 | 0.00081172 | -0.0014312 | -0.001175 | -0.06134 | -0.0026232 | 0.063965 | 0.061263 | -0.026791 | 0.0022687 | 0.0030975 | -2.1973 | 68.0557 | -54.4464 | 67.9321 | -53.7003 | -54.6387 | 0.80566 | -6.5414 | 68.0191 | -54.3594 | 68.0878 | -54.1122 | -54.4006 | -54.1443 | -0.17395 | -0.013733 | -0.13733 | 0.5722 | 55.0781 | -0.36621 | 55.2521 | -0.19226 | -0.086975 | -0.050354 | 0.018311 | 0.16022 | 0.12817 | -0.12817 | 0.21515 | -0.041199 | 0.74615 | 122.3785 | 0.24719 | 122.4472 | 122.5021 | 122.3785 | 122.3282 | 122.2916 | -122.5159 | -122.4289 | 122.2046 | 122.3602 | 52.0752 | 47.731
1722.8281 | 122.5433 | -53.6041 | 68.7927 | -0.06401 | 0.00020288 | 0.062025 | 0.11419 | 0.0020935 | -0.0048492 | -0.00074776 | -0.085754 | -0.0030506 | 0.060974 | 0.060836 | -0.027218 | 0.00055973 | 0.0028839 | -1.9547 | 68.5501 | -53.9337 | 68.5272 | -53.1372 | -54.0573 | 0.96588 | -6.2805 | 68.6325 | -53.7231 | 68.7607 | -53.4439 | -53.7552 | -53.5172 | -0.32959 | -0.24262 | -0.2655 | 0.46692 | 54.57 | -0.45319 | 54.8996 | -0.1236 | -0.11902 | -0.16022 | -0.032044 | 0.16022 | 0.086975 | -0.15106 | 0.20599 | -0.032043 | 0.79651 | 122.4609 | 0.27924 | 122.4838 | 122.4838 | 122.3557 | 122.1542 | 122.2366 | -122.7264 | -122.5159 | 122.1313 | 122.3648 | 51.6495 | 47.3236
1723.7656 | 122.6624 | -53.6316 | 68.6737 | -0.11742 | -1.0718e-05 | 0.061385 | 0.11291 | 0.00059812 | -0.0050628 | -0.00032036 | -0.033874 | -0.0041186 | 0.061402 | 0.062758 | -0.024441 | -8.1274e-05 | 0.0013885 | -2.0096 | 68.5547 | -53.9246 | 68.5364 | -53.1967 | -54.0115 | 0.83313 | -5.8044 | 68.5364 | -53.7552 | 68.7515 | -53.4302 | -53.7598 | -53.4531 | -0.29297 | -0.11902 | -0.13733 | 0.43488 | 54.4647 | -0.37994 | 54.7577 | -0.086975 | -0.1236 | -0.13733 | 0.07782 | 0.20142 | 0.17853 | -0.12817 | 0.30212 | -0.004578 | 0.72784 | 122.4609 | 0.32501 | 122.5067 | 122.4792 | 122.2916 | 122.1863 | 122.168 | -122.5983 | -122.4289 | 122.168 | 122.3831 | 51.622 | 47.8271
1724.8281 | 122.7173 | -53.9383 | 68.3807 | -0.11742 | 0.00084388 | 0.062453 | 0.11291 | -0.00025628 | -0.0007904 | -0.0026704 | -0.067444 | -0.0051868 | 0.06247 | 0.061263 | -0.0285 | 0.0014141 | -0.00010671 | -2.0462 | 68.2938 | -54.1443 | 68.2846 | -53.302 | -54.2542 | 0.86517 | -8.9264 | 68.2983 | -53.9978 | 68.5959 | -53.8284 | -54.1946 | -53.7552 | -0.20599 | -0.086975 | -0.09613 | 0.63629 | 54.8035 | -0.31586 | 55.0095 | -0.10986 | -0.05951 | -0.082397 | 0.21515 | 0.10986 | 0.18311 | -0.25635 | 0.24262 | -0.19684 | 0.84228 | 122.4289 | 0.16937 | 122.5937 | 122.438 | 122.2961 | 122.2321 | 122.2366 | -122.525 | -122.3785 | 122.2229 | 122.5342 | 51.8921 | 45.0119
1725.7656 | 122.58 | -53.0411 | 69.2413 | -0.048752 | 0.00020288 | 0.06053 | 0.11483 | -0.00046988 | -0.0020722 | -0.0050202 | 0.057678 | -0.0036914 | 0.063751 | 0.05699 | -0.026791 | 0.0012005 | 0.0048065 | -1.9363 | 69.2413 | -53.215 | 69.278 | -52.2217 | -53.215 | 1.181 | -6.7932 | 69.2047 | -53.1097 | 69.3466 | -52.8442 | -52.7206 | -52.6016 | -0.17395 | 0 | 0.036621 | 0.8194 | 54.2221 | -0.17395 | 54.3961 | 0 | -0.068664 | -0.036621 | 0.10529 | 0.19684 | 0.43945 | 0.32044 | 0.50812 | 0.3891 | 0.99335 | 122.493 | 0.2655 | 122.4564 | 122.4564 | 122.3145 | 122.2824 | 122.2458 | -122.4564 | -122.3511 | 122.319 | 122.3877 | 51.1047 | 46.2479
1726.8281 | 122.6669 | -53.4302 | 68.8797 | -0.10979 | 0.00084388 | 0.060103 | 0.11248 | 0.0029479 | -0.002713 | -0.002884 | -0.052185 | -0.0028368 | 0.063324 | 0.061049 | -0.026363 | 0.00098693 | -0.0011749 | -2.1378 | 68.898 | -53.5858 | 68.8248 | -52.8305 | -53.7735 | 0.80109 | -6.7978 | 68.8065 | -53.5172 | 68.9484 | -53.2425 | -53.5172 | -53.2516 | -0.15564 | 0.01831 | -0.054932 | 0.59967 | 54.2313 | -0.34332 | 54.3869 | -0.18768 | -0.086975 | -0.073242 | 0.068664 | 0.18768 | 0.17853 | -0.086975 | 0.2655 | 0 | 0.75531 | 122.4106 | 0.27466 | 122.4655 | 122.4838 | 122.3236 | 122.3282 | 122.2366 | -122.4655 | -122.3969 | 122.2549 | 122.3785 | 51.2924 | 46.6324
1727.7656 | 122.5891 | -53.5858 | 68.7378 | -0.1403 | 0.0029801 | 0.063307 | 0.11184 | 0.00038452 | -0.0001496 | -0.005661 | 0.0027466 | -0.0034778 | 0.063111 | 0.064467 | -0.027645 | 0.00098693 | 0.0052337 | -2.243 | 68.7149 | -53.7415 | 68.6966 | -52.858 | -53.8971 | 0.75989 | -6.2302 | 68.6646 | -53.6636 | 68.7836 | -53.3844 | -53.6957 | -53.4439 | -0.15564 | -0.022888 | -0.041199 | 0.72784 | 54.3457 | -0.31128 | 54.5013 | -0.15564 | -0.07782 | -0.073242 | 0.045776 | 0.20142 | 0.14191 | -0.10986 | 0.21973 | -0.032044 | 0.88348 | 122.438 | 0.27924 | 122.4472 | 122.4564 | 122.3282 | 122.3007 | 122.2504 | -122.4792 | -122.4014 | 122.2824 | 122.3694 | 51.3428 | 47.3557
1728.8281 | 122.6166 | -54.0207 | 68.3166 | -0.10216 | -0.0025741 | 0.060957 | 0.11163 | 0.0029479 | -0.0039948 | -0.0030976 | -0.082703 | -0.003905 | 0.064179 | 0.067244 | -0.027218 | 0.0031231 | 0.00053409 | -2.3026 | 68.2846 | -54.2358 | 68.2434 | -53.1555 | -54.3411 | 0.83771 | -6.0471 | 68.2755 | -54.0985 | 68.3578 | -53.8147 | -54.1077 | -53.8422 | -0.21515 | -0.032043 | -0.073242 | 0.86517 | 54.8584 | -0.32043 | 55.0735 | -0.10528 | -0.07782 | -0.041198 | 0.041199 | 0.20599 | 0.17853 | -0.086975 | 0.25635 | -0.009155 | 1.0803 | 122.4792 | 0.28381 | 122.4564 | 122.5204 | 122.374 | 122.3053 | 122.2961 | -122.5525 | -122.4152 | 122.2641 | 122.3785 | 51.7181 | 47.9736
1729.7656 | 122.5891 | -54.126 | 68.2526 | -0.094528 | -0.0012923 | 0.060103 | 0.11419 | 0.00017092 | -0.0014312 | -0.0018158 | -0.088806 | -0.0015552 | 0.062683 | 0.064681 | -0.026577 | 0.0024823 | 0.00032049 | -2.3254 | 68.2617 | -54.2725 | 68.129 | -53.3981 | -54.4235 | 0.77362 | -6.9077 | 68.1656 | -54.213 | 68.2709 | -53.952 | -54.245 | -53.9841 | -0.14648 | 0.009156 | -0.1236 | 0.72785 | 54.8996 | -0.29755 | 55.0461 | -0.15106 | -0.086975 | -0.086975 | 0.018311 | 0.17395 | 0.14191 | -0.11902 | 0.22888 | -0.032043 | 0.87433 | 122.4014 | 0.26093 | 122.4838 | 122.5342 | 122.3785 | 122.3877 | 122.2916 | -122.525 | -122.4655 | 122.2549 | 122.3969 | 51.8005 | 47.2183
1730.8438 | 122.5388 | -53.1601 | 69.2413 | -0.17845 | 0.0021255 | 0.062239 | 0.11227 | -0.0013245 | 0.000705 | -0.0024566 | -0.046081 | -0.0013416 | 0.065888 | 0.05699 | -0.027645 | 0.0041913 | -0.00010671 | -2.1378 | 69.2688 | -53.2745 | 69.0948 | -52.2629 | -53.421 | 1.0345 | -5.1407 | 69.2001 | -53.1784 | 69.2047 | -52.977 | -53.2928 | -53.0502 | -0.11444 | 0.027466 | -0.14648 | 0.89722 | 54.1946 | -0.26093 | 54.3091 | -0.14649 | -0.018311 | -0.041199 | -0.036621 | 0.1831 | 0.10986 | -0.13275 | 0.12817 | -0.11444 | 1.0117 | 122.3694 | 0.20142 | 122.3831 | 122.5433 | 122.3785 | 122.4289 | 122.3602 | -122.5159 | -122.4197 | 122.2549 | 122.3648 | 51.0223 | 48.0194
1731.7656 | 122.6212 | -53.2883 | 69.0491 | -0.14793 | -0.00086512 | 0.062025 | 0.1112 | 0.00059812 | -0.0022858 | -0.0024566 | 0.0027466 | -0.0030506 | 0.06546 | 0.060195 | -0.028072 | 0.00077333 | 0.0030975 | -2.2476 | 68.9667 | -53.4576 | 69.017 | -52.3315 | -53.54 | 1.0941 | -5.0903 | 68.9667 | -53.3615 | 69.072 | -53.1097 | -53.3981 | -53.1509 | -0.16937 | -0.082397 | -0.032043 | 0.95673 | 54.3823 | -0.25177 | 54.5517 | -0.082397 | -0.073242 | -0.082397 | 0.022888 | 0.17853 | 0.13733 | -0.10986 | 0.21057 | -0.036621 | 1.1261 | 122.4747 | 0.25177 | 122.4335 | 122.4243 | 122.3282 | 122.2549 | 122.2549 | -122.5067 | -122.4106 | 122.3053 | 122.3602 | 51.0406 | 48.1979
1732.8281 | 122.6212 | -54.2587 | 68.0878 | -0.18608 | 0.0027665 | 0.061812 | 0.11441 | 0.0010253 | -0.0042084 | -0.0020294 | -0.018616 | -0.0032642 | 0.065888 | 0.062117 | -0.027431 | -8.1274e-05 | 0.0035247 | -2.3254 | 68.0786 | -54.3777 | 68.042 | -53.3203 | -54.4922 | 0.87433 | -4.3442 | 67.9916 | -54.3137 | 68.1152 | -54.0665 | -54.3594 | -54.1031 | -0.11902 | -0.009156 | -0.045777 | 0.93842 | 55.1331 | -0.23346 | 55.2521 | -0.11444 | -0.054932 | -0.096131 | 0.027465 | 0.19226 | 0.15564 | -0.10071 | 0.21057 | -0.045776 | 1.0574 | 122.4197 | 0.24719 | 122.4289 | 122.4564 | 122.3053 | 122.3373 | 122.2504 | -122.4655 | -122.4014 | 122.3007 | 122.374 | 51.9333 | 49.9146
1733.7656 | 122.6669 | -54.2313 | 68.1061 | -0.1403 | 0.00084388 | 0.062666 | 0.11419 | -0.00025628 | -0.0016448 | -0.0018158 | -0.06134 | -0.0030506 | 0.063111 | 0.056136 | -0.026363 | 0.0029095 | 0.00010689 | -2.2842 | 68.1793 | -54.2953 | 68.1015 | -53.0869 | -54.5334 | 0.81482 | -4.1473 | 68.1198 | -54.2313 | 68.1793 | -54.039 | -54.3365 | -54.0665 | -0.064087 | 0.073242 | -0.004578 | 1.1444 | 55.0461 | -0.30212 | 55.1102 | -0.23804 | 0 | 0.013733 | 0.073242 | 0.19226 | 0.16479 | -0.10529 | 0.16479 | -0.10529 | 1.2085 | 122.3969 | 0.19226 | 122.4106 | 122.4747 | 122.3511 | 122.4106 | 122.3511 | -122.4014 | -122.3373 | 122.3328 | 122.4106 | 51.947 | 50.0839
1734.8281 | 122.6349 | -53.714 | 68.6234 | -0.10216 | 0.00084388 | 0.060957 | 0.11312 | -4.2682e-05 | -0.0031402 | -0.0013886 | -0.030823 | -0.0047594 | 0.062256 | 0.055281 | -0.025295 | -0.00029487 | -0.0030975 | -2.5085 | 68.7973 | -53.6545 | 68.6508 | -52.684 | -53.9108 | 0.51727 | -4.2572 | 68.6188 | -53.7277 | 68.7241 | -53.4668 | -53.7964 | -53.5355 | 0.059509 | 0.17395 | 0.027466 | 1.03 | 54.2313 | -0.19684 | 54.1718 | -0.25635 | -0.013733 | -0.004578 | 0.10071 | 0.24719 | 0.17853 | -0.082398 | 0.19226 | -0.068665 | 0.97046 | 122.3053 | 0.26093 | 122.4518 | 122.4518 | 122.3465 | 122.5113 | 122.3328 | -122.2778 | -122.3511 | 122.3648 | 122.438 | 51.2054 | 49.4568
1735.7656 | 122.644 | -54.6524 | 67.6895 | -0.07164 | -1.0718e-05 | 0.06053 | 0.11441 | 0.0016663 | -0.0014312 | -0.00032036 | -0.088806 | -0.002196 | 0.060547 | 0.059981 | -0.026791 | 0.00034613 | 0.0013885 | -2.6459 | 67.6712 | -54.8447 | 67.5522 | -54.0298 | -55.0278 | 0.61798 | -4.715 | 67.6254 | -54.744 | 67.7399 | -54.4647 | -54.7073 | -54.4922 | -0.19226 | -0.01831 | -0.13733 | 0.62256 | 55.2704 | -0.37537 | 55.4626 | -0.18311 | -0.091553 | -0.064087 | 0.050354 | 0.18768 | 0.16022 | -0.054931 | 0.25177 | 0.036622 | 0.81482 | 122.3969 | 0.27924 | 122.4838 | 122.5159 | 122.3694 | 122.3236 | 122.2778 | -122.5342 | -122.4335 | 122.2046 | 122.3923 | 52.0065 | 49.9374
1736.8281 | 122.6532 | -54.0619 | 68.2388 | -0.17082 | 0.0014847 | 0.063094 | 0.11248 | -0.00068368 | -0.0031402 | -0.00010676 | -0.036926 | -0.003905 | 0.062683 | 0.059767 | -0.027004 | 0.0029095 | 0.0016021 | -2.5223 | 68.2068 | -54.213 | 68.28 | -53.1464 | -54.2999 | 0.54016 | -4.6371 | 68.2251 | -54.126 | 68.3441 | -53.8101 | -54.1672 | -53.8834 | -0.15106 | -0.032044 | 0.041198 | 0.91553 | 54.6021 | -0.23804 | 54.7531 | -0.086975 | -0.064087 | -0.013733 | 0.10528 | 0.25177 | 0.17853 | -0.10529 | 0.24262 | -0.041198 | 1.0666 | 122.493 | 0.31586 | 122.4701 | 122.4197 | 122.3511 | 122.2687 | 122.287 | -122.4518 | -122.3648 | 122.3419 | 122.406 | 51.5396 | 49.4247
1737.7656 | 122.612 | -55.1743 | 67.1997 | -0.10216 | 0.00041648 | 0.063094 | 0.11483 | 0.0027343 | -0.002713 | -0.00032036 | -0.10101 | -0.003905 | 0.065033 | 0.058058 | -0.028072 | 0.0016277 | 0.00096129 | -2.9434 | 67.1997 | -55.3162 | 67.1173 | -54.538 | -55.4352 | 0.2243 | -5.2185 | 67.186 | -55.1926 | 67.1906 | -54.9042 | -55.3024 | -55.014 | -0.14191 | 0 | -0.082397 | 0.63629 | 55.3986 | -0.26093 | 55.5405 | -0.11902 | -0.018311 | -0.013733 | -0.009155 | 0.27008 | 0.16022 | -0.12817 | 0.17853 | -0.10986 | 0.7782 | 122.4335 | 0.28839 | 122.3831 | 122.5159 | 122.3785 | 122.374 | 122.3602 | -122.5159 | -122.3923 | 122.2916 | 122.3648 | 52.2308 | 49.9557
1738.8281 | 122.644 | -54.5883 | 67.7261 | -0.094528 | -0.00086512 | 0.06053 | 0.11184 | 0.0023071 | -0.0016448 | -0.00010676 | -0.018616 | -0.0030506 | 0.06012 | 0.063826 | -0.027004 | 0.00013253 | 0.0030975 | -2.9251 | 67.7628 | -54.6982 | 67.7353 | -53.6087 | -54.8264 | 0.31128 | -5.0583 | 67.7216 | -54.6158 | 67.7765 | -54.2999 | -54.6799 | -54.4693 | -0.10986 | 0.036621 | 0.009156 | 0.97961 | 54.8996 | -0.23804 | 55.0095 | -0.12817 | -0.027466 | -0.004577 | 0.050354 | 0.28839 | 0.11902 | -0.091553 | 0.14648 | -0.064087 | 1.0895 | 122.4335 | 0.31586 | 122.3923 | 122.4609 | 122.3373 | 122.3511 | 122.3099 | -122.4243 | -122.3419 | 122.3236 | 122.3648 | 51.6632 | 49.53
1739.7656 | 122.612 | -55.0095 | 67.2592 | -0.17845 | -1.0718e-05 | 0.061385 | 0.11099 | -0.0019653 | 0.0002778 | -0.0026704 | -0.079651 | -0.0034778 | 0.065674 | 0.062545 | -0.027218 | 0.0029095 | 0.0011749 | -2.9251 | 67.2867 | -55.1971 | 67.3141 | -54.2725 | -55.22 | 0.21515 | -4.5181 | 67.2867 | -55.0552 | 67.4103 | -54.6707 | -55.069 | -54.8264 | -0.18768 | 0.027466 | 0.054932 | 0.737 | 55.2246 | -0.21057 | 55.4123 | -0.022888 | -0.045777 | 0.027466 | 0.15106 | 0.33874 | 0.1831 | -0.05951 | 0.22888 | -0.013733 | 0.92468 | 122.5113 | 0.38452 | 122.4655 | 122.4838 | 122.3419 | 122.2961 | 122.2961 | -122.4564 | -122.3145 | 122.3236 | 122.4197 | 52.0844 | 50.4913
1740.8281 | 122.3465 | -55.3207 | 66.9846 | -0.06401 | 0.0014847 | 0.060957 | 0.11398 | 0.0025207 | -0.0016448 | 0.00010684 | -0.11932 | -0.0043322 | 0.061402 | 0.062758 | -0.025936 | 0.0035503 | -0.0020295 | -3.0853 | 67.4561 | -55.0644 | 67.3279 | -54.2175 | -55.2429 | 0.004578 | -5.4382 | 67.4423 | -54.9911 | 67.1356 | -55.0095 | -55.5725 | -55.2887 | 0.25635 | 0.4715 | 0.34332 | 1.1032 | 55.3253 | 0.07782 | 55.069 | -0.17853 | 0.32959 | 0.45776 | 0.15106 | 0.31128 | 0.032044 | -0.25177 | -0.29755 | -0.58136 | 0.84686 | 122.3923 | -0.01831 | 122.1268 | 122.5204 | 122.4335 | 122.7768 | 122.7631 | -122.049 | -121.9757 | 122.6486 | 122.4564 | 52.2354 | 49.8825
1741.7656 | 122.6669 | -55.101 | 67.2226 | -0.086899 | 0.0031937 | 0.063307 | 0.11248 | 0.0014527 | -0.0014312 | -0.00053396 | -0.049133 | -0.0041186 | 0.065247 | 0.058699 | -0.025722 | 0.0014141 | -0.0022431 | -3.3325 | 67.1585 | -55.2429 | 67.2775 | -54.4327 | -55.3024 | -0.21515 | -5.2597 | 67.2089 | -55.0919 | 67.3462 | -54.7714 | -55.1743 | -54.95 | -0.14191 | -0.064087 | 0.054932 | 0.66833 | 54.8859 | -0.20142 | 55.0278 | -0.059509 | 0.009155 | -0.013733 | 0.1236 | 0.32959 | 0.15106 | -0.073242 | 0.14191 | -0.082397 | 0.81024 | 122.5204 | 0.32044 | 122.438 | 122.4014 | 122.3007 | 122.2595 | 122.3099 | -122.4655 | -122.3145 | 122.3785 | 122.4472 | 51.7685 | 49.8413
1742.8281 | 122.7127 | -54.2679 | 68.0923 | -0.12505 | 0.00063028 | 0.061812 | 0.11377 | -0.0013245 | -0.0018586 | -0.0013886 | -0.055237 | -0.0026232 | 0.063538 | 0.059767 | -0.026363 | 0.0033367 | 0.00053409 | -2.9846 | 68.0603 | -54.4006 | 68.0603 | -53.2837 | -54.5471 | 0.24261 | -4.7516 | 68.0191 | -54.3091 | 68.1931 | -53.8193 | -54.5746 | -54.1718 | -0.13275 | -0.032043 | -0.032043 | 0.98419 | 54.5105 | -0.27924 | 54.6433 | -0.14648 | -0.041199 | -0.073242 | 0.10071 | 0.44861 | 0.09613 | -0.3067 | 0.13733 | -0.2655 | 1.1169 | 122.4609 | 0.48981 | 122.5021 | 122.4609 | 122.3282 | 122.3282 | 122.287 | -122.493 | -122.4014 | 122.3282 | 122.4609 | 51.2833 | 49.5163
1743.7656 | 122.6349 | -54.5013 | 67.8314 | -0.13267 | -0.00065152 | 0.060744 | 0.11099 | -0.0013245 | -0.0018586 | -0.0037384 | -0.012512 | -0.0024096 | 0.063751 | 0.055922 | -0.025936 | 0.0018413 | 0.0011749 | -3.1219 | 67.836 | -54.5975 | 67.7902 | -53.9108 | -54.7531 | 0.16937 | -4.9942 | 67.8314 | -54.5563 | 67.8772 | -54.1809 | -54.6158 | -54.3457 | -0.09613 | 0.004578 | -0.041199 | 0.59051 | 54.6707 | -0.25177 | 54.7668 | -0.15564 | -0.054931 | 0 | 0.045776 | 0.32043 | 0.15564 | -0.11444 | 0.21057 | -0.05951 | 0.68664 | 122.3877 | 0.37537 | 122.4335 | 122.4335 | 122.3877 | 122.3373 | 122.3328 | -122.4289 | -122.3877 | 122.2916 | 122.3785 | 51.3794 | 49.5071
1744.8281 | 122.6669 | -54.0894 | 68.2159 | -0.094528 | -0.00043792 | 0.062453 | 0.11377 | 0.0018799 | -0.0012176 | -0.001175 | -0.076599 | -0.0030506 | 0.065674 | 0.072158 | -0.026577 | 0.0014141 | -0.0018157 | -3.0991 | 68.2297 | -54.2725 | 68.2022 | -53.4897 | -54.4006 | 0.24261 | -4.747 | 68.1839 | -54.1672 | 68.3212 | -53.7323 | -54.1626 | -53.9154 | -0.18311 | 0.013733 | -0.013733 | 0.59967 | 54.332 | -0.31128 | 54.5151 | -0.12817 | -0.07782 | -0.032043 | 0.10529 | 0.35705 | 0.17395 | -0.073243 | 0.25177 | 0.004577 | 0.78278 | 122.4747 | 0.43487 | 122.4884 | 122.5021 | 122.3511 | 122.319 | 122.2733 | -122.4884 | -122.3831 | 122.2916 | 122.4106 | 50.9903 | 49.3423
1745.7656 | 122.6074 | -53.6865 | 68.6325 | -0.10216 | 0.0010575 | 0.060103 | 0.1127 | -0.00068368 | -0.0018586 | -0.003952 | -0.04303 | -0.0036914 | 0.063751 | 0.059127 | -0.026791 | 0.00034613 | -0.00053411 | -2.8702 | 68.5455 | -53.8605 | 68.5822 | -53.0731 | -53.9932 | 0.54016 | -5.1407 | 68.5684 | -53.801 | 68.6829 | -53.27 | -53.7552 | -53.5355 | -0.17395 | -0.086975 | -0.050354 | 0.6134 | 54.2267 | -0.3067 | 54.4006 | -0.13275 | -0.11444 | -0.064087 | 0.050354 | 0.41656 | 0.15106 | -0.068665 | 0.2655 | 0.045776 | 0.78735 | 122.4426 | 0.53101 | 122.4838 | 122.406 | 122.3694 | 122.2321 | 122.2549 | -122.493 | -122.4335 | 122.2687 | 122.3694 | 50.8163 | 48.5458
1746.8281 | 122.5983 | -54.1718 | 68.2068 | -0.10979 | 0.0012711 | 0.062666 | 0.11312 | -4.2682e-05 | -0.0042084 | -0.0013886 | -0.018616 | -0.0043322 | 0.065674 | 0.057204 | -0.027859 | -0.00072207 | -0.00096131 | -2.916 | 68.1656 | -54.3228 | 68.0603 | -53.6728 | -54.4922 | 0.55389 | -5.3329 | 68.074 | -54.245 | 68.1885 | -53.7689 | -54.2587 | -54.0253 | -0.15106 | -0.041199 | -0.14648 | 0.49896 | 54.7256 | -0.32043 | 54.8767 | -0.16937 | -0.073242 | -0.13275 | -0.01831 | 0.40283 | 0.14648 | -0.086975 | 0.21973 | -0.013733 | 0.65002 | 122.3831 | 0.47607 | 122.4335 | 122.4884 | 122.319 | 122.3373 | 122.2458 | -122.5296 | -122.4518 | 122.2321 | 122.3602 | 51.2558 | 48.8388
1747.7656 | 122.644 | -54.2542 | 68.0695 | -0.094528 | -0.00065152 | 0.061171 | 0.11419 | 0.0010253 | -0.0012176 | -0.00074776 | -0.097961 | -0.0028368 | 0.06546 | 0.062545 | -0.027431 | 0.0033367 | 0.0013885 | -3.1082 | 68.0008 | -54.4601 | 68.0511 | -53.8101 | -54.5334 | 0.32501 | -4.7836 | 67.9733 | -54.4006 | 68.129 | -53.7048 | -54.364 | -54.0802 | -0.20599 | -0.068665 | -0.018311 | 0.44403 | 54.5792 | -0.27924 | 54.7852 | -0.073242 | -0.14648 | -0.09613 | 0.059509 | 0.54932 | 0.17395 | -0.10986 | 0.32044 | 0.036621 | 0.65002 | 122.5113 | 0.6958 | 122.5296 | 122.4609 | 122.374 | 122.2549 | 122.2275 | -122.5296 | -122.4701 | 122.3053 | 122.3831 | 51.1459 | 49.4705
1748.8281 | 122.6807 | -53.952 | 68.3395 | -0.15556 | 0.0019119 | 0.060316 | 0.11312 | -0.00089728 | 0.0004914 | -0.00053396 | -0.091858 | -0.0047594 | 0.061615 | 0.056777 | -0.026577 | 0.0031231 | 0.0030975 | -2.8702 | 68.2571 | -54.158 | 68.2297 | -53.421 | -53.9703 | 0.48981 | -4.3762 | 68.2892 | -54.0527 | 68.4357 | -53.4348 | -54.0619 | -53.7872 | -0.20599 | -0.082398 | -0.10986 | 0.531 | 54.4418 | -0.018311 | 54.6478 | 0.18768 | -0.10071 | -0.050354 | 0.09613 | 0.51727 | 0.16479 | -0.10986 | 0.2655 | -0.009156 | 0.737 | 122.3877 | 0.61798 | 122.4884 | 122.4152 | 122.3419 | 122.2092 | 122.2412 | -122.4976 | -122.3923 | 122.1817 | 122.3877 | 51.0818 | 49.5758
1749.7656 | 122.6166 | -54.3503 | 67.9871 | -0.10979 | 0.00041648 | 0.058607 | 0.11355 | -0.00025628 | -0.0031402 | -0.0013886 | 0.0057984 | -0.002196 | 0.06247 | 0.059127 | -0.026577 | 0.00013253 | 0.00096129 | -2.7924 | 67.9504 | -54.5151 | 67.8864 | -53.9246 | -54.6661 | 0.58594 | -4.8203 | 67.9321 | -54.4189 | 67.9825 | -53.8971 | -54.4464 | -54.2038 | -0.16479 | -0.036622 | -0.10071 | 0.42572 | 54.9362 | -0.31586 | 55.101 | -0.15106 | -0.068664 | -0.054932 | -0.004578 | 0.45319 | 0.14649 | -0.09613 | 0.21515 | -0.027466 | 0.59052 | 122.4014 | 0.52185 | 122.4014 | 122.4655 | 122.3511 | 122.3007 | 122.2824 | -122.5021 | -122.406 | 122.2366 | 122.3328 | 51.5579 | 49.53
1750.8281 | 122.5204 | -53.7323 | 68.6874 | -0.17845 | 0.00084388 | 0.062666 | 0.11441 | 0.0029479 | -0.0033538 | -0.0013886 | -0.14069 | -0.0041186 | 0.063111 | 0.061904 | -0.026791 | 0.00077333 | 0.0071563 | -2.7557 | 68.6234 | -53.8879 | 68.4906 | -53.3432 | -54.1122 | 0.65918 | -4.8157 | 68.6371 | -53.7781 | 68.6691 | -53.302 | -53.833 | -53.6041 | -0.15564 | -0.064087 | -0.19684 | 0.3891 | 54.3915 | -0.37994 | 54.5471 | -0.2243 | -0.045776 | -0.050354 | -0.018311 | 0.4303 | 0.12817 | -0.10071 | 0.17395 | -0.054932 | 0.54474 | 122.3785 | 0.47607 | 122.4472 | 122.5113 | 122.4152 | 122.3557 | 122.3694 | -122.5754 | -122.4655 | 122.2229 | 122.4014 | 50.9766 | 48.9166
1751.7656 | 122.6669 | -53.4119 | 68.9163 | -0.13267 | 0.0034073 | 0.060957 | 0.11248 | 0.0010253 | -0.0014312 | -0.002884 | -0.082703 | -0.0032642 | 0.062256 | 0.065962 | -0.027218 | 0.0022687 | -0.0028839 | -2.8244 | 68.8751 | -53.5767 | 68.8339 | -52.8717 | -53.7094 | 0.84686 | -5.8868 | 68.866 | -53.4897 | 69.0262 | -52.9358 | -53.4805 | -53.2196 | -0.16479 | -0.041199 | -0.082398 | 0.54016 | 54.2587 | -0.29755 | 54.4235 | -0.13275 | -0.07782 | -0.050354 | 0.10986 | 0.47607 | 0.19226 | -0.068665 | 0.27008 | 0.009155 | 0.70496 | 122.4106 | 0.55389 | 122.5159 | 122.4518 | 122.3557 | 122.287 | 122.2778 | -122.493 | -122.406 | 122.2458 | 122.438 | 50.5875 | 47.525
1752.8438 | 122.5616 | -53.0182 | 69.3832 | -0.06401 | 0.0016983 | 0.060744 | 0.1112 | 0.0035889 | 0.000705 | -0.00032036 | -0.06134 | -0.0034778 | 0.064392 | 0.05934 | -0.024654 | 0.00055973 | 0.00010689 | -2.9388 | 69.3924 | -53.1372 | 69.1223 | -52.1896 | -53.27 | 0.63629 | -4.8752 | 69.3649 | -53.064 | 69.3008 | -52.597 | -53.1876 | -52.9449 | -0.11902 | 0.009155 | -0.26093 | 0.82855 | 53.6545 | -0.25177 | 53.7735 | -0.13275 | -0.045777 | -0.018311 | -0.082398 | 0.42114 | 0.073242 | -0.16937 | 0.11902 | -0.1236 | 0.94757 | 122.2595 | 0.46692 | 122.3648 | 122.5296 | 122.4289 | 122.4106 | 122.3831 | -122.5204 | -122.4472 | 122.1405 | 122.319 | 50.0793 | 48.143
1753.7656 | 122.6303 | -53.2013 | 69.1315 | -0.13267 | 0.0023391 | 0.061812 | 0.11526 | 0.00081172 | -0.0033538 | 0.0016022 | -0.082703 | -0.0024096 | 0.061615 | 0.062117 | -0.027859 | 0.00098693 | -0.00096131 | -2.8198 | 69.0537 | -53.389 | 69.0765 | -52.5421 | -53.3478 | 0.737 | -4.6738 | 69.0445 | -53.2562 | 69.2322 | -52.7573 | -53.2471 | -53.0273 | -0.18768 | -0.07782 | -0.054932 | 0.65918 | 53.9383 | -0.14648 | 54.126 | 0.041199 | -0.054932 | -0.086975 | 0.10071 | 0.44403 | 0.17395 | -0.045776 | 0.22888 | 0.009156 | 0.84686 | 122.4655 | 0.49896 | 122.4884 | 122.4426 | 122.3007 | 122.2549 | 122.2458 | -122.5204 | -122.3877 | 122.2778 | 122.4335 | 50.3815 | 48.5275
1754.8281 | 122.6669 | -53.7186 | 68.573 | -0.14793 | -0.0012923 | 0.063521 | 0.11013 | 0.00059812 | -0.0037812 | -0.0016022 | -0.030823 | -0.0054004 | 0.063751 | 0.059554 | -0.028072 | 0.0016277 | 0.00074769 | -2.9343 | 68.4814 | -53.952 | 68.5318 | -52.9587 | -54.0894 | 0.58136 | -4.9301 | 68.4723 | -53.8376 | 68.692 | -53.3295 | -53.801 | -53.5675 | -0.23346 | -0.091553 | -0.041199 | 0.75989 | 54.2999 | -0.37079 | 54.5334 | -0.13733 | -0.11902 | -0.10071 | 0.11902 | 0.3891 | 0.15106 | -0.082397 | 0.27008 | 0.036621 | 0.99335 | 122.4838 | 0.50812 | 122.5296 | 122.4335 | 122.3099 | 122.2 | 122.1909 | -122.525 | -122.4106 | 122.2504 | 122.4106 | 50.7843 | 48.7885
1755.7656 | 122.6257 | -53.4439 | 68.9117 | -0.07164 | 0.0019119 | 0.059889 | 0.11334 | -0.0038879 | -0.0020722 | 0.00074764 | 0.0057984 | -0.0034778 | 0.064392 | 0.054213 | -0.028286 | 0.00013253 | 0.0052337 | -3.2318 | 68.7515 | -53.7323 | 68.7469 | -52.6932 | -53.8467 | 0.14648 | -6.1249 | 68.7881 | -53.5446 | 68.9209 | -53.064 | -53.5217 | -53.302 | -0.28839 | -0.16022 | -0.16479 | 0.75073 | 53.5904 | -0.40283 | 53.8788 | -0.11444 | -0.10071 | -0.1236 | 0.009155 | 0.37994 | 0.14191 | -0.07782 | 0.24262 | 0.022888 | 1.0391 | 122.4792 | 0.48065 | 122.4655 | 122.4838 | 122.3328 | 122.1954 | 122.2321 | -122.644 | -122.4564 | 122.1909 | 122.3648 | 50.2121 | 47.319
1756.8281 | 122.6669 | -52.8305 | 69.4794 | -0.14793 | 0.0029801 | 0.061171 | 0.11398 | 0.0012391 | -0.0020722 | -0.0016022 | 0.051575 | -0.0026232 | 0.065247 | 0.058699 | -0.027645 | 0.0020551 | 0.0037385 | -2.9709 | 69.4336 | -53.0182 | 69.4427 | -52.0569 | -53.4943 | 0.49439 | -4.4083 | 69.3741 | -52.9404 | 69.5892 | -52.4185 | -52.9358 | -52.6657 | -0.18768 | -0.045776 | -0.036621 | 0.77362 | 53.3249 | -0.66376 | 53.5126 | -0.47607 | -0.10986 | -0.10529 | 0.10986 | 0.41199 | 0.1648 | -0.10529 | 0.27466 | 0.004578 | 0.9613 | 122.4609 | 0.52185 | 122.5296 | 122.4518 | 122.3145 | 122.2641 | 122.2046 | -122.4976 | -122.4197 | 122.2733 | 122.4197 | 49.8596 | 48.4222
1757.7656 | 122.612 | -52.9861 | 69.3649 | -0.079269 | -0.00065152 | 0.06053 | 0.1127 | -0.00046988 | -0.0024994 | -0.0030976 | 0.0027466 | -0.0047594 | 0.062683 | 0.060622 | -0.024654 | 0.00077333 | 0.0033111 | -3.1403 | 68.9941 | -53.4622 | 69.0765 | -52.3636 | -53.5355 | 0.27924 | -4.7058 | 69.0857 | -53.2013 | 69.3466 | -52.6016 | -53.1281 | -52.8717 | -0.47607 | -0.37079 | -0.28839 | 0.62256 | 53.2654 | -0.54932 | 53.7415 | -0.073242 | -0.21515 | -0.27924 | -0.01831 | 0.38452 | 0.11444 | -0.14191 | 0.32959 | 0.073242 | 1.0986 | 122.5388 | 0.59967 | 122.5479 | 122.4564 | 122.287 | 121.9803 | 122.0718 | -122.8271 | -122.5662 | 122.0627 | 122.3328 | 49.8459 | 48.2803
1758.8281 | 122.6166 | -54.0207 | 68.3716 | -0.10979 | -0.00086512 | 0.061598 | 0.11419 | -0.0011109 | -0.0029266 | -0.0037384 | -0.024719 | -0.0058276 | 0.064392 | 0.054 | -0.028927 | 0.00098693 | 0.0043793 | -2.9343 | 68.0511 | -54.3961 | 68.0374 | -53.2516 | -54.4601 | 0.60883 | -5.0171 | 68.1519 | -54.1214 | 68.3304 | -53.5721 | -54.0939 | -53.8651 | -0.37537 | -0.32044 | -0.33417 | 0.76904 | 54.6295 | -0.43945 | 55.0049 | -0.064087 | -0.10071 | -0.21973 | -0.041199 | 0.44861 | 0.15564 | -0.073242 | 0.25635 | 0.027466 | 1.1444 | 122.4335 | 0.54932 | 122.4518 | 122.4472 | 122.2733 | 122.0718 | 122.1725 | -122.7676 | -122.493 | 122.0581 | 122.3511 | 51.0864 | 49.0036
1759.7656 | 122.6212 | -53.9108 | 68.4357 | -0.094528 | -0.0015061 | 0.059462 | 0.11526 | 0.0020935 | -0.0022858 | -0.0026704 | -0.018616 | -0.0041186 | 0.063111 | 0.061049 | -0.026791 | 0.0016277 | 0.0013885 | -2.6459 | 68.4036 | -54.0436 | 68.3807 | -52.9678 | -54.1534 | 0.65918 | -4.6555 | 68.3945 | -53.952 | 68.4586 | -53.5446 | -54.0298 | -53.7918 | -0.13275 | -0.032044 | -0.054932 | 0.94299 | 54.57 | -0.24261 | 54.7028 | -0.10986 | -0.041198 | -0.041199 | 0.022888 | 0.36621 | 0.11902 | -0.11902 | 0.16022 | -0.07782 | 1.0757 | 122.4243 | 0.40741 | 122.4106 | 122.4472 | 122.3465 | 122.3145 | 122.3053 | -122.4792 | -122.3877 | 122.2916 | 122.3694 | 51.265 | 49.2554
1760.8281 | 122.6486 | -53.1281 | 69.191 | -0.056381 | -0.00022432 | 0.061171 | 0.11291 | -0.0021789 | -0.0022858 | -0.0037384 | -0.073547 | -0.0045458 | 0.065247 | 0.060195 | -0.028713 | 0.0012005 | 0.0030975 | -2.8061 | 69.1681 | -53.2791 | 69.2139 | -52.0294 | -53.389 | 0.61798 | -7.3654 | 69.1498 | -53.1784 | 69.2734 | -52.7069 | -53.2196 | -52.9724 | -0.15106 | -0.022888 | 0.022888 | 1.0986 | 53.746 | -0.26093 | 53.8971 | -0.10986 | -0.050354 | -0.041199 | 0.082397 | 0.42114 | 0.15564 | -0.091552 | 0.20599 | -0.041198 | 1.2497 | 122.493 | 0.4715 | 122.4518 | 122.4472 | 122.3282 | 122.2961 | 122.2778 | -122.4701 | -122.3694 | 122.3419 | 122.4014 | 50.322 | 45.7626
1761.7656 | 122.5983 | -52.6382 | 69.6808 | -0.15556 | 0.00084388 | 0.061812 | 0.1127 | 0.00038452 | -0.001004 | -0.00074776 | -0.04303 | -0.0036914 | 0.060974 | 0.063826 | -0.027431 | -8.1274e-05 | -0.0011749 | -2.8061 | 69.635 | -52.8259 | 69.603 | -51.5762 | -52.9999 | 0.68207 | -5.1773 | 69.5755 | -52.7115 | 69.7861 | -52.2583 | -52.7344 | -52.4963 | -0.18768 | -0.045776 | -0.07782 | 1.062 | 53.3203 | -0.36163 | 53.508 | -0.17395 | -0.073242 | -0.10529 | 0.10529 | 0.37994 | 0.14191 | -0.09613 | 0.21515 | -0.022888 | 1.2497 | 122.4289 | 0.45319 | 122.4976 | 122.4609 | 122.287 | 122.2733 | 122.2137 | -122.5067 | -122.3923 | 122.2412 | 122.4243 | 49.8322 | 47.4609
1762.8281 | 122.6303 | -52.9129 | 69.4382 | -0.18608 | 0.00063028 | 0.062453 | 0.11227 | 0.0025207 | -0.0022858 | -0.0013886 | -0.058289 | -0.003905 | 0.062683 | 0.060836 | -0.025936 | 0.0018413 | -0.0020295 | -3.0304 | 69.3741 | -53.0777 | 69.429 | -51.6769 | -53.1784 | 0.48065 | -5.7266 | 69.3695 | -52.9861 | 69.5068 | -52.5375 | -52.9861 | -52.7161 | -0.16479 | -0.064087 | -0.009155 | 1.236 | 53.3936 | -0.2655 | 53.5583 | -0.10071 | -0.073242 | -0.068664 | 0.068665 | 0.37537 | 0.19684 | -0.073242 | 0.27008 | 0 | 1.4008 | 122.5067 | 0.44861 | 122.493 | 122.4518 | 122.3557 | 122.287 | 122.2824 | -122.5159 | -122.4243 | 122.3419 | 122.4197 | 49.8825 | 47.1863
1763.7656 | 122.6715 | -52.6154 | 69.6991 | -0.17082 | 0.0021255 | 0.061598 | 0.11377 | -0.0028199 | -0.0052764 | -0.00074776 | -0.067444 | -0.0041186 | 0.063751 | 0.058486 | -0.027431 | 0.0018413 | 0.00096129 | -2.9388 | 69.6762 | -52.7573 | 69.6991 | -51.5259 | -52.8397 | 0.57678 | -4.9026 | 69.6854 | -52.6886 | 69.8044 | -52.1667 | -52.6978 | -52.446 | -0.14191 | -0.022889 | 0 | 1.0895 | 53.1921 | -0.22431 | 53.334 | -0.082398 | -0.073243 | -0.013733 | 0.10529 | 0.44861 | 0.16937 | -0.082398 | 0.24262 | -0.009155 | 1.2314 | 122.4564 | 0.52185 | 122.493 | 122.4335 | 122.374 | 122.2916 | 122.3007 | -122.4564 | -122.3877 | 122.3145 | 122.4197 | 49.6765 | 47.7127
1764.8281 | 122.612 | -53.1738 | 69.1681 | -0.10979 | -0.0010787 | 0.06288 | 0.11334 | 0.0018799 | -0.0037812 | -0.002884 | -0.097961 | -0.0030506 | 0.061829 | 0.064467 | -0.028713 | 0.0018413 | -0.0020295 | -3.1082 | 69.1589 | -53.3615 | 69.0491 | -52.2308 | -53.5217 | 0.3067 | -5.1315 | 69.1315 | -53.2562 | 69.223 | -52.7115 | -53.3295 | -53.0685 | -0.18768 | -0.009155 | -0.11902 | 0.94299 | 53.4805 | -0.3479 | 53.6682 | -0.16022 | -0.082398 | -0.036621 | 0.054931 | 0.46234 | 0.10529 | -0.15564 | 0.18768 | -0.073242 | 1.1307 | 122.4106 | 0.54474 | 122.4792 | 122.5204 | 122.3877 | 122.3328 | 122.3053 | -122.5296 | -122.4243 | 122.2229 | 122.3969 | 50.0656 | 48.0423
1765.7656 | 122.6212 | -52.1255 | 70.2118 | -0.13267 | 0.00063028 | 0.061598 | 0.1127 | 0.00038452 | -0.0024994 | -0.0024566 | -0.027771 | -0.0028368 | 0.063324 | 0.061049 | -0.026363 | 0.00055973 | 0.0018159 | -2.8748 | 70.2164 | -52.2263 | 70.1935 | -50.8667 | -52.3865 | 0.59509 | -4.7195 | 70.1752 | -52.2034 | 70.285 | -51.6769 | -52.2171 | -51.9974 | -0.10071 | 0.004578 | -0.018311 | 1.2589 | 52.7206 | -0.26093 | 52.8213 | -0.16022 | -0.07782 | -0.036621 | 0.073242 | 0.44861 | 0.12817 | -0.091553 | 0.20599 | -0.013733 | 1.3596 | 122.4197 | 0.52643 | 122.4884 | 122.4426 | 122.3785 | 122.3419 | 122.3007 | -122.438 | -122.4152 | 122.319 | 122.4106 | 49.2508 | 47.406
1766.8281 | 122.6624 | -51.9516 | 70.3491 | -0.14793 | 0.0012711 | 0.06523 | 0.11398 | 0.0018799 | -0.0014312 | -0.002884 | -0.04303 | -0.0047594 | 0.063751 | 0.065322 | -0.027645 | 0.0018413 | 0.0024567 | -3.0121 | 70.1981 | -52.272 | 70.2759 | -50.6332 | -52.4139 | 0.39368 | -5.4291 | 70.2438 | -52.0523 | 70.4636 | -51.4984 | -52.0706 | -51.8005 | -0.32043 | -0.15106 | -0.073242 | 1.3184 | 52.3453 | -0.46234 | 52.6657 | -0.14191 | -0.10071 | -0.10529 | 0.11444 | 0.45319 | 0.15106 | -0.11902 | 0.25177 | -0.018311 | 1.6388 | 122.5479 | 0.55389 | 122.5159 | 122.4701 | 122.2961 | 122.1497 | 122.1954 | -122.6212 | -122.4014 | 122.2275 | 122.4152 | 48.9395 | 46.5225
1767.7656 | 122.7173 | -51.9058 | 70.4681 | -0.094528 | -0.0010787 | 0.061385 | 0.11462 | 0.0048705 | -0.001004 | -0.0016022 | -0.067444 | -0.005614 | 0.06546 | 0.058913 | -0.026791 | 0.0035503 | -0.0024567 | -2.8519 | 70.4086 | -52.0477 | 70.4086 | -50.6973 | -52.1713 | 0.48523 | -4.4403 | 70.3583 | -51.9882 | 70.5963 | -51.4618 | -52.2079 | -51.7685 | -0.14191 | -0.05951 | -0.05951 | 1.2085 | 52.3911 | -0.2655 | 52.533 | -0.1236 | -0.082397 | -0.10986 | 0.12817 | 0.44403 | 0.13733 | -0.30212 | 0.21973 | -0.21973 | 1.3504 | 122.4564 | 0.52643 | 122.5845 | 122.4564 | 122.3465 | 122.3145 | 122.2641 | -122.5159 | -122.4564 | 122.3145 | 122.5021 | 49.054 | 47.4655
1768.8281 | 122.6212 | -51.8829 | 70.4956 | -0.12505 | -0.00022432 | 0.063094 | 0.11569 | 0.0016663 | -0.0024994 | 0.00010684 | -0.11627 | -0.0043322 | 0.063751 | 0.060408 | -0.027004 | 0.00098693 | 0.00074769 | -2.9572 | 70.4956 | -52.0523 | 70.3995 | -50.4547 | -52.1988 | 0.40283 | -5.4474 | 70.4498 | -51.947 | 70.5322 | -51.4389 | -51.9653 | -51.741 | -0.16937 | 0 | -0.09613 | 1.4282 | 52.2858 | -0.31586 | 52.4551 | -0.14648 | -0.064086 | -0.045776 | 0.036622 | 0.44403 | 0.14191 | -0.082397 | 0.20599 | -0.018311 | 1.5976 | 122.4518 | 0.50812 | 122.4792 | 122.5479 | 122.3969 | 122.3785 | 122.3328 | -122.5479 | -122.4426 | 122.2824 | 122.4152 | 48.9258 | 46.4355
1769.7656 | 122.6532 | -51.6724 | 70.6329 | -0.1403 | 0.00084388 | 0.061598 | 0.11377 | 0.0012391 | -0.0035674 | -0.0026704 | -0.073547 | -0.002196 | 0.064606 | 0.059981 | -0.026577 | 0.0035503 | 0.0020295 | -2.8885 | 70.6284 | -51.8692 | 70.5276 | -50.1938 | -52.0477 | 0.67749 | -5.0858 | 70.5688 | -51.7822 | 70.7565 | -51.1002 | -51.7502 | -51.5121 | -0.19684 | -0.004578 | -0.10529 | 1.4786 | 52.3499 | -0.37537 | 52.5467 | -0.17853 | -0.10986 | -0.064087 | 0.1236 | 0.5722 | 0.16022 | -0.07782 | 0.27008 | 0.032044 | 1.6754 | 122.3969 | 0.68207 | 122.5388 | 122.4976 | 122.3511 | 122.3007 | 122.2412 | -122.5021 | -122.4152 | 122.2 | 122.4289 | 48.7839 | 46.5866
1770.8281 | 122.6532 | -51.4297 | 70.8664 | -0.17082 | 0.0019119 | 0.064162 | 0.11377 | -0.00025628 | -0.0031402 | -0.00053396 | -0.04303 | -0.0047594 | 0.06247 | 0.066176 | -0.027218 | 0.0016277 | 0.0026703 | -3.0258 | 70.784 | -51.6632 | 70.8984 | -49.7772 | -51.7364 | 0.9201 | -5.7541 | 70.8115 | -51.5121 | 70.9946 | -50.8347 | -51.5533 | -51.2695 | -0.23346 | -0.082397 | 0.032043 | 1.6525 | 52.3499 | -0.3067 | 52.5833 | -0.073242 | -0.082397 | -0.054932 | 0.12817 | 0.59509 | 0.16022 | -0.1236 | 0.24262 | -0.041199 | 1.886 | 122.5616 | 0.67749 | 122.5067 | 122.4472 | 122.3236 | 122.2137 | 122.2412 | -122.5296 | -122.3785 | 122.3282 | 122.4243 | 48.4039 | 45.6757
1771.7656 | 122.6715 | -50.7614 | 71.5576 | -0.1403 | 0.0012711 | 0.062025 | 0.11227 | 0.0027343 | -0.0024994 | -0.002884 | -0.052185 | -0.0024096 | 0.065674 | 0.064681 | -0.025722 | 0.0026959 | -0.00053411 | -2.742 | 71.5988 | -50.8621 | 71.5942 | -48.8937 | -50.9857 | 0.92926 | -5.452 | 71.553 | -50.8026 | 71.814 | -50.0748 | -50.8896 | -50.6653 | -0.10071 | 0.041199 | 0.036621 | 1.8677 | 51.6907 | -0.2243 | 51.7914 | -0.1236 | -0.041198 | -0.004577 | 0.25635 | 0.68665 | 0.096131 | -0.12817 | 0.13733 | -0.086975 | 1.9684 | 122.4564 | 0.72784 | 122.6166 | 122.4609 | 122.3557 | 122.3602 | 122.3145 | -122.4197 | -122.3602 | 122.3557 | 122.5754 | 48.0194 | 45.3094
1772.8281 | 122.6212 | -50.9949 | 71.3516 | -0.17082 | -0.0010787 | 0.061171 | 0.11291 | -0.0011109 | -0.0007904 | -0.0013886 | -0.030823 | -0.0034778 | 0.063111 | 0.060836 | -0.026363 | 0.00034613 | 0.0011749 | -2.7374 | 71.3013 | -51.178 | 71.2509 | -49.2783 | -51.3474 | 0.87433 | -4.5181 | 71.2921 | -51.059 | 71.4066 | -50.4868 | -51.0818 | -50.853 | -0.18311 | -0.050354 | -0.10071 | 1.7166 | 51.8692 | -0.35248 | 52.0523 | -0.16937 | -0.064087 | -0.05951 | 0.054931 | 0.50812 | 0.14191 | -0.086975 | 0.20599 | -0.022888 | 1.8997 | 122.4289 | 0.5722 | 122.4655 | 122.4792 | 122.3511 | 122.2961 | 122.287 | -122.5296 | -122.4106 | 122.2458 | 122.4014 | 48.2574 | 46.4767
1773.7656 | 122.644 | -50.2075 | 72.1252 | -0.079269 | 0.0014847 | 0.062453 | 0.11334 | 0.0027343 | -0.0042084 | -0.0041656 | -0.070496 | -0.0043322 | 0.062897 | 0.054 | -0.025936 | 0.00013253 | 0.0022431 | -2.4124 | 72.0749 | -50.4364 | 72.0749 | -48.4314 | -50.528 | 1.062 | -4.747 | 72.0612 | -50.2762 | 72.2488 | -49.5987 | -50.3128 | -50.061 | -0.22888 | -0.050354 | -0.050354 | 1.7761 | 51.2695 | -0.32043 | 51.4984 | -0.091553 | -0.068664 | -0.064087 | 0.1236 | 0.60883 | 0.14649 | -0.10528 | 0.21515 | -0.036621 | 2.005 | 122.5113 | 0.67749 | 122.525 | 122.5113 | 122.3373 | 122.2824 | 122.2687 | -122.5616 | -122.4014 | 122.2824 | 122.4564 | 47.7951 | 45.4605
1774.8281 | 122.6212 | -50.4364 | 71.8552 | -0.14793 | 0.0014847 | 0.065016 | 0.11312 | 0.00059812 | -0.0012176 | -0.00032036 | -0.039978 | -0.0030506 | 0.061829 | 0.058699 | -0.02615 | 0.00034613 | 0.0020295 | -2.5314 | 71.9376 | -50.5508 | 71.814 | -48.5229 | -50.7294 | 0.97046 | -5.3192 | 71.8277 | -50.5234 | 71.9101 | -49.8047 | -50.5142 | -50.322 | -0.11444 | 0.082397 | -0.041199 | 1.9135 | 51.4069 | -0.29297 | 51.5213 | -0.17853 | -0.086975 | -0.027466 | 0.054931 | 0.63171 | 0.11444 | -0.07782 | 0.20142 | 0.009155 | 2.0279 | 122.3648 | 0.71869 | 122.4335 | 122.4884 | 122.3511 | 122.374 | 122.2641 | -122.406 | -122.3785 | 122.2504 | 122.3465 | 47.905 | 45.1172
1775.7656 | 122.6303 | -50.3494 | 71.9742 | -0.11742 | -0.00022432 | 0.062025 | 0.1127 | -0.00025628 | -0.0020722 | -0.004593 | -0.033874 | -0.0036914 | 0.064179 | 0.057845 | -0.026791 | 0.0022687 | 0.00032049 | -2.3849 | 71.9147 | -50.5554 | 71.8735 | -48.3948 | -50.6653 | 1.0254 | -5.2139 | 71.9376 | -50.3632 | 72.0016 | -49.7543 | -50.4684 | -50.2029 | -0.20599 | -0.059509 | -0.10071 | 1.9547 | 51.3748 | -0.31586 | 51.5808 | -0.10986 | -0.013733 | -0.036621 | 0.027466 | 0.59509 | 0.14648 | -0.11902 | 0.16022 | -0.10529 | 2.1606 | 122.4289 | 0.60883 | 122.3648 | 122.4701 | 122.3007 | 122.2641 | 122.287 | -122.5296 | -122.3373 | 122.2229 | 122.3511 | 47.9645 | 45.1355
1776.7656 | 122.6257 | -49.6948 | 72.6517 | -0.12505 | 0.0027665 | 0.062666 | 0.11505 | -0.00068368 | -0.001004 | -0.0016022 | -0.11322 | -0.0015552 | 0.063324 | 0.064467 | -0.02914 | 0.0041913 | 0.0016021 | -2.5543 | 72.6883 | -49.8184 | 72.5784 | -47.6624 | -49.9786 | 0.95215 | -5.7861 | 72.6196 | -49.7864 | 72.7249 | -49.0036 | -49.7818 | -49.5483 | -0.1236 | 0.036621 | -0.073242 | 2.0325 | 50.647 | -0.28381 | 50.7706 | -0.16022 | -0.091553 | -0.032043 | 0.073243 | 0.69122 | 0.14648 | -0.086975 | 0.23804 | 0.004578 | 2.1561 | 122.3969 | 0.78278 | 122.5113 | 122.5067 | 122.406 | 122.3831 | 122.3145 | -122.4701 | -122.438 | 122.2733 | 122.4197 | 47.1405 | 43.9087
1777.8281 | 122.6166 | -49.7589 | 72.5601 | -0.1403 | 0.0010575 | 0.062025 | 0.11248 | 0.00081172 | -0.0001496 | -0.0050202 | -0.030823 | -0.0054004 | 0.060974 | 0.062758 | -0.027431 | 0.0024823 | -0.00010671 | -2.6825 | 72.4594 | -49.9969 | 72.4869 | -47.7173 | -50.1022 | 0.84228 | -5.69 | 72.4869 | -49.8184 | 72.6837 | -49.1409 | -49.8322 | -49.5941 | -0.23804 | -0.10071 | -0.073243 | 2.0416 | 50.6012 | -0.34332 | 50.8392 | -0.10529 | -0.059509 | -0.073243 | 0.1236 | 0.61798 | 0.16479 | -0.073242 | 0.2243 | -0.013733 | 2.2797 | 122.4838 | 0.67749 | 122.5021 | 122.4564 | 122.3053 | 122.2183 | 122.2458 | -122.5571 | -122.3785 | 122.2458 | 122.4426 | 47.0764 | 44.0689
1778.7656 | 122.5845 | -49.855 | 72.5098 | -0.10979 | 0.0014847 | 0.061171 | 0.11697 | 0.0027343 | -0.0020722 | -0.001175 | -0.091858 | -0.0017688 | 0.06247 | 0.061904 | -0.025082 | 0.0026959 | -0.0020295 | -2.5864 | 72.5967 | -49.9466 | 72.4503 | -47.5433 | -50.1343 | 0.77362 | -7.2464 | 72.4915 | -49.91 | 72.5143 | -49.1684 | -50.0015 | -49.7681 | -0.091552 | 0.086975 | -0.05951 | 2.3117 | 50.6287 | -0.27923 | 50.7202 | -0.18768 | -0.054931 | -0.018311 | 0.004577 | 0.68665 | 0.086976 | -0.14648 | 0.14191 | -0.091553 | 2.4033 | 122.3969 | 0.74158 | 122.4243 | 122.5433 | 122.4014 | 122.4518 | 122.3465 | -122.4564 | -122.4197 | 122.3053 | 122.3694 | 47.2687 | 42.6086
1779.8281 | 122.6349 | -50.1846 | 72.1115 | -0.13267 | 0.0014847 | 0.063307 | 0.11398 | 0.0042297 | -0.0024994 | -0.002243 | -0.04303 | -0.0041186 | 0.06482 | 0.062972 | -0.027645 | 0.0018413 | 0.00096129 | -2.7328 | 72.1893 | -50.2762 | 72.2122 | -48.2941 | -50.3494 | 0.68207 | -5.5893 | 72.2031 | -50.1617 | 72.3129 | -49.3698 | -50.2304 | -50.0702 | -0.091553 | 0.07782 | 0.10071 | 1.8906 | 50.8667 | -0.16479 | 50.9583 | -0.073242 | 0.022888 | 0.091553 | 0.20142 | 0.81482 | 0.11444 | -0.045777 | 0.091553 | -0.068665 | 1.9821 | 122.4884 | 0.79193 | 122.4747 | 122.4655 | 122.3648 | 122.374 | 122.3877 | -122.3877 | -122.2733 | 122.3969 | 122.4976 | 47.4518 | 44.5953
1780.7656 | 122.6395 | -50.386 | 71.9513 | -0.15556 | -1.0718e-05 | 0.062453 | 0.11633 | 0.0020935 | -0.0020722 | -0.0048066 | -0.085754 | -0.005614 | 0.061188 | 0.062545 | -0.02914 | 0.0031231 | -0.0011749 | -2.8702 | 71.9238 | -50.592 | 71.814 | -48.5962 | -50.7477 | 0.61798 | -4.7699 | 71.8826 | -50.4684 | 72.052 | -49.6262 | -50.4684 | -50.2121 | -0.20599 | -0.027466 | -0.13733 | 1.7899 | 51.004 | -0.36163 | 51.21 | -0.15564 | -0.082398 | -0.068665 | 0.10071 | 0.75989 | 0.17395 | -0.082398 | 0.25635 | 0 | 1.9959 | 122.406 | 0.84229 | 122.5204 | 122.5159 | 122.3511 | 122.3099 | 122.2687 | -122.5433 | -122.4197 | 122.2 | 122.438 | 47.5159 | 45.6161
1781.8281 | 122.6578 | -49.9146 | 72.4091 | -0.14793 | -0.0015061 | 0.061812 | 0.11505 | -0.0028199 | -0.0031402 | 0.00032044 | -0.049133 | -0.0058276 | 0.061188 | 0.063826 | -0.027004 | 0.0035503 | -0.00032051 | -2.7374 | 72.3999 | -50.0793 | 72.377 | -47.818 | -50.1663 | 0.8194 | -5.5298 | 72.4091 | -49.9283 | 72.5555 | -49.2416 | -50.1755 | -49.9512 | -0.16479 | -0.009156 | -0.032044 | 2.0966 | 50.7339 | -0.25177 | 50.8987 | -0.086975 | -0.013733 | 0 | 0.14648 | 0.67291 | -0.036621 | -0.26093 | -0.022888 | -0.24719 | 2.2614 | 122.4564 | 0.68665 | 122.4838 | 122.4792 | 122.3373 | 122.3145 | 122.3236 | -122.4884 | -122.3373 | 122.2916 | 122.4701 | 47.1771 | 44.3848
1782.7656 | 122.6532 | -49.8093 | 72.5327 | -0.06401 | -0.00065152 | 0.064162 | 0.11462 | 0.0010253 | -0.0033538 | -0.002243 | -0.085754 | -0.0032642 | 0.063751 | 0.067458 | -0.027004 | 0.0012005 | 0.00032049 | -2.7878 | 72.496 | -49.9969 | 72.4548 | -47.5708 | -50.1343 | 0.81482 | -5.8044 | 72.4869 | -49.8962 | 72.6288 | -49.2966 | -49.8962 | -49.6399 | -0.18768 | -0.036621 | -0.07782 | 2.2385 | 50.6241 | -0.32501 | 50.8118 | -0.13733 | -0.086975 | -0.045777 | 0.09613 | 0.5127 | 0.16937 | -0.086975 | 0.25635 | 0 | 2.4261 | 122.4518 | 0.59967 | 122.525 | 122.493 | 122.3831 | 122.3053 | 122.2961 | -122.5296 | -122.4289 | 122.2641 | 122.438 | 47.0215 | 44.0048
1783.8281 | 122.5708 | -50.2945 | 72.0749 | -0.1403 | -0.00043792 | 0.062666 | 0.11441 | -0.00089728 | -0.0046356 | -0.0016022 | -0.11322 | -0.0043322 | 0.065247 | 0.061049 | -0.027645 | 0.00077333 | 0.0013885 | -2.861 | 72.2717 | -50.3128 | 71.9788 | -48.0286 | -50.5783 | 0.54474 | -5.8411 | 72.0749 | -50.3403 | 72.0932 | -49.8825 | -50.4822 | -50.2121 | -0.01831 | 0.19684 | -0.09613 | 2.2659 | 50.8392 | -0.28381 | 50.8575 | -0.2655 | -0.045776 | 0 | 0.018311 | 0.41199 | 0.082398 | -0.18768 | 0.12817 | -0.14191 | 2.2842 | 122.2916 | 0.45776 | 122.4335 | 122.5845 | 122.4152 | 122.5662 | 122.3694 | -122.3877 | -122.4152 | 122.2733 | 122.3877 | 47.4335 | 44.4534
1784.7656 | 122.6257 | -50.0565 | 72.2626 | -0.1403 | 0.00063028 | 0.061598 | 0.11163 | -0.00025628 | -0.0035674 | -0.0030976 | -0.00030524 | -0.003905 | 0.062256 | 0.058486 | -0.025936 | 0.0020551 | 0.0045929 | -2.655 | 72.2626 | -50.1846 | 72.2992 | -47.5754 | -50.2991 | 0.71411 | -6.0883 | 72.29 | -50.061 | 72.3267 | -49.6765 | -50.1892 | -49.9466 | -0.12817 | 0 | 0.036621 | 2.4811 | 50.7706 | -0.24261 | 50.8987 | -0.11444 | -0.004577 | 0.027466 | 0.064087 | 0.37994 | 0.10986 | -0.13275 | 0.11444 | -0.12817 | 2.6093 | 122.4838 | 0.38452 | 122.3877 | 122.4472 | 122.3511 | 122.319 | 122.3465 | -122.4472 | -122.3236 | 122.3557 | 122.3831 | 47.4014 | 43.9682
1785.8281 | 122.612 | -49.3057 | 73.1003 | -0.15556 | 0.0029801 | 0.063734 | 0.11163 | -0.0019653 | -0.0014312 | -0.0013886 | -0.0064086 | -0.0034778 | 0.06247 | 0.053572 | -0.025722 | 0.0018413 | -0.00010671 | -2.6047 | 73.0087 | -49.4522 | 72.995 | -46.7651 | -49.5804 | 0.96588 | -5.5984 | 73.0408 | -49.3195 | 73.1094 | -48.8983 | -49.3927 | -49.1684 | -0.14648 | -0.091553 | -0.10529 | 2.5406 | 50.2716 | -0.27466 | 50.4181 | -0.12817 | -0.013733 | -0.05951 | 0.009155 | 0.40741 | 0.13733 | -0.086975 | 0.15106 | -0.073242 | 2.6871 | 122.4472 | 0.42114 | 122.4289 | 122.4609 | 122.3602 | 122.3145 | 122.3465 | -122.5525 | -122.4197 | 122.3007 | 122.4152 | 46.7011 | 43.7073
1786.7656 | 122.6303 | -49.2874 | 73.0911 | -0.11742 | 0.0019119 | 0.062453 | 0.11483 | 0.0038025 | -0.0033538 | -0.00053396 | -0.09491 | -0.0017688 | 0.061829 | 0.063399 | -0.026577 | 0.0022687 | 0.0013885 | -2.7237 | 73.1049 | -49.4202 | 73.027 | -46.5866 | -49.585 | 0.90179 | -5.4199 | 73.082 | -49.3011 | 73.0728 | -48.9487 | -49.4202 | -49.1638 | -0.13275 | 0.013733 | -0.064086 | 2.7008 | 50.1892 | -0.29755 | 50.322 | -0.16479 | -0.013732 | -0.009155 | -0.01831 | 0.33875 | 0.1236 | -0.13275 | 0.13733 | -0.11902 | 2.8336 | 122.4472 | 0.35248 | 122.374 | 122.525 | 122.3831 | 122.3923 | 122.3694 | -122.5113 | -122.3923 | 122.3145 | 122.3602 | 46.5637 | 43.8675
1787.8281 | 122.612 | -49.4339 | 72.9172 | -0.12505 | -1.0718e-05 | 0.063307 | 0.11419 | 0.0016663 | -0.0035674 | -0.0035248 | -0.00030524 | -0.002196 | 0.06482 | 0.057418 | -0.026577 | -0.0015765 | 0.0028839 | -2.7237 | 72.8668 | -49.5667 | 72.8073 | -46.7056 | -49.7498 | 0.94299 | -5.5527 | 72.8394 | -49.4843 | 72.9446 | -49.1043 | -49.5483 | -49.3195 | -0.13275 | -0.050354 | -0.10986 | 2.7283 | 50.3769 | -0.31586 | 50.5096 | -0.18311 | -0.050354 | -0.07782 | 0.027466 | 0.32959 | 0.11444 | -0.11444 | 0.1648 | -0.064087 | 2.861 | 122.374 | 0.37994 | 122.4289 | 122.4335 | 122.3236 | 122.3007 | 122.2733 | -122.4838 | -122.4014 | 122.2412 | 122.3785 | 46.7102 | 43.8812
1788.7656 | 122.6486 | -48.8434 | 73.4756 | -0.11742 | 0.00084388 | 0.062025 | 0.1127 | 0.0029479 | -0.0035674 | -0.0030976 | -0.030823 | -0.0034778 | 0.062256 | 0.058699 | -0.027859 | 0.0031231 | 0.0028839 | -2.7603 | 73.3383 | -49.0677 | 73.3612 | -45.9869 | -49.2416 | 0.92926 | -5.5389 | 73.3429 | -48.9807 | 73.5306 | -48.5321 | -48.9395 | -48.7152 | -0.2243 | -0.13733 | -0.11444 | 2.8564 | 49.7726 | -0.39825 | 49.9969 | -0.17395 | -0.13733 | -0.13275 | 0.054932 | 0.31128 | 0.12817 | -0.09613 | 0.2655 | 0.041199 | 3.0807 | 122.4289 | 0.44861 | 122.5113 | 122.406 | 122.3236 | 122.1817 | 122.1863 | -122.5433 | -122.4564 | 122.2046 | 122.374 | 46.0831 | 43.3044
1789.8281 | 122.6761 | -49.3149 | 73.027 | -0.13267 | 0.00041648 | 0.065871 | 0.11334 | 0.0040161 | -0.0037812 | -0.002884 | -0.058289 | -0.0026232 | 0.060974 | 0.064894 | -0.026791 | 0.0018413 | 0.0016021 | -2.7695 | 73.0041 | -49.4385 | 72.9721 | -45.9595 | -49.4568 | 0.74158 | -5.6854 | 72.9538 | -49.3607 | 73.1415 | -48.9624 | -49.4202 | -49.1684 | -0.1236 | -0.022889 | -0.054932 | 3.3554 | 50.0565 | -0.14191 | 50.1801 | -0.01831 | -0.045777 | -0.073243 | 0.11444 | 0.35248 | 0.14648 | -0.10529 | 0.19226 | -0.059509 | 3.479 | 122.4106 | 0.39826 | 122.5021 | 122.4426 | 122.3145 | 122.319 | 122.2687 | -122.4655 | -122.3877 | 122.287 | 122.4564 | 46.5454 | 43.6295
1790.7656 | 122.6349 | -49.8825 | 72.464 | -0.14793 | 0.00084388 | 0.060957 | 0.11291 | 0.0014527 | -0.0039948 | 0.0020294 | -0.024719 | -0.0032642 | 0.064606 | 0.060836 | -0.02615 | 0.00055973 | -0.0033111 | -2.774 | 72.377 | -50.1022 | 72.3541 | -46.843 | -50.0656 | 0.74616 | -5.7587 | 72.3999 | -49.9329 | 72.4731 | -49.5758 | -49.9878 | -49.7726 | -0.21973 | -0.086975 | -0.10986 | 3.0395 | 50.6287 | -0.18311 | 50.8484 | 0.036621 | -0.050354 | -0.064087 | 0.009156 | 0.3067 | 0.10986 | -0.10529 | 0.16022 | -0.054932 | 3.2593 | 122.4564 | 0.35706 | 122.406 | 122.4792 | 122.3328 | 122.2595 | 122.2824 | -122.5662 | -122.3969 | 122.2366 | 122.3557 | 47.1085 | 44.1238
1791.7656 | 122.6852 | -48.7152 | 73.6038 | -0.16319 | 0.0012711 | 0.062025 | 0.11312 | -0.00046988 | -0.0033538 | -0.0013886 | -0.064392 | -0.0058276 | 0.06482 | 0.066817 | -0.026577 | 0.0016277 | 0.00032049 | -2.5314 | 73.5764 | -48.8983 | 73.6084 | -45.4376 | -48.9624 | 0.99335 | -5.5664 | 73.4985 | -48.8159 | 73.7 | -48.4085 | -48.9395 | -48.5779 | -0.1831 | -0.027466 | 0.004577 | 3.2776 | 49.7086 | -0.24719 | 49.8917 | -0.064087 | -0.10071 | -0.10529 | 0.09613 | 0.3067 | 0.13733 | -0.2243 | 0.23804 | -0.1236 | 3.4607 | 122.5067 | 0.40741 | 122.5159 | 122.4747 | 122.3145 | 122.2916 | 122.2137 | -122.5021 | -122.4197 | 122.3236 | 122.4152 | 46.1838 | 43.1488
1792.8281 | 122.5479 | -50.2121 | 72.2076 | -0.12505 | 0.00020288 | 0.061385 | 0.11654 | 0.0027343 | -0.0037812 | -0.001175 | -0.076599 | -0.0032642 | 0.066101 | 0.065535 | -0.027645 | 0.0026959 | 0.0030975 | -2.7924 | 72.1024 | -50.4684 | 71.8506 | -48.1064 | -50.6607 | 1.0117 | -5.5115 | 72.1527 | -50.2991 | 72.1481 | -50.0244 | -50.3906 | -50.1389 | -0.25635 | -0.10529 | -0.35706 | 2.1057 | 51.2238 | -0.44861 | 51.4801 | -0.19226 | -0.086975 | -0.054932 | -0.05951 | 0.18768 | 0.073242 | -0.17853 | 0.16022 | -0.091553 | 2.3621 | 122.319 | 0.27466 | 122.4472 | 122.5708 | 122.4518 | 122.3145 | 122.3648 | -122.6761 | -122.5067 | 122.0627 | 122.3602 | 47.4197 | 44.7006
1793.7656 | 122.6074 | -49.8093 | 72.5464 | -0.10216 | 0.0016983 | 0.062025 | 0.11377 | 0.0014527 | -0.0014312 | -0.0026704 | 0.011902 | -0.003905 | 0.06482 | 0.058486 | -0.02615 | 0.0024823 | 0.0054475 | -2.7283 | 72.8119 | -49.6719 | 72.5098 | -46.843 | -50.0519 | 0.77362 | -5.5298 | 72.5555 | -49.791 | 72.5876 | -49.5209 | -49.7818 | -49.6811 | 0.13733 | 0.2655 | -0.036621 | 2.9663 | 50.5829 | -0.24261 | 50.4456 | -0.37994 | 0.01831 | 0.009155 | 0.041198 | 0.28839 | 0.12817 | 0.027466 | 0.10986 | 0.009156 | 2.829 | 122.1817 | 0.27008 | 122.3785 | 122.4838 | 122.3465 | 122.6212 | 122.3648 | -122.2183 | -122.3373 | 122.319 | 122.3969 | 47.081 | 44.2795
1794.8281 | 122.6349 | -49.2783 | 73.0408 | -0.14793 | 0.0019119 | 0.062666 | 0.11377 | -0.0011109 | -0.0035674 | -0.00032036 | -0.036926 | -0.0047594 | 0.061829 | 0.057418 | -0.027218 | 0.00013253 | -0.0016021 | -2.5543 | 73.1049 | -49.379 | 73.0453 | -46.3257 | -49.5621 | 0.84228 | -5.5069 | 72.9996 | -49.3149 | 73.1232 | -48.999 | -49.5712 | -49.1501 | -0.10071 | 0.064087 | 0.004578 | 2.9526 | 50.1205 | -0.28381 | 50.2213 | -0.18311 | -0.036621 | -0.041198 | 0.082398 | 0.27924 | 0.12817 | -0.29297 | 0.1648 | -0.25635 | 3.0533 | 122.4243 | 0.31586 | 122.438 | 122.4838 | 122.3145 | 122.3831 | 122.2778 | -122.4197 | -122.3557 | 122.3236 | 122.4014 | 46.7239 | 43.7714
1795.7656 | 122.6303 | -48.8342 | 73.5031 | -0.20134 | -0.0017197 | 0.061812 | 0.11334 | 0.0020935 | -0.0029266 | -0.0020294 | -0.039978 | -0.0045458 | 0.063324 | 0.067671 | -0.027645 | -8.1274e-05 | -0.0022431 | -2.5909 | 73.4161 | -49.0173 | 73.4207 | -45.7764 | -49.1776 | 0.97504 | -5.2597 | 73.4161 | -48.912 | 73.5306 | -48.5596 | -48.9304 | -48.6923 | -0.1831 | -0.086975 | -0.082398 | 3.0579 | 49.8093 | -0.34332 | 49.9924 | -0.16022 | -0.077819 | -0.086975 | 0.027466 | 0.27466 | 0.14191 | -0.09613 | 0.21973 | -0.018311 | 3.241 | 122.438 | 0.35248 | 122.4426 | 122.4335 | 122.3282 | 122.2504 | 122.2504 | -122.5204 | -122.4152 | 122.2549 | 122.3648 | 46.2433 | 43.5745
1796.8281 | 122.6715 | -48.3124 | 74.0067 | -0.12505 | -0.00022432 | 0.062239 | 0.11441 | -0.00068368 | -0.0016448 | -0.0037384 | 0.0088502 | -0.0028368 | 0.061615 | 0.05699 | -0.027004 | 0.0014141 | 0.0020295 | -2.5635 | 74.0158 | -48.4589 | 73.9975 | -44.9158 | -48.5504 | 1.1169 | -4.6692 | 73.97 | -48.3673 | 74.0662 | -48.0331 | -48.3994 | -48.1888 | -0.14648 | 0.009155 | -0.009155 | 3.3966 | 49.4293 | -0.23804 | 49.5758 | -0.091553 | -0.054932 | -0.036621 | 0.059509 | 0.27924 | 0.1236 | -0.086975 | 0.17853 | -0.032043 | 3.5431 | 122.4564 | 0.33417 | 122.4335 | 122.4747 | 122.3373 | 122.3282 | 122.2824 | -122.4655 | -122.374 | 122.3099 | 122.3785 | 45.7489 | 43.6432
1797.7656 | 122.6669 | -48.0606 | 74.2767 | -0.1403 | 0.0012711 | 0.064375 | 0.11377 | -0.0013245 | -0.0014312 | -0.0026704 | -0.046081 | -0.003905 | 0.064179 | 0.059127 | -0.027859 | 0.0024823 | 0.0018159 | -2.4994 | 74.1852 | -48.2437 | 74.2081 | -44.5129 | -48.3994 | 1.1124 | -4.7562 | 74.1943 | -48.1476 | 74.3683 | -47.7448 | -48.1476 | -47.9416 | -0.1831 | -0.091552 | -0.068664 | 3.5477 | 49.173 | -0.33874 | 49.3561 | -0.15564 | -0.086975 | -0.082397 | 0.091553 | 0.31586 | 0.11902 | -0.086975 | 0.20599 | 0 | 3.7308 | 122.4518 | 0.40283 | 122.5159 | 122.4289 | 122.3419 | 122.2458 | 122.2549 | -122.5204 | -122.4243 | 122.2687 | 122.4289 | 45.5612 | 43.3044
1798.8281 | 122.6166 | -47.612 | 74.7299 | -0.12505 | -0.00065152 | 0.062239 | 0.11419 | -0.00025628 | -0.0046356 | -0.0013886 | -0.021667 | -0.0049732 | 0.061615 | 0.058486 | -0.026577 | 0.00077333 | 0.00053409 | -2.2842 | 74.5972 | -47.8455 | 74.6155 | -43.8995 | -47.9782 | 1.1993 | -4.541 | 74.6338 | -47.7448 | 74.7665 | -47.3923 | -47.7448 | -47.5204 | -0.23346 | -0.13275 | -0.11444 | 3.7125 | 48.8113 | -0.36621 | 49.0448 | -0.13275 | -0.13275 | -0.09613 | 0.036622 | 0.21973 | 0.091553 | -0.13275 | 0.2243 | 0 | 3.9459 | 122.4609 | 0.35248 | 122.5113 | 122.4426 | 122.3785 | 122.2092 | 122.2458 | -122.5754 | -122.4747 | 122.2275 | 122.3785 | 45.3278 | 43.071
1799.7656 | 122.6624 | -47.6761 | 74.6063 | -0.11742 | 0.0016983 | 0.063094 | 0.11334 | -4.2682e-05 | 0.0011322 | -0.00010676 | -0.052185 | -0.0054004 | 0.061615 | 0.057204 | -0.025082 | 0.0022687 | 0.0035247 | -2.2339 | 74.6658 | -47.7997 | 74.5743 | -44.0689 | -47.9965 | 1.1078 | -4.5502 | 74.5972 | -47.7173 | 74.762 | -47.374 | -47.8134 | -47.5021 | -0.1236 | 0.05951 | -0.032043 | 3.6072 | 48.7839 | -0.32044 | 48.9075 | -0.19684 | -0.041199 | -0.009155 | 0.15564 | 0.30212 | 0.17395 | -0.13733 | 0.21515 | -0.096131 | 3.7308 | 122.374 | 0.34332 | 122.4792 | 122.4655 | 122.3145 | 122.3419 | 122.2733 | -122.406 | -122.3236 | 122.2504 | 122.438 | 45.4422 | 43.1259
1800.8281 | 122.6532 | -48.317 | 74.0067 | -0.10216 | -1.0718e-05 | 0.06288 | 0.11163 | -0.0015381 | -0.0016448 | -0.0013886 | 0.014954 | -0.0043322 | 0.063111 | 0.059554 | -0.0285 | 0.00098693 | 0.0028839 | -2.3392 | 74.0341 | -48.4955 | 74.025 | -44.6228 | -48.5367 | 1.1078 | -4.6509 | 74.0341 | -48.3215 | 74.0707 | -48.0286 | -48.4268 | -48.2071 | -0.17853 | 0.027466 | 0.01831 | 3.6942 | 49.4247 | -0.21973 | 49.6033 | -0.041199 | -0.004577 | 0.027466 | 0.064087 | 0.28839 | 0.10986 | -0.10986 | 0.11444 | -0.10529 | 3.8727 | 122.5204 | 0.29297 | 122.3923 | 122.5296 | 122.3557 | 122.3511 | 122.3511 | -122.5021 | -122.3282 | 122.3419 | 122.3877 | 45.9778 | 43.6661
1801.7656 | 122.5937 | -47.7036 | 74.7253 | -0.086899 | 0.00041648 | 0.061812 | 0.11291 | -0.00068368 | -0.0037812 | -0.0020294 | -0.018616 | -0.003905 | 0.062683 | 0.059767 | -0.026363 | 0.00098693 | 0.0024567 | -2.1927 | 74.7391 | -47.7448 | 74.7574 | -43.7851 | -47.9416 | 0.98419 | -4.7974 | 74.5285 | -47.8775 | 74.5697 | -47.5067 | -47.8409 | -47.5571 | -0.041199 | 0.013733 | 0.032043 | 3.9185 | 48.6877 | -0.23804 | 48.7289 | -0.19684 | -0.17395 | -0.19684 | -0.15564 | 0.19684 | 0.14648 | -0.13733 | 0.32043 | 0.036621 | 3.9597 | 122.5021 | 0.37079 | 122.4472 | 122.4838 | 122.406 | 122.4426 | 122.2321 | -122.4701 | -122.6028 | 122.4609 | 122.2733 | 45.5109 | 42.9062
1802.8281 | 122.5754 | -47.6898 | 74.6658 | -0.10979 | 0.0021255 | 0.063521 | 0.1127 | -0.0011109 | -0.0029266 | -0.0035248 | -0.015564 | -0.003905 | 0.06247 | 0.061476 | -0.026363 | 0.00034613 | 0.0024567 | -2.4902 | 74.794 | -47.6624 | 74.8077 | -43.721 | -47.9553 | 0.85602 | -4.8248 | 74.6338 | -47.731 | 74.6979 | -47.4426 | -47.8271 | -47.6074 | 0.027465 | 0.12817 | 0.14191 | 3.9688 | 48.5458 | -0.2655 | 48.5184 | -0.29297 | -0.041199 | -0.032044 | 0.032043 | 0.24719 | 0.082397 | -0.13733 | 0.1236 | -0.09613 | 3.9413 | 122.4701 | 0.28839 | 122.4289 | 122.4564 | 122.3648 | 122.4838 | 122.3236 | -122.3282 | -122.3969 | 122.4976 | 122.3877 | 45.1996 | 42.865
1803.7656 | 122.644 | -47.5113 | 74.9084 | -0.10979 | 0.0012711 | 0.061812 | 0.11142 | 0.00038452 | -0.0012176 | 0.00010684 | -0.049133 | -0.0036914 | 0.063111 | 0.062972 | -0.027431 | 0.00034613 | 0.0011749 | -2.5543 | 74.6658 | -47.7997 | 74.6109 | -43.634 | -47.9553 | 1.1719 | -4.5822 | 74.6933 | -47.6715 | 74.826 | -47.3236 | -47.6486 | -47.4472 | -0.28839 | -0.24261 | -0.29755 | 3.8773 | 48.6832 | -0.44403 | 48.9716 | -0.15564 | -0.16022 | -0.21515 | -0.082397 | 0.18768 | 0.064087 | -0.13733 | 0.2243 | 0.022888 | 4.1656 | 122.4106 | 0.3479 | 122.4976 | 122.4655 | 122.3648 | 122.1771 | 122.2046 | -122.7081 | -122.58 | 122.1222 | 122.3373 | 44.957 | 42.9291
1804.8281 | 122.6349 | -48.2391 | 74.1257 | -0.15556 | -0.00022432 | 0.063948 | 0.11291 | -0.0011109 | -0.0024994 | -0.0024566 | -0.049133 | -0.0036914 | 0.062897 | 0.058486 | -0.027431 | 0.0020551 | 0.0037385 | -2.8427 | 74.231 | -48.2895 | 74.0204 | -44.4763 | -48.5504 | 0.90179 | -4.7104 | 74.0021 | -48.3582 | 74.1257 | -48.0057 | -48.3765 | -48.1064 | -0.050354 | 0.10529 | -0.10528 | 3.7628 | 49.1409 | -0.31128 | 49.1913 | -0.26093 | -0.11902 | -0.1236 | 0 | 0.23346 | 0.13275 | -0.13733 | 0.25177 | -0.018311 | 3.8132 | 122.3099 | 0.35248 | 122.4838 | 122.5204 | 122.3602 | 122.4701 | 122.2412 | -122.4152 | -122.4838 | 122.2595 | 122.3648 | 45.3964 | 43.5287
1805.7656 | 122.6303 | -47.4289 | 74.9359 | -0.16319 | -1.0718e-05 | 0.063307 | 0.11569 | 0.0040161 | -0.0020722 | -0.0013886 | -0.036926 | -0.0047594 | 0.063751 | 0.063613 | -0.026577 | 0.00013253 | 0.0022431 | -2.4399 | 75.1007 | -47.3785 | 74.9084 | -43.0801 | -47.699 | 1.1719 | -4.7882 | 74.9313 | -47.4472 | 74.9634 | -47.1634 | -47.5204 | -47.3373 | 0.050354 | 0.16479 | -0.027466 | 4.3488 | 48.6008 | -0.27008 | 48.5504 | -0.32043 | -0.018311 | -0.004578 | 0.027466 | 0.2655 | 0.091553 | -0.091553 | 0.10986 | -0.073242 | 4.2984 | 122.287 | 0.28381 | 122.4106 | 122.4792 | 122.3785 | 122.5296 | 122.3602 | -122.3145 | -122.3831 | 122.3373 | 122.3923 | 44.989 | 42.6407
1806.8438 | 122.5937 | -47.0398 | 75.3159 | -0.07164 | 0.0027665 | 0.063734 | 0.1159 | 0.0052979 | -0.006131 | -0.0033112 | -0.159 | -0.0045458 | 0.063538 | 0.06639 | -0.027218 | 0.0012005 | 0.0020295 | -2.1057 | 75.3433 | -47.1863 | 75.087 | -42.6865 | -47.1771 | 1.5381 | -4.5319 | 75.2747 | -47.1359 | 75.3799 | -46.7834 | -47.1405 | -46.9849 | -0.14648 | 0.027466 | -0.22888 | 4.3533 | 48.5779 | -0.13733 | 48.7244 | 0.009155 | -0.09613 | -0.041199 | 0.064087 | 0.25635 | 0.054932 | -0.10071 | 0.15106 | -0.004578 | 4.4998 | 122.2733 | 0.35248 | 122.5159 | 122.5296 | 122.4106 | 122.3831 | 122.3145 | -122.5021 | -122.4518 | 122.1268 | 122.4197 | 44.9341 | 42.5079
1807.7656 | 122.6257 | -47.1039 | 75.2197 | -0.10979 | -0.00022432 | 0.063094 | 0.11569 | -0.0015381 | -0.0016448 | -0.0026704 | -0.0033568 | -0.003905 | 0.063965 | 0.05699 | -0.026577 | 0.00013253 | 0.00096129 | -2.2339 | 75.2655 | -47.2046 | 75.1968 | -42.6682 | -47.3694 | 1.5015 | -4.5731 | 75.1923 | -47.1771 | 75.2655 | -46.9254 | -47.2321 | -47.0078 | -0.10071 | 0.045776 | -0.022889 | 4.4357 | 48.6053 | -0.2655 | 48.7061 | -0.16479 | -0.073242 | -0.027466 | 0.045776 | 0.17853 | 0.096131 | -0.12817 | 0.16937 | -0.054932 | 4.5364 | 122.4014 | 0.25177 | 122.4426 | 122.4701 | 122.3694 | 122.3694 | 122.2961 | -122.4243 | -122.3969 | 122.3007 | 122.3694 | 44.87 | 42.5308
1808.8281 | 122.6578 | -47.0535 | 75.3159 | -0.10216 | 0.0012711 | 0.062666 | 0.11163 | -4.2682e-05 | -0.006131 | -0.003952 | -0.0094604 | -0.0036914 | 0.062683 | 0.061049 | -0.027431 | -0.00050847 | -0.00053411 | -2.2842 | 75.2609 | -47.1817 | 75.238 | -42.6041 | -47.3648 | 1.474 | -4.4724 | 75.1877 | -47.1817 | 75.3571 | -46.7743 | -47.1176 | -46.9208 | -0.12817 | -0.054932 | -0.07782 | 4.4495 | 48.5275 | -0.31128 | 48.6557 | -0.1831 | -0.12817 | -0.12817 | 0.041199 | 0.27924 | 0.13275 | -0.064087 | 0.26093 | 0.064087 | 4.5776 | 122.4197 | 0.40741 | 122.5388 | 122.4426 | 122.3694 | 122.3145 | 122.2412 | -122.4976 | -122.4976 | 122.2916 | 122.4106 | 44.7693 | 42.5812
1809.7656 | 122.6578 | -47.6807 | 74.6841 | -0.048752 | 0.0014847 | 0.063307 | 0.11206 | 0.0018799 | -0.0007904 | -0.0030976 | -0.015564 | -0.0013416 | 0.061615 | 0.053786 | -0.025936 | 0.00034613 | -0.0018157 | -2.1103 | 74.5422 | -47.9004 | 74.5926 | -43.6615 | -47.9599 | 1.4465 | -6.6788 | 74.5285 | -47.8455 | 74.7574 | -47.374 | -47.7219 | -47.5204 | -0.21973 | -0.14191 | -0.091553 | 4.0192 | 49.1272 | -0.27924 | 49.3469 | -0.059509 | -0.16479 | -0.15564 | 0.073242 | 0.3067 | 0.16022 | -0.041199 | 0.32501 | 0.1236 | 4.2389 | 122.493 | 0.4715 | 122.6028 | 122.4426 | 122.374 | 122.2229 | 122.2092 | -122.5845 | -122.5296 | 122.2733 | 122.438 | 45.5704 | 41.0019
1810.8281 | 122.6303 | -47.1909 | 75.1602 | -0.15556 | 0.0019119 | 0.062453 | 0.11569 | 0.0046569 | -0.002713 | -0.002884 | -0.049133 | -0.003905 | 0.062042 | 0.063399 | -0.025509 | 0.0016277 | 0.0013885 | -1.9867 | 75.0687 | -47.4289 | 75.0137 | -43.0115 | -47.5388 | 1.6434 | -6.8756 | 75.032 | -47.2824 | 75.1831 | -46.9666 | -47.319 | -47.1176 | -0.23804 | -0.091552 | -0.14648 | 4.1794 | 48.8342 | -0.3479 | 49.0723 | -0.10986 | -0.091553 | -0.12817 | 0.022888 | 0.2243 | 0.073242 | -0.12817 | 0.16479 | -0.036621 | 4.4174 | 122.4426 | 0.31586 | 122.4655 | 122.4976 | 122.3145 | 122.2595 | 122.2229 | -122.5891 | -122.4426 | 122.2046 | 122.374 | 45.2042 | 40.3152
1811.7656 | 122.5662 | -47.3053 | 75.0641 | -0.025863 | -0.00043792 | 0.062239 | 0.11377 | 0.0025207 | -0.0037812 | -0.00032036 | -0.097961 | -0.0036914 | 0.062897 | 0.068526 | -0.028927 | -8.1274e-05 | 0.0022431 | -1.9638 | 75.1144 | -47.4518 | 74.9863 | -43.0801 | -47.5204 | 1.6159 | -6.6833 | 75.1785 | -47.2504 | 75.0824 | -47.0718 | -47.3785 | -47.2961 | -0.14648 | 0.050354 | -0.07782 | 4.2252 | 48.9212 | -0.21515 | 49.0677 | -0.068665 | 0.054932 | 0.11444 | 0.01831 | 0.23346 | 0.009155 | -0.073242 | -0.045777 | -0.12817 | 4.3716 | 122.438 | 0.17853 | 122.3328 | 122.5662 | 122.4289 | 122.4197 | 122.4838 | -122.5159 | -122.3145 | 122.2916 | 122.3877 | 45.3415 | 40.6219
1812.8438 | 122.6257 | -46.994 | 75.4166 | -0.056381 | 0.0010575 | 0.063521 | 0.11526 | 0.0027343 | -0.0057038 | -0.00010676 | -0.12543 | -0.0019824 | 0.065033 | 0.065749 | -0.028927 | 0.0063275 | 0.0054475 | -2.0096 | 75.3937 | -47.1313 | 75.2609 | -42.7322 | -47.3053 | 1.4832 | -5.0125 | 75.3571 | -47.0398 | 75.4074 | -46.7606 | -47.113 | -46.9254 | -0.13733 | -0.022888 | -0.15564 | 4.2618 | 48.4772 | -0.31128 | 48.6145 | -0.17395 | -0.045776 | -0.059509 | -0.009155 | 0.23346 | 0.068665 | -0.11902 | 0.11444 | -0.073242 | 4.3991 | 122.3923 | 0.27924 | 122.4472 | 122.525 | 122.3969 | 122.3877 | 122.3511 | -122.5479 | -122.4564 | 122.2549 | 122.4014 | 44.9844 | 41.9815
1813.7656 | 122.6166 | -46.1105 | 76.2268 | -0.10979 | -0.00043792 | 0.060316 | 0.11355 | -0.0013245 | -0.0039948 | -0.0016022 | -0.024719 | -0.0034778 | 0.063751 | 0.059554 | -0.024868 | -0.00093567 | -0.00053411 | -1.9867 | 76.2405 | -46.2524 | 76.1307 | -41.2582 | -46.4401 | 1.5015 | -6.2622 | 76.1673 | -46.1975 | 76.2817 | -45.8954 | -46.2479 | -46.0327 | -0.14191 | 0.013733 | -0.096131 | 4.8523 | 47.612 | -0.32959 | 47.7539 | -0.18768 | -0.086975 | -0.05951 | 0.054931 | 0.21515 | 0.07782 | -0.13733 | 0.16479 | -0.050354 | 4.9942 | 122.3831 | 0.30212 | 122.4792 | 122.493 | 122.3648 | 122.3511 | 122.2778 | -122.4792 | -122.4243 | 122.2412 | 122.3923 | 44.1238 | 39.8483
1814.8281 | 122.6578 | -46.5912 | 75.7919 | -0.16319 | 0.0012711 | 0.062025 | 0.11334 | -0.0015381 | -0.0035674 | -0.001175 | 0.014954 | -0.0049732 | 0.063324 | 0.061476 | -0.02615 | 0.00098693 | 0.00032049 | -2.1011 | 75.7645 | -46.7239 | 75.7416 | -42.0547 | -46.8658 | 1.6022 | -4.7424 | 75.7187 | -46.6324 | 75.7965 | -46.3348 | -46.6644 | -46.4676 | -0.13275 | -0.027466 | -0.050354 | 4.5364 | 48.1934 | -0.27466 | 48.3261 | -0.14191 | -0.041198 | -0.073242 | 0.004578 | 0.25635 | 0.1236 | -0.073242 | 0.16479 | -0.032044 | 4.6692 | 122.4655 | 0.29755 | 122.4289 | 122.4884 | 122.3511 | 122.3557 | 122.3099 | -122.5159 | -122.4243 | 122.3328 | 122.3877 | 44.4901 | 41.8488
1815.7656 | 122.6898 | -47.1909 | 75.174 | -0.10216 | -1.0718e-05 | 0.06288 | 0.11483 | -0.0011109 | -0.0022858 | -0.0024566 | -0.015564 | -0.0015552 | 0.063111 | 0.055709 | -0.026363 | 0.0012005 | -0.00074771 | -2.2064 | 75.0366 | -47.4243 | 75.0183 | -43.2358 | -47.5616 | 1.5839 | -4.7745 | 75 | -47.3511 | 75.2335 | -46.9299 | -47.2321 | -47.0627 | -0.23346 | -0.13733 | -0.15564 | 3.9551 | 48.7747 | -0.37079 | 49.0082 | -0.13733 | -0.16022 | -0.17395 | 0.059509 | 0.26093 | 0.12817 | -0.041199 | 0.28839 | 0.11902 | 4.1885 | 122.4426 | 0.42114 | 122.5845 | 122.4609 | 122.3511 | 122.2275 | 122.1909 | -122.5983 | -122.525 | 122.2092 | 122.4243 | 44.9844 | 42.4164
1816.8438 | 122.58 | -48.3078 | 74.1486 | -0.10216 | 0.0014847 | 0.060744 | 0.11676 | 0.0052979 | -0.0054902 | 0.00032044 | -0.14984 | -0.0045458 | 0.061188 | 0.064253 | -0.028713 | 0.00077333 | -0.0035247 | -2.3392 | 74.0479 | -48.4772 | 74.0753 | -44.7968 | -48.5733 | 1.4465 | -6.3126 | 74.057 | -48.3994 | 74.0982 | -48.111 | -48.4085 | -48.1888 | -0.16937 | -0.10071 | -0.073243 | 3.511 | 49.7543 | -0.2655 | 49.9237 | -0.09613 | -0.091553 | -0.091553 | -0.050354 | 0.19684 | 0.11902 | -0.10071 | 0.21057 | -0.009155 | 3.6804 | 122.5525 | 0.28839 | 122.4976 | 122.525 | 122.4564 | 122.3557 | 122.3648 | -122.6257 | -122.5479 | 122.3831 | 122.406 | 45.9686 | 41.9952
1817.7656 | 122.6898 | -46.9162 | 75.4486 | -0.12505 | 0.0014847 | 0.063094 | 0.11377 | -0.00089728 | -0.0007904 | -0.004593 | 0.021057 | -0.0034778 | 0.062256 | 0.058272 | -0.024441 | 0.00098693 | 0.0043793 | -2.1469 | 75.4898 | -46.9711 | 75.3799 | -42.6636 | -47.1542 | 1.6067 | -5.6168 | 75.3387 | -46.9894 | 75.5447 | -46.6232 | -46.9254 | -46.7468 | -0.054931 | 0.041199 | -0.068664 | 4.2526 | 48.5229 | -0.23804 | 48.5779 | -0.18311 | -0.073242 | -0.10986 | 0.096131 | 0.29297 | 0.16937 | -0.009155 | 0.24262 | 0.064087 | 4.3076 | 122.3511 | 0.36621 | 122.5342 | 122.4609 | 122.3282 | 122.406 | 122.2549 | -122.4197 | -122.438 | 122.2961 | 122.4609 | 44.7693 | 41.2994
1818.8281 | 122.6715 | -47.731 | 74.6017 | -0.06401 | -1.0718e-05 | 0.062453 | 0.11462 | -0.0021789 | -0.0048492 | -0.002884 | -0.021667 | -0.0036914 | 0.063751 | 0.056349 | -0.027218 | 0.00013253 | 0.0018159 | -2.1561 | 74.5926 | -47.9095 | 74.5468 | -44.0277 | -48.0011 | 1.5015 | -5.7861 | 74.5514 | -47.7814 | 74.6704 | -47.4976 | -47.8088 | -47.6028 | -0.17853 | -0.009156 | -0.054932 | 3.7033 | 49.2325 | -0.27008 | 49.411 | -0.091553 | -0.050354 | -0.050354 | 0.068664 | 0.23346 | 0.12817 | -0.07782 | 0.17853 | -0.027466 | 3.8818 | 122.4564 | 0.28381 | 122.4518 | 122.5021 | 122.3328 | 122.3236 | 122.2824 | -122.5113 | -122.3831 | 122.2778 | 122.4014 | 45.575 | 41.9449
1819.7656 | 122.6578 | -47.2275 | 75.1282 | -0.094528 | 0.00084388 | 0.06288 | 0.11526 | 0.0014527 | -0.0050628 | -0.0035248 | -0.036926 | -0.0047594 | 0.063538 | 0.06169 | -0.030209 | -0.0024311 | -0.00010671 | -2.3071 | 74.9496 | -47.5021 | 75.0412 | -43.6111 | -47.6028 | 1.4877 | -6.3034 | 74.9954 | -47.3328 | 75.2197 | -46.9894 | -47.287 | -47.0947 | -0.27466 | -0.17853 | -0.086975 | 3.6163 | 48.7152 | -0.37537 | 48.9899 | -0.10071 | -0.10529 | -0.13275 | 0.091553 | 0.23804 | 0.13275 | -0.059509 | 0.23804 | 0.045777 | 3.891 | 122.5433 | 0.34332 | 122.5525 | 122.4518 | 122.3282 | 122.1771 | 122.2229 | -122.6303 | -122.4609 | 122.2687 | 122.4472 | 44.9203 | 40.9241
1820.8281 | 122.6669 | -46.9299 | 75.4074 | -0.094528 | 0.00041648 | 0.062025 | 0.11377 | -0.0013245 | -0.0033538 | -0.0020294 | 0.0057984 | -0.005614 | 0.06482 | 0.065535 | -0.027218 | 0.0016277 | 0.00032049 | -2.2339 | 75.3616 | -47.1268 | 75.3479 | -42.9977 | -47.2183 | 1.4099 | -5.4749 | 75.3342 | -47.0306 | 75.4807 | -46.7285 | -47.0352 | -46.8155 | -0.19684 | -0.045777 | -0.05951 | 3.9322 | 48.3398 | -0.28839 | 48.5367 | -0.091553 | -0.10071 | -0.073243 | 0.073242 | 0.20142 | 0.11444 | -0.10529 | 0.21515 | -0.004577 | 4.129 | 122.4747 | 0.30212 | 122.5113 | 122.4884 | 122.3648 | 122.2916 | 122.2641 | -122.5342 | -122.4381 | 122.2778 | 122.4106 | 44.696 | 41.4551
1821.7656 | 122.644 | -46.2479 | 76.0574 | -0.12505 | 0.0023391 | 0.062666 | 0.11547 | 0.0020935 | -0.0039948 | -0.00053396 | -0.018616 | -0.0026232 | 0.062897 | 0.05699 | -0.026577 | 0.00034613 | 0.0024567 | -2.1423 | 76.1902 | -46.2982 | 76.0757 | -41.8533 | -46.4859 | 1.5793 | -6.7978 | 76.1124 | -46.2524 | 76.2177 | -46.0144 | -46.2753 | -46.0693 | -0.050354 | 0.13275 | 0.018311 | 4.3945 | 47.8271 | -0.23804 | 47.8775 | -0.18768 | -0.004577 | 0.054932 | 0.16022 | 0.23346 | 0.17853 | -0.027466 | 0.1831 | -0.022889 | 4.4449 | 122.374 | 0.23804 | 122.4701 | 122.4884 | 122.3648 | 122.4381 | 122.3602 | -122.3557 | -122.3099 | 122.3236 | 122.4655 | 44.1055 | 39.4501
1822.8281 | 122.8546 | -46.9849 | 75.4578 | -0.10979 | 0.0014847 | 0.061598 | 0.11355 | -0.0026063 | -0.002713 | -0.0037384 | -0.024719 | -0.0051868 | 0.064392 | 0.065962 | -0.027004 | 0.0022687 | 0.00053409 | -2.1606 | 75.1968 | -47.2366 | 75.1968 | -43.1992 | -47.2961 | 1.5015 | -6.7474 | 75.2243 | -47.0901 | 75.3891 | -46.7926 | -47.0352 | -46.9711 | -0.25177 | -0.26093 | -0.26093 | 3.7857 | 48.4863 | -0.31128 | 48.7381 | -0.05951 | -0.10529 | -0.23346 | -0.068665 | 0.19226 | 0.013733 | -0.050354 | 0.11902 | 0.054932 | 4.0375 | 122.4335 | 0.29755 | 122.4792 | 122.4335 | 122.3145 | 122.1817 | 122.2092 | -122.6944 | -122.5479 | 122.1817 | 122.374 | 44.8242 | 40.2374
1823.7656 | 122.6807 | -46.7011 | 75.6683 | -0.048752 | 0.00063028 | 0.061812 | 0.11483 | 0.0033753 | -0.0052764 | -0.0020294 | -0.021667 | -0.0051868 | 0.064179 | 0.058058 | -0.027645 | -0.0011493 | 0.0016021 | -2.1561 | 75.6638 | -46.8201 | 75.7645 | -42.4438 | -46.9757 | 1.6022 | -4.8889 | 75.6226 | -46.7514 | 75.705 | -46.4905 | -46.7651 | -46.5729 | -0.11902 | -0.004578 | 0.09613 | 4.2572 | 48.3032 | -0.27466 | 48.4222 | -0.15564 | -0.050354 | -0.045776 | 0.036621 | 0.21057 | 0.12817 | -0.064087 | 0.17853 | -0.013733 | 4.3762 | 122.5845 | 0.26093 | 122.4564 | 122.4838 | 122.374 | 122.3648 | 122.3236 | -122.4884 | -122.4197 | 122.4655 | 122.406 | 44.545 | 41.8121
1824.8281 | 122.6303 | -47.1359 | 75.2197 | -0.14793 | -0.0010787 | 0.065016 | 0.11355 | -4.2682e-05 | -0.0003632 | -0.004593 | -0.021667 | -0.0030506 | 0.063111 | 0.065749 | -0.027859 | -0.00093567 | -0.00096131 | -2.3071 | 75.0916 | -47.3602 | 75.0183 | -43.158 | -47.525 | 1.561 | -5.0354 | 75.1373 | -47.2229 | 75.2701 | -46.9437 | -47.2229 | -47.0535 | -0.2243 | -0.12817 | -0.20142 | 3.978 | 48.6969 | -0.3891 | 48.9212 | -0.1648 | -0.086975 | -0.082398 | 0.050354 | 0.19226 | 0.082397 | -0.086975 | 0.16937 | 0 | 4.2023 | 122.3785 | 0.27923 | 122.493 | 122.4518 | 122.3602 | 122.2275 | 122.2733 | -122.58 | -122.4426 | 122.1542 | 122.406 | 44.8288 | 42.1005
1825.7656 | 122.6395 | -47.612 | 74.7345 | -0.11742 | -0.00022432 | 0.062239 | 0.11611 | -0.00068368 | -0.0052764 | -0.0030976 | -0.015564 | -0.0045458 | 0.064179 | 0.062545 | -0.026791 | 0.00013253 | 0.00010689 | -2.2797 | 74.8627 | -47.5983 | 74.707 | -43.8766 | -47.8546 | 1.474 | -5.4382 | 74.707 | -47.6624 | 74.7711 | -47.4289 | -47.7036 | -47.493 | 0.013733 | 0.12817 | -0.027466 | 3.7354 | 49.086 | -0.24261 | 49.0723 | -0.25635 | -0.050354 | -0.027466 | 0.036621 | 0.18311 | 0.11902 | -0.091552 | 0.16937 | -0.041198 | 3.7216 | 122.3053 | 0.23346 | 122.4335 | 122.4609 | 122.3694 | 122.4747 | 122.319 | -122.3328 | -122.3969 | 122.319 | 122.3831 | 45.3323 | 42.1738
1826.7656 | 122.7219 | -47.4838 | 74.8535 | -0.06401 | 0.0012711 | 0.063521 | 0.11633 | 0.00017092 | -0.0035674 | 0.00010684 | -0.018616 | -0.0054004 | 0.064606 | 0.060408 | -0.027218 | 0.0012005 | 0.0024567 | -2.2934 | 74.7208 | -47.7448 | 74.7849 | -43.6157 | -47.7905 | 1.7807 | -7.5623 | 74.7345 | -47.5983 | 75.0137 | -47.1909 | -47.5204 | -47.3511 | -0.26093 | -0.13275 | -0.068665 | 3.8681 | 49.2645 | -0.3067 | 49.5255 | -0.045776 | -0.11444 | -0.11902 | 0.16022 | 0.29297 | 0.13275 | -0.036621 | 0.24719 | 0.07782 | 4.129 | 122.5296 | 0.40741 | 122.612 | 122.4655 | 122.3328 | 122.2046 | 122.2183 | -122.5983 | -122.4518 | 122.2687 | 122.4976 | 45.1904 | 39.9216
1827.8281 | 122.6669 | -47.2366 | 75.1236 | -0.11742 | -0.00065152 | 0.063521 | 0.11462 | -4.2682e-05 | -0.0024994 | -0.00053396 | -0.024719 | -0.0043322 | 0.060761 | 0.056563 | -0.026577 | 0.0024823 | 0.0020295 | -2.2202 | 75.0137 | -47.4747 | 75.1053 | -43.3182 | -47.4747 | 1.8814 | -7.7179 | 75.0732 | -47.2916 | 75.1831 | -46.9757 | -47.2458 | -47.0673 | -0.23804 | -0.10986 | -0.01831 | 3.9185 | 49.118 | -0.23804 | 49.3561 | 0 | -0.054932 | -0.050354 | 0.059509 | 0.26093 | 0.16937 | -0.009156 | 0.2243 | 0.045776 | 4.1565 | 122.58 | 0.31586 | 122.4747 | 122.4884 | 122.3648 | 122.2504 | 122.3099 | -122.5983 | -122.4152 | 122.3419 | 122.4197 | 45.0165 | 39.5187
1828.7656 | 122.5708 | -47.5433 | 74.8856 | -0.07164 | 0.00063028 | 0.063094 | 0.11483 | 0.0014527 | -0.0052764 | -0.0018158 | -0.073547 | -0.0032642 | 0.060974 | 0.063399 | -0.026363 | 0.0014141 | 0.0020295 | -2.1744 | 74.5834 | -47.9095 | 74.5605 | -44.2383 | -47.9599 | 1.7899 | -8.0887 | 74.5972 | -47.7768 | 74.7665 | -47.4014 | -47.699 | -47.4472 | -0.36621 | -0.30212 | -0.32501 | 3.3051 | 49.3332 | -0.41656 | 49.6994 | -0.050354 | -0.23346 | -0.28839 | -0.11902 | 0.14191 | 0.09613 | -0.15564 | 0.32959 | 0.077819 | 3.6713 | 122.4701 | 0.37537 | 122.5433 | 122.493 | 122.374 | 122.1268 | 122.1405 | -122.7951 | -122.6624 | 122.1039 | 122.3099 | 45.369 | 39.4547
1829.8281 | 122.5662 | -48.1613 | 74.295 | -0.094528 | 0.0027665 | 0.060316 | 0.11483 | 0.0018799 | -0.0042084 | -0.0013886 | -0.10712 | -0.0017688 | 0.062897 | 0.060195 | -0.028927 | 0.0012005 | -0.0030975 | -2.5452 | 74.3317 | -48.2346 | 74.0982 | -44.6503 | -48.4726 | 1.3596 | -7.8415 | 74.2401 | -48.1979 | 74.1898 | -48.0377 | -48.3124 | -48.0927 | -0.073242 | 0.036621 | -0.19684 | 3.511 | 49.5209 | -0.31128 | 49.5941 | -0.23804 | -0.036621 | -0.054932 | -0.10529 | 0.1236 | 0.068665 | -0.15106 | 0.10529 | -0.11444 | 3.5843 | 122.3328 | 0.16022 | 122.3877 | 122.5662 | 122.438 | 122.493 | 122.4014 | -122.5296 | -122.493 | 122.2595 | 122.3511 | 45.6161 | 40.3198
1830.7656 | 122.6807 | -47.6944 | 74.6887 | -0.12505 | 0.0012711 | 0.062453 | 0.1159 | 0.0029479 | -0.0033538 | -0.001175 | 0.16449 | -0.0024096 | 0.061402 | 0.063185 | -0.026577 | 0.00055973 | 0.0035247 | -2.4399 | 74.469 | -48.0057 | 74.501 | -44.426 | -48.0789 | 1.6708 | -7.7408 | 74.4598 | -47.9004 | 74.7391 | -47.4472 | -47.7768 | -47.5937 | -0.31128 | -0.21973 | -0.18768 | 3.2684 | 49.3652 | -0.38452 | 49.6765 | -0.073242 | -0.20599 | -0.22888 | 0.050354 | 0.24719 | 0.10071 | -0.082397 | 0.3067 | 0.1236 | 3.5797 | 122.5067 | 0.45319 | 122.6395 | 122.4747 | 122.3602 | 122.1634 | 122.1542 | -122.6944 | -122.5891 | 122.1954 | 122.4335 | 45.2545 | 39.9536
1831.8281 | 122.5021 | -47.2458 | 75.1694 | -0.07164 | -0.0010787 | 0.062666 | 0.11569 | 0.0018799 | -0.002713 | -0.00074776 | -0.052185 | -0.0036914 | 0.063324 | 0.062545 | -0.027218 | 0.00013253 | 0.0037385 | -2.3346 | 75.1831 | -47.3236 | 74.9954 | -43.3777 | -47.5891 | 1.4648 | -7.8003 | 75.119 | -47.2961 | 75.0458 | -46.9391 | -47.2321 | -47.2366 | -0.077819 | 0.013732 | -0.17395 | 3.8681 | 48.7106 | -0.34332 | 48.7885 | -0.2655 | -0.050354 | -0.050354 | -0.1236 | 0.3067 | 0.009156 | 0.013733 | 0.05951 | 0.064087 | 3.9459 | 122.319 | 0.35706 | 122.3419 | 122.5067 | 122.4152 | 122.4289 | 122.3648 | -122.493 | -122.4655 | 122.2412 | 122.2916 | 44.9112 | 39.4455
1832.7656 | 122.6532 | -46.9025 | 75.4211 | -0.025863 | -0.00022432 | 0.061598 | 0.11441 | 0.0014527 | -0.002713 | 0.00096124 | -0.036926 | -0.0026232 | 0.060547 | 0.05934 | -0.027004 | -0.00050847 | -0.00053411 | -2.2614 | 75.4349 | -47.0581 | 75.3983 | -42.9703 | -47.1771 | 1.4923 | -7.9376 | 75.3021 | -47.0489 | 75.4944 | -46.6919 | -47.0032 | -46.7972 | -0.15564 | 0.013732 | -0.022889 | 3.9322 | 48.3948 | -0.27466 | 48.5504 | -0.11902 | -0.14648 | -0.11902 | 0.073242 | 0.21057 | 0.10529 | -0.10071 | 0.25177 | 0.045776 | 4.0878 | 122.4564 | 0.35705 | 122.5433 | 122.493 | 122.3511 | 122.3373 | 122.2046 | -122.4792 | -122.4701 | 122.3007 | 122.3969 | 44.6411 | 38.9648
1833.8281 | 122.612 | -47.4976 | 74.9084 | -0.056381 | -0.0010787 | 0.064803 | 0.11611 | 0.0048705 | -0.001004 | -0.0054474 | -0.088806 | -0.0032642 | 0.060761 | 0.064467 | -0.02615 | 0.0016277 | -0.00010671 | -2.4673 | 74.8444 | -47.6715 | 74.8535 | -43.8858 | -47.7127 | 1.4786 | -8.2718 | 75.0229 | -47.406 | 74.9725 | -47.2778 | -47.6028 | -47.4106 | -0.17395 | -0.064087 | -0.054931 | 3.6118 | 48.9761 | -0.21515 | 49.1501 | -0.041199 | 0.091553 | 0.11444 | 0.064087 | 0.21973 | 0.086976 | -0.10528 | -0.004577 | -0.19684 | 3.7857 | 122.525 | 0.12817 | 122.3785 | 122.5159 | 122.4289 | 122.3419 | 122.5204 | -122.58 | -122.3145 | 122.3511 | 122.4701 | 45.0302 | 39.2258
1834.7656 | 122.6669 | -46.9116 | 75.4395 | -0.24712 | 0.0036209 | 0.061598 | 0.1159 | -4.2682e-05 | -0.0031402 | -0.002243 | 0.0057984 | -0.0028368 | 0.062256 | 0.061476 | -0.027859 | 0.0020551 | 0.00074769 | -2.4307 | 75.444 | -47.0398 | 75.3845 | -43.1259 | -47.1542 | 1.442 | -8.1024 | 75.3479 | -46.994 | 75.499 | -46.6782 | -46.9711 | -46.7972 | -0.12817 | 0.004578 | -0.054932 | 3.7857 | 48.3536 | -0.24262 | 48.4818 | -0.11444 | -0.082398 | -0.091553 | 0.059509 | 0.23346 | 0.11444 | -0.059509 | 0.19684 | 0.022889 | 3.9139 | 122.4243 | 0.31586 | 122.493 | 122.4838 | 122.3419 | 122.3557 | 122.2595 | -122.4792 | -122.4335 | 122.2961 | 122.4106 | 44.4809 | 38.8092
1835.8281 | 122.6486 | -47.3969 | 75 | -0.12505 | 0.0010575 | 0.063094 | 0.11505 | 0.00059812 | -0.0016448 | -0.002884 | 0.014954 | -0.0024096 | 0.06247 | 0.058913 | -0.027431 | -0.0013629 | 0.00096129 | -2.5131 | 74.7574 | -47.731 | 74.7574 | -43.7073 | -47.7722 | 1.4374 | -8.1024 | 74.8215 | -47.5204 | 75.0183 | -47.1359 | -47.4335 | -47.2458 | -0.33417 | -0.24262 | -0.24262 | 3.6896 | 48.8342 | -0.37537 | 49.1684 | -0.041199 | -0.1236 | -0.17853 | 0.018311 | 0.26093 | 0.15106 | -0.036621 | 0.27466 | 0.086975 | 4.0237 | 122.4884 | 0.38452 | 122.5388 | 122.4884 | 122.3419 | 122.1542 | 122.2183 | -122.731 | -122.5204 | 122.1542 | 122.4152 | 44.8837 | 39.2944
1836.7656 | 122.6028 | -49.8734 | 72.5052 | -0.033493 | -0.0015061 | 0.062025 | 0.11547 | -0.0015381 | -0.0029266 | -0.001175 | -0.091858 | -0.0024096 | 0.063324 | 0.06404 | -0.028927 | -0.00072207 | 0.0020295 | -2.8885 | 72.3724 | -50.1663 | 72.3312 | -47.3419 | -50.235 | 0.94757 | -8.9676 | 72.3862 | -50.0107 | 72.464 | -49.7223 | -50.0381 | -49.7818 | -0.29297 | -0.13275 | -0.17395 | 2.5314 | 50.8209 | -0.36163 | 51.1139 | -0.068664 | -0.13733 | -0.11902 | -0.041199 | 0.15106 | 0.091553 | -0.1648 | 0.22888 | -0.027466 | 2.8244 | 122.4976 | 0.28839 | 122.4747 | 122.5388 | 122.3969 | 122.2458 | 122.2595 | -122.6715 | -122.5159 | 122.2046 | 122.3373 | 46.9849 | 40.9058
1837.8281 | 122.5937 | -50.6012 | 71.8414 | -0.048752 | 0.00020288 | 0.056044 | 0.11248 | -0.00089728 | -0.0046356 | -0.0024566 | -0.052185 | -0.0019824 | 0.063751 | 0.061476 | -0.025509 | 0.00077333 | -0.00010671 | -2.71 | 71.9055 | -50.647 | 71.6766 | -48.1888 | -50.7843 | 0.97046 | -6.34 | 71.8323 | -50.6287 | 71.7224 | -50.4364 | -50.7385 | -50.5096 | -0.045777 | 0.064087 | -0.16479 | 2.4124 | 51.5717 | -0.18311 | 51.6174 | -0.13733 | -0.027466 | -0.009156 | -0.11902 | 0.1648 | 0.091552 | -0.13733 | 0.11902 | -0.10986 | 2.4582 | 122.3236 | 0.19226 | 122.3511 | 122.5525 | 122.4609 | 122.5067 | 122.4335 | -122.4884 | -122.4701 | 122.2778 | 122.3236 | 47.8912 | 44.2612
1838.7656 | 122.6166 | -49.7726 | 72.6105 | -0.041122 | -0.00022432 | 0.06288 | 0.11419 | 0.0029479 | -0.0052764 | -0.0013886 | -0.076599 | -0.0034778 | 0.063538 | 0.062758 | -0.027218 | 0.0012005 | -0.00053411 | -2.8015 | 72.6105 | -49.9283 | 72.5235 | -46.9254 | -50.0198 | 1.1719 | -6.308 | 72.6242 | -49.7818 | 72.6654 | -49.5621 | -49.9008 | -49.6628 | -0.15564 | 0 | -0.086975 | 2.8473 | 50.9445 | -0.24719 | 51.1002 | -0.091552 | -0.009155 | 0.013733 | 0.054931 | 0.21057 | 0.10986 | -0.12817 | 0.11902 | -0.11902 | 3.0029 | 122.4518 | 0.21973 | 122.4472 | 122.5388 | 122.406 | 122.3831 | 122.3969 | -122.5388 | -122.3923 | 122.2961 | 122.438 | 46.9711 | 43.4647
1839.8281 | 122.5433 | -50.8575 | 71.553 | -0.086899 | -0.0015061 | 0.060744 | 0.11526 | 0.0023071 | -0.002713 | -0.00096136 | -0.033874 | -0.0015552 | 0.066101 | 0.05934 | -0.025936 | 0.0029095 | -0.00010671 | -3.0075 | 71.608 | -50.9583 | 71.4111 | -48.4131 | -51.0956 | 1.0757 | -8.9401 | 71.5576 | -50.885 | 71.4981 | -50.7019 | -50.9995 | -50.7797 | -0.10071 | 0.054931 | -0.14191 | 2.4445 | 51.9333 | -0.23804 | 52.034 | -0.13733 | -0.027466 | 0.004577 | -0.054932 | 0.15564 | 0.07782 | -0.14191 | 0.10529 | -0.11444 | 2.5452 | 122.3694 | 0.18311 | 122.3831 | 122.5662 | 122.4426 | 122.4655 | 122.4152 | -122.5113 | -122.4381 | 122.2687 | 122.3557 | 47.85 | 41.9174
1840.7656 | 122.58 | -49.2142 | 73.233 | 0.1191 | -0.00043792 | 0.063307 | 0.1159 | 0.0016663 | -0.0033538 | -0.0052338 | -0.058289 | -0.0034778 | 0.064392 | 0.057631 | -0.025295 | -8.1274e-05 | 0.00096129 | -2.7969 | 73.2239 | -49.3744 | 72.8806 | -46.4218 | -49.7543 | 0.98419 | -8.6884 | 73.0408 | -49.3469 | 73.1232 | -49.0448 | -49.3607 | -49.1226 | -0.16022 | -0.009155 | -0.35248 | 2.7924 | 50.1984 | -0.54016 | 50.3586 | -0.37994 | -0.13275 | -0.19226 | -0.10986 | 0.16937 | 0.091552 | -0.14649 | 0.2243 | -0.013733 | 2.9526 | 122.2549 | 0.30212 | 122.4701 | 122.5983 | 122.3877 | 122.438 | 122.2549 | -122.6074 | -122.58 | 122.0947 | 122.3373 | 46.4172 | 40.5258
1841.8281 | 122.5662 | -49.9512 | 72.4777 | -0.11742 | -0.00065152 | 0.060957 | 0.1159 | 0.0035889 | -0.0014312 | -0.002243 | -0.039978 | -0.0047594 | 0.061402 | 0.059981 | -0.024654 | 0.0024823 | 0.0028839 | -2.9617 | 72.4228 | -50.1251 | 72.2946 | -47.1863 | -50.2716 | 0.95673 | -8.5968 | 72.3999 | -50.061 | 72.3953 | -49.7955 | -50.0885 | -49.8642 | -0.17395 | -0.054931 | -0.1831 | 2.7649 | 50.9079 | -0.32043 | 51.0818 | -0.14648 | -0.10986 | -0.07782 | -0.082397 | 0.15564 | 0.086975 | -0.13733 | 0.19684 | -0.027466 | 2.9388 | 122.4197 | 0.2655 | 122.4564 | 122.5479 | 122.4609 | 122.374 | 122.3511 | -122.6028 | -122.5388 | 122.2458 | 122.3465 | 46.9894 | 41.3544
1842.7656 | 122.5708 | -49.7681 | 72.6791 | -0.094528 | 0.00020288 | 0.061598 | 0.11398 | 0.0016663 | -0.0024994 | -0.0037384 | -0.027771 | -0.0015552 | 0.063111 | 0.06169 | -0.026577 | 0.00098693 | 0.0041657 | -2.9938 | 72.6654 | -49.8779 | 72.5418 | -47.0947 | -50.0702 | 0.97961 | -8.5922 | 72.6151 | -49.8413 | 72.5967 | -49.5712 | -49.9008 | -49.6628 | -0.10986 | -0.013733 | -0.13733 | 2.6733 | 50.7477 | -0.30212 | 50.8575 | -0.19226 | -0.073243 | -0.064087 | -0.082397 | 0.19684 | 0.10528 | -0.13275 | 0.17853 | -0.059509 | 2.7832 | 122.4197 | 0.27008 | 122.4381 | 122.5433 | 122.4564 | 122.4335 | 122.3831 | -122.5571 | -122.5204 | 122.3099 | 122.3648 | 46.7743 | 41.1758
1843.8281 | 122.5388 | -49.6033 | 72.8439 | -0.07164 | 0.0014847 | 0.062239 | 0.11526 | 0.0018799 | -0.0031402 | -0.0030976 | -0.10101 | -0.00091423 | 0.066315 | 0.062972 | -0.027431 | 0.0022687 | -0.00032051 | -3.0487 | 72.7295 | -49.7772 | 72.7386 | -46.6827 | -49.8459 | 1.0803 | -8.2031 | 72.8485 | -49.5621 | 72.7707 | -49.4522 | -49.7589 | -49.498 | -0.17395 | -0.11444 | -0.10529 | 2.9205 | 50.6836 | -0.24262 | 50.8575 | -0.068664 | 0.041198 | 0.004578 | -0.073242 | 0.15106 | 0.10529 | -0.15564 | 0.064087 | -0.19684 | 3.0945 | 122.5159 | 0.10986 | 122.3328 | 122.5067 | 122.4106 | 122.3328 | 122.4518 | -122.6212 | -122.406 | 122.3419 | 122.374 | 46.5546 | 41.4001
1844.7656 | 122.5891 | -49.5026 | 72.9309 | -0.10216 | -0.00065152 | 0.061598 | 0.11419 | 0.00038452 | -0.0012176 | -0.002884 | -0.046081 | -0.002196 | 0.06546 | 0.06169 | -0.024868 | 0.0029095 | -0.0022431 | -2.8015 | 72.9126 | -49.6262 | 72.8073 | -46.5637 | -49.7818 | 1.0986 | -6.1203 | 72.8394 | -49.5575 | 72.8851 | -49.2966 | -49.6262 | -49.3652 | -0.1236 | -0.01831 | -0.1236 | 2.9388 | 50.6012 | -0.27924 | 50.7248 | -0.15564 | -0.054932 | -0.091553 | -0.045776 | 0.20599 | 0.13733 | -0.1236 | 0.19226 | -0.068665 | 3.0624 | 122.4335 | 0.26093 | 122.4426 | 122.5388 | 122.3969 | 122.4152 | 122.3419 | -122.5571 | -122.4884 | 122.3099 | 122.3877 | 46.701 | 43.3823
1845.8281 | 122.5571 | -49.0723 | 73.3521 | -0.079269 | -1.0718e-05 | 0.060744 | 0.11782 | 0.00038452 | -0.0035674 | -0.00074776 | -0.076599 | -0.002196 | 0.064179 | 0.059767 | -0.026791 | 0.0026959 | 0.00074769 | -2.5818 | 73.3521 | -49.1638 | 73.2376 | -46.019 | -49.3607 | 1.268 | -5.3787 | 73.3246 | -49.1089 | 73.2742 | -48.9532 | -49.2599 | -49.0036 | -0.091552 | 0 | -0.11444 | 3.0533 | 50.3403 | -0.28839 | 50.4318 | -0.19684 | -0.036621 | -0.027466 | -0.07782 | 0.11902 | 0.068665 | -0.18768 | 0.10529 | -0.15106 | 3.1448 | 122.4014 | 0.15564 | 122.3831 | 122.5159 | 122.4335 | 122.4243 | 122.3969 | -122.5159 | -122.4609 | 122.3099 | 122.3465 | 46.4905 | 43.6935
1846.7656 | 122.6257 | -49.3927 | 73.0225 | -0.018234 | 0.0010575 | 0.062025 | 0.11483 | 0.0012391 | -0.0020722 | -0.0026704 | -0.021667 | -0.0043322 | 0.063965 | 0.061263 | -0.027218 | 0.0014141 | -0.00010671 | -2.6184 | 73.0316 | -49.498 | 72.9034 | -46.5271 | -49.6674 | 1.3229 | -4.7791 | 73.0225 | -49.3835 | 72.995 | -49.1821 | -49.5071 | -49.2599 | -0.10529 | 0.009155 | -0.11902 | 2.8656 | 50.7156 | -0.27466 | 50.8209 | -0.16937 | 0.009155 | 0 | -0.027466 | 0.21057 | 0.13275 | -0.11444 | 0.1236 | -0.1236 | 2.9709 | 122.4014 | 0.20142 | 122.3785 | 122.5296 | 122.406 | 122.4243 | 122.4152 | -122.5204 | -122.406 | 122.2961 | 122.3877 | 46.7743 | 44.6136
1847.8281 | 122.6074 | -49.6536 | 72.7295 | -0.13267 | -0.00022432 | 0.062666 | 0.11419 | 0.0020935 | -0.0035674 | -0.0016022 | -0.04303 | -0.0017688 | 0.063965 | 0.058058 | -0.025509 | 0.0035503 | 0.0075837 | -2.6276 | 72.7798 | -49.7589 | 72.6654 | -46.5408 | -49.9146 | 1.1673 | -5.4016 | 72.7524 | -49.6445 | 72.7386 | -49.4705 | -49.791 | -49.5438 | -0.10529 | 0.050354 | -0.064087 | 3.1128 | 50.8209 | -0.26093 | 50.9262 | -0.15564 | 0.009155 | 0.022888 | 0.009155 | 0.1831 | 0.10986 | -0.13733 | 0.10071 | -0.14648 | 3.2181 | 122.4243 | 0.17395 | 122.3831 | 122.5388 | 122.3969 | 122.4335 | 122.406 | -122.4884 | -122.374 | 122.319 | 122.3923 | 47.0261 | 44.252
1848.7656 | 122.5891 | -49.7818 | 72.6288 | -0.086899 | -0.0010787 | 0.060744 | 0.11505 | 0.00017092 | -0.0039948 | -0.002243 | -0.024719 | -0.0030506 | 0.063111 | 0.059981 | -0.026791 | 0.0031231 | 0.0016021 | -2.5131 | 72.6151 | -49.9329 | 72.4777 | -46.907 | -50.0748 | 1.2634 | -8.4183 | 72.5693 | -49.8459 | 72.5647 | -49.6078 | -49.8917 | -49.6719 | -0.15106 | -0.013733 | -0.15106 | 2.8748 | 51.0452 | -0.29297 | 51.1963 | -0.14191 | -0.064087 | -0.059509 | -0.064087 | 0.17395 | 0.10986 | -0.10986 | 0.17395 | -0.045777 | 3.0258 | 122.4106 | 0.23804 | 122.4106 | 122.5479 | 122.4152 | 122.3969 | 122.3511 | -122.5616 | -122.4747 | 122.2595 | 122.3465 | 47.2687 | 41.3635
1849.8281 | 122.6578 | -49.0997 | 73.2513 | -0.12505 | -1.0718e-05 | 0.062025 | 0.11419 | 0.0025207 | -0.0014312 | -0.00032036 | -0.039978 | -0.0026232 | 0.065033 | 0.057631 | -0.027004 | 0.0012005 | 0.0020295 | -2.6688 | 73.3292 | -49.1821 | 73.2468 | -45.9183 | -49.3607 | 1.2131 | -5.5298 | 73.2605 | -49.1135 | 73.3246 | -48.9304 | -49.2233 | -48.9807 | -0.082398 | 0.07782 | -0.004578 | 3.1815 | 50.3128 | -0.26093 | 50.3952 | -0.17853 | -0.013733 | 0.009155 | 0.073242 | 0.16937 | 0.11902 | -0.1236 | 0.13275 | -0.10986 | 3.2639 | 122.4289 | 0.1831 | 122.438 | 122.5113 | 122.374 | 122.4289 | 122.3602 | -122.4335 | -122.3648 | 122.3465 | 122.4243 | 46.431 | 43.5699
1850.7656 | 122.6028 | -49.7772 | 72.6105 | -0.056381 | 0.0049027 | 0.063094 | 0.11462 | -0.0030335 | -0.0022858 | -0.0020294 | -0.04303 | -0.0030506 | 0.063324 | 0.059127 | -0.028286 | 0.0026959 | 0.00096129 | -2.9892 | 72.5784 | -49.9374 | 72.5464 | -46.9894 | -50.0061 | 1.2314 | -8.075 | 72.6059 | -49.7772 | 72.6562 | -49.5621 | -49.8596 | -49.6353 | -0.16022 | -0.032044 | -0.064087 | 2.7878 | 51.0086 | -0.22888 | 51.1688 | -0.068665 | 0 | -0.004578 | 0.045776 | 0.21515 | 0.14191 | -0.082397 | 0.14191 | -0.082397 | 2.948 | 122.4838 | 0.21515 | 122.4335 | 122.5159 | 122.3831 | 122.3557 | 122.3831 | -122.5479 | -122.3877 | 122.3236 | 122.4335 | 46.788 | 41.7023
1851.8281 | 122.5662 | -48.9075 | 73.4756 | -0.07164 | 0.00041648 | 0.063307 | 0.11569 | 0.0042297 | -0.0050628 | -0.002884 | 0.079041 | -0.002196 | 0.065247 | 0.061263 | -0.028286 | 0.0014141 | 0.0018159 | -2.7374 | 73.4573 | -49.0631 | 73.2925 | -46.0968 | -49.6811 | 1.2085 | -7.1228 | 73.4802 | -48.9487 | 73.4253 | -48.8113 | -49.1272 | -48.8525 | -0.15564 | -0.018311 | -0.1831 | 2.8107 | 50.116 | -0.77362 | 50.2716 | -0.61798 | -0.041198 | 0.004578 | -0.050354 | 0.096131 | 0.054932 | -0.21973 | 0.09613 | -0.17853 | 2.9663 | 122.3557 | 0.13733 | 122.374 | 122.5204 | 122.4289 | 122.3648 | 122.3877 | -122.5388 | -122.4243 | 122.2 | 122.3328 | 46.17 | 41.7847
1852.7656 | 122.5525 | -48.7976 | 73.6176 | -0.094528 | 0.0021255 | 0.060957 | 0.11483 | 0.0014527 | -0.0039948 | -0.0026704 | -0.055237 | -0.0024096 | 0.063111 | 0.058699 | -0.027859 | 0.0018413 | 0.0037385 | -2.6321 | 73.5306 | -48.9944 | 73.439 | -45.694 | -49.1501 | 1.3458 | -5.5527 | 73.5855 | -48.8525 | 73.5306 | -48.674 | -48.967 | -48.7381 | -0.19684 | -0.086975 | -0.17853 | 3.1036 | 50.1434 | -0.35248 | 50.3403 | -0.15564 | -0.054932 | -0.032044 | -0.086975 | 0.1236 | 0.059509 | -0.16937 | 0.11444 | -0.11444 | 3.3005 | 122.4335 | 0.17853 | 122.3831 | 122.525 | 122.438 | 122.3282 | 122.3831 | -122.612 | -122.4701 | 122.2366 | 122.3282 | 46.1655 | 43.2449
1853.8281 | 122.5479 | -49.2325 | 73.2056 | -0.10216 | 0.0019119 | 0.061598 | 0.11569 | 0.0025207 | -0.0016448 | -0.00074776 | -0.052185 | -0.0024096 | 0.062683 | 0.056349 | -0.024441 | 0.0016277 | 0.0011749 | -2.6413 | 73.2422 | -49.3149 | 73.0408 | -46.2067 | -49.5667 | 1.4923 | -5.2139 | 73.1827 | -49.2416 | 73.1369 | -49.0814 | -49.4202 | -49.1272 | -0.082397 | 0.036621 | -0.16479 | 3.0258 | 50.7248 | -0.33417 | 50.8072 | -0.25177 | -0.009155 | -0.022888 | -0.068664 | 0.15106 | 0.10529 | -0.18768 | 0.11444 | -0.17853 | 3.1082 | 122.3557 | 0.16022 | 122.3785 | 122.5571 | 122.4243 | 122.4747 | 122.4152 | -122.5204 | -122.4472 | 122.2733 | 122.3694 | 46.5912 | 44.0186
1854.7656 | 122.5708 | -49.0036 | 73.4116 | -0.041122 | -0.0017197 | 0.061812 | 0.11526 | 0.0027343 | -0.001004 | -0.0013886 | -0.049133 | -0.0034778 | 0.062897 | 0.064467 | -0.026577 | 0.0018413 | 0.0020295 | -2.5314 | 73.2925 | -49.2279 | 73.2193 | -45.8267 | -49.3149 | 1.4236 | -5.4245 | 73.3337 | -49.0448 | 73.3795 | -48.8205 | -49.1272 | -48.912 | -0.2243 | -0.11902 | -0.19226 | 3.1769 | 50.4272 | -0.31128 | 50.6516 | -0.086975 | -0.041199 | -0.07782 | -0.032043 | 0.18311 | 0.091553 | -0.1236 | 0.13275 | -0.082397 | 3.4012 | 122.4472 | 0.2243 | 122.4243 | 122.5204 | 122.3785 | 122.2961 | 122.3373 | -122.6395 | -122.4564 | 122.2229 | 122.3831 | 46.4722 | 43.5791
1855.8281 | 122.6257 | -47.6395 | 74.7482 | -0.11742 | -0.00022432 | 0.063307 | 0.11462 | 0.0012391 | -0.0016448 | -0.00010676 | -0.0094604 | -0.0017688 | 0.062042 | 0.061904 | -0.028072 | 0.0024823 | 0.0016021 | -2.2339 | 74.8535 | -47.6761 | 74.6841 | -43.8858 | -47.8729 | 1.7212 | -4.834 | 74.8032 | -47.5937 | 74.7986 | -47.3785 | -47.9233 | -47.6669 | -0.036621 | 0.10529 | -0.064087 | 3.7537 | 49.3607 | -0.23346 | 49.3973 | -0.19684 | 0.045776 | 0.054932 | 0.050354 | 0.26093 | -0.027466 | -0.28381 | -0.073242 | -0.32959 | 3.7903 | 122.3602 | 0.21515 | 122.3923 | 122.5296 | 122.3969 | 122.493 | 122.4426 | -122.4243 | -122.3419 | 122.3236 | 122.438 | 45.4056 | 42.8055
1856.7656 | 122.612 | -49.3469 | 73.0682 | -0.1403 | 0.00084388 | 0.063094 | 0.11398 | 0.0010253 | -0.0037812 | 0.00053404 | -0.058289 | -0.0030506 | 0.061829 | 0.057204 | -0.026791 | 0.0024823 | 0.0056611 | -2.655 | 72.9675 | -49.5758 | 72.7753 | -46.344 | -49.8138 | 1.1856 | -5.1636 | 72.9767 | -49.4797 | 72.8851 | -49.5346 | -49.3011 | -49.0814 | -0.22888 | -0.10071 | -0.29297 | 3.0029 | 50.5325 | -0.46692 | 50.7614 | -0.23804 | -0.13275 | -0.091552 | -0.1831 | -0.18768 | 0.2655 | 0.045777 | 0.39825 | 0.17853 | 3.2318 | 122.3511 | -0.054932 | 122.3648 | 122.5433 | 122.4564 | 122.3145 | 122.3236 | -122.644 | -122.5479 | 122.1222 | 122.2321 | 46.6919 | 44.1834
1857.8281 | 122.5571 | -48.5962 | 73.7915 | -0.11742 | 0.0014847 | 0.062666 | 0.11782 | 0.0012391 | -0.0014312 | -0.00010676 | -0.033874 | -0.0024096 | 0.06546 | 0.057418 | -0.029995 | 0.00013253 | -0.00053411 | -2.6596 | 73.7503 | -48.7701 | 73.6633 | -45.3369 | -48.9166 | 1.2177 | -5.0034 | 73.7366 | -48.674 | 73.764 | -48.4634 | -48.7701 | -48.5138 | -0.17395 | -0.041199 | -0.12817 | 3.2593 | 49.8138 | -0.32044 | 49.9878 | -0.14648 | -0.07782 | -0.054932 | -0.027466 | 0.13275 | 0.082397 | -0.17395 | 0.16022 | -0.096131 | 3.4332 | 122.4335 | 0.21057 | 122.438 | 122.5204 | 122.4106 | 122.3465 | 122.3328 | -122.5616 | -122.4655 | 122.2595 | 122.3602 | 45.9366 | 43.5928
1858.7656 | 122.5937 | -49.6811 | 72.7158 | -0.086899 | -0.0010787 | 0.062239 | 0.11526 | 0.0016663 | -0.0033538 | -0.0058746 | -0.033874 | -0.0017688 | 0.065033 | 0.06169 | -0.025936 | -0.00029487 | -0.00074771 | -2.7466 | 72.6334 | -49.9283 | 72.4503 | -46.5408 | -50.1297 | 1.0162 | -5.5481 | 72.6425 | -49.8138 | 72.6654 | -49.5483 | -49.8642 | -49.5987 | -0.24719 | -0.082397 | -0.2655 | 3.1403 | 50.6973 | -0.44861 | 50.9445 | -0.20142 | -0.13275 | -0.073242 | -0.050354 | 0.13275 | 0.082397 | -0.18311 | 0.21515 | -0.050354 | 3.3875 | 122.3785 | 0.2655 | 122.4792 | 122.5616 | 122.4564 | 122.3145 | 122.3236 | -122.644 | -122.5296 | 122.1313 | 122.3465 | 46.9345 | 44.133
1859.8281 | 122.6807 | -49.5667 | 72.7524 | -0.11742 | 0.0012711 | 0.063094 | 0.11611 | 0.0016663 | -0.0014312 | -0.005661 | 0.018005 | -0.002196 | 0.065033 | 0.061049 | -0.027645 | 0.0012005 | 0.0028839 | -2.7878 | 72.7295 | -49.6994 | 72.7341 | -46.3486 | -49.8184 | 1.0986 | -5.7083 | 72.6974 | -49.6536 | 72.8256 | -49.3332 | -49.5987 | -49.3973 | -0.13275 | -0.022888 | -0.01831 | 3.2181 | 50.6653 | -0.25177 | 50.798 | -0.11902 | -0.086975 | -0.054931 | 0.073243 | 0.23346 | 0.16937 | -0.032044 | 0.25635 | 0.054931 | 3.3508 | 122.4335 | 0.32043 | 122.4792 | 122.4289 | 122.3511 | 122.2961 | 122.2641 | -122.4518 | -122.406 | 122.3007 | 122.3923 | 46.7789 | 43.8583
1860.7656 | 122.6761 | -49.3378 | 72.9904 | -0.16319 | 0.0016983 | 0.062666 | 0.11206 | 0.00081172 | -0.0018586 | -0.0016022 | -0.0033568 | -0.0024096 | 0.064179 | 0.060622 | -0.028286 | 0.0016277 | 0.0033111 | -2.8702 | 72.7936 | -49.6628 | 72.8897 | -45.9641 | -49.6902 | 1.2726 | -5.4886 | 72.8348 | -49.498 | 73.0316 | -49.1501 | -49.4156 | -49.1867 | -0.32501 | -0.19684 | -0.10071 | 3.3737 | 50.6104 | -0.35248 | 50.9354 | -0.027466 | -0.16022 | -0.15564 | 0.041199 | 0.18768 | 0.15106 | -0.077819 | 0.31128 | 0.082398 | 3.6987 | 122.5525 | 0.3479 | 122.5296 | 122.4564 | 122.3328 | 122.1313 | 122.1725 | -122.6532 | -122.4884 | 122.2275 | 122.3694 | 46.4676 | 43.8492
1861.8281 | 122.6852 | -48.4222 | 73.9197 | -0.086899 | 0.0031937 | 0.062666 | 0.11355 | 0.0010253 | -0.002713 | -0.0048066 | -0.00030524 | -0.0060412 | 0.063538 | 0.065322 | -0.027004 | 0.00098693 | 0.00053409 | -2.6047 | 73.7686 | -48.7061 | 73.7549 | -44.9387 | -48.793 | 1.4282 | -5.1773 | 73.7823 | -48.5413 | 73.9838 | -48.23 | -48.5001 | -48.2529 | -0.28381 | -0.15106 | -0.16479 | 3.4836 | 49.8505 | -0.37079 | 50.1343 | -0.086975 | -0.11902 | -0.13733 | 0.064087 | 0.19226 | 0.16937 | -0.07782 | 0.28839 | 0.041199 | 3.7674 | 122.4609 | 0.31128 | 122.525 | 122.4747 | 122.3236 | 122.1909 | 122.2046 | -122.6257 | -122.4609 | 122.1771 | 122.406 | 45.8176 | 43.2449
1862.7656 | 122.5845 | -49.8322 | 72.5876 | -0.094528 | -0.00043792 | 0.061812 | 0.11782 | -4.2682e-05 | -0.0029266 | -0.0030976 | -0.088806 | -0.0024096 | 0.064179 | 0.067244 | -0.027218 | 0.0014141 | 0.0041657 | -2.8931 | 72.5143 | -50.0519 | 72.3038 | -46.7011 | -50.1251 | 1.2085 | -5.603 | 72.5693 | -49.8825 | 72.5327 | -49.7086 | -50.0015 | -49.7406 | -0.21973 | -0.073242 | -0.28381 | 3.1311 | 51.0406 | -0.29297 | 51.2604 | -0.073242 | -0.050354 | -0.01831 | -0.054931 | 0.1236 | 0.091552 | -0.16937 | 0.14191 | -0.11902 | 3.3508 | 122.3557 | 0.17395 | 122.4152 | 122.5662 | 122.4518 | 122.3465 | 122.4014 | -122.6395 | -122.4701 | 122.1359 | 122.3648 | 46.9391 | 44.2291
1863.8281 | 122.6624 | -48.7473 | 73.6176 | -0.07164 | 0.0021255 | 0.062453 | 0.11483 | -0.0043151 | -0.001004 | -0.003952 | 0.057678 | -0.0034778 | 0.063751 | 0.056563 | -0.028286 | 0.00098693 | 0.0028839 | -2.6642 | 73.6725 | -48.8022 | 73.6633 | -45.1355 | -48.9166 | 1.5747 | -6.5277 | 73.6038 | -48.7335 | 73.5901 | -48.5687 | -48.8525 | -48.6328 | -0.054932 | 0.054931 | 0.045776 | 3.6118 | 50.322 | -0.16937 | 50.3769 | -0.11444 | 0.013732 | -0.013733 | -0.027466 | 0.17853 | 0.11444 | -0.10529 | 0.10071 | -0.11902 | 3.6667 | 122.4655 | 0.1648 | 122.3236 | 122.4747 | 122.3373 | 122.4197 | 122.3511 | -122.4197 | -122.3511 | 122.4106 | 122.3373 | 46.0831 | 42.2195
1864.7656 | 122.6303 | -48.4085 | 73.9105 | -0.11742 | 0.0010575 | 0.061385 | 0.11547 | 0.0031617 | -0.0029266 | -0.0024566 | -0.012512 | -0.0034778 | 0.06482 | 0.059554 | -0.027645 | 0.00098693 | -0.00010671 | -2.4948 | 73.9243 | -48.5321 | 73.9471 | -44.371 | -48.5458 | 1.6434 | -7.3425 | 73.9105 | -48.4085 | 74.025 | -48.1842 | -48.4909 | -48.3032 | -0.1236 | 0.013733 | 0.036622 | 4.0375 | 50.0519 | -0.13733 | 50.1755 | -0.013733 | 0 | 0 | 0.11444 | 0.2243 | 0.10528 | -0.082398 | 0.10528 | -0.082398 | 4.1611 | 122.4792 | 0.2243 | 122.4335 | 122.4564 | 122.319 | 122.3328 | 122.319 | -122.4426 | -122.319 | 122.3557 | 122.4335 | 45.9137 | 41.066
1865.8281 | 122.6303 | -49.1867 | 73.1506 | -0.13267 | 0.0016983 | 0.060744 | 0.11419 | -0.0011109 | -0.0031402 | -0.0018158 | -0.076599 | -0.0030506 | 0.062683 | 0.064681 | -0.029568 | 0.0024823 | 0.0024567 | -2.7283 | 73.2422 | -49.2508 | 73.1094 | -45.5978 | -49.4934 | 1.3641 | -6.1752 | 73.1827 | -49.2096 | 73.2651 | -48.9624 | -49.2371 | -49.054 | -0.064086 | 0.091552 | -0.041199 | 3.5889 | 50.5508 | -0.3067 | 50.6149 | -0.24262 | -0.022888 | 0.032043 | 0.11444 | 0.22431 | 0.13275 | -0.050354 | 0.15564 | -0.027466 | 3.653 | 122.3602 | 0.24719 | 122.4747 | 122.493 | 122.3923 | 122.4289 | 122.3694 | -122.4014 | -122.3602 | 122.2961 | 122.4518 | 46.4584 | 43.0115
1866.7656 | 122.612 | -49.5758 | 72.8302 | -0.11742 | -0.0010787 | 0.061598 | 0.11505 | 0.0029479 | -0.004422 | 0.00053404 | -0.079651 | -0.0041186 | 0.063111 | 0.064681 | -0.027645 | -0.0017901 | -0.0026703 | -2.8336 | 72.8714 | -49.7131 | 72.6746 | -46.3943 | -49.9329 | 1.2909 | -8.5739 | 72.7386 | -49.6674 | 72.7936 | -49.4247 | -49.736 | -49.4843 | -0.13733 | 0.041199 | -0.15564 | 3.1815 | 50.8667 | -0.35706 | 51.004 | -0.21973 | -0.091552 | -0.091553 | -0.036621 | 0.15106 | 0.091553 | -0.16022 | 0.1831 | -0.068665 | 3.3188 | 122.3877 | 0.24261 | 122.4609 | 122.5845 | 122.406 | 122.4472 | 122.3145 | -122.5433 | -122.4976 | 122.2504 | 122.3694 | 46.7422 | 41.0019
1867.8281 | 122.5342 | -49.498 | 72.9172 | -0.16319 | 0.0010575 | 0.061598 | 0.11505 | -0.00046988 | -0.0033538 | 0.0041656 | -0.097961 | -0.0026232 | 0.063324 | 0.058486 | -0.025722 | 0.0016277 | 0.0020295 | -2.7649 | 72.8668 | -49.6857 | 72.6837 | -46.1975 | -49.7543 | 1.5976 | -6.4453 | 72.8806 | -49.5575 | 72.8622 | -49.3332 | -49.6719 | -49.4156 | -0.18768 | -0.050354 | -0.23346 | 3.3005 | 51.0956 | -0.25635 | 51.2833 | -0.068664 | -0.059509 | -0.036621 | -0.054931 | 0.16479 | 0.082398 | -0.17395 | 0.14191 | -0.11444 | 3.4882 | 122.3694 | 0.2243 | 122.4197 | 122.5525 | 122.438 | 122.3648 | 122.3785 | -122.6028 | -122.4747 | 122.1817 | 122.3602 | 46.7331 | 43.0527
1868.7656 | 122.5845 | -50.4776 | 71.9055 | -0.10979 | -0.00022432 | 0.062239 | 0.11526 | 0.00081172 | -0.0048492 | -0.001175 | -0.058289 | -0.0036914 | 0.06247 | 0.059127 | -0.026363 | 0.0018413 | -0.00010671 | -2.9526 | 71.9055 | -50.6241 | 71.7865 | -47.8546 | -50.7889 | 1.2131 | -8.8486 | 71.8964 | -50.528 | 71.8872 | -50.3082 | -50.6561 | -50.386 | -0.14648 | 0 | -0.11902 | 2.623 | 51.6907 | -0.31128 | 51.8372 | -0.16479 | -0.050354 | -0.009156 | -0.018311 | 0.16937 | 0.091553 | -0.17853 | 0.14191 | -0.12817 | 2.7695 | 122.4106 | 0.21973 | 122.4152 | 122.5296 | 122.4243 | 122.3831 | 122.374 | -122.5296 | -122.4335 | 122.2641 | 122.3648 | 47.525 | 41.629
1869.8281 | 122.6944 | -51.7181 | 70.5597 | -0.15556 | 0.00084388 | 0.062453 | 0.11483 | 0.0016663 | -0.0035674 | -0.004593 | 0.011902 | -0.0036914 | 0.063538 | 0.056563 | -0.027218 | 0.0016277 | 0.0028839 | -3.035 | 70.6238 | -51.8555 | 70.8023 | -49.2279 | -52.0981 | 1.1169 | -7.6355 | 70.491 | -51.8738 | 70.7062 | -51.4664 | -51.7548 | -51.5213 | -0.13733 | 0.064087 | 0.24262 | 2.4902 | 52.8351 | -0.37994 | 52.9724 | -0.24261 | -0.15564 | -0.068664 | 0.14648 | 0.25177 | 0.19684 | -0.036621 | 0.35248 | 0.11902 | 2.6276 | 122.6578 | 0.40741 | 122.58 | 122.4792 | 122.3648 | 122.3419 | 122.2092 | -122.4152 | -122.4335 | 122.5204 | 122.4243 | 48.6832 | 44.0826
1870.7656 | 122.6624 | -51.86 | 70.5322 | -0.1403 | 0.00041648 | 0.061812 | 0.11633 | 0.0040161 | -0.0001496 | -0.0024566 | -0.049133 | -0.0030506 | 0.063538 | 0.059981 | -0.02615 | 0.0024823 | -0.0016021 | -3.1174 | 70.1569 | -52.3956 | 69.9921 | -49.9558 | -52.597 | 1.0986 | -7.6813 | 70.1111 | -52.2629 | 70.5734 | -51.6129 | -51.8967 | -51.6861 | -0.53558 | -0.37537 | -0.54016 | 1.9043 | 52.9587 | -0.737 | 53.4943 | -0.20142 | -0.40283 | -0.42114 | 0.041198 | 0.24719 | 0.17395 | -0.036621 | 0.57678 | 0.36621 | 2.4399 | 122.3877 | 0.65002 | 122.8363 | 122.5525 | 122.374 | 122.0169 | 121.9711 | -122.9279 | -122.7951 | 121.8521 | 122.4335 | 48.7427 | 44.1788
1871.8281 | 122.6715 | -51.1597 | 71.2006 | -0.12505 | -1.0718e-05 | 0.063094 | 0.11633 | 0.00038452 | -0.0029266 | -0.0041656 | 0.06073 | -0.0032642 | 0.062683 | 0.060195 | -0.028072 | -8.1274e-05 | 0.0028839 | -2.8976 | 71.0678 | -51.4023 | 71.077 | -48.5733 | -51.6815 | 1.1719 | -5.7266 | 71.0587 | -51.2466 | 71.2418 | -50.9125 | -51.2558 | -50.9903 | -0.24261 | -0.13275 | -0.1236 | 2.5864 | 52.3315 | -0.52185 | 52.5742 | -0.27924 | -0.086975 | -0.14191 | 0.041198 | 0.24719 | 0.16937 | -0.09613 | 0.25635 | -0.009155 | 2.829 | 122.4792 | 0.33417 | 122.4884 | 122.4701 | 122.3053 | 122.2275 | 122.2183 | -122.6028 | -122.4472 | 122.2366 | 122.4014 | 48.262 | 45.433
1872.7656 | 122.6761 | -51.6357 | 70.6741 | -0.094528 | 0.0010575 | 0.062666 | 0.11718 | 0.00081172 | 0.0011322 | 0.00032044 | -0.046081 | -0.0028368 | 0.062042 | 0.060195 | -0.027645 | 0.0014141 | 0.0024567 | -2.774 | 70.6741 | -51.8234 | 70.697 | -48.9487 | -51.8738 | 1.268 | -5.1498 | 70.6833 | -51.6632 | 70.7977 | -51.3702 | -51.86 | -51.6586 | -0.18768 | 0 | 0.022888 | 2.6871 | 52.9037 | -0.23804 | 53.0914 | -0.050354 | -0.027466 | 0.009156 | 0.1236 | 0.2655 | -0.022888 | -0.2243 | 0.004578 | -0.19684 | 2.8748 | 122.5204 | 0.29297 | 122.4609 | 122.4976 | 122.3465 | 122.3099 | 122.319 | -122.4976 | -122.3373 | 122.3328 | 122.4335 | 48.8617 | 46.4859
1873.8281 | 122.6715 | -50.853 | 71.4752 | -0.13267 | 0.00020288 | 0.063307 | 0.11334 | 0.0038025 | -0.001004 | -0.0033112 | -0.055237 | -0.0051868 | 0.062897 | 0.061263 | -0.027645 | 0.0018413 | 0.0063019 | -2.7832 | 71.489 | -50.9903 | 71.4981 | -48.0881 | -51.1002 | 1.2268 | -5.1041 | 71.4661 | -50.8667 | 71.5256 | -50.6332 | -50.9354 | -50.7248 | -0.13733 | 0.013733 | 0.022888 | 2.7649 | 52.0798 | -0.24719 | 52.2171 | -0.10986 | -0.013733 | -0.009156 | 0.050354 | 0.21973 | 0.12817 | -0.082398 | 0.14191 | -0.068665 | 2.9022 | 122.4884 | 0.23346 | 122.3923 | 122.4792 | 122.3328 | 122.3419 | 122.319 | -122.4655 | -122.3419 | 122.3511 | 122.3785 | 48.0698 | 45.7489
1874.7656 | 122.6212 | -51.1551 | 71.2326 | -0.10216 | -0.0010787 | 0.061598 | 0.11547 | 0.0038025 | -0.001004 | -0.0030976 | -0.064392 | -0.0036914 | 0.063751 | 0.063399 | -0.025722 | 0.00077333 | 0.0011749 | -3.0167 | 71.2326 | -51.3153 | 71.0999 | -48.5001 | -51.4481 | 1.1627 | -5.246 | 71.2555 | -51.2054 | 71.2326 | -50.9583 | -51.2787 | -51.0544 | -0.16022 | 0 | -0.13275 | 2.655 | 52.3178 | -0.29297 | 52.478 | -0.13275 | -0.050354 | 0.022888 | 0 | 0.19684 | 0.10071 | -0.1236 | 0.15106 | -0.073243 | 2.8152 | 122.4152 | 0.24719 | 122.438 | 122.5479 | 122.4609 | 122.3877 | 122.4106 | -122.5479 | -122.438 | 122.2549 | 122.3877 | 48.1384 | 45.9091
1875.8281 | 122.7036 | -50.7889 | 71.5485 | -0.17082 | 0.0029801 | 0.06288 | 0.11526 | -4.2682e-05 | -0.0029266 | -0.00074776 | -0.024719 | -0.0026232 | 0.060974 | 0.06169 | -0.028072 | -0.0015765 | 0.0048065 | -2.8976 | 71.5302 | -50.9216 | 71.5759 | -47.9095 | -51.0178 | 1.3138 | -4.4266 | 71.521 | -50.8026 | 71.7316 | -50.4272 | -50.9216 | -50.6927 | -0.13275 | -0.018311 | 0.027466 | 2.8793 | 52.1027 | -0.22888 | 52.2354 | -0.09613 | -0.013733 | -0.027466 | 0.1831 | 0.36163 | 0.09613 | -0.13275 | 0.10986 | -0.11902 | 3.0121 | 122.4976 | 0.37537 | 122.5342 | 122.4518 | 122.3236 | 122.319 | 122.3099 | -122.4701 | -122.3511 | 122.3648 | 122.5204 | 47.8912 | 46.3623
1876.7656 | 122.6944 | -51.178 | 71.1594 | -0.20134 | -0.0012923 | 0.061171 | 0.11291 | 0.00059812 | -0.004422 | -0.0013886 | -0.052185 | -0.0041186 | 0.063111 | 0.063185 | -0.027431 | 0.0026959 | -0.0011749 | -3.0533 | 71.3104 | -51.2283 | 71.196 | -48.4085 | -51.4206 | 1.2222 | -6.5369 | 71.1868 | -51.1917 | 71.2601 | -50.9216 | -51.2466 | -51.0178 | -0.050354 | 0.15106 | 0.036621 | 2.7695 | 52.4002 | -0.24261 | 52.4506 | -0.19226 | -0.013732 | 0.027466 | 0.10071 | 0.25635 | 0.16022 | -0.068664 | 0.17395 | -0.054932 | 2.8198 | 122.4243 | 0.27008 | 122.4518 | 122.5388 | 122.3785 | 122.4884 | 122.3648 | -122.3877 | -122.3511 | 122.374 | 122.4381 | 48.1247 | 44.6411
1877.8281 | 122.6761 | -50.9125 | 71.402 | -0.14793 | 0.00020288 | 0.066084 | 0.11505 | 0.0029479 | -0.0029266 | 0.00074764 | -0.0064086 | -0.003905 | 0.063111 | 0.057204 | -0.028286 | 0.00098693 | -0.0011749 | -3.0579 | 71.3791 | -51.1047 | 71.3516 | -48.2071 | -51.265 | 1.3367 | -5.9143 | 71.3379 | -50.9995 | 71.4798 | -50.6836 | -50.9995 | -50.766 | -0.19226 | -0.022889 | -0.050354 | 2.7054 | 52.2491 | -0.35248 | 52.4414 | -0.16022 | -0.086975 | -0.064087 | 0.077819 | 0.22888 | 0.14648 | -0.086975 | 0.23346 | 0 | 2.8976 | 122.4564 | 0.31586 | 122.4792 | 122.4838 | 122.3373 | 122.2916 | 122.2504 | -122.5067 | -122.4014 | 122.2641 | 122.3923 | 47.8546 | 44.9982
1878.7656 | 122.6257 | -51.0681 | 71.2555 | -0.086899 | 0.0019119 | 0.062239 | 0.11462 | 0.0016663 | -0.0018586 | -0.003952 | -0.00030524 | -0.0045458 | 0.062256 | 0.053359 | -0.028286 | -8.1274e-05 | -0.00032051 | -3.1219 | 71.1639 | -51.2924 | 71.1044 | -48.4772 | -51.4618 | 1.2177 | -6.2622 | 71.1502 | -51.1963 | 71.3104 | -50.853 | -51.1642 | -50.9399 | -0.2243 | -0.091553 | -0.15106 | 2.5909 | 52.2858 | -0.39368 | 52.5101 | -0.16937 | -0.12817 | -0.10528 | 0.054932 | 0.21515 | 0.12817 | -0.096131 | 0.25635 | 0.032043 | 2.8152 | 122.3969 | 0.34332 | 122.5067 | 122.4564 | 122.3465 | 122.2321 | 122.2183 | -122.5479 | -122.4518 | 122.1725 | 122.3785 | 47.9462 | 44.8059
1879.8281 | 122.6212 | -51.265 | 71.0587 | -0.10216 | 0.0012711 | 0.063734 | 0.11312 | -0.0017517 | -0.0022858 | -0.0058746 | -0.0033568 | -0.0043322 | 0.062897 | 0.056777 | -0.031063 | -0.00029487 | -0.00053411 | -2.9755 | 70.9946 | -51.4755 | 70.9259 | -48.6832 | -51.741 | 1.2131 | -5.9784 | 70.9122 | -51.416 | 71.0495 | -51.1185 | -51.329 | -51.1276 | -0.21057 | -0.064087 | -0.13275 | 2.5818 | 52.478 | -0.47607 | 52.6886 | -0.2655 | -0.15106 | -0.14648 | -0.009155 | 0.14649 | 0.13733 | -0.064087 | 0.28839 | 0.086975 | 2.7924 | 122.4014 | 0.29755 | 122.4655 | 122.4701 | 122.3282 | 122.2595 | 122.1771 | -122.5342 | -122.4747 | 122.1909 | 122.3145 | 48.2895 | 45.2866
1880.7656 | 122.644 | -52.3361 | 70.0012 | -0.11742 | -0.00043792 | 0.061385 | 0.11334 | 0.0020935 | -0.0007904 | -0.0013886 | -0.027771 | -0.0019824 | 0.064392 | 0.059767 | -0.027859 | -0.00029487 | 0.0030975 | -3.0533 | 69.9554 | -52.5421 | 69.9554 | -49.9878 | -52.597 | 1.1398 | -5.191 | 69.96 | -52.3682 | 70.0699 | -52.0889 | -52.4231 | -52.2079 | -0.20599 | -0.045777 | -0.045777 | 2.3483 | 53.476 | -0.26093 | 53.6819 | -0.054932 | -0.032043 | -0.041199 | 0.068664 | 0.24719 | 0.12817 | -0.086975 | 0.16022 | -0.054932 | 2.5543 | 122.4976 | 0.27924 | 122.438 | 122.4976 | 122.3282 | 122.2916 | 122.2961 | -122.5433 | -122.3694 | 122.2916 | 122.406 | 49.2828 | 47.1451
1881.8281 | 122.6303 | -52.3361 | 69.96 | -0.15556 | 0.0019119 | 0.062025 | 0.11697 | -0.0015381 | -0.0020722 | -0.002243 | -0.021667 | -0.003905 | 0.060547 | 0.057204 | -0.0285 | 0.00034613 | -0.00074771 | -3.1586 | 69.9692 | -52.478 | 70.0516 | -49.8459 | -52.6199 | 1.062 | -6.0425 | 69.9371 | -52.4277 | 70.0241 | -52.1164 | -52.4597 | -52.2171 | -0.14191 | 0.009155 | 0.091553 | 2.4902 | 53.3981 | -0.28381 | 53.54 | -0.14191 | -0.091552 | -0.022888 | 0.064087 | 0.21973 | 0.11902 | -0.1236 | 0.21057 | -0.032044 | 2.6321 | 122.5296 | 0.31128 | 122.4518 | 122.4472 | 122.3648 | 122.3053 | 122.2733 | -122.438 | -122.3877 | 122.3877 | 122.3602 | 49.1776 | 46.2936
1882.7656 | 122.6761 | -51.6129 | 70.7108 | -0.13267 | 0.00063028 | 0.062453 | 0.11697 | -4.2682e-05 | -0.0050628 | -0.0020294 | -0.055237 | -0.0026232 | 0.062897 | 0.063185 | -0.029354 | 0.00098693 | 0.0022431 | -2.9388 | 70.7199 | -51.7502 | 70.6879 | -48.8251 | -51.915 | 1.1261 | -5.3329 | 70.5551 | -51.8417 | 70.8206 | -51.3336 | -51.6953 | -51.4526 | -0.13733 | 0.009156 | -0.022888 | 2.7878 | 52.739 | -0.30212 | 52.8763 | -0.16479 | -0.22888 | -0.15564 | 0.10986 | 0.27924 | 0.16022 | -0.082397 | 0.3891 | 0.14648 | 2.9251 | 122.438 | 0.50812 | 122.6624 | 122.4701 | 122.3969 | 122.3328 | 122.168 | -122.4609 | -122.5525 | 122.3007 | 122.4335 | 48.674 | 46.2799
1883.8281 | 122.6486 | -51.8646 | 70.491 | -0.15556 | 0.00084388 | 0.062025 | 0.11462 | -0.00089728 | -0.0007904 | -0.002884 | -0.012512 | -0.0030506 | 0.061829 | 0.055922 | -0.026577 | -0.0015765 | 0.0024567 | -3.0121 | 70.4681 | -51.9699 | 70.4681 | -49.2096 | -52.1576 | 1.4923 | -5.983 | 70.459 | -51.9012 | 70.5185 | -51.6449 | -51.9608 | -51.7227 | -0.10529 | -0.022888 | -0.022888 | 2.655 | 53.3569 | -0.29297 | 53.4622 | -0.18768 | -0.036621 | -0.032044 | 0.027466 | 0.21973 | 0.14191 | -0.09613 | 0.17853 | -0.059509 | 2.7603 | 122.4381 | 0.25635 | 122.4197 | 122.4381 | 122.3602 | 122.3328 | 122.3236 | -122.4609 | -122.3923 | 122.3328 | 122.3831 | 48.8525 | 45.8817
1884.7656 | 122.6852 | -52.1118 | 70.2438 | -0.13267 | -0.00065152 | 0.062025 | 0.11697 | 0.0050843 | -0.002713 | 0.00010684 | -0.079651 | -0.0041186 | 0.061188 | 0.065535 | -0.029568 | 0.0018413 | -0.0016021 | -3.1174 | 70.1385 | -52.359 | 70.1294 | -49.6033 | -52.4323 | 1.4053 | -6.015 | 70.166 | -52.1393 | 70.2438 | -51.9516 | -51.915 | -51.7227 | -0.24719 | -0.10529 | -0.11444 | 2.5085 | 53.5172 | -0.32044 | 53.7643 | -0.073242 | -0.027466 | -0.077819 | 0 | 0.16022 | 0.3891 | 0.19684 | 0.41656 | 0.2243 | 2.7557 | 122.4884 | 0.18768 | 122.3831 | 122.4976 | 122.3053 | 122.2504 | 122.2778 | -122.6028 | -122.3831 | 122.2412 | 122.3557 | 48.9944 | 46.0968
1885.8281 | 122.4884 | -53.064 | 69.3466 | -0.079269 | 0.0014847 | 0.060744 | 0.11868 | 0.0018799 | 6.4004e-05 | -0.002243 | -0.10406 | -0.002196 | 0.063538 | 0.056563 | -0.026577 | 0.0073955 | 0.0035247 | -3.2043 | 69.4199 | -53.1052 | 69.2001 | -51.1322 | -53.4119 | 1.0117 | -6.5231 | 69.3192 | -53.1235 | 69.0353 | -52.7573 | -52.9266 | -52.7664 | -0.041199 | 0.073242 | -0.14648 | 1.9318 | 54.0756 | -0.3479 | 54.1168 | -0.3067 | -0.059509 | -0.027466 | -0.31128 | 0.3067 | 0.29755 | 0.13733 | 0.35706 | 0.19684 | 1.973 | 122.3053 | 0.36621 | 122.1588 | 122.525 | 122.4426 | 122.4838 | 122.3831 | -122.4518 | -122.4701 | 122.2641 | 122.0993 | 49.8596 | 46.5408
1886.7656 | 122.6257 | -53.1509 | 69.1818 | -0.15556 | 0.0023391 | 0.06053 | 0.11398 | 0.0023071 | -0.0018586 | -0.0020294 | -0.021667 | -0.0043322 | 0.064392 | 0.056777 | -0.027218 | 0.00098693 | 0.0026703 | -3.3142 | 69.1544 | -53.3524 | 69.104 | -51.1917 | -53.4897 | 1.1032 | -6.514 | 69.0948 | -53.2425 | 69.2413 | -52.9129 | -53.2059 | -53.0136 | -0.20142 | -0.027466 | -0.07782 | 1.9592 | 54.2541 | -0.33875 | 54.4556 | -0.13733 | -0.091553 | -0.086975 | 0.059509 | 0.23804 | 0.13733 | -0.054932 | 0.22888 | 0.036621 | 2.1606 | 122.4564 | 0.32959 | 122.4838 | 122.5067 | 122.3373 | 122.3053 | 122.2458 | -122.5342 | -122.4243 | 122.2549 | 122.3923 | 49.8367 | 46.637
1887.8281 | 122.6898 | -53.1967 | 69.136 | -0.14793 | 0.00041648 | 0.063094 | 0.11483 | -0.00068368 | -0.0016448 | -0.0024566 | -0.06134 | -0.0019824 | 0.061829 | 0.063613 | -0.027431 | 0.00034613 | 0.00096129 | -3.2547 | 69.1406 | -53.3157 | 69.1269 | -51.1047 | -53.5492 | 1.0483 | -6.1295 | 69.0948 | -53.2425 | 69.2459 | -52.9449 | -53.2562 | -53.0182 | -0.11902 | 0.004578 | -0.009155 | 2.092 | 54.245 | -0.35248 | 54.364 | -0.23346 | -0.045777 | -0.041198 | 0.10986 | 0.25177 | 0.17853 | -0.05951 | 0.22431 | -0.013733 | 2.211 | 122.4426 | 0.29755 | 122.4884 | 122.4564 | 122.3373 | 122.3373 | 122.2916 | -122.4518 | -122.3785 | 122.3236 | 122.4426 | 49.942 | 47.0673
1888.7656 | 122.5708 | -52.6337 | 69.7586 | -0.11742 | -0.0017197 | 0.06053 | 0.11526 | 0.00081172 | -0.0014312 | -0.00010676 | -0.0094604 | -0.0043322 | 0.061615 | 0.059981 | -0.028286 | 0.0029095 | 0.0073701 | -3.1036 | 69.7266 | -52.739 | 69.6716 | -50.2899 | -52.8809 | 1.0986 | -6.1295 | 69.7083 | -52.6932 | 69.7769 | -52.4002 | -52.6978 | -52.4826 | -0.10529 | -0.032044 | -0.086975 | 2.3438 | 53.7323 | -0.24719 | 53.8376 | -0.14191 | -0.059509 | -0.050354 | 0.018311 | 0.23346 | 0.15106 | -0.064087 | 0.21057 | -0.004578 | 2.449 | 122.4106 | 0.29297 | 122.4701 | 122.4655 | 122.4014 | 122.3602 | 122.3419 | -122.4976 | -122.4518 | 122.3053 | 122.4106 | 49.53 | 46.5042
1889.8281 | 122.6624 | -52.3636 | 69.9692 | -0.1403 | 0.00063028 | 0.062025 | 0.11697 | 0.00059812 | -0.0018586 | -0.0033112 | -0.085754 | -0.0032642 | 0.063324 | 0.067885 | -0.029568 | 0.00055973 | 0.0039521 | -3.2547 | 69.9417 | -52.5513 | 69.9051 | -49.9969 | -52.6978 | 1.0117 | -5.8868 | 69.9097 | -52.4506 | 70.0607 | -52.1164 | -52.4323 | -52.1576 | -0.18768 | -0.027466 | -0.064087 | 2.3666 | 53.3752 | -0.33417 | 53.5629 | -0.14648 | -0.086976 | -0.059509 | 0.091553 | 0.24719 | 0.20599 | -0.068665 | 0.29297 | 0.018311 | 2.5543 | 122.4564 | 0.33417 | 122.5113 | 122.493 | 122.3602 | 122.3053 | 122.2733 | -122.5204 | -122.4197 | 122.2687 | 122.4243 | 49.1089 | 46.4767
1890.7656 | 122.6624 | -52.2354 | 70.1157 | -0.10979 | 0.00041648 | 0.064375 | 0.11761 | 0.0018799 | -0.0005768 | -0.0024566 | -0.085754 | -0.0043322 | 0.063324 | 0.056777 | -0.028286 | 0.0020551 | 0.0018159 | -3.2089 | 70.0378 | -52.478 | 69.9921 | -49.8917 | -52.597 | 1.0391 | -5.9189 | 70.0607 | -52.3361 | 70.1523 | -52.002 | -52.327 | -52.0706 | -0.24261 | -0.07782 | -0.1236 | 2.3438 | 53.2745 | -0.36163 | 53.5172 | -0.11902 | -0.10071 | -0.054932 | 0.036621 | 0.23346 | 0.16479 | -0.091552 | 0.2655 | 0.009156 | 2.5864 | 122.4701 | 0.33417 | 122.4884 | 122.5159 | 122.3969 | 122.2733 | 122.2961 | -122.5937 | -122.4518 | 122.2275 | 122.3877 | 49.0265 | 46.3165
1891.8281 | 122.6486 | -52.7847 | 69.548 | -0.16319 | -0.0012923 | 0.064803 | 0.11761 | -0.0017517 | -0.0031402 | -0.00032036 | -0.039978 | -0.0051868 | 0.06247 | 0.05934 | -0.028713 | 0.00077333 | 0.00010689 | -3.1769 | 69.548 | -52.9404 | 69.5251 | -50.5554 | -53.0548 | 1.0712 | -5.7678 | 69.5206 | -52.8397 | 69.6304 | -52.5192 | -52.8397 | -52.6199 | -0.15564 | 0 | -0.022889 | 2.2293 | 53.8559 | -0.27008 | 54.0115 | -0.11444 | -0.054932 | -0.027466 | 0.082397 | 0.2655 | 0.16479 | -0.054932 | 0.21973 | 0 | 2.3849 | 122.4655 | 0.32043 | 122.4701 | 122.4884 | 122.3602 | 122.3328 | 122.3053 | -122.4884 | -122.3877 | 122.3099 | 122.4152 | 49.6078 | 47.0169
1892.7656 | 122.6852 | -52.1118 | 70.2347 | -0.06401 | 0.00063028 | 0.059676 | 0.11312 | -0.0015381 | -0.0031402 | -0.00096136 | -0.085754 | -0.0047594 | 0.062683 | 0.058272 | -0.028713 | 0.0020551 | 0.00053409 | -2.9526 | 70.3491 | -52.1439 | 70.3812 | -48.967 | -51.8097 | 1.1353 | -6.0196 | 70.2621 | -52.1072 | 70.3171 | -51.7914 | -52.1164 | -51.9241 | -0.032044 | 0.11444 | 0.14648 | 3.1448 | 53.2471 | 0.30212 | 53.2791 | 0.33417 | 0.004577 | 0.027466 | 0.082398 | 0.32043 | 0.18768 | -0.004578 | 0.18311 | -0.009155 | 3.1769 | 122.525 | 0.31586 | 122.4243 | 122.493 | 122.3694 | 122.4609 | 122.374 | -122.3785 | -122.3419 | 122.493 | 122.4289 | 49.1592 | 46.0922
1893.8281 | 122.6578 | -52.6337 | 69.6945 | -0.15556 | 0.00020288 | 0.060957 | 0.11398 | -0.0030335 | -0.0007904 | -0.002243 | -0.052185 | -0.0030506 | 0.063538 | 0.058058 | -0.029354 | -0.00072207 | 0.0022431 | -3.0808 | 69.7403 | -52.7161 | 69.6487 | -50.3677 | -52.9678 | 1.062 | -6.1707 | 69.6259 | -52.7069 | 69.7449 | -52.4368 | -52.7344 | -52.4963 | -0.082397 | 0.045776 | -0.045776 | 2.2659 | 53.6957 | -0.33417 | 53.7781 | -0.25177 | -0.073242 | -0.068665 | 0.050354 | 0.19684 | 0.13733 | -0.10071 | 0.21057 | -0.027466 | 2.3483 | 122.3648 | 0.27008 | 122.4518 | 122.4564 | 122.3328 | 122.374 | 122.2595 | -122.4106 | -122.4014 | 122.2824 | 122.3785 | 49.5529 | 46.463
1894.7656 | 122.6303 | -52.2354 | 70.1385 | -0.12505 | 0.0016983 | 0.061812 | 0.11377 | 0.0014527 | -0.0037812 | 0.00032044 | -0.039978 | -0.0043322 | 0.063538 | 0.062545 | -0.027218 | 0.00098693 | 0.0013885 | -2.8656 | 70.015 | -52.4597 | 69.9783 | -49.8825 | -52.6382 | 1.1353 | -6.0562 | 69.96 | -52.3544 | 70.1889 | -51.9791 | -52.2903 | -52.0523 | -0.2243 | -0.1236 | -0.16022 | 2.3529 | 53.3707 | -0.40283 | 53.595 | -0.17853 | -0.11902 | -0.17853 | 0.050354 | 0.25635 | 0.18311 | -0.054931 | 0.30212 | 0.064087 | 2.5772 | 122.4381 | 0.37537 | 122.5433 | 122.4747 | 122.3145 | 122.2504 | 122.1954 | -122.5983 | -122.493 | 122.2137 | 122.4243 | 49.3698 | 46.1792
1895.8281 | 122.6349 | -52.3087 | 70.0378 | -0.1403 | 0.0025529 | 0.062025 | 0.11526 | -0.0017517 | -0.0020722 | 0.00053404 | -0.015564 | -0.0024096 | 0.062897 | 0.063399 | -0.026577 | 0.00055973 | 0.00032049 | -2.98 | 70.0424 | -52.4506 | 69.9783 | -49.8962 | -52.5833 | 1.1261 | -6.1707 | 70.0241 | -52.3636 | 70.1111 | -51.9424 | -52.533 | -52.2766 | -0.14191 | 0.004577 | -0.059509 | 2.4124 | 53.4348 | -0.27466 | 53.5767 | -0.13275 | -0.054931 | -0.013733 | 0.073242 | 0.36621 | 0.032044 | -0.2243 | 0.086975 | -0.16937 | 2.5543 | 122.4289 | 0.42114 | 122.4747 | 122.493 | 122.3877 | 122.3511 | 122.3328 | -122.4884 | -122.4014 | 122.287 | 122.4197 | 49.3286 | 46.138
1896.7656 | 122.5891 | -52.597 | 69.8181 | -0.07164 | 0.00020288 | 0.060957 | 0.11676 | -0.00089728 | -0.0012176 | -0.00010676 | -0.091858 | -0.0019824 | 0.063965 | 0.061476 | -0.028286 | 0.00055973 | 0.00032049 | -3.0899 | 69.6442 | -52.8946 | 69.5206 | -50.5875 | -53.0319 | 1.149 | -6.0287 | 69.6808 | -52.7298 | 69.7495 | -52.4231 | -52.739 | -52.478 | -0.29755 | -0.17395 | -0.29755 | 2.0096 | 53.746 | -0.43487 | 54.0436 | -0.13733 | -0.13275 | -0.13733 | -0.068664 | 0.17395 | 0.11902 | -0.14191 | 0.25177 | -0.009156 | 2.3071 | 122.4152 | 0.3067 | 122.4792 | 122.5388 | 122.4106 | 122.2412 | 122.2778 | -122.7127 | -122.5479 | 122.1176 | 122.3465 | 49.5071 | 46.5683
1897.8281 | 122.7081 | -52.4734 | 69.9142 | -0.10216 | 0.00063028 | 0.060103 | 0.11398 | -0.0030335 | -0.0024994 | -0.00032036 | 0.027161 | -0.0047594 | 0.061402 | 0.060195 | -0.026577 | -0.00050847 | 0.0039521 | -2.9388 | 69.9142 | -52.565 | 69.873 | -50.0656 | -52.6749 | 1.2497 | -5.9601 | 69.8181 | -52.5467 | 69.9692 | -52.1851 | -52.4597 | -52.2858 | -0.091552 | 0 | -0.041199 | 2.4078 | 53.7231 | -0.20142 | 53.8147 | -0.10986 | -0.073242 | -0.096131 | 0.054931 | 0.28839 | 0.18768 | 0.013733 | 0.26093 | 0.086975 | 2.4994 | 122.438 | 0.36163 | 122.5159 | 122.4792 | 122.3648 | 122.3877 | 122.2916 | -122.4792 | -122.4609 | 122.3465 | 122.4426 | 49.5346 | 46.5134
1898.7656 | 122.644 | -52.3361 | 70.0378 | -0.14793 | 0.0019119 | 0.062025 | 0.11419 | 0.00081172 | -0.0031402 | -0.00074776 | -0.079651 | -0.0049732 | 0.061829 | 0.060408 | -0.02914 | 0.00055973 | 0.00053409 | -3.0533 | 70.0104 | -52.4689 | 70.0516 | -49.855 | -52.5696 | 1.3641 | -6.1478 | 69.9875 | -52.4185 | 70.134 | -52.0844 | -52.5421 | -52.3132 | -0.13275 | -0.027466 | 0.013733 | 2.4811 | 53.7003 | -0.23346 | 53.833 | -0.10071 | -0.082397 | -0.050354 | 0.09613 | 0.25177 | 0.022889 | -0.20599 | 0.10529 | -0.1236 | 2.6138 | 122.5204 | 0.33417 | 122.5525 | 122.4792 | 122.406 | 122.3465 | 122.3236 | -122.5067 | -122.4564 | 122.3877 | 122.4701 | 49.2828 | 46.1884
1899.7656 | 122.699 | -52.5192 | 69.8502 | -0.14793 | 0.00063028 | 0.063521 | 0.11676 | 0.0010253 | -0.0035674 | 0.00074764 | -0.091858 | -0.0032642 | 0.063751 | 0.064894 | -0.028713 | 0.00098693 | -0.00053411 | -3.0716 | 69.7678 | -52.7252 | 69.754 | -50.1801 | -52.8442 | 1.0803 | -6.0608 | 69.7723 | -52.6016 | 69.9463 | -52.2354 | -52.5696 | -52.2766 | -0.20599 | -0.082398 | -0.096131 | 2.3392 | 53.5995 | -0.32501 | 53.8055 | -0.11902 | -0.082398 | -0.07782 | 0.09613 | 0.28381 | 0.24262 | -0.050354 | 0.32501 | 0.032044 | 2.5452 | 122.4792 | 0.36621 | 122.5479 | 122.493 | 122.374 | 122.287 | 122.2916 | -122.5754 | -122.4518 | 122.2733 | 122.4655 | 49.4476 | 46.4584
1900.7656 | 122.6349 | -52.6291 | 69.7174 | -0.14793 | 0.00063028 | 0.060316 | 0.11462 | -0.0013245 | -0.0035674 | -0.0020294 | -0.018616 | -0.0058276 | 0.06247 | 0.060408 | -0.026791 | 0.00055973 | 0.0026703 | -3.0396 | 69.6899 | -52.7939 | 69.635 | -50.473 | -52.9541 | 1.1215 | -6.0883 | 69.6671 | -52.6932 | 69.7678 | -52.3773 | -52.7115 | -52.5192 | -0.16479 | -0.027466 | -0.082397 | 2.1561 | 53.7506 | -0.32501 | 53.9154 | -0.16022 | -0.064087 | -0.050354 | 0.050354 | 0.25177 | 0.10986 | -0.082398 | 0.17395 | -0.018311 | 2.3209 | 122.4289 | 0.31586 | 122.4609 | 122.4838 | 122.3602 | 122.319 | 122.2961 | -122.5113 | -122.4106 | 122.2641 | 122.3969 | 49.5895 | 46.5408
1901.8281 | 122.6028 | -52.89 | 69.4885 | -0.12505 | 0.0012711 | 0.062025 | 0.11782 | -0.0015381 | -0.0029266 | -0.0020294 | -0.11932 | -0.0015552 | 0.060761 | 0.062758 | -0.028286 | -0.00029487 | 0.0033111 | -3.1494 | 69.4748 | -53.0823 | 69.3237 | -50.8896 | -53.2516 | 1.03 | -6.1981 | 69.4519 | -52.9678 | 69.4977 | -52.6978 | -53.0182 | -52.7344 | -0.19226 | -0.013733 | -0.16479 | 2.0004 | 53.92 | -0.36163 | 54.1122 | -0.16937 | -0.077819 | -0.036621 | 0.009156 | 0.19226 | 0.15564 | -0.12817 | 0.23346 | -0.050354 | 2.1927 | 122.406 | 0.27008 | 122.4655 | 122.5571 | 122.4197 | 122.3648 | 122.3419 | -122.5708 | -122.4564 | 122.2137 | 122.3877 | 49.7406 | 46.6919
1902.7656 | 122.6715 | -52.6154 | 69.7174 | -0.079269 | 0.00020288 | 0.059462 | 0.11227 | 0.0046569 | -0.0005768 | -0.0016022 | 0.0057984 | -0.0043322 | 0.063111 | 0.058058 | -0.026791 | 0.0016277 | -0.00053411 | -3.0853 | 69.6991 | -52.7939 | 69.5892 | -50.3677 | -52.9449 | 1.1124 | -6.3721 | 69.635 | -52.7115 | 69.7815 | -52.3453 | -52.6749 | -52.478 | -0.17853 | -0.01831 | -0.12817 | 2.2476 | 53.7277 | -0.32959 | 53.9062 | -0.15106 | -0.096131 | -0.082397 | 0.064087 | 0.27008 | 0.13733 | -0.05951 | 0.23346 | 0.036621 | 2.4261 | 122.3831 | 0.36621 | 122.493 | 122.493 | 122.3465 | 122.3145 | 122.2504 | -122.5113 | -122.4289 | 122.2046 | 122.3969 | 49.53 | 46.2433
1903.8281 | 122.7081 | -52.5192 | 69.8639 | -0.10216 | 0.0010575 | 0.061812 | 0.11483 | 0.0025207 | -0.0033538 | -0.0024566 | -0.0094604 | -0.0024096 | 0.063751 | 0.05699 | -0.029354 | -0.00029487 | -0.0022431 | -3.1494 | 69.7769 | -52.7115 | 69.7586 | -50.2533 | -52.7618 | 1.5427 | -6.2393 | 69.7403 | -52.6108 | 69.9234 | -52.1896 | -52.5101 | -52.2949 | -0.19226 | -0.086975 | -0.10529 | 2.2659 | 54.0619 | -0.24261 | 54.2542 | -0.050354 | -0.091553 | -0.1236 | 0.059509 | 0.32959 | 0.2243 | 0.009155 | 0.31586 | 0.10071 | 2.4582 | 122.4701 | 0.42114 | 122.5342 | 122.4884 | 122.3511 | 122.2961 | 122.2595 | -122.5754 | -122.4747 | 122.2778 | 122.4426 | 49.3698 | 46.2799
1904.7656 | 122.5937 | -52.5513 | 69.841 | -0.06401 | 0.0016983 | 0.061385 | 0.11761 | 0.0048705 | -0.0012176 | -0.0018158 | -0.11017 | -0.0045458 | 0.063111 | 0.061263 | -0.027218 | 0.00034613 | 0.0035247 | -3.3005 | 69.8593 | -52.7161 | 69.6625 | -50.4593 | -52.9175 | 1.2589 | -6.7978 | 69.7678 | -52.6382 | 69.8227 | -52.3773 | -52.6932 | -52.4277 | -0.16479 | 0.018311 | -0.17853 | 2.092 | 53.8101 | -0.36621 | 53.9749 | -0.20142 | -0.086975 | -0.073242 | -0.01831 | 0.17395 | 0.1236 | -0.14191 | 0.21057 | -0.054931 | 2.2568 | 122.3785 | 0.26093 | 122.4609 | 122.5754 | 122.406 | 122.4106 | 122.319 | -122.5571 | -122.4792 | 122.2137 | 122.374 | 49.2508 | 45.7535
1905.9062 | 122.5571 | -52.9358 | 69.4931 | -0.056381 | -0.0015061 | 0.059462 | 0.11547 | 0.0014527 | -0.0042084 | -0.0024566 | -0.070496 | -0.0024096 | 0.062256 | 0.06169 | -0.026363 | 0.00098693 | 0.0022431 | -3.392 | 69.5526 | -53.0228 | 69.3787 | -50.7935 | -53.1876 | 0.99335 | -6.5323 | 69.429 | -52.9816 | 69.4382 | -52.7435 | -53.0457 | -52.8214 | -0.086975 | 0.059509 | -0.11444 | 2.1423 | 53.9291 | -0.25177 | 54.0161 | -0.1648 | -0.045776 | -0.064087 | -0.054932 | 0.19226 | 0.11444 | -0.10986 | 0.16022 | -0.064087 | 2.2293 | 122.4014 | 0.23804 | 122.4197 | 122.5754 | 122.4106 | 122.4884 | 122.3648 | -122.5159 | -122.4747 | 122.3145 | 122.374 | 49.5438 | 46.4035
1906.7656 | 122.6715 | -52.7069 | 69.635 | -0.13267 | 0.00084388 | 0.062239 | 0.11547 | 0.0016663 | 6.4004e-05 | -0.00096136 | 0.033264 | -0.0036914 | 0.065033 | 0.051863 | -0.027218 | 0.0035503 | 0.0041657 | -3.3279 | 69.6579 | -52.8397 | 69.6625 | -50.5417 | -53.2928 | 1.0849 | -6.5552 | 69.6304 | -52.7298 | 69.6991 | -52.478 | -52.7802 | -52.5192 | -0.13275 | 0.022888 | 0.027466 | 2.1652 | 53.7918 | -0.58594 | 53.9246 | -0.45319 | -0.022888 | -0.004578 | 0.064087 | 0.22888 | 0.18768 | -0.073242 | 0.21057 | -0.050354 | 2.298 | 122.5021 | 0.25177 | 122.4289 | 122.4976 | 122.3602 | 122.3648 | 122.3373 | -122.4747 | -122.3648 | 122.3694 | 122.406 | 49.379 | 46.1517
1907.8281 | 122.6761 | -52.6428 | 69.6945 | -0.10979 | 0.00063028 | 0.061598 | 0.11398 | -0.00089728 | -0.0016448 | -0.0020294 | 0.014954 | -0.0032642 | 0.061402 | 0.056777 | -0.027218 | -8.1274e-05 | 0.00096129 | -3.4195 | 69.6808 | -52.7802 | 69.6671 | -50.4181 | -52.9221 | 1.0986 | -6.3995 | 69.6487 | -52.7023 | 69.7403 | -52.3773 | -52.6611 | -52.4734 | -0.13733 | -0.013733 | -0.027466 | 2.2247 | 53.7415 | -0.27924 | 53.8788 | -0.14191 | -0.05951 | -0.045776 | 0.045776 | 0.2655 | 0.16937 | -0.018311 | 0.22888 | 0.041199 | 2.3621 | 122.4472 | 0.32501 | 122.4426 | 122.4609 | 122.3511 | 122.3236 | 122.2916 | -122.4747 | -122.3969 | 122.3099 | 122.3831 | 49.2233 | 46.2433
1908.7656 | 122.6257 | -52.153 | 70.2347 | -0.13267 | -1.0718e-05 | 0.060744 | 0.11419 | 0.0012391 | -0.0031402 | -0.0030976 | -0.018616 | -0.0041186 | 0.061615 | 0.051863 | -0.027004 | 0.00034613 | 0.00096129 | -3.3508 | 70.2759 | -52.1896 | 70.1797 | -49.7452 | -52.4323 | 1.0849 | -7.2739 | 70.1752 | -52.2171 | 70.2393 | -51.9058 | -52.2079 | -51.9791 | -0.036621 | 0.041199 | -0.054931 | 2.4078 | 53.2379 | -0.27924 | 53.2745 | -0.24262 | -0.064087 | -0.059509 | 0.004578 | 0.24719 | 0.17395 | -0.054932 | 0.23804 | 0.009155 | 2.4445 | 122.3694 | 0.31128 | 122.4564 | 122.4655 | 122.3923 | 122.4289 | 122.3282 | -122.4243 | -122.4518 | 122.3328 | 122.3923 | 48.8022 | 44.8792
1909.8281 | 122.5571 | -52.2995 | 70.1569 | -0.14793 | 0.0019119 | 0.062666 | 0.11654 | 0.0018799 | -0.0022858 | -0.002884 | -0.018616 | -0.00048703 | 0.063965 | 0.066817 | -0.0285 | 0.0024823 | -0.00032051 | -3.5477 | 70.079 | -52.4872 | 69.9371 | -50.3815 | -53.0411 | 1.0757 | -7.1365 | 70.0562 | -52.4048 | 70.1019 | -52.1255 | -52.4551 | -52.153 | -0.18768 | -0.077819 | -0.21973 | 1.918 | 53.3752 | -0.74158 | 53.5629 | -0.55389 | -0.10528 | -0.10071 | -0.054931 | 0.17395 | 0.14648 | -0.15564 | 0.25177 | -0.050354 | 2.1057 | 122.4243 | 0.27924 | 122.5067 | 122.5662 | 122.4609 | 122.3785 | 122.3557 | -122.644 | -122.5616 | 122.2366 | 122.4014 | 48.7518 | 45.163
1910.7969 | 122.699 | -51.9745 | 70.372 | -0.13267 | -0.00022432 | 0.061812 | 0.11654 | 0.0040161 | -0.0037812 | -0.0018158 | -0.058289 | -0.0026232 | 0.063111 | 0.059554 | -0.028286 | 0.0022687 | 0.0043793 | -3.4149 | 70.3583 | -52.1301 | 70.3812 | -49.5483 | -52.2217 | 1.2085 | -6.9305 | 70.2805 | -52.0477 | 70.372 | -51.9241 | -51.8463 | -51.6403 | -0.15564 | -0.013733 | 0.009156 | 2.4261 | 53.183 | -0.24719 | 53.3386 | -0.091553 | -0.073242 | -0.091552 | 0 | 0.050354 | 0.33417 | 0.12817 | 0.40741 | 0.20142 | 2.5818 | 122.5113 | 0.1236 | 122.4197 | 122.4884 | 122.3282 | 122.3328 | 122.2549 | -122.5021 | -122.4197 | 122.3557 | 122.3465 | 48.5596 | 45.0439
1911.8281 | 122.6166 | -52.2034 | 70.1843 | -0.14793 | 0.0019119 | 0.061598 | 0.11526 | 0.00059812 | -0.0020722 | -0.0016022 | -0.039978 | -0.0058276 | 0.06247 | 0.058272 | -0.025936 | 0.00077333 | 0.0028839 | -3.392 | 70.1019 | -52.3682 | 70.134 | -49.7543 | -52.4643 | 1.3504 | -6.7841 | 70.1065 | -52.2583 | 70.2393 | -51.9653 | -52.2537 | -52.0477 | -0.16479 | -0.082397 | -0.050354 | 2.449 | 53.5538 | -0.26093 | 53.7186 | -0.09613 | -0.054932 | -0.07782 | 0.054932 | 0.23804 | 0.15564 | -0.050354 | 0.21057 | 0.004578 | 2.6138 | 122.5021 | 0.29297 | 122.4976 | 122.4701 | 122.3648 | 122.3053 | 122.3099 | -122.5525 | -122.4426 | 122.3373 | 122.4426 | 48.8113 | 45.4193
1912.7656 | 122.6761 | -52.1255 | 70.1752 | -0.17082 | 0.0016983 | 0.061171 | 0.11633 | 0.0074341 | -0.0007904 | 0.00096124 | -0.04303 | -0.0041186 | 0.06012 | 0.05699 | -0.02914 | 0.00077333 | 0.00074769 | -3.4287 | 70.0333 | -52.3956 | 70.0928 | -49.6948 | -52.5101 | 1.1856 | -5.3329 | 70.0195 | -52.2903 | 70.285 | -51.8692 | -52.1942 | -51.9608 | -0.27008 | -0.14191 | -0.082398 | 2.4307 | 53.3112 | -0.38452 | 53.5812 | -0.11444 | -0.16479 | -0.15564 | 0.10986 | 0.25635 | 0.16479 | -0.068665 | 0.32959 | 0.09613 | 2.7008 | 122.4884 | 0.42114 | 122.5754 | 122.4289 | 122.3099 | 122.1588 | 122.1451 | -122.5708 | -122.4655 | 122.2183 | 122.4106 | 48.6969 | 46.7926
1913.8281 | 122.6578 | -52.5101 | 69.8914 | -0.14793 | 0.0010575 | 0.062453 | 0.1159 | 0.00059812 | -0.0050628 | -0.0018158 | -0.00030524 | -0.0030506 | 0.063538 | 0.059554 | -0.0285 | -0.00050847 | 0.0024567 | -3.6896 | 69.9371 | -52.5284 | 69.8776 | -50.0931 | -52.7161 | 1.0803 | -5.5801 | 69.873 | -52.4826 | 69.9326 | -52.2446 | -52.5787 | -52.3636 | -0.01831 | 0.045777 | -0.013732 | 2.417 | 53.5904 | -0.20599 | 53.6087 | -0.18768 | 0.027466 | -0.01831 | 0.041199 | 0.2655 | 0.14649 | -0.068664 | 0.11902 | -0.09613 | 2.4353 | 122.406 | 0.23804 | 122.4152 | 122.4655 | 122.3557 | 122.4472 | 122.3831 | -122.4197 | -122.374 | 122.3877 | 122.4426 | 48.8205 | 46.9299
1914.7656 | 122.6486 | -52.4918 | 69.8318 | -0.20897 | 0.0010575 | 0.062239 | 0.11633 | 0.00081172 | -0.0020722 | -0.00074776 | -0.073547 | -0.0028368 | 0.063111 | 0.059767 | -0.027004 | 0.0016277 | -0.0028839 | -3.5614 | 69.7769 | -52.684 | 69.809 | -50.2441 | -52.739 | 0.88348 | -6.6422 | 69.754 | -52.597 | 69.9142 | -52.2446 | -52.5558 | -52.327 | -0.19226 | -0.054931 | -0.022888 | 2.2476 | 53.3752 | -0.24719 | 53.5675 | -0.054932 | -0.10529 | -0.07782 | 0.082398 | 0.24719 | 0.16479 | -0.064087 | 0.27008 | 0.041199 | 2.4399 | 122.493 | 0.35248 | 122.5113 | 122.4609 | 122.3511 | 122.2687 | 122.2458 | -122.5159 | -122.4289 | 122.3007 | 122.406 | 48.9304 | 45.8496
1915.8281 | 122.6532 | -52.2079 | 70.134 | -0.16319 | -0.00065152 | 0.06288 | 0.1159 | -0.00025628 | -0.0022858 | -0.00074776 | -0.046081 | -0.0045458 | 0.064179 | 0.061049 | -0.026363 | 0.00077333 | 0.00053409 | -3.4836 | 70.2301 | -52.2629 | 70.1889 | -49.7543 | -52.4048 | 1.1169 | -6.3126 | 70.1981 | -52.1622 | 70.2072 | -51.9791 | -52.2949 | -52.0798 | -0.054931 | 0.096131 | 0.054932 | 2.4536 | 53.3249 | -0.19684 | 53.3798 | -0.14191 | 0.045777 | 0.064087 | 0.073242 | 0.22888 | 0.12817 | -0.086975 | 0.082397 | -0.13275 | 2.5085 | 122.4518 | 0.18311 | 122.3694 | 122.493 | 122.3602 | 122.4381 | 122.406 | -122.3969 | -122.2961 | 122.3969 | 122.4152 | 48.7244 | 45.8954
1916.7656 | 122.6395 | -52.4918 | 69.873 | -0.17845 | 0.0027665 | 0.059889 | 0.11633 | 0.00017092 | -0.0033538 | -0.0043792 | -0.027771 | -0.0024096 | 0.062042 | 0.058913 | -0.028927 | -0.00093567 | 0.0016021 | -3.5522 | 69.8181 | -52.6154 | 69.8181 | -50.1297 | -52.7802 | 1.0254 | -6.2942 | 69.8273 | -52.5421 | 69.928 | -52.2263 | -52.5513 | -52.327 | -0.1236 | -0.054932 | -0.054932 | 2.3621 | 53.5172 | -0.28839 | 53.6407 | -0.16479 | -0.050354 | -0.045776 | 0.054932 | 0.2655 | 0.16479 | -0.05951 | 0.21515 | -0.009156 | 2.4857 | 122.4335 | 0.31586 | 122.4701 | 122.4335 | 122.3694 | 122.3099 | 122.319 | -122.4884 | -122.4152 | 122.3099 | 122.4197 | 48.9395 | 46.1975
1917.7656 | 122.6807 | -52.3773 | 69.9371 | -0.14793 | 0.00084388 | 0.063521 | 0.1159 | 0.0025207 | -0.0012176 | -0.0024566 | -0.030823 | -0.0034778 | 0.062256 | 0.055068 | -0.026577 | -0.00050847 | 0.00032049 | -3.6392 | 69.8914 | -52.5604 | 69.9188 | -49.9969 | -52.6428 | 0.99335 | -6.4499 | 69.9005 | -52.4643 | 70.0516 | -52.1164 | -52.4277 | -52.2263 | -0.18311 | -0.045777 | -0.018311 | 2.3804 | 53.3707 | -0.2655 | 53.5538 | -0.082397 | -0.086975 | -0.036621 | 0.11444 | 0.26093 | 0.15106 | -0.050354 | 0.23804 | 0.036621 | 2.5635 | 122.4792 | 0.3479 | 122.5159 | 122.4518 | 122.3648 | 122.2687 | 122.2778 | -122.4976 | -122.4014 | 122.2961 | 122.4289 | 48.7381 | 45.9274
1918.7656 | 122.6349 | -52.4414 | 69.9234 | -0.14793 | 0.00063028 | 0.061171 | 0.11505 | 0.00081172 | -0.0018586 | -0.0041656 | -0.024719 | -0.0024096 | 0.061829 | 0.059981 | -0.027431 | 0.00055973 | 0.00074769 | -3.4744 | 69.8959 | -52.5467 | 69.928 | -49.9191 | -52.6703 | 0.8606 | -6.1752 | 69.9005 | -52.4643 | 69.9692 | -52.2034 | -52.5238 | -52.2858 | -0.10529 | -0.027466 | 0.004578 | 2.5223 | 53.302 | -0.22888 | 53.4073 | -0.1236 | -0.022888 | -0.022888 | 0.045776 | 0.23804 | 0.15564 | -0.082398 | 0.17853 | -0.05951 | 2.6276 | 122.4747 | 0.26093 | 122.4335 | 122.4426 | 122.3648 | 122.3373 | 122.3419 | -122.4701 | -122.3877 | 122.3694 | 122.4106 | 48.967 | 46.2662
1919.7656 | 122.644 | -52.5604 | 69.809 | -0.16319 | 0.00063028 | 0.064162 | 0.11569 | 0.0031617 | -0.001004 | 0.00032044 | -0.049133 | -0.0045458 | 0.061829 | 0.058913 | -0.027645 | 0.00013253 | 0.0033111 | -3.447 | 69.7769 | -52.7115 | 69.754 | -50.0977 | -52.8625 | 1.0025 | -6.4957 | 69.754 | -52.6062 | 69.8364 | -52.3178 | -52.6337 | -52.4231 | -0.15106 | -0.032043 | -0.054932 | 2.4628 | 53.5629 | -0.30212 | 53.714 | -0.15106 | -0.045776 | -0.054932 | 0.027466 | 0.24262 | 0.13733 | -0.073242 | 0.1831 | -0.027466 | 2.6138 | 122.4655 | 0.28839 | 122.4426 | 122.4884 | 122.3602 | 122.3373 | 122.3145 | -122.5204 | -122.4152 | 122.3145 | 122.3969 | 49.1135 | 46.0648
1920.8281 | 122.6578 | -52.272 | 70.1065 | -0.079269 | 0.0010575 | 0.06053 | 0.11419 | 0.0010253 | -0.0029266 | -0.0026704 | 0.0027466 | -0.0032642 | 0.062683 | 0.061263 | -0.02615 | 0.0014141 | 0.0011749 | -3.3783 | 70.0882 | -52.4323 | 70.015 | -49.6674 | -52.5604 | 1.0941 | -6.4178 | 70.0424 | -52.3087 | 70.1294 | -52.0294 | -52.3361 | -52.1347 | -0.16022 | -0.01831 | -0.091552 | 2.6047 | 53.3661 | -0.28839 | 53.5263 | -0.12817 | -0.036621 | -0.064087 | 0.022889 | 0.24262 | 0.13733 | -0.064087 | 0.17395 | -0.027466 | 2.7649 | 122.4472 | 0.27924 | 122.4381 | 122.5204 | 122.3511 | 122.3602 | 122.3145 | -122.5388 | -122.4152 | 122.287 | 122.4014 | 48.8937 | 45.8542
1921.7656 | 122.6395 | -51.8188 | 70.5597 | -0.13267 | 0.0012711 | 0.063094 | 0.11654 | -0.00089728 | -0.0033538 | -0.0026704 | -0.030823 | -0.0047594 | 0.064179 | 0.068312 | -0.028286 | 0.0029095 | -0.0011749 | -3.3005 | 70.5322 | -51.947 | 70.4727 | -48.9761 | -52.121 | 1.1124 | -6.2759 | 70.5093 | -51.8829 | 70.5963 | -51.5579 | -51.8967 | -51.6678 | -0.12817 | -0.027465 | -0.086975 | 2.8427 | 52.9312 | -0.30212 | 53.0594 | -0.17395 | -0.064087 | -0.050354 | 0.036621 | 0.26093 | 0.15106 | -0.077819 | 0.21515 | -0.013732 | 2.9709 | 122.4197 | 0.32501 | 122.4792 | 122.4792 | 122.3923 | 122.3511 | 122.3282 | -122.5067 | -122.4426 | 122.2916 | 122.4152 | 48.5184 | 45.5429
1922.7656 | 122.7722 | -52.4872 | 69.8639 | -0.10216 | 0.00063028 | 0.060744 | 0.11526 | -0.0038879 | -0.0020722 | -0.0035248 | -0.06134 | -0.003905 | 0.063111 | 0.064681 | -0.029354 | 0.00098693 | -0.00074771 | -3.2959 | 69.9554 | -52.5375 | 69.8685 | -50.0656 | -52.803 | 1.0849 | -6.6833 | 69.7861 | -52.5742 | 69.8776 | -52.2675 | -52.5833 | -52.3682 | -0.050354 | 0.091552 | 0.004577 | 2.4216 | 53.5721 | -0.31586 | 53.6224 | -0.2655 | -0.086975 | -0.07782 | 0.013733 | 0.21973 | 0.11902 | -0.09613 | 0.20599 | -0.009155 | 2.4719 | 122.406 | 0.3067 | 122.4518 | 122.493 | 122.3602 | 122.4426 | 122.2733 | -122.4014 | -122.4381 | 122.3557 | 122.3648 | 49.1913 | 45.8038
1923.8438 | 122.5754 | -52.5009 | 69.8868 | -0.13267 | -0.0023605 | 0.060744 | 0.11697 | 0.0018799 | -0.0035674 | 0.00032044 | -0.14984 | -0.0034778 | 0.063751 | 0.065322 | -0.028927 | 0.0035503 | 0.00032049 | -3.3371 | 70.0058 | -52.565 | 69.8639 | -49.6719 | -52.7298 | 1.1444 | -6.8024 | 69.9692 | -52.4734 | 69.96 | -52.2583 | -52.6291 | -52.4094 | -0.064086 | 0.11902 | -0.022888 | 2.829 | 53.6453 | -0.22888 | 53.7094 | -0.16479 | 0.027466 | 0.082397 | 0.073242 | 0.24261 | 0.091553 | -0.12817 | 0.064087 | -0.15564 | 2.8931 | 122.4289 | 0.21515 | 122.4335 | 122.5708 | 122.4426 | 122.5067 | 122.4701 | -122.4518 | -122.3602 | 122.3648 | 122.4609 | 49.1638 | 45.6985
1924.7656 | 122.612 | -52.4185 | 69.9921 | -0.13267 | -1.0718e-05 | 0.061171 | 0.11804 | 0.0042297 | -0.0035674 | 0.00053404 | -0.14374 | -0.0026232 | 0.06546 | 0.062758 | -0.027431 | 0.0026959 | -0.0028839 | -3.154 | 69.9188 | -52.652 | 69.809 | -49.791 | -52.7664 | 1.2451 | -6.5094 | 69.9051 | -52.4826 | 70.0104 | -52.1759 | -52.5055 | -52.2766 | -0.23346 | -0.073242 | -0.1831 | 2.6276 | 53.6636 | -0.3479 | 53.8971 | -0.11444 | -0.064087 | -0.086975 | 0.018311 | 0.24262 | 0.14191 | -0.086975 | 0.20599 | -0.022888 | 2.861 | 122.4609 | 0.3067 | 122.493 | 122.5708 | 122.3877 | 122.3373 | 122.3236 | -122.644 | -122.4747 | 122.2275 | 122.4289 | 49.2645 | 45.9091
1925.8281 | 122.6807 | -52.2217 | 70.1385 | -0.10216 | -0.00065152 | 0.061171 | 0.11611 | 0.00017092 | -0.0024994 | -0.005661 | -0.00030524 | -0.0043322 | 0.064606 | 0.055709 | -0.026791 | 0.0018413 | 0.0035247 | -3.4332 | 70.134 | -52.3727 | 70.079 | -49.4385 | -52.4826 | 1.1993 | -6.0837 | 70.1111 | -52.2583 | 70.1981 | -51.9333 | -52.2583 | -52.0523 | -0.15106 | -0.004578 | -0.059509 | 2.7832 | 53.421 | -0.26093 | 53.5721 | -0.10986 | -0.036621 | -0.027466 | 0.059509 | 0.28839 | 0.16937 | -0.036621 | 0.20599 | 0 | 2.9343 | 122.4518 | 0.32501 | 122.4564 | 122.5067 | 122.3694 | 122.3557 | 122.3328 | -122.5113 | -122.3969 | 122.3007 | 122.4197 | 48.7885 | 46.138
1926.7656 | 122.6807 | -52.3224 | 70.0745 | -0.07164 | -0.0021469 | 0.057967 | 0.11654 | -0.00068368 | -0.0024994 | -0.0018158 | 0.0057984 | -0.0049732 | 0.064179 | 0.059554 | -0.028927 | 0.00013253 | 0.0043793 | -3.4424 | 70.0287 | -52.478 | 69.9921 | -49.5575 | -52.5833 | 1.1765 | -6.3171 | 69.9738 | -52.4231 | 70.0699 | -52.0523 | -52.3682 | -52.1164 | -0.15564 | -0.045776 | -0.082398 | 2.7649 | 53.4988 | -0.26093 | 53.6545 | -0.10529 | -0.10071 | -0.10071 | -0.004578 | 0.27008 | 0.20599 | -0.045776 | 0.3067 | 0.054932 | 2.9205 | 122.4701 | 0.37079 | 122.493 | 122.5067 | 122.3969 | 122.3511 | 122.2961 | -122.5525 | -122.4976 | 122.3145 | 122.3923 | 48.88 | 46.0052
1927.8281 | 122.5937 | -52.0706 | 70.3766 | -0.094528 | 0.00020288 | 0.063094 | 0.11676 | -0.0011109 | -0.0022858 | -0.0020294 | -0.12848 | -0.0032642 | 0.061829 | 0.064467 | -0.0285 | 0.00034613 | 0.00096129 | -3.3051 | 70.372 | -52.153 | 70.3171 | -49.1455 | -52.2903 | 1.2268 | -6.2622 | 70.3445 | -52.0477 | 70.3217 | -51.8509 | -52.1805 | -51.9333 | -0.082397 | -0.004578 | -0.059509 | 2.9251 | 53.2974 | -0.21973 | 53.3798 | -0.13733 | 0.022889 | -0.032044 | -0.054932 | 0.21973 | 0.13733 | -0.10986 | 0.11444 | -0.13275 | 3.0075 | 122.4701 | 0.19684 | 122.3694 | 122.525 | 122.3923 | 122.4426 | 122.4152 | -122.5296 | -122.4243 | 122.3877 | 122.3923 | 48.7656 | 45.8084
1928.7656 | 122.6715 | -52.0432 | 70.3217 | -0.12505 | -0.0010787 | 0.060744 | 0.11505 | 0.00038452 | -0.0035674 | -0.0035248 | -0.00030524 | -0.0028368 | 0.06247 | 0.058699 | -0.02615 | 0.0012005 | -0.0026703 | -3.2639 | 70.3125 | -52.1805 | 70.2209 | -49.2142 | -52.359 | 1.2222 | -6.3858 | 70.2667 | -52.1255 | 70.3583 | -51.7776 | -52.0889 | -51.8784 | -0.13733 | -0.009155 | -0.10071 | 2.829 | 53.2654 | -0.31586 | 53.4027 | -0.17853 | -0.082397 | -0.054931 | 0.036621 | 0.2655 | 0.16479 | -0.045776 | 0.24719 | 0.036621 | 2.9663 | 122.4014 | 0.3479 | 122.4838 | 122.493 | 122.3923 | 122.3557 | 122.3099 | -122.5021 | -122.4472 | 122.2641 | 122.4014 | 48.7793 | 45.6573
1929.8281 | 122.5433 | -51.709 | 70.7108 | -0.086899 | 0.00063028 | 0.061385 | 0.1174 | 0.0025207 | -0.0035674 | -0.00053396 | -0.11322 | -0.0030506 | 0.06482 | 0.060836 | -0.027218 | 0.0031231 | -0.0011749 | -3.2593 | 70.5734 | -51.9424 | 70.5002 | -48.8068 | -52.1072 | 1.2039 | -6.1798 | 70.6421 | -51.7456 | 70.665 | -51.5121 | -51.8417 | -51.6037 | -0.23346 | -0.13733 | -0.21057 | 2.9022 | 52.9129 | -0.39825 | 53.1464 | -0.16479 | -0.036621 | -0.068664 | -0.045776 | 0.19684 | 0.10529 | -0.13275 | 0.14191 | -0.096131 | 3.1357 | 122.4426 | 0.23346 | 122.4106 | 122.5159 | 122.3877 | 122.2824 | 122.3511 | -122.6532 | -122.4564 | 122.2092 | 122.374 | 48.4497 | 45.5292
1930.7969 | 122.5983 | -51.0818 | 71.3013 | -0.10216 | 0.0019119 | 0.059248 | 0.11718 | 0.00059812 | -0.0029266 | -0.0020294 | -0.073547 | -0.00070063 | 0.064392 | 0.064894 | -0.027645 | 0.0020551 | 0.0016021 | -3.1769 | 71.3379 | -51.1917 | 71.2189 | -47.8455 | -51.3657 | 1.355 | -6.5186 | 71.3242 | -51.123 | 71.3654 | -50.8484 | -51.1917 | -50.972 | -0.10986 | 0.036621 | -0.082398 | 3.2364 | 52.4368 | -0.28381 | 52.5467 | -0.17395 | -0.041199 | 0.022888 | 0.064086 | 0.23346 | 0.10986 | -0.10986 | 0.15106 | -0.068664 | 3.3463 | 122.4106 | 0.27466 | 122.4884 | 122.5296 | 122.4472 | 122.4197 | 122.406 | -122.493 | -122.4243 | 122.3007 | 122.4472 | 47.905 | 44.5633
1931.8281 | 122.5479 | -51.059 | 71.3516 | -0.10979 | 0.0010575 | 0.063307 | 0.11825 | 0.0035889 | -0.0029266 | -0.002884 | -0.11017 | -0.0036914 | 0.061188 | 0.062758 | -0.028286 | 0.00034613 | 0.0026703 | -3.2089 | 71.4523 | -51.1093 | 71.3013 | -47.7814 | -51.3153 | 1.5015 | -5.571 | 71.3562 | -51.0681 | 71.3013 | -50.9033 | -51.2375 | -51.0269 | -0.050354 | 0.10071 | -0.050354 | 3.2776 | 52.5604 | -0.25635 | 52.6108 | -0.20599 | -0.009155 | 0.004577 | -0.050354 | 0.15564 | 0.032043 | -0.17853 | 0.041198 | -0.16937 | 3.3279 | 122.4106 | 0.16479 | 122.3694 | 122.5616 | 122.4243 | 122.5113 | 122.4152 | -122.4609 | -122.4197 | 122.3602 | 122.3602 | 47.85 | 45.488
1932.7656 | 122.6898 | -51.0452 | 71.3058 | -0.11742 | -0.00086512 | 0.061385 | 0.11526 | -0.0028199 | -0.0020722 | -0.0035248 | 0.042419 | -0.003905 | 0.062042 | 0.053572 | -0.027431 | 0.0022687 | 0.0030975 | -3.1815 | 71.2418 | -51.2238 | 71.228 | -47.7631 | -51.2695 | 1.5656 | -5.8456 | 71.2463 | -51.0956 | 71.3928 | -50.7248 | -51.0361 | -50.8713 | -0.17853 | -0.064087 | -0.07782 | 3.2822 | 52.6108 | -0.2243 | 52.7893 | -0.045776 | -0.050354 | -0.059509 | 0.086975 | 0.32043 | 0.17395 | 0.009155 | 0.2243 | 0.059509 | 3.4607 | 122.4518 | 0.37079 | 122.4884 | 122.4655 | 122.3419 | 122.287 | 122.2916 | -122.5296 | -122.4014 | 122.2733 | 122.438 | 47.8638 | 45.1996
1933.8125 | 122.5204 | -50.6516 | 71.759 | -0.06401 | 0.00063028 | 0.062025 | 0.11676 | 0.0027343 | -0.0001496 | -0.002243 | -0.09491 | -0.0026232 | 0.064179 | 0.060408 | -0.028713 | 0.0029095 | -0.00053411 | -3.5522 | 71.6492 | -50.8896 | 71.5759 | -47.3145 | -50.9811 | 1.6663 | -5.3604 | 71.6721 | -50.7065 | 71.7499 | -50.4181 | -50.7523 | -50.6058 | -0.23804 | -0.10986 | -0.1831 | 3.3371 | 52.3178 | -0.32959 | 52.5558 | -0.091553 | -0.054932 | -0.086975 | -0.009155 | 0.23346 | 0.045776 | -0.10071 | 0.10071 | -0.045776 | 3.5751 | 122.4655 | 0.28839 | 122.4564 | 122.5388 | 122.3785 | 122.3007 | 122.3236 | -122.6486 | -122.4655 | 122.2275 | 122.4014 | 47.0993 | 45.2911
1934.7656 | 122.5708 | -50.885 | 71.5805 | -0.11742 | 0.0021255 | 0.061171 | 0.11569 | 0.0023071 | -0.0020722 | -0.00074776 | -0.00030524 | -0.00091423 | 0.061402 | 0.062545 | -0.028072 | 0.0020551 | 0.0028839 | -3.5156 | 71.5668 | -50.9628 | 71.4752 | -47.374 | -51.091 | 1.5244 | -6.5826 | 71.5302 | -50.9216 | 71.4798 | -50.6424 | -50.9583 | -50.7706 | -0.07782 | -0.013733 | -0.10529 | 3.511 | 52.4094 | -0.20599 | 52.4872 | -0.12817 | -0.036621 | -0.050354 | -0.10071 | 0.24262 | 0.11444 | -0.073242 | 0.15106 | -0.036621 | 3.5889 | 122.438 | 0.27924 | 122.4014 | 122.5296 | 122.4518 | 122.4518 | 122.4152 | -122.5433 | -122.5021 | 122.3602 | 122.3648 | 47.3694 | 44.3024
1935.8281 | 122.6807 | -50.8804 | 71.4752 | -0.27 | 0.0016983 | 0.058821 | 0.11569 | 0.0010253 | -0.0052764 | -0.0037384 | 0.036316 | -0.0049732 | 0.063111 | 0.057204 | -0.027645 | 0.00098693 | -0.00096131 | -3.4927 | 71.4752 | -50.9811 | 71.5302 | -47.2229 | -51.0178 | 1.6434 | -5.3238 | 71.4935 | -50.8484 | 71.5393 | -50.5829 | -50.9216 | -50.7889 | -0.10071 | 0 | 0.054931 | 3.6575 | 52.5238 | -0.13733 | 52.6245 | -0.036621 | 0.032043 | 0.01831 | 0.064087 | 0.29755 | 0.091553 | -0.041199 | 0.05951 | -0.073242 | 3.7582 | 122.5113 | 0.2655 | 122.3877 | 122.4564 | 122.3419 | 122.3557 | 122.374 | -122.4564 | -122.3236 | 122.4106 | 122.4197 | 47.3877 | 45.5566
1936.7656 | 122.6669 | -50.9216 | 71.4249 | -0.13267 | 0.0031937 | 0.061812 | 0.11462 | -0.00068368 | -0.01019 | -0.0050202 | 0.097351 | -0.0028368 | 0.063111 | 0.056136 | -0.027004 | 0.0012005 | 0.00032049 | -3.653 | 71.4706 | -51.0132 | 71.6034 | -47.4564 | -51.5808 | 1.4786 | -6.6467 | 71.3516 | -50.9857 | 71.4844 | -50.6424 | -50.9537 | -50.7523 | -0.091553 | 0.045776 | 0.17853 | 3.4653 | 52.4002 | -0.65918 | 52.4918 | -0.56763 | -0.064087 | -0.073242 | 0.059509 | 0.27924 | 0.16937 | -0.032043 | 0.23346 | 0.032044 | 3.5568 | 122.6166 | 0.34332 | 122.4701 | 122.4838 | 122.3373 | 122.3923 | 122.2733 | -122.4381 | -122.4106 | 122.525 | 122.406 | 47.2687 | 44.2749
1937.8438 | 122.5525 | -50.6927 | 71.7545 | -0.048752 | -0.00022432 | 0.062666 | 0.11547 | -0.00068368 | -0.0042084 | -0.0037384 | 0.018005 | -0.00048703 | 0.065888 | 0.051009 | -0.027859 | 0.00055973 | 0.00053409 | -3.5889 | 71.727 | -50.8392 | 71.4661 | -47.3373 | -51.0956 | 1.7441 | -6.1661 | 71.6354 | -50.8163 | 71.6446 | -50.5096 | -50.8347 | -50.6149 | -0.14648 | -0.027466 | -0.28839 | 3.3554 | 52.4368 | -0.40283 | 52.5833 | -0.25635 | -0.1236 | -0.11902 | -0.10986 | 0.1831 | 0.07782 | -0.14191 | 0.20142 | -0.018311 | 3.5019 | 122.3053 | 0.3067 | 122.4609 | 122.5662 | 122.4518 | 122.4197 | 122.3282 | -122.5937 | -122.5708 | 122.1588 | 122.3373 | 47.1039 | 44.5267
1938.7812 | 122.6349 | -50.7111 | 71.6949 | -0.13267 | 0.0019119 | 0.061812 | 0.11526 | -0.0023925 | -0.0046356 | -0.0037384 | 0.0088502 | -0.0049732 | 0.064392 | 0.061904 | -0.028072 | 0.00077333 | 0.00096129 | -3.5706 | 71.6949 | -50.8163 | 71.64 | -47.0673 | -50.9171 | 1.886 | -5.3055 | 71.64 | -50.7019 | 71.7178 | -50.4547 | -50.7523 | -50.5783 | -0.10528 | 0 | -0.054931 | 3.6438 | 52.597 | -0.20599 | 52.7023 | -0.10071 | 0.009156 | -0.054931 | 0.022888 | 0.25635 | 0.13275 | -0.041198 | 0.1236 | -0.050354 | 3.7491 | 122.4564 | 0.24719 | 122.4197 | 122.5113 | 122.3419 | 122.406 | 122.3511 | -122.5113 | -122.3969 | 122.3511 | 122.4289 | 47.1405 | 45.4056
1939.8438 | 122.6166 | -50.6561 | 71.7453 | -0.10216 | -0.0015061 | 0.062025 | 0.11846 | 0.0014527 | -0.0039948 | -0.0018158 | -0.076599 | -0.00091423 | 0.064606 | 0.064681 | -0.027218 | 0.00098693 | 0.0050201 | -3.5248 | 71.6629 | -50.8621 | 71.5302 | -47.2183 | -51.0269 | 1.5884 | -4.8523 | 71.6995 | -50.7431 | 71.7361 | -50.473 | -50.8026 | -50.5417 | -0.20599 | -0.082397 | -0.21515 | 3.4378 | 52.2446 | -0.37079 | 52.4506 | -0.16479 | -0.086975 | -0.045776 | -0.009155 | 0.18311 | 0.11444 | -0.14648 | 0.20142 | -0.059509 | 3.6438 | 122.3923 | 0.27008 | 122.4792 | 122.525 | 122.4426 | 122.319 | 122.3557 | -122.6074 | -122.4884 | 122.1863 | 122.3923 | 47.1313 | 45.8038
1940.7656 | 122.6852 | -50.9537 | 71.402 | -0.086899 | -0.00043792 | 0.06288 | 0.11569 | 0.0035889 | -0.0001496 | -0.002884 | 0.0057984 | -0.0028368 | 0.062683 | 0.060408 | -0.026791 | 0.00034613 | 0.0058747 | -3.5477 | 71.4066 | -51.0818 | 71.3379 | -47.493 | -51.2009 | 1.7212 | -4.953 | 71.3562 | -51.0406 | 71.4523 | -50.6836 | -50.9995 | -50.7706 | -0.12817 | 0.004577 | -0.064087 | 3.4607 | 52.6749 | -0.24719 | 52.803 | -0.11902 | -0.086975 | -0.045777 | 0.050354 | 0.27008 | 0.1831 | -0.045777 | 0.27008 | 0.041198 | 3.5889 | 122.4197 | 0.35706 | 122.493 | 122.4884 | 122.3969 | 122.3602 | 122.3099 | -122.4838 | -122.4426 | 122.2916 | 122.406 | 47.406 | 46.0007
1941.8281 | 122.6257 | -50.7935 | 71.6034 | -0.10216 | 0.00020288 | 0.061598 | 0.11569 | -0.00068368 | -0.0033538 | -0.0041656 | -0.024719 | -0.0049732 | 0.062897 | 0.055495 | -0.027645 | 0.0018413 | -0.0022431 | -3.598 | 71.5302 | -50.9354 | 71.5118 | -47.287 | -51.1139 | 1.8127 | -4.4769 | 71.5073 | -50.8942 | 71.5988 | -50.5463 | -50.8896 | -50.6744 | -0.14191 | -0.073243 | -0.091553 | 3.5065 | 52.6062 | -0.32044 | 52.7481 | -0.17853 | -0.10071 | -0.096131 | -0.004578 | 0.24719 | 0.11902 | -0.09613 | 0.21973 | 0.004578 | 3.6484 | 122.4472 | 0.3479 | 122.493 | 122.4655 | 122.4014 | 122.3236 | 122.3007 | -122.5388 | -122.4976 | 122.3053 | 122.3923 | 47.1954 | 46.3165
1942.7656 | 122.6944 | -51.1826 | 71.1685 | -0.12505 | 0.00041648 | 0.061598 | 0.11676 | -0.0021789 | -0.0007904 | -0.00096136 | 0.024109 | -0.0034778 | 0.063538 | 0.054427 | -0.028927 | 0.00077333 | -0.0016021 | -3.685 | 71.2006 | -51.3062 | 71.1319 | -47.7997 | -51.3886 | 1.7715 | -5.9601 | 71.1227 | -51.2512 | 71.2509 | -50.8759 | -51.2009 | -51.0178 | -0.1236 | 0.032044 | -0.036621 | 3.3829 | 52.9541 | -0.20599 | 53.0777 | -0.082398 | -0.068665 | -0.045776 | 0.082398 | 0.3067 | 0.16479 | -0.018311 | 0.23346 | 0.050354 | 3.5065 | 122.438 | 0.37537 | 122.5021 | 122.5067 | 122.374 | 122.3831 | 122.3053 | -122.4747 | -122.4197 | 122.3145 | 122.4335 | 47.4976 | 45.2225
1943.875 | 122.5754 | -50.647 | 71.8002 | 0.073319 | 0.0019119 | 0.062453 | 0.11804 | 0.0012391 | -0.0033538 | 0.00096124 | -0.13458 | -0.0026232 | 0.061402 | 0.062972 | -0.025936 | -8.1274e-05 | -0.0013885 | -3.598 | 71.814 | -50.7614 | 71.6446 | -47.0901 | -50.9766 | 1.9867 | -4.747 | 71.7682 | -50.6927 | 71.7407 | -50.441 | -50.7889 | -50.5417 | -0.11444 | 0.013733 | -0.15564 | 3.5568 | 52.6337 | -0.32959 | 52.7481 | -0.21515 | -0.045776 | -0.032044 | -0.059509 | 0.20599 | 0.10529 | -0.14191 | 0.15106 | -0.09613 | 3.6713 | 122.406 | 0.25177 | 122.4335 | 122.5754 | 122.4609 | 122.4609 | 122.4152 | -122.5616 | -122.493 | 122.2916 | 122.3877 | 47.049 | 45.9
1944.7656 | 122.5662 | -50.9171 | 71.4798 | -0.06401 | 0.0014847 | 0.063094 | 0.11697 | 0.0042297 | -0.0016448 | 0.001175 | -0.13153 | -0.0045458 | 0.064392 | 0.060622 | -0.028286 | 0.0039777 | 0.0013885 | -3.7125 | 71.4111 | -51.1368 | 71.2692 | -47.6074 | -51.329 | 1.973 | -4.715 | 71.4661 | -50.9995 | 71.4066 | -50.7889 | -51.1322 | -50.8301 | -0.21973 | -0.068664 | -0.21057 | 3.3096 | 52.89 | -0.41199 | 53.1097 | -0.19226 | -0.082398 | -0.013733 | -0.073242 | 0.12817 | 0.086975 | -0.21515 | 0.16937 | -0.13275 | 3.5294 | 122.406 | 0.21057 | 122.406 | 122.5479 | 122.4655 | 122.3282 | 122.3831 | -122.6166 | -122.4792 | 122.1863 | 122.3236 | 47.2046 | 46.2021
1945.8281 | 122.644 | -50.6012 | 71.7636 | -0.056381 | -0.0017197 | 0.062666 | 0.11441 | 0.00081172 | -0.0018586 | -0.0037384 | 0.030212 | -0.0049732 | 0.06247 | 0.059127 | -0.026363 | 0.0012005 | 0.00032049 | -3.479 | 71.6766 | -50.7797 | 71.6995 | -46.994 | -50.853 | 1.8448 | -4.4403 | 71.6949 | -50.6561 | 71.8231 | -50.3082 | -50.6012 | -50.2075 | -0.17853 | -0.086975 | -0.064087 | 3.6072 | 52.446 | -0.25177 | 52.6245 | -0.073242 | -0.054932 | -0.068665 | 0.059509 | 0.29297 | 0.39368 | 0 | 0.44861 | 0.054932 | 3.7857 | 122.4792 | 0.3479 | 122.4792 | 122.4564 | 122.3511 | 122.2778 | 122.2961 | -122.5433 | -122.4197 | 122.3007 | 122.4243 | 47.1222 | 46.1609
1946.7656 | 122.6486 | -50.5005 | 71.8369 | -0.079269 | 0.0029801 | 0.059889 | 0.11932 | -0.0038879 | -0.0039948 | -0.0020294 | 0.042419 | -0.0036914 | 0.064606 | 0.060622 | -0.029354 | 0.0031231 | 0.00096129 | -3.4515 | 71.7224 | -50.7751 | 71.7911 | -46.8338 | -50.766 | 1.7487 | -4.2343 | 71.7361 | -50.6058 | 71.8185 | -50.2533 | -50.3906 | -50.1846 | -0.27466 | -0.11444 | -0.045776 | 3.6667 | 52.2491 | -0.2655 | 52.5238 | 0.009155 | -0.10529 | -0.10071 | -0.018311 | 0.24719 | 0.31586 | 0.10986 | 0.42114 | 0.21515 | 3.9413 | 122.5662 | 0.35248 | 122.4243 | 122.4976 | 122.3419 | 122.2229 | 122.2366 | -122.612 | -122.4426 | 122.2916 | 122.319 | 47.0489 | 46.2662
1947.8281 | 122.6303 | -50.3952 | 72.0383 | -0.07164 | 0.00020288 | 0.061812 | 0.11654 | 0.0018799 | -0.0031402 | -0.00053396 | 0.011902 | -0.005614 | 0.062256 | 0.061049 | -0.0285 | 0.00077333 | 0.0030975 | -3.5934 | 71.9101 | -50.6104 | 71.8918 | -46.7056 | -50.6653 | 1.8311 | -4.2709 | 71.9009 | -50.4684 | 72.0108 | -50.0793 | -50.4501 | -50.386 | -0.21515 | -0.12817 | -0.14648 | 3.6896 | 52.2263 | -0.27008 | 52.4414 | -0.054931 | -0.073242 | -0.13733 | -0.027466 | 0.31586 | 0.009156 | -0.054931 | 0.082398 | 0.018311 | 3.9047 | 122.5021 | 0.3891 | 122.4792 | 122.5204 | 122.3694 | 122.3053 | 122.2961 | -122.6486 | -122.5067 | 122.287 | 122.406 | 46.8018 | 46.1243
1948.7656 | 122.5754 | -49.942 | 72.5052 | -0.025863 | -0.00043792 | 0.062025 | 0.11611 | 0.0012391 | -0.0048492 | -0.0030976 | -0.14069 | -0.0032642 | 0.063324 | 0.06169 | -0.027218 | 0.00034613 | -0.0020295 | -3.4287 | 72.4365 | -50.148 | 72.258 | -46.1517 | -50.1114 | 1.973 | -4.1977 | 72.3862 | -50.0107 | 72.4091 | -49.736 | -50.0519 | -49.8779 | -0.20599 | -0.068665 | -0.24719 | 3.7903 | 51.915 | -0.16937 | 52.121 | 0.036621 | -0.068664 | -0.11902 | -0.09613 | 0.20599 | 0.064087 | -0.10986 | 0.13275 | -0.041199 | 3.9963 | 122.406 | 0.27466 | 122.4197 | 122.5845 | 122.3969 | 122.3785 | 122.3282 | -122.6532 | -122.5159 | 122.2 | 122.3511 | 46.5134 | 45.7443
1949.8281 | 122.5388 | -50.0931 | 72.3633 | -0.041122 | 0.0012711 | 0.055403 | 0.11782 | -0.00068368 | -0.002713 | -0.00010676 | -0.052185 | -0.0030506 | 0.063324 | 0.054 | -0.026791 | 0.00098693 | 0.0011749 | -3.3646 | 72.4457 | -50.0977 | 72.2351 | -46.1563 | -50.3174 | 1.8127 | -4.4403 | 72.3312 | -50.1297 | 72.2717 | -49.8734 | -50.1984 | -49.9329 | -0.004577 | 0.082398 | -0.12817 | 3.9368 | 51.9058 | -0.2243 | 51.9104 | -0.21973 | -0.036621 | -0.032043 | -0.091552 | 0.21973 | 0.16022 | -0.10528 | 0.19684 | -0.068664 | 3.9413 | 122.3328 | 0.25635 | 122.4014 | 122.5433 | 122.4609 | 122.5388 | 122.4243 | -122.4609 | -122.493 | 122.3282 | 122.3648 | 46.7285 | 45.6528
1950.7656 | 122.6486 | -49.9832 | 72.4136 | -0.10216 | 0.0019119 | 0.062025 | 0.11462 | 0.00038452 | -0.0022858 | 0.00032044 | 0.021057 | -0.0030506 | 0.065033 | 0.05699 | -0.027431 | -0.00072207 | 0.00010689 | -3.5751 | 72.3541 | -50.1022 | 72.3862 | -46.019 | -50.2533 | 1.9775 | -4.1611 | 72.3038 | -50.0427 | 72.4228 | -49.6994 | -50.0015 | -49.8276 | -0.11902 | -0.059509 | -0.027466 | 3.9642 | 51.9608 | -0.27008 | 52.0798 | -0.15106 | -0.05951 | -0.10986 | 0.009156 | 0.28381 | 0.15564 | -0.018311 | 0.21515 | 0.041199 | 4.0833 | 122.4884 | 0.34332 | 122.4655 | 122.4564 | 122.3465 | 122.3373 | 122.287 | -122.5159 | -122.4564 | 122.3694 | 122.406 | 46.4081 | 45.8221
1951.8281 | 122.6944 | -50.2029 | 72.1573 | -0.06401 | 0.0010575 | 0.060316 | 0.11569 | -4.2682e-05 | -0.0012176 | -0.0067292 | 0.042419 | -0.00048703 | 0.063538 | 0.056563 | -0.029354 | 0.00013253 | 0.00074769 | -3.7674 | 72.0428 | -50.4135 | 72.29 | -46.7011 | -50.8621 | 1.9547 | -4.2709 | 72.02 | -50.3448 | 72.2351 | -49.91 | -50.2258 | -50.0473 | -0.21057 | -0.11444 | 0.13275 | 3.5019 | 52.1576 | -0.65918 | 52.3682 | -0.44861 | -0.14191 | -0.13733 | 0.077819 | 0.29297 | 0.15564 | -0.022888 | 0.29755 | 0.11902 | 3.7125 | 122.7036 | 0.43488 | 122.58 | 122.4564 | 122.3648 | 122.2458 | 122.2229 | -122.5708 | -122.5021 | 122.493 | 122.438 | 46.4355 | 45.932
1952.7656 | 122.612 | -50.0061 | 72.4091 | -0.06401 | -0.0010787 | 0.062453 | 0.11804 | 0.0016663 | -0.0031402 | -0.003952 | -0.06134 | -0.0028368 | 0.061402 | 0.067244 | -0.028713 | 0.0029095 | 0.0026703 | -3.8315 | 72.3358 | -50.2487 | 72.1664 | -46.2936 | -50.3586 | 1.9043 | -5.0446 | 72.3358 | -50.1068 | 72.3404 | -49.8047 | -50.1663 | -49.9466 | -0.24261 | -0.073243 | -0.24262 | 3.7125 | 51.9104 | -0.35248 | 52.153 | -0.10986 | -0.10071 | -0.073243 | -0.068665 | 0.20142 | 0.05951 | -0.16022 | 0.16022 | -0.059509 | 3.9551 | 122.4152 | 0.30212 | 122.4472 | 122.5845 | 122.4426 | 122.3419 | 122.3419 | -122.6578 | -122.5159 | 122.1725 | 122.3465 | 46.1746 | 44.9615
1953.8281 | 122.6166 | -49.7772 | 72.6379 | -0.041122 | 0.0023391 | 0.063307 | 0.11718 | 0.0050843 | -0.0033538 | -0.00032036 | -0.070496 | -0.0026232 | 0.062897 | 0.05699 | -0.028927 | 0.00098693 | -0.00010671 | -3.7125 | 72.6334 | -49.9329 | 72.5464 | -45.7626 | -50.0198 | 2.0737 | -4.4174 | 72.6334 | -49.791 | 72.6151 | -49.5529 | -49.9191 | -49.6902 | -0.15564 | -0.004577 | -0.091552 | 4.0146 | 51.8509 | -0.24261 | 52.0065 | -0.086975 | -0.013733 | -0.004577 | -0.022888 | 0.22431 | 0.086975 | -0.14191 | 0.10071 | -0.12817 | 4.1702 | 122.4792 | 0.23804 | 122.406 | 122.5662 | 122.4243 | 122.4106 | 122.4106 | -122.5708 | -122.4289 | 122.3236 | 122.3923 | 46.0648 | 45.3598
1954.7656 | 122.5845 | -49.942 | 72.4915 | -0.056381 | -0.0012923 | 0.062666 | 0.11526 | -0.0015381 | -0.0020722 | -0.0041656 | 0.0057984 | -0.002196 | 0.062897 | 0.061049 | -0.025509 | 0.00034613 | 0.0020295 | -3.566 | 72.4686 | -50.0427 | 72.3999 | -45.9366 | -50.1389 | 2.1286 | -4.1885 | 72.4411 | -49.9558 | 72.4182 | -49.6994 | -50.0473 | -49.8917 | -0.10071 | -0.022888 | -0.091553 | 4.0054 | 52.0706 | -0.19684 | 52.1713 | -0.09613 | -0.013733 | -0.050354 | -0.073242 | 0.24262 | 0.050354 | -0.10529 | 0.064087 | -0.091552 | 4.1061 | 122.4426 | 0.25635 | 122.374 | 122.5113 | 122.3969 | 122.4106 | 122.3831 | -122.5342 | -122.4472 | 122.3419 | 122.3602 | 46.376 | 45.7535
1955.7656 | 122.6349 | -50.3769 | 72.0291 | -0.094528 | 0.0019119 | 0.061385 | 0.11697 | 0.0016663 | -0.0035674 | -0.0033112 | 0.0088502 | -0.0024096 | 0.064179 | 0.059981 | -0.027859 | 0.00013253 | -0.0016021 | -3.5477 | 71.9147 | -50.5554 | 71.9101 | -46.6827 | -50.647 | 2.0462 | -3.9871 | 71.9559 | -50.4135 | 71.9925 | -50.1343 | -50.4639 | -50.2625 | -0.17853 | -0.11444 | -0.11902 | 3.6942 | 52.4231 | -0.27008 | 52.6016 | -0.091553 | -0.036621 | -0.073242 | -0.036621 | 0.24262 | 0.11444 | -0.086975 | 0.15106 | -0.050354 | 3.8727 | 122.4655 | 0.27924 | 122.406 | 122.4701 | 122.3694 | 122.2916 | 122.3328 | -122.5845 | -122.4426 | 122.287 | 122.3694 | 46.8292 | 46.3898
1956.8281 | 122.6898 | -50.2991 | 72.1161 | -0.025863 | 0.00041648 | 0.062666 | 0.11483 | 0.0018799 | -0.0024994 | -0.002243 | 0.0027466 | -0.0032642 | 0.062256 | 0.058486 | -0.027218 | 0.00098693 | 0.0028839 | -3.4607 | 72.0657 | -50.386 | 72.0886 | -46.463 | -50.4959 | 2.2614 | -4.0421 | 72.0291 | -50.3586 | 72.1161 | -49.9878 | -50.3265 | -50.1068 | -0.086975 | -0.050354 | -0.027466 | 3.8361 | 52.5604 | -0.19684 | 52.6474 | -0.10986 | -0.05951 | -0.086975 | 0 | 0.31128 | 0.19226 | -0.027466 | 0.25177 | 0.032044 | 3.923 | 122.4747 | 0.37079 | 122.4747 | 122.4518 | 122.3877 | 122.3648 | 122.3282 | -122.5021 | -122.4747 | 122.3877 | 122.4152 | 46.8384 | 46.257
1957.7656 | 122.5754 | -50.0061 | 72.4274 | -0.041122 | 0.0012711 | 0.060316 | 0.11526 | 0.00081172 | -0.0046356 | 0.00053404 | -0.039978 | -0.0034778 | 0.065247 | 0.058699 | -0.0285 | 0.0018413 | -0.00032051 | -3.5019 | 72.3129 | -50.2213 | 72.2214 | -46.1975 | -50.3082 | 2.2202 | -4.0741 | 72.3587 | -50.061 | 72.3312 | -49.8001 | -50.1297 | -49.9283 | -0.21515 | -0.11444 | -0.20599 | 3.8086 | 52.2263 | -0.30212 | 52.4414 | -0.086976 | -0.054931 | -0.068664 | -0.09613 | 0.20599 | 0.07782 | -0.1236 | 0.13275 | -0.068665 | 4.0237 | 122.4426 | 0.26093 | 122.3923 | 122.5342 | 122.4197 | 122.319 | 122.3648 | -122.6486 | -122.4884 | 122.2275 | 122.3373 | 46.5042 | 45.932
1958.8281 | 122.6028 | -50.3632 | 72.0703 | -0.056381 | -0.0015061 | 0.061171 | 0.11676 | 0.0027343 | -0.0029266 | -0.003952 | -0.070496 | -0.0026232 | 0.061615 | 0.063613 | -0.027645 | 0.00098693 | 0.0016021 | -3.5065 | 72.084 | -50.4776 | 71.9513 | -46.6553 | -50.5875 | 1.9867 | -4.7791 | 72.1161 | -50.322 | 72.0154 | -50.1297 | -50.5646 | -50.3998 | -0.11444 | 0.013733 | -0.11902 | 3.7079 | 52.3499 | -0.2243 | 52.4643 | -0.10986 | 0.041199 | 0.045777 | -0.054931 | 0.23346 | -0.036621 | -0.20142 | -0.07782 | -0.24262 | 3.8223 | 122.4289 | 0.19226 | 122.3373 | 122.5616 | 122.438 | 122.4472 | 122.4792 | -122.5479 | -122.3923 | 122.3145 | 122.3785 | 46.8567 | 45.5841
1959.7656 | 122.6944 | -49.9603 | 72.4319 | -0.018234 | -0.00065152 | 0.06288 | 0.11633 | 0.0016663 | -0.0007904 | -0.00074776 | 0.018005 | -0.003905 | 0.063965 | 0.055281 | -0.029781 | -0.00050847 | 0.0030975 | -3.5889 | 72.2809 | -50.1984 | 72.2992 | -46.0922 | -50.2579 | 2.1927 | -3.9139 | 72.2992 | -50.0748 | 72.4274 | -49.6765 | -50.0244 | -49.8413 | -0.23804 | -0.15106 | -0.13275 | 3.8681 | 52.153 | -0.29755 | 52.3911 | -0.05951 | -0.11444 | -0.13275 | -0.004578 | 0.28381 | 0.11902 | -0.064087 | 0.23346 | 0.050354 | 4.1061 | 122.4976 | 0.39825 | 122.5021 | 122.4792 | 122.374 | 122.2412 | 122.2595 | -122.6303 | -122.5067 | 122.2595 | 122.3877 | 46.3715 | 46.0464
1960.8281 | 122.5571 | -49.9466 | 72.5143 | -0.056381 | 0.00041648 | 0.060744 | 0.11569 | -0.0021789 | -0.0012176 | 0.0024566 | -0.067444 | -0.0034778 | 0.062042 | 0.056136 | -0.024441 | 0.0022687 | 0.0024567 | -3.6118 | 72.496 | -50.061 | 72.1619 | -46.2341 | -50.1846 | 2.1011 | -3.923 | 72.3953 | -50.0702 | 72.3999 | -49.7406 | -50.0565 | -49.9146 | -0.11444 | -0.01831 | -0.35248 | 3.7125 | 52.0477 | -0.23804 | 52.1622 | -0.1236 | -0.1236 | -0.11902 | -0.11444 | 0.20599 | 0.032043 | -0.10986 | 0.15564 | 0.013732 | 3.8269 | 122.2229 | 0.32959 | 122.4701 | 122.5571 | 122.4655 | 122.4426 | 122.3419 | -122.5754 | -122.5845 | 122.1085 | 122.3465 | 46.3348 | 46.0236
1961.7656 | 122.6166 | -50.2808 | 72.139 | -0.048752 | -0.00043792 | 0.061385 | 0.1174 | 0.0048705 | -0.0063446 | -0.00096136 | -0.064392 | -0.0036914 | 0.061188 | 0.063399 | -0.026791 | -0.00050847 | -0.00074771 | -3.5019 | 72.1939 | -50.3723 | 72.0657 | -46.4584 | -50.5142 | 1.9821 | -4.0192 | 72.1664 | -50.2808 | 72.1069 | -50.0427 | -50.3815 | -50.1617 | -0.091552 | 0.054932 | -0.073242 | 3.8223 | 52.2629 | -0.23346 | 52.3544 | -0.14191 | 0 | 0.027466 | -0.032043 | 0.23804 | 0.11902 | -0.10071 | 0.11902 | -0.10071 | 3.9139 | 122.438 | 0.23804 | 122.3877 | 122.5662 | 122.4472 | 122.4747 | 122.4472 | -122.5113 | -122.4197 | 122.3465 | 122.3877 | 46.7789 | 46.2616
1962.8281 | 122.612 | -50.3815 | 72.0657 | -0.10216 | -1.0718e-05 | 0.060316 | 0.11718 | 0.0029479 | -0.0029266 | -0.0020294 | -0.049133 | -0.0019824 | 0.063111 | 0.062331 | -0.027218 | 0.0014141 | -0.0013885 | -3.566 | 72.0016 | -50.56 | 71.9055 | -46.7011 | -50.7202 | 1.9409 | -4.1473 | 71.9696 | -50.4639 | 72.02 | -50.1068 | -50.4501 | -50.2579 | -0.17853 | -0.064087 | -0.16022 | 3.6804 | 52.3224 | -0.33875 | 52.5009 | -0.16022 | -0.082397 | -0.096131 | -0.045777 | 0.27466 | 0.1236 | -0.068664 | 0.20599 | 0.013733 | 3.8589 | 122.4655 | 0.35706 | 122.4838 | 122.5616 | 122.4335 | 122.3831 | 122.3511 | -122.6257 | -122.5296 | 122.287 | 122.4014 | 46.8155 | 46.2341
1963.7656 | 122.5616 | -50.3677 | 72.0978 | -0.041122 | -0.0010787 | 0.063094 | 0.11846 | -0.00025628 | 6.4004e-05 | -0.00096136 | -0.030823 | -0.0030506 | 0.063111 | 0.060836 | -0.026791 | -0.00072207 | 0.0045929 | -3.5934 | 72.0612 | -50.4868 | 71.8781 | -46.7514 | -50.7156 | 2.0279 | -4.2206 | 72.0062 | -50.4318 | 72.0062 | -50.1205 | -50.4547 | -50.2396 | -0.11902 | -0.036621 | -0.21973 | 3.6163 | 52.3956 | -0.3479 | 52.5146 | -0.22888 | -0.064087 | -0.091552 | -0.091552 | 0.24719 | 0.12817 | -0.086975 | 0.19226 | -0.022888 | 3.7354 | 122.3648 | 0.31128 | 122.4381 | 122.5479 | 122.4381 | 122.4289 | 122.374 | -122.5845 | -122.5296 | 122.2458 | 122.374 | 46.7743 | 46.1472
1964.8281 | 122.5754 | -50.1846 | 72.29 | -0.033493 | 0.00084388 | 0.060316 | 0.11761 | 0.0023071 | -0.0037812 | -0.0018158 | -0.0064086 | -0.0041186 | 0.063751 | 0.057204 | -0.027004 | 0.00077333 | -0.0041657 | -3.6163 | 72.2305 | -50.3036 | 72.084 | -46.3898 | -50.441 | 2.1286 | -3.7033 | 72.171 | -50.2625 | 72.1481 | -49.9695 | -50.2945 | -50.0977 | -0.11902 | -0.059509 | -0.20599 | 3.7949 | 52.3132 | -0.25635 | 52.4323 | -0.13733 | -0.07782 | -0.11902 | -0.14191 | 0.21515 | 0.086975 | -0.10986 | 0.16479 | -0.032044 | 3.9139 | 122.3877 | 0.29297 | 122.4106 | 122.5342 | 122.4335 | 122.4152 | 122.3557 | -122.5937 | -122.5525 | 122.2687 | 122.3328 | 46.5683 | 46.4813
1965.7656 | 122.6761 | -50.2121 | 72.1893 | -0.086899 | 0.0012711 | 0.059248 | 0.11441 | 0.00081172 | -0.0035674 | -0.002243 | 0.024109 | -0.003905 | 0.061615 | 0.059127 | -0.027431 | -0.00050847 | -0.0016021 | -3.6484 | 72.1024 | -50.3632 | 72.1252 | -46.3852 | -50.441 | 2.0828 | -4.3716 | 72.0657 | -50.2945 | 72.1893 | -49.9146 | -50.2396 | -50.0702 | -0.15106 | -0.086975 | -0.064087 | 3.8269 | 52.2949 | -0.22888 | 52.446 | -0.07782 | -0.082398 | -0.1236 | 0 | 0.29755 | 0.14191 | -0.027466 | 0.22431 | 0.054932 | 3.978 | 122.4884 | 0.37994 | 122.4838 | 122.4655 | 122.3602 | 122.3145 | 122.2778 | -122.5525 | -122.4838 | 122.3373 | 122.4014 | 46.5637 | 45.8405
1966.8281 | 122.5983 | -50.4227 | 72.0245 | -0.10216 | -1.0718e-05 | 0.060316 | 0.11654 | 0.0025207 | -0.0035674 | -0.0043792 | -0.012512 | -0.002196 | 0.06247 | 0.062972 | -0.027431 | 0.0016277 | 0.0060883 | -3.7216 | 71.9376 | -50.5783 | 71.9009 | -46.6965 | -50.6561 | 2.0325 | -3.891 | 72.0062 | -50.441 | 71.9421 | -50.1801 | -50.5188 | -50.3403 | -0.15564 | -0.086975 | -0.1236 | 3.7262 | 52.4551 | -0.23346 | 52.6108 | -0.07782 | -0.018311 | -0.01831 | -0.082397 | 0.24261 | 0.082397 | -0.096131 | 0.10071 | -0.07782 | 3.8818 | 122.4792 | 0.26093 | 122.3831 | 122.5159 | 122.4472 | 122.3602 | 122.4289 | -122.6028 | -122.4655 | 122.3236 | 122.3648 | 46.701 | 46.5317
1967.7656 | 122.6074 | -50.4181 | 72.0245 | -0.11742 | 0.0016983 | 0.061385 | 0.11633 | -0.0013245 | -0.002713 | -0.003952 | 0.0088502 | -0.0030506 | 0.062256 | 0.061049 | -0.027218 | 0.0029095 | 0.0054475 | -3.6942 | 71.965 | -50.5096 | 71.9101 | -46.7056 | -50.6195 | 2.2522 | -3.7949 | 71.9467 | -50.4318 | 71.9742 | -50.1526 | -50.4822 | -50.2762 | -0.091553 | -0.059509 | -0.11444 | 3.7125 | 52.6703 | -0.20142 | 52.7618 | -0.10986 | -0.013733 | -0.07782 | -0.050354 | 0.2655 | 0.14191 | -0.064087 | 0.15564 | -0.050354 | 3.804 | 122.4197 | 0.27924 | 122.406 | 122.4747 | 122.3785 | 122.3831 | 122.3648 | -122.5342 | -122.4564 | 122.3282 | 122.3923 | 46.7239 | 46.6232
1968.8281 | 122.6166 | -50.3448 | 72.084 | -0.10979 | 0.00084388 | 0.060957 | 0.11868 | 0.0033753 | -0.0024994 | -0.002884 | -0.082703 | -0.0026232 | 0.062897 | 0.066603 | -0.027859 | -0.0011493 | 0.00010689 | -3.9368 | 72.0154 | -50.5554 | 71.9193 | -46.6965 | -50.6332 | 2.1423 | -3.8132 | 72.0062 | -50.4044 | 72.0657 | -50.0977 | -50.4639 | -50.2213 | -0.21057 | -0.068664 | -0.16479 | 3.6484 | 52.4872 | -0.28839 | 52.6978 | -0.07782 | -0.059509 | -0.077819 | -0.01831 | 0.24719 | 0.1236 | -0.11902 | 0.18311 | -0.059509 | 3.8589 | 122.4747 | 0.3067 | 122.4701 | 122.5708 | 122.4106 | 122.3602 | 122.3511 | -122.6395 | -122.4884 | 122.2641 | 122.4106 | 46.4081 | 46.5317
1969.7656 | 122.6349 | -50.8118 | 71.5668 | -0.14793 | -0.00022432 | 0.060957 | 0.11697 | 0.00059812 | -0.0005768 | 0.00074764 | 0.011902 | -0.0043322 | 0.060761 | 0.063613 | -0.027004 | 0.00055973 | 0.0037385 | -4.01 | 71.5485 | -50.9628 | 71.489 | -47.3328 | -51.0773 | 2.0554 | -3.8086 | 71.4661 | -50.8987 | 71.5622 | -50.5188 | -50.8713 | -50.6882 | -0.15106 | -0.01831 | -0.077819 | 3.479 | 52.8671 | -0.2655 | 53.0182 | -0.11444 | -0.086975 | -0.10071 | -0.004577 | 0.29297 | 0.1236 | -0.059509 | 0.21057 | 0.027466 | 3.6301 | 122.4518 | 0.37994 | 122.4609 | 122.5113 | 122.3648 | 122.3602 | 122.2778 | -122.5296 | -122.4655 | 122.3007 | 122.374 | 46.8018 | 47.0032
1970.8281 | 122.5479 | -50.7156 | 71.727 | -0.041122 | 0.0010575 | 0.060957 | 0.11676 | 0.0020935 | -0.0037812 | -0.0035248 | -0.027771 | -0.0036914 | 0.06546 | 0.054427 | -0.028286 | 0.00055973 | -0.0013885 | -3.9276 | 71.6766 | -50.9216 | 71.5118 | -47.287 | -51.0452 | 2.2018 | -3.9597 | 71.6354 | -50.798 | 71.6263 | -50.5142 | -50.8484 | -50.5737 | -0.20599 | -0.050354 | -0.21515 | 3.4286 | 52.9175 | -0.32959 | 53.1235 | -0.1236 | -0.082398 | -0.091553 | -0.10071 | 0.20142 | 0.14191 | -0.13275 | 0.22431 | -0.050354 | 3.6346 | 122.4335 | 0.28381 | 122.4243 | 122.5983 | 122.4335 | 122.3923 | 122.3511 | -122.6486 | -122.525 | 122.2275 | 122.3419 | 46.788 | 46.756
1971.7656 | 122.644 | -49.7681 | 72.6013 | -0.048752 | 0.0010575 | 0.060957 | 0.11569 | 0.0031617 | -0.0020722 | -0.003952 | 0.018005 | -0.003905 | 0.063965 | 0.056563 | -0.027431 | -0.00050847 | 0.0018159 | -3.4882 | 72.5784 | -49.91 | 72.5784 | -45.7169 | -50.0107 | 2.3254 | -4.0146 | 72.5372 | -49.8642 | 72.6288 | -49.5117 | -49.8322 | -49.6536 | -0.14191 | -0.022888 | -0.022888 | 4.0512 | 52.0935 | -0.24262 | 52.2354 | -0.10071 | -0.096131 | -0.064087 | 0.027466 | 0.25635 | 0.11444 | -0.064087 | 0.21057 | 0.032044 | 4.1931 | 122.4884 | 0.35248 | 122.493 | 122.4884 | 122.4014 | 122.3465 | 122.3053 | -122.5113 | -122.4655 | 122.3465 | 122.3969 | 46.2799 | 45.7535
1972.8281 | 122.6166 | -49.9466 | 72.4731 | -0.079269 | 0.00084388 | 0.061812 | 0.11697 | 0.0023071 | -0.0018586 | -0.0033112 | -0.06134 | -0.0013416 | 0.062897 | 0.062972 | -0.02615 | -0.00029487 | 0.0013885 | -3.6667 | 72.4869 | -50.0565 | 72.345 | -46.0373 | -50.2396 | 2.2522 | -3.6942 | 72.4548 | -50.0107 | 72.4411 | -49.6994 | -50.0473 | -49.8413 | -0.10986 | 0.013732 | -0.12817 | 3.9093 | 52.1988 | -0.29297 | 52.3087 | -0.1831 | -0.064087 | -0.018311 | -0.032044 | 0.24719 | 0.10528 | -0.10071 | 0.16937 | -0.036621 | 4.0192 | 122.4014 | 0.31128 | 122.4518 | 122.5433 | 122.4655 | 122.4335 | 122.4014 | -122.5296 | -122.4838 | 122.2916 | 122.3877 | 46.2799 | 46.2524
1973.7656 | 122.6349 | -49.7589 | 72.5967 | -0.14793 | -1.0718e-05 | 0.06288 | 0.11697 | 0.00017092 | -0.0033538 | 0.00032044 | 0.018005 | -0.003905 | 0.063538 | 0.059554 | -0.027645 | -8.1274e-05 | 0.0020295 | -3.8498 | 72.5647 | -49.9008 | 72.551 | -45.7489 | -50.0336 | 2.2202 | -3.7308 | 72.5693 | -49.8413 | 72.6105 | -49.3195 | -49.7498 | -49.6445 | -0.14191 | -0.032044 | -0.045777 | 4.01 | 51.9791 | -0.27466 | 52.121 | -0.13275 | -0.082398 | -0.027466 | 0.013733 | 0.43945 | 0.11444 | 0.009155 | 0.19684 | 0.091553 | 4.1519 | 122.4518 | 0.52185 | 122.4518 | 122.4655 | 122.4106 | 122.3236 | 122.3282 | -122.4976 | -122.4381 | 122.3099 | 122.3694 | 45.9091 | 46.0281
1974.8281 | 122.5479 | -49.4659 | 72.9675 | -0.018234 | -0.00086512 | 0.059889 | 0.11569 | -0.0019653 | -0.0042084 | -0.003952 | -0.052185 | -0.0030506 | 0.063538 | 0.063185 | -0.027859 | 0.0022687 | 0.0037385 | -3.4698 | 72.9538 | -49.5987 | 72.7844 | -45.4239 | -49.7314 | 2.3529 | -3.6438 | 72.8989 | -49.5621 | 72.908 | -49.2416 | -49.5621 | -49.3698 | -0.13275 | -0.013733 | -0.1831 | 4.0421 | 51.8188 | -0.2655 | 51.9516 | -0.13275 | -0.096131 | -0.068664 | -0.059509 | 0.2243 | 0.09613 | -0.096131 | 0.19226 | 0 | 4.1748 | 122.3831 | 0.32043 | 122.4701 | 122.5525 | 122.4609 | 122.4197 | 122.3648 | -122.5662 | -122.5296 | 122.2504 | 122.374 | 45.9961 | 45.8221
1975.7656 | 122.5983 | -49.6674 | 72.7615 | -0.041122 | 0.0023391 | 0.063307 | 0.11633 | -0.0036743 | -0.0016448 | -0.0013886 | -0.027771 | -0.0036914 | 0.06546 | 0.061049 | -0.0285 | -0.0041401 | -0.00074771 | -3.3875 | 72.7341 | -49.7681 | 72.6105 | -45.6711 | -49.91 | 2.4033 | -3.8361 | 72.6379 | -49.7406 | 72.6929 | -49.4293 | -49.7635 | -49.5667 | -0.10071 | -0.027466 | -0.15106 | 3.9963 | 52.0706 | -0.24262 | 52.1713 | -0.14191 | -0.073243 | -0.1236 | -0.068665 | 0.23804 | 0.10071 | -0.096131 | 0.17395 | -0.022888 | 4.097 | 122.3785 | 0.31128 | 122.4335 | 122.5021 | 122.3785 | 122.4014 | 122.3053 | -122.5296 | -122.5021 | 122.2778 | 122.3602 | 46.2799 | 45.8313
1976.8281 | 122.6578 | -49.1867 | 73.2376 | -0.086899 | -0.0015061 | 0.061598 | 0.11547 | 0.0010253 | -0.0018586 | -0.0013886 | -0.00030524 | -0.003905 | 0.059906 | 0.060195 | -0.027645 | 0.00098693 | -0.00010671 | -3.2135 | 73.2559 | -49.2462 | 73.2056 | -44.8151 | -49.3607 | 2.5589 | -3.4195 | 73.1781 | -49.2004 | 73.2468 | -48.8754 | -49.2096 | -49.0311 | -0.059509 | 0.01831 | -0.032044 | 4.3716 | 51.7456 | -0.17395 | 51.8051 | -0.11444 | -0.013732 | -0.059509 | 0.009155 | 0.31128 | 0.15564 | -0.022888 | 0.16937 | -0.009156 | 4.4312 | 122.4518 | 0.32501 | 122.4472 | 122.5021 | 122.3785 | 122.4426 | 122.3648 | -122.4838 | -122.438 | 122.3923 | 122.4335 | 45.9732 | 45.7672
1977.7656 | 122.5754 | -49.1089 | 73.3292 | -0.079269 | -1.0718e-05 | 0.062239 | 0.11697 | 0.0012391 | -0.0031402 | -0.0024566 | -0.00030524 | -0.0024096 | 0.061829 | 0.059981 | -0.029781 | 0.00077333 | 0.0016021 | -3.3279 | 73.2971 | -49.2142 | 73.1781 | -44.7968 | -49.3515 | 2.4445 | -3.6209 | 73.2513 | -49.1638 | 73.2422 | -48.8754 | -49.2096 | -49.0036 | -0.10528 | -0.032044 | -0.15106 | 4.3121 | 51.5533 | -0.24261 | 51.6586 | -0.13733 | -0.054931 | -0.07782 | -0.086976 | 0.23346 | 0.10529 | -0.10071 | 0.16022 | -0.045777 | 4.4174 | 122.3923 | 0.28839 | 122.406 | 122.5113 | 122.4152 | 122.406 | 122.3602 | -122.5433 | -122.493 | 122.287 | 122.3511 | 45.7809 | 45.488
1978.8438 | 122.699 | -49.173 | 73.1964 | -0.11742 | 0.0044755 | 0.059889 | 0.11804 | -0.0017517 | -0.0003632 | -0.0037384 | 0.042419 | -0.0045458 | 0.063538 | 0.060408 | -0.027859 | 0.00034613 | 0.0026703 | -3.1128 | 73.1598 | -49.3744 | 73.0453 | -44.9524 | -49.4659 | 2.3895 | -3.4882 | 73.0911 | -49.2691 | 73.233 | -48.8892 | -49.2233 | -49.0448 | -0.20142 | -0.036621 | -0.15106 | 4.2206 | 51.5625 | -0.29297 | 51.7639 | -0.091552 | -0.09613 | -0.10529 | 0.036621 | 0.28381 | 0.12817 | -0.050354 | 0.2243 | 0.045776 | 4.422 | 122.4197 | 0.37994 | 122.5021 | 122.5342 | 122.3602 | 122.3328 | 122.2641 | -122.5708 | -122.4655 | 122.2183 | 122.406 | 46.0602 | 45.6848
1979.7656 | 122.6028 | -49.205 | 73.2605 | -0.086899 | 0.0016983 | 0.06288 | 0.11441 | -0.0011109 | -0.0003632 | -0.001175 | -0.018616 | -0.0024096 | 0.064392 | 0.062117 | -0.027431 | -0.0011493 | -0.00074771 | -3.4149 | 73.1552 | -49.3469 | 73.0637 | -45.0165 | -49.4751 | 2.4124 | -3.5202 | 73.114 | -49.2691 | 73.1689 | -48.9532 | -49.2828 | -49.0677 | -0.14191 | -0.10529 | -0.19684 | 4.1885 | 51.6174 | -0.27008 | 51.7593 | -0.12817 | -0.064087 | -0.14648 | -0.091553 | 0.25177 | 0.13733 | -0.07782 | 0.20142 | -0.013733 | 4.3304 | 122.4106 | 0.31586 | 122.438 | 122.5021 | 122.3831 | 122.3602 | 122.319 | -122.6074 | -122.5296 | 122.2687 | 122.374 | 45.7901 | 45.6848
1980.7656 | 122.6166 | -49.8276 | 72.6242 | -0.07164 | -0.00043792 | 0.062239 | 0.11676 | 0.0025207 | -0.0063446 | -0.00010676 | -0.088806 | -0.0034778 | 0.065247 | 0.05934 | -0.028927 | -0.00072207 | -0.00010671 | -3.685 | 72.5739 | -49.9924 | 72.4869 | -45.9045 | -50.0839 | 2.3026 | -3.8315 | 72.583 | -49.8596 | 72.6151 | -49.5529 | -49.9374 | -49.6674 | -0.16479 | -0.050354 | -0.13733 | 3.923 | 52.1301 | -0.25635 | 52.2949 | -0.091552 | -0.032043 | -0.041199 | -0.009156 | 0.27466 | 0.16022 | -0.10986 | 0.19226 | -0.07782 | 4.0878 | 122.4792 | 0.3067 | 122.4747 | 122.5662 | 122.4426 | 122.4014 | 122.4106 | -122.6166 | -122.4838 | 122.3145 | 122.4426 | 46.1426 | 45.9961
1981.8281 | 122.7173 | -49.649 | 72.7249 | -0.07164 | -0.00043792 | 0.062239 | 0.11611 | -0.00025628 | -0.0037812 | -0.002243 | 0.28046 | -0.0064684 | 0.065888 | 0.061049 | -0.027645 | 0.00098693 | -0.00010671 | -3.6301 | 72.6288 | -49.8138 | 72.702 | -45.5704 | -49.8642 | 2.3941 | -3.7399 | 72.6334 | -49.7635 | 72.7753 | -49.324 | -49.6994 | -49.5117 | -0.16479 | -0.096131 | -0.022889 | 4.0787 | 52.0432 | -0.21515 | 52.2079 | -0.050354 | -0.11444 | -0.091553 | 0.050354 | 0.32501 | 0.13733 | -0.050354 | 0.25177 | 0.064087 | 4.2435 | 122.5159 | 0.43945 | 122.5388 | 122.4426 | 122.3969 | 122.2778 | 122.2824 | -122.5388 | -122.4884 | 122.3511 | 122.4243 | 46.019 | 45.9091
1982.7656 | 122.5662 | -49.823 | 72.6471 | -0.033493 | 0.00020288 | 0.062239 | 0.11718 | -0.0034607 | -0.0031402 | -0.00032036 | -0.058289 | -0.00048703 | 0.063965 | 0.064681 | -0.02615 | -0.00072207 | -0.0020295 | -3.6072 | 72.5967 | -49.9603 | 72.4365 | -45.9686 | -50.1434 | 2.2568 | -3.7445 | 72.5693 | -49.8871 | 72.5418 | -49.6078 | -49.9466 | -49.7406 | -0.13733 | -0.050354 | -0.21057 | 3.8544 | 52.0798 | -0.32044 | 52.2171 | -0.18311 | -0.064087 | -0.07782 | -0.10529 | 0.21515 | 0.082397 | -0.1236 | 0.14648 | -0.059509 | 3.9917 | 122.3969 | 0.27924 | 122.4289 | 122.5571 | 122.4564 | 122.4197 | 122.3923 | -122.6074 | -122.5342 | 122.2595 | 122.3648 | 46.2158 | 46.0785
1983.8281 | 122.7081 | -49.4659 | 72.8897 | -0.13267 | 0.0012711 | 0.061385 | 0.11868 | -0.00068368 | -0.0033538 | -0.00074776 | -0.052185 | -0.0036914 | 0.061615 | 0.066817 | -0.028072 | 0.0022687 | -0.00074771 | -3.5706 | 72.8714 | -49.6262 | 72.8394 | -45.3735 | -49.7635 | 2.124 | -3.653 | 72.8531 | -49.5438 | 72.9721 | -49.173 | -49.53 | -49.292 | -0.16022 | -0.01831 | -0.050354 | 4.0924 | 51.59 | -0.29755 | 51.7502 | -0.13733 | -0.07782 | -0.036621 | 0.082398 | 0.29297 | 0.17395 | -0.064087 | 0.25177 | 0.013733 | 4.2526 | 122.4655 | 0.37079 | 122.5159 | 122.4976 | 122.3969 | 122.3373 | 122.319 | -122.5159 | -122.4335 | 122.3053 | 122.438 | 45.8954 | 45.813
1984.7656 | 122.5662 | -49.9237 | 72.551 | -0.10216 | -1.0718e-05 | 0.060316 | 0.1159 | -0.00025628 | -0.004422 | -0.0026704 | -0.015564 | -0.001128 | 0.063324 | 0.056563 | -0.027859 | 0.0014141 | 0.0026703 | -3.7628 | 72.496 | -50.0519 | 72.3633 | -46.0648 | -50.1755 | 2.2293 | -3.7674 | 72.5189 | -49.9603 | 72.377 | -49.7589 | -49.9283 | -49.7498 | -0.12817 | -0.054931 | -0.18768 | 3.8589 | 52.153 | -0.25177 | 52.2812 | -0.1236 | -0.036621 | -0.032043 | -0.17395 | 0.1648 | 0.17395 | -0.004578 | 0.21057 | 0.032043 | 3.9871 | 122.4152 | 0.20142 | 122.3373 | 122.5479 | 122.4792 | 122.4197 | 122.4426 | -122.6028 | -122.5113 | 122.287 | 122.3007 | 46.1609 | 46.1563
1985.7656 | 122.5708 | -49.0814 | 73.3795 | -0.06401 | -0.00043792 | 0.059889 | 0.1174 | 0.00038452 | -0.004422 | -0.0026704 | -0.070496 | -0.001128 | 0.063538 | 0.06169 | -0.027431 | 0.00013253 | -0.00010671 | -3.5431 | 73.3063 | -49.2645 | 73.1506 | -44.87 | -49.3835 | 2.3483 | -3.7491 | 73.3154 | -49.1592 | 73.2697 | -48.8846 | -49.2142 | -49.0128 | -0.1831 | -0.073243 | -0.22888 | 4.2114 | 51.4297 | -0.30212 | 51.6129 | -0.11902 | -0.07782 | -0.064087 | -0.10986 | 0.19684 | 0.068665 | -0.13275 | 0.14648 | -0.054931 | 4.3945 | 122.4152 | 0.27466 | 122.4289 | 122.5708 | 122.4747 | 122.3877 | 122.3969 | -122.644 | -122.5388 | 122.2321 | 122.3511 | 45.5383 | 45.3323
1986.8281 | 122.5937 | -49.1638 | 73.2422 | -0.079269 | 0.0021255 | 0.062239 | 0.11547 | -0.0038879 | -0.0039948 | -0.0033112 | -0.024719 | -0.0024096 | 0.063965 | 0.058913 | -0.026577 | 0.00055973 | 0.0063019 | -3.273 | 73.2101 | -49.3149 | 73.1552 | -44.8654 | -49.3835 | 2.4994 | -3.6942 | 73.2239 | -49.173 | 73.2559 | -48.88 | -49.2233 | -49.0768 | -0.15106 | -0.032043 | -0.086975 | 4.2984 | 51.6632 | -0.21973 | 51.8143 | -0.068665 | -0.009156 | -0.01831 | 0.013733 | 0.28381 | 0.086975 | -0.05951 | 0.096131 | -0.050354 | 4.4495 | 122.4701 | 0.29297 | 122.4289 | 122.525 | 122.3969 | 122.374 | 122.3877 | -122.5571 | -122.4152 | 122.319 | 122.4197 | 45.8908 | 45.4697
1987.7656 | 122.6166 | -49.2828 | 73.1232 | -0.086899 | 0.0012711 | 0.06288 | 0.11761 | 0.0020935 | -0.0033538 | -0.00010676 | -0.10406 | -0.00048703 | 0.063324 | 0.064467 | -0.027859 | 0.00055973 | 0.0011749 | -3.3646 | 73.114 | -49.4293 | 73.0133 | -45.076 | -49.5712 | 2.5314 | -3.7308 | 73.0865 | -49.3607 | 73.1186 | -49.0448 | -49.3835 | -49.173 | -0.14648 | -0.009155 | -0.10986 | 4.2068 | 51.8143 | -0.28839 | 51.9608 | -0.14191 | -0.07782 | -0.036621 | -0.004578 | 0.23804 | 0.10986 | -0.10071 | 0.18768 | -0.022888 | 4.3533 | 122.4426 | 0.31586 | 122.4792 | 122.5433 | 122.4472 | 122.3969 | 122.3694 | -122.5525 | -122.4838 | 122.2961 | 122.4014 | 45.9183 | 45.5521
1988.8281 | 122.58 | -49.53 | 72.8714 | 0.080948 | 0.00063028 | 0.061812 | 0.11911 | 0.0014527 | -0.002713 | -0.0037384 | -0.09491 | -0.0028368 | 0.064606 | 0.061049 | -0.027645 | 0.0033367 | 0.0039521 | -3.5751 | 72.8989 | -49.6445 | 72.7478 | -45.4834 | -49.8596 | 2.3163 | -3.8498 | 72.876 | -49.6033 | 72.8577 | -49.3515 | -49.7131 | -49.4614 | -0.11444 | 0.027466 | -0.1236 | 4.0466 | 51.8463 | -0.32959 | 51.9608 | -0.21515 | -0.073242 | 0.004578 | -0.013733 | 0.17853 | 0.068664 | -0.18311 | 0.14191 | -0.10986 | 4.1611 | 122.3923 | 0.25177 | 122.4609 | 122.5433 | 122.4792 | 122.4289 | 122.406 | -122.5159 | -122.4747 | 122.2778 | 122.3877 | 45.9549 | 45.6802
1989.7656 | 122.58 | -49.4339 | 72.995 | -0.056381 | 0.0025529 | 0.061385 | 0.11782 | -0.0015381 | -0.0018586 | -0.0013886 | -0.015564 | -0.001128 | 0.063965 | 0.060195 | -0.026577 | 0.0018413 | 0.0041657 | -3.4561 | 73.0225 | -49.5621 | 72.8027 | -45.3552 | -49.7314 | 2.5269 | -3.8681 | 72.9309 | -49.4934 | 72.8897 | -49.2188 | -49.5758 | -49.3423 | -0.12817 | 0.027466 | -0.19226 | 4.0787 | 51.9608 | -0.29755 | 52.0889 | -0.16937 | -0.059509 | -0.064087 | -0.10529 | 0.21515 | 0.091553 | -0.14191 | 0.15106 | -0.082398 | 4.2068 | 122.3648 | 0.27466 | 122.3831 | 122.5845 | 122.4243 | 122.4564 | 122.3648 | -122.5571 | -122.4884 | 122.2366 | 122.3236 | 45.9778 | 45.5658
1990.8281 | 122.6028 | -49.3469 | 73.0591 | -0.056381 | -0.0015061 | 0.063094 | 0.11761 | 0.0020935 | -0.0033538 | -0.0050202 | -0.076599 | -0.0019824 | 0.063751 | 0.069167 | -0.027004 | 0.0022687 | -0.00032051 | -3.5019 | 73.0499 | -49.4614 | 72.963 | -45.1447 | -49.5987 | 2.3346 | -3.7582 | 73.0362 | -49.3881 | 73.0545 | -49.1089 | -49.4751 | -49.2416 | -0.11444 | -0.009155 | -0.09613 | 4.2023 | 51.6815 | -0.25177 | 51.796 | -0.13733 | -0.041199 | -0.022888 | -0.004578 | 0.23804 | 0.10529 | -0.12817 | 0.14648 | -0.086975 | 4.3167 | 122.4243 | 0.27924 | 122.4426 | 122.5113 | 122.4243 | 122.3969 | 122.3831 | -122.5204 | -122.4472 | 122.3099 | 122.4014 | 45.845 | 45.5887
1991.7656 | 122.612 | -49.1684 | 73.2285 | -0.048752 | -0.00022432 | 0.062239 | 0.11804 | 0.00081172 | -0.002713 | -0.001175 | -0.14374 | -0.002196 | 0.062897 | 0.058058 | -0.02914 | 0.0014141 | 0.0048065 | -3.3646 | 73.3154 | -49.2325 | 73.2193 | -44.8151 | -49.3561 | 2.2934 | -3.7125 | 73.2697 | -49.2004 | 73.233 | -48.912 | -49.2554 | -48.9212 | -0.064087 | 0.086975 | -0.009156 | 4.3533 | 51.4618 | -0.18768 | 51.5259 | -0.1236 | -0.032043 | 0.041198 | 0.004577 | 0.25635 | 0.24719 | -0.086975 | 0.27923 | -0.054932 | 4.4174 | 122.4518 | 0.28839 | 122.4335 | 122.5479 | 122.4701 | 122.4838 | 122.438 | -122.4609 | -122.4289 | 122.3877 | 122.4014 | 45.8038 | 45.4559
1992.8281 | 122.6028 | -49.8093 | 72.6471 | -0.06401 | 0.0014847 | 0.062025 | 0.11654 | 0.0031617 | -0.0022858 | -0.00053396 | -0.049133 | -0.001128 | 0.062042 | 0.065322 | -0.027218 | 0.00098693 | 0.0016021 | -3.7537 | 72.5739 | -49.9832 | 72.4915 | -45.9229 | -50.0793 | 2.0828 | -3.8727 | 72.5601 | -49.8642 | 72.6196 | -49.5392 | -49.8825 | -49.6353 | -0.17395 | -0.073242 | -0.15564 | 3.8864 | 51.8921 | -0.27008 | 52.066 | -0.096131 | -0.054932 | -0.086975 | -0.027466 | 0.27008 | 0.17395 | -0.073242 | 0.22888 | -0.01831 | 4.0604 | 122.4747 | 0.32501 | 122.4838 | 122.5571 | 122.4243 | 122.3831 | 122.3694 | -122.6303 | -122.5113 | 122.3007 | 122.4289 | 46.0556 | 45.9366
1993.7656 | 122.5937 | -49.1272 | 73.2559 | -0.12505 | -0.00086512 | 0.063307 | 0.11569 | -0.00089728 | -0.004422 | -0.00096136 | -0.088806 | -0.0054004 | 0.063111 | 0.065962 | -0.02615 | 0.00098693 | 0.0024567 | -3.685 | 73.3246 | -49.2371 | 73.1461 | -44.9249 | -49.4156 | 1.8997 | -3.8681 | 73.2422 | -49.1913 | 73.2742 | -48.8617 | -49.2233 | -49.0265 | -0.10986 | 0.068665 | -0.10986 | 4.2023 | 51.0269 | -0.28839 | 51.1368 | -0.17853 | -0.064087 | -0.013733 | 0.018311 | 0.2655 | 0.10071 | -0.096131 | 0.1648 | -0.032044 | 4.3121 | 122.3831 | 0.32959 | 122.4655 | 122.5616 | 122.4335 | 122.4518 | 122.3694 | -122.493 | -122.4472 | 122.2733 | 122.4014 | 45.4422 | 45.2591
1994.7656 | 122.6257 | -49.1867 | 73.2376 | -0.056381 | -1.0718e-05 | 0.064162 | 0.11718 | 0.0040161 | -0.0014312 | -0.003952 | -0.039978 | -0.0060412 | 0.062256 | 0.057845 | -0.027645 | 0.00034613 | 0.00096129 | -3.8544 | 73.2101 | -49.3652 | 73.027 | -45.076 | -49.4751 | 2.1698 | -3.978 | 73.1552 | -49.2462 | 73.1964 | -48.967 | -49.3011 | -49.086 | -0.17853 | -0.027466 | -0.21057 | 4.1107 | 51.3565 | -0.28839 | 51.535 | -0.10986 | -0.059509 | -0.082398 | -0.041199 | 0.21973 | 0.10071 | -0.11444 | 0.16022 | -0.054931 | 4.2892 | 122.3923 | 0.27924 | 122.4426 | 122.5754 | 122.4014 | 122.3969 | 122.3419 | -122.6028 | -122.4838 | 122.2137 | 122.3831 | 45.3323 | 45.2087
1995.8281 | 122.5937 | -49.086 | 73.3383 | -0.07164 | -0.0012923 | 0.065016 | 0.11804 | 0.0023071 | -0.0022858 | -0.0020294 | -0.067444 | -0.0034778 | 0.064179 | 0.062331 | -0.027645 | 0.00098693 | 0.0048065 | -3.9688 | 73.2239 | -49.3286 | 73.1506 | -44.9341 | -49.4156 | 2.124 | -3.9139 | 73.2056 | -49.2096 | 73.2971 | -48.8617 | -49.1638 | -48.9761 | -0.24261 | -0.11444 | -0.18768 | 4.1519 | 51.21 | -0.32959 | 51.4526 | -0.086975 | -0.1236 | -0.13275 | -0.041199 | 0.22431 | 0.10986 | -0.077819 | 0.23346 | 0.045777 | 4.3945 | 122.4792 | 0.3479 | 122.5067 | 122.5525 | 122.4152 | 122.3099 | 122.2916 | -122.6669 | -122.5479 | 122.2366 | 122.3831 | 45.1172 | 45.1721
1996.7656 | 122.5571 | -48.9532 | 73.4573 | -0.1403 | -0.00022432 | 0.060744 | 0.11804 | 0.0046569 | -0.0050628 | -0.0024566 | -0.079651 | -0.0028368 | 0.063324 | 0.059981 | -0.02914 | -0.00050847 | 0.00074769 | -3.891 | 73.4116 | -49.1547 | 73.288 | -44.664 | -49.2691 | 2.1469 | -4.1382 | 73.4528 | -48.9853 | 73.4253 | -48.7518 | -49.1043 | -48.88 | -0.20142 | -0.045776 | -0.16937 | 4.2892 | 51.1002 | -0.31586 | 51.3016 | -0.11444 | -0.032044 | -0.004577 | -0.032043 | 0.20142 | 0.073242 | -0.15106 | 0.10529 | -0.11902 | 4.4907 | 122.4426 | 0.23346 | 122.4106 | 122.5662 | 122.4381 | 122.3648 | 122.406 | -122.612 | -122.4426 | 122.2412 | 122.3785 | 45.0623 | 44.8151
1997.8281 | 122.6303 | -48.9716 | 73.4528 | -0.033493 | -0.0017197 | 0.059248 | 0.11633 | 0.0010253 | -0.0029266 | -0.0026704 | -0.012512 | -0.003905 | 0.063751 | 0.058486 | -0.027218 | 0.0024823 | -0.00096131 | -3.6163 | 73.4711 | -49.0952 | 73.2651 | -44.696 | -49.2874 | 2.2934 | -4.0375 | 73.3795 | -49.0631 | 73.4024 | -48.7473 | -49.0723 | -48.8754 | -0.1236 | 0.01831 | -0.18768 | 4.2755 | 51.265 | -0.31586 | 51.3886 | -0.19226 | -0.091552 | -0.073242 | -0.050354 | 0.22431 | 0.096131 | -0.10071 | 0.18768 | -0.009156 | 4.3991 | 122.3602 | 0.31586 | 122.4655 | 122.5662 | 122.4426 | 122.4426 | 122.3511 | -122.5479 | -122.5159 | 122.2366 | 122.374 | 45.3552 | 44.9341
1998.7656 | 122.6395 | -49.173 | 73.2697 | -0.10979 | 0.00020288 | 0.063734 | 0.11782 | -0.00089728 | -0.0024994 | -0.002243 | -0.036926 | -0.0032642 | 0.063324 | 0.057631 | -0.029995 | 0.0016277 | 0.0020295 | -3.5843 | 73.2376 | -49.3423 | 73.0499 | -45.0394 | -49.4797 | 2.3438 | -4.0283 | 73.1781 | -49.2783 | 73.1781 | -48.9349 | -49.2691 | -49.0585 | -0.16937 | -0.032043 | -0.21973 | 4.1336 | 51.5167 | -0.3067 | 51.6861 | -0.13733 | -0.10528 | -0.091552 | -0.091552 | 0.23804 | 0.11444 | -0.09613 | 0.21973 | 0.009155 | 4.303 | 122.3923 | 0.34332 | 122.4564 | 122.58 | 122.4564 | 122.4106 | 122.3511 | -122.612 | -122.5479 | 122.2229 | 122.3511 | 45.5887 | 45.1447
1999.8281 | 122.5479 | -50.0015 | 72.4548 | -0.079269 | -0.0010787 | 0.062025 | 0.11718 | -0.0023925 | -0.002713 | 0.00096124 | -0.058289 | -0.0028368 | 0.063965 | 0.068312 | -0.02914 | 0.00013253 | 0.0043793 | -3.5202 | 72.3816 | -50.1801 | 72.2031 | -46.2708 | -50.3815 | 2.1652 | -4.4495 | 72.3404 | -50.1114 | 72.345 | -49.8367 | -50.2213 | -49.942 | -0.17853 | -0.073242 | -0.25177 | 3.7308 | 52.1667 | -0.37994 | 52.3453 | -0.20142 | -0.10986 | -0.11444 | -0.10986 | 0.16479 | 0.059509 | -0.21973 | 0.16937 | -0.10986 | 3.9093 | 122.3831 | 0.27466 | 122.4564 | 122.5616 | 122.4518 | 122.3831 | 122.3419 | -122.6349 | -122.5662 | 122.2046 | 122.3465 | 46.4813 | 45.5521
2000.7656 | 122.5983 | -49.6216 | 72.8027 | -0.086899 | 0.00084388 | 0.061171 | 0.12017 | -0.00089728 | -0.0052764 | -0.0035248 | -0.021667 | -0.0017688 | 0.06546 | 0.055068 | -0.028713 | 0.00055973 | -0.00053411 | -3.479 | 72.7798 | -49.7955 | 72.6196 | -45.6619 | -49.9512 | 2.2339 | -4.0558 | 72.7066 | -49.704 | 72.7341 | -49.3835 | -49.7223 | -49.5392 | -0.17395 | -0.022888 | -0.1831 | 3.9597 | 51.8555 | -0.32959 | 52.0294 | -0.15564 | -0.082397 | -0.09613 | -0.068664 | 0.23804 | 0.082397 | -0.10071 | 0.16479 | -0.018311 | 4.1336 | 122.4152 | 0.32043 | 122.438 | 122.5754 | 122.4106 | 122.4014 | 122.3282 | -122.5983 | -122.5067 | 122.2412 | 122.3557 | 46.1426 | 45.5658
2001.8281 | 122.5662 | -49.5483 | 72.8851 | -0.079269 | -0.00043792 | 0.064375 | 0.11676 | 0.0031617 | -0.0039948 | -0.00053396 | -0.049133 | -0.0030506 | 0.064606 | 0.059767 | -0.027218 | 0.0024823 | 0.00032049 | -3.4927 | 72.8531 | -49.6994 | 72.7249 | -45.4834 | -49.8367 | 2.2751 | -4.0237 | 72.8439 | -49.6216 | 72.821 | -49.3378 | -49.6902 | -49.4476 | -0.15106 | -0.032044 | -0.16022 | 4.0649 | 51.8234 | -0.28839 | 51.9745 | -0.13733 | -0.073242 | -0.041199 | -0.064087 | 0.21057 | 0.10071 | -0.14191 | 0.17395 | -0.068665 | 4.216 | 122.4243 | 0.28381 | 122.4426 | 122.5525 | 122.4655 | 122.4014 | 122.3923 | -122.5845 | -122.5067 | 122.2733 | 122.3694 | 46.0556 | 45.5246
2002.7656 | 122.6166 | -49.2599 | 73.1735 | -0.048752 | 0.0010575 | 0.061812 | 0.1174 | 0.0016663 | -0.0016448 | -0.0037384 | -0.027771 | -0.0032642 | 0.063538 | 0.059981 | -0.028072 | 0.00013253 | 0.0020295 | -3.2639 | 73.1415 | -49.4293 | 73.0087 | -45.0394 | -49.5483 | 2.4078 | -3.923 | 73.0957 | -49.3195 | 73.1186 | -49.1638 | -49.2233 | -49.0402 | -0.16937 | -0.032044 | -0.16479 | 4.2206 | 51.6678 | -0.28839 | 51.8372 | -0.11902 | -0.059509 | -0.07782 | -0.054932 | 0.096131 | 0.21973 | 0.036621 | 0.27924 | 0.09613 | 4.39 | 122.438 | 0.15564 | 122.438 | 122.5708 | 122.4152 | 122.4014 | 122.3557 | -122.6028 | -122.493 | 122.2687 | 122.3785 | 45.9961 | 45.3369
2003.8281 | 122.5937 | -49.086 | 73.3521 | -0.086899 | 0.0031937 | 0.064589 | 0.11804 | 0.0010253 | -0.0029266 | -0.0024566 | -0.04303 | -0.0036914 | 0.065033 | 0.064467 | -0.026577 | 0.00034613 | 0.0016021 | -3.2822 | 73.32 | -49.2371 | 73.1232 | -44.8288 | -49.4385 | 2.3941 | -4.0375 | 73.2697 | -49.1364 | 73.3063 | -48.8571 | -49.205 | -48.967 | -0.15106 | -0.032044 | -0.22888 | 4.2572 | 51.4801 | -0.35248 | 51.6312 | -0.20142 | -0.050354 | -0.082398 | -0.045777 | 0.22888 | 0.11902 | -0.11902 | 0.16937 | -0.068664 | 4.4083 | 122.3602 | 0.27924 | 122.4426 | 122.5571 | 122.406 | 122.406 | 122.3557 | -122.5891 | -122.4884 | 122.2092 | 122.3923 | 45.8038 | 45.0485
2004.7656 | 122.5433 | -49.2508 | 73.2056 | -0.07164 | -0.0019333 | 0.062666 | 0.11953 | 0.0035889 | -0.0005768 | -0.0016022 | -0.04303 | -0.0024096 | 0.063751 | 0.054 | -0.0285 | 0.00055973 | 0.0011749 | -3.1677 | 73.1506 | -49.4019 | 73.0728 | -45.0027 | -49.5163 | 2.5314 | -4.0192 | 73.1506 | -49.2737 | 73.1506 | -49.0128 | -49.4751 | -49.2416 | -0.15106 | -0.054931 | -0.13275 | 4.248 | 51.7822 | -0.2655 | 51.9333 | -0.11444 | -0.022889 | -0.054931 | -0.054931 | 0.23804 | 0.009155 | -0.22431 | 0.032044 | -0.20142 | 4.3991 | 122.4747 | 0.26093 | 122.4243 | 122.5525 | 122.4243 | 122.4014 | 122.4014 | -122.6074 | -122.4792 | 122.3236 | 122.4014 | 46.0831 | 45.2316
2005.8281 | 122.6166 | -48.8846 | 73.5443 | -0.10216 | -0.00065152 | 0.062239 | 0.11782 | 0.0027343 | -0.0003632 | 0.00010684 | 0.054627 | -0.0034778 | 0.063324 | 0.060195 | -0.026577 | 0.00055973 | 0.0011749 | -3.1219 | 73.4436 | -49.086 | 73.3612 | -44.5267 | -49.1684 | 2.5314 | -3.9139 | 73.439 | -48.9716 | 73.4802 | -48.6694 | -48.9761 | -48.7885 | -0.20142 | -0.10071 | -0.18311 | 4.3579 | 51.416 | -0.28381 | 51.6174 | -0.082397 | -0.086975 | -0.10529 | -0.064087 | 0.21515 | 0.096131 | -0.091552 | 0.18311 | -0.004577 | 4.5593 | 122.4472 | 0.30212 | 122.4518 | 122.5296 | 122.4106 | 122.3282 | 122.3236 | -122.6303 | -122.5159 | 122.2458 | 122.3648 | 45.7626 | 44.9707
2006.7656 | 122.5983 | -48.9899 | 73.4116 | -0.07164 | 0.0012711 | 0.061598 | 0.11611 | -0.0021789 | -0.0042084 | -0.0035248 | -0.030823 | -0.0017688 | 0.061402 | 0.056777 | -0.027859 | 0.0018413 | 0.00074769 | -3.0441 | 73.4116 | -49.1135 | 73.3109 | -44.6091 | -49.2554 | 2.536 | -3.9505 | 73.3658 | -49.0448 | 73.3887 | -48.7839 | -49.1089 | -48.8983 | -0.1236 | 0 | -0.10071 | 4.3808 | 51.5259 | -0.2655 | 51.6495 | -0.14191 | -0.054932 | -0.045776 | -0.022888 | 0.20599 | 0.091553 | -0.11902 | 0.14649 | -0.064087 | 4.5044 | 122.4243 | 0.26093 | 122.4335 | 122.525 | 122.4106 | 122.4014 | 122.3557 | -122.525 | -122.4564 | 122.3007 | 122.3785 | 45.9457 | 45.0394
2007.8281 | 122.5983 | -49.1684 | 73.2605 | -0.10216 | 0.0019119 | 0.062666 | 0.11782 | 0.00038452 | -0.0037812 | -0.0041656 | -0.039978 | -0.0045458 | 0.063324 | 0.054213 | -0.030422 | 0.00077333 | 0.0028839 | -3.0487 | 73.1781 | -49.3515 | 73.0911 | -44.8746 | -49.4476 | 2.623 | -4.0192 | 73.1781 | -49.2554 | 73.201 | -48.9578 | -49.2554 | -49.0768 | -0.1831 | -0.082397 | -0.16937 | 4.2938 | 51.7914 | -0.27924 | 51.9745 | -0.096131 | -0.086975 | -0.082397 | -0.059509 | 0.21057 | 0.091553 | -0.086975 | 0.17853 | 0 | 4.4769 | 122.4426 | 0.29755 | 122.4564 | 122.5296 | 122.4335 | 122.3465 | 122.3465 | -122.612 | -122.5159 | 122.2595 | 122.3694 | 46.1197 | 45.1492
2008.7656 | 122.5937 | -49.205 | 73.2147 | -0.041122 | -0.00022432 | 0.063094 | 0.11654 | 0.0059387 | -0.0014312 | -0.0016022 | -0.036926 | -0.003905 | 0.064179 | 0.054 | -0.026577 | 0.0026959 | 0.0011749 | -3.1723 | 73.2101 | -49.3286 | 73.0865 | -44.9387 | -49.53 | 2.6184 | -4.01 | 73.1232 | -49.3011 | 73.1781 | -49.0036 | -49.2966 | -49.0906 | -0.1236 | -0.004578 | -0.12817 | 4.2664 | 51.8234 | -0.32501 | 51.947 | -0.20142 | -0.09613 | -0.091553 | -0.036621 | 0.20142 | 0.11444 | -0.091553 | 0.21057 | 0.004577 | 4.39 | 122.4152 | 0.29755 | 122.4792 | 122.5388 | 122.4243 | 122.4152 | 122.3282 | -122.5433 | -122.5159 | 122.2916 | 122.3831 | 46.0327 | 45.195
2009.8281 | 122.5708 | -49.1776 | 73.2834 | -0.086899 | -0.00065152 | 0.062025 | 0.11846 | 0.0042297 | -0.0018586 | -0.0018158 | -0.027771 | -0.002196 | 0.063965 | 0.056136 | -0.027859 | 0.0014141 | 0.0035247 | -3.1906 | 73.2101 | -49.3423 | 73.0316 | -44.9203 | -49.5438 | 2.6642 | -4.2252 | 73.2056 | -49.2279 | 73.1689 | -49.0082 | -49.3332 | -49.1043 | -0.16479 | -0.073242 | -0.25177 | 4.2572 | 51.8417 | -0.36621 | 52.0065 | -0.20142 | -0.050354 | -0.07782 | -0.11444 | 0.16937 | 0.073242 | -0.15564 | 0.1236 | -0.10529 | 4.422 | 122.374 | 0.21973 | 122.3969 | 122.5525 | 122.4335 | 122.3877 | 122.3831 | -122.6257 | -122.5113 | 122.2092 | 122.3465 | 45.9869 | 44.9524
2010.7656 | 122.5754 | -49.0265 | 73.3978 | -0.13267 | -0.00065152 | 0.061385 | 0.11868 | 0.0027343 | -0.001004 | -0.002884 | -0.06134 | -0.003905 | 0.064392 | 0.062758 | -0.027004 | 0.0020551 | 0.0013885 | -3.035 | 73.4116 | -49.1318 | 73.2697 | -44.577 | -49.2874 | 2.7557 | -4.1794 | 73.3887 | -49.054 | 73.3292 | -48.8388 | -49.1821 | -48.9487 | -0.10529 | 0.013733 | -0.12817 | 4.4495 | 51.7822 | -0.26093 | 51.8875 | -0.15564 | -0.027466 | -0.009155 | -0.068664 | 0.18768 | 0.07782 | -0.15564 | 0.10529 | -0.12817 | 4.5547 | 122.4014 | 0.21515 | 122.3831 | 122.5433 | 122.4426 | 122.438 | 122.4152 | -122.5296 | -122.4518 | 122.2961 | 122.3557 | 45.9915 | 44.8471
2011.8281 | 122.6028 | -49.054 | 73.3795 | -0.18608 | -0.0021469 | 0.062666 | 0.11761 | 0.00017092 | -0.0031402 | -0.0026704 | -0.027771 | -0.0051868 | 0.061829 | 0.061476 | -0.027645 | 0.00055973 | -0.00010671 | -2.9572 | 73.3932 | -49.1592 | 73.2239 | -44.6686 | -49.3286 | 2.8152 | -4.0649 | 73.32 | -49.1043 | 73.3292 | -48.848 | -49.1318 | -48.9532 | -0.10529 | 0.013733 | -0.15564 | 4.3854 | 51.8692 | -0.27466 | 51.9745 | -0.16937 | -0.050354 | -0.05951 | -0.050354 | 0.20599 | 0.10071 | -0.07782 | 0.15106 | -0.027466 | 4.4907 | 122.3831 | 0.25635 | 122.4335 | 122.5525 | 122.4243 | 122.4472 | 122.374 | -122.5388 | -122.4838 | 122.2778 | 122.3831 | 46.0968 | 44.989
2012.7656 | 122.5479 | -48.9395 | 73.4985 | -0.079269 | 0.00041648 | 0.063094 | 0.11846 | 0.0027343 | -0.0029266 | 0.0013886 | -0.06134 | -0.0034778 | 0.064179 | 0.062545 | -0.028286 | -0.00029487 | 0.0028839 | -2.8564 | 73.4482 | -49.118 | 73.2788 | -44.5496 | -49.2828 | 2.8931 | -5.191 | 73.4436 | -49.0311 | 73.4207 | -48.761 | -49.0997 | -48.8892 | -0.17853 | -0.050354 | -0.21973 | 4.39 | 51.8326 | -0.34332 | 52.0111 | -0.16479 | -0.091553 | -0.054931 | -0.07782 | 0.17853 | 0.050354 | -0.16022 | 0.14191 | -0.068664 | 4.5685 | 122.3969 | 0.27008 | 122.4518 | 122.5662 | 122.4747 | 122.3877 | 122.3831 | -122.6166 | -122.5296 | 122.2183 | 122.3602 | 46.0831 | 43.7485
2013.8281 | 122.5708 | -49.2783 | 73.1323 | -0.12505 | 0.00041648 | 0.064375 | 0.11633 | 0.00059812 | -0.0018586 | -0.002884 | -0.027771 | -0.0028368 | 0.064179 | 0.058699 | -0.027431 | 0.0016277 | -0.00032051 | -2.9205 | 73.1186 | -49.4202 | 72.9721 | -45.0668 | -49.6262 | 2.8015 | -4.509 | 73.0774 | -49.3835 | 73.0637 | -49.1226 | -49.4339 | -49.2096 | -0.14191 | -0.013733 | -0.16022 | 4.2114 | 52.0798 | -0.3479 | 52.2217 | -0.20599 | -0.10529 | -0.054931 | -0.068664 | 0.15564 | 0.068664 | -0.15564 | 0.17395 | -0.050354 | 4.3533 | 122.3923 | 0.26093 | 122.4472 | 122.5388 | 122.4609 | 122.3969 | 122.3557 | -122.5525 | -122.5159 | 122.2504 | 122.3419 | 46.3577 | 44.7693
2014.7656 | 122.6074 | -49.1135 | 73.3017 | -0.094528 | 0.0014847 | 0.061812 | 0.1159 | -0.00089728 | -0.0057038 | -0.0030976 | -0.033874 | -0.00091423 | 0.062256 | 0.061904 | -0.028927 | 0.00098693 | 0.0041657 | -3.0945 | 73.2147 | -49.3332 | 73.114 | -44.8425 | -49.4568 | 2.7374 | -5.1041 | 73.233 | -49.2188 | 73.2788 | -48.8937 | -49.1867 | -49.0311 | -0.21973 | -0.086975 | -0.18768 | 4.2709 | 51.8509 | -0.34332 | 52.0706 | -0.1236 | -0.10529 | -0.068665 | -0.022888 | 0.21973 | 0.082397 | -0.073243 | 0.18768 | 0.032043 | 4.4907 | 122.4472 | 0.32501 | 122.4976 | 122.5479 | 122.4518 | 122.3282 | 122.3465 | -122.6349 | -122.5204 | 122.2275 | 122.3923 | 46.019 | 44.0094
2015.8281 | 122.5662 | -48.9761 | 73.4665 | -0.20134 | 0.0023391 | 0.062666 | 0.11996 | 0.00059812 | -0.0024994 | 0.0024566 | -0.04303 | -0.0017688 | 0.063751 | 0.058058 | -0.026791 | 0.00055973 | 0.0013885 | -3.1265 | 73.4161 | -49.118 | 73.2376 | -44.6915 | -49.3195 | 2.7374 | -4.9393 | 73.407 | -49.0265 | 73.3841 | -48.7885 | -49.1226 | -48.8937 | -0.14191 | -0.050354 | -0.22888 | 4.2847 | 51.7136 | -0.34332 | 51.8555 | -0.20142 | -0.050354 | -0.05951 | -0.082398 | 0.18768 | 0.082397 | -0.14648 | 0.13275 | -0.096131 | 4.4266 | 122.3557 | 0.23804 | 122.4106 | 122.5342 | 122.4335 | 122.3923 | 122.3831 | -122.5845 | -122.493 | 122.2137 | 122.3602 | 45.8496 | 44.0369
2016.7656 | 122.612 | -49.0448 | 73.3887 | -0.10979 | -0.00043792 | 0.062239 | 0.11996 | 0.0020935 | -0.0033538 | -0.002884 | -0.030823 | -0.0015552 | 0.061829 | 0.062331 | -0.027645 | 0.0014141 | -0.0030975 | -3.1586 | 73.3841 | -49.1821 | 73.233 | -44.6548 | -49.3195 | 2.8152 | -4.5273 | 73.3063 | -49.1089 | 73.3612 | -48.8205 | -49.1364 | -48.9212 | -0.13733 | -0.004578 | -0.15564 | 4.39 | 51.86 | -0.27466 | 51.9974 | -0.13733 | -0.064087 | -0.082398 | -0.027466 | 0.2243 | 0.1236 | -0.091553 | 0.18768 | -0.027466 | 4.5273 | 122.4152 | 0.28839 | 122.4701 | 122.5662 | 122.4152 | 122.4289 | 122.3511 | -122.5708 | -122.4976 | 122.2778 | 122.406 | 45.8862 | 44.5175
2017.8281 | 122.5662 | -49.0356 | 73.407 | -0.10979 | 0.00063028 | 0.062666 | 0.11868 | 0.0065795 | -0.0029266 | -0.003952 | -0.039978 | -0.0034778 | 0.063751 | 0.062972 | -0.027218 | 0.00098693 | 0.00074769 | -3.1311 | 73.3612 | -49.2004 | 73.2056 | -44.6823 | -49.3973 | 2.7969 | -4.5181 | 73.3475 | -49.0997 | 73.3017 | -48.8754 | -49.205 | -48.9624 | -0.16479 | -0.045776 | -0.20142 | 4.3533 | 51.8326 | -0.36163 | 51.9974 | -0.19684 | -0.064086 | -0.059509 | -0.10528 | 0.16022 | 0.073243 | -0.16937 | 0.13733 | -0.10529 | 4.5181 | 122.406 | 0.2243 | 122.4014 | 122.5616 | 122.4472 | 122.3969 | 122.3831 | -122.6074 | -122.5067 | 122.2412 | 122.3373 | 45.9045 | 44.5175
2018.7656 | 122.5571 | -49.2096 | 73.2193 | -0.056381 | 0.00063028 | 0.065443 | 0.11825 | 0.0048705 | -0.0039948 | -0.0024566 | -0.052185 | -0.0015552 | 0.062042 | 0.05699 | -0.028286 | -0.00072207 | -0.0024567 | -2.9251 | 73.201 | -49.3332 | 73.0728 | -44.8975 | -49.5163 | 2.8473 | -4.4907 | 73.1689 | -49.2279 | 73.1689 | -49.0128 | -49.3652 | -49.0997 | -0.1236 | -0.01831 | -0.14648 | 4.3121 | 52.0569 | -0.3067 | 52.1805 | -0.1831 | -0.01831 | -0.050354 | -0.050354 | 0.19684 | 0.10986 | -0.15564 | 0.12817 | -0.13733 | 4.4357 | 122.406 | 0.21515 | 122.3969 | 122.5342 | 122.3969 | 122.4106 | 122.3785 | -122.5525 | -122.4472 | 122.2824 | 122.3785 | 46.2845 | 44.7189
2019.8281 | 122.6257 | -48.8525 | 73.6038 | -0.06401 | -1.0718e-05 | 0.062666 | 0.1174 | 0.00017092 | -0.0012176 | -0.0043792 | -0.036926 | -0.0045458 | 0.063751 | 0.058486 | -0.025509 | 0.0016277 | 0.0018159 | -2.8793 | 73.5443 | -48.9944 | 73.4344 | -44.371 | -49.1364 | 2.9709 | -4.454 | 73.5397 | -48.9166 | 73.5535 | -48.5275 | -49.0036 | -48.7427 | -0.14191 | -0.059509 | -0.16937 | 4.4815 | 51.8234 | -0.28381 | 51.9653 | -0.14191 | -0.064087 | -0.064087 | -0.050354 | 0.32501 | 0.10986 | -0.15106 | 0.17395 | -0.086975 | 4.6234 | 122.4289 | 0.3891 | 122.4701 | 122.5388 | 122.4564 | 122.3969 | 122.3923 | -122.5983 | -122.5204 | 122.287 | 122.406 | 45.9732 | 44.3985
2020.7656 | 122.6212 | -48.8159 | 73.645 | -0.13267 | 0.00084388 | 0.062666 | 0.11804 | 0.0012391 | -0.0016448 | -0.003952 | -0.033874 | -0.0043322 | 0.063751 | 0.061263 | -0.0285 | 0.0016277 | -0.00053411 | -2.7512 | 73.5535 | -48.9532 | 73.5031 | -44.2245 | -49.0997 | 3.067 | -4.3945 | 73.5809 | -48.8388 | 73.5901 | -48.5825 | -48.9166 | -48.6786 | -0.13733 | -0.091553 | -0.14191 | 4.5914 | 51.8829 | -0.28381 | 52.0203 | -0.14648 | -0.022888 | -0.064087 | -0.054932 | 0.23346 | 0.13733 | -0.10071 | 0.16022 | -0.07782 | 4.7287 | 122.4564 | 0.25635 | 122.4289 | 122.5067 | 122.4197 | 122.3694 | 122.3969 | -122.5983 | -122.4838 | 122.319 | 122.406 | 46.0648 | 44.4214
2021.8281 | 122.5891 | -49.2599 | 73.1689 | -0.07164 | 0.00084388 | 0.062666 | 0.11569 | -0.0017517 | -0.001004 | -0.0065156 | -0.04303 | -0.0015552 | 0.063324 | 0.060408 | -0.028072 | 0.00077333 | 0.00032049 | -3.0121 | 73.1461 | -49.4247 | 73.0133 | -44.957 | -49.5575 | 2.9251 | -4.5731 | 73.1049 | -49.3103 | 73.1277 | -49.0448 | -49.3515 | -49.1547 | -0.16479 | -0.022888 | -0.15564 | 4.303 | 52.1851 | -0.29755 | 52.3499 | -0.13275 | -0.050354 | -0.064087 | -0.041198 | 0.21515 | 0.10529 | -0.091552 | 0.15564 | -0.041198 | 4.4678 | 122.4381 | 0.2655 | 122.4381 | 122.5708 | 122.4152 | 122.406 | 122.3648 | -122.5937 | -122.4792 | 122.2733 | 122.3877 | 46.2479 | 44.6869
2022.7656 | 122.5845 | -48.9624 | 73.4894 | -0.07164 | 0.0010575 | 0.062666 | 0.11697 | -0.0017517 | -0.0022858 | -0.0041656 | -0.036926 | -0.0017688 | 0.062897 | 0.059127 | -0.028713 | 0.0037641 | 0.00096129 | -2.9343 | 73.4482 | -49.1364 | 73.1918 | -44.6457 | -49.1867 | 2.9984 | -4.6417 | 73.439 | -49.0219 | 73.3932 | -48.7701 | -49.118 | -48.8617 | -0.17395 | -0.041199 | -0.29755 | 4.3167 | 51.9608 | -0.22431 | 52.1347 | -0.050354 | -0.05951 | -0.050354 | -0.09613 | 0.19226 | 0.10071 | -0.15564 | 0.16022 | -0.09613 | 4.4907 | 122.3282 | 0.25177 | 122.4152 | 122.5845 | 122.4609 | 122.4106 | 122.4014 | -122.6257 | -122.5113 | 122.1542 | 122.3557 | 46.0281 | 44.3207
2023.8281 | 122.5662 | -49.054 | 73.3704 | -0.10216 | 0.0025529 | 0.062239 | 0.11911 | 0.00017092 | -0.0033538 | -0.0016022 | -0.030823 | -0.003905 | 0.060974 | 0.058486 | -0.027645 | 0.00077333 | 0.0020295 | -2.8381 | 73.3383 | -49.2142 | 73.1827 | -44.7327 | -49.3698 | 3.0487 | -4.6417 | 73.3383 | -49.118 | 73.2651 | -48.9212 | -49.2416 | -49.0036 | -0.16022 | -0.032043 | -0.18768 | 4.3213 | 52.1027 | -0.31586 | 52.2629 | -0.15564 | -0.064087 | -0.032043 | -0.10529 | 0.13275 | 0.050354 | -0.18768 | 0.11444 | -0.1236 | 4.4815 | 122.3969 | 0.19684 | 122.3831 | 122.5525 | 122.4564 | 122.3923 | 122.3923 | -122.5845 | -122.4884 | 122.2366 | 122.319 | 46.2158 | 44.4122
2024.7656 | 122.5616 | -48.8663 | 73.5855 | -0.07164 | 0.0012711 | 0.064589 | 0.1159 | 0.0031617 | -0.0031402 | -0.0016022 | -0.049133 | -0.0051868 | 0.062256 | 0.05464 | -0.029568 | 0.0022687 | 0.0020295 | -2.71 | 73.5397 | -49.0356 | 73.3749 | -44.4122 | -49.1913 | 3.2227 | -4.6967 | 73.5214 | -48.9166 | 73.4894 | -48.7152 | -49.0173 | -48.7976 | -0.16937 | -0.045776 | -0.21057 | 4.454 | 52.0889 | -0.32501 | 52.2583 | -0.15564 | -0.050354 | -0.064087 | -0.09613 | 0.15106 | 0.068665 | -0.15106 | 0.11902 | -0.10071 | 4.6234 | 122.4106 | 0.20142 | 122.406 | 122.5754 | 122.438 | 122.406 | 122.3877 | -122.6212 | -122.5021 | 122.2412 | 122.3557 | 46.1563 | 44.1696
2025.8281 | 122.5754 | -49.0677 | 73.3749 | -0.06401 | 0.0010575 | 0.063094 | 0.11975 | 0.0055115 | 6.4004e-05 | -0.00074776 | -0.036926 | -0.0045458 | 0.063751 | 0.057418 | -0.027004 | -0.00029487 | -0.00010671 | -2.8244 | 73.407 | -49.1318 | 73.2422 | -44.632 | -49.3469 | 2.9617 | -4.8248 | 73.3658 | -49.0952 | 73.2971 | -48.9029 | -49.2325 | -49.0402 | -0.064087 | 0.032043 | -0.13275 | 4.4357 | 52.0294 | -0.27924 | 52.0935 | -0.21515 | -0.027466 | -0.009155 | -0.07782 | 0.16479 | 0.027466 | -0.1648 | 0.054932 | -0.13733 | 4.4998 | 122.374 | 0.19226 | 122.3923 | 122.5388 | 122.4609 | 122.4747 | 122.4335 | -122.5067 | -122.4701 | 122.3099 | 122.3648 | 46.2433 | 44.2429
2026.7656 | 122.4564 | -49.0448 | 73.3292 | -0.07164 | 0.0031937 | 0.064589 | 0.11804 | -0.00046988 | -0.0031402 | -0.0024566 | -0.027771 | -0.0047594 | 0.064606 | 0.05934 | -0.02615 | 0.00077333 | -0.00074771 | -2.8748 | 73.3658 | -49.2096 | 73.1552 | -44.7281 | -49.411 | 2.9297 | -4.9072 | 73.3292 | -49.1318 | 73.2651 | -48.912 | -49.2371 | -48.793 | -0.16479 | 0.036621 | -0.17395 | 4.3167 | 51.9745 | -0.36621 | 52.1393 | -0.20142 | -0.086975 | 0 | -0.064087 | 0.13275 | 0.25177 | -0.19226 | 0.33874 | -0.10529 | 4.4815 | 122.3648 | 0.21973 | 122.3969 | 122.5754 | 122.4609 | 122.4106 | 122.374 | -122.5388 | -122.4609 | 122.2 | 122.3099 | 46.17 | 44.1376
2027.8281 | 122.5708 | -49.0402 | 73.3841 | -0.056381 | -1.0718e-05 | 0.064162 | 0.11718 | 0.00081172 | -0.0029266 | -0.002243 | -0.058289 | -0.001128 | 0.063538 | 0.061049 | -0.028713 | 0.0035503 | 0.00053409 | -2.742 | 73.3475 | -49.1959 | 73.2239 | -44.6548 | -49.3469 | 3.0441 | -4.8386 | 73.3795 | -49.1043 | 73.3292 | -48.8754 | -49.1638 | -48.9578 | -0.15564 | -0.036621 | -0.16022 | 4.3854 | 52.0844 | -0.3067 | 52.24 | -0.15106 | -0.064087 | -0.004577 | -0.054931 | 0.16479 | 0.082397 | -0.1236 | 0.14648 | -0.059509 | 4.541 | 122.4197 | 0.22888 | 122.4335 | 122.5433 | 122.4838 | 122.3877 | 122.4197 | -122.58 | -122.4884 | 122.2641 | 122.3694 | 46.2982 | 44.2017
2028.7656 | 122.5388 | -49.1592 | 73.2513 | -0.15556 | -0.00043792 | 0.062025 | 0.11782 | 0.0050843 | -0.0050628 | -0.0013886 | -0.04303 | -0.0024096 | 0.064179 | 0.064467 | -0.029995 | 0.00055973 | 0.0039521 | -2.8061 | 73.201 | -49.3652 | 73.0637 | -44.902 | -49.5117 | 2.9572 | -5.2414 | 73.201 | -49.2554 | 73.1689 | -49.0402 | -49.3515 | -49.1089 | -0.20599 | -0.050354 | -0.18768 | 4.2572 | 52.1164 | -0.35248 | 52.3224 | -0.14648 | -0.09613 | -0.050354 | -0.082398 | 0.11902 | 0.050354 | -0.19226 | 0.14648 | -0.09613 | 4.4632 | 122.4289 | 0.21515 | 122.4243 | 122.5662 | 122.4564 | 122.3602 | 122.3602 | -122.6166 | -122.5067 | 122.2229 | 122.3282 | 46.3531 | 43.9178
2029.8281 | 122.5662 | -48.9624 | 73.4756 | -0.086899 | 0.0027665 | 0.060316 | 0.11846 | -0.00025628 | -0.0029266 | -0.0020294 | -0.036926 | -0.00091423 | 0.064392 | 0.059981 | -0.027431 | 0.0026959 | 0.0048065 | -2.7283 | 73.4802 | -49.0585 | 73.3566 | -44.4397 | -49.2554 | 3.0945 | -5.1544 | 73.4024 | -48.9899 | 73.4207 | -48.7839 | -49.0906 | -48.8663 | -0.096131 | 0.004578 | -0.11902 | 4.5227 | 52.0569 | -0.29297 | 52.153 | -0.19684 | -0.027466 | -0.073242 | -0.054932 | 0.17853 | 0.09613 | -0.12817 | 0.1236 | -0.10071 | 4.6188 | 122.4152 | 0.20599 | 122.4106 | 122.5388 | 122.3923 | 122.4426 | 122.3648 | -122.5342 | -122.4655 | 122.319 | 122.3831 | 46.2341 | 43.808
2030.7656 | 122.6257 | -48.674 | 73.7549 | -0.2166 | -1.0718e-05 | 0.059248 | 0.11846 | 0.00059812 | -0.001004 | -0.0026704 | -0.049133 | -0.0013416 | 0.065888 | 0.054213 | -0.027645 | 0.00077333 | 0.00074769 | -2.6505 | 73.7778 | -48.7701 | 73.6176 | -44.0231 | -48.9349 | 3.2501 | -5.1041 | 73.7 | -48.7061 | 73.7183 | -48.4589 | -48.7701 | -48.5413 | -0.096131 | 0.022888 | -0.13733 | 4.6509 | 51.9241 | -0.26093 | 52.0203 | -0.16479 | -0.032044 | -0.054932 | -0.036621 | 0.21515 | 0.13275 | -0.096131 | 0.16479 | -0.064087 | 4.747 | 122.3877 | 0.24719 | 122.4243 | 122.5479 | 122.406 | 122.4518 | 122.374 | -122.525 | -122.4609 | 122.2916 | 122.3923 | 46.0236 | 43.5699
2031.8281 | 122.6624 | -48.88 | 73.6038 | -0.10979 | -0.00086512 | 0.061598 | 0.11804 | 0.0052979 | -0.0035674 | -0.0048066 | -0.064392 | -0.0028368 | 0.063538 | 0.060836 | -0.029781 | -0.0013629 | 0.00010689 | -2.829 | 73.5123 | -49.0448 | 73.3246 | -44.4672 | -49.2462 | 2.9434 | -5.5344 | 73.5123 | -48.967 | 73.5031 | -49.0402 | -49.1089 | -48.6786 | -0.1648 | -0.091553 | -0.27924 | 4.4128 | 51.8234 | -0.36621 | 51.9882 | -0.20142 | -0.086975 | -0.091553 | -0.10071 | -0.16022 | 0.20142 | -0.22888 | 0.28839 | -0.14191 | 4.5776 | 122.3694 | -0.073242 | 122.4701 | 122.5571 | 122.4792 | 122.3923 | 122.3923 | -122.6486 | -122.5708 | 122.2046 | 122.3831 | 46.051 | 43.3456
2032.7656 | 122.5662 | -48.7839 | 73.6633 | -0.11742 | -0.00065152 | 0.063094 | 0.11868 | 0.0020935 | -0.0029266 | -0.002243 | -0.021667 | -0.0028368 | 0.06247 | 0.060195 | -0.027645 | 0.00013253 | 0.0028839 | -2.8473 | 73.7137 | -48.8617 | 73.4161 | -44.4901 | -48.9899 | 3.2684 | -5.2597 | 73.6862 | -48.7564 | 73.5764 | -48.6694 | -48.9349 | -48.7198 | -0.077819 | 0.050354 | -0.24719 | 4.2938 | 52.0523 | -0.20599 | 52.1301 | -0.12817 | 0.027466 | 0.022888 | -0.086975 | 0.11444 | 0.064087 | -0.15106 | 0.036621 | -0.17853 | 4.3716 | 122.2778 | 0.086975 | 122.3328 | 122.5754 | 122.4426 | 122.4976 | 122.4701 | -122.525 | -122.4197 | 122.2 | 122.3602 | 45.9366 | 43.5242
2033.8281 | 122.5845 | -48.9029 | 73.526 | -0.12505 | -0.0017197 | 0.062666 | 0.11846 | 0.00017092 | 0.0002778 | 0.0016022 | -0.036926 | -0.0024096 | 0.06247 | 0.060836 | -0.026363 | 0.00098693 | -0.00096131 | -2.8793 | 73.5168 | -49.0356 | 73.2101 | -44.2017 | -48.9807 | 2.9938 | -5.5618 | 73.4985 | -48.9578 | 73.4344 | -48.7656 | -49.0952 | -49.3332 | -0.13275 | -0.009155 | -0.31586 | 4.7012 | 51.8967 | -0.07782 | 52.0294 | 0.054932 | -0.054932 | -0.027466 | -0.091553 | 0.13733 | -0.4303 | -0.19226 | -0.37537 | -0.13733 | 4.834 | 122.2458 | 0.19226 | 122.3923 | 122.5525 | 122.4564 | 122.4197 | 122.4014 | -122.5616 | -122.4838 | 122.113 | 122.3373 | 46.0236 | 43.3411
2034.7656 | 122.6578 | -48.7152 | 73.7549 | -0.094528 | 0.0019119 | 0.062453 | 0.11846 | 0.0018799 | -0.0022858 | -0.0020294 | -0.046081 | -0.0026232 | 0.064392 | 0.061263 | -0.0285 | 0.00098693 | -0.0018157 | -2.6138 | 73.7045 | -48.8708 | 73.4985 | -44.2566 | -49.1089 | 3.1723 | -6.1386 | 73.6771 | -48.7976 | 73.613 | -48.6328 | -49.173 | -48.9029 | -0.15564 | -0.050354 | -0.25635 | 4.4586 | 51.8875 | -0.39368 | 52.0432 | -0.23804 | -0.082397 | -0.07782 | -0.14191 | 0.082398 | -0.18768 | -0.45776 | -0.10529 | -0.37537 | 4.6143 | 122.3694 | 0.16479 | 122.4106 | 122.5754 | 122.4747 | 122.4197 | 122.3923 | -122.6257 | -122.5525 | 122.2137 | 122.3282 | 46.1014 | 42.5766
2035.8281 | 122.5983 | -48.6694 | 73.7732 | -0.033493 | 0.0010575 | 0.060957 | 0.1174 | 0.0023071 | -0.0020722 | -0.0013886 | -0.012512 | -0.0034778 | 0.063324 | 0.060408 | -0.0285 | 0.0018413 | 0.0024567 | -2.3758 | 73.7503 | -48.8113 | 73.6084 | -44.0781 | -48.9578 | 3.4149 | -6.102 | 73.6954 | -48.7381 | 73.7366 | -48.4589 | -48.7793 | -48.5641 | -0.14191 | -0.022888 | -0.1648 | 4.5914 | 52.0844 | -0.28839 | 52.2263 | -0.14648 | -0.068664 | -0.077819 | -0.036621 | 0.21057 | 0.10529 | -0.10986 | 0.17395 | -0.041199 | 4.7333 | 122.4197 | 0.27924 | 122.4747 | 122.5616 | 122.4335 | 122.4197 | 122.3648 | -122.5845 | -122.5113 | 122.2778 | 122.406 | 46.2936 | 42.5674
2036.7656 | 122.5388 | -48.9075 | 73.5306 | -0.094528 | -0.0017197 | 0.062453 | 0.11804 | 0.0012391 | -0.0014312 | -0.0018158 | -0.04303 | -0.0019824 | 0.064179 | 0.060836 | -0.029354 | -8.1274e-05 | 0.0058747 | -2.3575 | 73.5306 | -49.0128 | 73.3887 | -44.3665 | -49.1913 | 3.4012 | -5.9463 | 73.5214 | -48.9395 | 73.439 | -48.7381 | -49.0631 | -48.8342 | -0.10529 | 0 | -0.14191 | 4.541 | 52.3087 | -0.28381 | 52.4139 | -0.17853 | -0.032043 | -0.009156 | -0.091553 | 0.16937 | 0.073242 | -0.15564 | 0.10529 | -0.1236 | 4.6463 | 122.4014 | 0.20142 | 122.3785 | 122.5433 | 122.4609 | 122.4381 | 122.4289 | -122.5433 | -122.4701 | 122.2961 | 122.3465 | 46.55 | 42.9611
2037.8281 | 122.6028 | -48.761 | 73.7228 | -0.10216 | 0.0023391 | 0.059676 | 0.11782 | -0.0030335 | -0.002713 | -0.002243 | 0.042419 | -0.0045458 | 0.063111 | 0.046096 | -0.027218 | -0.0030719 | 0.00053409 | -2.3209 | 73.6954 | -48.8663 | 73.5031 | -44.2429 | -49.0402 | 3.566 | -5.6122 | 73.613 | -48.8022 | 73.6679 | -48.761 | -48.9899 | -48.6649 | -0.10529 | -0.027465 | -0.21973 | 4.5181 | 52.327 | -0.27924 | 52.4323 | -0.17395 | -0.041199 | -0.10986 | -0.054931 | 0 | 0.09613 | -0.22888 | 0.13733 | -0.18768 | 4.6234 | 122.3694 | 0.041199 | 122.4701 | 122.5616 | 122.4152 | 122.4564 | 122.374 | -122.5891 | -122.525 | 122.2641 | 122.4289 | 46.4401 | 43.1488
2038.7656 | 122.6349 | -48.9441 | 73.4985 | -0.048752 | -0.0012923 | 0.060744 | 0.11846 | -0.0015381 | -0.0022858 | -0.0018158 | -0.027771 | -0.0024096 | 0.062683 | 0.061904 | -0.027218 | 0.0014141 | 0.0016021 | -2.4124 | 73.4848 | -49.0631 | 73.3612 | -44.4992 | -49.2279 | 3.5614 | -5.6488 | 73.4436 | -48.9761 | 73.4299 | -48.7473 | -49.0448 | -48.8297 | -0.11902 | -0.013733 | -0.13733 | 4.4449 | 52.5055 | -0.28381 | 52.6245 | -0.16479 | -0.032043 | -0.054931 | -0.068664 | 0.19684 | 0.11444 | -0.10071 | 0.14648 | -0.068665 | 4.5639 | 122.4243 | 0.22888 | 122.406 | 122.5479 | 122.4197 | 122.4289 | 122.3877 | -122.5616 | -122.4747 | 122.3053 | 122.374 | 46.5317 | 43.2953
2039.8281 | 122.5754 | -49.0311 | 73.4756 | -0.10979 | -0.0012923 | 0.062025 | 0.11953 | -0.0013245 | -0.0050628 | -0.0041656 | -0.06134 | -0.0026232 | 0.063965 | 0.064467 | -0.028072 | 0.00013253 | 0.0011749 | -2.4124 | 73.4344 | -49.1226 | 73.288 | -44.6045 | -49.3332 | 3.4515 | -5.5756 | 73.4528 | -49.0219 | 73.3521 | -48.7885 | -49.4797 | -49.1913 | -0.091553 | -0.041199 | -0.18768 | 4.4266 | 52.4826 | -0.30212 | 52.5742 | -0.21057 | 0.009155 | -0.022888 | -0.1236 | 0.24262 | -0.16022 | -0.44861 | -0.16937 | -0.45776 | 4.5181 | 122.4106 | 0.23346 | 122.374 | 122.5571 | 122.4747 | 122.4655 | 122.4838 | -122.5983 | -122.4976 | 122.319 | 122.3831 | 46.6187 | 43.4555
2040.7656 | 122.5937 | -48.8159 | 73.6084 | -0.079269 | 0.0010575 | 0.06288 | 0.11804 | 0.0020935 | -0.0031402 | -0.0018158 | -0.036926 | -0.0013416 | 0.063111 | 0.061263 | -0.028927 | -0.00029487 | 0.0024567 | -2.4261 | 73.6359 | -48.9532 | 73.4756 | -44.3298 | -49.1272 | 3.3829 | -5.4428 | 73.5535 | -48.8754 | 73.5626 | -48.6237 | -48.9258 | -48.7244 | -0.13733 | 0.027466 | -0.13275 | 4.4861 | 52.1988 | -0.31128 | 52.3361 | -0.17395 | -0.059509 | -0.054931 | -0.045776 | 0.19226 | 0.091553 | -0.10986 | 0.15106 | -0.050354 | 4.6234 | 122.4289 | 0.25177 | 122.438 | 122.5891 | 122.4289 | 122.4518 | 122.3694 | -122.5616 | -122.4838 | 122.2916 | 122.3785 | 46.3898 | 43.3731
2041.8281 | 122.5891 | -48.7976 | 73.6771 | -0.12505 | -1.0718e-05 | 0.061598 | 0.11697 | 0.0014527 | -0.0039948 | -0.001175 | -0.09491 | -0.0041186 | 0.063111 | 0.059767 | -0.027218 | 0.0022687 | 0.0043793 | -2.655 | 73.6816 | -48.8983 | 73.4528 | -44.3436 | -49.1959 | 3.0716 | -5.3421 | 73.6679 | -48.8159 | 73.5718 | -48.6099 | -48.9532 | -48.7244 | -0.10071 | 0.004578 | -0.2243 | 4.454 | 51.8692 | -0.39825 | 51.9699 | -0.29755 | -0.018311 | -0.009155 | -0.10529 | 0.18768 | 0.073242 | -0.15564 | 0.091553 | -0.13733 | 4.5547 | 122.3511 | 0.20599 | 122.3877 | 122.58 | 122.4838 | 122.4792 | 122.4655 | -122.5754 | -122.493 | 122.2504 | 122.3694 | 46.1426 | 43.4555
2042.7656 | 122.6212 | -48.6923 | 73.7091 | -0.10216 | 0.00063028 | 0.063094 | 0.1159 | 0.0016663 | -0.0012176 | -0.0037384 | -0.024719 | -0.003905 | 0.06247 | 0.057631 | -0.028072 | 0.0024823 | 0.0013885 | -2.5314 | 73.7274 | -48.8297 | 73.7045 | -44.0506 | -48.9761 | 3.5156 | -5.3375 | 73.6816 | -48.7381 | 73.7045 | -48.4863 | -48.7839 | -48.6191 | -0.13733 | 0.018311 | -0.004577 | 4.6417 | 52.2079 | -0.28381 | 52.3453 | -0.14648 | -0.045776 | -0.027465 | -0.004577 | 0.20599 | 0.073242 | -0.091553 | 0.11902 | -0.045777 | 4.7791 | 122.5342 | 0.25177 | 122.4426 | 122.5571 | 122.4197 | 122.4197 | 122.374 | -122.5388 | -122.4472 | 122.3969 | 122.3969 | 46.1609 | 43.3548
2043.8281 | 122.5845 | -49.0723 | 73.3932 | -0.025863 | 0.0019119 | 0.059462 | 0.11975 | 0.0025207 | -0.0012176 | -0.0058746 | -0.00030524 | -0.0036914 | 0.064179 | 0.057631 | -0.025936 | -0.0024311 | 0.0060883 | -2.6184 | 73.3521 | -49.2004 | 73.1918 | -44.8105 | -49.3469 | 3.3829 | -5.3925 | 73.3337 | -49.086 | 73.2971 | -48.8571 | -49.1547 | -48.967 | -0.12817 | -0.041199 | -0.20142 | 4.2618 | 52.4551 | -0.27466 | 52.5833 | -0.14648 | -0.013733 | -0.05951 | -0.096131 | 0.21515 | 0.10529 | -0.082397 | 0.11902 | -0.068664 | 4.39 | 122.3923 | 0.22888 | 122.3831 | 122.5525 | 122.4197 | 122.4243 | 122.406 | -122.5937 | -122.4792 | 122.2641 | 122.3694 | 46.4539 | 43.6798
2044.7656 | 122.6074 | -48.9166 | 73.5123 | -0.07164 | 0.00041648 | 0.060957 | 0.11654 | 0.0031617 | -0.004422 | -0.003952 | -0.04303 | -0.0036914 | 0.064606 | 0.061476 | -0.027645 | 0.0033367 | -0.00096131 | -2.3712 | 73.4711 | -49.0952 | 73.3337 | -44.5953 | -49.2325 | 3.4607 | -5.3192 | 73.4253 | -48.9807 | 73.4619 | -48.7244 | -49.0173 | -48.8022 | -0.17853 | -0.041199 | -0.17853 | 4.3213 | 52.3773 | -0.31586 | 52.5558 | -0.13733 | -0.064087 | -0.086975 | -0.050354 | 0.19226 | 0.11444 | -0.10071 | 0.17853 | -0.036621 | 4.4998 | 122.4289 | 0.25635 | 122.4426 | 122.5662 | 122.406 | 122.3877 | 122.3419 | -122.6074 | -122.493 | 122.2504 | 122.3785 | 46.5454 | 43.5974
2045.8281 | 122.612 | -48.7793 | 73.6771 | -0.07164 | -0.00065152 | 0.060957 | 0.11804 | -0.0038879 | -0.0029266 | -0.0018158 | -0.00030524 | -0.0024096 | 0.06247 | 0.061263 | -0.027645 | 0.00055973 | 0.0058747 | -2.2614 | 73.5123 | -49.0356 | 73.3841 | -44.4901 | -49.1684 | 3.6896 | -5.452 | 73.5443 | -48.912 | 73.5672 | -48.5504 | -48.88 | -48.674 | -0.25635 | -0.16479 | -0.29297 | 4.2892 | 52.4689 | -0.3891 | 52.7252 | -0.13275 | -0.13275 | -0.13275 | -0.10986 | 0.22888 | 0.10529 | -0.10071 | 0.23804 | 0.032043 | 4.5456 | 122.4197 | 0.36163 | 122.4792 | 122.5479 | 122.4564 | 122.2916 | 122.3236 | -122.7127 | -122.5891 | 122.1634 | 122.3465 | 46.5179 | 43.3273
2046.7656 | 122.6349 | -49.4293 | 72.995 | 0.004654 | 0.00084388 | 0.063948 | 0.11911 | -0.00068368 | -0.0016448 | -0.0020294 | -0.018616 | -0.0032642 | 0.06546 | 0.055281 | -0.028072 | 0.00077333 | -0.00053411 | -2.3483 | 73.0225 | -49.5392 | 72.8531 | -45.3094 | -49.6857 | 3.5934 | -5.4199 | 72.9858 | -49.4705 | 72.9492 | -49.2188 | -49.5071 | -49.324 | -0.10986 | 0.027466 | -0.14191 | 4.1199 | 53.0228 | -0.25635 | 53.1326 | -0.14648 | -0.041199 | -0.009155 | -0.045776 | 0.21057 | 0.10529 | -0.07782 | 0.14648 | -0.036621 | 4.2297 | 122.3923 | 0.25177 | 122.4197 | 122.5616 | 122.4564 | 122.4518 | 122.4152 | -122.5342 | -122.4655 | 122.2824 | 122.3785 | 47.081 | 44.0094
2047.8281 | 122.5983 | -49.0906 | 73.3383 | -0.17082 | 0.0012711 | 0.061598 | 0.11846 | 0.00059812 | -0.0024994 | -0.003952 | -0.0033568 | -0.0043322 | 0.063324 | 0.059767 | -0.026577 | 0.0014141 | 0.0043793 | -2.3163 | 73.3383 | -49.2416 | 73.1186 | -44.8883 | -49.4064 | 3.5843 | -5.3513 | 73.2971 | -49.1684 | 73.2239 | -48.9166 | -49.2096 | -49.0402 | -0.15106 | 0 | -0.21973 | 4.2023 | 52.6749 | -0.31586 | 52.8259 | -0.16479 | -0.07782 | -0.041199 | -0.11444 | 0.17395 | 0.050354 | -0.11902 | 0.12817 | -0.041199 | 4.3533 | 122.3602 | 0.25177 | 122.3923 | 122.58 | 122.4655 | 122.4289 | 122.3877 | -122.58 | -122.5067 | 122.2092 | 122.3145 | 46.7743 | 43.7393
2048.7656 | 122.5571 | -49.3103 | 73.1644 | -0.094528 | -0.00043792 | 0.063307 | 0.11825 | 0.0040161 | -0.0063446 | -0.0020294 | 0.094299 | -0.0013416 | 0.063324 | 0.061263 | -0.027431 | -0.00050847 | 0.0050201 | -2.4765 | 73.1186 | -49.4339 | 72.9401 | -45.1859 | -49.6033 | 3.653 | -5.5206 | 73.1094 | -49.3423 | 73.0499 | -49.1318 | -49.4202 | -49.2462 | -0.1236 | -0.045777 | -0.22431 | 4.1245 | 52.9633 | -0.29297 | 53.0869 | -0.16937 | -0.032043 | -0.054932 | -0.11444 | 0.17853 | 0.064087 | -0.10986 | 0.09613 | -0.07782 | 4.248 | 122.374 | 0.21057 | 122.3923 | 122.5525 | 122.4518 | 122.4289 | 122.4197 | -122.5983 | -122.5067 | 122.2504 | 122.3602 | 46.8338 | 43.7897
2049.8281 | 122.5937 | -48.8068 | 73.5992 | -0.056381 | 0.00084388 | 0.063307 | 0.12103 | -0.0013245 | -0.0024994 | -0.001175 | -0.036926 | -0.002196 | 0.063324 | 0.055281 | -0.028286 | 0.0020551 | -0.0024567 | -2.2293 | 73.5992 | -48.9807 | 73.4894 | -44.3939 | -49.086 | 3.6942 | -5.3284 | 73.5626 | -48.8571 | 73.6038 | -48.5779 | -48.8754 | -48.6877 | -0.17395 | 0 | -0.10986 | 4.4128 | 52.5009 | -0.27924 | 52.6749 | -0.10529 | -0.050354 | -0.036621 | 0.004578 | 0.22888 | 0.11902 | -0.068664 | 0.16937 | -0.01831 | 4.5868 | 122.4701 | 0.27924 | 122.4609 | 122.58 | 122.4197 | 122.406 | 122.3694 | -122.58 | -122.4564 | 122.2961 | 122.4106 | 46.5775 | 43.4784
2050.7656 | 122.6166 | -49.0402 | 73.3841 | 0.004654 | 0.0027665 | 0.065871 | 0.11953 | 0.0020935 | -0.0048492 | -0.00010676 | -0.06134 | -0.003905 | 0.065033 | 0.062758 | -0.0285 | 0.00013253 | -0.00074771 | -2.1973 | 73.3612 | -49.2004 | 73.2239 | -44.7693 | -49.3607 | 3.6209 | -5.5435 | 73.3246 | -49.1043 | 73.3109 | -48.8571 | -49.1638 | -48.9395 | -0.16022 | -0.022888 | -0.16022 | 4.2709 | 52.6611 | -0.32044 | 52.8214 | -0.16022 | -0.064087 | -0.059509 | -0.073242 | 0.1831 | 0.10071 | -0.1236 | 0.16479 | -0.059509 | 4.4312 | 122.4243 | 0.24719 | 122.4152 | 122.5616 | 122.4289 | 122.4014 | 122.3648 | -122.5845 | -122.4884 | 122.2641 | 122.3511 | 46.843 | 43.4967
2051.8281 | 122.6166 | -49.0677 | 73.4024 | -0.033493 | -0.00086512 | 0.06053 | 0.11825 | -0.00025628 | -0.0022858 | -0.0013886 | -0.027771 | -0.0030506 | 0.062897 | 0.058913 | -0.026363 | 0.00055973 | 0.0018159 | -2.2385 | 73.3887 | -49.2096 | 73.1873 | -44.7968 | -49.3561 | 3.5156 | -5.7541 | 73.3154 | -49.118 | 73.32 | -48.848 | -49.1684 | -48.9441 | -0.14191 | -0.013733 | -0.21515 | 4.2709 | 52.5833 | -0.28839 | 52.7252 | -0.14648 | -0.050354 | -0.086975 | -0.082398 | 0.21973 | 0.1236 | -0.10071 | 0.17395 | -0.050354 | 4.4128 | 122.3969 | 0.27008 | 122.438 | 122.5983 | 122.4335 | 122.4564 | 122.3831 | -122.612 | -122.5204 | 122.2549 | 122.3877 | 46.8292 | 43.3136
2052.7656 | 122.6074 | -49.2142 | 73.2101 | -0.07164 | 0.0014847 | 0.064162 | 0.11825 | 0.00059812 | -0.004422 | 0.00032044 | -0.11322 | -0.0017688 | 0.06247 | 0.058272 | -0.026363 | 0.0022687 | 0.0022431 | -2.2705 | 73.1827 | -49.4064 | 73.0362 | -45.0348 | -49.5575 | 3.3966 | -5.7312 | 73.1506 | -49.2828 | 73.1689 | -48.9761 | -49.3103 | -49.1135 | -0.19226 | -0.027466 | -0.17395 | 4.1794 | 52.6108 | -0.34332 | 52.803 | -0.15106 | -0.068665 | -0.059509 | -0.041199 | 0.23804 | 0.10071 | -0.096131 | 0.16937 | -0.027466 | 4.3716 | 122.4426 | 0.3067 | 122.4518 | 122.5891 | 122.4335 | 122.3969 | 122.3648 | -122.6166 | -122.493 | 122.2504 | 122.3831 | 46.9437 | 43.483
2053.8281 | 122.5891 | -48.9944 | 73.4253 | -0.10216 | 0.00041648 | 0.06288 | 0.11718 | 0.0029479 | -0.0037812 | -0.00053396 | -0.055237 | -0.0047594 | 0.063538 | 0.06874 | -0.027645 | 0.0029095 | 0.0022431 | -2.243 | 73.4253 | -49.0997 | 73.2651 | -44.696 | -49.2828 | 3.4653 | -5.7037 | 73.3932 | -49.0402 | 73.3978 | -48.8297 | -49.1135 | -48.9212 | -0.10528 | 0 | -0.16022 | 4.2984 | 52.4597 | -0.28839 | 52.565 | -0.18311 | -0.045776 | -0.032043 | -0.027466 | 0.1648 | 0.073242 | -0.11902 | 0.11902 | -0.073242 | 4.4037 | 122.3648 | 0.21057 | 122.438 | 122.525 | 122.4335 | 122.4197 | 122.3877 | -122.525 | -122.4655 | 122.2595 | 122.3923 | 46.7514 | 43.2907
2054.7656 | 122.6074 | -48.967 | 73.4711 | -0.094528 | -0.00043792 | 0.061812 | 0.11761 | 0.00017092 | -0.0035674 | -0.0013886 | 0.011902 | -0.0032642 | 0.06482 | 0.058058 | -0.027645 | 0.00098693 | 0.00053409 | -2.243 | 73.4756 | -49.1135 | 73.2697 | -44.6915 | -49.2783 | 3.4882 | -5.6717 | 73.4024 | -49.0356 | 73.3978 | -48.7747 | -49.0768 | -48.8663 | -0.14648 | 0.004578 | -0.20142 | 4.2755 | 52.4551 | -0.31128 | 52.6016 | -0.16479 | -0.068665 | -0.068664 | -0.073242 | 0.19226 | 0.10071 | -0.10986 | 0.16937 | -0.041198 | 4.422 | 122.3831 | 0.26093 | 122.4335 | 122.5891 | 122.4381 | 122.4426 | 122.3694 | -122.5845 | -122.5067 | 122.2366 | 122.3648 | 46.7239 | 43.2953
2055.8281 | 122.5983 | -48.9258 | 73.5123 | -0.13267 | 0.0019119 | 0.061171 | 0.11654 | -0.00068368 | -0.0039948 | -0.0018158 | -0.039978 | -0.0028368 | 0.064179 | 0.058699 | -0.027859 | 0.00034613 | 0.0018159 | -2.1881 | 73.4116 | -49.1913 | 73.2834 | -44.632 | -49.2645 | 3.6438 | -5.603 | 73.4161 | -49.0494 | 73.4711 | -48.6877 | -48.999 | -48.8297 | -0.2655 | -0.10071 | -0.22888 | 4.2938 | 52.5696 | -0.33874 | 52.8351 | -0.073242 | -0.1236 | -0.09613 | -0.041199 | 0.23804 | 0.09613 | -0.073242 | 0.21973 | 0.050354 | 4.5593 | 122.4747 | 0.36163 | 122.5204 | 122.6028 | 122.4655 | 122.3373 | 122.3419 | -122.7036 | -122.5616 | 122.2092 | 122.3969 | 46.7377 | 43.3228
2056.7656 | 122.5845 | -49.2645 | 73.1827 | -0.14793 | 0.0021255 | 0.060316 | 0.11782 | 0.0010253 | -0.0042084 | -0.0052338 | 0.051575 | -0.0047594 | 0.063324 | 0.056349 | -0.028072 | -0.0017901 | 0.0043793 | -2.2293 | 73.1644 | -49.3698 | 72.995 | -45.1035 | -49.5255 | 3.7079 | -5.5801 | 73.114 | -49.3011 | 73.082 | -49.0585 | -49.3515 | -49.2004 | -0.10529 | -0.01831 | -0.18768 | 4.1611 | 52.9724 | -0.26093 | 53.0777 | -0.15564 | -0.036621 | -0.068664 | -0.10071 | 0.20599 | 0.064087 | -0.086975 | 0.10071 | -0.050354 | 4.2664 | 122.3648 | 0.24261 | 122.3831 | 122.5342 | 122.4152 | 122.4289 | 122.3785 | -122.5525 | -122.4838 | 122.2595 | 122.3465 | 47.0352 | 43.6844
2057.7656 | 122.5754 | -49.0997 | 73.3383 | -0.11742 | -0.00065152 | 0.061812 | 0.11611 | 0.00059812 | -0.0020722 | 0.00053404 | 0.011902 | -0.0045458 | 0.06482 | 0.06404 | -0.0285 | 0.0012005 | 0.0039521 | -2.1698 | 73.3063 | -49.2096 | 73.2147 | -44.8105 | -49.3378 | 3.8223 | -5.4382 | 73.2697 | -49.1455 | 73.2422 | -48.88 | -49.2004 | -49.0265 | -0.10986 | -0.032044 | -0.1236 | 4.2892 | 52.9221 | -0.23804 | 53.0319 | -0.12817 | -0.045777 | -0.068665 | -0.096131 | 0.21973 | 0.073242 | -0.10071 | 0.11902 | -0.054931 | 4.3991 | 122.4243 | 0.2655 | 122.3877 | 122.5159 | 122.4152 | 122.406 | 122.3694 | -122.5479 | -122.4838 | 122.3145 | 122.3419 | 46.9299 | 43.6615
2058.8281 | 122.7036 | -49.3927 | 72.9492 | -0.041122 | -1.0718e-05 | 0.059676 | 0.11846 | -0.00068368 | -0.0022858 | -0.006302 | 0.066834 | -0.0054004 | 0.061829 | 0.054 | -0.0285 | 0.00077333 | 0.00032049 | -2.1606 | 72.9172 | -49.585 | 72.9218 | -45.2545 | -49.6124 | 3.8452 | -5.1773 | 72.9584 | -49.4888 | 72.9401 | -49.1272 | -49.411 | -49.2691 | -0.19226 | -0.032044 | -0.027466 | 4.1382 | 53.2379 | -0.21973 | 53.4302 | -0.027466 | -0.096131 | 0.009155 | -0.009156 | 0.2655 | 0.1236 | -0.018311 | 0.21973 | 0.07782 | 4.3304 | 122.5067 | 0.36163 | 122.4289 | 122.5021 | 122.4472 | 122.3099 | 122.3511 | -122.5342 | -122.4381 | 122.3145 | 122.3328 | 47.2321 | 44.2154
2059.7656 | 122.6395 | -49.4888 | 72.9446 | -0.094528 | 0.0027665 | 0.061171 | 0.11569 | 0.0035889 | -0.004422 | -0.003952 | 0.045471 | -0.0017688 | 0.06247 | 0.062331 | -0.027859 | -0.00029487 | -0.0022431 | -2.1606 | 72.8989 | -49.617 | 72.8622 | -45.369 | -49.6811 | 3.7216 | -5.4153 | 72.8577 | -49.5255 | 72.9126 | -49.2462 | -49.53 | -49.3423 | -0.12817 | -0.045776 | -0.082397 | 4.1199 | 53.2104 | -0.19226 | 53.3386 | -0.064087 | -0.036621 | -0.086975 | -0.032043 | 0.24262 | 0.14648 | -0.041198 | 0.18311 | -0.004577 | 4.248 | 122.4792 | 0.27924 | 122.4381 | 122.5159 | 122.3831 | 122.3877 | 122.3465 | -122.5616 | -122.4701 | 122.3511 | 122.4014 | 47.3282 | 44.0735
2060.8281 | 122.7081 | -49.4568 | 72.8943 | -0.086899 | -0.0017197 | 0.062666 | 0.11911 | -0.0045289 | -0.0052764 | -0.002243 | 0.06073 | -0.0043322 | 0.061402 | 0.057204 | -0.029568 | -0.0017901 | 0.00096129 | -2.2385 | 72.9126 | -49.5575 | 72.8668 | -45.3278 | -49.6902 | 3.717 | -5.571 | 72.8165 | -49.5575 | 72.9721 | -49.1867 | -49.4659 | -49.292 | -0.10071 | 0.018311 | -0.027466 | 4.129 | 53.1738 | -0.23346 | 53.2745 | -0.13275 | -0.10071 | -0.07782 | 0.07782 | 0.27008 | 0.16479 | -0.009155 | 0.2655 | 0.091553 | 4.2297 | 122.4243 | 0.37079 | 122.5296 | 122.4701 | 122.374 | 122.3694 | 122.2733 | -122.4518 | -122.4518 | 122.3236 | 122.4289 | 47.2183 | 43.8858
2061.7656 | 122.5708 | -49.2416 | 73.1827 | -0.048752 | 0.0021255 | 0.06053 | 0.11889 | -4.2682e-05 | -0.0018586 | -0.0013886 | -0.13458 | -0.00070063 | 0.060761 | 0.057845 | -0.029995 | -0.0013629 | 0.00010689 | -2.2156 | 73.1689 | -49.3881 | 73.0087 | -45.1035 | -49.2004 | 3.7491 | -5.5161 | 73.1506 | -49.3149 | 73.0865 | -49.0677 | -49.3698 | -49.173 | -0.14648 | -0.013733 | -0.17395 | 4.1382 | 52.9907 | 0.041199 | 53.1372 | 0.18768 | -0.073242 | -0.032043 | -0.09613 | 0.17395 | 0.068664 | -0.12817 | 0.14191 | -0.054932 | 4.2847 | 122.3969 | 0.24719 | 122.4014 | 122.5571 | 122.4655 | 122.4106 | 122.3923 | -122.5708 | -122.4976 | 122.2504 | 122.3282 | 47.0261 | 43.7256
2062.8281 | 122.612 | -49.5255 | 72.9263 | -0.086899 | 0.00063028 | 0.060103 | 0.11697 | 0.0016663 | -0.0035674 | -0.0035248 | -0.055237 | -0.001128 | 0.062897 | 0.064681 | -0.028927 | 0.00034613 | 0.00096129 | -2.3575 | 72.8851 | -49.6857 | 72.7112 | -45.5704 | -49.855 | 3.598 | -5.722 | 72.8394 | -49.5941 | 72.8165 | -49.3286 | -49.6399 | -49.4385 | -0.16022 | -0.041199 | -0.21515 | 3.9551 | 53.1235 | -0.32959 | 53.2837 | -0.16937 | -0.068664 | -0.086976 | -0.10986 | 0.19684 | 0.086975 | -0.11444 | 0.15564 | -0.045777 | 4.1153 | 122.3969 | 0.2655 | 122.4106 | 122.5708 | 122.4335 | 122.4106 | 122.3648 | -122.612 | -122.5204 | 122.2366 | 122.3419 | 47.168 | 43.8034
2063.7656 | 122.5708 | -49.2645 | 73.2193 | -0.06401 | -0.0010787 | 0.061385 | 0.12167 | -0.0023925 | -0.0050628 | -0.0016022 | -0.027771 | -0.0054004 | 0.065888 | 0.055495 | -0.027218 | 0.00034613 | 0.00096129 | -2.1698 | 73.1781 | -49.3881 | 73.027 | -45.0806 | -49.5163 | 3.6118 | -5.6213 | 73.1781 | -49.292 | 73.114 | -49.054 | -49.3607 | -49.1592 | -0.1236 | -0.041198 | -0.19226 | 4.184 | 52.8763 | -0.25177 | 52.9999 | -0.12817 | -0.027466 | -0.041198 | -0.10529 | 0.21057 | 0.10528 | -0.096131 | 0.13275 | -0.068665 | 4.3076 | 122.4152 | 0.23804 | 122.406 | 122.5662 | 122.4701 | 122.4426 | 122.4426 | -122.6074 | -122.5113 | 122.2916 | 122.3785 | 47.0947 | 43.6432
2064.8438 | 122.7036 | -49.3423 | 73.0362 | -0.17082 | 0.0010575 | 0.061812 | 0.11804 | 0.0031617 | -0.0012176 | -0.0013886 | -0.018616 | -0.0049732 | 0.064392 | 0.060836 | -0.025509 | 0.0014141 | 0.0018159 | -2.0096 | 72.9904 | -49.498 | 72.9904 | -45.163 | -49.6033 | 3.685 | -5.5481 | 72.9721 | -49.4019 | 73.082 | -49.0906 | -49.3973 | -49.1959 | -0.15564 | -0.045777 | -0.045777 | 4.1794 | 53.0273 | -0.26093 | 53.183 | -0.10529 | -0.059509 | -0.064087 | 0.045776 | 0.25177 | 0.14648 | -0.054932 | 0.20599 | 0.004577 | 4.335 | 122.4884 | 0.31128 | 122.4838 | 122.4884 | 122.374 | 122.3328 | 122.3145 | -122.5342 | -122.438 | 122.3328 | 122.4243 | 47.3328 | 43.7942
2065.7656 | 122.6395 | -49.3469 | 73.0133 | -0.094528 | -0.0023605 | 0.061598 | 0.11633 | 0.00017092 | -0.0029266 | -0.0020294 | 0.024109 | -0.0041186 | 0.062256 | 0.066603 | -0.0285 | -0.0013629 | -0.00053411 | -2.0645 | 72.963 | -49.5071 | 72.9309 | -45.2911 | -49.6078 | 3.7811 | -5.5893 | 72.9309 | -49.4614 | 73.0179 | -49.1272 | -49.4019 | -49.2416 | -0.16022 | -0.050354 | -0.082398 | 4.0558 | 53.1281 | -0.26093 | 53.2883 | -0.10071 | -0.11444 | -0.082398 | 0.004577 | 0.21973 | 0.10529 | -0.054931 | 0.21973 | 0.05951 | 4.216 | 122.438 | 0.33417 | 122.4792 | 122.4701 | 122.3923 | 122.3099 | 122.2778 | -122.5204 | -122.4747 | 122.2778 | 122.3648 | 47.2824 | 43.7576
2066.8281 | 122.5937 | -49.2371 | 73.201 | -0.13267 | -0.0017197 | 0.062453 | 0.11953 | 0.00059812 | -0.0048492 | -0.001175 | -0.09491 | -0.0030506 | 0.062683 | 0.064253 | -0.027218 | 0.00077333 | -0.0011749 | -2.1149 | 73.201 | -49.3835 | 73.0865 | -45.0073 | -49.5209 | 3.7994 | -5.6259 | 73.1552 | -49.2783 | 73.1827 | -49.0128 | -49.3149 | -49.1089 | -0.14648 | 0 | -0.11444 | 4.2297 | 53.0365 | -0.28381 | 53.183 | -0.13733 | -0.041198 | -0.045777 | -0.018311 | 0.2243 | 0.12817 | -0.077819 | 0.16937 | -0.036621 | 4.3762 | 122.4701 | 0.2655 | 122.4609 | 122.5845 | 122.4335 | 122.4381 | 122.3923 | -122.5845 | -122.4792 | 122.3236 | 122.4197 | 47.1222 | 43.6111
2067.7656 | 122.5983 | -49.3607 | 73.1094 | -0.025863 | 0.0023391 | 0.061171 | 0.11996 | -0.0023925 | -0.0033538 | -0.0041656 | -0.04303 | -0.003905 | 0.061829 | 0.063399 | -0.02914 | 0.00013253 | -0.0026703 | -2.0691 | 73.114 | -49.4614 | 72.9446 | -45.2454 | -49.617 | 3.772 | -5.6442 | 73.1003 | -49.3744 | 73.027 | -49.118 | -49.4202 | -49.2371 | -0.10071 | 0.004578 | -0.16479 | 4.1153 | 53.1326 | -0.25635 | 53.2333 | -0.15564 | -0.013733 | -0.009155 | -0.082397 | 0.24262 | 0.1236 | -0.059509 | 0.13733 | -0.045776 | 4.216 | 122.406 | 0.25635 | 122.4014 | 122.5754 | 122.4747 | 122.4747 | 122.4609 | -122.5708 | -122.4838 | 122.3053 | 122.3877 | 47.2916 | 43.7164
2068.8281 | 122.6028 | -49.2462 | 73.2101 | -0.10979 | 0.00063028 | 0.062239 | 0.1159 | -0.00089728 | -0.0003632 | -0.0043792 | -0.0094604 | -0.0019824 | 0.065888 | 0.057845 | -0.025295 | 0.00055973 | 0.00010689 | -1.8311 | 73.1644 | -49.3698 | 73.0637 | -45.0302 | -49.4293 | 3.8361 | -5.484 | 73.1506 | -49.2966 | 73.1186 | -49.0082 | -49.3011 | -49.1409 | -0.1236 | -0.045776 | -0.14648 | 4.216 | 53.0823 | -0.18311 | 53.2059 | -0.059509 | -0.050354 | -0.059509 | -0.091553 | 0.23804 | 0.10529 | -0.054931 | 0.15564 | -0.004577 | 4.3396 | 122.4335 | 0.28839 | 122.4152 | 122.5342 | 122.4472 | 122.4106 | 122.3969 | -122.58 | -122.5067 | 122.3099 | 122.3648 | 47.4152 | 43.7622
2069.7656 | 122.6028 | -49.3378 | 73.0911 | -0.048752 | 0.0012711 | 0.062239 | 0.12124 | 0.0020935 | -0.0033538 | -0.0013886 | -0.085754 | -0.0028368 | 0.065247 | 0.064253 | -0.0285 | 0.0024823 | -0.00032051 | -1.8082 | 73.0682 | -49.4843 | 72.995 | -45.195 | -49.6078 | 3.7674 | -5.4428 | 73.0408 | -49.3927 | 73.0453 | -49.1592 | -49.4522 | -49.2462 | -0.14648 | -0.022888 | -0.09613 | 4.1428 | 53.1052 | -0.27008 | 53.2516 | -0.1236 | -0.054931 | -0.050354 | -0.045776 | 0.17853 | 0.091553 | -0.11444 | 0.14648 | -0.059509 | 4.2892 | 122.4792 | 0.23346 | 122.438 | 122.5525 | 122.4335 | 122.406 | 122.3785 | -122.5754 | -122.4838 | 122.3328 | 122.3831 | 47.5296 | 43.895
2070.8281 | 122.699 | -49.1959 | 73.1781 | -0.17082 | 0.0014847 | 0.062025 | 0.1159 | -0.0011109 | -0.0018586 | -0.004593 | 0.024109 | -0.003905 | 0.062897 | 0.052291 | -0.027218 | -0.0026447 | -0.0022431 | -1.2589 | 73.1689 | -49.3378 | 73.1552 | -44.9295 | -49.3835 | 4.0329 | -5.4382 | 73.1277 | -49.2371 | 73.2147 | -48.9166 | -49.2004 | -49.0494 | -0.14191 | -0.009156 | -0.022889 | 4.2664 | 53.2288 | -0.18768 | 53.3707 | -0.045776 | -0.041199 | -0.050354 | 0.036621 | 0.27924 | 0.14648 | -0.004577 | 0.18768 | 0.036622 | 4.4083 | 122.493 | 0.32043 | 122.4518 | 122.5067 | 122.3648 | 122.3648 | 122.3236 | -122.5159 | -122.4152 | 122.3511 | 122.4106 | 47.937 | 43.7576
2071.7656 | 122.6578 | -49.3423 | 73.0499 | -0.11742 | 0.0021255 | 0.062025 | 0.11804 | 0.00038452 | -0.0037812 | -0.00010676 | 0.011902 | -0.0049732 | 0.060974 | 0.06404 | -0.028713 | -0.00029487 | 0.0011749 | -1.1307 | 73.0133 | -49.4659 | 72.9996 | -45.1721 | -49.5483 | 4.0329 | -5.3787 | 72.9904 | -49.4019 | 73.0408 | -49.086 | -49.3927 | -49.2004 | -0.1236 | -0.036621 | -0.050354 | 4.1702 | 53.3752 | -0.20599 | 53.4988 | -0.082398 | -0.059509 | -0.05951 | -0.009156 | 0.25635 | 0.14191 | -0.050354 | 0.20142 | 0.009155 | 4.2938 | 122.4655 | 0.31586 | 122.4426 | 122.4792 | 122.3923 | 122.3557 | 122.3328 | -122.5159 | -122.4518 | 122.3419 | 122.3831 | 48.2117 | 43.9636
2072.8281 | 122.6303 | -49.3698 | 73.0453 | -0.094528 | -1.0718e-05 | 0.062239 | 0.11761 | -0.0030335 | -0.0016448 | -0.0035248 | 0.027161 | -0.0045458 | 0.061615 | 0.062117 | -0.027645 | 0.00055973 | 0.0018159 | -1.2268 | 72.9675 | -49.5117 | 72.9538 | -45.2133 | -49.5941 | 4.1016 | -5.3101 | 72.9721 | -49.4385 | 73.0316 | -49.118 | -49.4156 | -49.2416 | -0.14191 | -0.07782 | -0.091553 | 4.1565 | 53.4714 | -0.2243 | 53.6133 | -0.082397 | -0.068665 | -0.073242 | -0.013733 | 0.25177 | 0.12817 | -0.045776 | 0.19684 | 0.022889 | 4.2984 | 122.4655 | 0.32043 | 122.4701 | 122.4792 | 122.4106 | 122.3373 | 122.3419 | -122.5571 | -122.4838 | 122.3236 | 122.4014 | 48.143 | 44.0598
2073.7656 | 122.6532 | -49.2691 | 73.1461 | -0.094528 | 0.00063028 | 0.062239 | 0.11868 | 0.00038452 | -0.0039948 | -0.003952 | -0.00030524 | -0.0030506 | 0.061829 | 0.059981 | -0.027859 | 0.00098693 | 0.0011749 | -1.1536 | 73.0728 | -49.3973 | 73.0911 | -45.0348 | -49.4705 | 3.9963 | -5.2551 | 73.0865 | -49.3149 | 73.1598 | -48.999 | -49.2737 | -49.118 | -0.12817 | -0.073242 | -0.054932 | 4.2343 | 53.2654 | -0.20142 | 53.3936 | -0.073242 | -0.045776 | -0.059509 | 0.013733 | 0.27008 | 0.15106 | -0.004578 | 0.19684 | 0.041198 | 4.3625 | 122.4884 | 0.31586 | 122.4747 | 122.4701 | 122.4014 | 122.3419 | 122.3557 | -122.5433 | -122.4609 | 122.3602 | 122.4289 | 48.1155 | 44.014
2074.8281 | 122.5891 | -49.5117 | 72.9584 | -0.086899 | 0.0014847 | 0.06053 | 0.11996 | 0.0025207 | -0.0035674 | 0.00074764 | -0.10406 | -0.002196 | 0.064179 | 0.058486 | -0.028713 | 0.0016277 | 0.0016021 | -1.2497 | 72.8668 | -49.6811 | 72.7753 | -45.4376 | -49.8047 | 3.8223 | -5.5618 | 72.8897 | -49.5621 | 72.876 | -49.2874 | -49.6078 | -49.4156 | -0.16937 | -0.091553 | -0.18311 | 4.0741 | 53.334 | -0.29297 | 53.5034 | -0.1236 | -0.050354 | -0.068665 | -0.082397 | 0.2243 | 0.096131 | -0.09613 | 0.14648 | -0.045776 | 4.2435 | 122.4564 | 0.27466 | 122.4381 | 122.5479 | 122.4518 | 122.3785 | 122.4014 | -122.6395 | -122.5204 | 122.287 | 122.3877 | 48.262 | 43.9499
2075.7656 | 122.5571 | -49.2783 | 73.1461 | -0.07164 | 0.00084388 | 0.062666 | 0.11654 | 0.0014527 | -0.0037812 | -0.00096136 | 0.011902 | -0.0032642 | 0.064606 | 0.059554 | -0.025295 | -0.00072207 | 0.0016021 | -1.2085 | 73.1003 | -49.4385 | 72.9996 | -45.1126 | -49.5621 | 3.9276 | -5.5435 | 73.0957 | -49.3515 | 73.0728 | -49.0768 | -49.3835 | -49.2096 | -0.16022 | -0.045776 | -0.14648 | 4.1656 | 53.2059 | -0.28381 | 53.3661 | -0.1236 | -0.073242 | -0.050354 | -0.073242 | 0.20142 | 0.068664 | -0.10529 | 0.14191 | -0.032044 | 4.3259 | 122.4381 | 0.27466 | 122.4243 | 122.5388 | 122.4472 | 122.3785 | 122.374 | -122.5845 | -122.4976 | 122.2778 | 122.3511 | 48.0698 | 43.7347
2076.8281 | 122.6349 | -49.3973 | 73.0041 | -0.094528 | -0.00043792 | 0.060316 | 0.1174 | 0.0020935 | 0.0009186 | -0.0033112 | 0.0027466 | -0.0049732 | 0.063965 | 0.065535 | -0.028072 | 0.00034613 | 0.0016021 | -1.1261 | 72.9721 | -49.5255 | 72.9172 | -45.2454 | -49.6307 | 3.9688 | -5.3787 | 72.9401 | -49.4705 | 72.9721 | -49.1501 | -49.4568 | -49.2874 | -0.12817 | -0.032043 | -0.086975 | 4.1519 | 53.3661 | -0.23346 | 53.4943 | -0.10529 | -0.073242 | -0.064087 | -0.032043 | 0.24719 | 0.10986 | -0.059509 | 0.1831 | 0.013733 | 4.2801 | 122.4426 | 0.32044 | 122.4426 | 122.4976 | 122.4106 | 122.3694 | 122.3373 | -122.5296 | -122.4747 | 122.3145 | 122.3694 | 48.2712 | 44.0186
2077.7656 | 122.5845 | -49.3057 | 73.1461 | -0.07164 | -0.00065152 | 0.062239 | 0.11911 | -0.0013245 | -0.0022858 | -0.00096136 | -0.0033568 | -0.0041186 | 0.064179 | 0.061476 | -0.028072 | -0.0013629 | 0.0045929 | -1.1215 | 73.114 | -49.4522 | 72.963 | -45.1721 | -49.5987 | 3.9368 | -5.4108 | 73.0728 | -49.3561 | 73.0499 | -49.0997 | -49.3881 | -49.2279 | -0.14648 | -0.032043 | -0.1831 | 4.1336 | 53.2425 | -0.29297 | 53.389 | -0.14648 | -0.050354 | -0.073242 | -0.09613 | 0.20599 | 0.07782 | -0.082398 | 0.12817 | -0.032044 | 4.2801 | 122.4152 | 0.25635 | 122.406 | 122.5662 | 122.4289 | 122.4197 | 122.3785 | -122.5983 | -122.5021 | 122.2687 | 122.3557 | 48.1842 | 43.895
2078.8281 | 122.5891 | -49.2599 | 73.2101 | -0.07164 | 0.00084388 | 0.061171 | 0.11953 | 0.0010253 | -0.0037812 | -0.0037384 | -0.082703 | -0.0036914 | 0.063111 | 0.065962 | -0.02914 | 0.0041913 | 0.0026703 | -1.149 | 73.1689 | -49.4156 | 72.9904 | -45.1355 | -49.5529 | 3.9597 | -5.4749 | 73.1415 | -49.3286 | 73.114 | -49.0494 | -49.3607 | -49.1638 | -0.15564 | -0.041199 | -0.21973 | 4.1245 | 53.2196 | -0.29297 | 53.3752 | -0.13733 | -0.068664 | -0.068665 | -0.09613 | 0.21057 | 0.096131 | -0.10071 | 0.16479 | -0.032044 | 4.2801 | 122.406 | 0.27924 | 122.4426 | 122.5845 | 122.4701 | 122.4289 | 122.4014 | -122.6257 | -122.5388 | 122.2504 | 122.374 | 48.111 | 43.7851
2079.7656 | 122.5616 | -49.3561 | 73.0957 | -0.12505 | 0.00063028 | 0.060744 | 0.12103 | 0.0020935 | -0.0039948 | -0.0020294 | -0.091858 | -0.0036914 | 0.062897 | 0.061476 | -0.027645 | 0.00055973 | -0.00010671 | -1.2222 | 73.0408 | -49.5255 | 72.9263 | -45.2225 | -49.6536 | 3.9642 | -5.4932 | 73.0545 | -49.4064 | 73.0133 | -49.1638 | -49.498 | -49.292 | -0.16937 | -0.054932 | -0.16937 | 4.1336 | 53.3203 | -0.29755 | 53.4897 | -0.12817 | -0.050354 | -0.041199 | -0.082397 | 0.19226 | 0.064087 | -0.14191 | 0.11444 | -0.091553 | 4.303 | 122.4518 | 0.24262 | 122.4197 | 122.5662 | 122.4609 | 122.3969 | 122.4106 | -122.6212 | -122.5021 | 122.2824 | 122.3694 | 48.1339 | 43.8629
2080.8281 | 122.5662 | -49.498 | 72.9446 | -0.079269 | -0.00065152 | 0.061598 | 0.11761 | -0.0036743 | -0.0050628 | -0.0041656 | -0.030823 | -0.003905 | 0.062256 | 0.05464 | -0.028072 | 0.0029095 | 0.0013885 | -1.236 | 72.9309 | -49.6353 | 72.7753 | -45.4651 | -49.8047 | 4.129 | -5.484 | 72.9172 | -49.5575 | 72.7432 | -49.2233 | -49.5346 | -49.3652 | -0.13733 | -0.013733 | -0.16937 | 4.0329 | 53.627 | -0.3067 | 53.7643 | -0.16937 | -0.059509 | -0.027466 | -0.20142 | 0.27466 | 0.13275 | -0.036621 | 0.19226 | 0.022888 | 4.1702 | 122.4106 | 0.33417 | 122.3007 | 122.5662 | 122.4747 | 122.4289 | 122.4152 | -122.58 | -122.5021 | 122.2733 | 122.2412 | 48.262 | 44.014
2081.7656 | 122.5754 | -49.5071 | 72.9446 | -0.048752 | 0.00063028 | 0.060744 | 0.11846 | 0.0010253 | -0.0033538 | -0.0048066 | -0.11017 | -0.0017688 | 0.064179 | 0.063613 | -0.027004 | 0.0029095 | 0.0028839 | -1.1581 | 72.8897 | -49.6857 | 72.7798 | -45.4514 | -49.8184 | 4.0192 | -5.3101 | 72.876 | -49.5712 | 72.8439 | -49.292 | -49.4751 | -49.324 | -0.17853 | -0.054932 | -0.16479 | 4.0558 | 53.5263 | -0.31128 | 53.7048 | -0.13275 | -0.064087 | -0.068664 | -0.10071 | 0.21515 | 0.1831 | 0.032043 | 0.24719 | 0.09613 | 4.2343 | 122.4655 | 0.27924 | 122.4152 | 122.5754 | 122.4472 | 122.3969 | 122.3831 | -122.6303 | -122.5159 | 122.287 | 122.3511 | 48.349 | 44.1971
2082.8281 | 122.6303 | -49.6078 | 72.7936 | -0.094528 | 0.0016983 | 0.06288 | 0.11889 | -0.00046988 | -0.0059174 | -0.0013886 | 0.027161 | -0.0017688 | 0.063751 | 0.05934 | -0.029354 | -0.00050847 | 0.0016021 | -1.1902 | 72.7798 | -49.7498 | 72.6883 | -45.5017 | -50.1022 | 4.0054 | -5.484 | 72.8027 | -49.6674 | 72.789 | -49.3652 | -49.7131 | -49.4934 | -0.14191 | -0.013733 | -0.10529 | 4.1061 | 53.6133 | -0.49439 | 53.7552 | -0.35248 | -0.059509 | 0.009155 | -0.004578 | 0.24262 | 0.11444 | -0.10529 | 0.17395 | -0.045777 | 4.248 | 122.438 | 0.30212 | 122.4564 | 122.5296 | 122.4701 | 122.3877 | 122.4106 | -122.5433 | -122.4609 | 122.2961 | 122.3969 | 48.4177 | 44.1238
2083.7656 | 122.6166 | -49.5941 | 72.8668 | -0.16319 | 0.00041648 | 0.060744 | 0.11761 | 0.0029479 | -0.0014312 | -0.0016022 | -0.0064086 | -0.0030506 | 0.06482 | 0.059981 | -0.026363 | -8.1274e-05 | 0.0026703 | -1.1353 | 72.8256 | -49.7772 | 72.6791 | -45.5292 | -49.8825 | 4.184 | -5.4108 | 72.8302 | -49.6399 | 72.7707 | -49.3561 | -49.6674 | -49.5026 | -0.18311 | -0.041198 | -0.18768 | 4.0649 | 53.7781 | -0.28839 | 53.9612 | -0.10528 | -0.045777 | -0.036621 | -0.09613 | 0.23804 | 0.091553 | -0.073242 | 0.13733 | -0.027465 | 4.248 | 122.4564 | 0.28381 | 122.4106 | 122.6028 | 122.4701 | 122.4197 | 122.4243 | -122.644 | -122.5067 | 122.2733 | 122.3648 | 48.4589 | 44.1833
2084.8281 | 122.5525 | -49.6445 | 72.8119 | -0.079269 | -0.00022432 | 0.062453 | 0.11868 | -4.2682e-05 | -0.0033538 | -0.0018158 | -0.097961 | -5.9826e-05 | 0.062683 | 0.061904 | -0.025722 | 0.0044049 | 0.00053409 | -1.1948 | 72.789 | -49.8001 | 72.6379 | -45.6299 | -49.9512 | 4.0421 | -5.571 | 72.7707 | -49.6994 | 72.7249 | -49.4522 | -49.7864 | -49.5621 | -0.15564 | -0.022889 | -0.17395 | 4.0146 | 53.6865 | -0.3067 | 53.8422 | -0.15106 | -0.054932 | -0.041199 | -0.086975 | 0.19226 | 0.082397 | -0.14191 | 0.13733 | -0.086975 | 4.1702 | 122.438 | 0.24719 | 122.4243 | 122.5891 | 122.4701 | 122.4335 | 122.4152 | -122.612 | -122.5113 | 122.2824 | 122.3694 | 48.4497 | 44.0735
2085.7656 | 122.6166 | -49.617 | 72.821 | -0.033493 | 0.00084388 | 0.060957 | 0.11846 | -0.00046988 | -0.0035674 | -0.00053396 | -0.058289 | -0.0017688 | 0.063111 | 0.05165 | -0.0238 | 0.0018413 | -0.0013885 | -1.1444 | 72.7982 | -49.7635 | 72.6791 | -45.5475 | -49.8962 | 4.0878 | -5.5069 | 72.7524 | -49.6628 | 72.7798 | -49.2371 | -49.7223 | -49.4934 | -0.14648 | -0.022888 | -0.14191 | 4.0695 | 53.7048 | -0.27924 | 53.8513 | -0.13275 | -0.045777 | -0.068665 | -0.041199 | 0.37994 | 0.1236 | -0.10529 | 0.16937 | -0.059509 | 4.216 | 122.4426 | 0.42572 | 122.4426 | 122.5616 | 122.4152 | 122.4152 | 122.3694 | -122.5845 | -122.4838 | 122.2961 | 122.3969 | 48.4726 | 44.1101
2086.8281 | 122.6212 | -49.6674 | 72.7753 | -0.086899 | -0.00022432 | 0.061598 | 0.11953 | 0.00038452 | -0.0024994 | -0.0035248 | -0.097961 | -0.0034778 | 0.060974 | 0.062331 | -0.028286 | -8.1274e-05 | -0.00032051 | -1.2177 | 72.7158 | -49.8276 | 72.6105 | -45.6665 | -49.9374 | 3.9459 | -5.5435 | 72.702 | -49.7269 | 72.7066 | -49.4431 | -49.7681 | -49.5621 | -0.16022 | -0.05951 | -0.16479 | 4.0009 | 53.6133 | -0.27008 | 53.7735 | -0.10986 | -0.05951 | -0.073243 | -0.068665 | 0.2243 | 0.10529 | -0.10071 | 0.1648 | -0.041198 | 4.1611 | 122.4381 | 0.28381 | 122.4335 | 122.5433 | 122.4289 | 122.3831 | 122.3694 | -122.6028 | -122.5021 | 122.2778 | 122.374 | 48.4497 | 44.1238
2087.7656 | 122.5983 | -49.7772 | 72.6974 | -0.13267 | -0.0010787 | 0.061385 | 0.11718 | 0.0010253 | -0.0031402 | -0.0037384 | 0.011902 | -0.0030506 | 0.065674 | 0.058699 | -0.027218 | 0.00098693 | -0.00032051 | -1.0986 | 72.6746 | -49.9008 | 72.4869 | -45.8313 | -50.0977 | 4.1977 | -5.5298 | 72.6288 | -49.8276 | 72.583 | -49.5621 | -49.855 | -49.6994 | -0.1236 | -0.022888 | -0.21057 | 3.9459 | 53.9749 | -0.32043 | 54.0985 | -0.19684 | -0.050354 | -0.068665 | -0.11444 | 0.21515 | 0.07782 | -0.07782 | 0.12817 | -0.027466 | 4.0695 | 122.3877 | 0.2655 | 122.4106 | 122.5754 | 122.4564 | 122.4518 | 122.406 | -122.5983 | -122.525 | 122.2641 | 122.3602 | 48.6786 | 44.2474
2088.8281 | 122.5296 | -49.8505 | 72.5967 | -0.10979 | 0.0019119 | 0.060744 | 0.12081 | 0.0023071 | -0.002713 | -0.0026704 | -0.067444 | -0.0017688 | 0.065247 | 0.066176 | -0.028927 | 0.0031231 | 0.00074769 | -1.2405 | 72.5693 | -50.0061 | 72.4182 | -45.9503 | -50.1663 | 4.0192 | -5.6442 | 72.5647 | -49.9054 | 72.5006 | -49.6674 | -49.9832 | -49.7635 | -0.15564 | -0.027466 | -0.17853 | 3.9001 | 53.8696 | -0.31586 | 54.0253 | -0.16022 | -0.054932 | -0.032044 | -0.096131 | 0.18311 | 0.086975 | -0.13275 | 0.14191 | -0.077819 | 4.0558 | 122.4243 | 0.23804 | 122.406 | 122.5754 | 122.4701 | 122.4197 | 122.4152 | -122.6028 | -122.5021 | 122.2687 | 122.3511 | 48.6099 | 44.2062
2089.7656 | 122.5754 | -49.8322 | 72.5967 | -0.10216 | 0.0010575 | 0.061385 | 0.11846 | 0.0014527 | -0.0016448 | -0.0030976 | -0.082703 | -0.0028368 | 0.062256 | 0.060408 | -0.027218 | 0.0022687 | 0.00096129 | -1.1765 | 72.5876 | -49.9558 | 72.4457 | -45.9091 | -50.1434 | 4.0741 | -5.5252 | 72.5876 | -49.8871 | 72.5281 | -49.6353 | -49.9695 | -49.7543 | -0.1236 | -0.009156 | -0.15106 | 3.923 | 53.9062 | -0.31128 | 54.0298 | -0.18768 | -0.054932 | -0.009156 | -0.068665 | 0.19684 | 0.07782 | -0.13733 | 0.13275 | -0.082397 | 4.0466 | 122.4014 | 0.25177 | 122.4152 | 122.5433 | 122.4747 | 122.4197 | 122.4197 | -122.5525 | -122.4838 | 122.2778 | 122.3602 | 48.6557 | 44.3069
2090.8281 | 122.6028 | -49.7818 | 72.6288 | -0.094528 | 0.0019119 | 0.061812 | 0.11846 | 0.0020935 | -0.004422 | -0.0020294 | -0.06134 | -0.0026232 | 0.065674 | 0.062972 | -0.028927 | 0.0020551 | 0.0013885 | -1.0849 | 72.6242 | -49.9054 | 72.4915 | -45.8084 | -50.061 | 4.2114 | -5.5115 | 72.6196 | -49.8138 | 72.5967 | -49.5575 | -49.8917 | -49.6765 | -0.1236 | -0.004577 | -0.13733 | 3.9734 | 53.9932 | -0.27924 | 54.1168 | -0.15564 | -0.032044 | -0.009155 | -0.032043 | 0.2243 | 0.10529 | -0.10986 | 0.13733 | -0.07782 | 4.097 | 122.3969 | 0.25635 | 122.4106 | 122.5296 | 122.4335 | 122.406 | 122.4014 | -122.5342 | -122.4426 | 122.2733 | 122.3785 | 48.6969 | 44.2703
2091.7656 | 122.6624 | -49.8276 | 72.5967 | -0.06401 | -0.00065152 | 0.062453 | 0.11804 | 0.00081172 | -0.0035674 | 0.00032044 | -0.055237 | -0.0034778 | 0.062683 | 0.067671 | -0.027645 | 0.00098693 | 0.0011749 | -1.2039 | 72.5601 | -49.9878 | 72.4411 | -45.8908 | -50.1068 | 4.1885 | -5.6168 | 72.5555 | -49.8779 | 72.6288 | -49.5758 | -49.9512 | -49.704 | -0.16022 | -0.036621 | -0.15564 | 3.9368 | 54.0161 | -0.27924 | 54.1763 | -0.11902 | -0.050354 | -0.041199 | 0.032043 | 0.25177 | 0.1236 | -0.1236 | 0.17395 | -0.073242 | 4.097 | 122.4289 | 0.30212 | 122.5067 | 122.5479 | 122.4335 | 122.3877 | 122.3831 | -122.5845 | -122.4747 | 122.2687 | 122.4564 | 48.6237 | 44.2108
2092.8281 | 122.6212 | -49.7772 | 72.6379 | -0.07164 | 0.00020288 | 0.061812 | 0.11804 | 0.0042297 | -0.0020722 | -0.0058746 | -0.027771 | -0.0024096 | 0.064606 | 0.061904 | -0.027431 | 0.00013253 | -0.00074771 | -1.2589 | 72.6151 | -49.9466 | 72.4731 | -45.8542 | -50.0473 | 4.184 | -5.4565 | 72.5922 | -49.8505 | 72.6059 | -49.5255 | -49.855 | -49.649 | -0.16937 | -0.022888 | -0.16479 | 3.923 | 53.9612 | -0.27008 | 54.1306 | -0.10071 | -0.073242 | -0.045776 | -0.032043 | 0.25177 | 0.12817 | -0.07782 | 0.20142 | -0.004578 | 4.0924 | 122.4197 | 0.32501 | 122.4564 | 122.5616 | 122.4426 | 122.3923 | 122.3694 | -122.5845 | -122.4884 | 122.2504 | 122.3831 | 48.5184 | 44.3207
2093.7656 | 122.6303 | -49.7177 | 72.7249 | -0.079269 | -0.00022432 | 0.062025 | 0.11889 | 0.0027343 | 6.4004e-05 | -0.005661 | -0.0064086 | -0.0028368 | 0.062897 | 0.055922 | -0.026363 | 0.00055973 | 0.00074769 | -1.2497 | 72.6974 | -49.8825 | 72.5464 | -45.7993 | -50.0107 | 4.1656 | -5.6305 | 72.6425 | -49.7772 | 72.6517 | -49.4568 | -49.7772 | -49.5941 | -0.16479 | -0.027466 | -0.17853 | 3.9185 | 53.8834 | -0.29297 | 54.0482 | -0.12817 | -0.05951 | -0.082398 | -0.073243 | 0.26093 | 0.1236 | -0.05951 | 0.18311 | 0 | 4.0833 | 122.4289 | 0.32044 | 122.4289 | 122.58 | 122.4197 | 122.4152 | 122.3602 | -122.6074 | -122.5021 | 122.2641 | 122.3694 | 48.468 | 44.0872
2094.8281 | 122.6166 | -49.5575 | 72.8714 | -0.10216 | 0.00020288 | 0.061171 | 0.11953 | 0.00017092 | -0.0035674 | -0.004593 | -0.015564 | -0.0019824 | 0.063538 | 0.063613 | -0.026791 | 0.00013253 | -0.00096131 | -1.1032 | 72.8119 | -49.7314 | 72.7112 | -45.5475 | -49.8413 | 4.3488 | -5.5344 | 72.8119 | -49.6445 | 72.8256 | -49.3103 | -49.6399 | -49.4431 | -0.17395 | -0.059509 | -0.16022 | 4.01 | 53.9062 | -0.28381 | 54.0802 | -0.10986 | -0.086975 | -0.059509 | -0.045776 | 0.24719 | 0.11444 | -0.082398 | 0.20142 | 0.004577 | 4.184 | 122.4426 | 0.33417 | 122.4701 | 122.5433 | 122.4564 | 122.3694 | 122.3694 | -122.6028 | -122.5159 | 122.2687 | 122.3831 | 48.4543 | 44.0231
2095.7656 | 122.6303 | -49.585 | 72.8577 | -0.10979 | -0.00086512 | 0.063094 | 0.11932 | 0.0016663 | -0.0039948 | 0.00032044 | -0.04303 | -0.0041186 | 0.062042 | 0.065322 | -0.029568 | 0.00013253 | 0.0041657 | -1.0666 | 72.8302 | -49.7452 | 72.6425 | -45.4514 | -49.736 | 4.3716 | -5.4657 | 72.8073 | -49.6445 | 72.8348 | -49.3195 | -49.6307 | -49.4522 | -0.16022 | -0.027466 | -0.21515 | 4.1336 | 53.9566 | -0.15106 | 54.1168 | 0.009155 | -0.059509 | -0.050354 | -0.022888 | 0.2655 | 0.13275 | -0.045776 | 0.19226 | 0.013733 | 4.2938 | 122.3877 | 0.32501 | 122.4792 | 122.5754 | 122.4518 | 122.4152 | 122.3923 | -122.6028 | -122.5021 | 122.2275 | 122.4197 | 48.5184 | 44.1193
2096.8281 | 122.6074 | -49.5026 | 72.9309 | -0.10216 | 0.0025529 | 0.060316 | 0.11804 | 0.0027343 | -0.0035674 | -0.0018158 | -0.058289 | -0.0030506 | 0.063111 | 0.060836 | -0.027218 | 0.0031231 | 0.0033111 | -1.0025 | 72.9263 | -49.6262 | 72.7936 | -45.3461 | -49.736 | 4.3579 | -6.0242 | 72.8531 | -49.5621 | 72.9034 | -49.2554 | -49.6033 | -49.3835 | -0.1236 | -0.004577 | -0.13733 | 4.1565 | 53.8605 | -0.23346 | 53.9841 | -0.10986 | -0.05951 | -0.07782 | -0.027466 | 0.24719 | 0.11902 | -0.10071 | 0.17853 | -0.041198 | 4.2801 | 122.4197 | 0.3067 | 122.4655 | 122.5525 | 122.4152 | 122.4289 | 122.3557 | -122.5571 | -122.493 | 122.2961 | 122.406 | 48.5001 | 43.4784
2097.7656 | 122.612 | -49.7314 | 72.7112 | -0.27763 | 0.0014847 | 0.061598 | 0.11611 | -0.0017517 | -0.0037812 | -0.0020294 | -0.033874 | -0.002196 | 0.06247 | 0.065322 | -0.029354 | 0.00013253 | 0.00032049 | -0.94757 | 72.7112 | -49.8505 | 72.5739 | -45.5704 | -49.9649 | 4.2389 | -5.5984 | 72.6746 | -49.7864 | 72.6746 | -49.4751 | -49.8047 | -49.5987 | -0.11902 | 0 | -0.13733 | 4.1611 | 53.9703 | -0.23346 | 54.0894 | -0.11444 | -0.054932 | -0.036621 | -0.036621 | 0.25635 | 0.13275 | -0.073242 | 0.18768 | -0.01831 | 4.2801 | 122.4243 | 0.31128 | 122.4609 | 122.5616 | 122.4609 | 122.4426 | 122.406 | -122.5616 | -122.4976 | 122.3053 | 122.406 | 48.7839 | 44.133
2098.8281 | 122.6944 | -49.7726 | 72.5967 | -0.07164 | -1.0718e-05 | 0.06053 | 0.11868 | -0.0032471 | -0.0022858 | 0.00032044 | -0.030823 | -0.00048703 | 0.063538 | 0.059127 | -0.027218 | 0.0012005 | 0.00074769 | -1.1169 | 72.5647 | -49.9374 | 72.5052 | -45.6665 | -50.0793 | 4.1107 | -5.6259 | 72.551 | -49.8322 | 72.6608 | -49.4934 | -49.8093 | -49.6078 | -0.16479 | -0.032044 | -0.091553 | 4.1061 | 53.8834 | -0.3067 | 54.0482 | -0.14191 | -0.059509 | -0.045777 | 0.064087 | 0.27924 | 0.16479 | -0.036621 | 0.2243 | 0.022888 | 4.2709 | 122.4426 | 0.33874 | 122.493 | 122.5021 | 122.3831 | 122.3373 | 122.3236 | -122.5342 | -122.4289 | 122.2778 | 122.4335 | 48.6557 | 44.1467
2099.7656 | 122.5891 | -49.9008 | 72.5235 | -0.11742 | 0.00063028 | 0.061598 | 0.12039 | 0.0020935 | -0.0031402 | -0.0020294 | -0.033874 | -0.0036914 | 0.063751 | 0.056136 | -0.027645 | 0.0020551 | 0.0011749 | -1.1398 | 72.551 | -50.0427 | 72.345 | -45.9045 | -50.2258 | 3.9871 | -5.7312 | 72.4869 | -49.9466 | 72.4777 | -49.6765 | -50.0153 | -49.8001 | -0.14191 | 0.027465 | -0.17853 | 3.9963 | 53.8879 | -0.32501 | 54.0298 | -0.18311 | -0.045776 | -0.036622 | -0.045777 | 0.2243 | 0.10071 | -0.11444 | 0.14648 | -0.068665 | 4.1382 | 122.3877 | 0.27008 | 122.4243 | 122.5937 | 122.4335 | 122.4518 | 122.3877 | -122.5662 | -122.4701 | 122.2458 | 122.3785 | 48.761 | 44.1696
2100.8281 | 122.612 | -49.9558 | 72.496 | -0.14793 | -1.0718e-05 | 0.063734 | 0.12124 | 0.0029479 | -0.0031402 | -0.0065156 | 0.0027466 | -0.00027343 | 0.062042 | 0.055709 | -0.028286 | -0.00093567 | 0.00032049 | -1.181 | 72.4411 | -50.1343 | 72.4869 | -45.8176 | -50.4639 | 3.9688 | -5.8319 | 72.4319 | -50.029 | 72.3953 | -49.7681 | -50.1022 | -49.8917 | -0.17853 | -0.054932 | -0.009156 | 4.1382 | 53.9246 | -0.50812 | 54.1031 | -0.32959 | -0.073242 | -0.064087 | -0.10071 | 0.18768 | 0.064087 | -0.14648 | 0.13733 | -0.073242 | 4.3167 | 122.6212 | 0.26093 | 122.4243 | 122.5754 | 122.4609 | 122.3969 | 122.3877 | -122.6303 | -122.525 | 122.4426 | 122.3511 | 48.7747 | 44.1238
2101.7656 | 122.5937 | -50.2579 | 72.1664 | -0.1403 | -0.00022432 | 0.063307 | 0.12081 | 0.0025207 | -0.0037812 | -0.002884 | -0.055237 | -0.0043322 | 0.064606 | 0.063185 | -0.024868 | 0.0020551 | -0.00053411 | -1.2177 | 72.2809 | -50.322 | 72.0428 | -46.2524 | -50.5508 | 3.9139 | -5.983 | 72.1069 | -50.3082 | 72.1573 | -49.9924 | -50.4272 | -50.1755 | -0.064086 | 0.11444 | -0.1236 | 4.0054 | 54.1718 | -0.29297 | 54.2358 | -0.22888 | -0.050354 | -0.059509 | -0.009155 | 0.2655 | 0.082398 | -0.16937 | 0.13275 | -0.11902 | 4.0695 | 122.3648 | 0.31586 | 122.4655 | 122.6028 | 122.4152 | 122.5388 | 122.3648 | -122.4884 | -122.4747 | 122.3007 | 122.4152 | 49.0402 | 44.2749
2102.8281 | 122.5845 | -50.3998 | 72.0245 | -0.15556 | 0.0016983 | 0.062666 | 0.11911 | 0.0020935 | -0.0024994 | -0.004593 | -0.052185 | -0.002196 | 0.064179 | 0.065108 | -0.028927 | -0.00050847 | 0.0020295 | -1.1398 | 72.0062 | -50.5325 | 71.9147 | -46.3715 | -50.6744 | 4.0695 | -5.6488 | 71.9971 | -50.4593 | 71.9925 | -50.148 | -50.4776 | -50.2808 | -0.13275 | -0.01831 | -0.10986 | 4.0283 | 54.4693 | -0.27466 | 54.6021 | -0.14191 | -0.05951 | -0.027466 | -0.032043 | 0.25177 | 0.11902 | -0.07782 | 0.17853 | -0.01831 | 4.1611 | 122.4472 | 0.31128 | 122.4518 | 122.5388 | 122.4564 | 122.406 | 122.3969 | -122.5571 | -122.4838 | 122.3145 | 122.3923 | 49.2599 | 44.751
2103.7656 | 122.5845 | -50.1343 | 72.2946 | -0.11742 | -0.00043792 | 0.063948 | 0.12039 | 0.0050843 | -0.0022858 | -0.0013886 | -0.058289 | -0.0047594 | 0.062042 | 0.056777 | -0.027004 | 0.00034613 | 0.0037385 | -1.1902 | 72.2534 | -50.2853 | 72.1573 | -46.019 | -50.4044 | 4.2023 | -5.5389 | 72.2351 | -50.1846 | 72.2488 | -49.8734 | -50.2029 | -50.0153 | -0.15106 | -0.041199 | -0.13733 | 4.1153 | 54.3365 | -0.27008 | 54.4876 | -0.11902 | -0.050354 | -0.05951 | -0.045777 | 0.26093 | 0.11902 | -0.068665 | 0.16937 | -0.018311 | 4.2664 | 122.4426 | 0.31128 | 122.4335 | 122.5388 | 122.4197 | 122.3877 | 122.3694 | -122.58 | -122.4792 | 122.2916 | 122.3831 | 48.9441 | 44.5953
2104.8281 | 122.644 | -50.2716 | 72.1252 | -0.11742 | -0.00065152 | 0.062025 | 0.11911 | 0.0031617 | -0.0024994 | -0.002243 | -0.10406 | -0.0049732 | 0.065674 | 0.06404 | -0.027645 | 0.0016277 | 0.00032049 | -1.1536 | 72.1161 | -50.4181 | 72.0062 | -46.2296 | -50.5417 | 4.1107 | -5.3925 | 72.1161 | -50.3357 | 72.1207 | -49.9924 | -50.3311 | -50.1526 | -0.14648 | -0.009155 | -0.11902 | 4.0421 | 54.3823 | -0.27008 | 54.5288 | -0.1236 | -0.064087 | -0.009155 | -0.004577 | 0.27923 | 0.11902 | -0.05951 | 0.1831 | 0.004577 | 4.1885 | 122.4243 | 0.34332 | 122.4564 | 122.5342 | 122.4518 | 122.3877 | 122.3877 | -122.5433 | -122.4609 | 122.2778 | 122.3923 | 49.118 | 44.8791
2105.7656 | 122.5662 | -50.4318 | 72.0108 | -0.10216 | 0.00084388 | 0.063094 | 0.12188 | -0.0019653 | -0.0050628 | -0.0030976 | -0.058289 | -0.0015552 | 0.062042 | 0.059127 | -0.026577 | 0.0014141 | 0.00074769 | -1.2405 | 71.965 | -50.592 | 71.8277 | -46.4447 | -50.7431 | 3.9734 | -5.8411 | 71.9147 | -50.5234 | 71.9421 | -50.1938 | -50.528 | -50.3311 | -0.16022 | -0.045776 | -0.1831 | 3.9871 | 54.4052 | -0.31128 | 54.5654 | -0.15106 | -0.091552 | -0.09613 | -0.068664 | 0.23804 | 0.10071 | -0.09613 | 0.19226 | -0.004578 | 4.1473 | 122.4197 | 0.32959 | 122.4655 | 122.5571 | 122.438 | 122.3969 | 122.3465 | -122.6028 | -122.5342 | 122.2595 | 122.374 | 49.1913 | 44.5908
2106.8281 | 122.6303 | -50.2945 | 72.1527 | -0.041122 | -0.00022432 | 0.065657 | 0.11932 | 0.0020935 | -0.004422 | -0.0013886 | -0.070496 | -0.003905 | 0.06247 | 0.05934 | -0.026363 | 0.00013253 | 0.0013885 | -1.149 | 72.139 | -50.4089 | 72.0016 | -46.1655 | -50.5371 | 4.1702 | -5.5573 | 72.1069 | -50.3357 | 72.1298 | -50.0015 | -50.3357 | -50.1526 | -0.11444 | -0.013733 | -0.15106 | 4.129 | 54.4647 | -0.24261 | 54.5792 | -0.12817 | -0.041198 | -0.045776 | -0.022888 | 0.29297 | 0.14191 | -0.041198 | 0.1831 | 0 | 4.2435 | 122.4106 | 0.33417 | 122.4655 | 122.5479 | 122.4426 | 122.4335 | 122.4014 | -122.5616 | -122.4884 | 122.2961 | 122.4243 | 49.1455 | 44.7372
2107.7656 | 122.4792 | -50.1617 | 72.2763 | -0.094528 | -0.0030013 | 0.06288 | 0.12039 | -0.00025628 | -0.0035674 | -0.0033112 | -0.033874 | -0.002196 | 0.066742 | 0.060408 | -0.027431 | 0.00055973 | 0.0011749 | -1.2268 | 72.258 | -50.2899 | 72.084 | -45.9915 | -50.4868 | 4.0878 | -6.0379 | 72.2672 | -50.2304 | 72.2076 | -49.9329 | -50.3174 | -50.0702 | -0.12817 | -0.01831 | -0.19226 | 4.1702 | 54.2496 | -0.32501 | 54.3777 | -0.19684 | -0.068665 | -0.009155 | -0.068664 | 0.22888 | 0.091553 | -0.15564 | 0.16022 | -0.086975 | 4.2984 | 122.374 | 0.29755 | 122.4381 | 122.5479 | 122.4976 | 122.4197 | 122.4289 | -122.5662 | -122.5067 | 122.2458 | 122.3694 | 48.9349 | 44.1238
2108.8281 | 122.5891 | -50.3998 | 72.0062 | -0.094528 | -1.0718e-05 | 0.064162 | 0.1206 | 0.0040161 | -0.0029266 | -0.0026704 | -0.030823 | -0.0030506 | 0.06247 | 0.06169 | -0.026791 | 0.00098693 | 0.00096129 | -1.2909 | 71.8002 | -50.7614 | 71.7636 | -46.2799 | -50.7843 | 4.0878 | -5.9418 | 71.9513 | -50.4913 | 72.0016 | -50.116 | -50.4639 | -50.2762 | -0.36163 | -0.20599 | -0.24262 | 4.1199 | 54.4876 | -0.38452 | 54.8492 | -0.022888 | -0.091553 | -0.054932 | -0.004578 | 0.28381 | 0.1236 | -0.064087 | 0.21515 | 0.027466 | 4.4815 | 122.525 | 0.37537 | 122.493 | 122.5616 | 122.4426 | 122.2 | 122.3511 | -122.7676 | -122.4976 | 122.1634 | 122.4014 | 49.1089 | 44.458
2109.7656 | 122.5159 | -50.5188 | 71.9147 | -0.12505 | 0.0014847 | 0.062453 | 0.11804 | 0.0027343 | -0.0042084 | -0.0018158 | -0.055237 | -0.0028368 | 0.065247 | 0.056777 | -0.027431 | 0.0069683 | -0.0022431 | -1.2817 | 71.6217 | -50.9399 | 71.5942 | -46.4264 | -50.9949 | 4.0237 | -6.0059 | 71.8323 | -50.6058 | 71.5713 | -49.9969 | -50.3906 | -50.3403 | -0.42114 | -0.29297 | -0.32043 | 4.0924 | 54.5425 | -0.47607 | 54.9637 | -0.054932 | -0.086975 | -0.082398 | -0.34332 | 0.52185 | 0.17853 | 0.12817 | 0.2655 | 0.21515 | 4.5135 | 122.5342 | 0.60883 | 122.1771 | 122.5616 | 122.438 | 122.1405 | 122.3511 | -122.8546 | -122.5204 | 122.113 | 122.0901 | 49.2371 | 44.5129
2110.8281 | 122.6486 | -51.1871 | 71.1365 | -0.1403 | 0.0014847 | 0.061812 | 0.11868 | 0.0020935 | -0.0024994 | -0.0013886 | -0.0094604 | -0.0030506 | 0.060761 | 0.060408 | -0.028286 | 0.0020551 | 0.0033111 | -1.3779 | 71.1365 | -51.4023 | 71.0175 | -47.0398 | -51.5442 | 3.8269 | -5.9372 | 71.1182 | -51.2741 | 71.2738 | -50.8301 | -51.2283 | -51.0406 | -0.21515 | 0 | -0.11902 | 4.1473 | 55.014 | -0.35706 | 55.2292 | -0.14191 | -0.086975 | -0.018311 | 0.13733 | 0.35706 | 0.14648 | -0.041199 | 0.23346 | 0.045776 | 4.3625 | 122.4197 | 0.44403 | 122.5479 | 122.5388 | 122.3923 | 122.3236 | 122.3053 | -122.5388 | -122.4106 | 122.2046 | 122.4609 | 49.8093 | 45.2499
2111.7656 | 122.58 | -51.3062 | 71.0953 | -0.018234 | 0.0010575 | 0.064162 | 0.1206 | 0.0023071 | -0.0024994 | -0.0018158 | -0.067444 | -0.0013416 | 0.062042 | 0.060408 | -0.030422 | 0.00077333 | 0.0037385 | -1.3138 | 71.0999 | -51.4526 | 70.9854 | -46.9116 | -51.5625 | 3.9734 | -6.0104 | 71.2006 | -51.2375 | 71.1411 | -50.9995 | -51.3565 | -51.1871 | -0.14649 | 0.004578 | -0.10986 | 4.3945 | 55.2795 | -0.25635 | 55.426 | -0.10986 | 0.068664 | 0.10529 | 0.045776 | 0.3067 | 0.11902 | -0.050354 | 0.050354 | -0.11902 | 4.541 | 122.4381 | 0.23804 | 122.3785 | 122.5525 | 122.4381 | 122.406 | 122.5067 | -122.5479 | -122.3328 | 122.2916 | 122.4472 | 49.9924 | 45.2957
2112.8281 | 122.6166 | -50.6699 | 71.7361 | 0.050431 | 0.0012711 | 0.063307 | 0.11846 | -0.0036743 | -0.0042084 | -0.004593 | -0.046081 | -0.002196 | 0.065247 | 0.063613 | -0.027645 | 0.00055973 | 0.0035247 | -1.2497 | 71.6904 | -50.8575 | 71.5851 | -46.3989 | -50.9674 | 4.3076 | -5.9372 | 71.64 | -50.7797 | 71.7041 | -50.4135 | -50.7614 | -50.5554 | -0.18768 | -0.045776 | -0.15106 | 4.2709 | 54.9774 | -0.29755 | 55.1651 | -0.10986 | -0.10986 | -0.09613 | -0.032043 | 0.25635 | 0.11444 | -0.091553 | 0.2243 | 0.01831 | 4.4586 | 122.4426 | 0.36621 | 122.4838 | 122.5479 | 122.4197 | 122.3602 | 122.3099 | -122.5937 | -122.5159 | 122.2549 | 122.374 | 49.4202 | 44.7327
2113.7656 | 122.5845 | -50.9354 | 71.4981 | -0.11742 | 0.0012711 | 0.064803 | 0.12146 | 0.0018799 | -0.0063446 | -0.0013886 | -0.027771 | -0.0026232 | 0.062897 | 0.062331 | -0.027431 | 0.0016277 | -0.00053411 | -1.3504 | 71.553 | -51.0315 | 71.5164 | -46.8842 | -51.3474 | 4.1336 | -6.1844 | 71.4706 | -51.0269 | 71.402 | -50.7202 | -51.0681 | -50.8072 | -0.09613 | 0.054932 | 0.01831 | 4.0512 | 55.069 | -0.41199 | 55.1651 | -0.31586 | -0.091553 | -0.027466 | -0.09613 | 0.21515 | 0.12817 | -0.13275 | 0.21973 | -0.041198 | 4.1473 | 122.5479 | 0.3067 | 122.4289 | 122.5845 | 122.4976 | 122.4884 | 122.406 | -122.5296 | -122.525 | 122.4518 | 122.3373 | 49.585 | 44.751
2114.8281 | 122.58 | -50.647 | 71.8277 | -0.094528 | -0.00043792 | 0.064589 | 0.12146 | 0.00038452 | -0.0039948 | -0.0050202 | -0.04303 | -0.001128 | 0.063324 | 0.058272 | -0.027218 | 0.00055973 | 0.0026703 | -1.4511 | 71.7133 | -50.8072 | 71.608 | -46.5775 | -51.004 | 4.2847 | -6.134 | 71.727 | -50.6973 | 71.7133 | -50.4089 | -50.7568 | -50.5325 | -0.16022 | -0.11444 | -0.21973 | 4.0695 | 54.9316 | -0.35705 | 55.0919 | -0.19684 | -0.050354 | -0.10071 | -0.11444 | 0.23804 | 0.11444 | -0.10986 | 0.16479 | -0.059509 | 4.2297 | 122.4152 | 0.28839 | 122.4106 | 122.5204 | 122.4243 | 122.3602 | 122.374 | -122.6349 | -122.525 | 122.2549 | 122.3602 | 49.1959 | 44.5129
2115.7656 | 122.5525 | -50.8026 | 71.6217 | -0.13267 | 0.0025529 | 0.06288 | 0.12146 | 0.0020935 | -0.0024994 | -0.0020294 | -0.049133 | -0.0045458 | 0.065247 | 0.059767 | -0.027645 | 0.0016277 | 0.00053409 | -1.236 | 71.5485 | -51.0223 | 71.3745 | -46.669 | -51.178 | 4.3625 | -6.0242 | 71.553 | -50.9171 | 71.5256 | -50.5692 | -50.9399 | -50.7111 | -0.21973 | -0.073242 | -0.24719 | 4.1336 | 55.1651 | -0.37537 | 55.3848 | -0.15564 | -0.11444 | -0.068664 | -0.09613 | 0.23346 | 0.091552 | -0.13733 | 0.20599 | -0.022888 | 4.3533 | 122.3969 | 0.3479 | 122.4426 | 122.5708 | 122.4701 | 122.3511 | 122.3557 | -122.644 | -122.5388 | 122.1771 | 122.3282 | 49.5667 | 44.7784
2116.8281 | 122.5983 | -51.0269 | 71.3882 | -0.12505 | 0.0021255 | 0.062025 | 0.11953 | -0.0017517 | -0.0037812 | -0.0048066 | -0.058289 | -0.0024096 | 0.063111 | 0.060408 | -0.027859 | 0.0018413 | 0.0026703 | -1.2222 | 71.2555 | -51.2604 | 71.1273 | -46.9025 | -51.4069 | 4.4632 | -6.0516 | 71.3104 | -51.1368 | 71.3013 | -50.8209 | -51.1597 | -50.9399 | -0.23346 | -0.13275 | -0.26093 | 4.1245 | 55.4901 | -0.37994 | 55.7236 | -0.14648 | -0.10986 | -0.07782 | -0.086975 | 0.20599 | 0.086976 | -0.13275 | 0.19684 | -0.022888 | 4.3579 | 122.3877 | 0.31586 | 122.4381 | 122.5159 | 122.4472 | 122.2824 | 122.3373 | -122.6486 | -122.525 | 122.1542 | 122.3282 | 49.8047 | 44.9753
2117.7656 | 122.6074 | -51.2192 | 71.2051 | -0.07164 | 0.0014847 | 0.060957 | 0.1206 | 0.0038025 | -0.0042084 | -0.001175 | -0.049133 | -0.0034778 | 0.060974 | 0.05934 | -0.028713 | -0.0015765 | -0.0018157 | -1.2039 | 71.0632 | -51.4801 | 71.0266 | -47.1039 | -51.535 | 4.4449 | -6.0745 | 71.1044 | -51.3245 | 71.1502 | -50.9399 | -51.3016 | -51.0956 | -0.26093 | -0.14191 | -0.17853 | 4.1153 | 55.6641 | -0.31586 | 55.925 | -0.054931 | -0.10529 | -0.10071 | -0.054931 | 0.27924 | 0.1236 | -0.082398 | 0.22888 | 0.022888 | 4.3762 | 122.5067 | 0.38452 | 122.4747 | 122.5433 | 122.4289 | 122.2824 | 122.3236 | -122.6852 | -122.5296 | 122.2458 | 122.3694 | 50.0153 | 45.1447
2118.8281 | 122.7448 | -51.0132 | 71.3608 | -0.086899 | -0.0032151 | 0.060957 | 0.11846 | -0.00089728 | -0.0052764 | 0.00053404 | 0.069885 | -0.0036914 | 0.064392 | 0.052718 | -0.030422 | -0.0032855 | -0.0020295 | -1.1581 | 71.3837 | -51.1002 | 71.3654 | -46.7926 | -51.1551 | 4.6097 | -5.8548 | 71.3516 | -51.0269 | 71.5988 | -50.7339 | -51.2695 | -51.0361 | -0.086975 | 0.022888 | 0.004577 | 4.2206 | 55.6229 | -0.14191 | 55.7098 | -0.054931 | -0.013733 | -0.009155 | 0.23804 | 0.27924 | -0.022888 | -0.25635 | -0.009155 | -0.24261 | 4.3076 | 122.4655 | 0.29297 | 122.6257 | 122.4838 | 122.3785 | 122.3969 | 122.3648 | -122.4609 | -122.3877 | 122.3785 | 122.612 | 49.855 | 45.1584
2119.7656 | 122.5616 | -50.6516 | 71.7819 | -0.12505 | 0.0021255 | 0.060103 | 0.12188 | -0.00068368 | -0.0052764 | -0.0020294 | -0.058289 | -0.0017688 | 0.063965 | 0.058913 | -0.028927 | 0.0031231 | 0.0026703 | -1.2268 | 71.7865 | -50.7751 | 71.6309 | -46.5134 | -50.9445 | 4.5776 | -5.9967 | 71.7636 | -50.679 | 71.6995 | -50.4135 | -50.7797 | -50.5508 | -0.1236 | 0.004578 | -0.15106 | 4.1382 | 55.2292 | -0.29297 | 55.3528 | -0.16937 | -0.027466 | -0.01831 | -0.082397 | 0.23804 | 0.10071 | -0.12817 | 0.12817 | -0.10071 | 4.2618 | 122.406 | 0.2655 | 122.3785 | 122.5616 | 122.4426 | 122.438 | 122.4152 | -122.5571 | -122.4609 | 122.2824 | 122.3511 | 49.4247 | 44.6548
2120.8281 | 122.5525 | -51.1688 | 71.283 | -0.094528 | 0.0014847 | 0.062025 | 0.11804 | 0.00059812 | -0.0018586 | -0.00096136 | -0.049133 | -0.0026232 | 0.063965 | 0.065322 | -0.025936 | 0.0012005 | -0.0016021 | -1.268 | 71.2509 | -51.3016 | 71.0541 | -47.0856 | -51.5121 | 4.3625 | -6.2805 | 71.2234 | -51.2421 | 71.196 | -50.7065 | -51.4069 | -51.178 | -0.13275 | -0.032043 | -0.22888 | 4.0833 | 55.5313 | -0.34332 | 55.6641 | -0.21057 | -0.073242 | -0.059509 | -0.086975 | 0.46234 | -0.009156 | -0.23804 | 0.064086 | -0.1648 | 4.216 | 122.3557 | 0.53558 | 122.438 | 122.5525 | 122.4655 | 122.4197 | 122.3923 | -122.5845 | -122.525 | 122.2229 | 122.3648 | 49.9008 | 44.8883
2121.7656 | 122.5891 | -50.6882 | 71.7499 | -0.10216 | 0.0012711 | 0.063734 | 0.11911 | 0.0025207 | -0.0020722 | -0.0018158 | -0.055237 | -0.0024096 | 0.063538 | 0.063185 | -0.0285 | 0.0014141 | 0.0030975 | -1.2039 | 71.6904 | -50.8621 | 71.5897 | -46.6919 | -50.972 | 4.6188 | -6.0974 | 71.7087 | -50.7477 | 71.6904 | -50.4227 | -50.7751 | -50.5783 | -0.17395 | -0.059509 | -0.16022 | 3.9963 | 55.307 | -0.28381 | 55.481 | -0.10986 | -0.05951 | -0.041199 | -0.059509 | 0.2655 | 0.10986 | -0.086975 | 0.16937 | -0.027465 | 4.1702 | 122.4518 | 0.32501 | 122.4381 | 122.5525 | 122.4564 | 122.3785 | 122.3969 | -122.612 | -122.4976 | 122.2778 | 122.3785 | 49.4843 | 44.5908
2122.8281 | 122.5891 | -50.8759 | 71.553 | -0.094528 | 0.00084388 | 0.063734 | 0.11996 | 0.0050843 | -0.0063446 | -0.0035248 | -0.076599 | -0.0019824 | 0.061829 | 0.058058 | -0.030209 | 0.00055973 | 0.00074769 | -1.2405 | 71.5622 | -50.9811 | 71.4386 | -46.6278 | -51.1368 | 4.4861 | -6.2119 | 71.5942 | -50.8896 | 71.489 | -50.6332 | -50.9903 | -50.7797 | -0.10529 | 0.009155 | -0.11444 | 4.248 | 55.3619 | -0.26093 | 55.4672 | -0.15564 | -0.013733 | 0.041198 | -0.064087 | 0.24261 | 0.09613 | -0.11444 | 0.10986 | -0.10071 | 4.3533 | 122.4197 | 0.25635 | 122.3785 | 122.5433 | 122.4838 | 122.438 | 122.4701 | -122.5342 | -122.4426 | 122.3145 | 122.3648 | 49.6353 | 44.664
2123.7656 | 122.58 | -50.9491 | 71.5073 | -0.12505 | -0.00065152 | 0.065016 | 0.11911 | 0.00017092 | -0.0037812 | -0.0035248 | -0.055237 | -0.0017688 | 0.061615 | 0.062972 | -0.02615 | 0.00077333 | 0.00010689 | -1.2131 | 71.5439 | -50.9766 | 71.3974 | -46.788 | -51.2375 | 4.454 | -6.1386 | 71.4203 | -51.0361 | 71.3699 | -50.7111 | -51.0773 | -50.8438 | -0.027465 | 0.036621 | -0.10986 | 4.1611 | 55.4031 | -0.28839 | 55.4306 | -0.26093 | -0.086975 | -0.086975 | -0.13733 | 0.23804 | 0.10529 | -0.12817 | 0.19226 | -0.041199 | 4.1885 | 122.374 | 0.32501 | 122.406 | 122.5204 | 122.4564 | 122.493 | 122.3694 | -122.4838 | -122.5433 | 122.3465 | 122.319 | 49.736 | 44.8105
2124.8281 | 122.7127 | -50.7431 | 71.6263 | -0.12505 | -0.00043792 | 0.063521 | 0.11676 | 0.0023071 | 0.0002778 | -0.0018158 | -0.024719 | -0.0034778 | 0.062683 | 0.060195 | -0.028713 | 0.0033367 | 0.0054475 | -1.0941 | 71.4661 | -51.0086 | 71.5851 | -46.4264 | -50.9537 | 4.7699 | -6.015 | 71.5393 | -50.8347 | 71.6766 | -50.2396 | -50.7889 | -50.5783 | -0.2655 | -0.16022 | -0.041199 | 4.3167 | 55.513 | -0.21057 | 55.7785 | 0.054932 | -0.091553 | -0.086975 | 0.050354 | 0.50354 | 0.16479 | -0.045776 | 0.25635 | 0.045777 | 4.5822 | 122.5937 | 0.59509 | 122.5113 | 122.4747 | 122.374 | 122.2092 | 122.2824 | -122.6349 | -122.4609 | 122.3282 | 122.4197 | 49.649 | 44.7281
2125.7656 | 122.6303 | -51.178 | 71.2418 | -0.048752 | -0.0010787 | 0.060957 | 0.12124 | 0.0050843 | -0.0035674 | -0.0016022 | -0.021667 | -0.0030506 | 0.064179 | 0.058486 | -0.030636 | 0.0022687 | -0.00096131 | -1.1627 | 71.228 | -51.3199 | 71.1044 | -46.9849 | -51.4526 | 4.4632 | -6.1707 | 71.1227 | -51.3153 | 71.1823 | -50.7065 | -51.2421 | -51.0406 | -0.14191 | -0.013733 | -0.13733 | 4.1931 | 55.6412 | -0.27466 | 55.7831 | -0.13275 | -0.13733 | -0.11902 | -0.059509 | 0.4715 | 0.13733 | -0.064086 | 0.27466 | 0.073243 | 4.335 | 122.4243 | 0.60883 | 122.4976 | 122.5479 | 122.4381 | 122.406 | 122.3007 | -122.5616 | -122.5571 | 122.2824 | 122.3602 | 50.0153 | 45.0073
2126.8281 | 122.612 | -50.9491 | 71.4798 | -0.086899 | -0.0015061 | 0.061812 | 0.12124 | 0.0042297 | -0.0003632 | -0.0043792 | -0.049133 | -0.0047594 | 0.063965 | 0.061904 | -0.028286 | 0.0029095 | 0.0020295 | -1.2405 | 71.4798 | -51.0864 | 71.3287 | -46.8613 | -51.2604 | 4.4266 | -6.0471 | 71.4432 | -51.0132 | 71.4569 | -50.6836 | -51.0315 | -50.8484 | -0.13733 | 0 | -0.15106 | 4.0878 | 55.3757 | -0.31128 | 55.513 | -0.17395 | -0.064087 | -0.036621 | -0.022888 | 0.2655 | 0.10071 | -0.082397 | 0.1648 | -0.01831 | 4.2252 | 122.4152 | 0.32959 | 122.4701 | 122.5662 | 122.4564 | 122.4289 | 122.3923 | -122.5662 | -122.493 | 122.2778 | 122.406 | 49.7086 | 44.902
2127.7656 | 122.6074 | -50.6424 | 71.7545 | -0.07164 | 0.00084388 | 0.063521 | 0.11975 | -0.0030335 | -0.002713 | -0.0024566 | -0.052185 | -0.0034778 | 0.063538 | 0.057418 | -0.027431 | 0.0022687 | -0.0024567 | -1.1856 | 71.7178 | -50.8484 | 71.64 | -46.6095 | -50.8942 | 4.6692 | -5.9326 | 71.727 | -50.6973 | 71.7361 | -50.354 | -50.7019 | -50.5096 | -0.20599 | -0.036622 | -0.11444 | 4.0329 | 55.3116 | -0.25177 | 55.5176 | -0.045776 | -0.054932 | -0.027466 | -0.018311 | 0.28839 | 0.13275 | -0.059509 | 0.18768 | -0.004577 | 4.2389 | 122.4884 | 0.34332 | 122.4335 | 122.5662 | 122.4243 | 122.3602 | 122.3694 | -122.6028 | -122.4518 | 122.2824 | 122.3785 | 49.4568 | 44.7098
2128.8281 | 122.5845 | -50.7385 | 71.7133 | -0.079269 | 0.0010575 | 0.059889 | 0.11911 | -0.00089728 | -0.0039948 | -0.0041656 | 0.0057984 | -0.0036914 | 0.066101 | 0.06404 | -0.029568 | 0.00013253 | 0.00032049 | -1.1993 | 71.6812 | -50.9079 | 71.5073 | -46.7697 | -51.0315 | 4.6051 | -6.1752 | 71.6263 | -50.7751 | 71.6171 | -50.4364 | -50.8255 | -50.6378 | -0.16937 | -0.032044 | -0.20599 | 3.9688 | 55.3436 | -0.29297 | 55.513 | -0.1236 | -0.036621 | -0.086975 | -0.096131 | 0.30212 | 0.10071 | -0.086975 | 0.13733 | -0.050354 | 4.1382 | 122.4152 | 0.33875 | 122.3923 | 122.5891 | 122.4014 | 122.4197 | 122.3648 | -122.6212 | -122.4884 | 122.2458 | 122.3557 | 49.5392 | 44.5633
2129.7656 | 122.5525 | -51.6861 | 70.7748 | -0.13267 | 0.00063028 | 0.061598 | 0.12188 | 0.0018799 | -0.0016448 | -0.002884 | -0.079651 | -0.0030506 | 0.063111 | 0.06404 | -0.027431 | 0.0035503 | 0.0018159 | -1.3687 | 70.7428 | -51.8463 | 70.6192 | -47.5388 | -51.9333 | 4.2892 | -7.0496 | 70.752 | -51.7181 | 70.6375 | -51.4389 | -51.8143 | -51.5808 | -0.16022 | -0.032043 | -0.15564 | 4.1473 | 55.9753 | -0.24719 | 56.1356 | -0.086976 | -0.032044 | -0.022888 | -0.13733 | 0.24719 | 0.10529 | -0.12817 | 0.13733 | -0.09613 | 4.3076 | 122.4655 | 0.27924 | 122.3557 | 122.5891 | 122.4701 | 122.4289 | 122.438 | -122.6212 | -122.493 | 122.3053 | 122.3236 | 50.3174 | 44.6365
2130.8281 | 122.612 | -51.123 | 71.3104 | -0.1403 | -1.0718e-05 | 0.062666 | 0.11911 | -0.0015381 | -0.0033538 | -0.0024566 | -0.06134 | -0.0017688 | 0.063538 | 0.063399 | -0.027859 | 0.0012005 | 0.0028839 | -1.2405 | 71.347 | -51.21 | 71.2006 | -47.0215 | -51.4069 | 4.422 | -6.8069 | 71.2646 | -51.178 | 71.2509 | -50.8163 | -51.1917 | -50.9903 | -0.086975 | 0.036621 | -0.10986 | 4.1016 | 55.545 | -0.28381 | 55.632 | -0.19684 | -0.054932 | -0.045777 | -0.059509 | 0.3067 | 0.13275 | -0.068664 | 0.18768 | -0.013732 | 4.1885 | 122.4106 | 0.36163 | 122.4289 | 122.5571 | 122.4426 | 122.4701 | 122.3877 | -122.5204 | -122.4884 | 122.3236 | 122.374 | 49.8825 | 44.3161
2131.7656 | 122.6028 | -50.8301 | 71.608 | -0.048752 | 0.0023391 | 0.061812 | 0.11761 | -0.0015381 | -0.0035674 | -0.002243 | -0.064392 | -0.0028368 | 0.063111 | 0.062117 | -0.028286 | 0.0014141 | 0.0028839 | -1.1719 | 71.5485 | -51.004 | 71.5073 | -46.6324 | -51.1047 | 4.715 | -6.7612 | 71.5668 | -50.9125 | 71.5851 | -50.5005 | -50.885 | -50.7156 | -0.17395 | -0.059509 | -0.10071 | 4.1977 | 55.545 | -0.27466 | 55.719 | -0.10071 | -0.082398 | -0.041199 | -0.022888 | 0.32959 | 0.11444 | -0.054932 | 0.19684 | 0.027466 | 4.3716 | 122.5113 | 0.41199 | 122.4976 | 122.5525 | 122.4792 | 122.3785 | 122.3969 | -122.612 | -122.5204 | 122.3373 | 122.4152 | 49.6582 | 44.0689
2132.8281 | 122.6028 | -50.647 | 71.7773 | -0.07164 | 0.0010575 | 0.06288 | 0.1174 | 0.0044433 | -0.0035674 | -0.0016022 | -0.055237 | -0.0024096 | 0.063324 | 0.067031 | -0.02914 | 0.0016277 | 0.0026703 | -1.2131 | 71.759 | -50.7889 | 71.6629 | -46.5225 | -50.9033 | 4.6143 | -6.9122 | 71.7865 | -50.6836 | 71.7682 | -50.3174 | -50.6927 | -50.5051 | -0.14191 | -0.018311 | -0.11444 | 4.1245 | 55.2612 | -0.25635 | 55.4031 | -0.11444 | -0.036621 | 0.009155 | -0.009156 | 0.32959 | 0.14191 | -0.045776 | 0.17853 | -0.009155 | 4.2664 | 122.4518 | 0.36621 | 122.4518 | 122.5479 | 122.4701 | 122.406 | 122.4335 | -122.5662 | -122.4609 | 122.3099 | 122.4152 | 49.4339 | 43.7347
2133.7656 | 122.612 | -50.2579 | 72.1664 | 0.1191 | -0.0023605 | 0.063094 | 0.11953 | 0.0044433 | -0.001004 | -0.00074776 | -0.052185 | -0.0034778 | 0.064179 | 0.065749 | -0.0285 | 0.0020551 | -0.00074771 | -1.2314 | 72.1252 | -50.4227 | 71.9833 | -46.2479 | -50.592 | 4.715 | -6.7749 | 72.0932 | -50.3174 | 72.1024 | -49.9969 | -50.3632 | -50.1389 | -0.16479 | -0.041199 | -0.18311 | 4.01 | 54.9728 | -0.33417 | 55.1376 | -0.16937 | -0.059509 | -0.073242 | -0.064087 | 0.26093 | 0.11902 | -0.10529 | 0.17853 | -0.045776 | 4.1748 | 122.406 | 0.32043 | 122.4197 | 122.5479 | 122.4106 | 122.3831 | 122.3511 | -122.5891 | -122.4838 | 122.2412 | 122.3602 | 49.0265 | 43.483
2134.8281 | 122.5891 | -50.0427 | 72.4182 | -0.086899 | -0.00022432 | 0.061385 | 0.11825 | 0.0010253 | -0.0052764 | -0.001175 | -0.015564 | -0.0049732 | 0.06482 | 0.055068 | -0.027645 | -0.00072207 | 0.00053409 | -1.1765 | 72.3907 | -50.1846 | 72.2031 | -46.0007 | -50.3494 | 4.7745 | -6.5598 | 72.3679 | -50.0931 | 72.3404 | -49.7314 | -50.0931 | -49.9191 | -0.14191 | -0.027466 | -0.21515 | 4.0421 | 54.8172 | -0.3067 | 54.9591 | -0.16479 | -0.050354 | -0.050354 | -0.07782 | 0.31128 | 0.1236 | -0.050354 | 0.17395 | 0 | 4.184 | 122.3877 | 0.36163 | 122.4335 | 122.5754 | 122.4609 | 122.4335 | 122.4106 | -122.6028 | -122.5113 | 122.2458 | 122.3831 | 48.8663 | 43.483
2135.7656 | 122.6028 | -50.0427 | 72.3724 | -0.086899 | -0.00022432 | 0.06288 | 0.11911 | 0.00081172 | 0.0004914 | -0.0041656 | -0.033874 | -0.0017688 | 0.064179 | 0.065535 | -0.029781 | 0.0022687 | -0.0028839 | -1.1307 | 72.3999 | -50.1297 | 72.1848 | -45.7809 | -50.2075 | 4.9301 | -6.3538 | 72.3587 | -50.0702 | 72.3541 | -49.7406 | -50.0885 | -49.9237 | -0.086975 | 0.027465 | -0.18768 | 4.2618 | 54.9728 | -0.1648 | 55.0598 | -0.07782 | -0.027465 | -0.013733 | -0.018311 | 0.30212 | 0.11902 | -0.045776 | 0.14648 | -0.018311 | 4.3488 | 122.3145 | 0.32959 | 122.4243 | 122.5296 | 122.4289 | 122.4426 | 122.4014 | -122.5021 | -122.4426 | 122.2275 | 122.3969 | 48.912 | 43.689
2136.8281 | 122.58 | -49.7864 | 72.6151 | -0.07164 | 0.0016983 | 0.064375 | 0.1206 | 0.0018799 | -0.0018586 | -0.0013886 | -0.046081 | -0.0024096 | 0.063965 | 0.057204 | -0.027218 | 0.0031231 | 0.00032049 | -1.1215 | 72.6013 | -49.9741 | 72.4091 | -45.7443 | -50.1938 | 4.7104 | -6.2439 | 72.583 | -49.8917 | 72.4045 | -49.823 | -49.6124 | -49.5026 | -0.18768 | -0.013733 | -0.20599 | 4.0421 | 54.4968 | -0.40741 | 54.6844 | -0.21973 | -0.10529 | -0.032043 | -0.21057 | -0.036621 | 0.28381 | 0.17395 | 0.3891 | 0.27924 | 4.2297 | 122.3831 | 0.068665 | 122.2961 | 122.5754 | 122.4747 | 122.3877 | 122.3694 | -122.5891 | -122.5067 | 122.1954 | 122.1909 | 48.6649 | 43.5425
2137.7656 | 122.5479 | -50.061 | 72.3679 | -0.39207 | 0.0029801 | 0.059248 | 0.11761 | 0.0018799 | -0.0035674 | -0.00032036 | -0.06134 | -0.0013416 | 0.062897 | 0.057631 | -0.02615 | 0.00013253 | 0.0052337 | -1.0117 | 72.3267 | -50.2304 | 72.1481 | -45.9549 | -50.354 | 4.7012 | -6.4682 | 72.3404 | -50.1297 | 72.3129 | -49.823 | -50.1755 | -49.9695 | -0.16937 | -0.041199 | -0.21973 | 4.1061 | 54.7623 | -0.29297 | 54.9316 | -0.1236 | -0.068665 | -0.027466 | -0.054932 | 0.23804 | 0.091553 | -0.11444 | 0.16022 | -0.045776 | 4.2755 | 122.3785 | 0.3067 | 122.4426 | 122.5571 | 122.4701 | 122.3877 | 122.4014 | -122.5983 | -122.4976 | 122.2092 | 122.374 | 49.0494 | 43.5928
2138.8281 | 122.6807 | -49.6445 | 72.6883 | -0.17845 | 0.0014847 | 0.060957 | 0.11846 | -0.0013245 | -0.0033538 | -0.0018158 | -0.015564 | -0.0049732 | 0.059906 | 0.056777 | -0.029354 | -0.00050847 | 0.0020295 | -1.0803 | 72.6608 | -49.8001 | 72.6471 | -45.4239 | -49.9054 | 4.5044 | -6.0516 | 72.6425 | -49.7314 | 72.8027 | -49.2828 | -49.649 | -49.4751 | -0.15564 | -0.027465 | -0.041198 | 4.2206 | 54.1489 | -0.26093 | 54.3045 | -0.10529 | -0.086975 | -0.045776 | 0.11444 | 0.36163 | 0.16937 | -0.004578 | 0.25635 | 0.082397 | 4.3762 | 122.4472 | 0.44861 | 122.5342 | 122.4609 | 122.374 | 122.3053 | 122.287 | -122.4884 | -122.4197 | 122.2916 | 122.4472 | 48.5641 | 43.5928
2139.7656 | 122.6303 | -49.855 | 72.5647 | -0.12505 | -0.00022432 | 0.066512 | 0.11953 | -0.0030335 | -0.0020722 | -0.002884 | -0.055237 | -0.0032642 | 0.062256 | 0.05934 | -0.027218 | -0.0011493 | 0.0026703 | -1.1765 | 72.5281 | -50.0015 | 72.464 | -45.7626 | -50.116 | 4.7607 | -6.5689 | 72.5143 | -49.91 | 72.5327 | -49.5483 | -49.9237 | -49.7269 | -0.14648 | -0.036621 | -0.10071 | 4.0924 | 54.6158 | -0.26093 | 54.7623 | -0.11444 | -0.054931 | -0.050354 | -0.032043 | 0.3067 | 0.12817 | -0.068664 | 0.1831 | -0.013733 | 4.2389 | 122.4655 | 0.36163 | 122.4426 | 122.5296 | 122.4243 | 122.3831 | 122.3694 | -122.5662 | -122.4747 | 122.319 | 122.3877 | 48.6786 | 43.2861
2140.8281 | 122.6028 | -50.0839 | 72.3358 | -0.11742 | -0.0012923 | 0.062666 | 0.12103 | 0.0020935 | -0.0016448 | -0.004593 | -0.04303 | -0.0030506 | 0.063751 | 0.055709 | -0.026791 | 0.0020551 | 0.0024567 | -1.1856 | 72.3495 | -50.2167 | 72.1573 | -46.138 | -50.3998 | 4.7241 | -6.6422 | 72.2992 | -50.148 | 72.2855 | -49.8138 | -50.1984 | -49.9695 | -0.13275 | 0.013733 | -0.17853 | 3.9459 | 54.808 | -0.31586 | 54.9408 | -0.1831 | -0.064087 | -0.036621 | -0.050354 | 0.27008 | 0.11444 | -0.11444 | 0.17853 | -0.050354 | 4.0787 | 122.374 | 0.33417 | 122.4335 | 122.5662 | 122.4472 | 122.4335 | 122.3831 | -122.5525 | -122.4838 | 122.2412 | 122.3694 | 48.8983 | 43.4418
2141.7656 | 122.58 | -49.8138 | 72.6151 | -0.086899 | -0.0015061 | 0.063094 | 0.12188 | 0.0027343 | -0.0007904 | -0.00074776 | -0.070496 | -0.00091423 | 0.064606 | 0.063185 | -0.02914 | 0.0016277 | 0.0024567 | -1.1398 | 72.6654 | -49.9008 | 72.4869 | -45.6573 | -50.0931 | 4.8248 | -6.6422 | 72.6288 | -49.8413 | 72.5418 | -49.5621 | -49.942 | -49.7406 | -0.086975 | 0.050354 | -0.12817 | 4.1565 | 54.6387 | -0.27924 | 54.7256 | -0.19226 | -0.027466 | 0.013733 | -0.073242 | 0.25177 | 0.073242 | -0.12817 | 0.10071 | -0.10071 | 4.2435 | 122.3877 | 0.27924 | 122.3831 | 122.5662 | 122.4701 | 122.4792 | 122.4426 | -122.5159 | -122.4564 | 122.3007 | 122.3557 | 48.674 | 43.1717
2142.8281 | 122.5754 | -49.7452 | 72.6837 | -0.10216 | 0.00063028 | 0.062025 | 0.11825 | 0.00059812 | -0.0031402 | -0.0016022 | -0.052185 | -0.0028368 | 0.061615 | 0.059767 | -0.027431 | -0.00029487 | 0.0020295 | -1.181 | 72.702 | -49.8688 | 72.5327 | -45.6436 | -50.0702 | 4.834 | -6.6193 | 72.6929 | -49.791 | 72.6105 | -49.4934 | -49.8917 | -49.6536 | -0.1236 | 0.01831 | -0.15106 | 4.1016 | 54.5792 | -0.32501 | 54.7028 | -0.20142 | -0.045777 | 0.009155 | -0.073242 | 0.25177 | 0.091553 | -0.14648 | 0.13733 | -0.10071 | 4.2252 | 122.4014 | 0.29755 | 122.4014 | 122.5708 | 122.4838 | 122.4472 | 122.438 | -122.5525 | -122.4747 | 122.2778 | 122.3557 | 48.5641 | 43.1259
2143.7656 | 122.5616 | -49.6353 | 72.821 | -0.10216 | 0.0010575 | 0.062239 | 0.1206 | -0.0015381 | -0.0037812 | -0.0018158 | -0.082703 | -0.0026232 | 0.061402 | 0.062331 | -0.027431 | 0.00077333 | 0.0011749 | -1.1124 | 72.7661 | -49.8001 | 72.6242 | -45.5338 | -49.9695 | 4.9164 | -6.7245 | 72.7478 | -49.6857 | 72.7203 | -49.3744 | -49.736 | -49.5346 | -0.16479 | -0.054932 | -0.19684 | 4.1016 | 54.5517 | -0.33417 | 54.7165 | -0.16937 | -0.050354 | -0.073242 | -0.10071 | 0.26093 | 0.10071 | -0.10071 | 0.15106 | -0.050354 | 4.2664 | 122.4243 | 0.31128 | 122.406 | 122.5662 | 122.4335 | 122.4014 | 122.3831 | -122.6212 | -122.5067 | 122.2595 | 122.3557 | 48.5229 | 42.9108
2144.8281 | 122.6807 | -49.7406 | 72.6196 | -0.10979 | 0.00063028 | 0.062453 | 0.12017 | -0.00068368 | -0.0046356 | -0.00010676 | -0.036926 | -0.0015552 | 0.062897 | 0.06639 | -0.028072 | 0.0016277 | -0.00010671 | -1.1444 | 72.67 | -49.9146 | 72.4869 | -45.726 | -50.0885 | 4.921 | -6.6788 | 72.6013 | -49.8276 | 72.67 | -49.411 | -49.7818 | -49.5804 | -0.17395 | 0.050354 | -0.13275 | 4.0146 | 54.6616 | -0.3479 | 54.8355 | -0.17395 | -0.086975 | -0.018311 | 0.050354 | 0.32959 | 0.16022 | -0.041198 | 0.24719 | 0.045777 | 4.1885 | 122.4014 | 0.41656 | 122.4976 | 122.5845 | 122.4289 | 122.4106 | 122.3419 | -122.5342 | -122.4472 | 122.2275 | 122.4106 | 48.5962 | 43.0618
2145.7656 | 122.4564 | -49.6765 | 72.7615 | -0.17845 | -0.00086512 | 0.061812 | 0.12146 | -0.00046988 | -0.0035674 | -0.00032036 | -0.067444 | -0.0034778 | 0.062256 | 0.066176 | -0.029781 | 0.0014141 | -0.00032051 | -1.1124 | 72.757 | -49.8184 | 72.5693 | -45.6207 | -49.9786 | 4.715 | -6.7291 | 72.7478 | -49.7314 | 72.6883 | -49.3973 | -49.791 | -49.7269 | -0.14191 | -0.004578 | -0.19226 | 4.0558 | 54.3915 | -0.30212 | 54.5334 | -0.16022 | -0.054931 | -0.013733 | -0.073243 | 0.27924 | -0.050354 | -0.11444 | 0.004577 | -0.05951 | 4.1977 | 122.3877 | 0.33417 | 122.4197 | 122.5754 | 122.4792 | 122.4335 | 122.4243 | -122.58 | -122.493 | 122.2458 | 122.3648 | 48.5641 | 42.9474
2146.8281 | 122.6761 | -49.4705 | 72.876 | -0.14793 | 0.0010575 | 0.064803 | 0.11825 | -4.2682e-05 | -0.0022858 | -0.00096136 | -0.015564 | -0.0041186 | 0.059906 | 0.061049 | -0.029354 | -0.00072207 | 0.0020295 | -0.95673 | 72.8348 | -49.617 | 72.8348 | -45.2179 | -49.6994 | 4.8706 | -6.6284 | 72.8531 | -49.5255 | 72.9584 | -49.1089 | -49.4934 | -49.292 | -0.14648 | -0.041199 | -0.041199 | 4.2526 | 54.3411 | -0.22888 | 54.4876 | -0.082398 | -0.054932 | -0.022889 | 0.082397 | 0.36163 | 0.17853 | -0.022888 | 0.23346 | 0.032044 | 4.3991 | 122.4518 | 0.41656 | 122.4838 | 122.4518 | 122.3785 | 122.3053 | 122.3236 | -122.493 | -122.4014 | 122.3053 | 122.4289 | 48.5138 | 42.8421
2147.7656 | 122.6852 | -49.2783 | 73.0865 | -0.14793 | -0.00086512 | 0.062025 | 0.11932 | -0.00068368 | -0.0050628 | -0.0018158 | -0.049133 | -0.0058276 | 0.063324 | 0.054854 | -0.027645 | 0.00098693 | -0.00096131 | -0.96588 | 73.1003 | -49.4659 | 72.9813 | -45.2042 | -49.5895 | 4.9484 | -6.7383 | 73.0728 | -49.3423 | 73.1552 | -48.9395 | -49.3057 | -49.1226 | -0.18768 | 0.013733 | -0.10529 | 4.0741 | 54.2267 | -0.31128 | 54.4144 | -0.1236 | -0.064087 | -0.013733 | 0.068664 | 0.33874 | 0.15564 | -0.027466 | 0.21973 | 0.036621 | 4.2618 | 122.4472 | 0.40283 | 122.4976 | 122.5662 | 122.4152 | 122.3785 | 122.3511 | -122.5525 | -122.4289 | 122.2595 | 122.4335 | 48.3124 | 42.54
2148.8281 | 122.6349 | -49.3561 | 73.0225 | -0.17082 | 0.0012711 | 0.062453 | 0.11996 | -0.0026063 | -0.0024994 | -0.0033112 | 0.018005 | -0.0032642 | 0.060333 | 0.059554 | -0.026577 | -0.00050847 | 0.0024567 | -0.9201 | 72.9996 | -49.5209 | 72.9309 | -45.1996 | -49.6353 | 4.9255 | -6.5735 | 72.9492 | -49.4385 | 73.0179 | -49.0311 | -49.3973 | -49.2096 | -0.16479 | -0.022888 | -0.091553 | 4.1565 | 54.2816 | -0.27924 | 54.4464 | -0.11444 | -0.082398 | -0.073242 | -0.004578 | 0.32501 | 0.14648 | -0.041199 | 0.22888 | 0.041199 | 4.3213 | 122.4518 | 0.40741 | 122.4564 | 122.5204 | 122.3877 | 122.3557 | 122.3053 | -122.5433 | -122.4609 | 122.287 | 122.374 | 48.436 | 42.7826
2149.7656 | 122.6761 | -49.2508 | 73.0957 | -0.17082 | 0.0016983 | 0.058821 | 0.12039 | -0.00068368 | -0.0039948 | -0.0026704 | 0.027161 | -0.0034778 | 0.063965 | 0.062117 | -0.031063 | -0.00093567 | -0.00010671 | -0.94757 | 73.0774 | -49.4247 | 73.0591 | -45.108 | -49.5117 | 5.0034 | -6.6467 | 73.0682 | -49.2966 | 73.1461 | -48.9487 | -49.324 | -49.1135 | -0.17395 | -0.01831 | -0.036621 | 4.1428 | 54.2542 | -0.26093 | 54.4281 | -0.086975 | -0.045777 | -0.027466 | 0.050354 | 0.30212 | 0.13733 | -0.073243 | 0.18311 | -0.027466 | 4.3167 | 122.4838 | 0.3479 | 122.4426 | 122.5021 | 122.3648 | 122.3282 | 122.319 | -122.5204 | -122.3923 | 122.3099 | 122.3969 | 48.3032 | 42.6041
2150.8281 | 122.5891 | -49.1913 | 73.2239 | -0.10216 | -0.0019333 | 0.062239 | 0.11975 | 0.0014527 | -0.0031402 | -0.0033112 | -0.091858 | -0.0028368 | 0.065247 | 0.065322 | -0.028713 | 0.0012005 | -0.00074771 | -1.0025 | 73.2376 | -49.3607 | 73.0453 | -45.2408 | -49.5804 | 4.7424 | -6.8619 | 73.201 | -49.2554 | 73.1873 | -48.8983 | -49.2874 | -49.0997 | -0.16937 | 0.013733 | -0.17853 | 3.9505 | 53.9337 | -0.3891 | 54.1031 | -0.21973 | -0.064087 | -0.022888 | -0.036621 | 0.29297 | 0.091553 | -0.096131 | 0.15564 | -0.032044 | 4.1199 | 122.406 | 0.35706 | 122.4426 | 122.5983 | 122.4564 | 122.4289 | 122.3923 | -122.5845 | -122.4792 | 122.2366 | 122.3785 | 48.1888 | 42.3294
2151.7656 | 122.6349 | -49.0219 | 73.3337 | -0.06401 | 0.0010575 | 0.062025 | 0.11868 | 0.0018799 | -0.0003632 | -0.0043792 | 0.051575 | -0.0045458 | 0.063538 | 0.056136 | -0.0285 | 0.00013253 | 0.0020295 | -0.99792 | 73.3475 | -49.1821 | 73.3063 | -44.8288 | -49.4568 | 4.8981 | -6.7749 | 73.2925 | -49.1043 | 73.3246 | -48.7106 | -49.0952 | -48.9075 | -0.16022 | 0.013733 | -0.027466 | 4.1931 | 53.92 | -0.43487 | 54.0802 | -0.27466 | -0.082397 | -0.041198 | -0.009155 | 0.31128 | 0.11444 | -0.073242 | 0.19684 | 0.009155 | 4.3533 | 122.4884 | 0.39368 | 122.4289 | 122.5296 | 122.3969 | 122.3694 | 122.3145 | -122.5159 | -122.438 | 122.3282 | 122.3465 | 48.024 | 42.247
2152.8438 | 122.6166 | -48.9258 | 73.4756 | -0.086899 | 0.00084388 | 0.060957 | 0.1206 | 0.00081172 | -0.0020722 | -0.002884 | -0.09491 | -0.0026232 | 0.061829 | 0.064467 | -0.028927 | -0.0011493 | -0.0013885 | -0.94757 | 73.4802 | -49.0631 | 73.4344 | -44.8059 | -49.2004 | 5.0583 | -6.633 | 73.4665 | -48.9944 | 73.494 | -48.6191 | -48.9899 | -48.8205 | -0.13733 | 0.004578 | -0.041199 | 4.1199 | 53.9841 | -0.27466 | 54.1214 | -0.13733 | -0.068665 | -0.009155 | 0.018311 | 0.3067 | 0.10529 | -0.064087 | 0.17395 | 0.004578 | 4.2572 | 122.4976 | 0.37537 | 122.4884 | 122.5433 | 122.4609 | 122.406 | 122.3923 | -122.5388 | -122.4701 | 122.3602 | 122.4197 | 47.9782 | 42.2928
2153.7656 | 122.7081 | -49.0219 | 73.3749 | -0.12505 | 0.00041648 | 0.062239 | 0.11911 | 0.0033753 | -0.0029266 | 0.00074764 | -0.070496 | -0.0019824 | 0.063965 | 0.065322 | -0.029354 | 0.0024823 | 0.0013885 | -1.03 | 73.3292 | -49.2142 | 73.2376 | -45.0027 | -49.3378 | 4.8614 | -6.7017 | 73.288 | -49.1318 | 73.3932 | -48.6877 | -49.054 | -48.8617 | -0.19226 | -0.045776 | -0.13733 | 4.0192 | 53.8834 | -0.31586 | 54.0756 | -0.1236 | -0.10986 | -0.086975 | 0.018311 | 0.33417 | 0.16022 | -0.032043 | 0.27008 | 0.07782 | 4.2114 | 122.4518 | 0.44403 | 122.525 | 122.5433 | 122.4197 | 122.3511 | 122.3099 | -122.5891 | -122.5067 | 122.2595 | 122.4152 | 47.9919 | 42.3203
2154.7656 | 122.7036 | -48.9716 | 73.3658 | -0.20897 | 0.0023391 | 0.062025 | 0.11975 | 0.0067933 | -0.0012176 | -0.0058746 | -0.018616 | -0.003905 | 0.063111 | 0.058486 | -0.029354 | 0.0016277 | 0.0011749 | -0.90179 | 73.3566 | -49.1135 | 73.4161 | -44.632 | -49.1959 | 4.8065 | -6.6513 | 73.3429 | -49.0448 | 73.4573 | -48.6053 | -49.0173 | -48.8297 | -0.14191 | -0.009156 | 0.050354 | 4.3396 | 53.7781 | -0.2243 | 53.92 | -0.082398 | -0.073242 | -0.022888 | 0.091552 | 0.36621 | 0.14191 | -0.045776 | 0.21515 | 0.027466 | 4.4815 | 122.5296 | 0.43945 | 122.5021 | 122.4701 | 122.3877 | 122.3282 | 122.3145 | -122.4792 | -122.4106 | 122.3877 | 122.4289 | 48.0698 | 42.3203
2155.7656 | 122.5845 | -48.8205 | 73.5992 | -0.056381 | 0.0014847 | 0.063307 | 0.11868 | -0.0013245 | -0.0046356 | -0.0050202 | 0.024109 | -0.0030506 | 0.062897 | 0.059127 | -0.027645 | 0.00055973 | -0.00053411 | -0.80566 | 73.5764 | -48.9441 | 73.4985 | -44.5816 | -48.9853 | 5.0537 | -6.6788 | 73.5718 | -48.8571 | 73.5626 | -48.4909 | -48.8525 | -48.7289 | -0.1236 | -0.022888 | -0.10071 | 4.2389 | 53.8742 | -0.16479 | 53.9978 | -0.041199 | -0.036621 | -0.027466 | -0.036621 | 0.32959 | 0.091553 | -0.032043 | 0.12817 | 0.004578 | 4.3625 | 122.4426 | 0.36621 | 122.4197 | 122.5204 | 122.4289 | 122.3969 | 122.3923 | -122.5433 | -122.4564 | 122.319 | 122.3831 | 48.0148 | 42.1417
2156.7656 | 122.6852 | -48.88 | 73.4482 | -0.14793 | -0.00065152 | 0.062239 | 0.11804 | -4.2682e-05 | -0.0029266 | -0.0018158 | -0.036926 | -0.0032642 | 0.062042 | 0.063185 | -0.028927 | -0.00093567 | 0.00032049 | -0.97504 | 73.3932 | -49.1043 | 73.4482 | -44.6869 | -49.1913 | 5.0949 | -6.7062 | 73.4024 | -48.9899 | 73.5397 | -48.5504 | -48.9075 | -48.7289 | -0.2243 | -0.054931 | 0 | 4.1931 | 53.9749 | -0.31128 | 54.1992 | -0.086975 | -0.10986 | -0.045776 | 0.091553 | 0.32959 | 0.15106 | -0.027466 | 0.26093 | 0.082397 | 4.4174 | 122.5525 | 0.43945 | 122.5296 | 122.4976 | 122.3923 | 122.2733 | 122.2824 | -122.5525 | -122.438 | 122.3282 | 122.4197 | 47.905 | 42.1738
2157.8281 | 122.6807 | -48.7473 | 73.6313 | -0.16319 | 0.00063028 | 0.061598 | 0.11889 | -0.0021789 | -0.0012176 | -0.00010676 | -0.06134 | -0.0047594 | 0.059052 | 0.059981 | -0.028713 | 0.0022687 | -0.0030975 | -0.87891 | 73.613 | -48.8846 | 73.5718 | -44.5312 | -48.9944 | 4.9438 | -6.7337 | 73.5809 | -48.8022 | 73.6267 | -48.2071 | -48.6374 | -48.5641 | -0.13733 | -0.018311 | -0.05951 | 4.216 | 53.6911 | -0.24719 | 53.8284 | -0.10986 | -0.054932 | -0.050354 | -0.004578 | 0.54016 | 0.1831 | 0.10986 | 0.23804 | 0.16479 | 4.3533 | 122.4564 | 0.59509 | 122.4289 | 122.4976 | 122.3831 | 122.3602 | 122.3282 | -122.5159 | -122.4335 | 122.319 | 122.374 | 47.8683 | 42.0135
2158.7656 | 122.6715 | -48.8068 | 73.5535 | -0.13267 | 0.0012711 | 0.063094 | 0.11889 | 0.0023071 | -0.0033538 | -0.0048066 | -0.024719 | -0.005614 | 0.061188 | 0.054213 | -0.027218 | -8.1274e-05 | 0.0020295 | -0.87891 | 73.5214 | -48.9578 | 73.5123 | -44.577 | -49.0631 | 4.953 | -6.6971 | 73.5077 | -48.8754 | 73.6176 | -48.468 | -48.8205 | -48.6649 | -0.15106 | -0.032044 | -0.041199 | 4.2297 | 53.7598 | -0.25635 | 53.9108 | -0.10529 | -0.068664 | -0.045777 | 0.064087 | 0.33874 | 0.14191 | -0.013733 | 0.21057 | 0.054931 | 4.3808 | 122.4701 | 0.40741 | 122.493 | 122.4792 | 122.3831 | 122.3282 | 122.3145 | -122.5113 | -122.4289 | 122.319 | 122.4243 | 47.9279 | 42.1097
2159.7656 | 122.7036 | -48.6053 | 73.764 | -0.048752 | -0.00043792 | 0.062453 | 0.11718 | 0.00038452 | -0.0035674 | 0.00032044 | -0.033874 | -0.0047594 | 0.061188 | 0.059981 | -0.027004 | 0.0016277 | -0.0024567 | -0.83313 | 73.764 | -48.7427 | 73.7549 | -44.2657 | -48.848 | 5.1956 | -6.6147 | 73.7183 | -48.642 | 73.8739 | -48.23 | -48.6099 | -48.4406 | -0.13733 | 0 | -0.009155 | 4.3396 | 53.801 | -0.24261 | 53.9383 | -0.10528 | -0.036621 | -0.045776 | 0.10986 | 0.37537 | 0.1648 | -0.004577 | 0.20142 | 0.032044 | 4.4769 | 122.4976 | 0.41199 | 122.5159 | 122.5067 | 122.3602 | 122.3694 | 122.3236 | -122.5067 | -122.406 | 122.3602 | 122.4792 | 47.7722 | 41.9907
2160.8281 | 122.6944 | -48.6603 | 73.6954 | -0.07164 | 0.00020288 | 0.060103 | 0.1174 | -0.0013245 | -0.0007904 | -0.0033112 | 0.014954 | -0.0049732 | 0.060761 | 0.065108 | -0.0285 | -8.1274e-05 | -0.0028839 | -0.81024 | 73.6633 | -48.8617 | 73.613 | -44.426 | -48.9304 | 5.1178 | -6.5598 | 73.6084 | -48.7793 | 73.7778 | -48.2483 | -48.642 | -48.5001 | -0.20142 | -0.032044 | -0.082398 | 4.2343 | 53.7781 | -0.27008 | 53.9795 | -0.068665 | -0.11902 | -0.086976 | 0.082397 | 0.41199 | 0.16022 | 0.01831 | 0.27924 | 0.13733 | 4.4357 | 122.4747 | 0.53101 | 122.5571 | 122.525 | 122.3877 | 122.3236 | 122.2687 | -122.5571 | -122.4747 | 122.2733 | 122.438 | 47.85 | 42.1005
2161.7656 | 122.6944 | -48.6237 | 73.764 | -0.14793 | 0.0012711 | 0.063094 | 0.11761 | -0.0043151 | -0.0052764 | -0.003952 | 0.0027466 | -0.0051868 | 0.066101 | 0.056563 | -0.029568 | -8.1274e-05 | 0.0052337 | -0.78735 | 73.7732 | -48.7793 | 73.6954 | -44.3527 | -48.8846 | 5.0537 | -6.6376 | 73.7045 | -48.6832 | 73.819 | -48.2117 | -48.5962 | -48.4314 | -0.15564 | 0.009155 | -0.068664 | 4.2709 | 53.6774 | -0.26093 | 53.833 | -0.10529 | -0.05951 | -0.059509 | 0.054932 | 0.41199 | 0.19226 | 0.027466 | 0.25177 | 0.086976 | 4.4266 | 122.4747 | 0.4715 | 122.5021 | 122.5525 | 122.3877 | 122.3969 | 122.3282 | -122.5433 | -122.4472 | 122.319 | 122.4426 | 47.8363 | 41.9861
2162.8281 | 122.6532 | -48.8022 | 73.6038 | -0.13267 | 0.00041648 | 0.060316 | 0.11996 | -0.0013245 | -0.0031402 | -0.003952 | -0.015564 | -0.0030506 | 0.066101 | 0.065108 | -0.030422 | -0.00029487 | 0.0024567 | -0.83771 | 73.5626 | -48.967 | 73.4299 | -44.545 | -48.9853 | 4.8935 | -6.7978 | 73.5397 | -48.8571 | 73.5947 | -48.4268 | -48.8205 | -48.6649 | -0.16479 | -0.041199 | -0.17395 | 4.2572 | 53.6957 | -0.18311 | 53.8605 | -0.018311 | -0.054932 | -0.064087 | -0.009155 | 0.37537 | 0.13733 | -0.018311 | 0.19226 | 0.036621 | 4.422 | 122.3969 | 0.4303 | 122.4518 | 122.5296 | 122.3969 | 122.3648 | 122.3419 | -122.5708 | -122.4609 | 122.2321 | 122.3969 | 47.9645 | 42.0044
2163.7656 | 122.7036 | -48.8205 | 73.5672 | -0.13267 | 0.0014847 | 0.062666 | 0.11911 | 0.0033753 | -0.0014312 | -0.0018158 | -0.0094604 | -0.0041186 | 0.062897 | 0.062117 | -0.028713 | 0.0016277 | 0.0028839 | -0.79651 | 73.5855 | -48.9349 | 73.5077 | -44.6274 | -49.0402 | 5.2826 | -6.6101 | 73.5123 | -48.88 | 73.6313 | -48.3948 | -48.7793 | -48.6557 | -0.11444 | 0.01831 | -0.05951 | 4.1931 | 54.1031 | -0.21973 | 54.2175 | -0.10529 | -0.059509 | -0.054932 | 0.064087 | 0.42572 | 0.16479 | 0.041199 | 0.2243 | 0.10071 | 4.3076 | 122.4426 | 0.48523 | 122.5113 | 122.5204 | 122.3923 | 122.406 | 122.3328 | -122.5021 | -122.4472 | 122.3282 | 122.4518 | 48.024 | 42.2104
2164.8281 | 122.7036 | -48.9761 | 73.3932 | -0.07164 | 0.00063028 | 0.062666 | 0.12039 | 0.0020935 | -0.001004 | -0.0018158 | -0.024719 | -0.003905 | 0.063111 | 0.060622 | -0.0285 | -0.0013629 | 0.0043793 | -0.81024 | 73.4161 | -49.1089 | 73.32 | -44.8929 | -49.2233 | 5.3375 | -6.7932 | 73.3704 | -48.9944 | 73.4619 | -48.5641 | -48.9532 | -48.8068 | -0.13275 | 0.022888 | -0.073243 | 4.0833 | 54.3137 | -0.24719 | 54.4464 | -0.11444 | -0.018311 | -0.022889 | 0.068664 | 0.41199 | 0.16937 | 0.022888 | 0.18768 | 0.041199 | 4.216 | 122.4289 | 0.4303 | 122.4564 | 122.525 | 122.3648 | 122.3923 | 122.3465 | -122.5021 | -122.3877 | 122.2961 | 122.438 | 48.1659 | 42.1829
2165.7656 | 122.5937 | -49.0448 | 73.3978 | -0.13267 | 0.0031937 | 0.063307 | 0.12231 | 0.0010253 | -0.0018586 | -0.0018158 | -0.14984 | -0.001128 | 0.063965 | 0.058272 | -0.028286 | -0.00093567 | 0.0028839 | -1.0483 | 73.32 | -49.2279 | 73.2788 | -45.0714 | -49.411 | 5.2689 | -6.9122 | 73.3566 | -49.0997 | 73.3429 | -48.7335 | -49.1272 | -48.9395 | -0.1831 | -0.07782 | -0.11902 | 3.9734 | 54.3137 | -0.36621 | 54.4968 | -0.18311 | -0.054931 | -0.041199 | -0.054931 | 0.31128 | 0.10529 | -0.082397 | 0.16022 | -0.027466 | 4.1565 | 122.5067 | 0.36621 | 122.4426 | 122.5479 | 122.4564 | 122.3648 | 122.4014 | -122.6257 | -122.4976 | 122.3236 | 122.3877 | 47.9965 | 42.1326
2166.8281 | 122.6715 | -48.9349 | 73.4482 | -0.13267 | 0.0010575 | 0.060744 | 0.11804 | 0.0016663 | -0.0046356 | -0.0013886 | -0.018616 | -0.0047594 | 0.062897 | 0.060836 | -0.02615 | 0.00034613 | 0.00074769 | -0.83771 | 73.4253 | -49.0814 | 73.3246 | -44.7556 | -49.2279 | 5.2643 | -6.8939 | 73.3841 | -49.0265 | 73.4665 | -48.555 | -48.9578 | -48.8068 | -0.14648 | -0.022888 | -0.1236 | 4.1794 | 54.1992 | -0.29297 | 54.3457 | -0.14648 | -0.091552 | -0.064087 | 0.018311 | 0.37994 | 0.12817 | -0.022888 | 0.21973 | 0.068664 | 4.3259 | 122.406 | 0.4715 | 122.493 | 122.5067 | 122.4106 | 122.3602 | 122.319 | -122.5296 | -122.4747 | 122.2595 | 122.4014 | 48.0972 | 42.041
2167.7656 | 122.6578 | -48.8617 | 73.5214 | -0.12505 | 0.0019119 | 0.064162 | 0.11911 | -0.0032471 | -0.0031402 | -0.0043792 | -0.04303 | -0.0036914 | 0.061615 | 0.058913 | -0.028072 | -0.00029487 | 0.0024567 | -0.81024 | 73.5306 | -49.0128 | 73.4436 | -44.7464 | -49.1135 | 5.4062 | -6.7749 | 73.5031 | -48.912 | 73.5992 | -48.3856 | -49.0311 | -48.7701 | -0.15106 | 0.009156 | -0.077819 | 4.1153 | 54.2679 | -0.25177 | 54.4189 | -0.10071 | -0.050354 | -0.01831 | 0.07782 | 0.47607 | 0.091552 | -0.16937 | 0.14191 | -0.11902 | 4.2664 | 122.4564 | 0.52643 | 122.5113 | 122.5433 | 122.4152 | 122.3923 | 122.3648 | -122.5342 | -122.4335 | 122.3053 | 122.4609 | 48.0515 | 42.0868
2168.8281 | 122.6532 | -48.9258 | 73.4802 | -0.11742 | 0.00020288 | 0.061171 | 0.11654 | -0.00089728 | -0.0059174 | -0.00010676 | 0.0027466 | -0.003905 | 0.064606 | 0.051222 | -0.029568 | 0.00077333 | -0.0013885 | -0.82398 | 73.4344 | -49.0723 | 73.3749 | -44.8196 | -49.2096 | 5.4108 | -6.7474 | 73.4161 | -48.9853 | 73.4756 | -48.5733 | -48.912 | -48.7885 | -0.14648 | -0.045777 | -0.10529 | 4.1061 | 54.3365 | -0.28381 | 54.483 | -0.13733 | -0.05951 | -0.064087 | -0.004578 | 0.35248 | 0.13733 | 0.013733 | 0.19684 | 0.073243 | 4.2526 | 122.4472 | 0.41199 | 122.4609 | 122.5067 | 122.4014 | 122.3602 | 122.3419 | -122.5525 | -122.4655 | 122.3007 | 122.4014 | 48.1018 | 42.1783
2169.7656 | 122.6852 | -48.8205 | 73.558 | -0.079269 | 0.0016983 | 0.060103 | 0.11953 | 0.00081172 | -0.0039948 | -0.00096136 | -0.015564 | -0.0041186 | 0.063111 | 0.059127 | -0.028927 | -0.00029487 | 0.0022431 | -0.81482 | 73.5168 | -48.9807 | 73.439 | -44.7006 | -49.1364 | 5.2963 | -6.7429 | 73.4802 | -48.9349 | 73.5855 | -48.4497 | -48.8434 | -48.6832 | -0.16022 | -0.041198 | -0.11902 | 4.1199 | 54.1168 | -0.31586 | 54.277 | -0.15564 | -0.11444 | -0.077819 | 0.027466 | 0.37079 | 0.13733 | -0.022888 | 0.25177 | 0.091553 | 4.2801 | 122.4197 | 0.48523 | 122.5204 | 122.4976 | 122.4152 | 122.3373 | 122.3007 | -122.5388 | -122.493 | 122.2595 | 122.406 | 48.0057 | 42.0776
2170.8438 | 122.6303 | -49.0311 | 73.407 | -0.06401 | 0.00041648 | 0.060103 | 0.11932 | 0.0020935 | -0.0046356 | -0.0013886 | -0.11017 | -0.0017688 | 0.060547 | 0.061904 | -0.029995 | 0.00013253 | 0.0018159 | -0.78278 | 73.4253 | -49.1959 | 73.2605 | -45.0256 | -49.3103 | 5.3329 | -6.7474 | 73.407 | -49.0768 | 73.3795 | -48.6786 | -49.086 | -48.9166 | -0.16479 | 0.018311 | -0.14648 | 4.0054 | 54.364 | -0.27924 | 54.5288 | -0.11444 | -0.045776 | 0 | -0.027465 | 0.35248 | 0.11444 | -0.054932 | 0.16022 | -0.009156 | 4.1702 | 122.4564 | 0.39825 | 122.4564 | 122.6212 | 122.4838 | 122.4564 | 122.438 | -122.6028 | -122.4838 | 122.2916 | 122.4106 | 48.2483 | 42.2836
2171.7656 | 122.7951 | -48.7518 | 73.6542 | -0.079269 | -0.00022432 | 0.063734 | 0.12039 | 0.0010253 | -0.0035674 | -0.0048066 | -0.00030524 | -0.0036914 | 0.061188 | 0.057631 | -0.028072 | -0.0017901 | -0.0013885 | -0.70953 | 73.5626 | -48.9441 | 73.5718 | -44.5724 | -49.0723 | 5.4382 | -6.5231 | 73.5443 | -48.8434 | 73.7137 | -48.317 | -48.7152 | -48.761 | -0.19226 | -0.091553 | -0.082398 | 4.1794 | 54.1901 | -0.32043 | 54.3823 | -0.12817 | -0.091553 | -0.10986 | 0.059509 | 0.43488 | -0.009155 | 0.036621 | 0.082398 | 0.12817 | 4.3716 | 122.5159 | 0.52643 | 122.5571 | 122.5067 | 122.3877 | 122.3145 | 122.2961 | -122.5983 | -122.4976 | 122.3236 | 122.4655 | 48.0423 | 42.2287
2172.8281 | 122.6715 | -48.967 | 73.4436 | -0.10979 | 0.00041648 | 0.06288 | 0.11996 | 0.00081172 | -0.0048492 | -0.0016022 | -0.012512 | -0.0024096 | 0.06247 | 0.062331 | -0.027431 | 0.0012005 | 0.00074769 | -0.84228 | 73.3932 | -49.1501 | 73.3154 | -44.902 | -49.205 | 5.1773 | -6.8115 | 73.3704 | -49.0219 | 73.4253 | -48.5779 | -48.9807 | -48.8342 | -0.1831 | -0.050354 | -0.12817 | 4.0649 | 54.1443 | -0.23804 | 54.3274 | -0.054932 | -0.054932 | -0.073243 | -0.018311 | 0.3891 | 0.13275 | -0.013733 | 0.18768 | 0.041199 | 4.248 | 122.4655 | 0.44403 | 122.4472 | 122.5433 | 122.3923 | 122.3602 | 122.3373 | -122.5937 | -122.4655 | 122.2824 | 122.3923 | 48.1247 | 42.1555
2173.7656 | 122.6624 | -48.9441 | 73.4573 | -0.17845 | 0.00063028 | 0.058821 | 0.1206 | 0.0016663 | -0.0024994 | -0.001175 | -0.052185 | -0.0051868 | 0.06546 | 0.059767 | -0.029781 | 0.0020551 | 0.0037385 | -0.73242 | 73.4024 | -49.0952 | 73.3521 | -44.838 | -49.2371 | 5.2368 | -6.926 | 73.3841 | -49.0128 | 73.4665 | -48.5733 | -48.9532 | -48.7976 | -0.15106 | -0.054931 | -0.10528 | 4.1061 | 54.1809 | -0.29297 | 54.332 | -0.14191 | -0.068664 | -0.073242 | 0.009156 | 0.37079 | 0.14648 | -0.009155 | 0.21515 | 0.059509 | 4.2572 | 122.4472 | 0.43945 | 122.4792 | 122.4976 | 122.3969 | 122.3465 | 122.3282 | -122.5525 | -122.4701 | 122.2961 | 122.4106 | 48.2117 | 42.0181
2174.8281 | 122.6578 | -49.0585 | 73.2971 | -0.15556 | -0.00043792 | 0.062453 | 0.12081 | 0.00059812 | -0.0020722 | -0.0013886 | -0.033874 | -0.0036914 | 0.063111 | 0.058486 | -0.028927 | 0.0020551 | -0.00032051 | -0.79651 | 73.2788 | -49.2279 | 73.233 | -45.0394 | -49.3423 | 5.1636 | -6.9717 | 73.2925 | -49.1364 | 73.3429 | -48.6877 | -49.0997 | -48.9258 | -0.16937 | -0.01831 | -0.064087 | 4.0192 | 54.2221 | -0.28381 | 54.3915 | -0.11444 | -0.07782 | -0.004577 | 0.045777 | 0.37079 | 0.13275 | -0.041198 | 0.21057 | 0.036622 | 4.1885 | 122.4609 | 0.44861 | 122.4792 | 122.5067 | 122.4289 | 122.3373 | 122.3511 | -122.525 | -122.4335 | 122.2916 | 122.4014 | 48.262 | 42.0868
2175.7656 | 122.644 | -48.848 | 73.5489 | -0.10979 | 0.00041648 | 0.06288 | 0.12124 | 0.0010253 | -0.0042084 | -0.00074776 | -0.021667 | -0.0041186 | 0.063111 | 0.062545 | -0.028927 | 0.0014141 | 0.0030975 | -0.76446 | 73.5443 | -48.9807 | 73.4482 | -44.6869 | -49.1226 | 5.2597 | -7.0312 | 73.4985 | -48.9304 | 73.5397 | -48.4589 | -48.8663 | -48.7152 | -0.13275 | -0.004577 | -0.10071 | 4.1611 | 54.1077 | -0.27466 | 54.2404 | -0.14191 | -0.082398 | -0.050354 | -0.009155 | 0.3891 | 0.13275 | -0.018311 | 0.21515 | 0.064087 | 4.2938 | 122.4289 | 0.4715 | 122.4701 | 122.525 | 122.4289 | 122.3923 | 122.3465 | -122.5296 | -122.4792 | 122.2961 | 122.3877 | 48.0835 | 41.8167
2176.8281 | 122.6898 | -48.848 | 73.5077 | -0.12505 | -1.0718e-05 | 0.060957 | 0.11911 | -4.2682e-05 | -0.002713 | -0.0037384 | -0.018616 | -0.0032642 | 0.061188 | 0.062117 | -0.027218 | 0.00034613 | 0.00096129 | -0.72784 | 73.5031 | -49.0128 | 73.439 | -44.7189 | -49.1226 | 5.3101 | -6.8573 | 73.4711 | -48.9349 | 73.5718 | -48.4634 | -48.8571 | -48.7152 | -0.1648 | -0.004577 | -0.068664 | 4.129 | 54.158 | -0.27466 | 54.3228 | -0.10986 | -0.086976 | -0.036621 | 0.064087 | 0.38452 | 0.13275 | -0.009156 | 0.21973 | 0.07782 | 4.2938 | 122.4518 | 0.4715 | 122.5067 | 122.5159 | 122.406 | 122.3511 | 122.319 | -122.5204 | -122.4426 | 122.287 | 122.4197 | 48.1201 | 41.9907
2177.7656 | 122.6852 | -48.5504 | 73.8098 | -0.12505 | -1.0718e-05 | 0.060957 | 0.11996 | 0.0016663 | -0.0039948 | -0.0026704 | -0.030823 | -0.0032642 | 0.059906 | 0.060622 | -0.02914 | 0.00098693 | 0.00010689 | -0.71411 | 73.7823 | -48.7106 | 73.7549 | -44.2795 | -48.9029 | 5.3558 | -6.7566 | 73.7549 | -48.6374 | 73.8693 | -48.1293 | -48.5367 | -48.3948 | -0.16022 | -0.027465 | -0.054931 | 4.2709 | 53.9062 | -0.35248 | 54.0665 | -0.19226 | -0.086975 | -0.054931 | 0.05951 | 0.42114 | 0.15564 | 0.013733 | 0.24262 | 0.10071 | 4.4312 | 122.4655 | 0.50812 | 122.5067 | 122.493 | 122.3923 | 122.3328 | 122.3053 | -122.5204 | -122.4472 | 122.3053 | 122.4197 | 47.8363 | 41.7938
2178.8281 | 122.6532 | -48.8434 | 73.5306 | -0.079269 | 0.0010575 | 0.060103 | 0.11804 | 0.00017092 | -0.0020722 | -0.0018158 | -0.033874 | -0.0049732 | 0.060761 | 0.064681 | -0.029568 | 0.00013253 | -0.0018157 | -0.70038 | 73.494 | -49.0128 | 73.4802 | -44.7006 | -49.0906 | 5.3696 | -6.8802 | 73.4802 | -48.8892 | 73.558 | -48.4589 | -48.8571 | -48.6923 | -0.16937 | -0.036621 | -0.050354 | 4.1428 | 54.213 | -0.24719 | 54.3823 | -0.07782 | -0.045776 | -0.050354 | 0.027465 | 0.38452 | 0.15106 | -0.013733 | 0.19684 | 0.032043 | 4.3121 | 122.493 | 0.4303 | 122.4472 | 122.5067 | 122.3694 | 122.3373 | 122.3236 | -122.5433 | -122.4197 | 122.3236 | 122.4014 | 48.143 | 41.9632
2179.7656 | 122.6624 | -48.7106 | 73.7 | -0.12505 | -0.00022432 | 0.06288 | 0.11953 | 0.00017092 | -0.0007904 | -0.0030976 | -0.058289 | -0.003905 | 0.062897 | 0.061263 | -0.030849 | 0.0012005 | 0.0016021 | -0.74158 | 73.6588 | -48.8434 | 73.6359 | -44.5038 | -48.9578 | 5.4382 | -6.8344 | 73.645 | -48.7473 | 73.7274 | -48.3215 | -48.7106 | -48.5641 | -0.13275 | -0.041199 | -0.064087 | 4.2068 | 54.1489 | -0.24719 | 54.2816 | -0.11444 | -0.036621 | -0.054931 | 0.027466 | 0.3891 | 0.14648 | 0 | 0.1831 | 0.036621 | 4.3396 | 122.4792 | 0.42572 | 122.4747 | 122.5021 | 122.3923 | 122.3694 | 122.3557 | -122.5433 | -122.4472 | 122.3465 | 122.438 | 47.9691 | 41.8762
2180.8281 | 122.8409 | -48.4863 | 73.938 | -0.10216 | -0.0038559 | 0.059676 | 0.11932 | -0.0023925 | -0.0022858 | -0.0030976 | -0.018616 | -0.0032642 | 0.06247 | 0.053572 | -0.028286 | -0.00050847 | 0.0013885 | -0.70496 | 73.819 | -48.674 | 73.8602 | -44.1513 | -48.6649 | 5.5206 | -6.8253 | 73.8327 | -48.555 | 73.9838 | -48.0148 | -48.4268 | -48.3765 | -0.18768 | -0.11902 | -0.07782 | 4.335 | 54.007 | -0.17853 | 54.1946 | 0.009155 | -0.068665 | -0.10529 | 0.045777 | 0.4715 | 0.10986 | 0.059509 | 0.17853 | 0.12817 | 4.5227 | 122.5342 | 0.54016 | 122.5388 | 122.493 | 122.3877 | 122.3053 | 122.319 | -122.612 | -122.493 | 122.3465 | 122.4701 | 47.7814 | 41.6611
2181.7656 | 122.6807 | -48.5733 | 73.8281 | -0.12505 | 0.0019119 | 0.060957 | 0.11911 | -0.00089728 | -0.0020722 | -0.0035248 | -0.058289 | -0.0058276 | 0.064179 | 0.05699 | -0.0285 | 0.0016277 | -0.00010671 | -0.71869 | 73.7915 | -48.7473 | 73.7228 | -44.3207 | -48.8205 | 5.4382 | -6.8253 | 73.7686 | -48.6465 | 73.8602 | -48.1339 | -48.5458 | -48.3994 | -0.17395 | -0.036621 | -0.10529 | 4.2526 | 54.0115 | -0.24719 | 54.1855 | -0.073243 | -0.073242 | -0.059509 | 0.032043 | 0.43945 | 0.17395 | 0.027466 | 0.24719 | 0.10071 | 4.4266 | 122.4701 | 0.5127 | 122.5067 | 122.5388 | 122.4152 | 122.3648 | 122.3419 | -122.5754 | -122.4747 | 122.2961 | 122.4335 | 47.8546 | 41.748
2182.7656 | 122.612 | -48.7244 | 73.6542 | -0.16319 | -0.00022432 | 0.061598 | 0.11975 | -0.00046988 | -0.0039948 | -0.001175 | -0.033874 | -0.0028368 | 0.063538 | 0.060195 | -0.027859 | 0.00013253 | -0.0030975 | -0.72784 | 73.6542 | -48.8617 | 73.5901 | -44.5129 | -48.9899 | 5.3284 | -6.9763 | 73.6267 | -48.7747 | 73.6633 | -48.1476 | -48.6511 | -48.5504 | -0.13733 | 0 | -0.064087 | 4.2114 | 54.0527 | -0.2655 | 54.1901 | -0.12817 | -0.050354 | -0.027466 | 0.009155 | 0.57678 | 0.17395 | 0.073242 | 0.2243 | 0.1236 | 4.3488 | 122.4518 | 0.62714 | 122.438 | 122.5159 | 122.4014 | 122.3785 | 122.3511 | -122.5159 | -122.4289 | 122.3145 | 122.3877 | 47.9965 | 41.748
2183.8281 | 122.6761 | -48.381 | 74.0341 | -0.07164 | 0.00063028 | 0.061598 | 0.12231 | 0.00038452 | -0.0029266 | -0.0020294 | -0.036926 | -0.002196 | 0.061402 | 0.065108 | -0.028927 | 0.00098693 | 0.0035247 | -0.62256 | 73.9929 | -48.5092 | 73.9655 | -44.0048 | -48.5916 | 5.4153 | -6.752 | 73.9563 | -48.4406 | 74.0479 | -47.9416 | -48.3902 | -48.2529 | -0.12817 | -0.041199 | -0.068665 | 4.3762 | 53.7964 | -0.21057 | 53.9246 | -0.082398 | -0.05951 | -0.07782 | 0.013733 | 0.43945 | 0.12817 | -0.009156 | 0.18768 | 0.050354 | 4.5044 | 122.4747 | 0.49896 | 122.4884 | 122.5021 | 122.3969 | 122.374 | 122.3373 | -122.5433 | -122.4747 | 122.3465 | 122.4289 | 47.7585 | 41.629
2184.7656 | 122.6532 | -48.6145 | 73.7778 | -0.15556 | -0.0010787 | 0.062453 | 0.11975 | -4.2682e-05 | -0.0059174 | -0.0013886 | -0.049133 | -0.003905 | 0.062042 | 0.062972 | -0.02615 | 0.0022687 | -0.0018157 | -0.6958 | 73.7778 | -48.7564 | 73.7091 | -44.3893 | -48.8937 | 5.1453 | -6.9763 | 73.7366 | -48.6694 | 73.8281 | -48.1934 | -48.6053 | -48.4543 | -0.14191 | 0 | -0.068665 | 4.2252 | 53.7598 | -0.27924 | 53.9017 | -0.13733 | -0.054932 | -0.041199 | 0.050354 | 0.42114 | 0.16022 | 0.009155 | 0.21515 | 0.064087 | 4.3671 | 122.4655 | 0.47608 | 122.4976 | 122.5342 | 122.406 | 122.3923 | 122.3511 | -122.5342 | -122.4472 | 122.3236 | 122.4426 | 47.9187 | 41.6382
2185.8281 | 122.6532 | -48.436 | 73.9288 | -0.033493 | 0.00063028 | 0.06288 | 0.12103 | 0.0029479 | -0.0022858 | 0.00053404 | -0.024719 | -0.0041186 | 0.062897 | 0.055709 | -0.028927 | 0.00098693 | -0.0024567 | -0.72327 | 73.9059 | -48.6282 | 73.8327 | -44.1879 | -48.7518 | 5.1636 | -7.0129 | 73.8922 | -48.5184 | 73.9655 | -48.0423 | -48.4772 | -48.317 | -0.19226 | -0.022888 | -0.09613 | 4.248 | 53.5995 | -0.31586 | 53.7918 | -0.1236 | -0.082398 | -0.036621 | 0.036621 | 0.39368 | 0.11902 | -0.041199 | 0.20142 | 0.041199 | 4.4403 | 122.4609 | 0.47608 | 122.4838 | 122.5342 | 122.4106 | 122.3419 | 122.3282 | -122.5571 | -122.4472 | 122.2687 | 122.4014 | 47.7127 | 41.423
2186.7656 | 122.6624 | -48.4909 | 73.9059 | -0.11742 | 0.0021255 | 0.063094 | 0.12081 | 0.0027343 | -0.0018586 | -0.0016022 | -0.09491 | -0.0028368 | 0.063324 | 0.062545 | -0.0285 | 0.00013253 | 0.00032049 | -0.61798 | 73.8693 | -48.6237 | 73.8464 | -44.1376 | -48.7701 | 5.1315 | -6.9168 | 73.8464 | -48.5367 | 73.9471 | -48.0881 | -48.5184 | -48.3398 | -0.13275 | -0.036621 | -0.059509 | 4.3533 | 53.6224 | -0.27924 | 53.7552 | -0.14648 | -0.045776 | -0.059509 | 0.041199 | 0.40283 | 0.15106 | -0.027466 | 0.19684 | 0.01831 | 4.4861 | 122.4701 | 0.44861 | 122.4838 | 122.493 | 122.3831 | 122.3602 | 122.3373 | -122.5296 | -122.4426 | 122.3373 | 122.4381 | 47.8729 | 41.5741
2187.8281 | 122.6212 | -48.5138 | 73.8739 | -0.094528 | -0.00022432 | 0.061171 | 0.11975 | -0.00046988 | -0.0048492 | -0.00053396 | 0.11871 | -0.0017688 | 0.063538 | 0.061263 | -0.0285 | -0.0024311 | -0.0011749 | -0.6546 | 73.8602 | -48.674 | 73.7915 | -44.2566 | -48.7976 | 5.1178 | -7.1411 | 73.7823 | -48.5825 | 73.9014 | -48.1384 | -48.555 | -48.381 | -0.16022 | -0.013733 | -0.082397 | 4.2572 | 53.6316 | -0.28381 | 53.7918 | -0.1236 | -0.068664 | -0.091552 | 0.027466 | 0.37537 | 0.13275 | -0.041199 | 0.20142 | 0.027465 | 4.4174 | 122.4655 | 0.44403 | 122.4838 | 122.5342 | 122.3648 | 122.374 | 122.2961 | -122.5479 | -122.4564 | 122.3053 | 122.4152 | 47.8592 | 41.3727
2188.7656 | 122.6624 | -48.4863 | 73.8922 | -0.14793 | -0.0012923 | 0.062239 | 0.12039 | 0.0016663 | -0.0005768 | 0.00074764 | -0.055237 | -0.0034778 | 0.06247 | 0.063613 | -0.029354 | 0.00034613 | 0.00053409 | -0.61798 | 73.8876 | -48.642 | 73.8098 | -44.2154 | -48.7747 | 5.2048 | -6.9489 | 73.8556 | -48.5458 | 73.9243 | -48.0927 | -48.5092 | -48.3536 | -0.15564 | -0.004578 | -0.082398 | 4.2709 | 53.6911 | -0.28839 | 53.8467 | -0.13275 | -0.059509 | -0.036621 | 0.032043 | 0.39368 | 0.13275 | -0.022888 | 0.19226 | 0.036621 | 4.4266 | 122.4518 | 0.45319 | 122.4701 | 122.5296 | 122.4014 | 122.374 | 122.3419 | -122.5342 | -122.438 | 122.2961 | 122.4106 | 47.8683 | 41.5375
2189.8281 | 122.6578 | -48.2025 | 74.1669 | -0.1403 | -0.00043792 | 0.061385 | 0.11932 | -0.00068368 | -0.0018586 | -0.0030976 | -0.073547 | -0.0036914 | 0.061188 | 0.062331 | -0.026791 | -0.00093567 | 0.0041657 | -0.54474 | 74.1074 | -48.3765 | 74.1074 | -43.7485 | -48.4909 | 5.2963 | -6.8939 | 74.0936 | -48.2803 | 74.2264 | -47.7997 | -48.2208 | -48.056 | -0.17395 | -0.059509 | -0.059509 | 4.454 | 53.4988 | -0.28839 | 53.6728 | -0.11444 | -0.077819 | -0.073242 | 0.059509 | 0.40283 | 0.14648 | -0.01831 | 0.2243 | 0.059509 | 4.628 | 122.4838 | 0.48065 | 122.5067 | 122.4838 | 122.374 | 122.3099 | 122.2961 | -122.5433 | -122.4472 | 122.3099 | 122.4289 | 47.6578 | 41.3086
2190.7656 | 122.6715 | -48.2117 | 74.1669 | -0.06401 | -0.00043792 | 0.055403 | 0.11932 | -0.0032471 | -0.0014312 | -0.00074776 | -0.036926 | -0.0043322 | 0.061402 | 0.056349 | -0.029568 | -0.00050847 | -0.00053411 | -0.35706 | 74.2218 | -48.3353 | 74.1074 | -43.7485 | -48.3856 | 5.3146 | -6.7795 | 74.1257 | -48.2437 | 74.2538 | -47.7356 | -48.1567 | -48.0331 | -0.1236 | 0.054932 | -0.059509 | 4.4632 | 53.5263 | -0.17395 | 53.6499 | -0.050354 | -0.032043 | -0.041199 | 0.086975 | 0.47607 | 0.17853 | 0.054932 | 0.21057 | 0.086975 | 4.5868 | 122.4426 | 0.50812 | 122.4976 | 122.5571 | 122.3694 | 122.4335 | 122.3373 | -122.5021 | -122.4106 | 122.319 | 122.4655 | 47.8546 | 41.4322
2191.8281 | 122.644 | -48.3994 | 74.0067 | -0.10216 | -0.00022432 | 0.062666 | 0.11911 | -0.0021789 | -0.0052764 | 0.00010684 | -0.049133 | -0.0045458 | 0.064179 | 0.059981 | -0.027431 | -0.00029487 | 0.0035247 | -0.6134 | 73.97 | -48.5733 | 73.8785 | -44.1284 | -48.7106 | 5.1041 | -7.0541 | 73.9563 | -48.4589 | 74.0112 | -47.9736 | -48.4085 | -48.2574 | -0.17395 | -0.036621 | -0.12817 | 4.2709 | 53.5034 | -0.31128 | 53.6774 | -0.13733 | -0.059509 | -0.050354 | 0.004577 | 0.42572 | 0.14191 | -0.009155 | 0.20142 | 0.050354 | 4.4449 | 122.4518 | 0.48523 | 122.4701 | 122.5433 | 122.4152 | 122.3694 | 122.3557 | -122.58 | -122.4655 | 122.2778 | 122.4106 | 47.7859 | 41.3452
2192.7656 | 122.644 | -48.3215 | 74.0524 | -0.11742 | -0.00022432 | 0.062239 | 0.1206 | -0.0021789 | -0.0039948 | 0.00096124 | -0.049133 | -0.002196 | 0.062256 | 0.064467 | -0.028072 | 0.00098693 | -0.0011749 | -0.61798 | 74.0341 | -48.4909 | 73.9655 | -44.0231 | -48.6374 | 5.1682 | -7.283 | 73.9883 | -48.3994 | 74.0799 | -47.9141 | -48.3627 | -48.2071 | -0.16937 | -0.01831 | -0.086975 | 4.2984 | 53.4897 | -0.31586 | 53.6591 | -0.14648 | -0.07782 | -0.064087 | 0.027466 | 0.40741 | 0.11444 | -0.041199 | 0.19226 | 0.036621 | 4.4678 | 122.4564 | 0.48523 | 122.4792 | 122.525 | 122.3877 | 122.3557 | 122.3099 | -122.5433 | -122.4518 | 122.287 | 122.4014 | 47.7036 | 41.0385
2193.8281 | 122.6898 | -48.381 | 73.9975 | -0.094528 | -0.00086512 | 0.060744 | 0.11975 | 0.0014527 | -0.0033538 | -0.0016022 | -0.027771 | -0.0043322 | 0.063538 | 0.05699 | -0.029781 | 0.0012005 | -0.0045929 | -0.67749 | 73.9655 | -48.5275 | 73.9975 | -44.1193 | -48.6328 | 5.3055 | -7.0862 | 73.9105 | -48.4589 | 74.0753 | -47.9141 | -48.3215 | -48.1659 | -0.14648 | -0.032044 | 0 | 4.2618 | 53.6865 | -0.25177 | 53.833 | -0.10529 | -0.07782 | -0.086976 | 0.077819 | 0.46692 | 0.21515 | 0.059509 | 0.29297 | 0.13733 | 4.4083 | 122.525 | 0.54474 | 122.5342 | 122.493 | 122.3694 | 122.3465 | 122.2916 | -122.525 | -122.4564 | 122.3785 | 122.4564 | 47.7036 | 41.2949
2194.7656 | 122.6807 | -48.2162 | 74.1577 | -0.13267 | 0.00063028 | 0.061171 | 0.11911 | -0.0017517 | -0.0022858 | -0.0037384 | -0.039978 | -0.003905 | 0.063751 | 0.060622 | -0.028927 | 0.0026959 | 0.00032049 | -0.6546 | 74.1394 | -48.4222 | 74.0479 | -43.8995 | -48.4772 | 5.3009 | -7.0724 | 74.1348 | -48.3078 | 74.1943 | -47.7951 | -48.2254 | -48.0927 | -0.20599 | -0.018311 | -0.10986 | 4.3167 | 53.5172 | -0.26093 | 53.7231 | -0.054932 | -0.091552 | -0.022888 | 0.036621 | 0.42114 | 0.1236 | -0.009155 | 0.21515 | 0.082397 | 4.5227 | 122.4701 | 0.5127 | 122.5021 | 122.5616 | 122.4426 | 122.3557 | 122.3511 | -122.58 | -122.4655 | 122.2641 | 122.4106 | 47.5616 | 41.1438
2195.8281 | 122.6669 | -48.3536 | 74.0433 | -0.16319 | 0.0016983 | 0.061598 | 0.11932 | 0.00017092 | -0.0029266 | -0.0013886 | -0.024719 | -0.0036914 | 0.064392 | 0.059127 | -0.029568 | 0.0014141 | 0.00032049 | -0.60425 | 74.0067 | -48.4863 | 73.9609 | -44.0552 | -48.6053 | 5.1819 | -7.1732 | 73.9929 | -48.4039 | 74.0707 | -47.905 | -48.3536 | -48.1934 | -0.13275 | -0.036621 | -0.082398 | 4.2984 | 53.5355 | -0.25177 | 53.6682 | -0.11902 | -0.050354 | -0.050354 | 0.027466 | 0.44861 | 0.16022 | 0 | 0.21057 | 0.050354 | 4.4312 | 122.4472 | 0.49896 | 122.4747 | 122.493 | 122.3969 | 122.3602 | 122.3465 | -122.5296 | -122.4472 | 122.3145 | 122.4243 | 47.7493 | 41.1804
2196.7656 | 122.8363 | -48.2162 | 74.1669 | -0.07164 | 0.0019119 | 0.061598 | 0.12167 | 0.0012391 | -0.0033538 | -0.001175 | -0.033874 | -0.0054004 | 0.061615 | 0.067031 | -0.028927 | 0.00013253 | -0.00053411 | -0.55847 | 74.1028 | -48.4085 | 74.1348 | -43.7805 | -48.4268 | 5.3558 | -6.9717 | 74.0982 | -48.2803 | 74.2447 | -47.7402 | -48.1293 | -47.7951 | -0.19226 | -0.064087 | -0.032043 | 4.4357 | 53.5721 | -0.21057 | 53.7643 | -0.018311 | -0.064086 | -0.068664 | 0.07782 | 0.47608 | 0.42114 | 0.086976 | 0.48523 | 0.15106 | 4.628 | 122.5433 | 0.54016 | 122.525 | 122.5113 | 122.3785 | 122.319 | 122.3145 | -122.5754 | -122.4472 | 122.3511 | 122.4609 | 47.6578 | 41.2445
2197.7656 | 122.6624 | -48.1293 | 74.2767 | -0.13267 | 0.00041648 | 0.063307 | 0.11975 | 0.0014527 | -0.0031402 | -0.0018158 | -0.076599 | -0.0026232 | 0.062897 | 0.059767 | -0.026577 | 0.00098693 | 0.0016021 | -0.5722 | 74.2401 | -48.2666 | 74.1989 | -43.6295 | -48.3948 | 5.2872 | -7.0679 | 74.2447 | -48.1796 | 74.3088 | -47.7036 | -48.1339 | -47.9919 | -0.13733 | -0.036621 | -0.077819 | 4.4998 | 53.4164 | -0.2655 | 53.5538 | -0.12817 | -0.050354 | -0.032043 | 0.032044 | 0.42572 | 0.13733 | -0.004578 | 0.18768 | 0.045776 | 4.6371 | 122.4655 | 0.47607 | 122.4884 | 122.5067 | 122.4243 | 122.3694 | 122.374 | -122.5433 | -122.4564 | 122.3282 | 122.438 | 47.5571 | 41.0614
2198.8281 | 122.6578 | -48.2758 | 74.0845 | -0.11742 | 0.0014847 | 0.062453 | 0.12103 | -0.0013245 | -0.0039948 | -0.0020294 | -0.06134 | -0.0028368 | 0.062256 | 0.056349 | -0.0285 | -0.00072207 | 0.0030975 | -0.55847 | 74.0616 | -48.4406 | 74.0112 | -43.895 | -48.6008 | 5.2277 | -7.0312 | 74.0616 | -48.3673 | 74.1165 | -47.8546 | -48.2986 | -48.1613 | -0.16479 | -0.022889 | -0.073243 | 4.3808 | 53.5034 | -0.32501 | 53.6682 | -0.16022 | -0.091553 | -0.022889 | 0.032043 | 0.42114 | 0.11444 | -0.022888 | 0.20599 | 0.068665 | 4.5456 | 122.4518 | 0.5127 | 122.4838 | 122.5021 | 122.4289 | 122.3373 | 122.3373 | -122.525 | -122.4518 | 122.287 | 122.3923 | 47.7173 | 41.2445
2199.7656 | 122.7173 | -48.2895 | 74.0616 | -0.13267 | -1.0718e-05 | 0.060957 | 0.11996 | 0.00038452 | -0.002713 | -0.00096136 | -0.030823 | -0.0032642 | 0.063324 | 0.056563 | -0.029354 | 0.0020551 | -0.00032051 | -0.53101 | 74.0616 | -48.4726 | 74.025 | -43.8858 | -48.5458 | 5.1865 | -7.0129 | 73.9975 | -48.3902 | 74.1623 | -47.8317 | -48.2574 | -48.1384 | -0.1831 | 0 | -0.036621 | 4.4037 | 53.476 | -0.25635 | 53.6591 | -0.073242 | -0.10071 | -0.064086 | 0.10071 | 0.45776 | 0.15106 | 0.032044 | 0.25177 | 0.13275 | 4.5868 | 122.4976 | 0.55847 | 122.5525 | 122.5342 | 122.3877 | 122.3511 | 122.287 | -122.5342 | -122.4518 | 122.3145 | 122.4518 | 47.7585 | 41.2766
2200.8281 | 122.7127 | -48.2712 | 74.1119 | -0.10979 | 0.0023391 | 0.061171 | 0.11953 | -0.0032471 | -0.0029266 | -0.0048066 | -0.0094604 | -0.0036914 | 0.062683 | 0.058272 | -0.027004 | 0.0016277 | -0.00032051 | -0.54016 | 74.0707 | -48.4131 | 74.0707 | -43.7942 | -48.4863 | 5.1773 | -6.9717 | 74.0295 | -48.3582 | 74.2126 | -47.7631 | -48.2071 | -48.0789 | -0.14191 | -0.041198 | -0.041198 | 4.4769 | 53.4485 | -0.21515 | 53.5904 | -0.073242 | -0.086975 | -0.082397 | 0.10071 | 0.50812 | 0.19226 | 0.064087 | 0.27924 | 0.15106 | 4.6188 | 122.4838 | 0.59509 | 122.5708 | 122.4838 | 122.3877 | 122.3419 | 122.3007 | -122.525 | -122.4701 | 122.3419 | 122.4838 | 47.731 | 41.2994
2201.7656 | 122.6715 | -48.1979 | 74.1943 | -0.10979 | 0.0029801 | 0.062239 | 0.11996 | 0.0046569 | -0.0005768 | -0.002884 | -0.070496 | -0.0032642 | 0.063324 | 0.067885 | -0.029354 | 0.0026959 | -0.00010671 | -0.50354 | 74.1806 | -48.3398 | 74.144 | -43.6615 | -48.4497 | 5.1086 | -7.077 | 74.1486 | -48.23 | 74.231 | -47.7722 | -48.2117 | -48.0515 | -0.14191 | -0.013733 | -0.050354 | 4.5364 | 53.3066 | -0.25177 | 53.4485 | -0.10986 | -0.032043 | -0.045776 | 0.036621 | 0.42572 | 0.14648 | -0.013733 | 0.17853 | 0.01831 | 4.6783 | 122.4838 | 0.45776 | 122.4609 | 122.5204 | 122.3785 | 122.3785 | 122.3465 | -122.5342 | -122.4243 | 122.3419 | 122.4289 | 47.6944 | 41.1209
2202.8281 | 122.6532 | -48.4726 | 73.9517 | -0.12505 | 0.00041648 | 0.061812 | 0.12146 | -0.0026063 | -0.0046356 | 0.00032044 | -0.046081 | -0.0024096 | 0.063751 | 0.062545 | -0.029354 | 0.0018413 | -0.00074771 | -0.49896 | 73.9517 | -48.5687 | 73.9197 | -44.0872 | -48.8708 | 5.1773 | -7.2464 | 73.9243 | -48.5413 | 73.9792 | -47.9645 | -48.4543 | -48.2895 | -0.096131 | 0 | -0.032043 | 4.3854 | 53.6499 | -0.39825 | 53.746 | -0.30212 | -0.068665 | -0.027466 | 0.027466 | 0.50812 | 0.1831 | 0.01831 | 0.25177 | 0.086975 | 4.4815 | 122.4884 | 0.57678 | 122.5204 | 122.5204 | 122.4655 | 122.4243 | 122.3969 | -122.5204 | -122.493 | 122.3923 | 122.4518 | 47.9736 | 41.2262
2203.7656 | 122.6578 | -48.3582 | 74.0387 | -0.14793 | 0.0036209 | 0.061812 | 0.11953 | -0.00068368 | -0.0022858 | -0.00074776 | -0.04303 | -0.0019824 | 0.063751 | 0.054854 | -0.030422 | 0.00055973 | 0.0024567 | -0.48523 | 74.0387 | -48.5046 | 73.9655 | -43.9499 | -48.5504 | 5.2139 | -7.1869 | 74.0204 | -48.3994 | 74.1989 | -48.0743 | -48.3353 | -48.2254 | -0.14648 | 0 | -0.073242 | 4.4083 | 53.5721 | -0.19226 | 53.7186 | -0.045776 | -0.041199 | -0.01831 | 0.16022 | 0.28381 | 0.13275 | 0.022888 | 0.17395 | 0.064087 | 4.5547 | 122.4701 | 0.32501 | 122.5983 | 122.5433 | 122.4197 | 122.3969 | 122.3785 | -122.5433 | -122.438 | 122.3236 | 122.5571 | 47.8729 | 41.1713
2204.8281 | 122.6624 | -48.2666 | 74.1257 | -0.1403 | 0.0021255 | 0.061598 | 0.11932 | 0.0040161 | -0.0016448 | -0.00032036 | -0.046081 | -0.0032642 | 0.061402 | 0.064681 | -0.025509 | 0.0012005 | 0.0041657 | -0.52185 | 74.0891 | -48.381 | 74.0479 | -43.8217 | -48.5229 | 5.1544 | -6.9122 | 74.0936 | -48.3353 | 74.1623 | -47.8363 | -48.2803 | -48.1293 | -0.11444 | -0.036621 | -0.077819 | 4.4449 | 53.421 | -0.25635 | 53.5355 | -0.14191 | -0.068664 | -0.032043 | 0.036621 | 0.4303 | 0.13733 | -0.013732 | 0.20599 | 0.054932 | 4.5593 | 122.4289 | 0.49896 | 122.4976 | 122.4701 | 122.4289 | 122.3557 | 122.3602 | -122.5067 | -122.4609 | 122.3145 | 122.4289 | 47.7448 | 41.3544
2205.7656 | 122.6624 | -47.905 | 74.4827 | -0.12505 | -0.00065152 | 0.060103 | 0.11868 | -0.00089728 | -0.0039948 | -0.00096136 | -0.052185 | -0.0043322 | 0.063538 | 0.059554 | -0.028072 | -0.00072207 | -0.0024567 | -0.6134 | 74.4644 | -48.0881 | 74.3912 | -43.4052 | -48.1567 | 5.3238 | -6.8115 | 74.4553 | -47.9645 | 74.6292 | -47.6166 | -47.9416 | -47.7951 | -0.18311 | -0.01831 | -0.091553 | 4.4998 | 53.2288 | -0.25177 | 53.4119 | -0.068664 | -0.05951 | -0.027466 | 0.14648 | 0.28839 | 0.10986 | -0.036621 | 0.16937 | 0.022889 | 4.6829 | 122.4792 | 0.3479 | 122.5937 | 122.5525 | 122.4197 | 122.3694 | 122.3602 | -122.5708 | -122.4472 | 122.2961 | 122.5342 | 47.2916 | 41.0934
2206.8281 | 122.6624 | -48.1934 | 74.1852 | -0.10979 | -0.00043792 | 0.06288 | 0.11911 | 0.00081172 | -0.0014312 | -0.001175 | -0.036926 | -0.0032642 | 0.062683 | 0.054427 | -0.028286 | -0.0013629 | 0.0018159 | -0.43488 | 74.1623 | -48.3398 | 74.1394 | -43.7302 | -48.4314 | 5.2643 | -6.7886 | 74.1669 | -48.2529 | 74.2035 | -47.7493 | -48.2162 | -48.056 | -0.14648 | -0.022889 | -0.045777 | 4.4632 | 53.4576 | -0.23804 | 53.6041 | -0.091552 | -0.05951 | -0.018311 | 0.01831 | 0.44403 | 0.13733 | -0.022889 | 0.19684 | 0.036621 | 4.6097 | 122.4792 | 0.50354 | 122.4564 | 122.5021 | 122.4197 | 122.3557 | 122.3602 | -122.525 | -122.4381 | 122.3328 | 122.3969 | 47.7585 | 41.4047
2207.7656 | 122.6486 | -48.2849 | 74.1257 | -0.06401 | 0.0012711 | 0.061812 | 0.11996 | -0.0038879 | -0.004422 | -0.0050202 | -0.030823 | -0.0036914 | 0.063751 | 0.058913 | -0.02914 | 0.0014141 | 0.0011749 | -0.5127 | 74.0891 | -48.4222 | 74.0067 | -43.8766 | -48.6099 | 4.985 | -6.9626 | 74.057 | -48.3353 | 74.1486 | -47.8683 | -48.3032 | -48.1339 | -0.13733 | -0.036621 | -0.11902 | 4.4083 | 53.27 | -0.32501 | 53.4073 | -0.18768 | -0.050354 | -0.068664 | 0.022889 | 0.41656 | 0.15106 | -0.018311 | 0.20142 | 0.032043 | 4.5456 | 122.4289 | 0.46692 | 122.4838 | 122.5113 | 122.3923 | 122.374 | 122.3419 | -122.5479 | -122.4609 | 122.2916 | 122.4335 | 47.7722 | 41.3223
2208.8281 | 122.6761 | -48.1155 | 74.2722 | -0.29289 | 0.0014847 | 0.061385 | 0.12124 | -0.00089728 | -0.0014312 | -0.0026704 | -0.033874 | -0.0036914 | 0.063111 | 0.059981 | -0.028713 | -8.1274e-05 | 0.00032049 | -0.38452 | 74.2401 | -48.2758 | 74.2355 | -43.5791 | -48.317 | 5.2002 | -7.1594 | 74.1989 | -48.1888 | 74.3088 | -47.6028 | -48.0515 | -47.9416 | -0.16022 | -0.032044 | -0.036621 | 4.5364 | 53.3157 | -0.20142 | 53.476 | -0.041199 | -0.073242 | -0.073242 | 0.036621 | 0.5127 | 0.17395 | 0.064087 | 0.24719 | 0.13733 | 4.6967 | 122.5113 | 0.58594 | 122.4976 | 122.5159 | 122.3877 | 122.3557 | 122.3145 | -122.5479 | -122.4609 | 122.3511 | 122.4243 | 47.731 | 40.9561
2209.7656 | 122.6761 | -48.2712 | 74.1302 | -0.14793 | 0.00020288 | 0.061385 | 0.11996 | -4.2682e-05 | -0.0054902 | 0.00010684 | -0.030823 | -0.0051868 | 0.061829 | 0.058699 | -0.028927 | 0.0012005 | 0.0016021 | -0.45776 | 74.1074 | -48.4497 | 74.0204 | -43.8904 | -48.5504 | 5.1773 | -7.5256 | 74.0662 | -48.3353 | 74.1806 | -47.8043 | -48.2483 | -48.1155 | -0.17853 | -0.022888 | -0.10986 | 4.3808 | 53.4485 | -0.27924 | 53.627 | -0.10071 | -0.064087 | -0.064087 | 0.050354 | 0.46692 | 0.15564 | 0.022888 | 0.21973 | 0.086975 | 4.5593 | 122.4701 | 0.53101 | 122.5159 | 122.5571 | 122.4014 | 122.3785 | 122.3373 | -122.58 | -122.4655 | 122.2916 | 122.4518 | 47.8134 | 40.7455
2210.8281 | 122.7402 | -48.1979 | 74.1531 | -0.10216 | -0.00043792 | 0.061812 | 0.12167 | -0.0011109 | -0.0035674 | -0.0050202 | -0.027771 | -0.0043322 | 0.063324 | 0.058486 | -0.028713 | -0.0047809 | 0.00032049 | -0.39825 | 74.176 | -48.349 | 74.1623 | -43.7119 | -48.3765 | 5.3467 | -7.1869 | 74.1394 | -48.2346 | 74.4415 | -47.8683 | -48.3994 | -48.1659 | -0.15106 | 0.022888 | 0.009155 | 4.4861 | 53.5446 | -0.17853 | 53.6957 | -0.027466 | -0.036621 | -0.013733 | 0.28839 | 0.32959 | 0.032043 | -0.20142 | 0.068664 | -0.16479 | 4.6371 | 122.5113 | 0.36621 | 122.6761 | 122.525 | 122.374 | 122.374 | 122.3373 | -122.5021 | -122.3877 | 122.3602 | 122.6395 | 47.7997 | 41.011
2211.7656 | 122.6944 | -48.0194 | 74.3683 | -0.10979 | 0.0016983 | 0.062025 | 0.12017 | 0.00059812 | -0.0035674 | -0.0035248 | -0.030823 | -0.0043322 | 0.063111 | 0.056349 | -0.031277 | 0.00077333 | -0.00010671 | -0.39368 | 74.3454 | -48.1979 | 74.2767 | -43.5562 | -48.2849 | 5.452 | -7.1686 | 74.3088 | -48.111 | 74.4141 | -47.5571 | -48.0103 | -47.8729 | -0.17853 | -0.022888 | -0.091553 | 4.4632 | 53.4714 | -0.2655 | 53.6499 | -0.086975 | -0.091553 | -0.059509 | 0.045776 | 0.46234 | 0.14648 | 0.009155 | 0.23804 | 0.10071 | 4.6417 | 122.4747 | 0.55389 | 122.525 | 122.5433 | 122.4197 | 122.3648 | 122.3282 | -122.5662 | -122.4792 | 122.2961 | 122.4335 | 47.6257 | 40.8508
2212.8281 | 122.6578 | -48.2712 | 74.1165 | -0.1403 | 0.0019119 | 0.061171 | 0.12103 | -4.2682e-05 | -0.0020722 | -0.0026704 | -0.046081 | -0.0043322 | 0.062683 | 0.059554 | -0.030636 | -0.00072207 | -0.0020295 | -0.32044 | 74.1165 | -48.4177 | 74.0799 | -43.8858 | -48.4772 | 5.5206 | -7.1365 | 74.0662 | -48.3261 | 74.1577 | -47.7631 | -48.2529 | -48.1155 | -0.14649 | 0 | -0.036621 | 4.3854 | 53.7918 | -0.20599 | 53.9383 | -0.059509 | -0.054932 | -0.050354 | 0.041199 | 0.50812 | 0.15564 | 0.01831 | 0.21057 | 0.073242 | 4.5319 | 122.4976 | 0.56305 | 122.4838 | 122.5342 | 122.3923 | 122.3877 | 122.3373 | -122.5342 | -122.4426 | 122.3511 | 122.4289 | 47.9507 | 41.1346
2213.7656 | 122.699 | -48.175 | 74.1714 | -0.12505 | -0.0010787 | 0.060957 | 0.12167 | 0.00017092 | -0.0001496 | -0.0060882 | 0.018005 | -0.002196 | 0.063538 | 0.059127 | -0.026363 | 0.00077333 | -0.00053411 | -0.31586 | 74.1806 | -48.3215 | 74.1852 | -43.6981 | -48.3902 | 5.6396 | -7.6996 | 74.0982 | -48.2712 | 74.2584 | -47.6715 | -48.1339 | -48.0286 | -0.14648 | 0.009155 | 0.013733 | 4.4769 | 53.8147 | -0.21515 | 53.9612 | -0.068665 | -0.09613 | -0.073242 | 0.086975 | 0.50354 | 0.14648 | 0.041199 | 0.24261 | 0.13733 | 4.6234 | 122.5067 | 0.59967 | 122.5296 | 122.5021 | 122.3694 | 122.3557 | 122.2733 | -122.493 | -122.4426 | 122.3602 | 122.4335 | 47.8592 | 40.4755
2214.8281 | 122.58 | -48.3078 | 74.1577 | -0.094528 | 0.0010575 | 0.060316 | 0.12274 | 0.0016663 | -0.0033538 | -0.00010676 | -0.070496 | -0.0028368 | 0.062042 | 0.064253 | -0.027859 | 0.00055973 | 0.00074769 | -0.42114 | 74.1257 | -48.4451 | 73.9838 | -44.014 | -48.587 | 5.3696 | -7.8873 | 74.1211 | -48.3444 | 74.1028 | -48.0606 | -48.4543 | -48.2208 | -0.13733 | -0.032044 | -0.17395 | 4.2938 | 53.6774 | -0.27924 | 53.8147 | -0.14191 | -0.036621 | -0.036621 | -0.054932 | 0.24719 | 0.086975 | -0.14648 | 0.1236 | -0.10986 | 4.4312 | 122.4289 | 0.28381 | 122.4472 | 122.5708 | 122.4655 | 122.4335 | 122.4289 | -122.6028 | -122.5021 | 122.2916 | 122.4106 | 47.8867 | 40.4205
2215.7656 | 122.6257 | -48.4131 | 73.9883 | -0.10216 | 0.0012711 | 0.060316 | 0.12316 | -0.0036743 | -0.004422 | -0.0026704 | -0.030823 | -0.0030506 | 0.062683 | 0.05699 | -0.030209 | 0.0018413 | -0.00074771 | -0.35248 | 73.9334 | -48.5779 | 73.9105 | -44.1513 | -48.6465 | 5.4108 | -8.1528 | 73.9334 | -48.4817 | 73.9929 | -47.9462 | -48.4406 | -48.2941 | -0.16479 | -0.054931 | -0.07782 | 4.2618 | 53.8239 | -0.23346 | 53.9886 | -0.068664 | -0.068664 | -0.054931 | 0.004578 | 0.46692 | 0.11902 | -0.027466 | 0.18768 | 0.041198 | 4.4266 | 122.4884 | 0.53558 | 122.4747 | 122.5113 | 122.4152 | 122.3465 | 122.3465 | -122.5662 | -122.4701 | 122.3236 | 122.406 | 48.0606 | 40.2603
2216.8281 | 122.6166 | -48.4817 | 73.9746 | -0.056381 | 0.0016983 | 0.059462 | 0.12274 | 0.0012391 | -0.0039948 | -0.0026704 | -0.11322 | -0.00070063 | 0.063538 | 0.065322 | -0.028286 | 0.0035503 | -0.00053411 | -0.39825 | 73.9563 | -48.6465 | 73.8098 | -44.3115 | -48.761 | 5.2322 | -8.226 | 73.9426 | -48.5687 | 73.9243 | -48.024 | -48.5092 | -48.3627 | -0.1648 | -0.01831 | -0.16479 | 4.1702 | 53.714 | -0.27924 | 53.8788 | -0.11444 | -0.086976 | -0.032043 | -0.050354 | 0.45776 | 0.11902 | -0.027466 | 0.20599 | 0.05951 | 4.335 | 122.4564 | 0.54474 | 122.493 | 122.6028 | 122.5113 | 122.438 | 122.4243 | -122.6212 | -122.5433 | 122.2916 | 122.406 | 48.0835 | 40.2557
2217.7656 | 122.6669 | -48.349 | 74.0662 | -0.10216 | 0.0019119 | 0.062025 | 0.11911 | 0.00017092 | -0.0016448 | -0.002884 | -0.0033568 | -0.0017688 | 0.061615 | 0.06404 | -0.026791 | 0.0022687 | 0.0030975 | -0.35248 | 74.0158 | -48.4451 | 74.0295 | -43.9957 | -48.5275 | 5.452 | -7.9788 | 74.0158 | -48.4039 | 74.1028 | -47.8134 | -48.2849 | -48.1659 | -0.09613 | -0.050354 | -0.036621 | 4.3533 | 53.801 | -0.17853 | 53.8971 | -0.082398 | -0.054932 | -0.050354 | 0.036621 | 0.53558 | 0.1831 | 0.064087 | 0.23804 | 0.11902 | 4.4495 | 122.4747 | 0.59052 | 122.5067 | 122.4609 | 122.4197 | 122.3648 | 122.3648 | -122.5113 | -122.4701 | 122.3785 | 122.4518 | 47.9965 | 40.3702
2218.8281 | 122.6166 | -48.2986 | 74.1577 | -0.056381 | 0.0010575 | 0.061385 | 0.12103 | -4.2682e-05 | -0.0048492 | 0.00032044 | -0.14679 | -0.0019824 | 0.064392 | 0.070662 | -0.0285 | 0.0022687 | -0.0033111 | -0.39825 | 74.1028 | -48.468 | 73.9975 | -43.9957 | -48.6008 | 5.2277 | -7.8278 | 74.1257 | -48.3627 | 74.1211 | -47.85 | -48.3582 | -48.1705 | -0.16937 | -0.054932 | -0.16022 | 4.303 | 53.5263 | -0.30212 | 53.6957 | -0.13275 | -0.064087 | -0.032044 | -0.036621 | 0.44861 | 0.12817 | -0.059509 | 0.19226 | 0.004578 | 4.4724 | 122.4655 | 0.5127 | 122.4838 | 122.5708 | 122.4884 | 122.4014 | 122.4243 | -122.6257 | -122.5204 | 122.2961 | 122.4197 | 47.9004 | 40.4709
2219.7656 | 122.5616 | -48.381 | 74.1028 | -0.10979 | 0.00084388 | 0.060103 | 0.11996 | -0.00046988 | -0.0024994 | -0.00053396 | -0.036926 | -0.0030506 | 0.06482 | 0.063185 | -0.027218 | -8.1274e-05 | 0.0028839 | -0.44403 | 74.0433 | -48.4955 | 73.9105 | -44.1193 | -48.6191 | 5.191 | -7.7866 | 74.057 | -48.4268 | 74.0112 | -47.9095 | -48.3994 | -48.2712 | -0.11444 | -0.059509 | -0.19226 | 4.2618 | 53.5721 | -0.23804 | 53.6865 | -0.1236 | -0.045777 | -0.045776 | -0.091553 | 0.4715 | 0.10986 | -0.018311 | 0.15564 | 0.027466 | 4.3762 | 122.406 | 0.51727 | 122.438 | 122.5388 | 122.4838 | 122.4243 | 122.438 | -122.5983 | -122.5296 | 122.2916 | 122.3923 | 47.937 | 40.5945
2220.8281 | 122.6074 | -48.2117 | 74.2126 | -0.094528 | 0.00020288 | 0.059889 | 0.11996 | 0.0061523 | -0.001004 | 0.00032044 | -0.09491 | -0.0043322 | 0.063111 | 0.06169 | -0.027645 | 0.00034613 | -0.00010671 | -0.45776 | 74.2126 | -48.3902 | 74.0753 | -43.927 | -48.4817 | 5.246 | -7.6309 | 74.1714 | -48.2986 | 74.1898 | -47.7448 | -48.2346 | -48.0881 | -0.17853 | 0 | -0.13733 | 4.2847 | 53.4576 | -0.27008 | 53.6362 | -0.091552 | -0.086975 | -0.041198 | -0.022888 | 0.46692 | 0.1236 | -0.022888 | 0.21057 | 0.064087 | 4.4632 | 122.4655 | 0.55389 | 122.4884 | 122.6028 | 122.4701 | 122.4243 | 122.3831 | -122.6028 | -122.5113 | 122.287 | 122.4014 | 47.7539 | 40.5807
2221.7656 | 122.5983 | -48.2254 | 74.2264 | -0.010605 | 0.0025529 | 0.060957 | 0.12017 | 0.0023071 | 0.0013458 | -0.001175 | 0.0057984 | -0.002196 | 0.062256 | 0.053786 | -0.027004 | 0.0016277 | 0.0041657 | -0.41657 | 74.1852 | -48.3398 | 74.1165 | -43.8675 | -48.4039 | 5.3925 | -7.6492 | 74.1486 | -48.262 | 74.1898 | -47.731 | -48.2162 | -48.0789 | -0.11444 | -0.041198 | -0.10986 | 4.3579 | 53.6179 | -0.17853 | 53.7323 | -0.064087 | -0.036621 | -0.077819 | -0.036621 | 0.49439 | 0.14648 | 0.009155 | 0.18311 | 0.045776 | 4.4724 | 122.4564 | 0.53101 | 122.4518 | 122.525 | 122.4106 | 122.4106 | 122.374 | -122.5662 | -122.4884 | 122.3419 | 122.4152 | 47.8088 | 40.5762
2222.8281 | 122.6166 | -48.1384 | 74.2859 | -0.06401 | 0.00063028 | 0.060744 | 0.12167 | 0.0027343 | -0.006131 | -0.001175 | -0.085754 | -0.0030506 | 0.063538 | 0.060836 | -0.027859 | 0.0012005 | -0.00032051 | -0.40741 | 74.2767 | -48.3078 | 74.1623 | -43.7347 | -48.4314 | 5.4337 | -7.3334 | 74.2493 | -48.2025 | 74.2813 | -47.6578 | -48.1705 | -48.0011 | -0.16937 | -0.009156 | -0.1236 | 4.4037 | 53.5721 | -0.29297 | 53.7415 | -0.1236 | -0.064087 | -0.036621 | -0.004578 | 0.48065 | 0.13733 | -0.032043 | 0.20142 | 0.032044 | 4.5731 | 122.4701 | 0.54474 | 122.4838 | 122.5845 | 122.4518 | 122.4152 | 122.3877 | -122.5937 | -122.4884 | 122.3007 | 122.4197 | 47.731 | 40.8051
2223.7656 | 122.6028 | -48.1476 | 74.2859 | -0.056381 | 0.00063028 | 0.061812 | 0.12103 | 0.0033753 | -0.0014312 | -0.00096136 | -0.064392 | -0.0019824 | 0.064606 | 0.063613 | -0.028286 | 0.0012005 | 0.0033111 | -0.37079 | 74.3042 | -48.2941 | 74.1028 | -43.7897 | -48.436 | 5.3604 | -7.3746 | 74.2355 | -48.2162 | 74.2355 | -47.699 | -48.1979 | -48.0469 | -0.14648 | 0.01831 | -0.18311 | 4.3579 | 53.508 | -0.28839 | 53.6545 | -0.14191 | -0.068665 | -0.050354 | -0.050354 | 0.44861 | 0.10071 | -0.050354 | 0.16937 | 0.018311 | 4.5044 | 122.3969 | 0.51727 | 122.4518 | 122.5983 | 122.4518 | 122.4518 | 122.3831 | -122.58 | -122.5021 | 122.2504 | 122.3831 | 47.7768 | 40.773
2224.8281 | 122.5937 | -48.1796 | 74.2813 | -0.17082 | -0.00086512 | 0.059676 | 0.12081 | 0.00081172 | -0.0035674 | -0.002884 | -0.021667 | -0.0036914 | 0.064392 | 0.061904 | -0.027218 | 0.0018413 | 0.0013885 | -0.29755 | 74.2859 | -48.3444 | 74.0845 | -43.7805 | -48.4634 | 5.4382 | -7.2556 | 74.2767 | -48.2117 | 74.2126 | -47.7081 | -48.1613 | -48.0469 | -0.16479 | 0.004578 | -0.19684 | 4.3991 | 53.6179 | -0.28381 | 53.7827 | -0.11902 | -0.032044 | -0.004578 | -0.068665 | 0.4715 | 0.13275 | 0.01831 | 0.16479 | 0.050354 | 4.5639 | 122.4289 | 0.50354 | 122.4243 | 122.6303 | 122.4884 | 122.4655 | 122.4564 | -122.6257 | -122.493 | 122.2641 | 122.3923 | 47.8821 | 40.9241
2225.7656 | 122.6349 | -48.0698 | 74.3958 | -0.07164 | -0.00065152 | 0.061385 | 0.12039 | 0.0038025 | -0.0031402 | -0.0013886 | -0.10101 | -0.0015552 | 0.063324 | 0.053359 | -0.028072 | 0.0031231 | 0.00032049 | -0.27008 | 74.3774 | -48.2117 | 74.2493 | -43.6661 | -48.3353 | 5.278 | -7.2922 | 74.3088 | -48.1247 | 74.3546 | -47.58 | -48.0927 | -47.9233 | -0.14191 | -0.018311 | -0.14648 | 4.4037 | 53.3478 | -0.2655 | 53.4897 | -0.1236 | -0.054932 | -0.086975 | -0.041199 | 0.48981 | 0.14648 | -0.022888 | 0.20142 | 0.032044 | 4.5456 | 122.4609 | 0.54474 | 122.4792 | 122.5891 | 122.4335 | 122.4472 | 122.3785 | -122.6074 | -122.5204 | 122.319 | 122.4243 | 47.7997 | 40.7776
2226.8281 | 122.5983 | -48.056 | 74.4049 | -0.0029755 | 0.00020288 | 0.060744 | 0.1206 | -0.0021789 | -0.0031402 | -0.0033112 | 0.0027466 | -0.002196 | 0.061615 | 0.061476 | -0.027431 | -0.0011493 | 0.00053409 | -0.37079 | 74.382 | -48.23 | 74.1852 | -43.721 | -48.349 | 5.2689 | -7.3837 | 74.35 | -48.1339 | 74.3362 | -47.7722 | -48.1155 | -47.9324 | -0.17395 | -0.022888 | -0.21973 | 4.335 | 53.3249 | -0.29297 | 53.4988 | -0.11902 | -0.07782 | -0.054931 | -0.068664 | 0.28381 | 0.1236 | -0.05951 | 0.20142 | 0.01831 | 4.509 | 122.4152 | 0.36163 | 122.4701 | 122.612 | 122.4838 | 122.438 | 122.406 | -122.6349 | -122.5388 | 122.2412 | 122.3923 | 47.6852 | 40.6723
2227.7656 | 122.6166 | -48.1064 | 74.3546 | -0.086899 | -1.0718e-05 | 0.061385 | 0.12124 | 0.0042297 | -0.0037812 | -0.00010676 | -0.073547 | -0.0017688 | 0.06482 | 0.056136 | -0.029568 | 0.0031231 | 0.00053409 | -0.35248 | 74.3866 | -48.2162 | 74.2081 | -43.7485 | -48.3353 | 5.191 | -7.2739 | 74.3179 | -48.1247 | 74.3317 | -47.6074 | -48.1018 | -47.9553 | -0.10986 | 0.032044 | -0.14648 | 4.3579 | 53.2974 | -0.22888 | 53.4073 | -0.11902 | -0.018311 | -0.036621 | -0.022888 | 0.49896 | 0.15106 | 0.004577 | 0.16937 | 0.022888 | 4.4678 | 122.4243 | 0.51727 | 122.4564 | 122.6028 | 122.4426 | 122.493 | 122.4243 | -122.5708 | -122.4792 | 122.3145 | 122.438 | 47.7539 | 40.8325
2228.8281 | 122.5525 | -48.2208 | 74.2538 | -0.20134 | 0.0021255 | 0.061598 | 0.12167 | 0.0018799 | -0.0024994 | 0.00010684 | -0.070496 | -0.0030506 | 0.065247 | 0.062117 | -0.026791 | 0.0026959 | 0.0033111 | -0.39825 | 74.2035 | -48.3673 | 74.0341 | -43.9957 | -48.5779 | 4.985 | -7.4341 | 74.1852 | -48.3078 | 74.1531 | -47.7814 | -48.3215 | -48.1384 | -0.14649 | -0.050354 | -0.21973 | 4.2252 | 53.2059 | -0.35706 | 53.3524 | -0.21057 | -0.086975 | -0.068664 | -0.10071 | 0.43945 | 0.082397 | -0.10071 | 0.16937 | -0.013733 | 4.3716 | 122.4014 | 0.52643 | 122.4609 | 122.5708 | 122.493 | 122.4243 | 122.406 | -122.6212 | -122.5616 | 122.2549 | 122.374 | 47.8226 | 40.7867
2229.7656 | 122.6303 | -48.1339 | 74.2813 | -0.07164 | 0.0010575 | 0.058821 | 0.11996 | 0.00017092 | -0.0052764 | -0.0018158 | 0.014954 | -0.002196 | 0.063965 | 0.056563 | -0.028713 | 0.0022687 | 0.0022431 | -0.34332 | 74.2767 | -48.2666 | 74.1577 | -43.7622 | -48.6145 | 4.9347 | -7.2556 | 74.2859 | -48.175 | 74.2813 | -47.644 | -48.1567 | -48.0011 | -0.13275 | -0.004578 | -0.1236 | 4.3716 | 53.0685 | -0.48065 | 53.2013 | -0.3479 | -0.041199 | 0.004578 | 0 | 0.48981 | 0.13275 | -0.022888 | 0.17395 | 0.018311 | 4.5044 | 122.4243 | 0.53101 | 122.4564 | 122.5433 | 122.4609 | 122.4106 | 122.4197 | -122.5479 | -122.4564 | 122.2916 | 122.4152 | 47.7905 | 40.8783
2230.8281 | 122.7264 | -48.0652 | 74.4049 | -0.13267 | -0.0012923 | 0.061598 | 0.11975 | 0.00038452 | -0.0039948 | -0.0018158 | -0.036926 | -0.002196 | 0.062683 | 0.065322 | -0.028072 | 0.0018413 | -0.00010671 | -0.34332 | 74.35 | -48.2071 | 74.2493 | -43.721 | -48.3398 | 5.1407 | -7.2647 | 74.3362 | -48.1293 | 74.3683 | -47.5616 | -48.0377 | -47.937 | -0.14191 | -0.054931 | -0.15564 | 4.3442 | 53.2059 | -0.27466 | 53.3478 | -0.13275 | -0.064086 | -0.068664 | -0.036621 | 0.50354 | 0.12817 | 0.027466 | 0.19226 | 0.091552 | 4.4861 | 122.4564 | 0.56763 | 122.4976 | 122.5571 | 122.4655 | 122.4152 | 122.4014 | -122.612 | -122.5342 | 122.3145 | 122.4335 | 47.7219 | 40.8005
2231.7656 | 122.58 | -47.9187 | 74.5377 | -0.12505 | 0.0025529 | 0.061171 | 0.11975 | 0.0012391 | -0.0037812 | 0.0018158 | -0.088806 | -0.002196 | 0.065033 | 0.061476 | -0.027004 | 0.0035503 | -0.00074771 | -0.30212 | 74.4965 | -48.0698 | 74.3546 | -43.5333 | -48.2162 | 5.1773 | -7.3105 | 74.4827 | -48.0057 | 74.469 | -47.4564 | -47.9736 | -47.7997 | -0.15106 | -0.041199 | -0.18311 | 4.3854 | 53.096 | -0.29755 | 53.2471 | -0.14648 | -0.086975 | -0.054932 | -0.068665 | 0.46234 | 0.11902 | -0.054932 | 0.20599 | 0.032043 | 4.5364 | 122.4243 | 0.54932 | 122.4747 | 122.5662 | 122.4884 | 122.4152 | 122.4014 | -122.6074 | -122.5433 | 122.2733 | 122.3877 | 47.6166 | 40.6082
2232.8281 | 122.644 | -47.9782 | 74.4781 | -0.018234 | 0.00041648 | 0.060957 | 0.12081 | -0.00046988 | 0.0002778 | 0.00032044 | -0.015564 | -0.0017688 | 0.063965 | 0.057204 | -0.02914 | 0.0024823 | 0.0024567 | -0.31128 | 74.3958 | -48.1796 | 74.2493 | -43.7256 | -48.2758 | 5.3146 | -7.7454 | 74.4003 | -48.0698 | 74.3866 | -47.4792 | -48.0148 | -47.8363 | -0.20142 | -0.082397 | -0.22888 | 4.2526 | 53.2928 | -0.29755 | 53.4943 | -0.096131 | -0.091553 | -0.077819 | -0.091552 | 0.49896 | 0.14191 | -0.036622 | 0.23346 | 0.054931 | 4.454 | 122.4289 | 0.59052 | 122.4564 | 122.5754 | 122.4701 | 122.374 | 122.3785 | -122.6578 | -122.5479 | 122.2275 | 122.3648 | 47.6669 | 40.2328
2233.7656 | 122.6074 | -47.9965 | 74.4461 | -0.10216 | -0.00043792 | 0.063094 | 0.12039 | -0.00089728 | -0.004422 | -0.0016022 | -0.049133 | -0.0019824 | 0.06482 | 0.057631 | -0.028072 | 0.00098693 | 0.0018159 | -0.29297 | 74.4736 | -48.111 | 74.3088 | -43.6386 | -48.2666 | 4.9576 | -7.7408 | 74.4049 | -48.0377 | 74.4324 | -47.4792 | -48.0103 | -47.8317 | -0.11444 | 0.027466 | -0.13733 | 4.3579 | 52.9541 | -0.27008 | 53.0685 | -0.15564 | -0.041199 | -0.041199 | -0.013733 | 0.51727 | 0.16479 | -0.013733 | 0.20599 | 0.027466 | 4.4724 | 122.4197 | 0.55847 | 122.4701 | 122.5845 | 122.4426 | 122.4701 | 122.4014 | -122.5571 | -122.4838 | 122.3053 | 122.4289 | 47.7036 | 40.2557
2234.8281 | 122.5891 | -47.8088 | 74.6613 | -0.23186 | 0.0027665 | 0.063734 | 0.12167 | 0.0052979 | -0.0033538 | -0.0020294 | -0.046081 | -0.0034778 | 0.064606 | 0.060195 | -0.028072 | 0.0031231 | 0.0022431 | -0.38452 | 74.5926 | -47.9828 | 74.437 | -43.5059 | -48.1339 | 4.8065 | -7.5851 | 74.5926 | -47.8775 | 74.5972 | -47.3694 | -47.8592 | -47.6898 | -0.17395 | -0.068665 | -0.2243 | 4.303 | 52.6154 | -0.32501 | 52.7893 | -0.15106 | -0.068664 | -0.068665 | -0.064087 | 0.43945 | 0.11902 | -0.050354 | 0.18768 | 0.01831 | 4.4769 | 122.4197 | 0.50812 | 122.4747 | 122.5754 | 122.4701 | 122.4014 | 122.4014 | -122.644 | -122.5388 | 122.2458 | 122.406 | 47.4243 | 40.2237
2235.7656 | 122.5754 | -47.8134 | 74.6338 | -0.10216 | 0.00084388 | 0.063948 | 0.11889 | 0.0061523 | -0.004422 | -0.0069428 | -0.00030524 | -0.0030506 | 0.062042 | 0.06169 | -0.026577 | -8.1274e-05 | 0.00096129 | -0.33875 | 74.6246 | -47.9828 | 74.6201 | -43.2861 | -48.23 | 4.9164 | -7.5348 | 74.6201 | -47.9004 | 74.5789 | -47.3694 | -47.8729 | -47.612 | -0.16937 | -0.009155 | -0.013733 | 4.5273 | 52.7298 | -0.41656 | 52.8992 | -0.24719 | -0.086975 | -0.013733 | -0.054932 | 0.44403 | 0.20142 | -0.059509 | 0.28839 | 0.027466 | 4.6967 | 122.6028 | 0.53101 | 122.4792 | 122.6074 | 122.5204 | 122.4381 | 122.4335 | -122.6166 | -122.5342 | 122.4335 | 122.3923 | 47.4747 | 40.2786
2236.8281 | 122.6578 | -47.7173 | 74.6704 | -0.16319 | -0.00043792 | 0.063307 | 0.12017 | -0.00025628 | -0.0042084 | 0.00074764 | -0.030823 | -0.0032642 | 0.064606 | 0.058699 | -0.029354 | -8.1274e-05 | 0.00096129 | -0.28839 | 74.6841 | -47.8592 | 74.5285 | -43.3182 | -48.0469 | 5.1819 | -7.2098 | 74.6567 | -47.7631 | 74.707 | -47.2046 | -47.7081 | -47.5754 | -0.14191 | 0.013733 | -0.14191 | 4.3991 | 52.8992 | -0.32959 | 53.0411 | -0.18768 | -0.045777 | -0.013733 | 0.036621 | 0.51269 | 0.14191 | 0.009155 | 0.18768 | 0.054932 | 4.541 | 122.3877 | 0.55847 | 122.4701 | 122.5433 | 122.4197 | 122.4014 | 122.374 | -122.5296 | -122.4335 | 122.2458 | 122.4243 | 47.4289 | 40.5075
2237.7656 | 122.6669 | -47.7493 | 74.6658 | -0.12505 | 0.00020288 | 0.061385 | 0.12081 | 0.0027343 | -0.0020722 | -0.0035248 | -0.030823 | -0.0030506 | 0.065674 | 0.056349 | -0.030849 | 0.0012005 | 0.0020295 | -0.32044 | 74.6475 | -47.9141 | 74.4736 | -43.4097 | -48.1018 | 5.2597 | -7.3105 | 74.588 | -47.8363 | 74.6613 | -47.287 | -47.7768 | -47.612 | -0.16479 | -0.018311 | -0.19226 | 4.3396 | 53.009 | -0.35248 | 53.1738 | -0.18768 | -0.086975 | -0.07782 | -0.004578 | 0.46234 | 0.13733 | -0.027465 | 0.2243 | 0.05951 | 4.5044 | 122.3877 | 0.54932 | 122.4976 | 122.5616 | 122.4243 | 122.3969 | 122.3373 | -122.58 | -122.5021 | 122.2229 | 122.4106 | 47.4289 | 40.4388
2238.8281 | 122.6028 | -47.7814 | 74.6338 | -0.10216 | -0.00022432 | 0.063521 | 0.1206 | 0.0014527 | -0.0024994 | 0.001175 | -0.06134 | -0.0024096 | 0.065247 | 0.06169 | -0.02914 | -0.0011493 | -0.00032051 | -0.33875 | 74.6521 | -47.9279 | 74.4415 | -43.5196 | -48.1659 | 5.1819 | -7.4295 | 74.5972 | -47.8683 | 74.6796 | -47.4152 | -47.8683 | -47.6578 | -0.14648 | 0.018311 | -0.19226 | 4.2618 | 52.9633 | -0.38452 | 53.1097 | -0.23804 | -0.086975 | -0.036621 | 0.045776 | 0.36621 | 0.1236 | -0.086975 | 0.21057 | 0 | 4.4083 | 122.3694 | 0.45319 | 122.5479 | 122.58 | 122.4655 | 122.4335 | 122.3785 | -122.5616 | -122.5021 | 122.2229 | 122.4609 | 47.4426 | 40.3519
2239.7656 | 122.5525 | -47.8683 | 74.6063 | -0.1403 | -0.00022432 | 0.061171 | 0.12188 | 0.00017092 | -0.0024994 | -0.00096136 | -0.049133 | -0.0024096 | 0.06482 | 0.058272 | -0.030422 | 0.0016277 | -0.0018157 | -0.32501 | 74.6063 | -48.0148 | 74.4003 | -43.5379 | -48.1796 | 5.3741 | -7.2784 | 74.556 | -47.9141 | 74.5102 | -47.4152 | -47.9279 | -47.7859 | -0.14648 | 0 | -0.20599 | 4.3304 | 53.2425 | -0.31128 | 53.389 | -0.16479 | -0.045777 | -0.050354 | -0.09613 | 0.45319 | 0.082397 | -0.059509 | 0.12817 | -0.013732 | 4.4769 | 122.4152 | 0.49896 | 122.4243 | 122.6212 | 122.4701 | 122.4747 | 122.4243 | -122.6212 | -122.5204 | 122.2687 | 122.3785 | 47.5433 | 40.5899
2240.8281 | 122.5845 | -47.8683 | 74.5789 | -0.094528 | 0.00063028 | 0.063948 | 0.12103 | 0.0057251 | -0.0037812 | -0.0037384 | -0.085754 | -0.0015552 | 0.062683 | 0.059127 | -0.029568 | -8.1274e-05 | 0.0018159 | -0.3479 | 74.5834 | -48.0331 | 74.3408 | -43.5974 | -48.2346 | 5.2734 | -7.3837 | 74.5331 | -47.937 | 74.4965 | -47.4838 | -47.905 | -47.731 | -0.16479 | 0.004578 | -0.23804 | 4.2709 | 53.1418 | -0.36621 | 53.3066 | -0.20142 | -0.068665 | -0.045776 | -0.082397 | 0.38452 | 0.13733 | -0.036621 | 0.20599 | 0.032044 | 4.4357 | 122.374 | 0.45319 | 122.4335 | 122.6166 | 122.4701 | 122.4518 | 122.4014 | -122.612 | -122.5159 | 122.2092 | 122.3648 | 47.5204 | 40.4846
2241.7656 | 122.5204 | -48.0103 | 74.4461 | -0.041122 | 0.0012711 | 0.063094 | 0.12252 | 0.0027343 | -0.0014312 | -0.0013886 | -0.049133 | -0.0028368 | 0.06546 | 0.059767 | -0.025936 | 0.0024823 | -0.0013885 | -0.33875 | 74.4644 | -48.1522 | 74.231 | -43.7759 | -48.3444 | 5.1773 | -7.4661 | 74.4232 | -48.0881 | 74.3362 | -47.58 | -48.1155 | -47.9416 | -0.14191 | 0.018311 | -0.21515 | 4.2343 | 53.1876 | -0.33417 | 53.3295 | -0.19226 | -0.07782 | -0.022888 | -0.10986 | 0.4303 | 0.068665 | -0.10529 | 0.14648 | -0.027466 | 4.3762 | 122.3831 | 0.50812 | 122.4243 | 122.6166 | 122.5113 | 122.4747 | 122.4335 | -122.5983 | -122.5342 | 122.2412 | 122.3465 | 47.6715 | 40.5441
2242.8281 | 122.6807 | -47.9141 | 74.4598 | -0.11742 | 0.0021255 | 0.062453 | 0.11953 | 0.0033753 | -0.0029266 | -0.00074776 | -0.021667 | -0.0032642 | 0.065247 | 0.060195 | -0.0285 | 0.0024823 | 0.00096129 | -0.2655 | 74.4873 | -48.0606 | 74.3408 | -43.6066 | -48.2346 | 5.1727 | -7.2098 | 74.469 | -47.9828 | 74.4965 | -47.3557 | -47.9828 | -47.731 | -0.14648 | 0.027466 | -0.11902 | 4.3076 | 53.0869 | -0.32043 | 53.2333 | -0.17395 | -0.068664 | 0.009155 | 0.036621 | 0.55847 | 0.18311 | -0.068664 | 0.25177 | 0 | 4.454 | 122.4014 | 0.62714 | 122.4792 | 122.5479 | 122.4518 | 122.4014 | 122.3831 | -122.5204 | -122.4426 | 122.2549 | 122.4106 | 47.6486 | 40.7043
2243.7656 | 122.5845 | -49.2188 | 73.2147 | -0.31578 | 0.0019119 | 0.06053 | 0.12167 | 0.00081172 | -0.0029266 | -0.0020294 | -0.036926 | -0.0017688 | 0.063111 | 0.062545 | -0.028927 | 0.0018413 | 0.0016021 | -0.26093 | 73.1552 | -49.4247 | 72.9355 | -44.8837 | -49.6399 | 5.0034 | -7.5256 | 73.1232 | -49.3423 | 73.1415 | -48.7473 | -49.324 | -49.1135 | -0.20599 | -0.05951 | -0.27924 | 4.335 | 54.2221 | -0.42114 | 54.4281 | -0.21515 | -0.1236 | -0.091553 | -0.073243 | 0.4715 | 0.10529 | -0.10529 | 0.22888 | 0.01831 | 4.541 | 122.3602 | 0.59509 | 122.4838 | 122.58 | 122.4655 | 122.374 | 122.3419 | -122.6395 | -122.5571 | 122.1542 | 122.3602 | 48.9578 | 41.6931
2244.8281 | 122.7081 | -49.6445 | 72.6837 | -0.1403 | -0.00043792 | 0.065443 | 0.12188 | 0.0070069 | -0.0031402 | -0.002884 | 0.0057984 | -0.0032642 | 0.065674 | 0.067885 | -0.029781 | 0.0020551 | 0.0026703 | -0.44403 | 72.7066 | -49.8322 | 72.6562 | -45.0119 | -49.91 | 4.8111 | -7.6309 | 72.6059 | -49.7681 | 72.7798 | -49.0768 | -49.6262 | -49.4522 | -0.18768 | 0.022888 | -0.027466 | 4.6326 | 54.4556 | -0.2655 | 54.6432 | -0.07782 | -0.1236 | -0.07782 | 0.09613 | 0.56763 | 0.19226 | 0.01831 | 0.31586 | 0.14191 | 4.8203 | 122.4884 | 0.69122 | 122.5479 | 122.5388 | 122.374 | 122.3511 | 122.2504 | -122.5159 | -122.4518 | 122.3007 | 122.4243 | 49.2004 | 42.0135
2245.7656 | 122.5754 | -49.9237 | 72.5281 | -0.086899 | -0.00022432 | 0.063734 | 0.12316 | 0.00038452 | -0.004422 | -0.0013886 | -0.064392 | -0.0028368 | 0.061829 | 0.06404 | -0.029568 | 0.0018413 | -0.0011749 | -0.51727 | 72.5143 | -50.0656 | 72.345 | -45.2957 | -50.2167 | 4.5456 | -7.6126 | 72.496 | -49.9695 | 72.4503 | -49.4202 | -50.0015 | -49.7955 | -0.14191 | -0.013733 | -0.1831 | 4.628 | 54.4693 | -0.29297 | 54.6112 | -0.15106 | -0.045776 | -0.032043 | -0.07782 | 0.50354 | 0.12817 | -0.07782 | 0.17395 | -0.032044 | 4.7699 | 122.4106 | 0.54932 | 122.4197 | 122.58 | 122.4655 | 122.438 | 122.4197 | -122.5937 | -122.4976 | 122.2687 | 122.374 | 49.4064 | 42.3111
2246.7656 | 122.7219 | -50.1343 | 72.2443 | -0.12505 | 0.00063028 | 0.061171 | 0.11953 | -0.0028199 | -0.0018586 | -0.002243 | 0.072937 | -0.0047594 | 0.063751 | 0.053145 | -0.028286 | -0.00072207 | 0.0035247 | -0.49896 | 72.2168 | -50.3174 | 72.1436 | -45.4239 | -50.3952 | 4.8203 | -7.3608 | 72.1664 | -50.2121 | 72.2809 | -49.5209 | -50.061 | -49.9512 | -0.18311 | -0.027466 | -0.10071 | 4.7104 | 54.9545 | -0.26093 | 55.1376 | -0.07782 | -0.07782 | -0.07782 | 0.036621 | 0.6134 | 0.1831 | 0.073242 | 0.26093 | 0.15106 | 4.8935 | 122.4609 | 0.69122 | 122.493 | 122.5342 | 122.3785 | 122.3511 | 122.3007 | -122.5616 | -122.4564 | 122.2778 | 122.4152 | 49.6353 | 42.7734
2247.8281 | 122.5708 | -50.3952 | 72.0337 | -0.1403 | 0.0010575 | 0.06288 | 0.12146 | -0.00068368 | -0.0033538 | -0.0037384 | -0.085754 | -0.0043322 | 0.064392 | 0.064467 | -0.031063 | 0.00098693 | -0.0013885 | -0.54932 | 72.0337 | -50.5646 | 71.8414 | -45.7581 | -50.7477 | 4.8019 | -7.6126 | 71.9971 | -50.473 | 71.9742 | -49.91 | -50.4913 | -50.2899 | -0.16937 | 0 | -0.19226 | 4.6371 | 55.1971 | -0.35248 | 55.3665 | -0.18311 | -0.077819 | -0.036621 | -0.059509 | 0.48523 | 0.10529 | -0.09613 | 0.1831 | -0.018311 | 4.8065 | 122.406 | 0.56305 | 122.4472 | 122.5983 | 122.4701 | 122.4289 | 122.3923 | -122.5983 | -122.5067 | 122.2366 | 122.3694 | 49.8459 | 42.7826
2248.7656 | 122.5983 | -50.5692 | 71.8826 | -0.12505 | 0.00084388 | 0.06288 | 0.12231 | -0.00046988 | -0.0020722 | 0.0030976 | -0.10406 | -0.0032642 | 0.06247 | 0.065749 | -0.028286 | 0.0020551 | 0.0035247 | -0.58594 | 71.8735 | -50.7202 | 71.4752 | -46.0968 | -50.4364 | 4.8019 | -7.5668 | 71.8689 | -50.6149 | 71.846 | -50.0198 | -50.6149 | -50.441 | -0.15106 | -0.009155 | -0.40741 | 4.4724 | 55.3711 | 0.13275 | 55.5222 | 0.28381 | -0.045776 | -0.013733 | -0.036621 | 0.54932 | 0.12817 | -0.045776 | 0.17395 | 0 | 4.6234 | 122.1954 | 0.59509 | 122.4609 | 122.5937 | 122.4838 | 122.4426 | 122.438 | -122.6028 | -122.4976 | 122.0444 | 122.4152 | 49.9832 | 43.0023
2249.8281 | 122.644 | -50.5646 | 71.8002 | -0.1403 | -0.00043792 | 0.063094 | 0.12274 | -0.00046988 | -0.0046356 | -0.0035248 | -0.04303 | -0.001128 | 0.063965 | 0.058699 | -0.028286 | 0.0018413 | 0.0026703 | -0.59509 | 71.7957 | -50.7797 | 71.6629 | -45.9503 | -51.0132 | 4.747 | -7.5119 | 71.759 | -50.6561 | 71.8185 | -50.0381 | -50.6058 | -50.4044 | -0.21515 | -0.004578 | -0.13733 | 4.6143 | 55.3116 | -0.44861 | 55.5267 | -0.23346 | -0.091553 | -0.041199 | 0.01831 | 0.52643 | 0.16022 | -0.041199 | 0.25177 | 0.050354 | 4.8294 | 122.4426 | 0.61798 | 122.4747 | 122.5754 | 122.4152 | 122.3602 | 122.3236 | -122.58 | -122.4564 | 122.2275 | 122.3831 | 49.9695 | 43.0527
2250.7656 | 122.6166 | -50.7202 | 71.6995 | -0.13267 | -0.0012923 | 0.061812 | 0.12252 | -0.0023925 | -0.0042084 | -0.00010676 | -0.046081 | -0.0028368 | 0.064179 | 0.061263 | -0.028286 | 0.00055973 | 0.0045929 | -0.60883 | 71.6721 | -50.8896 | 71.5027 | -45.9732 | -51.0544 | 4.5731 | -7.4661 | 71.6675 | -50.7935 | 71.6995 | -50.1572 | -50.7614 | -50.5508 | -0.16937 | -0.027466 | -0.19684 | 4.747 | 55.2933 | -0.33417 | 55.4626 | -0.16479 | -0.073242 | -0.032044 | 0 | 0.56305 | 0.16937 | -0.041199 | 0.24261 | 0.032043 | 4.9164 | 122.3923 | 0.63629 | 122.493 | 122.5616 | 122.4609 | 122.3923 | 122.3877 | -122.5891 | -122.493 | 122.2229 | 122.4197 | 50.1114 | 43.2541
2251.8438 | 122.731 | -50.8163 | 71.5759 | -0.07164 | -0.00065152 | 0.061171 | 0.12103 | -0.0060241 | -0.0029266 | -0.00053396 | 0.0088502 | -0.0060412 | 0.063538 | 0.055281 | -0.030422 | -8.1274e-05 | 0.0030975 | -0.46692 | 71.5851 | -50.9354 | 71.3196 | -46.0052 | -50.885 | 4.6875 | -7.0908 | 71.5164 | -50.853 | 71.6446 | -50.1297 | -50.6882 | -50.5737 | -0.11902 | 0.009155 | -0.25635 | 4.8111 | 55.5038 | -0.068665 | 55.6229 | 0.050354 | -0.036621 | -0.05951 | 0.068664 | 0.68664 | 0.24262 | 0.12817 | 0.27924 | 0.1648 | 4.9301 | 122.2549 | 0.72327 | 122.4976 | 122.5204 | 122.3694 | 122.4014 | 122.3328 | -122.5113 | -122.4289 | 122.1359 | 122.4609 | 50.3494 | 43.7256
2252.7656 | 122.5891 | -50.7843 | 71.6675 | -0.07164 | 0.0019119 | 0.060957 | 0.12445 | 0.0061523 | -0.006131 | -0.0024566 | -0.046081 | -0.002196 | 0.064179 | 0.058913 | -0.029995 | 0.0026959 | 0.00074769 | -0.56305 | 71.6125 | -50.9811 | 71.5897 | -45.6345 | -50.9949 | 4.509 | -7.3425 | 71.6354 | -50.8438 | 71.5897 | -50.2716 | -50.8347 | -50.6607 | -0.19684 | -0.054931 | -0.077819 | 5.1498 | 55.2933 | -0.21057 | 55.4901 | -0.013733 | -0.059509 | -0.032043 | -0.077819 | 0.5127 | 0.1236 | -0.050354 | 0.18311 | 0.009155 | 5.3467 | 122.5708 | 0.57221 | 122.4335 | 122.5937 | 122.4792 | 122.3969 | 122.4197 | -122.6486 | -122.5113 | 122.374 | 122.374 | 50.2213 | 43.4418
2253.8281 | 122.6395 | -50.9995 | 71.4111 | -0.1403 | -0.0010787 | 0.060103 | 0.12017 | -0.00089728 | -0.0029266 | -0.0041656 | 0.042419 | -0.0024096 | 0.064606 | 0.054427 | -0.030422 | -0.00072207 | -0.00074771 | -0.55847 | 71.3882 | -51.178 | 71.283 | -46.0281 | -51.3107 | 4.7562 | -7.2739 | 71.3562 | -51.059 | 71.4157 | -50.3723 | -50.9628 | -50.8163 | -0.17853 | -0.022888 | -0.12817 | 4.9713 | 55.7556 | -0.31128 | 55.9341 | -0.13275 | -0.059509 | -0.054932 | 0.004577 | 0.62714 | 0.18311 | 0.036621 | 0.24262 | 0.09613 | 5.1498 | 122.4609 | 0.68665 | 122.4747 | 122.5662 | 122.4152 | 122.3877 | 122.3557 | -122.5891 | -122.4701 | 122.2824 | 122.4152 | 50.441 | 43.7256
2254.7656 | 122.6395 | -50.8621 | 71.5897 | -0.079269 | 0.00020288 | 0.063521 | 0.12124 | -4.2682e-05 | -0.0033538 | -0.0043792 | -0.085754 | -0.0019824 | 0.064392 | 0.063613 | -0.027645 | 0.0018413 | -0.00032051 | -0.57678 | 71.5805 | -51.0178 | 71.402 | -45.7535 | -51.1734 | 4.5731 | -7.2693 | 71.553 | -50.9216 | 71.5622 | -50.2625 | -50.885 | -50.6653 | -0.15564 | -0.009156 | -0.18768 | 5.1086 | 55.4352 | -0.31128 | 55.5908 | -0.15564 | -0.059509 | -0.036621 | -0.027466 | 0.59967 | 0.19684 | -0.022888 | 0.25635 | 0.036621 | 5.2643 | 122.4197 | 0.65918 | 122.4838 | 122.5983 | 122.4747 | 122.4426 | 122.4152 | -122.6074 | -122.5113 | 122.2641 | 122.4243 | 50.2853 | 43.5928
2255.8281 | 122.6898 | -51.0956 | 71.2692 | -0.17845 | 0.0014847 | 0.063307 | 0.12252 | -0.0013245 | -0.001004 | -0.00010676 | 0.0088502 | -0.0047594 | 0.062683 | 0.058058 | -0.028713 | -8.1274e-05 | 0.0022431 | -0.49896 | 71.2326 | -51.265 | 71.2189 | -45.9686 | -51.3519 | 4.5685 | -7.1915 | 71.2006 | -51.1826 | 71.3516 | -50.4501 | -51.059 | -50.8896 | -0.16937 | -0.036621 | -0.050354 | 5.127 | 55.6641 | -0.25635 | 55.8334 | -0.086975 | -0.086975 | -0.068664 | 0.082398 | 0.64545 | 0.20599 | 0.036621 | 0.29297 | 0.1236 | 5.2963 | 122.4838 | 0.73242 | 122.5342 | 122.4976 | 122.3831 | 122.3282 | 122.2961 | -122.5342 | -122.4518 | 122.3145 | 122.4472 | 50.5966 | 43.9041
2256.7656 | 122.6852 | -51.0223 | 71.3837 | -0.14793 | -0.00065152 | 0.061385 | 0.12188 | -0.0028199 | -0.0037812 | -0.001175 | 0.011902 | -0.0045458 | 0.06247 | 0.056136 | -0.028713 | 0.00034613 | -0.0026703 | -0.54932 | 71.3791 | -51.1688 | 71.2875 | -45.8267 | -51.2787 | 4.4449 | -7.2327 | 71.3562 | -51.0773 | 71.402 | -50.386 | -50.9766 | -50.8163 | -0.14648 | -0.004578 | -0.09613 | 5.1956 | 55.4672 | -0.25635 | 55.6137 | -0.10986 | -0.054932 | -0.027466 | 0.018311 | 0.63629 | 0.20599 | 0.045777 | 0.26093 | 0.10071 | 5.3421 | 122.4564 | 0.69122 | 122.4792 | 122.5479 | 122.4335 | 122.4014 | 122.3785 | -122.5525 | -122.4609 | 122.3099 | 122.4243 | 50.473 | 43.7897
2257.8281 | 122.731 | -51.416 | 70.9396 | -0.13267 | -0.00043792 | 0.063734 | 0.1221 | 0.0029479 | -0.0042084 | -0.00010676 | -0.064392 | -0.0045458 | 0.063111 | 0.06404 | -0.0285 | 0.00098693 | 0.0054475 | -0.54016 | 70.8984 | -51.6037 | 70.871 | -46.3074 | -51.6769 | 4.5685 | -7.5668 | 70.8847 | -51.503 | 71.0403 | -50.9949 | -51.2512 | -51.1047 | -0.18768 | -0.041199 | -0.068664 | 5.1086 | 55.9845 | -0.26093 | 56.1722 | -0.073242 | -0.086975 | -0.054931 | 0.10071 | 0.42114 | 0.31128 | 0.16479 | 0.39825 | 0.25177 | 5.2963 | 122.4747 | 0.50812 | 122.5433 | 122.5021 | 122.3877 | 122.3145 | 122.3007 | -122.5433 | -122.4426 | 122.287 | 122.4564 | 50.8759 | 43.8492
2258.7656 | 122.6898 | -51.4618 | 70.9076 | -0.16319 | 0.0051163 | 0.064375 | 0.12338 | 0.0025207 | -0.0016448 | -0.0016022 | -0.046081 | -0.0049732 | 0.064179 | 0.058699 | -0.028072 | 0.0024823 | -0.0030975 | -0.6546 | 70.8389 | -51.6541 | 70.8664 | -46.2799 | -51.6907 | 4.5136 | -7.3975 | 70.8618 | -51.5442 | 70.9808 | -50.798 | -51.4023 | -51.2512 | -0.19226 | -0.068665 | -0.041199 | 5.1819 | 55.9753 | -0.22888 | 56.1676 | -0.036621 | -0.082397 | -0.045777 | 0.073242 | 0.66376 | 0.21057 | 0.059509 | 0.29297 | 0.14191 | 5.3741 | 122.5204 | 0.74615 | 122.525 | 122.493 | 122.406 | 122.3007 | 122.3236 | -122.5616 | -122.4518 | 122.3282 | 122.4426 | 50.8072 | 44.0643
2259.8281 | 122.699 | -51.7136 | 70.6375 | -0.14793 | 0.00041648 | 0.063948 | 0.12039 | 0.0044433 | -0.0007904 | -0.0030976 | -0.012512 | -0.0036914 | 0.063751 | 0.059767 | -0.0285 | 0.0014141 | 0.0033111 | -0.59967 | 70.6146 | -51.8921 | 70.6192 | -46.5454 | -51.9928 | 4.4952 | -7.608 | 70.578 | -51.7731 | 70.7382 | -51.0635 | -51.6861 | -51.5076 | -0.17853 | -0.022888 | -0.01831 | 5.1682 | 56.2088 | -0.27924 | 56.3873 | -0.10071 | -0.059509 | -0.059509 | 0.10071 | 0.65002 | 0.20599 | 0.027466 | 0.2655 | 0.086975 | 5.3467 | 122.5113 | 0.70953 | 122.5113 | 122.5067 | 122.3511 | 122.3282 | 122.2916 | -122.5296 | -122.4106 | 122.3328 | 122.4518 | 51.1139 | 44.1055
2260.7656 | 122.699 | -51.7548 | 70.5963 | -0.17082 | -0.00022432 | 0.063094 | 0.12167 | -4.2682e-05 | -0.0029266 | -0.0020294 | -0.049133 | -0.0041186 | 0.061188 | 0.058058 | -0.02914 | 0.0029095 | 0.0024567 | -0.46692 | 70.61 | -51.9012 | 70.578 | -46.5134 | -51.9974 | 4.3854 | -7.4844 | 70.5963 | -51.8372 | 70.697 | -51.0818 | -51.6953 | -51.5488 | -0.14648 | 0.013733 | -0.01831 | 5.2414 | 56.1401 | -0.24261 | 56.2866 | -0.09613 | -0.082397 | 0 | 0.10071 | 0.67291 | 0.20599 | 0.05951 | 0.28839 | 0.14191 | 5.3879 | 122.4792 | 0.75531 | 122.5342 | 122.5113 | 122.4335 | 122.3648 | 122.3511 | -122.4976 | -122.4335 | 122.3328 | 122.4518 | 51.2878 | 44.2703
2261.8281 | 122.6669 | -51.7548 | 70.6055 | -0.20134 | -0.00043792 | 0.061812 | 0.12167 | 0.00081172 | 6.4004e-05 | -0.0024566 | -0.00030524 | -0.0032642 | 0.063965 | 0.058699 | -0.028072 | 0.00077333 | -0.00074771 | -0.58136 | 70.5917 | -51.9333 | 70.5002 | -46.582 | -52.0157 | 4.5044 | -8.0841 | 70.5643 | -51.8738 | 70.6421 | -51.091 | -51.709 | -51.5717 | -0.17853 | -0.013733 | -0.10529 | 5.1727 | 56.2592 | -0.26093 | 56.4377 | -0.082397 | -0.11902 | -0.041199 | 0.036621 | 0.66376 | 0.18311 | 0.045777 | 0.30212 | 0.16479 | 5.3513 | 122.4335 | 0.78278 | 122.5159 | 122.525 | 122.438 | 122.3465 | 122.319 | -122.5388 | -122.4792 | 122.2549 | 122.3969 | 51.1734 | 43.6707
2262.7656 | 122.6212 | -52.0889 | 70.3262 | -0.094528 | 0.00063028 | 0.061171 | 0.1253 | -0.0023925 | -0.0020722 | -0.0050202 | -0.11017 | -0.0024096 | 0.063751 | 0.066176 | -0.029995 | 0.0014141 | 0.0013885 | -0.65002 | 70.3217 | -52.2537 | 70.1935 | -46.9574 | -52.3819 | 4.2526 | -8.2077 | 70.3171 | -52.1439 | 70.3171 | -51.4709 | -52.0935 | -51.9287 | -0.16479 | -0.004578 | -0.13275 | 5.1315 | 56.3416 | -0.29297 | 56.5063 | -0.12817 | -0.054932 | -0.009155 | -0.009155 | 0.61798 | 0.16022 | -0.004578 | 0.21515 | 0.050354 | 5.2963 | 122.4472 | 0.67291 | 122.4609 | 122.5754 | 122.4609 | 122.4106 | 122.406 | -122.58 | -122.4701 | 122.2824 | 122.406 | 51.4389 | 43.8812
2263.8281 | 122.644 | -51.915 | 70.4636 | -0.1403 | -0.00086512 | 0.062025 | 0.12167 | 0.0020935 | -0.0022858 | -0.002243 | -0.0033568 | -0.0051868 | 0.062683 | 0.056136 | -0.027645 | 0.00077333 | 0.00053409 | -0.59967 | 70.4269 | -52.0706 | 70.3903 | -46.637 | -52.1759 | 4.2435 | -8.0109 | 70.4361 | -52.0248 | 70.5002 | -51.2466 | -51.8738 | -51.7181 | -0.15564 | -0.036621 | -0.073242 | 5.278 | 56.1584 | -0.26093 | 56.3141 | -0.10528 | -0.10986 | -0.027466 | 0.036621 | 0.66833 | 0.19684 | 0.041199 | 0.3067 | 0.15106 | 5.4337 | 122.4609 | 0.7782 | 122.525 | 122.4976 | 122.4609 | 122.3419 | 122.3511 | -122.5342 | -122.4884 | 122.3053 | 122.4152 | 51.3153 | 43.9041
2264.7656 | 122.7219 | -51.915 | 70.4132 | -0.18608 | 0.0031937 | 0.061171 | 0.12103 | 0.00017092 | -0.0035674 | -0.0018158 | -0.067444 | -0.0043322 | 0.063324 | 0.059554 | -0.030422 | 0.0014141 | -0.0016021 | -0.4715 | 70.3674 | -52.0935 | 70.3995 | -46.5683 | -52.3132 | 4.3167 | -7.8094 | 70.3995 | -52.0111 | 70.5322 | -51.2375 | -51.8875 | -51.709 | -0.17853 | -0.045776 | -0.013733 | 5.3467 | 56.2317 | -0.39825 | 56.4102 | -0.21973 | -0.09613 | -0.013733 | 0.11902 | 0.67749 | 0.20599 | 0.027466 | 0.30212 | 0.1236 | 5.5252 | 122.493 | 0.77362 | 122.5433 | 122.4609 | 122.4106 | 122.2824 | 122.3145 | -122.5067 | -122.4243 | 122.3145 | 122.4472 | 51.4435 | 44.1055
2265.8281 | 122.6669 | -52.1759 | 70.1981 | -0.10216 | 0.0023391 | 0.064162 | 0.12338 | -0.00089728 | -0.0048492 | -0.0030976 | -0.11932 | -0.0024096 | 0.06482 | 0.068099 | -0.029568 | 0.0033367 | -0.00074771 | -0.62256 | 70.2118 | -52.3727 | 70.0699 | -46.8613 | -52.5146 | 4.2618 | -7.9514 | 70.1797 | -52.2903 | 70.2393 | -51.5213 | -52.1667 | -51.9974 | -0.19684 | 0.013733 | -0.12817 | 5.3146 | 56.4377 | -0.33875 | 56.6345 | -0.14191 | -0.11444 | -0.01831 | 0.041199 | 0.6546 | 0.17853 | 0.009155 | 0.29297 | 0.1236 | 5.5115 | 122.4426 | 0.76904 | 122.5296 | 122.5845 | 122.4701 | 122.3877 | 122.3557 | -122.5708 | -122.4884 | 122.2458 | 122.4152 | 51.5533 | 44.2245
2266.7656 | 122.7539 | -52.121 | 70.2621 | -0.16319 | -0.00022432 | 0.061171 | 0.1221 | 0.0029479 | -0.0048492 | -0.003952 | -0.012512 | -0.005614 | 0.062683 | 0.058272 | -0.027859 | -0.0013629 | 0.00074769 | -0.60883 | 70.2347 | -52.2537 | 70.1889 | -46.7011 | -52.3544 | 4.3945 | -7.782 | 70.2484 | -52.1622 | 70.2759 | -51.4252 | -52.0569 | -52.0706 | -0.13275 | -0.027466 | -0.073242 | 5.4199 | 56.5155 | -0.23346 | 56.6483 | -0.10071 | -0.041198 | -0.013733 | 0.013733 | 0.6958 | 0.050354 | 0.064087 | 0.091552 | 0.10529 | 5.5527 | 122.4426 | 0.737 | 122.438 | 122.4884 | 122.4106 | 122.3557 | 122.3694 | -122.5159 | -122.4243 | 122.3099 | 122.3969 | 51.5121 | 44.339
2267.8281 | 122.7997 | -52.2446 | 70.1431 | -0.10979 | -1.0718e-05 | 0.063094 | 0.12487 | -4.2682e-05 | -0.0048492 | -0.0026704 | -0.082703 | -0.0036914 | 0.064179 | 0.063185 | -0.027645 | 0.0016277 | 0.00010689 | -0.54016 | 70.1385 | -52.4048 | 70.0882 | -46.7972 | -52.478 | 4.3579 | -7.869 | 70.0745 | -52.3087 | 70.253 | -51.6495 | -52.3865 | -52.0477 | -0.16022 | -0.004577 | -0.054931 | 5.4474 | 56.6025 | -0.23346 | 56.7627 | -0.073242 | -0.064087 | -0.068664 | 0.10986 | 0.59509 | 0.19684 | -0.14191 | 0.26093 | -0.07782 | 5.6076 | 122.493 | 0.65918 | 122.5616 | 122.5433 | 122.3831 | 122.3831 | 122.319 | -122.5479 | -122.4518 | 122.3328 | 122.4976 | 51.7044 | 44.3756
2268.7656 | 122.6624 | -52.3132 | 70.0333 | -0.16319 | 0.0027665 | 0.063094 | 0.12252 | 0.0027343 | -0.0046356 | -0.002243 | -0.039978 | -0.003905 | 0.064179 | 0.058913 | -0.030422 | 0.0014141 | 0.00010689 | -0.59509 | 70.0058 | -52.4734 | 70.0012 | -46.8338 | -52.5375 | 4.2297 | -7.8003 | 70.0012 | -52.4323 | 70.1019 | -51.6357 | -52.2629 | -52.1027 | -0.16022 | -0.027466 | -0.032043 | 5.4794 | 56.543 | -0.22431 | 56.7032 | -0.064087 | -0.11902 | -0.032043 | 0.068665 | 0.67749 | 0.21057 | 0.050354 | 0.32959 | 0.16937 | 5.6396 | 122.4747 | 0.79651 | 122.5342 | 122.4792 | 122.4335 | 122.319 | 122.3145 | -122.5067 | -122.4655 | 122.3145 | 122.4152 | 51.7181 | 44.5129
2269.8281 | 122.6715 | -52.5421 | 69.8318 | -0.10216 | -0.00043792 | 0.062025 | 0.12231 | -0.0045289 | -0.0031402 | -0.0026704 | -0.0033568 | -0.0028368 | 0.064179 | 0.055495 | -0.027645 | 0.0012005 | -0.00053411 | -0.63171 | 69.8044 | -52.7115 | 69.7357 | -47.1085 | -52.7985 | 4.1977 | -7.9651 | 69.7632 | -52.6062 | 69.873 | -51.828 | -52.4734 | -52.3407 | -0.16937 | -0.027466 | -0.09613 | 5.4337 | 56.7398 | -0.25635 | 56.9092 | -0.086975 | -0.064087 | -0.068664 | 0.041199 | 0.71411 | 0.20142 | 0.068664 | 0.2655 | 0.13275 | 5.603 | 122.4472 | 0.7782 | 122.4792 | 122.5159 | 122.3694 | 122.3465 | 122.3053 | -122.5433 | -122.438 | 122.2778 | 122.4152 | 51.9104 | 44.577
2270.7656 | 122.6624 | -52.7573 | 69.6259 | -0.11742 | 0.0012711 | 0.063307 | 0.12402 | -0.00089728 | -0.001004 | -0.0013886 | -0.036926 | -0.002196 | 0.064179 | 0.058272 | -0.029568 | 0.00034613 | -0.0020295 | -0.59052 | 69.6213 | -52.89 | 69.5435 | -47.3236 | -53.0045 | 4.1977 | -7.8186 | 69.6075 | -52.8305 | 69.6579 | -52.0615 | -52.6978 | -52.5696 | -0.13275 | -0.004577 | -0.082397 | 5.4337 | 56.955 | -0.24719 | 57.0877 | -0.11444 | -0.073242 | -0.01831 | 0.032044 | 0.6958 | 0.18768 | 0.059509 | 0.26093 | 0.13275 | 5.5664 | 122.4335 | 0.76904 | 122.4884 | 122.5113 | 122.438 | 122.3785 | 122.3648 | -122.5159 | -122.4564 | 122.3007 | 122.4152 | 52.1667 | 44.9387
2271.8281 | 122.7081 | -53.009 | 69.3512 | -0.06401 | 0.00020288 | 0.064162 | 0.12252 | 0.0018799 | -0.0022858 | -0.0033112 | -0.058289 | -0.0045458 | 0.061615 | 0.059767 | -0.0285 | 0.0016277 | -0.00053411 | -0.6134 | 69.3192 | -53.2013 | 69.3283 | -47.5342 | -53.2425 | 4.1016 | -7.6904 | 69.3008 | -53.0777 | 69.4473 | -52.2812 | -52.9449 | -52.7573 | -0.19226 | -0.032043 | -0.022888 | 5.4749 | 57.1106 | -0.23346 | 57.3029 | -0.041199 | -0.068665 | -0.050354 | 0.096131 | 0.72784 | 0.25177 | 0.064087 | 0.32043 | 0.13275 | 5.6671 | 122.5296 | 0.79651 | 122.525 | 122.5204 | 122.3785 | 122.3282 | 122.3099 | -122.5525 | -122.4289 | 122.3373 | 122.4564 | 52.3956 | 45.3186
2272.7656 | 122.7127 | -52.858 | 69.4839 | -0.10979 | 0.0014847 | 0.063094 | 0.12402 | 0.0018799 | -0.0005768 | -0.0037384 | -0.021667 | -0.0045458 | 0.063111 | 0.069167 | -0.027859 | 0.00098693 | -0.0011749 | -0.49896 | 69.4519 | -53.0365 | 69.5114 | -47.4289 | -53.3432 | 4.3121 | -7.5623 | 69.4336 | -52.9541 | 69.5801 | -52.1255 | -52.7939 | -52.6199 | -0.17853 | -0.032044 | 0.027466 | 5.4291 | 57.1701 | -0.48523 | 57.3486 | -0.3067 | -0.096131 | -0.050354 | 0.09613 | 0.73242 | 0.23804 | 0.064087 | 0.33417 | 0.16022 | 5.6076 | 122.5479 | 0.82855 | 122.5342 | 122.4884 | 122.3877 | 122.3099 | 122.2916 | -122.5204 | -122.4381 | 122.3694 | 122.438 | 52.359 | 45.2957
2273.8281 | 122.6944 | -52.9724 | 69.3604 | -0.18608 | 0.00084388 | 0.066512 | 0.12124 | -0.00046988 | -0.0033538 | -0.0050202 | -0.06134 | -0.0030506 | 0.064179 | 0.062972 | -0.027431 | 0.0012005 | 0.0020295 | -0.65002 | 69.3375 | -53.1692 | 69.3878 | -47.3099 | -53.2379 | 4.335 | -7.7911 | 69.3512 | -53.0365 | 69.4977 | -52.2308 | -52.8946 | -52.7298 | -0.19684 | -0.022889 | 0.027465 | 5.6625 | 57.3074 | -0.2655 | 57.5043 | -0.068665 | -0.064087 | -0.009156 | 0.13733 | 0.74158 | 0.24262 | 0.07782 | 0.3067 | 0.14191 | 5.8594 | 122.5571 | 0.80566 | 122.5342 | 122.5067 | 122.3877 | 122.3099 | 122.3236 | -122.5296 | -122.3969 | 122.3602 | 122.4701 | 52.3224 | 45.1813
2274.7656 | 122.6852 | -53.1555 | 69.2001 | -0.11742 | 0.00063028 | 0.062239 | 0.12423 | 0.00081172 | 6.4004e-05 | -0.002884 | -0.06134 | -0.0030506 | 0.061188 | 0.054854 | -0.028713 | 0.0020551 | 0.00032049 | -0.5127 | 69.191 | -53.2928 | 69.1818 | -47.4747 | -53.3844 | 4.3854 | -7.6447 | 69.1589 | -53.215 | 69.2917 | -52.4185 | -53.0914 | -52.9312 | -0.13733 | -0.009155 | -0.01831 | 5.6808 | 57.5409 | -0.22888 | 57.6782 | -0.091552 | -0.059509 | -0.041198 | 0.091553 | 0.737 | 0.22431 | 0.064087 | 0.28381 | 0.1236 | 5.8182 | 122.4747 | 0.79651 | 122.5067 | 122.4838 | 122.374 | 122.3465 | 122.3145 | -122.493 | -122.4152 | 122.3373 | 122.4472 | 52.6428 | 45.5109
2275.8281 | 122.6486 | -53.3295 | 69.0445 | -0.16319 | -0.00043792 | 0.064589 | 0.12509 | -0.00025628 | -0.0035674 | -0.0058746 | -0.033874 | -0.00091423 | 0.06247 | 0.058486 | -0.027431 | 0.00013253 | 0.0011749 | -0.54474 | 69.0445 | -53.4668 | 68.9758 | -47.6578 | -53.5629 | 4.3488 | -7.7866 | 69.0079 | -53.3752 | 69.0903 | -52.597 | -53.2654 | -53.1143 | -0.13733 | 0 | -0.068665 | 5.6717 | 57.6782 | -0.23346 | 57.8156 | -0.09613 | -0.045776 | -0.036621 | 0.045776 | 0.73242 | 0.21515 | 0.064087 | 0.26093 | 0.10986 | 5.809 | 122.4426 | 0.7782 | 122.4655 | 122.5113 | 122.3831 | 122.374 | 122.3373 | -122.5113 | -122.4197 | 122.3053 | 122.4197 | 52.7847 | 45.5429
2276.7656 | 122.7127 | -53.5309 | 68.8156 | -0.094528 | -1.0718e-05 | 0.064162 | 0.12252 | -0.00025628 | -0.0022858 | -0.0030976 | -0.064392 | -0.0043322 | 0.062897 | 0.05934 | -0.029354 | 0.0026959 | -0.0022431 | -0.55389 | 68.7973 | -53.6819 | 68.8156 | -47.8958 | -53.7689 | 4.335 | -8.0154 | 68.7881 | -53.6041 | 68.9026 | -52.7756 | -53.4622 | -53.2974 | -0.15106 | -0.018311 | 0 | 5.6351 | 57.8659 | -0.23804 | 58.017 | -0.086975 | -0.073242 | -0.027466 | 0.086975 | 0.75531 | 0.23346 | 0.068665 | 0.3067 | 0.14191 | 5.7861 | 122.4976 | 0.82855 | 122.5067 | 122.4792 | 122.3923 | 122.3282 | 122.319 | -122.4976 | -122.4197 | 122.3465 | 122.4335 | 52.977 | 45.5154
2277.8281 | 122.6578 | -53.4714 | 68.8843 | -0.12505 | 0.0019119 | 0.06288 | 0.12359 | 0.00059812 | -0.0033538 | -0.0013886 | -0.052185 | -0.0041186 | 0.063324 | 0.064894 | -0.028927 | 0.00034613 | 0.00096129 | -0.54474 | 68.8705 | -53.6362 | 68.8202 | -47.8271 | -53.746 | 4.3167 | -7.7179 | 68.866 | -53.5583 | 68.9301 | -52.7527 | -53.4348 | -53.2791 | -0.16479 | -0.013733 | -0.064087 | 5.6442 | 57.7881 | -0.27466 | 57.9529 | -0.10986 | -0.086975 | -0.01831 | 0.045777 | 0.71869 | 0.19226 | 0.036622 | 0.27924 | 0.1236 | 5.809 | 122.4564 | 0.80566 | 122.4884 | 122.5067 | 122.4243 | 122.3419 | 122.3373 | -122.5204 | -122.4426 | 122.2916 | 122.4014 | 52.9266 | 45.7535
2278.7656 | 122.6303 | -53.7689 | 68.5867 | -0.15556 | -0.0010787 | 0.06288 | 0.12381 | 0.0010253 | -0.0048492 | -0.0016022 | -0.079651 | -0.0058276 | 0.063751 | 0.064681 | -0.028713 | -0.00093567 | -0.00053411 | -0.55389 | 68.5638 | -53.9612 | 68.5181 | -48.143 | -54.0848 | 4.1656 | -7.8873 | 68.5455 | -53.8788 | 68.6279 | -53.0594 | -53.7186 | -53.5629 | -0.19226 | -0.022888 | -0.068665 | 5.6259 | 57.9346 | -0.31586 | 58.1268 | -0.1236 | -0.10986 | -0.041199 | 0.041199 | 0.70953 | 0.20599 | 0.050354 | 0.31586 | 0.16022 | 5.8182 | 122.4792 | 0.8194 | 122.5067 | 122.525 | 122.4243 | 122.3328 | 122.3145 | -122.5479 | -122.4655 | 122.287 | 122.3969 | 53.215 | 45.8817
2279.8281 | 122.6944 | -53.8239 | 68.541 | -0.13267 | 0.0021255 | 0.064162 | 0.12423 | 0.0029479 | -0.0001496 | -0.001175 | -0.064392 | -0.0041186 | 0.063111 | 0.066817 | -0.02914 | 0.0018413 | -0.0018157 | -0.53558 | 68.5318 | -53.9795 | 68.5043 | -48.0972 | -54.0573 | 4.2435 | -7.7637 | 68.4723 | -53.8742 | 68.6417 | -53.0548 | -53.7598 | -53.5767 | -0.15564 | -0.009156 | -0.036622 | 5.7266 | 58.0673 | -0.23346 | 58.223 | -0.07782 | -0.050354 | -0.068665 | 0.10071 | 0.76904 | 0.24719 | 0.064087 | 0.29755 | 0.11444 | 5.8823 | 122.4838 | 0.8194 | 122.5159 | 122.5113 | 122.3465 | 122.3557 | 122.2961 | -122.5204 | -122.4152 | 122.3282 | 122.4655 | 53.2883 | 46.0602
2280.7656 | 122.7173 | -54.007 | 68.3212 | -0.37682 | 0.0036209 | 0.064162 | 0.12402 | 0.0035889 | -0.0014312 | -0.002884 | -0.076599 | -0.0030506 | 0.061829 | 0.065962 | -0.02914 | 0.0022687 | -0.00074771 | -0.55389 | 68.2709 | -54.1946 | 68.3029 | -48.2529 | -54.2404 | 4.1061 | -7.6309 | 68.2938 | -54.1168 | 68.4357 | -53.2516 | -53.952 | -53.7827 | -0.18768 | -0.050354 | -0.018311 | 5.7541 | 58.1131 | -0.23346 | 58.3008 | -0.045776 | -0.10986 | -0.027466 | 0.11444 | 0.75531 | 0.2243 | 0.054932 | 0.33417 | 0.1648 | 5.9418 | 122.4976 | 0.86517 | 122.5525 | 122.4655 | 122.4106 | 122.2778 | 122.3007 | -122.5159 | -122.438 | 122.3099 | 122.4426 | 53.4531 | 46.376
2281.8281 | 122.6944 | -53.8513 | 68.4677 | -0.10979 | -0.00022432 | 0.064803 | 0.12616 | 0.0023071 | -0.0020722 | -0.0037384 | -0.055237 | -0.0034778 | 0.062042 | 0.062117 | -0.027645 | 0.00077333 | 0.0016021 | -0.53101 | 68.4448 | -54.0573 | 68.4448 | -47.9874 | -54.1351 | 4.2206 | -7.4203 | 68.4494 | -53.952 | 68.573 | -53.0685 | -53.7918 | -53.6362 | -0.20599 | -0.022888 | -0.022888 | 5.864 | 58.0719 | -0.28381 | 58.2779 | -0.07782 | -0.10071 | -0.01831 | 0.10529 | 0.78278 | 0.21515 | 0.059509 | 0.31586 | 0.16022 | 6.0699 | 122.5021 | 0.88348 | 122.525 | 122.5021 | 122.4014 | 122.2961 | 122.3007 | -122.525 | -122.4197 | 122.2961 | 122.4243 | 53.3203 | 46.431
2282.7656 | 122.6578 | -53.9429 | 68.4448 | -0.16319 | -0.00086512 | 0.063307 | 0.12445 | 0.00059812 | -0.0012176 | -0.0024566 | -0.039978 | -0.0051868 | 0.06546 | 0.063613 | -0.028713 | 0.0024823 | -0.00074771 | -0.5722 | 68.4402 | -54.0985 | 68.3441 | -48.1018 | -54.1946 | 4.1061 | -7.9285 | 68.3899 | -54.0115 | 68.4631 | -53.1921 | -53.8742 | -53.7277 | -0.15564 | -0.004577 | -0.10071 | 5.8411 | 58.049 | -0.25177 | 58.2047 | -0.09613 | -0.068665 | -0.054931 | 0.018311 | 0.75073 | 0.21515 | 0.068664 | 0.28381 | 0.13733 | 5.9967 | 122.4426 | 0.8194 | 122.4747 | 122.5388 | 122.4014 | 122.3831 | 122.3328 | -122.5433 | -122.4564 | 122.287 | 122.406 | 53.3707 | 46.0144
2283.8281 | 122.6624 | -54.1397 | 68.2388 | -0.14793 | 0.00041648 | 0.061598 | 0.1221 | -0.00046988 | -0.001004 | -0.003952 | -0.015564 | -0.0045458 | 0.064392 | 0.056563 | -0.03149 | 0.00077333 | 0.0028839 | -0.59967 | 68.2617 | -54.277 | 68.1793 | -48.1979 | -54.3594 | 4.097 | -8.0383 | 68.2297 | -54.1901 | 68.2251 | -53.4164 | -54.0115 | -53.9062 | -0.13733 | 0.022888 | -0.05951 | 5.9418 | 58.2367 | -0.21973 | 58.374 | -0.082397 | -0.050354 | -0.009156 | -0.013733 | 0.72327 | 0.23346 | 0.12817 | 0.28381 | 0.17853 | 6.0791 | 122.4564 | 0.77362 | 122.4152 | 122.5388 | 122.4197 | 122.4014 | 122.3694 | -122.5159 | -122.4289 | 122.319 | 122.3648 | 53.54 | 46.1014
2284.7656 | 122.6578 | -54.2816 | 68.129 | -0.12505 | -0.0027877 | 0.06288 | 0.12274 | -0.00046988 | -0.0039948 | -0.0037384 | -0.024719 | -0.0054004 | 0.062042 | 0.057204 | -0.028072 | -0.00029487 | 0.0026703 | -0.58594 | 68.0878 | -54.4464 | 68.042 | -48.2941 | -54.5197 | 4.1977 | -8.139 | 68.074 | -54.3411 | 68.1381 | -53.4805 | -54.1855 | -54.1077 | -0.16479 | -0.041198 | -0.086975 | 5.9875 | 58.4793 | -0.23804 | 58.6441 | -0.073242 | -0.059509 | -0.054931 | 0.009156 | 0.80109 | 0.17395 | 0.09613 | 0.23346 | 0.15564 | 6.1523 | 122.4884 | 0.86059 | 122.4792 | 122.5342 | 122.4152 | 122.3694 | 122.3557 | -122.5754 | -122.4701 | 122.3236 | 122.4197 | 53.6957 | 46.1426
2285.8281 | 122.6807 | -54.2358 | 68.1244 | -0.086899 | -0.00065152 | 0.06288 | 0.12381 | -0.0021789 | -0.0024994 | -0.0065156 | -0.018616 | -0.0030506 | 0.064179 | 0.062117 | -0.028286 | 0.0016277 | 0.00053409 | -0.66376 | 68.1152 | -54.3961 | 68.074 | -48.2803 | -54.4968 | 4.3213 | -8.1711 | 68.1061 | -54.3091 | 68.1656 | -53.4485 | -54.1763 | -54.0298 | -0.16022 | -0.009156 | -0.050354 | 5.9555 | 58.5571 | -0.26093 | 58.7173 | -0.10071 | -0.073242 | -0.018311 | 0.041198 | 0.78735 | 0.20599 | 0.059509 | 0.27924 | 0.13275 | 6.1157 | 122.4701 | 0.8606 | 122.4747 | 122.5113 | 122.4152 | 122.3511 | 122.3419 | -122.5204 | -122.4335 | 122.3099 | 122.4014 | 53.5721 | 46.0648
2286.7656 | 122.6578 | -54.3228 | 68.0695 | -0.12505 | 0.00063028 | 0.063307 | 0.12081 | 0.0029479 | -0.0037812 | -0.0018158 | -0.049133 | -0.0030506 | 0.063965 | 0.062545 | -0.030209 | 0.0014141 | 0.0013885 | -0.60425 | 68.0695 | -54.4647 | 67.9459 | -48.2574 | -54.5563 | 4.1931 | -8.107 | 68.0283 | -54.3823 | 68.0923 | -53.508 | -54.2587 | -54.0848 | -0.14191 | 0 | -0.1236 | 6.0654 | 58.5159 | -0.23346 | 58.6578 | -0.091552 | -0.059509 | -0.041199 | 0.022888 | 0.81482 | 0.23804 | 0.064087 | 0.29755 | 0.1236 | 6.2073 | 122.4106 | 0.87433 | 122.4747 | 122.5342 | 122.4106 | 122.3923 | 122.3511 | -122.5342 | -122.4518 | 122.2687 | 122.4152 | 53.7186 | 46.2158
2287.8281 | 122.6257 | -54.5197 | 67.9138 | -0.1403 | -1.0718e-05 | 0.06288 | 0.12744 | -0.0011109 | -0.0048492 | -0.002243 | -0.13153 | -0.0013416 | 0.061402 | 0.062545 | -0.02914 | 0.0022687 | -0.0011749 | -0.72327 | 67.8497 | -54.7302 | 67.7307 | -48.5413 | -54.8309 | 4.0512 | -8.2855 | 67.8635 | -54.6112 | 67.8818 | -53.7918 | -54.5197 | -54.3457 | -0.21057 | -0.064087 | -0.18311 | 5.9784 | 58.5709 | -0.31128 | 58.7814 | -0.10071 | -0.091553 | -0.050354 | -0.032043 | 0.72784 | 0.17395 | 0 | 0.2655 | 0.091553 | 6.189 | 122.4609 | 0.8194 | 122.493 | 122.58 | 122.4747 | 122.3694 | 122.3831 | -122.644 | -122.525 | 122.2504 | 122.4014 | 53.7964 | 46.2341
2288.7656 | 122.6669 | -54.6295 | 67.749 | -0.12505 | 0.0010575 | 0.061598 | 0.12338 | -0.00046988 | -0.0046356 | -0.0035248 | -0.097961 | -0.0051868 | 0.060761 | 0.05699 | -0.027218 | -0.00093567 | 0.0016021 | -0.70038 | 67.7582 | -54.776 | 67.6804 | -48.6282 | -54.6844 | 4.0146 | -8.6472 | 67.6987 | -54.7165 | 67.7948 | -53.8055 | -54.5425 | -54.4052 | -0.14648 | 0.009156 | -0.068664 | 6.0013 | 58.6441 | -0.054931 | 58.7906 | 0.091553 | -0.086975 | -0.050354 | 0.045777 | 0.82397 | 0.22431 | 0.086975 | 0.31128 | 0.17395 | 6.1478 | 122.4564 | 0.91095 | 122.5113 | 122.5342 | 122.4152 | 122.3877 | 122.3282 | -122.525 | -122.4655 | 122.3099 | 122.4243 | 53.9291 | 45.9824
2289.8281 | 122.6486 | -54.6982 | 67.6712 | -0.12505 | 0.0010575 | 0.062239 | 0.12316 | 0.0014527 | -0.0007904 | -0.0018158 | -0.012512 | -0.0054004 | 0.061188 | 0.062117 | -0.028713 | -0.0017901 | 0.00096129 | -0.65002 | 67.63 | -54.8584 | 67.6117 | -48.5916 | -54.9316 | 4.0375 | -8.8394 | 67.63 | -54.7943 | 67.7536 | -53.8742 | -54.5654 | -54.4693 | -0.16022 | -0.041199 | -0.05951 | 6.1066 | 58.7357 | -0.23346 | 58.8959 | -0.073243 | -0.096131 | -0.041199 | 0.082397 | 0.82397 | 0.22888 | 0.13275 | 0.32501 | 0.22888 | 6.2668 | 122.4701 | 0.9201 | 122.5479 | 122.4884 | 122.4243 | 122.3282 | 122.3282 | -122.5296 | -122.4655 | 122.3099 | 122.4518 | 54.0482 | 45.8588
2290.7656 | 122.7127 | -54.8218 | 67.5339 | -0.1403 | 0.00020288 | 0.065016 | 0.12423 | 0.0016663 | -0.0018586 | 0.00032044 | -0.076599 | -0.0043322 | 0.065247 | 0.061049 | -0.029568 | 0.00055973 | 0.0026703 | -0.63629 | 67.5018 | -54.9957 | 67.5247 | -48.6191 | -55.0461 | 3.9597 | -8.8211 | 67.4973 | -54.895 | 67.6346 | -53.9841 | -54.7302 | -54.5746 | -0.17395 | -0.032044 | -0.009156 | 6.2027 | 58.7814 | -0.22431 | 58.9554 | -0.050354 | -0.073243 | -0.036622 | 0.10071 | 0.83771 | 0.24719 | 0.091552 | 0.32044 | 0.1648 | 6.3766 | 122.5204 | 0.91095 | 122.5296 | 122.4976 | 122.3923 | 122.3236 | 122.319 | -122.5296 | -122.4289 | 122.3465 | 122.4564 | 54.1855 | 46.0007
2291.8281 | 122.6761 | -55.0049 | 67.3599 | -0.1403 | -0.0010787 | 0.06288 | 0.12509 | -0.0026063 | -0.0007904 | -0.001175 | -0.021667 | -0.0030506 | 0.062042 | 0.062972 | -0.027859 | 0.00077333 | 0.0020295 | -0.58136 | 67.337 | -55.1971 | 67.2684 | -48.8617 | -55.2567 | 3.9963 | -9.4345 | 67.2913 | -55.1147 | 67.4057 | -54.1763 | -54.9133 | -54.7714 | -0.19226 | -0.022888 | -0.091552 | 6.1432 | 59.0012 | -0.25177 | 59.1934 | -0.059509 | -0.10986 | -0.068664 | 0.045777 | 0.82855 | 0.23346 | 0.091553 | 0.34332 | 0.20142 | 6.3355 | 122.4655 | 0.93841 | 122.5204 | 122.5342 | 122.406 | 122.3419 | 122.2961 | -122.5571 | -122.4747 | 122.2733 | 122.4106 | 54.4235 | 45.5704
2292.7656 | 122.6532 | -55.1514 | 67.2043 | -0.12505 | 0.00041648 | 0.063307 | 0.12487 | 0.0038025 | -0.0048492 | -0.0024566 | -0.021667 | -0.0034778 | 0.061829 | 0.06404 | -0.031277 | 0.00055973 | -0.00010671 | -0.57678 | 67.1951 | -55.3162 | 67.1265 | -48.8937 | -55.4169 | 3.9322 | -8.9951 | 67.1585 | -55.2383 | 67.2592 | -54.3365 | -55.0507 | -54.9271 | -0.16479 | -0.009156 | -0.07782 | 6.2576 | 59.0836 | -0.2655 | 59.2484 | -0.10071 | -0.086975 | -0.045777 | 0.054931 | 0.81482 | 0.2243 | 0.10071 | 0.31128 | 0.18768 | 6.4224 | 122.4426 | 0.90179 | 122.4976 | 122.5113 | 122.3969 | 122.3465 | 122.3099 | -122.5204 | -122.4426 | 122.2778 | 122.4106 | 54.5746 | 46.1563
2293.8281 | 122.731 | -55.1102 | 67.2089 | -0.11742 | 0.00020288 | 0.061171 | 0.12381 | 0.0014527 | -0.0018586 | -0.00096136 | -0.033874 | -0.003905 | 0.064606 | 0.061476 | -0.0285 | 0.00098693 | 0.0045929 | -0.56763 | 67.2226 | -55.2979 | 67.1768 | -48.8205 | -55.3253 | 4.0833 | -8.9539 | 67.1768 | -55.188 | 67.3279 | -54.2496 | -54.9683 | -54.8447 | -0.18768 | 0.013733 | -0.032043 | 6.2897 | 59.1934 | -0.21515 | 59.3811 | -0.027465 | -0.07782 | -0.032043 | 0.11902 | 0.8606 | 0.2655 | 0.14191 | 0.34332 | 0.21973 | 6.4774 | 122.4747 | 0.93841 | 122.5159 | 122.5204 | 122.3648 | 122.3328 | 122.287 | -122.5067 | -122.3969 | 122.287 | 122.438 | 54.5425 | 46.1563
2294.7656 | 122.6807 | -55.394 | 66.9937 | -0.10216 | -0.00065152 | 0.063734 | 0.12359 | -0.0030335 | -0.006131 | -0.0060882 | -0.021667 | -0.0051868 | 0.062683 | 0.062972 | -0.027645 | 0.0016277 | 0.0033111 | -0.64087 | 66.9571 | -55.5771 | 66.9388 | -49.0036 | -55.6046 | 3.9963 | -9.0912 | 66.9342 | -55.4855 | 67.0441 | -54.5288 | -55.2383 | -55.1422 | -0.1831 | -0.036621 | -0.054931 | 6.3904 | 59.3903 | -0.21057 | 59.5734 | -0.027466 | -0.091553 | -0.059509 | 0.050354 | 0.86517 | 0.25177 | 0.15564 | 0.34332 | 0.24719 | 6.5735 | 122.5159 | 0.95673 | 122.5296 | 122.5342 | 122.4197 | 122.3511 | 122.3282 | -122.5708 | -122.4792 | 122.3328 | 122.438 | 54.7531 | 46.3028
2295.8281 | 122.6898 | -55.6366 | 66.7282 | -0.1403 | 0.00084388 | 0.064803 | 0.12487 | 0.00017092 | -0.0024994 | -0.0033112 | -0.091858 | -0.0047594 | 0.063538 | 0.06169 | -0.030209 | 0.0022687 | 0.00032049 | -0.60883 | 66.7191 | -55.7968 | 66.7007 | -49.118 | -55.8701 | 4.0421 | -8.9722 | 66.6687 | -55.7144 | 66.8381 | -54.7623 | -55.5176 | -55.2795 | -0.16022 | -0.009155 | -0.027465 | 6.5186 | 59.6787 | -0.23346 | 59.8389 | -0.073242 | -0.07782 | -0.059509 | 0.10986 | 0.87433 | 0.35706 | 0.11902 | 0.43488 | 0.19684 | 6.6788 | 122.4976 | 0.95215 | 122.5525 | 122.5159 | 122.3831 | 122.3557 | 122.3053 | -122.525 | -122.4426 | 122.3373 | 122.4747 | 55.0278 | 46.6644
2296.7656 | 122.6578 | -55.7602 | 66.6183 | -0.15556 | 0.0010575 | 0.062453 | 0.12658 | -0.0015381 | -0.0052764 | -0.00096136 | -0.039978 | -0.0030506 | 0.062256 | 0.063826 | -0.028286 | -8.1274e-05 | 0.00096129 | -0.68207 | 66.5863 | -55.9067 | 66.5543 | -49.1638 | -56.0074 | 4.097 | -8.9264 | 66.5817 | -55.838 | 66.6687 | -54.9225 | -55.6595 | -55.5222 | -0.14648 | -0.032043 | -0.064087 | 6.5964 | 59.8572 | -0.24719 | 60.0037 | -0.10071 | -0.07782 | -0.036621 | 0.050354 | 0.83771 | 0.23804 | 0.10071 | 0.31586 | 0.17853 | 6.7429 | 122.4609 | 0.91553 | 122.5067 | 122.493 | 122.4197 | 122.3465 | 122.3419 | -122.525 | -122.4564 | 122.3145 | 122.4289 | 55.0781 | 46.8338
2297.8281 | 122.6807 | -56.0211 | 66.3528 | -0.094528 | 0.0010575 | 0.064803 | 0.12551 | -0.0026063 | -0.0033538 | 0.00074764 | -0.070496 | -0.0032642 | 0.061615 | 0.057845 | -0.029354 | 0.00034613 | 0.0020295 | -0.66376 | 66.394 | -56.1493 | 66.2979 | -49.3195 | -56.2592 | 4.097 | -8.7891 | 66.3437 | -56.0761 | 66.4856 | -55.3253 | -55.8792 | -55.751 | -0.12817 | 0.041199 | -0.054931 | 6.7017 | 60.1181 | -0.23804 | 60.2463 | -0.10986 | -0.054932 | -0.009155 | 0.13275 | 0.6958 | 0.27008 | 0.14191 | 0.32501 | 0.19684 | 6.8298 | 122.4472 | 0.75073 | 122.5616 | 122.5433 | 122.4197 | 122.4152 | 122.3648 | -122.5021 | -122.4289 | 122.319 | 122.5067 | 55.3574 | 47.2321
2298.7656 | 122.699 | -56.0989 | 66.2659 | -0.16319 | 0.0031937 | 0.063094 | 0.12487 | 0.0020935 | -0.0007904 | -0.0030976 | -0.09491 | -0.0034778 | 0.065888 | 0.058699 | -0.028713 | 0.0014141 | 0.0024567 | -0.67291 | 66.243 | -56.2683 | 66.2384 | -49.324 | -56.3553 | 4.1428 | -8.7021 | 66.1972 | -56.1722 | 66.3437 | -55.2292 | -55.9937 | -55.8243 | -0.16937 | -0.022888 | -0.027466 | 6.7749 | 60.2417 | -0.25635 | 60.4111 | -0.086975 | -0.073242 | -0.068664 | 0.07782 | 0.86975 | 0.27466 | 0.10529 | 0.3479 | 0.17853 | 6.9443 | 122.5067 | 0.94299 | 122.5159 | 122.5113 | 122.3694 | 122.3419 | 122.2961 | -122.5342 | -122.438 | 122.3373 | 122.4426 | 55.426 | 47.3969
2299.8281 | 122.6807 | -56.575 | 65.8127 | -0.12505 | 0.0023391 | 0.064803 | 0.12487 | 0.0027343 | -0.0029266 | -0.00096136 | -0.046081 | -0.0032642 | 0.065247 | 0.06169 | -0.028927 | 0.00055973 | 0.00074769 | -0.737 | 65.7806 | -56.7215 | 65.744 | -49.9146 | -56.7993 | 4.01 | -8.7433 | 65.7898 | -56.6483 | 65.8676 | -55.687 | -56.4239 | -56.2866 | -0.14648 | -0.032043 | -0.068664 | 6.6605 | 60.585 | -0.2243 | 60.7315 | -0.077819 | -0.073242 | -0.022888 | 0.054932 | 0.88806 | 0.28839 | 0.15106 | 0.36163 | 0.2243 | 6.8069 | 122.4655 | 0.9613 | 122.5159 | 122.5021 | 122.438 | 122.3557 | 122.3648 | -122.5342 | -122.4609 | 122.319 | 122.4426 | 55.838 | 47.8317
2300.7656 | 122.6761 | -56.8268 | 65.5792 | -0.12505 | -0.0010787 | 0.063521 | 0.12744 | 0.0010253 | -0.0003632 | -0.0013886 | -0.036926 | -0.0049732 | 0.061829 | 0.058272 | -0.029568 | 0.0024823 | 0.0020295 | -0.71411 | 65.5518 | -56.9641 | 65.5197 | -49.9832 | -57.0282 | 4.0054 | -9.0317 | 65.5472 | -56.8909 | 65.6342 | -55.9113 | -56.6711 | -56.5384 | -0.13733 | -0.027466 | -0.05951 | 6.8436 | 60.8322 | -0.20142 | 60.9695 | -0.064087 | -0.064087 | -0.032044 | 0.054931 | 0.91553 | 0.28839 | 0.15564 | 0.35248 | 0.21973 | 6.9809 | 122.4838 | 0.97961 | 122.525 | 122.5159 | 122.438 | 122.3785 | 122.374 | -122.5433 | -122.4701 | 122.3465 | 122.4609 | 56.1127 | 47.7951
2301.8281 | 122.7219 | -56.9183 | 65.4602 | -0.079269 | 0.00041648 | 0.061598 | 0.12402 | -0.0034607 | -0.002713 | -0.0024566 | -0.018616 | -0.0034778 | 0.062042 | 0.058272 | -0.027004 | 0.00013253 | 0.0028839 | -0.70496 | 65.4282 | -57.0969 | 65.451 | -49.9878 | -57.074 | 3.9185 | -9.137 | 65.3732 | -57.0145 | 65.5701 | -56.0074 | -56.8222 | -56.6391 | -0.17853 | -0.032043 | -0.009155 | 6.9305 | 60.8368 | -0.15564 | 61.0153 | 0.022888 | -0.09613 | -0.086975 | 0.10986 | 0.91095 | 0.27924 | 0.09613 | 0.37537 | 0.19226 | 7.1091 | 122.5479 | 1.0071 | 122.5845 | 122.525 | 122.3877 | 122.3465 | 122.2916 | -122.5571 | -122.4747 | 122.3694 | 122.4884 | 56.2134 | 47.7814
2302.7656 | 122.6761 | -57.0831 | 65.2863 | -0.10979 | 0.0012711 | 0.063307 | 0.12658 | -0.00025628 | -0.0035674 | -0.0035248 | -0.052185 | -0.0028368 | 0.063324 | 0.062758 | -0.028927 | 0.00098693 | 0.00032049 | -0.70496 | 65.2176 | -57.2891 | 65.1718 | -50.2304 | -57.399 | 3.7033 | -9.3338 | 65.2084 | -57.2021 | 65.3137 | -56.2134 | -56.9916 | -56.8497 | -0.20599 | -0.068665 | -0.11444 | 6.8527 | 60.7864 | -0.31586 | 60.9924 | -0.10986 | -0.11902 | -0.07782 | 0.027466 | 0.86975 | 0.23346 | 0.091553 | 0.35248 | 0.21057 | 7.0587 | 122.4609 | 0.98877 | 122.5159 | 122.5067 | 122.4106 | 122.3007 | 122.2916 | -122.5754 | -122.4884 | 122.2549 | 122.3969 | 56.3782 | 47.7493
2303.8281 | 122.6807 | -57.1793 | 65.1855 | -0.086899 | 0.00041648 | 0.064375 | 0.12637 | -0.0011109 | -0.0035674 | -0.001175 | -0.033874 | -0.0049732 | 0.062897 | 0.062758 | -0.033199 | 0.00077333 | 0.0013885 | -0.67749 | 65.1947 | -57.3166 | 65.213 | -50.0473 | -57.2845 | 3.7399 | -9.3063 | 65.1489 | -57.2342 | 65.2039 | -56.3461 | -56.868 | -56.8176 | -0.13733 | 0.009155 | 0.027466 | 7.132 | 60.9192 | -0.10529 | 61.0565 | 0.032043 | -0.054932 | -0.036621 | 0.01831 | 0.83313 | 0.36163 | 0.31128 | 0.41656 | 0.36621 | 7.2693 | 122.5296 | 0.88806 | 122.438 | 122.5113 | 122.3831 | 122.374 | 122.3282 | -122.5021 | -122.4197 | 122.3923 | 122.3831 | 56.5018 | 47.8729
2304.7656 | 122.6624 | -57.431 | 64.9704 | -0.17845 | 0.00084388 | 0.062239 | 0.12466 | -0.0013245 | -0.0031402 | -0.0026704 | -0.039978 | -0.0013416 | 0.064606 | 0.057204 | -0.029354 | 0.00055973 | 0.0020295 | -0.81024 | 64.9246 | -57.5912 | 64.8422 | -50.7294 | -57.7332 | 3.4653 | -9.5673 | 64.9063 | -57.5363 | 64.9612 | -56.5475 | -57.3486 | -57.1655 | -0.16022 | -0.045776 | -0.12817 | 6.7017 | 60.8963 | -0.30212 | 61.0565 | -0.14191 | -0.10529 | -0.064087 | -0.009155 | 0.88348 | 0.2655 | 0.082397 | 0.37079 | 0.18768 | 6.8619 | 122.4335 | 0.98877 | 122.4976 | 122.5159 | 122.4426 | 122.3557 | 122.3373 | -122.5616 | -122.5067 | 122.2733 | 122.3923 | 56.6208 | 47.8638
2305.8281 | 122.6898 | -57.5272 | 64.856 | -0.25475 | 0.00063028 | 0.063948 | 0.1268 | -0.0015381 | -0.0035674 | -0.0033112 | -0.036926 | -0.005614 | 0.064179 | 0.06639 | -0.029568 | -0.00029487 | 0.0016021 | -0.79193 | 64.8102 | -57.7011 | 64.769 | -50.5142 | -57.7423 | 3.566 | -9.3155 | 64.8239 | -57.5638 | 64.9292 | -56.5933 | -57.3669 | -57.2479 | -0.17395 | -0.045776 | -0.086975 | 7.0129 | 61.0931 | -0.21515 | 61.2671 | -0.041199 | -0.036621 | -0.032043 | 0.073242 | 0.93384 | 0.27924 | 0.16022 | 0.31586 | 0.19684 | 7.1869 | 122.4701 | 0.97046 | 122.493 | 122.5113 | 122.3877 | 122.3373 | 122.3511 | -122.5571 | -122.4197 | 122.2961 | 122.4564 | 56.7352 | 48.2117
2306.7656 | 122.7036 | -57.4173 | 64.9704 | -0.11742 | 0.00020288 | 0.063094 | 0.12722 | -0.00068368 | -0.0050628 | -0.0041656 | -0.018616 | -0.0032642 | 0.062042 | 0.055495 | -0.028713 | 0.0014141 | -0.00010671 | -0.75531 | 64.9612 | -57.5821 | 64.9429 | -50.2213 | -57.5912 | 3.6118 | -8.8989 | 64.9017 | -57.486 | 65.0711 | -56.4011 | -57.2113 | -57.0969 | -0.1648 | -0.009155 | -0.027466 | 7.196 | 61.0291 | -0.17395 | 61.1938 | -0.009156 | -0.068665 | -0.068665 | 0.10071 | 1.0162 | 0.32043 | 0.20599 | 0.3891 | 0.27466 | 7.3608 | 122.525 | 1.0849 | 122.5571 | 122.5433 | 122.3877 | 122.3785 | 122.319 | -122.5525 | -122.4564 | 122.3602 | 122.4884 | 56.662 | 48.5184
2307.8281 | 122.6532 | -57.6645 | 64.7507 | -0.13267 | -1.0718e-05 | 0.064162 | 0.12594 | 0.0016663 | -0.0020722 | -0.002884 | -0.076599 | -0.0015552 | 0.062042 | 0.061263 | -0.029354 | 0.0024823 | -0.00010671 | -0.75531 | 64.7141 | -57.811 | 64.6591 | -50.4547 | -57.8888 | 3.566 | -8.9355 | 64.6957 | -57.7332 | 64.7644 | -56.7398 | -57.5317 | -57.3807 | -0.14648 | -0.036621 | -0.091552 | 7.2098 | 61.2305 | -0.2243 | 61.377 | -0.07782 | -0.068664 | -0.054931 | 0.013733 | 0.92468 | 0.28381 | 0.13275 | 0.35248 | 0.20142 | 7.3563 | 122.4701 | 0.99335 | 122.4976 | 122.525 | 122.4289 | 122.3785 | 122.3602 | -122.5616 | -122.4838 | 122.3236 | 122.4289 | 56.9092 | 48.7289
2308.7656 | 122.731 | -57.9437 | 64.4028 | -0.094528 | 0.0012711 | 0.065657 | 0.12744 | -0.0030335 | -0.0031402 | -0.0024566 | -0.039978 | -0.0041186 | 0.063965 | 0.062758 | -0.027645 | 0.00034613 | 0.0028839 | -0.77362 | 64.3982 | -58.1177 | 64.4073 | -50.6699 | -58.0948 | 3.6209 | -8.9401 | 64.389 | -58.017 | 64.5218 | -56.9641 | -57.7332 | -57.637 | -0.17395 | -0.004578 | 0.004578 | 7.2739 | 61.5646 | -0.15106 | 61.7386 | 0.022888 | -0.073242 | -0.013733 | 0.11902 | 0.97961 | 0.3067 | 0.21057 | 0.37994 | 0.28381 | 7.4478 | 122.525 | 1.0529 | 122.5388 | 122.5159 | 122.406 | 122.3419 | 122.3328 | -122.5204 | -122.4197 | 122.3511 | 122.4655 | 57.1701 | 49.0036
2309.8281 | 122.6761 | -58.0627 | 64.3295 | -0.1403 | -0.00043792 | 0.06288 | 0.13021 | -0.0017517 | -0.0035674 | -0.002243 | -0.064392 | -0.0019824 | 0.063324 | 0.065535 | -0.030209 | 0.0020551 | -0.0030975 | -0.78735 | 64.2929 | -58.223 | 64.27 | -50.6973 | -58.2367 | 3.5019 | -9.1553 | 64.2792 | -58.1451 | 64.357 | -57.1289 | -57.9163 | -57.7927 | -0.16022 | -0.036621 | -0.059509 | 7.3654 | 61.5646 | -0.17395 | 61.7249 | -0.013733 | -0.082398 | -0.050354 | 0.027466 | 0.93384 | 0.27008 | 0.14648 | 0.35248 | 0.22888 | 7.5256 | 122.493 | 1.0162 | 122.5021 | 122.5159 | 122.4243 | 122.3557 | 122.3419 | -122.5525 | -122.4747 | 122.3328 | 122.4197 | 57.2754 | 48.9075
2310.7656 | 122.7219 | -58.0353 | 64.3158 | -0.086899 | -0.0012923 | 0.063521 | 0.1253 | -0.00068368 | -0.0020722 | -0.00032036 | -0.024719 | -0.0045458 | 0.061829 | 0.069167 | -0.029354 | -0.00029487 | 0.00096129 | -0.76904 | 64.325 | -58.2138 | 64.3066 | -50.4776 | -58.2092 | 3.5843 | -9.0546 | 64.3021 | -58.1131 | 64.4394 | -57.0374 | -57.811 | -57.7194 | -0.17853 | 0.009155 | -0.009155 | 7.5577 | 61.6196 | -0.17395 | 61.7981 | 0.004577 | -0.07782 | -0.013733 | 0.1236 | 0.99792 | 0.31586 | 0.2243 | 0.39368 | 0.30212 | 7.7362 | 122.5204 | 1.0757 | 122.5525 | 122.5388 | 122.4152 | 122.3602 | 122.3373 | -122.5296 | -122.4289 | 122.3419 | 122.4747 | 57.2662 | 48.9807
2311.8438 | 122.6349 | -58.1955 | 64.2517 | -0.086899 | -0.0012923 | 0.065443 | 0.13043 | 0.0040161 | -0.001004 | -0.0020294 | -0.15289 | -0.0030506 | 0.06546 | 0.067885 | -0.027004 | 0.00013253 | 0.0039521 | -0.79651 | 64.1922 | -58.3786 | 64.1418 | -50.7477 | -58.4152 | 3.4058 | -9.7046 | 64.2059 | -58.2367 | 64.2746 | -57.2662 | -58.0856 | -57.8888 | -0.18311 | -0.059509 | -0.10986 | 7.4478 | 61.6013 | -0.21973 | 61.7844 | -0.036621 | -0.041198 | -0.045776 | 0.022888 | 0.92926 | 0.3067 | 0.10986 | 0.3479 | 0.15106 | 7.6309 | 122.5204 | 0.97046 | 122.5113 | 122.5708 | 122.4426 | 122.3877 | 122.4014 | -122.6303 | -122.4884 | 122.3373 | 122.4701 | 57.399 | 48.4909
2312.7656 | 122.6807 | -58.1818 | 64.1647 | -0.15556 | -0.00022432 | 0.063521 | 0.12722 | -0.0038879 | -0.0063446 | -0.0033112 | -0.012512 | -0.003905 | 0.063111 | 0.060622 | -0.027859 | 0.0012005 | -0.00010671 | -0.80109 | 64.1327 | -58.4061 | 64.0732 | -50.6882 | -58.4518 | 3.3966 | -9.9976 | 64.1098 | -58.3054 | 64.2014 | -57.2571 | -58.0627 | -57.9254 | -0.2243 | -0.032044 | -0.091553 | 7.4936 | 61.5784 | -0.27008 | 61.8027 | -0.045776 | -0.1236 | -0.054932 | 0.036621 | 0.92468 | 0.25635 | 0.11902 | 0.37994 | 0.24262 | 7.7179 | 122.4792 | 1.0483 | 122.5067 | 122.5388 | 122.4152 | 122.3145 | 122.2916 | -122.5708 | -122.4701 | 122.2549 | 122.3831 | 57.3807 | 48.1842
2313.8281 | 122.7448 | -58.4747 | 63.8443 | -0.086899 | 0.0012711 | 0.062025 | 0.12616 | 0.00081172 | -0.0033538 | -0.004593 | 0.0088502 | -0.0032642 | 0.062897 | 0.059554 | -0.028713 | 0.00034613 | 0.0039521 | -0.76446 | 63.858 | -58.6441 | 63.8443 | -50.9262 | -58.6121 | 3.4607 | -10.025 | 63.8397 | -58.5617 | 63.9587 | -57.4722 | -58.2687 | -58.1772 | -0.16937 | 0.013733 | 0 | 7.5485 | 61.9354 | -0.13733 | 62.1048 | 0.032043 | -0.086976 | -0.004577 | 0.11444 | 1.0025 | 0.29755 | 0.20599 | 0.38452 | 0.29297 | 7.7179 | 122.4884 | 1.0895 | 122.5204 | 122.5021 | 122.4014 | 122.3328 | 122.3145 | -122.4884 | -122.406 | 122.319 | 122.4335 | 57.7103 | 48.4497
2314.7656 | 122.6944 | -58.6212 | 63.7665 | -0.14793 | 0.0016983 | 0.063521 | 0.1268 | -0.0013245 | -0.0042084 | -0.003952 | -0.033874 | -0.0043322 | 0.063324 | 0.060408 | -0.028927 | 0.00055973 | 0.0050201 | -0.78278 | 63.7207 | -58.7952 | 63.6978 | -51.0315 | -58.7952 | 3.2593 | -9.993 | 63.707 | -58.7265 | 63.8168 | -57.6141 | -58.4335 | -58.3054 | -0.17395 | -0.045776 | -0.068664 | 7.5897 | 61.8805 | -0.17395 | 62.0544 | 0 | -0.10529 | -0.059509 | 0.050354 | 1.0071 | 0.31586 | 0.18768 | 0.42114 | 0.29297 | 7.7637 | 122.493 | 1.1124 | 122.5433 | 122.5159 | 122.4335 | 122.3419 | 122.3282 | -122.5616 | -122.493 | 122.319 | 122.438 | 57.8384 | 48.6282
2315.8281 | 122.644 | -58.5983 | 63.7665 | -0.1403 | 0.0027665 | 0.062025 | 0.1268 | 0.00017092 | -0.0014312 | -0.002884 | -0.064392 | -0.0045458 | 0.062042 | 0.06169 | -0.028927 | 0.00013253 | 0.0024567 | -0.76904 | 63.7024 | -58.7769 | 63.7024 | -50.853 | -58.8226 | 3.2364 | -9.6817 | 63.7024 | -58.6761 | 63.8351 | -57.6462 | -58.4518 | -58.3191 | -0.17853 | -0.064086 | -0.064086 | 7.7454 | 61.8347 | -0.2243 | 62.0132 | -0.045777 | -0.077819 | -0.064086 | 0.068665 | 0.95215 | 0.27924 | 0.14649 | 0.35706 | 0.2243 | 7.9239 | 122.4792 | 1.03 | 122.5113 | 122.4792 | 122.3785 | 122.3007 | 122.3007 | -122.5433 | -122.4426 | 122.3007 | 122.4335 | 57.8293 | 48.9166
2316.7656 | 122.6898 | -58.8089 | 63.5605 | -0.079269 | 0.00063028 | 0.064162 | 0.1268 | -0.0013245 | -0.0022858 | -0.0035248 | -0.039978 | -0.0047594 | 0.061615 | 0.054213 | -0.028927 | 0.0014141 | -0.00032051 | -0.75531 | 63.533 | -58.96 | 63.5284 | -50.972 | -58.9783 | 3.3691 | -9.8099 | 63.5056 | -58.8959 | 63.6246 | -57.7835 | -58.6258 | -58.5068 | -0.15106 | -0.027466 | -0.032044 | 7.8369 | 62.178 | -0.16937 | 62.3291 | -0.01831 | -0.086975 | -0.054932 | 0.064087 | 1.0254 | 0.30212 | 0.18311 | 0.3891 | 0.27008 | 7.988 | 122.4884 | 1.1124 | 122.5204 | 122.493 | 122.4014 | 122.3419 | 122.3145 | -122.5204 | -122.4564 | 122.3373 | 122.4335 | 58.0536 | 48.999
2317.8281 | 122.7264 | -59.0149 | 63.3682 | -0.10216 | 0.00020288 | 0.064803 | 0.12744 | 0.0023071 | -0.0052764 | -0.0026704 | -0.13458 | -0.0034778 | 0.065247 | 0.062545 | -0.030209 | 0.0014141 | 0.0022431 | -0.74158 | 63.3316 | -59.2026 | 63.3362 | -51.0544 | -58.7997 | 3.3051 | -9.9426 | 63.2721 | -59.0881 | 63.4232 | -57.9529 | -58.8226 | -58.6899 | -0.18768 | -0.036621 | -0.032043 | 7.9605 | 62.3199 | 0.21515 | 62.5076 | 0.40283 | -0.073242 | -0.09613 | 0.054932 | 1.062 | 0.32501 | 0.19226 | 0.39825 | 0.2655 | 8.1482 | 122.5388 | 1.1353 | 122.5113 | 122.5342 | 122.3602 | 122.3465 | 122.287 | -122.5708 | -122.4564 | 122.3511 | 122.4381 | 58.2733 | 49.0723
2318.7656 | 122.699 | -59.0332 | 63.3408 | -0.1403 | -1.0718e-05 | 0.063521 | 0.12637 | -0.0013245 | -0.0037812 | -0.001175 | -0.036926 | -0.002196 | 0.065247 | 0.055922 | -0.030209 | 0.0012005 | 0.00032049 | -0.76446 | 63.2996 | -59.2209 | 63.2538 | -51.178 | -59.2438 | 3.5019 | -10.2631 | 63.2629 | -59.1248 | 63.4003 | -57.9895 | -58.8272 | -58.7128 | -0.18768 | -0.041198 | -0.086975 | 7.8552 | 62.5351 | -0.21057 | 62.7228 | -0.022888 | -0.091553 | -0.07782 | 0.05951 | 1.0437 | 0.32043 | 0.20599 | 0.41199 | 0.29755 | 8.0429 | 122.4747 | 1.1353 | 122.525 | 122.5204 | 122.3877 | 122.3328 | 122.2961 | -122.5616 | -122.4655 | 122.287 | 122.4335 | 58.2687 | 48.7701
2319.8281 | 122.7219 | -59.2072 | 63.1714 | -0.1403 | -0.0019333 | 0.06288 | 0.12765 | -0.0021789 | -0.004422 | -0.0052338 | -0.027771 | -0.0041186 | 0.062897 | 0.056777 | -0.030209 | 0.0020551 | -0.0026703 | -0.80566 | 63.1348 | -59.3857 | 63.0936 | -51.2146 | -59.3948 | 3.3966 | -10.2631 | 63.0798 | -59.317 | 63.2263 | -58.1635 | -59.0057 | -58.873 | -0.17853 | -0.036621 | -0.07782 | 7.9926 | 62.6038 | -0.18768 | 62.7823 | -0.009155 | -0.10986 | -0.091553 | 0.054931 | 1.0437 | 0.33417 | 0.20142 | 0.44403 | 0.31128 | 8.1711 | 122.4792 | 1.1536 | 122.5433 | 122.5204 | 122.3969 | 122.3419 | 122.287 | -122.5571 | -122.4884 | 122.3007 | 122.4335 | 58.4015 | 48.9441
2320.7656 | 122.5937 | -59.3903 | 62.9654 | -0.11742 | 0.0010575 | 0.064375 | 0.12893 | 0.0023071 | -0.0039948 | -0.0030976 | -0.027771 | -0.0030506 | 0.065033 | 0.058699 | -0.028927 | 0.0016277 | 0.00032049 | -0.75531 | 62.9654 | -59.5367 | 62.9745 | -51.265 | -59.5276 | 3.3279 | -10.0571 | 62.9379 | -59.4543 | 63.002 | -58.049 | -58.9828 | -59.0744 | -0.14648 | 0 | 0.009155 | 8.1253 | 62.7182 | -0.13733 | 62.8647 | 0.009155 | -0.064087 | -0.027466 | 0.036621 | 1.3412 | 0.31586 | 0.40741 | 0.37994 | 0.4715 | 8.2718 | 122.5113 | 1.4053 | 122.4564 | 122.5021 | 122.3923 | 122.3557 | 122.3282 | -122.5021 | -122.4197 | 122.3648 | 122.3923 | 58.6349 | 49.3332
2321.8438 | 122.7219 | -59.523 | 62.8464 | -0.1403 | -0.0049239 | 0.061598 | 0.12701 | -0.0015381 | -0.002713 | -0.002884 | -0.0064086 | -0.0060412 | 0.06482 | 0.067885 | -0.029995 | -8.1274e-05 | 0.00010689 | -0.59509 | 62.851 | -59.7015 | 62.7914 | -51.5076 | -59.6466 | 3.186 | -10.0983 | 62.7914 | -59.6008 | 62.9517 | -58.4702 | -59.317 | -59.2026 | -0.17853 | 0.004577 | -0.054932 | 8.0154 | 62.709 | -0.1236 | 62.8876 | 0.054932 | -0.07782 | -0.054932 | 0.10528 | 1.0529 | 0.32043 | 0.20599 | 0.39825 | 0.28381 | 8.194 | 122.493 | 1.1307 | 122.5525 | 122.5525 | 122.3923 | 122.374 | 122.3145 | -122.5479 | -122.4472 | 122.3145 | 122.4747 | 58.9279 | 49.4247
2322.7656 | 122.7402 | -59.6146 | 62.7457 | -0.010605 | 0.00041648 | 0.064803 | 0.1285 | 0.00059812 | -0.0020722 | -0.00074776 | -0.0064086 | -0.0058276 | 0.060974 | 0.05699 | -0.030209 | -0.0041401 | 0.0011749 | -0.76446 | 62.7365 | -59.7519 | 62.764 | -51.5442 | -59.761 | 3.1265 | -9.9106 | 62.709 | -59.6558 | 62.9425 | -58.5297 | -59.7015 | -59.4635 | -0.13733 | -0.009156 | 0.01831 | 8.0704 | 62.7411 | -0.14648 | 62.8784 | -0.009155 | -0.041199 | -0.036622 | 0.19684 | 1.0849 | 0.15106 | -0.086975 | 0.19226 | -0.045776 | 8.2077 | 122.5159 | 1.1261 | 122.5983 | 122.4884 | 122.3648 | 122.3511 | 122.3236 | -122.4976 | -122.4014 | 122.3785 | 122.5571 | 58.8501 | 49.704
2323.8281 | 122.6944 | -59.967 | 62.4252 | -0.10216 | 0.00020288 | 0.06523 | 0.12637 | -0.0019653 | -0.0039948 | 0.0013886 | -0.039978 | -0.0030506 | 0.064179 | 0.059981 | -0.029354 | 0.0014141 | -0.0013885 | -0.82398 | 62.3703 | -60.1364 | 62.3795 | -52.0294 | -60.1364 | 2.9434 | -10.231 | 62.3566 | -60.0494 | 62.4573 | -58.9142 | -59.7748 | -59.6512 | -0.16937 | -0.054932 | -0.045776 | 7.9376 | 62.9105 | -0.16937 | 63.0798 | 0 | -0.082397 | -0.068665 | 0.032043 | 1.0529 | 0.31586 | 0.19226 | 0.39825 | 0.27466 | 8.107 | 122.5159 | 1.1353 | 122.5067 | 122.5067 | 122.406 | 122.3373 | 122.3236 | -122.5616 | -122.4747 | 122.3465 | 122.4243 | 59.1431 | 49.736
2324.7656 | 122.6898 | -59.9854 | 62.4252 | -0.094528 | -0.0012923 | 0.065871 | 0.12872 | -0.0019653 | -0.0014312 | -0.00096136 | -0.027771 | -0.0028368 | 0.062256 | 0.062331 | -0.029781 | 0.0044049 | -0.0013885 | -0.81024 | 62.439 | -60.0769 | 62.4115 | -51.9196 | -60.0723 | 3.1448 | -10.318 | 62.3703 | -60.0357 | 62.3795 | -58.8501 | -59.6924 | -59.6008 | -0.091552 | 0.013733 | -0.013733 | 8.0658 | 63.1302 | -0.086975 | 63.2217 | 0.004577 | -0.050354 | -0.054932 | -0.045776 | 1.1353 | 0.38452 | 0.29297 | 0.43488 | 0.34332 | 8.1573 | 122.4884 | 1.1856 | 122.4152 | 122.5159 | 122.406 | 122.4243 | 122.3557 | -122.5021 | -122.4609 | 122.3969 | 122.3648 | 59.1751 | 49.6674
2325.8281 | 122.7264 | -60.0266 | 62.3566 | -0.07164 | 0.00020288 | 0.063948 | 0.1285 | -0.00068368 | -0.0067718 | -0.003952 | -0.06134 | -0.0043322 | 0.063111 | 0.058913 | -0.028286 | 0.00034613 | 0.0016021 | -0.81482 | 62.3016 | -60.1913 | 62.3749 | -52.2537 | -60.3424 | 3.0441 | -10.2356 | 62.2833 | -60.0952 | 62.4344 | -58.9417 | -59.7656 | -59.6741 | -0.16479 | -0.054931 | 0.018311 | 7.7728 | 63.0707 | -0.31586 | 63.2355 | -0.15106 | -0.068665 | -0.073242 | 0.07782 | 1.0849 | 0.35248 | 0.26093 | 0.42114 | 0.32959 | 7.9376 | 122.5662 | 1.1536 | 122.5296 | 122.493 | 122.3785 | 122.3282 | 122.3099 | -122.5479 | -122.4518 | 122.4014 | 122.4609 | 59.2117 | 49.791
2326.7656 | 122.6761 | -59.9442 | 62.4664 | -0.094528 | 0.00041648 | 0.066512 | 0.13278 | 0.0070069 | -0.0050628 | 0.0016022 | -0.18951 | -0.0024096 | 0.06247 | 0.066603 | -0.027218 | 0.0046185 | -0.00053411 | -0.88806 | 62.4573 | -60.1181 | 62.3245 | -51.7731 | -60.2509 | 2.9297 | -10.1761 | 62.4619 | -60.0128 | 62.4344 | -58.992 | -59.8938 | -59.7015 | -0.17395 | -0.009156 | -0.14191 | 8.1711 | 62.8738 | -0.3067 | 63.0478 | -0.13275 | -0.068664 | -0.004578 | -0.032044 | 0.95215 | 0.24262 | 0.050354 | 0.31128 | 0.11902 | 8.345 | 122.4426 | 1.0208 | 122.4472 | 122.5754 | 122.4747 | 122.4014 | 122.406 | -122.5845 | -122.4792 | 122.2687 | 122.3785 | 59.0561 | 49.7681
2327.8281 | 122.612 | -60.1685 | 62.2604 | -0.06401 | 0.0010575 | 0.065443 | 0.13 | -0.0011109 | -0.0059174 | -0.00053396 | -0.09491 | -0.0024096 | 0.063751 | 0.063613 | -0.02914 | 0.0014141 | 0.0030975 | -0.86517 | 62.2513 | -60.3333 | 62.0956 | -52.0752 | -60.3973 | 2.9205 | -10.5606 | 62.233 | -60.2463 | 62.2284 | -59.1248 | -60.0266 | -59.8892 | -0.1648 | -0.009155 | -0.1648 | 8.0933 | 63.089 | -0.22888 | 63.2538 | -0.064087 | -0.07782 | -0.027466 | -0.032043 | 1.0437 | 0.27924 | 0.14191 | 0.35706 | 0.21973 | 8.2581 | 122.4289 | 1.1215 | 122.4747 | 122.5845 | 122.4792 | 122.4197 | 122.4014 | -122.5937 | -122.5067 | 122.2641 | 122.3969 | 59.3033 | 49.6078
2328.7656 | 122.6898 | -60.2097 | 62.1506 | -0.15556 | -0.00022432 | 0.065016 | 0.12808 | 0.0018799 | -0.0033538 | 0.00010684 | 0.0027466 | -0.0043322 | 0.06482 | 0.058272 | -0.028286 | 0.0016277 | -0.0018157 | -0.83313 | 62.146 | -60.3973 | 62.1048 | -51.915 | -60.4065 | 3.0121 | -10.6934 | 62.0956 | -60.3149 | 62.233 | -59.111 | -59.9762 | -59.8801 | -0.18768 | -0.004578 | -0.045777 | 8.2947 | 63.2217 | -0.19684 | 63.4094 | -0.009155 | -0.10528 | -0.054932 | 0.082397 | 1.0986 | 0.32959 | 0.23346 | 0.43487 | 0.33874 | 8.4824 | 122.5021 | 1.2039 | 122.5479 | 122.5433 | 122.4106 | 122.3557 | 122.3053 | -122.5479 | -122.4655 | 122.3145 | 122.4426 | 59.3765 | 49.5163
2329.8281 | 122.6715 | -60.3149 | 62.0911 | -0.094528 | 0.00063028 | 0.065016 | 0.12893 | 0.0016663 | -0.0029266 | -0.0048066 | -0.0064086 | -0.0043322 | 0.064179 | 0.058272 | -0.028713 | 0.0018413 | -0.0022431 | -0.8606 | 62.0087 | -60.4752 | 62.0361 | -51.9333 | -60.4523 | 2.861 | -10.7666 | 62.0224 | -60.3653 | 62.114 | -59.2072 | -60.1135 | -59.9854 | -0.16022 | -0.082397 | -0.054931 | 8.3817 | 63.176 | -0.13733 | 63.3362 | 0.022888 | -0.050354 | -0.068664 | 0.022889 | 1.1078 | 0.32959 | 0.20142 | 0.37994 | 0.25177 | 8.5419 | 122.5113 | 1.1581 | 122.4792 | 122.4838 | 122.3877 | 122.3236 | 122.3373 | -122.5662 | -122.4564 | 122.3511 | 122.4289 | 59.4543 | 49.5483
2330.7656 | 122.7173 | -60.3745 | 62.0178 | -0.10216 | 0.0016983 | 0.063734 | 0.12765 | -0.0011109 | -0.0039948 | -0.0033112 | -0.024719 | -0.0047594 | 0.063324 | 0.057631 | -0.029354 | -0.00029487 | 0.0013885 | -0.86975 | 61.9949 | -60.4889 | 62.0224 | -51.8234 | -60.4523 | 2.8427 | -10.7071 | 61.9766 | -60.3973 | 62.0956 | -59.4818 | -60.0861 | -59.9533 | -0.11444 | -0.022888 | 0.004578 | 8.551 | 63.2172 | -0.07782 | 63.3316 | 0.036621 | -0.022888 | -0.041198 | 0.07782 | 0.89264 | 0.42114 | 0.28839 | 0.44403 | 0.31128 | 8.6655 | 122.5113 | 0.91553 | 122.493 | 122.4838 | 122.374 | 122.3694 | 122.3511 | -122.5067 | -122.4152 | 122.3969 | 122.4701 | 59.5047 | 49.6674
2331.8438 | 122.5159 | -60.3607 | 62.1277 | -0.10979 | 0.00041648 | 0.064803 | 0.12936 | 0.0010253 | -0.0046356 | -0.0037384 | -0.052185 | -0.0026232 | 0.062897 | 0.057418 | -0.027645 | 0.00055973 | 0.0028839 | -0.87433 | 62.0636 | -60.4935 | 61.94 | -51.8555 | -60.5804 | 2.8198 | -10.7437 | 62.059 | -60.4156 | 62.0132 | -59.3262 | -60.2142 | -60.0815 | -0.13275 | -0.064087 | -0.18768 | 8.5052 | 63.1805 | -0.21973 | 63.3133 | -0.086975 | -0.054931 | -0.068665 | -0.11444 | 1.0345 | 0.27924 | 0.14648 | 0.33417 | 0.20142 | 8.638 | 122.4335 | 1.0895 | 122.4289 | 122.5571 | 122.4747 | 122.4243 | 122.4197 | -122.6212 | -122.5433 | 122.3007 | 122.374 | 59.4864 | 49.617
2332.7656 | 122.6852 | -60.434 | 61.9034 | -0.17082 | 0.00020288 | 0.064375 | 0.13021 | 0.0020935 | -0.0039948 | -0.00010676 | -0.04303 | -0.0030506 | 0.061829 | 0.058486 | -0.028927 | 0.0031231 | 0.00074769 | -0.87891 | 61.8576 | -60.64 | 61.8988 | -51.7914 | -60.6674 | 2.8519 | -10.6934 | 61.8713 | -60.5255 | 61.9904 | -59.3628 | -60.2692 | -60.1227 | -0.20599 | -0.045776 | -0.004577 | 8.6426 | 63.2858 | -0.23346 | 63.4918 | -0.027465 | -0.091553 | -0.032043 | 0.086975 | 1.0712 | 0.31128 | 0.16479 | 0.40283 | 0.25635 | 8.8486 | 122.5388 | 1.1627 | 122.5159 | 122.4976 | 122.3969 | 122.2916 | 122.3053 | -122.5433 | -122.4289 | 122.3328 | 122.4243 | 59.5551 | 49.7406
2333.8281 | 122.644 | -60.8002 | 61.6379 | -0.10979 | -1.0718e-05 | 0.064589 | 0.12722 | 0.0010253 | -0.0042084 | -0.0016022 | -0.033874 | -0.0058276 | 0.060974 | 0.061476 | -0.027859 | 0.00055973 | 0.0013885 | -0.88348 | 61.615 | -60.9238 | 61.5417 | -52.0844 | -60.9512 | 2.9663 | -10.8398 | 61.5875 | -60.8276 | 61.5921 | -59.7153 | -60.6445 | -60.5118 | -0.1236 | -0.022888 | -0.09613 | 8.7158 | 63.7665 | -0.15106 | 63.8901 | -0.027466 | -0.027466 | -0.050354 | -0.045776 | 1.0849 | 0.28839 | 0.15564 | 0.31586 | 0.18311 | 8.8394 | 122.4655 | 1.1124 | 122.4197 | 122.5388 | 122.4152 | 122.4152 | 122.3877 | -122.5616 | -122.4655 | 122.3419 | 122.3923 | 59.9167 | 49.9603
2334.7656 | 122.5708 | -60.9009 | 61.5372 | 0.035172 | 0.0019119 | 0.064162 | 0.12979 | 0.00059812 | -0.0042084 | -0.0041656 | -0.09491 | -0.0015552 | 0.065247 | 0.066176 | -0.028713 | 0.00077333 | 0.0037385 | -0.97961 | 61.5509 | -61.0291 | 61.3495 | -52.2537 | -61.1389 | 2.7557 | -10.9177 | 61.5143 | -60.9879 | 61.4822 | -59.8434 | -60.7773 | -60.6262 | -0.12817 | 0.013733 | -0.18768 | 8.6472 | 63.6566 | -0.23804 | 63.7848 | -0.10986 | -0.086975 | -0.022888 | -0.054931 | 1.0574 | 0.27466 | 0.1236 | 0.36163 | 0.21057 | 8.7753 | 122.3785 | 1.1444 | 122.4701 | 122.58 | 122.5021 | 122.4518 | 122.4152 | -122.5662 | -122.525 | 122.2504 | 122.3831 | 59.9213 | 49.9832
2335.8281 | 122.6166 | -60.9467 | 61.5692 | -0.06401 | -0.0017197 | 0.063948 | 0.12936 | 0.0018799 | -0.0003632 | -0.0020294 | -0.024719 | -0.0030506 | 0.064179 | 0.057418 | -0.027218 | 0.0026959 | 0.00074769 | -0.84228 | 61.4731 | -61.1023 | 61.3129 | -52.2812 | -61.1252 | 2.7466 | -10.6796 | 61.4319 | -60.997 | 61.4044 | -59.8984 | -60.8047 | -60.791 | -0.15564 | -0.096131 | -0.25635 | 8.6655 | 63.6932 | -0.17853 | 63.8489 | -0.022888 | -0.050354 | -0.13733 | -0.1648 | 1.0483 | 0.15564 | 0.14191 | 0.20599 | 0.19226 | 8.8211 | 122.4152 | 1.0986 | 122.4014 | 122.5754 | 122.4289 | 122.4197 | 122.3785 | -122.6715 | -122.5662 | 122.2595 | 122.3511 | 60.1044 | 50.267
2336.7812 | 122.6624 | -60.8963 | 61.4777 | -0.13267 | -0.0010787 | 0.064375 | 0.12893 | 0.0031617 | -0.0037812 | -0.0043792 | -0.015564 | -0.0028368 | 0.064179 | 0.062117 | -0.028927 | 0.0018413 | 0.0030975 | -0.86975 | 61.4685 | -61.0474 | 61.4594 | -52.0203 | -61.0474 | 2.8885 | -10.5606 | 61.4319 | -60.9695 | 61.5143 | -59.7702 | -60.6857 | -60.585 | -0.15106 | -0.009155 | -0.01831 | 8.876 | 63.7848 | -0.15106 | 63.9359 | 0 | -0.073242 | -0.045776 | 0.036621 | 1.1261 | 0.31128 | 0.21057 | 0.38452 | 0.28381 | 9.0271 | 122.5067 | 1.1993 | 122.4838 | 122.5159 | 122.4014 | 122.3648 | 122.3282 | -122.525 | -122.4472 | 122.3557 | 122.4106 | 60.0266 | 50.3357
2337.8438 | 122.5937 | -61.0565 | 61.3678 | -0.086899 | 0.00063028 | 0.066298 | 0.13171 | -0.0017517 | -0.0037812 | 0.00074764 | -0.091858 | -0.0028368 | 0.062897 | 0.066603 | -0.029568 | 0.0014141 | 0.00074769 | -0.96588 | 61.3495 | -61.2305 | 61.2488 | -52.1896 | -61.1343 | 2.8015 | -10.6064 | 61.3495 | -61.116 | 61.3403 | -59.9991 | -60.9329 | -60.7727 | -0.17395 | -0.018311 | -0.11902 | 8.8669 | 63.858 | -0.077819 | 64.032 | 0.096131 | -0.059509 | -0.018311 | -0.027466 | 1.0574 | 0.28381 | 0.1236 | 0.34332 | 0.18311 | 9.0408 | 122.4792 | 1.1169 | 122.4564 | 122.58 | 122.4655 | 122.406 | 122.406 | -122.5983 | -122.4838 | 122.3053 | 122.3969 | 60.0906 | 50.4501
2338.7656 | 122.6624 | -61.1801 | 61.235 | -0.056381 | 0.0021255 | 0.06288 | 0.12829 | 0.00038452 | -0.0014312 | -0.0024566 | -0.015564 | -0.0045458 | 0.063965 | 0.061263 | -0.029568 | 0.0018413 | 0.0039521 | -0.85144 | 61.2167 | -61.3083 | 61.1755 | -52.24 | -61.2946 | 2.8931 | -10.6476 | 61.1893 | -61.2305 | 61.2167 | -60.0494 | -60.9924 | -60.8688 | -0.12817 | -0.01831 | -0.059509 | 8.9401 | 64.0732 | -0.11444 | 64.2014 | 0.013733 | -0.050354 | -0.045776 | -0.01831 | 1.1307 | 0.31128 | 0.18768 | 0.36163 | 0.23804 | 9.0683 | 122.4838 | 1.181 | 122.4472 | 122.525 | 122.4197 | 122.3969 | 122.3694 | -122.5433 | -122.4655 | 122.3557 | 122.3969 | 60.3287 | 50.5325
2339.8281 | 122.6257 | -61.1893 | 61.2122 | -0.033493 | 0.0010575 | 0.063094 | 0.12915 | 0.0020935 | -0.0029266 | -0.0020294 | -0.11322 | -0.0028368 | 0.06546 | 0.062117 | -0.027645 | 0.0033367 | -0.0022431 | -0.9201 | 61.1801 | -61.3815 | 61.1114 | -52.3727 | -61.4273 | 2.8427 | -10.9268 | 61.2076 | -61.2534 | 61.235 | -60.0906 | -61.0245 | -60.8826 | -0.19226 | -0.032043 | -0.10071 | 8.8165 | 64.032 | -0.23804 | 64.2242 | -0.045776 | -0.064087 | -0.004577 | 0.022888 | 1.0986 | 0.3067 | 0.16479 | 0.37079 | 0.22888 | 9.0088 | 122.493 | 1.1627 | 122.4884 | 122.5616 | 122.4609 | 122.3694 | 122.3969 | -122.5937 | -122.4655 | 122.3007 | 122.4243 | 60.2692 | 50.2625
2340.7656 | 122.58 | -61.3724 | 61.0565 | -0.12505 | 0.00020288 | 0.066298 | 0.12936 | 0.0031617 | -0.004422 | -0.0065156 | -0.11932 | -0.0028368 | 0.06247 | 0.067458 | -0.027218 | 0.0029095 | -0.0020295 | -0.93384 | 61.0336 | -61.5601 | 60.9055 | -52.5009 | -61.6058 | 2.6871 | -11.174 | 61.0245 | -61.4502 | 61.0153 | -60.3012 | -61.2534 | -61.0886 | -0.18768 | -0.022889 | -0.15106 | 8.8715 | 64.0594 | -0.23346 | 64.2471 | -0.045776 | -0.07782 | -0.032044 | -0.041199 | 1.0712 | 0.28381 | 0.11902 | 0.36163 | 0.19684 | 9.0591 | 122.4655 | 1.149 | 122.4655 | 122.5937 | 122.4747 | 122.406 | 122.3969 | -122.6166 | -122.5067 | 122.2778 | 122.3877 | 60.4385 | 50.1984
2341.8594 | 122.6898 | -61.4136 | 60.8734 | -0.11742 | 0.0021255 | 0.06758 | 0.13 | 0.00017092 | -0.0020722 | -0.0018158 | -0.06134 | -0.0045458 | 0.06247 | 0.066176 | -0.028286 | 0.0026959 | 0.00074769 | -0.96588 | 60.965 | -61.5646 | 60.91 | -52.3453 | -61.5692 | 2.8107 | -10.8444 | 60.9192 | -61.4868 | 61.0657 | -60.228 | -61.1481 | -61.0199 | -0.15106 | 0.091553 | 0.036621 | 9.0683 | 64.2242 | -0.15564 | 64.3753 | -0.004578 | -0.073242 | 0.045776 | 0.19226 | 1.1856 | 0.39368 | 0.2655 | 0.46692 | 0.33874 | 9.2194 | 122.4747 | 1.2588 | 122.5525 | 122.5296 | 122.406 | 122.3785 | 122.3328 | -122.438 | -122.3602 | 122.3236 | 122.4792 | 60.4477 | 50.5692
2342.7656 | 122.5845 | -61.5326 | 60.8643 | -0.086899 | 0.0010575 | 0.06758 | 0.12872 | 0.00017092 | -0.0050628 | -0.0035248 | -0.097961 | -0.003905 | 0.066101 | 0.058913 | -0.028927 | 0.0035503 | -0.00096131 | -1.0071 | 60.8826 | -61.7294 | 60.6903 | -52.5925 | -61.8027 | 2.7512 | -11.3754 | 60.8551 | -61.6196 | 60.8459 | -60.4614 | -61.4044 | -61.2396 | -0.19684 | 0.01831 | -0.17395 | 8.9401 | 64.2838 | -0.27008 | 64.4806 | -0.073242 | -0.086975 | -0.009155 | -0.018311 | 1.0712 | 0.29297 | 0.12817 | 0.37994 | 0.21515 | 9.137 | 122.4197 | 1.1581 | 122.4655 | 122.612 | 122.4747 | 122.4152 | 122.3877 | -122.5937 | -122.4838 | 122.2229 | 122.3785 | 60.5255 | 50.1572
2343.8281 | 122.6074 | -61.7752 | 60.6445 | -0.041122 | 0.0023391 | 0.066298 | 0.12915 | -0.0015381 | -0.0014312 | -0.00096136 | -0.049133 | -0.0036914 | 0.06482 | 0.059554 | -0.027645 | 0.0014141 | 0.0037385 | -0.96588 | 60.6445 | -61.9354 | 60.5255 | -52.7573 | -61.9492 | 2.774 | -11.4853 | 60.6033 | -61.8484 | 60.6491 | -60.5988 | -61.5875 | -61.441 | -0.16022 | 0 | -0.11902 | 9.0179 | 64.5493 | -0.17395 | 64.7095 | -0.013733 | -0.073242 | -0.041198 | 0.004578 | 1.1765 | 0.33417 | 0.18768 | 0.40741 | 0.26093 | 9.1782 | 122.4609 | 1.2497 | 122.4976 | 122.58 | 122.4518 | 122.4197 | 122.3785 | -122.58 | -122.493 | 122.3007 | 122.4243 | 60.8093 | 50.2899
2344.7656 | 122.7127 | -61.7706 | 60.5942 | -0.18608 | -0.0010787 | 0.06288 | 0.13021 | -0.0015381 | -0.0007904 | -0.0050202 | 0.054627 | -0.0034778 | 0.063111 | 0.060408 | -0.028713 | 0.00077333 | 0.0041657 | -0.91553 | 60.6079 | -61.94 | 60.5667 | -52.6382 | -61.9308 | 2.7878 | -11.467 | 60.5209 | -61.853 | 60.6583 | -60.5484 | -61.4868 | -61.3998 | -0.16937 | 0.013733 | -0.027466 | 9.1324 | 64.5584 | -0.16022 | 64.7278 | 0.009155 | -0.082397 | -0.073242 | 0.064087 | 1.2222 | 0.37079 | 0.28381 | 0.45319 | 0.36621 | 9.3018 | 122.5067 | 1.3046 | 122.5113 | 122.5479 | 122.374 | 122.3785 | 122.2916 | -122.5342 | -122.4472 | 122.3373 | 122.4289 | 60.8551 | 50.3036
2345.8438 | 122.6074 | -61.9904 | 60.434 | -0.094528 | 0.00041648 | 0.065871 | 0.13192 | 0.0038025 | -0.0003632 | -0.0024566 | -0.082703 | -0.00091423 | 0.063538 | 0.058913 | -0.029781 | 0.0035503 | 0.00074769 | -0.96588 | 60.4019 | -62.146 | 60.3012 | -52.9541 | -62.2009 | 2.7283 | -11.4578 | 60.3973 | -62.059 | 60.3973 | -60.8459 | -61.8164 | -61.6653 | -0.15564 | -0.032043 | -0.13275 | 9.0363 | 64.7186 | -0.21057 | 64.8743 | -0.054932 | -0.068665 | -0.036621 | -0.036621 | 1.1444 | 0.32501 | 0.17395 | 0.39368 | 0.24262 | 9.1919 | 122.4472 | 1.2131 | 122.4564 | 122.5479 | 122.4564 | 122.3923 | 122.3877 | -122.58 | -122.493 | 122.2916 | 122.3877 | 61.0245 | 50.5325
2346.7812 | 122.6944 | -61.8988 | 60.4523 | -0.094528 | 0.00084388 | 0.065657 | 0.12893 | -0.0021789 | -0.0037812 | -0.0035248 | 0.045471 | -0.002196 | 0.06546 | 0.059554 | -0.02914 | 0.00055973 | 0.0018159 | -0.95673 | 60.4706 | -62.059 | 60.3653 | -52.7252 | -62.0453 | 2.6779 | -11.293 | 60.3973 | -61.9995 | 60.4752 | -60.7315 | -61.6699 | -61.5646 | -0.16022 | 0.01831 | -0.086976 | 9.1736 | 64.5767 | -0.14648 | 64.7369 | 0.013733 | -0.10071 | -0.054932 | 0.022888 | 1.1673 | 0.33417 | 0.22888 | 0.43488 | 0.32959 | 9.3338 | 122.4243 | 1.268 | 122.4747 | 122.5296 | 122.3969 | 122.3694 | 122.2961 | -122.5113 | -122.4518 | 122.2641 | 122.374 | 60.9421 | 50.6058
2347.8438 | 122.6028 | -61.972 | 60.4752 | -0.12505 | -0.0015061 | 0.065657 | 0.1315 | 0.0029479 | -0.0057038 | -0.002884 | -0.10101 | 0.00015377 | 0.065033 | 0.062972 | -0.02914 | 0.0016277 | 0.00053409 | -0.90637 | 60.4523 | -62.1323 | 60.2875 | -52.7435 | -62.2467 | 2.536 | -11.3342 | 60.4523 | -62.0316 | 60.4065 | -60.8688 | -61.8576 | -61.6653 | -0.16022 | -0.022888 | -0.18768 | 9.2285 | 64.5081 | -0.27466 | 64.6683 | -0.11444 | -0.059509 | -0.022888 | -0.068665 | 1.1032 | 0.3067 | 0.11444 | 0.36621 | 0.17395 | 9.3887 | 122.4197 | 1.1627 | 122.438 | 122.5845 | 122.4838 | 122.4243 | 122.4243 | -122.6074 | -122.5067 | 122.2595 | 122.3785 | 61.0657 | 50.6378
2348.7656 | 122.7081 | -61.9492 | 60.4477 | -0.12505 | 0.0010575 | 0.064803 | 0.12829 | -0.0034607 | -0.0014312 | -0.00032036 | 0.042419 | -0.0054004 | 0.063538 | 0.05464 | -0.0285 | -8.1274e-05 | 0.0050201 | -0.81024 | 60.4065 | -62.0773 | 60.2463 | -52.4414 | -62.0041 | 2.861 | -11.0458 | 60.3836 | -62.0087 | 60.5026 | -60.672 | -61.6516 | -61.5509 | -0.12817 | -0.041199 | -0.20142 | 9.5078 | 64.8102 | -0.054931 | 64.9384 | 0.073243 | -0.059509 | -0.064087 | 0.054932 | 1.2772 | 0.39825 | 0.29755 | 0.45776 | 0.35706 | 9.6359 | 122.3236 | 1.3367 | 122.5113 | 122.4838 | 122.3923 | 122.3557 | 122.3328 | -122.525 | -122.4564 | 122.1954 | 122.4518 | 61.1389 | 50.9033
2349.8281 | 122.58 | -62.0544 | 60.4065 | -0.14793 | -1.0718e-05 | 0.064162 | 0.13107 | 0.0018799 | -0.0037812 | -0.002884 | -0.0033568 | -0.0032642 | 0.065033 | 0.058486 | -0.029354 | 0.00077333 | 0.00053409 | -0.92926 | 60.3882 | -62.1597 | 60.2463 | -52.5238 | -62.1964 | 2.6321 | -11.0504 | 60.3607 | -62.0819 | 60.3195 | -60.8597 | -61.8347 | -61.734 | -0.10529 | -0.01831 | -0.16022 | 9.5306 | 64.6866 | -0.14191 | 64.7919 | -0.036621 | -0.027466 | -0.045776 | -0.086975 | 1.1948 | 0.32043 | 0.21973 | 0.3479 | 0.24719 | 9.6359 | 122.406 | 1.2222 | 122.4014 | 122.5479 | 122.4426 | 122.4426 | 122.4152 | -122.5662 | -122.4884 | 122.3007 | 122.374 | 61.1252 | 51.004
2350.7656 | 122.6212 | -62.1323 | 60.3012 | -0.06401 | -1.0718e-05 | 0.06523 | 0.12936 | -0.00046988 | -0.0014312 | -0.0043792 | 0.021057 | -0.0032642 | 0.063538 | 0.057631 | -0.027859 | 0.00098693 | 0.0011749 | -0.90179 | 60.2646 | -62.2696 | 60.2234 | -52.5284 | -62.2421 | 2.6459 | -11.0916 | 60.2371 | -62.2055 | 60.2554 | -60.9192 | -61.9034 | -61.7844 | -0.13733 | -0.036621 | -0.077819 | 9.6039 | 64.7781 | -0.10986 | 64.9155 | 0.027466 | -0.073242 | -0.064086 | -0.045776 | 1.2131 | 0.3479 | 0.22888 | 0.42114 | 0.30212 | 9.7412 | 122.493 | 1.2863 | 122.4609 | 122.5342 | 122.4426 | 122.3969 | 122.3694 | -122.5708 | -122.5067 | 122.3557 | 122.3877 | 61.2305 | 51.0406
2351.8438 | 122.6212 | -62.1735 | 60.2417 | -0.094528 | 0.00084388 | 0.065657 | 0.13385 | 0.0029479 | -0.0048492 | -0.0035248 | -0.09491 | -0.0043322 | 0.065888 | 0.059981 | -0.029354 | 0.0044049 | 0.00032049 | -0.88348 | 60.228 | -62.3245 | 60.1547 | -52.5055 | -62.3428 | 2.6047 | -10.8948 | 60.2417 | -62.2147 | 60.2737 | -60.9512 | -61.9675 | -61.8164 | -0.15106 | -0.013733 | -0.086975 | 9.668 | 64.7781 | -0.16937 | 64.9292 | -0.01831 | -0.041199 | 0 | 0.032044 | 1.2222 | 0.35706 | 0.20599 | 0.39825 | 0.24719 | 9.819 | 122.4792 | 1.2634 | 122.4884 | 122.5525 | 122.4564 | 122.4014 | 122.4152 | -122.5662 | -122.4564 | 122.3282 | 122.4472 | 61.29 | 51.2787
2352.7656 | 122.6395 | -61.9583 | 60.466 | -0.1403 | 0.0019119 | 0.065871 | 0.13107 | 0.0014527 | -0.0016448 | -0.0020294 | -0.085754 | -0.0032642 | 0.066315 | 0.059127 | -0.028286 | 0.0018413 | 0.0020295 | -0.89264 | 60.4385 | -62.1506 | 60.3378 | -52.1301 | -62.1231 | 2.9343 | -10.7803 | 60.4065 | -62.027 | 60.4568 | -60.7361 | -61.734 | -61.6058 | -0.19226 | -0.027465 | -0.12817 | 9.8282 | 64.8926 | -0.1648 | 65.0848 | 0.027466 | -0.068665 | -0.059509 | -0.009155 | 1.2222 | 0.35248 | 0.2243 | 0.42114 | 0.29297 | 10.0204 | 122.4884 | 1.2909 | 122.4838 | 122.5891 | 122.4335 | 122.3969 | 122.3648 | -122.6166 | -122.493 | 122.2961 | 122.4152 | 61.0657 | 51.178
2353.8281 | 122.6166 | -62.114 | 60.347 | -0.07164 | 0.00020288 | 0.064589 | 0.13085 | 0.0027343 | -0.0035674 | -0.003952 | -0.039978 | -0.0032642 | 0.063538 | 0.066603 | -0.0285 | 0.00098693 | 0.0028839 | -0.87433 | 60.3149 | -62.2467 | 60.1547 | -52.3453 | -62.3657 | 2.8748 | -11.2244 | 60.2921 | -62.1826 | 60.2646 | -60.9009 | -61.908 | -61.7661 | -0.13275 | -0.032044 | -0.19226 | 9.7687 | 64.9887 | -0.25177 | 65.1215 | -0.11902 | -0.068664 | -0.054932 | -0.082398 | 1.2131 | 0.3479 | 0.20599 | 0.41656 | 0.27466 | 9.9014 | 122.4014 | 1.2817 | 122.4472 | 122.5616 | 122.4747 | 122.4289 | 122.406 | -122.5937 | -122.5296 | 122.2687 | 122.3785 | 61.2396 | 50.8896
2354.7656 | 122.7081 | -62.1918 | 60.1868 | 0.12672 | 0.0010575 | 0.066298 | 0.12829 | 0.00059812 | -0.0022858 | -0.0037384 | 0.039368 | -0.0045458 | 0.063324 | 0.059127 | -0.0285 | 0.0014141 | 0.0022431 | -1.0208 | 60.1273 | -62.3795 | 60.1501 | -52.2583 | -62.3291 | 3.0075 | -11.1099 | 60.1227 | -62.265 | 60.2371 | -60.9009 | -61.8988 | -61.7889 | -0.18768 | -0.05951 | -0.036622 | 9.9335 | 65.1993 | -0.13733 | 65.387 | 0.050354 | -0.073243 | -0.064087 | 0.050354 | 1.2909 | 0.40283 | 0.29297 | 0.47608 | 0.36621 | 10.1212 | 122.5296 | 1.3641 | 122.5021 | 122.5067 | 122.3877 | 122.319 | 122.3145 | -122.5662 | -122.4518 | 122.3419 | 122.4289 | 61.171 | 51.0818
2355.8438 | 122.6257 | -62.2971 | 60.1044 | -0.11742 | 0.00041648 | 0.065657 | 0.13256 | 0.0018799 | -0.0035674 | -0.0026704 | -0.10101 | -0.0034778 | 0.063751 | 0.062117 | -0.029781 | 0.0031231 | 0.0045929 | -0.84686 | 60.0632 | -62.5259 | 59.9762 | -52.3819 | -62.5122 | 2.8381 | -11.2061 | 60.0952 | -62.3291 | 60.0998 | -61.0748 | -62.0773 | -61.9492 | -0.22888 | -0.041199 | -0.12817 | 9.9152 | 65.1352 | -0.21515 | 65.3641 | 0.013733 | -0.032044 | -0.009155 | -0.004578 | 1.2222 | 0.3479 | 0.21973 | 0.37994 | 0.25177 | 10.144 | 122.5021 | 1.2543 | 122.4289 | 122.5891 | 122.4243 | 122.3602 | 122.3923 | -122.6303 | -122.4335 | 122.2733 | 122.3969 | 61.4502 | 51.091
2356.7656 | 122.5845 | -62.3611 | 60.0906 | -0.094528 | -0.00043792 | 0.066298 | 0.13064 | -0.0030335 | -0.0042084 | -0.001175 | -0.030823 | -0.0028368 | 0.065033 | 0.057418 | -0.0285 | 0.00098693 | 0.00053409 | -0.93842 | 60.0586 | -62.5214 | 59.8389 | -52.6245 | -62.4985 | 2.7924 | -11.1282 | 60.0677 | -62.4435 | 60.0082 | -61.1206 | -62.1506 | -62.0407 | -0.16022 | -0.032043 | -0.25177 | 9.7366 | 65.1535 | -0.13733 | 65.3137 | 0.022888 | -0.082397 | -0.022888 | -0.082397 | 1.2405 | 0.32044 | 0.21057 | 0.40283 | 0.29297 | 9.8969 | 122.3602 | 1.3229 | 122.4518 | 122.58 | 122.5113 | 122.4197 | 122.4289 | -122.612 | -122.5342 | 122.2 | 122.3694 | 61.4227 | 51.2329
2357.8281 | 122.6532 | -62.384 | 60.0494 | -0.056381 | 0.0029801 | 0.06523 | 0.13128 | 0.0010253 | -0.0057038 | -0.0060882 | -0.076599 | -0.0019824 | 0.06247 | 0.057845 | -0.030209 | 0.00098693 | 0.0033111 | -0.9201 | 60.022 | -62.5671 | 59.8984 | -52.3727 | -62.6266 | 2.7512 | -11.0687 | 59.9991 | -62.4481 | 60.0449 | -61.1252 | -62.1597 | -61.9995 | -0.18311 | -0.027465 | -0.15106 | 10.0113 | 65.1352 | -0.24262 | 65.3183 | -0.059509 | -0.064087 | -0.050354 | -0.004577 | 1.2589 | 0.38452 | 0.2243 | 0.44861 | 0.28839 | 10.1944 | 122.4655 | 1.3229 | 122.493 | 122.5891 | 122.4472 | 122.406 | 122.3831 | -122.6166 | -122.4976 | 122.2824 | 122.4289 | 61.4639 | 51.3153
2358.7656 | 122.7081 | -62.5534 | 59.8297 | -0.056381 | 0.0029801 | 0.066725 | 0.13064 | -0.0032471 | -0.0016448 | -0.0018158 | 0.057678 | -0.0034778 | 0.062256 | 0.062545 | -0.027218 | -8.1274e-05 | 0.0030975 | -0.89264 | 59.8206 | -62.677 | 59.816 | -52.3865 | -62.6633 | 2.8152 | -11.1832 | 59.7885 | -62.5809 | 59.8892 | -61.2213 | -62.233 | -62.1506 | -0.1236 | -0.009155 | -0.013733 | 10.1669 | 65.3687 | -0.10986 | 65.4922 | 0.013733 | -0.027466 | -0.041199 | 0.059509 | 1.3321 | 0.40283 | 0.32044 | 0.4303 | 0.3479 | 10.2905 | 122.493 | 1.3596 | 122.4701 | 122.4976 | 122.3694 | 122.374 | 122.3419 | -122.5067 | -122.4106 | 122.3694 | 122.4426 | 61.6608 | 51.3702
2359.8281 | 122.7036 | -62.6358 | 59.7656 | -0.1403 | 0.0025529 | 0.06523 | 0.12936 | 0.0016663 | -0.002713 | -0.0018158 | 0.024109 | -0.0041186 | 0.065033 | 0.061263 | -0.030636 | 0.0054729 | 0.0052337 | -0.89722 | 59.7336 | -62.7457 | 59.7244 | -52.4094 | -62.7411 | 2.5772 | -11.1465 | 59.697 | -62.6724 | 59.7153 | -61.2122 | -62.3245 | -62.2284 | -0.10986 | -0.032043 | -0.041199 | 10.2264 | 65.213 | -0.10529 | 65.3229 | 0.004578 | -0.036621 | -0.068665 | -0.050354 | 1.4236 | 0.40741 | 0.31128 | 0.44403 | 0.3479 | 10.3363 | 122.4701 | 1.4603 | 122.3877 | 122.4792 | 122.3694 | 122.3694 | 122.3328 | -122.5113 | -122.438 | 122.3602 | 122.3511 | 61.7386 | 51.4893
2360.7656 | 122.6532 | -62.8098 | 59.5871 | -0.16319 | 0.0016983 | 0.066725 | 0.13043 | 0.0018799 | -0.0054902 | -0.002243 | -0.021667 | -0.0036914 | 0.063111 | 0.058058 | -0.029354 | 0.00098693 | 0.0035247 | -0.91553 | 59.5779 | -62.9425 | 59.5367 | -52.7069 | -63.0295 | 2.4765 | -11.5585 | 59.5551 | -62.8372 | 59.5917 | -61.528 | -62.5442 | -62.4207 | -0.13275 | -0.009155 | -0.050354 | 10.1028 | 65.2863 | -0.21973 | 65.419 | -0.086975 | -0.027466 | -0.032043 | 0.004578 | 1.2817 | 0.3891 | 0.2655 | 0.41656 | 0.29297 | 10.2356 | 122.4792 | 1.3092 | 122.4289 | 122.5204 | 122.3923 | 122.3877 | 122.3648 | -122.5296 | -122.4243 | 122.3465 | 122.4014 | 61.8942 | 51.2512
2361.8438 | 122.6898 | -62.9608 | 59.4406 | -0.13267 | 0.0010575 | 0.065016 | 0.12829 | 0.0010253 | -0.0046356 | 0.0016022 | 0.011902 | -0.0051868 | 0.063538 | 0.059767 | -0.029995 | 0.00013253 | 0.0018159 | -0.90637 | 59.3903 | -63.1165 | 59.4131 | -52.9404 | -63.0615 | 2.504 | -11.3068 | 59.3811 | -63.0203 | 59.4681 | -61.6333 | -62.6587 | -62.558 | -0.15564 | -0.050354 | -0.027466 | 10.0204 | 65.4648 | -0.10071 | 65.6204 | 0.054932 | -0.05951 | -0.059509 | 0.027466 | 1.3275 | 0.40283 | 0.30212 | 0.46234 | 0.36163 | 10.1761 | 122.5296 | 1.387 | 122.4884 | 122.5067 | 122.4014 | 122.3511 | 122.3419 | -122.5571 | -122.4609 | 122.374 | 122.4289 | 62.0544 | 51.6541
2362.7656 | 122.6944 | -63.0661 | 59.285 | -0.13267 | -0.00086512 | 0.066084 | 0.13085 | -0.0021789 | -0.004422 | -0.001175 | 0.021057 | -0.0054004 | 0.063965 | 0.057204 | -0.028927 | -0.00050847 | 0.0050201 | -0.85144 | 59.2667 | -63.2492 | 59.2667 | -53.0502 | -63.2126 | 2.449 | -11.2244 | 59.2392 | -63.1302 | 59.3811 | -61.7111 | -62.7457 | -62.6404 | -0.18311 | -0.01831 | -0.01831 | 10.0159 | 65.5151 | -0.14648 | 65.6982 | 0.036622 | -0.064087 | -0.045776 | 0.096131 | 1.355 | 0.42572 | 0.32043 | 0.48981 | 0.38452 | 10.199 | 122.5159 | 1.4191 | 122.5113 | 122.5159 | 122.3694 | 122.3328 | 122.3053 | -122.5342 | -122.4152 | 122.3328 | 122.4472 | 62.2147 | 51.8417
2363.8281 | 122.5983 | -63.1668 | 59.285 | -0.06401 | 0.0021255 | 0.067366 | 0.13299 | 0.0025207 | -0.0048492 | -0.0041656 | -0.13458 | -0.0028368 | 0.063324 | 0.064894 | -0.025722 | 0.0056867 | 0.0016021 | -0.91095 | 59.3079 | -63.3179 | 59.0973 | -53.1692 | -63.4232 | 2.1973 | -11.2335 | 59.2804 | -63.2263 | 59.1339 | -61.6379 | -62.915 | -62.851 | -0.15106 | 0.022888 | -0.18768 | 9.9976 | 65.3641 | -0.25635 | 65.5151 | -0.10529 | -0.059509 | -0.004577 | -0.15106 | 1.5289 | 0.31586 | 0.25177 | 0.37537 | 0.31128 | 10.1486 | 122.4152 | 1.5884 | 122.3602 | 122.6257 | 122.5067 | 122.4747 | 122.4472 | -122.6028 | -122.5113 | 122.2641 | 122.3007 | 62.2559 | 51.9333
2364.7656 | 122.5937 | -63.1165 | 59.3353 | -0.094528 | -0.00022432 | 0.066512 | 0.13256 | 0.00017092 | -0.0003632 | -0.0013886 | -0.036926 | -0.003905 | 0.064179 | 0.055281 | -0.028713 | 0.0026959 | 0.0022431 | -0.94299 | 59.3216 | -63.2675 | 59.1202 | -52.9312 | -63.3179 | 2.1378 | -11.261 | 59.3262 | -63.1714 | 59.285 | -61.8256 | -62.8876 | -62.7548 | -0.15106 | -0.013733 | -0.21515 | 10.1852 | 65.2542 | -0.20142 | 65.4053 | -0.050354 | -0.054932 | -0.009155 | -0.050354 | 1.2909 | 0.36163 | 0.22888 | 0.41657 | 0.28381 | 10.3363 | 122.3877 | 1.3458 | 122.4564 | 122.5891 | 122.4976 | 122.438 | 122.4426 | -122.6028 | -122.5067 | 122.2366 | 122.4014 | 62.1735 | 51.8555
2365.8281 | 122.5983 | -63.1119 | 59.3628 | -0.17082 | -0.0012923 | 0.064375 | 0.13171 | -0.00046988 | -0.0074128 | -0.004593 | -0.033874 | -0.0036914 | 0.064606 | 0.058058 | -0.028072 | -8.1274e-05 | 0.00074769 | -0.89722 | 59.3491 | -63.2538 | 59.2026 | -52.8625 | -63.2996 | 2.3392 | -11.1694 | 59.317 | -63.1439 | 59.2987 | -61.8118 | -62.8738 | -62.7411 | -0.14191 | -0.013733 | -0.16022 | 10.2493 | 65.451 | -0.18768 | 65.593 | -0.045777 | -0.032044 | -0.045776 | -0.064087 | 1.3 | 0.37079 | 0.23804 | 0.40283 | 0.27008 | 10.3912 | 122.4564 | 1.3321 | 122.4426 | 122.6028 | 122.4609 | 122.4609 | 122.4289 | -122.6166 | -122.5067 | 122.3145 | 122.4106 | 62.2147 | 51.9424
2366.7656 | 122.612 | -63.2492 | 59.2072 | -0.079269 | -1.0718e-05 | 0.063521 | 0.13235 | 0.0046569 | -0.0018586 | 0.00053404 | -0.039978 | -0.0030506 | 0.064606 | 0.065962 | -0.0285 | 0.0016277 | -0.00010671 | -0.93842 | 59.1888 | -63.3911 | 59.0012 | -53.0731 | -63.4598 | 2.2476 | -11.1832 | 59.1339 | -63.3362 | 59.1385 | -61.9308 | -63.0112 | -62.8922 | -0.14191 | -0.01831 | -0.20599 | 10.1761 | 65.4968 | -0.21057 | 65.6387 | -0.068665 | -0.086975 | -0.073242 | -0.068664 | 1.3184 | 0.35706 | 0.23804 | 0.44403 | 0.32501 | 10.318 | 122.3923 | 1.4053 | 122.4747 | 122.58 | 122.4701 | 122.4381 | 122.3831 | -122.5983 | -122.5433 | 122.2504 | 122.3877 | 62.3108 | 52.066
2367.8438 | 122.5891 | -63.3179 | 59.111 | -0.11742 | -0.00022432 | 0.066512 | 0.1332 | 0.0012391 | -0.0039948 | -0.003952 | -0.09491 | -0.0030506 | 0.066315 | 0.060836 | -0.027645 | 0.0050457 | -0.00096131 | -0.9201 | 59.0652 | -63.4872 | 58.9828 | -53.0365 | -63.5193 | 2.1835 | -11.1511 | 59.0652 | -63.4094 | 59.0927 | -62.0041 | -63.089 | -62.9425 | -0.16937 | -0.045776 | -0.12817 | 10.2814 | 65.5014 | -0.20142 | 65.6708 | -0.032043 | -0.091553 | -0.045776 | -0.018311 | 1.3138 | 0.37537 | 0.22888 | 0.46692 | 0.32044 | 10.4507 | 122.4701 | 1.4053 | 122.5021 | 122.5525 | 122.4747 | 122.3831 | 122.3831 | -122.5983 | -122.5204 | 122.3007 | 122.4106 | 62.3978 | 52.1667
2368.7656 | 122.5891 | -63.3591 | 59.0973 | -0.13267 | 0.00020288 | 0.065657 | 0.13021 | 0.00038452 | -0.0046356 | -0.0018158 | 0.027161 | -0.0028368 | 0.062897 | 0.061476 | -0.026363 | 0.0018413 | 0.0022431 | -0.90637 | 59.0561 | -63.4872 | 58.9417 | -53.0548 | -63.5422 | 2.2247 | -11.3068 | 59.024 | -63.4003 | 59.0332 | -62.0361 | -63.0798 | -62.9974 | -0.12817 | -0.041199 | -0.15564 | 10.3043 | 65.5838 | -0.1831 | 65.712 | -0.054931 | -0.041199 | -0.073242 | -0.064087 | 1.3229 | 0.36163 | 0.27924 | 0.40283 | 0.32044 | 10.4324 | 122.4289 | 1.3641 | 122.4335 | 122.5433 | 122.4243 | 122.4152 | 122.3831 | -122.5845 | -122.4976 | 122.3007 | 122.3923 | 62.4527 | 52.0523
2369.8281 | 122.6395 | -63.4598 | 58.96 | -0.086899 | -0.00043792 | 0.065871 | 0.13128 | 0.0035889 | -0.002713 | -0.0026704 | -0.058289 | -0.0043322 | 0.062897 | 0.061263 | -0.029354 | 0.0037641 | -0.0030975 | -0.96588 | 58.9783 | -63.6246 | 58.8364 | -53.1097 | -63.6429 | 2.3392 | -11.412 | 58.9371 | -63.5468 | 58.9462 | -62.114 | -63.2034 | -63.0798 | -0.16479 | 0.01831 | -0.1236 | 10.35 | 65.799 | -0.1831 | 65.9637 | -0.01831 | -0.086975 | -0.022888 | -0.013733 | 1.3458 | 0.37994 | 0.25635 | 0.46692 | 0.34332 | 10.5148 | 122.4609 | 1.4328 | 122.493 | 122.6028 | 122.4838 | 122.438 | 122.3969 | -122.5845 | -122.5067 | 122.2961 | 122.406 | 62.4939 | 52.0477
2370.7656 | 122.7081 | -63.3316 | 59.0332 | -0.056381 | 0.00041648 | 0.066084 | 0.13 | -0.0026063 | -0.0022858 | -0.0024566 | 0.0057984 | -0.0028368 | 0.066529 | 0.054 | -0.030849 | 0.0016277 | 0.00074769 | -0.90179 | 59.0195 | -63.4781 | 58.8135 | -52.9861 | -63.3453 | 2.298 | -11.4395 | 58.9691 | -63.4094 | 59.1248 | -61.8942 | -62.9745 | -62.9013 | -0.14648 | -0.013733 | -0.21973 | 10.3455 | 65.6296 | -0.013733 | 65.7761 | 0.13275 | -0.07782 | -0.064087 | 0.091553 | 1.4374 | 0.4303 | 0.35706 | 0.50812 | 0.43488 | 10.4919 | 122.2916 | 1.5152 | 122.5342 | 122.4976 | 122.3785 | 122.3511 | 122.3007 | -122.5113 | -122.4426 | 122.1451 | 122.4564 | 62.4298 | 51.8921
2371.8594 | 122.6807 | -63.4232 | 58.9325 | -0.10216 | -1.0718e-05 | 0.066939 | 0.1315 | 0.0070069 | -0.0007904 | 0.00074764 | -0.064392 | -0.0026232 | 0.06546 | 0.060836 | -0.029568 | 0.0018413 | 0.0063019 | -1.0117 | 58.9508 | -63.62 | 58.873 | -52.8259 | -63.6475 | 2.1469 | -11.3022 | 58.9828 | -63.4598 | 59.0057 | -62.0773 | -63.1577 | -63.0157 | -0.19684 | 0.018311 | -0.059509 | 10.5972 | 65.5701 | -0.2243 | 65.7669 | -0.027466 | -0.036621 | 0.050354 | 0.073242 | 1.3458 | 0.40741 | 0.2655 | 0.44403 | 0.30212 | 10.7941 | 122.493 | 1.3824 | 122.4655 | 122.5708 | 122.4426 | 122.374 | 122.406 | -122.5525 | -122.3923 | 122.2961 | 122.4289 | 62.4115 | 52.121
2372.7656 | 122.6669 | -63.3545 | 59.0378 | -0.086899 | 0.00041648 | 0.064162 | 0.13043 | -0.0019653 | -0.0035674 | -0.002884 | 0.018005 | -0.0026232 | 0.065033 | 0.057418 | -0.030849 | 0.0020551 | 0.0020295 | -0.95215 | 58.9737 | -63.533 | 58.96 | -52.6703 | -63.5284 | 2.4078 | -11.2473 | 58.9554 | -63.4232 | 59.0195 | -62.0087 | -63.0844 | -62.9745 | -0.17853 | -0.064087 | -0.07782 | 10.6842 | 65.7623 | -0.17395 | 65.9409 | 0.004578 | -0.068665 | -0.082398 | -0.018311 | 1.3458 | 0.37994 | 0.27008 | 0.44861 | 0.33875 | 10.8627 | 122.493 | 1.4145 | 122.4426 | 122.5067 | 122.3785 | 122.3282 | 122.3099 | -122.5708 | -122.4609 | 122.3145 | 122.374 | 62.4023 | 52.1072
2373.8281 | 122.6212 | -63.4964 | 58.9417 | -0.10979 | -1.0718e-05 | 0.066298 | 0.13342 | 0.0025207 | -0.0020722 | -0.0033112 | -0.073547 | -0.0013416 | 0.061615 | 0.059767 | -0.029781 | 0.0022687 | 0.00096129 | -0.98877 | 58.9508 | -63.6612 | 58.7585 | -52.9266 | -63.7207 | 2.3666 | -11.5173 | 58.9096 | -63.5559 | 58.8867 | -62.1368 | -63.2401 | -63.1073 | -0.1648 | 0.009156 | -0.18311 | 10.5698 | 65.863 | -0.2243 | 66.0278 | -0.059509 | -0.059509 | -0.032043 | -0.054931 | 1.3596 | 0.3891 | 0.25635 | 0.44861 | 0.31586 | 10.7346 | 122.4197 | 1.4191 | 122.4426 | 122.612 | 122.4655 | 122.4472 | 122.406 | -122.6028 | -122.4976 | 122.2549 | 122.3831 | 62.5076 | 51.9791
2374.7656 | 122.6761 | -63.4781 | 58.8776 | -0.094528 | 0.00041648 | 0.065871 | 0.13235 | 0.00081172 | -0.002713 | -0.0026704 | 0.033264 | -0.0051868 | 0.063111 | 0.059554 | -0.028072 | 0.0026959 | 0.0020295 | -0.91553 | 58.8409 | -63.6749 | 58.8547 | -52.7527 | -63.6292 | 2.4719 | -11.3525 | 58.8181 | -63.5513 | 58.9279 | -62.0407 | -63.1393 | -63.0432 | -0.19684 | -0.036621 | -0.022888 | 10.7254 | 65.95 | -0.15106 | 66.1469 | 0.045777 | -0.073243 | -0.059509 | 0.050354 | 1.4374 | 0.43487 | 0.33875 | 0.50812 | 0.41199 | 10.9222 | 122.5296 | 1.5106 | 122.4792 | 122.5159 | 122.3694 | 122.319 | 122.2961 | -122.5525 | -122.4289 | 122.3328 | 122.406 | 62.5626 | 52.1255
2375.8281 | 122.6395 | -63.6383 | 58.7997 | -0.06401 | 0.0014847 | 0.065443 | 0.13128 | 0.0027343 | -0.002713 | -0.0033112 | -0.11017 | -0.0024096 | 0.065033 | 0.067885 | -0.030422 | 0.0031231 | 0.0011749 | -0.89264 | 58.7723 | -63.8168 | 58.6533 | -52.977 | -63.8718 | 2.2934 | -11.5585 | 58.7173 | -63.707 | 58.7585 | -62.2513 | -63.3957 | -63.2538 | -0.17853 | -0.027466 | -0.14648 | 10.6613 | 65.9317 | -0.23346 | 66.1102 | -0.054932 | -0.068664 | -0.082398 | -0.041199 | 1.387 | 0.38452 | 0.24262 | 0.45319 | 0.31128 | 10.8398 | 122.4701 | 1.4557 | 122.4655 | 122.5891 | 122.4243 | 122.4106 | 122.3557 | -122.6166 | -122.5067 | 122.2916 | 122.3969 | 62.7457 | 52.0798
2376.7656 | 122.6303 | -63.7894 | 58.6395 | -0.094528 | -0.00022432 | 0.068007 | 0.13235 | 0.00059812 | -0.0035674 | -0.0013886 | -0.088806 | -0.0024096 | 0.065247 | 0.067031 | -0.02914 | 0.0012005 | -0.0028839 | -0.90637 | 58.5983 | -63.9359 | 58.5114 | -53.2471 | -63.9496 | 2.1561 | -11.5997 | 58.5892 | -63.8489 | 58.6258 | -62.3749 | -63.5101 | -63.3682 | -0.14648 | -0.041198 | -0.12817 | 10.5423 | 65.9454 | -0.16022 | 66.0919 | -0.013733 | -0.059509 | -0.050354 | -0.013733 | 1.4145 | 0.42114 | 0.27924 | 0.48065 | 0.33875 | 10.6888 | 122.4472 | 1.474 | 122.4747 | 122.5342 | 122.438 | 122.3877 | 122.3785 | -122.5754 | -122.4884 | 122.3007 | 122.4152 | 62.883 | 52.1896
2377.8281 | 122.6166 | -63.8351 | 58.6533 | -0.086899 | -1.0718e-05 | 0.065443 | 0.1315 | -4.2682e-05 | -0.0014312 | -0.002884 | -0.0033568 | -0.0045458 | 0.064179 | 0.061904 | -0.0285 | 0.00077333 | 0.0060883 | -0.97504 | 58.5617 | -64.0091 | 58.4244 | -53.2471 | -64.0457 | 2.2568 | -11.9797 | 58.5205 | -63.9221 | 58.493 | -62.4756 | -63.5788 | -63.5605 | -0.17395 | -0.091552 | -0.22888 | 10.5881 | 66.0919 | -0.21057 | 66.2659 | -0.036621 | -0.086975 | -0.13275 | -0.16022 | 1.3596 | 0.27466 | 0.25635 | 0.36163 | 0.34332 | 10.762 | 122.4335 | 1.4465 | 122.4152 | 122.5708 | 122.4426 | 122.3969 | 122.3557 | -122.6624 | -122.5754 | 122.2595 | 122.3282 | 62.8601 | 51.8555
2378.7656 | 122.5891 | -63.826 | 58.6212 | -0.10216 | -1.0718e-05 | 0.064162 | 0.13021 | -0.0023925 | -0.006131 | -0.00010676 | -0.00030524 | -0.0030506 | 0.06482 | 0.056563 | -0.02914 | 0.00055973 | 0.0043793 | -0.9201 | 58.6075 | -63.9587 | 58.4885 | -53.064 | -64.0091 | 2.4673 | -11.7783 | 58.5342 | -63.8763 | 58.5663 | -62.4023 | -63.5284 | -63.446 | -0.13275 | -0.013733 | -0.13275 | 10.762 | 66.2933 | -0.18311 | 66.4261 | -0.050354 | -0.050354 | -0.086975 | -0.054932 | 1.4236 | 0.37994 | 0.29755 | 0.4303 | 0.3479 | 10.8948 | 122.4472 | 1.474 | 122.4426 | 122.5662 | 122.4106 | 122.4335 | 122.3602 | -122.58 | -122.4976 | 122.3145 | 122.3923 | 62.9059 | 52.0477
2379.8281 | 122.6257 | -63.8626 | 58.5754 | -0.18608 | 0.0012711 | 0.067366 | 0.13427 | 0.00017092 | -0.0042084 | -0.001175 | -0.085754 | -0.0028368 | 0.065033 | 0.065535 | -0.028286 | 0.0022687 | 0.0041657 | -0.91553 | 58.5526 | -64.0182 | 58.461 | -53.0045 | -64.0182 | 2.4445 | -11.4761 | 58.5434 | -63.8947 | 58.5571 | -62.439 | -63.5971 | -63.4415 | -0.15564 | -0.022888 | -0.11444 | 10.8582 | 66.3071 | -0.15564 | 66.4627 | 0 | -0.032043 | -0.032043 | -0.01831 | 1.4236 | 0.42114 | 0.2655 | 0.45319 | 0.29755 | 11.0138 | 122.4792 | 1.4557 | 122.4518 | 122.5708 | 122.438 | 122.4152 | 122.406 | -122.5937 | -122.4701 | 122.3236 | 122.4197 | 62.9471 | 52.3865
2380.7656 | 122.5754 | -63.9267 | 58.5114 | 0.14961 | -0.0027877 | 0.064375 | 0.13128 | 0.0020935 | -0.0035674 | -0.0020294 | -0.012512 | -0.0036914 | 0.06482 | 0.069808 | -0.027859 | 0.00055973 | 0.00032049 | -0.97504 | 58.5388 | -64.0732 | 58.3237 | -53.0731 | -64.151 | 2.3575 | -12.3367 | 58.4747 | -64.0045 | 58.4518 | -62.5122 | -63.6566 | -63.5376 | -0.14648 | 0.027465 | -0.18768 | 10.8536 | 66.2842 | -0.2243 | 66.4307 | -0.07782 | -0.07782 | -0.036622 | -0.05951 | 1.4145 | 0.3891 | 0.27008 | 0.46692 | 0.3479 | 11.0001 | 122.3969 | 1.4923 | 122.4564 | 122.612 | 122.4792 | 122.4655 | 122.4014 | -122.5845 | -122.5159 | 122.2504 | 122.3785 | 62.9517 | 51.59
2381.8594 | 122.6486 | -63.9038 | 58.4656 | -0.1403 | 0.00063028 | 0.065657 | 0.13342 | 0.0052979 | -0.0037812 | -0.0030976 | -0.067444 | -0.0032642 | 0.064606 | 0.064467 | -0.028286 | 0.0031231 | -0.00010671 | -0.98877 | 58.4564 | -64.119 | 58.3191 | -52.9633 | -64.1647 | 2.3254 | -11.4487 | 58.4244 | -63.9908 | 58.4793 | -62.4985 | -63.652 | -63.4964 | -0.21515 | -0.009155 | -0.14648 | 10.9406 | 66.2292 | -0.26092 | 66.4444 | -0.045776 | -0.086975 | -0.041199 | 0.013733 | 1.4053 | 0.40741 | 0.25177 | 0.49439 | 0.33874 | 11.1557 | 122.4381 | 1.4923 | 122.4701 | 122.5754 | 122.4152 | 122.3602 | 122.3282 | -122.5845 | -122.4564 | 122.2229 | 122.3831 | 62.915 | 52.4551
2382.7656 | 122.612 | -63.7802 | 58.6166 | -0.10979 | -1.0718e-05 | 0.066939 | 0.13214 | -0.0013245 | -0.0018586 | 0.00010684 | -0.055237 | -0.0034778 | 0.064179 | 0.062117 | -0.027004 | 0.0012005 | 0.0018159 | -0.94299 | 58.6166 | -63.9725 | 58.4473 | -52.7939 | -63.9954 | 2.4582 | -11.3663 | 58.5754 | -63.8718 | 58.6029 | -62.3566 | -63.501 | -63.3865 | -0.19226 | 0 | -0.16937 | 10.9863 | 66.2384 | -0.21515 | 66.4307 | -0.022888 | -0.091553 | -0.041199 | -0.013733 | 1.4236 | 0.39368 | 0.27923 | 0.48523 | 0.37079 | 11.1786 | 122.4197 | 1.5152 | 122.4747 | 122.5891 | 122.4472 | 122.3969 | 122.3557 | -122.5891 | -122.4884 | 122.2275 | 122.3831 | 62.8372 | 52.4139
2383.8438 | 122.6212 | -63.9771 | 58.3878 | -0.14793 | -0.0010787 | 0.067793 | 0.13192 | 0.0044433 | -0.0046356 | -0.0054474 | 0.0027466 | -0.0043322 | 0.063111 | 0.057418 | -0.029568 | 0.00055973 | 0.00074769 | -0.9613 | 58.3923 | -64.1281 | 58.3191 | -52.8717 | -64.1602 | 2.4902 | -11.3571 | 58.3557 | -64.0503 | 58.3649 | -62.4573 | -63.6017 | -63.5239 | -0.15106 | 0.004578 | -0.068664 | 11.1053 | 66.4673 | -0.1831 | 66.6183 | -0.032043 | -0.073242 | -0.032043 | -0.022888 | 1.5198 | 0.45319 | 0.37537 | 0.52643 | 0.44861 | 11.2564 | 122.4472 | 1.593 | 122.4152 | 122.5204 | 122.406 | 122.3694 | 122.3328 | -122.5159 | -122.438 | 122.2961 | 122.3419 | 63.0157 | 52.6199
2384.7656 | 122.699 | -63.826 | 58.5983 | -0.079269 | 0.00084388 | 0.066939 | 0.13256 | 0.0018799 | -0.0031402 | -0.00074776 | -0.10406 | -0.0030506 | 0.065247 | 0.060195 | -0.029781 | 0.0035503 | 0.0013885 | -0.88348 | 58.5114 | -64.0778 | 58.4198 | -52.739 | -64.0686 | 2.5635 | -12.1445 | 58.5251 | -63.9267 | 58.5342 | -62.3199 | -63.5834 | -63.533 | -0.25177 | -0.086975 | -0.17853 | 11.087 | 66.3895 | -0.24261 | 66.6412 | 0.009155 | -0.10071 | -0.073243 | -0.064087 | 1.506 | 0.29297 | 0.24262 | 0.39368 | 0.34332 | 11.3388 | 122.4976 | 1.6068 | 122.4609 | 122.5891 | 122.4518 | 122.3373 | 122.3511 | -122.6761 | -122.525 | 122.2458 | 122.3602 | 62.9425 | 51.6815
2385.7656 | 122.58 | -64.064 | 58.4015 | -0.010605 | -1.0718e-05 | 0.067366 | 0.1332 | 0.0018799 | -0.0035674 | 0.00010684 | -0.015564 | -0.0036914 | 0.065033 | 0.056777 | -0.027645 | 0.0022687 | 0.00096129 | -1.0574 | 58.3878 | -64.1876 | 58.1863 | -52.977 | -64.2563 | 2.5726 | -12.2543 | 58.3466 | -64.0961 | 58.3328 | -62.5809 | -63.7436 | -63.652 | -0.1236 | -0.013733 | -0.21515 | 11.087 | 66.6367 | -0.19226 | 66.7603 | -0.068665 | -0.032043 | -0.054931 | -0.068664 | 1.4832 | 0.41199 | 0.32043 | 0.44403 | 0.35248 | 11.2106 | 122.374 | 1.5152 | 122.4289 | 122.5754 | 122.4426 | 122.4518 | 122.4106 | -122.5891 | -122.4976 | 122.2504 | 122.3969 | 63.0066 | 51.8097
2386.8594 | 122.5891 | -64.1556 | 58.2733 | -0.17082 | 0.00020288 | 0.066939 | 0.13427 | 0.00059812 | -0.0033538 | -0.00096136 | -0.06134 | -0.0045458 | 0.065033 | 0.06639 | -0.028927 | 0.0031231 | 0.0016021 | -0.88348 | 58.2596 | -64.325 | 58.0856 | -53.0273 | -64.4302 | 2.504 | -11.0504 | 58.255 | -64.2288 | 58.2184 | -62.7182 | -63.8901 | -63.7711 | -0.16937 | -0.013732 | -0.18768 | 11.1282 | 66.6595 | -0.27466 | 66.8289 | -0.10529 | -0.073242 | -0.01831 | -0.054931 | 1.4374 | 0.38452 | 0.2655 | 0.45776 | 0.33874 | 11.2976 | 122.4106 | 1.5106 | 122.4472 | 122.5845 | 122.4838 | 122.4152 | 122.4106 | -122.5983 | -122.5021 | 122.2412 | 122.374 | 63.2721 | 53.1052
2387.7656 | 122.6486 | -64.1693 | 58.2642 | -0.086899 | -0.00065152 | 0.065657 | 0.13299 | -0.00068368 | -0.0037812 | -0.0033112 | -0.039978 | -0.0043322 | 0.064606 | 0.064467 | -0.028713 | 0.0020551 | 0.0011749 | -0.91553 | 58.2504 | -64.3387 | 58.1085 | -52.9587 | -64.357 | 2.6001 | -11.0413 | 58.2184 | -64.2288 | 58.2321 | -62.6587 | -63.8397 | -63.739 | -0.16937 | -0.013733 | -0.15564 | 11.2106 | 66.7694 | -0.18768 | 66.9388 | -0.018311 | -0.059509 | -0.045776 | -0.032043 | 1.5106 | 0.4303 | 0.32959 | 0.48981 | 0.3891 | 11.38 | 122.4472 | 1.5701 | 122.4609 | 122.5891 | 122.4472 | 122.4197 | 122.3877 | -122.6028 | -122.493 | 122.2778 | 122.4014 | 63.2538 | 53.1281
2388.8438 | 122.6944 | -64.2242 | 58.1314 | -0.010605 | -0.0015061 | 0.068434 | 0.13427 | -0.0011109 | -0.0020722 | -0.0018158 | -0.012512 | -0.0041186 | 0.065033 | 0.058058 | -0.027859 | 0.00098693 | 0.00053409 | -0.8606 | 58.0902 | -64.3982 | 58.0994 | -52.8671 | -64.3799 | 2.7054 | -11.2427 | 58.0719 | -64.3112 | 58.2092 | -62.6862 | -63.858 | -63.7436 | -0.17395 | -0.041199 | -0.032044 | 11.3571 | 66.9296 | -0.15564 | 67.1036 | 0.01831 | -0.086975 | -0.05951 | 0.07782 | 1.5381 | 0.48065 | 0.36621 | 0.56763 | 0.45319 | 11.5311 | 122.4976 | 1.6251 | 122.5204 | 122.4884 | 122.3831 | 122.3145 | 122.2961 | -122.5296 | -122.4426 | 122.3236 | 122.4335 | 63.3636 | 52.9816
2389.7656 | 122.5891 | -64.3707 | 58.0719 | -0.23186 | -0.00065152 | 0.065443 | 0.13235 | -0.0060241 | -0.0050628 | -0.002243 | -0.036926 | -0.0026232 | 0.066742 | 0.057845 | -0.028286 | 0.0020551 | 0.00074769 | -0.9201 | 58.1131 | -64.5035 | 57.8934 | -53.1692 | -64.5401 | 2.5269 | -11.0504 | 58.0307 | -64.4028 | 58.0124 | -62.8693 | -64.0411 | -63.945 | -0.13275 | 0.041199 | -0.17853 | 11.2015 | 66.8976 | -0.16937 | 67.0303 | -0.036621 | -0.032043 | -0.041198 | -0.059509 | 1.5015 | 0.42572 | 0.32959 | 0.45776 | 0.36163 | 11.3342 | 122.3969 | 1.5335 | 122.4152 | 122.6166 | 122.4335 | 122.4838 | 122.4014 | -122.5754 | -122.4747 | 122.2641 | 122.3831 | 63.4506 | 53.3203
2390.8281 | 122.7081 | -64.2242 | 58.0582 | -0.14793 | 0.00084388 | 0.068648 | 0.13513 | 0.0027343 | 0.000705 | -0.00096136 | -0.027771 | -0.003905 | 0.063538 | 0.058486 | -0.02914 | 0.0020551 | 0.0033111 | -0.85602 | 58.049 | -64.4485 | 57.93 | -53.0731 | -64.2838 | 2.7328 | -10.5286 | 58.0399 | -64.3387 | 58.1818 | -62.6999 | -63.858 | -63.7665 | -0.2243 | -0.009156 | -0.12817 | 11.1511 | 66.9571 | -0.059509 | 67.1814 | 0.16479 | -0.11444 | -0.018311 | 0.1236 | 1.5244 | 0.45776 | 0.36621 | 0.57221 | 0.48065 | 11.3754 | 122.3785 | 1.6388 | 122.5204 | 122.4976 | 122.3785 | 122.2733 | 122.2641 | -122.5067 | -122.3969 | 122.1542 | 122.406 | 63.3682 | 53.6957
2391.7656 | 122.7036 | -64.2746 | 58.0811 | -0.18608 | -0.00022432 | 0.066725 | 0.13406 | -0.0019653 | 6.4004e-05 | -0.00032036 | -0.064392 | -0.0032642 | 0.063965 | 0.055281 | -0.02914 | 0.00077333 | 0.0022431 | -0.85144 | 58.0856 | -64.4257 | 57.8659 | -53.064 | -64.2654 | 2.8427 | -10.5423 | 58.0261 | -64.3662 | 58.1589 | -62.709 | -63.9038 | -63.7939 | -0.15106 | 0.004577 | -0.21515 | 11.2106 | 67.1173 | 0.009155 | 67.2684 | 0.16022 | -0.091553 | -0.054932 | 0.07782 | 1.5656 | 0.48065 | 0.37079 | 0.57221 | 0.46234 | 11.3617 | 122.2916 | 1.6571 | 122.525 | 122.5113 | 122.3923 | 122.3602 | 122.3007 | -122.5067 | -122.4472 | 122.1405 | 122.4335 | 63.4232 | 53.7323
2392.8281 | 122.6532 | -64.5264 | 57.8888 | -0.10979 | -1.0718e-05 | 0.06523 | 0.13449 | 0.0010253 | -0.004422 | -0.0033112 | -0.085754 | -0.0032642 | 0.063538 | 0.065962 | -0.030209 | 0.0031231 | -0.0018157 | -0.88348 | 57.8751 | -64.6866 | 57.7835 | -53.0777 | -64.6957 | 2.5909 | -11.0687 | 57.9117 | -64.5401 | 57.9025 | -62.9929 | -64.183 | -64.0732 | -0.16022 | -0.013733 | -0.10529 | 11.4487 | 67.1173 | -0.16937 | 67.2775 | -0.009156 | -0.013733 | 0.022888 | 0.013733 | 1.5335 | 0.45319 | 0.34332 | 0.46692 | 0.35706 | 11.6089 | 122.4701 | 1.5472 | 122.4426 | 122.5616 | 122.4518 | 122.4014 | 122.438 | -122.5754 | -122.4289 | 122.3099 | 122.4289 | 63.6429 | 53.4576
2393.7656 | 122.5754 | -64.6545 | 57.7744 | -0.13267 | 0.0027665 | 0.068434 | 0.13555 | -0.00046988 | -0.0033538 | -0.0013886 | -0.10406 | -0.0030506 | 0.063538 | 0.061476 | -0.031063 | 0.0020551 | 0.0039521 | -0.88806 | 57.811 | -64.7964 | 57.6462 | -53.2883 | -64.8285 | 2.5909 | -12.117 | 57.7698 | -64.7141 | 57.7377 | -63.1393 | -64.3295 | -64.2242 | -0.14191 | 0.036621 | -0.12817 | 11.3663 | 67.2455 | -0.17395 | 67.3874 | -0.032043 | -0.059509 | -0.004578 | -0.036621 | 1.5152 | 0.4303 | 0.32501 | 0.48981 | 0.38452 | 11.5082 | 122.4426 | 1.5747 | 122.4518 | 122.6074 | 122.4838 | 122.4655 | 122.4243 | -122.5708 | -122.4884 | 122.3007 | 122.3923 | 63.7665 | 52.5375
2394.8281 | 122.6349 | -64.5401 | 57.8522 | -0.12505 | -0.00043792 | 0.067366 | 0.13534 | 0.0010253 | -0.002713 | -0.0016022 | -0.058289 | -0.003905 | 0.065247 | 0.064894 | -0.030209 | 0.0018413 | 0.0016021 | -0.82855 | 57.8384 | -64.7507 | 57.7286 | -53.1509 | -64.7415 | 2.7786 | -11.586 | 57.8613 | -64.5676 | 57.8796 | -63.0249 | -64.1739 | -64.0915 | -0.21057 | -0.013733 | -0.1236 | 11.3892 | 67.3187 | -0.20142 | 67.5293 | 0.009155 | -0.027466 | 0.009155 | 0.027466 | 1.5152 | 0.44861 | 0.36621 | 0.47607 | 0.39368 | 11.5997 | 122.4792 | 1.5427 | 122.4472 | 122.5891 | 122.4289 | 122.3785 | 122.4014 | -122.6028 | -122.4197 | 122.2687 | 122.4197 | 63.7115 | 52.9541
2395.7656 | 122.5662 | -64.6042 | 57.8339 | -0.06401 | 0.00041648 | 0.063307 | 0.13256 | 0.0025207 | -0.0029266 | -0.0020294 | -0.0094604 | -0.0026232 | 0.063538 | 0.061904 | -0.027431 | 0.0018413 | 0.0028839 | -0.90637 | 57.7927 | -64.7644 | 57.6691 | -53.1876 | -64.8697 | 2.7191 | -11.2198 | 57.8064 | -64.6774 | 57.7515 | -63.1027 | -64.2746 | -64.2014 | -0.16022 | -0.041198 | -0.1648 | 11.4166 | 67.3233 | -0.2655 | 67.4835 | -0.10529 | -0.073242 | -0.027466 | -0.082397 | 1.5015 | 0.40283 | 0.32959 | 0.47607 | 0.40283 | 11.5768 | 122.4335 | 1.5747 | 122.4289 | 122.5571 | 122.4838 | 122.3969 | 122.4106 | -122.5983 | -122.5113 | 122.2733 | 122.3557 | 63.6978 | 53.3844
2396.8594 | 122.6852 | -64.7186 | 57.6462 | -0.18608 | 0.0010575 | 0.06758 | 0.13192 | 0.0031617 | 0.000705 | -0.003952 | -0.046081 | -0.003905 | 0.064179 | 0.060195 | -0.029781 | 0.0016277 | 0.00053409 | -0.89264 | 57.637 | -64.8743 | 57.6233 | -53.1326 | -64.8651 | 2.7512 | -11.087 | 57.6141 | -64.769 | 57.7469 | -63.0981 | -64.3021 | -64.1922 | -0.15564 | -0.009155 | -0.022888 | 11.586 | 67.4698 | -0.14648 | 67.6254 | 0.009156 | -0.050354 | -0.032043 | 0.10071 | 1.6205 | 0.52643 | 0.41656 | 0.57678 | 0.46692 | 11.7416 | 122.4976 | 1.6708 | 122.5159 | 122.5113 | 122.3831 | 122.3557 | 122.3328 | -122.5204 | -122.4152 | 122.3419 | 122.4655 | 63.826 | 53.6316
2397.7656 | 122.644 | -64.6729 | 57.7469 | -0.11742 | -0.00022432 | 0.067793 | 0.1347 | 0.00038452 | -0.0048492 | -0.0020294 | -0.088806 | -0.0026232 | 0.060761 | 0.068099 | -0.028927 | 0.0046185 | 0.00074769 | -0.93842 | 57.7515 | -64.8285 | 57.5775 | -53.0457 | -64.8926 | 2.6642 | -10.8673 | 57.7286 | -64.7369 | 57.6691 | -63.1805 | -64.3616 | -64.2654 | -0.15564 | 0.004578 | -0.16937 | 11.6272 | 67.337 | -0.21973 | 67.4927 | -0.064087 | -0.064086 | -0.01831 | -0.07782 | 1.4923 | 0.40741 | 0.31128 | 0.4715 | 0.37537 | 11.7828 | 122.406 | 1.5564 | 122.406 | 122.58 | 122.4655 | 122.4243 | 122.4014 | -122.5754 | -122.4838 | 122.2504 | 122.3419 | 63.7344 | 53.8055
2398.8281 | 122.7081 | -64.7049 | 57.6279 | -0.17845 | -0.00022432 | 0.066725 | 0.13235 | 0.0018799 | -0.0005768 | -0.0026704 | 0.039368 | -0.0024096 | 0.066101 | 0.062545 | -0.028713 | 0.0012005 | 0.0030975 | -0.87891 | 57.6416 | -64.8926 | 57.5867 | -52.9724 | -64.8651 | 2.7832 | -11.2289 | 57.5958 | -64.769 | 57.7423 | -63.0615 | -64.2334 | -64.1876 | -0.18768 | 0.013733 | -0.041199 | 11.7325 | 67.4881 | -0.16022 | 67.6758 | 0.027466 | -0.064087 | -0.032044 | 0.11444 | 1.6434 | 0.51727 | 0.4715 | 0.58136 | 0.53558 | 11.9202 | 122.4792 | 1.7075 | 122.5113 | 122.5342 | 122.3648 | 122.3465 | 122.3007 | -122.5204 | -122.3969 | 122.2916 | 122.4472 | 63.826 | 53.476
2399.7656 | 122.5433 | -64.7873 | 57.6645 | -0.079269 | 0.0019119 | 0.066725 | 0.13577 | 0.00059812 | -0.0035674 | -0.00096136 | -0.11017 | -0.00070063 | 0.063965 | 0.06404 | -0.028286 | 0.0041913 | -0.00010671 | -0.89722 | 57.6416 | -64.9612 | 57.4585 | -53.1418 | -65.0299 | 2.5085 | -11.5494 | 57.6141 | -64.8605 | 57.5775 | -63.2996 | -64.4897 | -64.357 | -0.17395 | -0.022888 | -0.20599 | 11.6455 | 67.2958 | -0.24262 | 67.4698 | -0.068664 | -0.073243 | -0.050354 | -0.086975 | 1.4877 | 0.4303 | 0.29755 | 0.50354 | 0.37079 | 11.8195 | 122.4197 | 1.561 | 122.4381 | 122.6028 | 122.4747 | 122.4289 | 122.4014 | -122.6257 | -122.525 | 122.2458 | 122.3648 | 63.8901 | 53.2379
2400.7656 | 122.6212 | -64.7781 | 57.6324 | -0.10979 | 0.0016983 | 0.06758 | 0.13598 | 0.0016663 | -0.0018586 | -0.0016022 | -0.073547 | -0.0015552 | 0.065674 | 0.062545 | -0.029354 | 0.0041913 | -0.0011749 | -0.87433 | 57.6141 | -64.9612 | 57.5089 | -52.9999 | -64.9246 | 2.5543 | -11.0229 | 57.6187 | -64.7827 | 57.6828 | -63.1622 | -64.3341 | -64.2792 | -0.18311 | -0.01831 | -0.1236 | 11.7783 | 67.3325 | -0.14648 | 67.5156 | 0.036621 | -0.004578 | -0.013733 | 0.050354 | 1.6159 | 0.49896 | 0.44403 | 0.50354 | 0.44861 | 11.9614 | 122.4701 | 1.6205 | 122.4655 | 122.5754 | 122.4014 | 122.3923 | 122.3969 | -122.5937 | -122.4152 | 122.287 | 122.4609 | 63.9038 | 53.7552
2401.8594 | 122.6852 | -64.769 | 57.6324 | -0.11742 | -1.0718e-05 | 0.067366 | 0.13385 | 0.00059812 | -0.0022858 | -0.0020294 | -0.049133 | -0.003905 | 0.065674 | 0.066176 | -0.028927 | 0.0024823 | 0.0035247 | -0.93842 | 57.5958 | -64.9612 | 57.4951 | -52.9495 | -65.0116 | 2.4399 | -11.0046 | 57.6004 | -64.8743 | 57.6874 | -63.1531 | -64.3066 | -64.2563 | -0.19226 | -0.036621 | -0.13733 | 11.8195 | 67.2089 | -0.24262 | 67.4011 | -0.050354 | -0.10529 | -0.032043 | 0.054932 | 1.6159 | 0.51269 | 0.46234 | 0.61798 | 0.56763 | 12.0117 | 122.4564 | 1.7212 | 122.5616 | 122.5571 | 122.4747 | 122.3648 | 122.3694 | -122.5937 | -122.5067 | 122.2641 | 122.4564 | 63.8306 | 53.7643
2402.7656 | 122.5845 | -64.8651 | 57.5775 | -0.094528 | 0.0027665 | 0.06758 | 0.13598 | 0.0023071 | -0.0039948 | -0.0024566 | -0.091858 | -0.003905 | 0.06546 | 0.060836 | -0.029995 | 0.0039777 | -0.0011749 | -0.88348 | 57.5317 | -65.0482 | 57.3441 | -53.0869 | -65.1123 | 2.4261 | -11.0825 | 57.4951 | -64.9475 | 57.4493 | -63.3224 | -64.5401 | -64.4302 | -0.18311 | -0.045777 | -0.23346 | 11.7783 | 67.2913 | -0.24719 | 67.4744 | -0.064087 | -0.082398 | -0.082398 | -0.12817 | 1.5427 | 0.43487 | 0.32501 | 0.51727 | 0.40741 | 11.9614 | 122.3923 | 1.6251 | 122.3969 | 122.58 | 122.4426 | 122.3969 | 122.3602 | -122.6257 | -122.525 | 122.2092 | 122.3145 | 63.9816 | 53.7827
2403.8281 | 122.6532 | -64.9429 | 57.4219 | -0.19371 | -0.00065152 | 0.06758 | 0.13192 | 0.0038025 | -0.0035674 | -0.001175 | 0.027161 | -0.0047594 | 0.064606 | 0.055281 | -0.027431 | 0.0024823 | 0.0039521 | -0.86517 | 57.3853 | -65.1077 | 57.3669 | -52.9221 | -65.1443 | 2.5314 | -11.3617 | 57.4036 | -65.0253 | 57.431 | -63.3728 | -64.5401 | -64.4623 | -0.16479 | -0.036621 | -0.054932 | 12.0209 | 67.4744 | -0.20142 | 67.6392 | -0.036621 | -0.082398 | -0.018311 | 0.009155 | 1.5701 | 0.48065 | 0.40283 | 0.56305 | 0.48523 | 12.1857 | 122.4747 | 1.6525 | 122.4564 | 122.493 | 122.4289 | 122.3282 | 122.3465 | -122.5296 | -122.4472 | 122.3099 | 122.374 | 64.0778 | 53.5812
2404.7656 | 122.6486 | -65.0162 | 57.3944 | -0.11742 | -0.0010787 | 0.06523 | 0.13513 | 0.00081172 | -0.0018586 | -0.002884 | -0.06134 | -0.0019824 | 0.06247 | 0.061476 | -0.030209 | 0.0052593 | 0.00032049 | -0.89722 | 57.3532 | -65.2267 | 57.2433 | -53.0319 | -65.213 | 2.5955 | -11.6318 | 57.3624 | -65.062 | 57.3898 | -63.4094 | -64.6271 | -64.5126 | -0.21057 | -0.041199 | -0.15106 | 11.9843 | 67.6117 | -0.19684 | 67.8223 | 0.013733 | -0.045777 | -0.032043 | -0.004577 | 1.6068 | 0.50354 | 0.3891 | 0.54932 | 0.43488 | 12.1948 | 122.4701 | 1.6525 | 122.4518 | 122.58 | 122.4243 | 122.3694 | 122.3785 | -122.6212 | -122.4564 | 122.2595 | 122.406 | 64.119 | 53.3844
2405.8438 | 122.7127 | -65.0024 | 57.3624 | -0.14793 | 0.00020288 | 0.066084 | 0.1347 | 0.00017092 | -0.0042084 | -0.001175 | 0.011902 | -0.005614 | 0.061615 | 0.064894 | -0.027859 | 0.0026959 | 0.0016021 | -0.86517 | 57.3349 | -65.1535 | 57.3257 | -52.8809 | -65.3091 | 2.2842 | -11.5814 | 57.2891 | -65.0803 | 57.431 | -63.3499 | -64.65 | -64.4714 | -0.15106 | -0.027466 | -0.036621 | 12.1216 | 67.2867 | -0.3067 | 67.4377 | -0.15564 | -0.07782 | -0.073242 | 0.068664 | 1.6525 | 0.53101 | 0.35248 | 0.60882 | 0.4303 | 12.2726 | 122.4792 | 1.7303 | 122.5113 | 122.4884 | 122.3694 | 122.3373 | 122.2916 | -122.5159 | -122.4426 | 122.3282 | 122.4335 | 64.1373 | 53.421
2406.7656 | 122.644 | -65.0894 | 57.2845 | -0.12505 | 0.0016983 | 0.068648 | 0.13662 | -0.0011109 | -0.0029266 | -0.0033112 | -0.076599 | -0.002196 | 0.063751 | 0.066176 | -0.029995 | 0.0035503 | 0.0033111 | -0.93842 | 57.2891 | -65.2679 | 57.1472 | -53.0411 | -65.3229 | 2.3666 | -11.7142 | 57.2708 | -65.1718 | 57.3029 | -63.4964 | -64.7781 | -64.6042 | -0.17853 | 0.004578 | -0.13733 | 12.0483 | 67.4561 | -0.23346 | 67.6346 | -0.054932 | -0.082397 | -0.013733 | 0.01831 | 1.593 | 0.48523 | 0.31128 | 0.56763 | 0.39368 | 12.2269 | 122.4152 | 1.6754 | 122.4747 | 122.5571 | 122.4426 | 122.3785 | 122.3602 | -122.5525 | -122.4564 | 122.2366 | 122.3923 | 64.151 | 53.3752
2407.8281 | 122.6349 | -65.2313 | 57.1655 | -0.10216 | -0.0010787 | 0.067793 | 0.13256 | 0.0023071 | -0.0012176 | -0.0043792 | -0.085754 | -0.0028368 | 0.064179 | 0.062758 | -0.031277 | 0.0026959 | 0.0011749 | -0.87891 | 57.193 | -65.3595 | 57.074 | -53.0136 | -65.3824 | 2.4765 | -11.8973 | 57.1335 | -65.2863 | 57.1747 | -63.5971 | -64.8193 | -64.7369 | -0.12817 | 0.027466 | -0.091552 | 12.2177 | 67.7078 | -0.15106 | 67.836 | -0.022888 | -0.054932 | -0.032043 | 0.009156 | 1.6342 | 0.49439 | 0.41199 | 0.54932 | 0.46692 | 12.3459 | 122.4335 | 1.6891 | 122.4609 | 122.5525 | 122.4197 | 122.4243 | 122.3648 | -122.525 | -122.4518 | 122.3053 | 122.406 | 64.3524 | 53.334
2408.7656 | 122.6715 | -65.2267 | 57.1426 | -0.10979 | -0.00065152 | 0.06758 | 0.13214 | -4.2682e-05 | -0.0035674 | -0.0060882 | 0.014954 | -0.0028368 | 0.062897 | 0.061049 | -0.028072 | 0.0024823 | 0.0020295 | -0.95215 | 57.1701 | -65.3366 | 57.0786 | -53.0457 | -65.4053 | 2.3575 | -11.8607 | 57.1106 | -65.2863 | 57.1793 | -63.5605 | -64.769 | -64.7141 | -0.10986 | 0.027466 | -0.064087 | 12.1811 | 67.5842 | -0.17853 | 67.6941 | -0.068664 | -0.059509 | -0.032043 | 0.036621 | 1.6663 | 0.5127 | 0.45776 | 0.5722 | 0.51727 | 12.291 | 122.4152 | 1.7258 | 122.4655 | 122.5067 | 122.3969 | 122.3969 | 122.3373 | -122.4792 | -122.4289 | 122.3053 | 122.406 | 64.2746 | 53.3661
2409.8281 | 122.5937 | -65.3549 | 57.1014 | -0.094528 | 0.0016983 | 0.066298 | 0.13598 | 0.0065795 | -0.0031402 | -0.002243 | -0.10101 | -0.0013416 | 0.065033 | 0.06874 | -0.028072 | 0.0044049 | -0.0016021 | -0.92926 | 57.0465 | -65.5106 | 56.9458 | -53.1509 | -65.538 | 2.449 | -11.9064 | 57.0511 | -65.3915 | 57.0648 | -63.6978 | -64.9384 | -64.8605 | -0.15564 | -0.054931 | -0.15564 | 12.204 | 67.804 | -0.18311 | 67.9596 | -0.027466 | -0.036622 | -0.050354 | -0.036621 | 1.6571 | 0.49438 | 0.41656 | 0.53101 | 0.45319 | 12.3596 | 122.4564 | 1.6937 | 122.4564 | 122.5571 | 122.4426 | 122.4014 | 122.406 | -122.612 | -122.493 | 122.3007 | 122.4197 | 64.4257 | 53.4485
2410.7656 | 122.5525 | -65.3961 | 57.019 | -0.13267 | 0.00020288 | 0.067366 | 0.13513 | 0.00059812 | -0.0033538 | -0.002884 | -0.052185 | -0.0028368 | 0.064392 | 0.068312 | -0.02914 | 0.0029095 | -0.00074771 | -0.90179 | 56.955 | -65.6296 | 56.8405 | -53.2608 | -65.6204 | 2.4536 | -11.3846 | 56.8954 | -65.5197 | 56.9412 | -63.7848 | -64.9384 | -64.8788 | -0.23346 | -0.064087 | -0.17853 | 12.1353 | 67.8497 | -0.2243 | 68.0832 | 0.009156 | -0.1236 | -0.1236 | -0.07782 | 1.6113 | 0.51727 | 0.45776 | 0.64087 | 0.58136 | 12.3688 | 122.4701 | 1.7349 | 122.4609 | 122.5845 | 122.4152 | 122.3511 | 122.2916 | -122.6486 | -122.5388 | 122.2366 | 122.3373 | 64.4943 | 54.0115
2411.7656 | 122.699 | -65.538 | 56.7947 | -0.17082 | 0.00041648 | 0.066725 | 0.13513 | -0.00089728 | -0.0022858 | 0.00053404 | -0.030823 | -0.002196 | 0.066742 | 0.063185 | -0.02914 | 0.00055973 | 0.0020295 | -0.88348 | 56.7993 | -65.7028 | 56.7764 | -53.3524 | -65.6982 | 2.417 | -11.6226 | 56.6803 | -65.657 | 56.9092 | -63.8443 | -65.0665 | -64.9979 | -0.16479 | 0.004577 | -0.018311 | 12.1857 | 67.955 | -0.16022 | 68.1198 | 0.004578 | -0.11902 | -0.11444 | 0.11444 | 1.6937 | 0.54016 | 0.4715 | 0.65918 | 0.59051 | 12.3505 | 122.4792 | 1.8127 | 122.5662 | 122.5021 | 122.3373 | 122.3373 | 122.2183 | -122.4976 | -122.4518 | 122.3145 | 122.4472 | 64.6545 | 53.9154
2412.7656 | 122.644 | -65.5701 | 56.813 | -0.1403 | 0.0010575 | 0.065871 | 0.1347 | -0.00068368 | -0.0029266 | -0.0026704 | -0.04303 | -0.0030506 | 0.064606 | 0.068526 | -0.029354 | 0.0022687 | 0.0033111 | -0.84686 | 56.8314 | -65.7532 | 56.7123 | -53.3203 | -65.7394 | 2.3941 | -11.4029 | 56.7947 | -65.6616 | 56.8405 | -63.8809 | -65.126 | -65.0574 | -0.18311 | 0.018311 | -0.10071 | 12.2498 | 67.9642 | -0.16937 | 68.1473 | 0.013733 | -0.091553 | -0.01831 | 0.027466 | 1.6891 | 0.5127 | 0.44403 | 0.60425 | 0.53558 | 12.4329 | 122.4655 | 1.7807 | 122.5021 | 122.5845 | 122.4564 | 122.4014 | 122.3648 | -122.5662 | -122.4747 | 122.2824 | 122.4106 | 64.7232 | 54.1672
2413.8281 | 122.6074 | -65.4373 | 56.9733 | -0.12505 | -0.00043792 | 0.067152 | 0.13513 | 0.00017092 | -0.004422 | -0.0030976 | -0.058289 | -0.002196 | 0.065674 | 0.068953 | -0.029354 | 0.0014141 | 0.0016021 | -0.89722 | 56.9458 | -65.5975 | 56.7947 | -53.1921 | -65.6525 | 2.3392 | -11.6272 | 56.9458 | -65.5472 | 56.9321 | -63.7848 | -65.0528 | -64.9704 | -0.16022 | -0.027466 | -0.17853 | 12.2452 | 67.7765 | -0.21515 | 67.9367 | -0.054932 | -0.10986 | -0.027466 | -0.041199 | 1.6525 | 0.46692 | 0.38452 | 0.57678 | 0.49438 | 12.4054 | 122.3923 | 1.7624 | 122.4792 | 122.5433 | 122.493 | 122.3831 | 122.3831 | -122.5708 | -122.5204 | 122.2321 | 122.3694 | 64.5401 | 53.8101
2414.7656 | 122.6166 | -65.7944 | 56.6299 | -0.10216 | 0.0019119 | 0.068648 | 0.13705 | 0.0031617 | -0.0007904 | 0.001175 | -0.049133 | -0.0017688 | 0.062897 | 0.064467 | -0.029781 | 0.0039777 | 0.0039521 | -0.86517 | 56.6345 | -65.9821 | 56.4835 | -53.5309 | -65.9546 | 2.4216 | -11.6409 | 56.5796 | -65.8859 | 56.5979 | -64.0594 | -65.332 | -65.2634 | -0.18768 | 0.004577 | -0.14648 | 12.2635 | 68.2159 | -0.16022 | 68.4036 | 0.027466 | -0.091552 | -0.050354 | -0.032044 | 1.7349 | 0.53101 | 0.46234 | 0.62256 | 0.55389 | 12.4512 | 122.4655 | 1.8265 | 122.4838 | 122.6166 | 122.4655 | 122.4289 | 122.374 | -122.612 | -122.5159 | 122.2778 | 122.3923 | 64.9292 | 54.1534
2415.8281 | 122.6303 | -65.8173 | 56.5613 | -0.10979 | 0.00020288 | 0.066939 | 0.13534 | 0.0016663 | -0.0014312 | -0.0020294 | -0.04303 | -0.0030506 | 0.064606 | 0.066817 | -0.029354 | 0.00098693 | 0.0030975 | -0.93384 | 56.5887 | -65.9866 | 56.4377 | -53.5767 | -66.0187 | 2.243 | -11.673 | 56.5521 | -65.8951 | 56.5933 | -64.0915 | -65.3732 | -65.2908 | -0.16937 | 0.027466 | -0.1236 | 12.2406 | 68.0603 | -0.20142 | 68.2297 | -0.032044 | -0.07782 | -0.009155 | 0.032044 | 1.7258 | 0.52643 | 0.44403 | 0.60425 | 0.52185 | 12.41 | 122.4243 | 1.8036 | 122.4884 | 122.5754 | 122.4472 | 122.406 | 122.3694 | -122.5479 | -122.4564 | 122.2549 | 122.4106 | 64.8834 | 54.1443
2416.7656 | 122.699 | -65.712 | 56.6345 | -0.13267 | 0.0010575 | 0.067793 | 0.13534 | -4.2682e-05 | -0.0012176 | -0.0026704 | -0.052185 | -0.0043322 | 0.062042 | 0.062972 | -0.030209 | 0.0039777 | 0.0018159 | -0.90179 | 56.6162 | -65.9271 | 56.5247 | -53.4439 | -65.9546 | 2.4216 | -11.4395 | 56.5659 | -65.831 | 56.7169 | -63.9633 | -65.2405 | -65.126 | -0.21515 | -0.01831 | -0.10986 | 12.2681 | 68.1335 | -0.24262 | 68.3487 | -0.027466 | -0.11902 | -0.068664 | 0.082398 | 1.7487 | 0.58594 | 0.4715 | 0.70496 | 0.59052 | 12.4832 | 122.4518 | 1.8677 | 122.5479 | 122.5433 | 122.3969 | 122.3282 | 122.2778 | -122.5616 | -122.4655 | 122.2366 | 122.4289 | 64.8102 | 54.2725
2417.8281 | 122.5845 | -65.7944 | 56.6299 | -0.079269 | 0.00063028 | 0.068007 | 0.13449 | 0.00017092 | -0.0035674 | 0.00053404 | -0.088806 | -0.0049732 | 0.063324 | 0.066603 | -0.030422 | 0.0056867 | 0.0048065 | -0.90637 | 56.6208 | -65.9683 | 56.4789 | -53.3569 | -66.0095 | 2.3392 | -11.5036 | 56.5933 | -65.8356 | 56.5796 | -64.1144 | -65.4007 | -65.3091 | -0.17395 | -0.009155 | -0.15106 | 12.4374 | 68.1335 | -0.21515 | 68.3075 | -0.041198 | -0.041198 | -0.036621 | -0.050354 | 1.68 | 0.48523 | 0.39368 | 0.52643 | 0.43488 | 12.6114 | 122.4472 | 1.7212 | 122.4152 | 122.5891 | 122.4289 | 122.4152 | 122.3877 | -122.5983 | -122.4655 | 122.2733 | 122.374 | 64.888 | 54.2908
2418.7656 | 122.6303 | -65.95 | 56.4697 | -0.15556 | 0.0038345 | 0.068007 | 0.13577 | 0.0042297 | -0.0039948 | -0.0020294 | -0.04303 | -0.0026232 | 0.062683 | 0.061904 | -0.030636 | 0.0026959 | 0.0028839 | -0.90179 | 56.5247 | -66.0416 | 56.3919 | -53.4943 | -66.0599 | 2.243 | -11.4853 | 56.4697 | -65.9775 | 56.4835 | -64.1876 | -65.451 | -65.3961 | -0.091553 | 0.054931 | -0.07782 | 12.4557 | 68.1931 | -0.10986 | 68.2846 | -0.01831 | -0.027466 | 0 | 0.013732 | 1.7624 | 0.55389 | 0.49896 | 0.58136 | 0.52643 | 12.5473 | 122.4335 | 1.7899 | 122.4609 | 122.5662 | 122.4472 | 122.4747 | 122.4197 | -122.5113 | -122.4472 | 122.3419 | 122.4335 | 65.0482 | 54.4647
2419.8281 | 122.5754 | -66.1285 | 56.2958 | -0.07164 | 0.00063028 | 0.067152 | 0.13769 | -0.0013245 | -0.0037812 | -0.001175 | -0.079651 | -0.0024096 | 0.062897 | 0.065108 | -0.029995 | 0.0037641 | 0.0024567 | -1.0025 | 56.3278 | -66.2567 | 56.1768 | -53.6591 | -66.2796 | 2.2064 | -11.824 | 56.3095 | -66.1606 | 56.2683 | -64.3982 | -65.6662 | -65.6204 | -0.12817 | 0.032044 | -0.11902 | 12.4695 | 68.335 | -0.15106 | 68.4631 | -0.022888 | -0.032043 | 0.013733 | -0.027465 | 1.7303 | 0.50812 | 0.46234 | 0.54016 | 0.49438 | 12.5977 | 122.4335 | 1.7624 | 122.4289 | 122.5845 | 122.4701 | 122.4564 | 122.438 | -122.5525 | -122.4564 | 122.3053 | 122.3969 | 65.126 | 54.3045
2420.7656 | 122.5983 | -66.2384 | 56.2134 | -0.079269 | -0.0030013 | 0.066725 | 0.13598 | -0.0013245 | -0.0020722 | -0.003952 | -0.0094604 | -0.002196 | 0.064392 | 0.05934 | -0.028927 | 0.0044049 | 0.0026703 | -0.98419 | 56.2271 | -66.3666 | 56.0623 | -53.7598 | -66.3757 | 2.2888 | -11.9797 | 56.1813 | -66.3025 | 56.1493 | -64.4577 | -65.7394 | -65.6845 | -0.12817 | 0.013733 | -0.15106 | 12.4786 | 68.5272 | -0.13733 | 68.6554 | -0.009155 | -0.064087 | -0.032044 | -0.064087 | 1.7807 | 0.55389 | 0.49896 | 0.61798 | 0.56305 | 12.6068 | 122.4289 | 1.8448 | 122.4518 | 122.5937 | 122.4838 | 122.4655 | 122.4197 | -122.58 | -122.5159 | 122.3007 | 122.3877 | 65.2542 | 54.2587
2421.8438 | 122.7127 | -66.4856 | 55.9158 | -0.094528 | -0.00065152 | 0.068221 | 0.13278 | -0.00025628 | -0.0020722 | -0.0052338 | 0.082092 | -0.0036914 | 0.064392 | 0.060408 | -0.027431 | 0.00055973 | 0.0065155 | -0.96588 | 55.8655 | -66.6779 | 55.8014 | -54.0985 | -66.6412 | 2.1927 | -11.8973 | 55.8105 | -66.5543 | 55.9296 | -64.6454 | -65.9271 | -65.9225 | -0.19226 | -0.050354 | -0.11444 | 12.3871 | 68.6783 | -0.15564 | 68.8705 | 0.036621 | -0.068664 | -0.10529 | 0.013732 | 1.8402 | 0.56305 | 0.55847 | 0.63171 | 0.62714 | 12.5793 | 122.4792 | 1.9089 | 122.4838 | 122.5433 | 122.3648 | 122.3511 | 122.2961 | -122.5937 | -122.4701 | 122.287 | 122.4152 | 65.5197 | 54.5883
2422.7656 | 122.5983 | -66.4902 | 55.9891 | -0.11742 | -1.0718e-05 | 0.068221 | 0.13577 | 0.00081172 | -0.0042084 | -0.0037384 | -0.030823 | -0.0015552 | 0.065888 | 0.064253 | -0.029568 | 0.0046185 | -0.00032051 | -0.97504 | 55.9341 | -66.6367 | 55.7831 | -54.158 | -66.6916 | 2.0737 | -11.8973 | 55.9113 | -66.5405 | 55.8884 | -64.6912 | -65.9821 | -65.9592 | -0.14648 | -0.054932 | -0.20599 | 12.3322 | 68.5638 | -0.20142 | 68.7103 | -0.054931 | -0.050354 | -0.07782 | -0.10071 | 1.799 | 0.53101 | 0.50812 | 0.58136 | 0.55847 | 12.4786 | 122.4197 | 1.8494 | 122.4289 | 122.5708 | 122.4518 | 122.4243 | 122.4014 | -122.6257 | -122.5296 | 122.2733 | 122.3785 | 65.5151 | 54.5929
2423.8438 | 122.6532 | -66.4581 | 56.0074 | -0.12505 | -0.00022432 | 0.065657 | 0.13513 | -0.00025628 | -0.0052764 | 0.00032044 | 0.0088502 | -0.0032642 | 0.063965 | 0.060408 | -0.030636 | 0.0031231 | 0.0052337 | -0.98877 | 55.925 | -66.6458 | 55.7693 | -54.0802 | -66.6779 | 2.1149 | -11.5723 | 55.8975 | -66.5588 | 55.8609 | -64.7186 | -66.0461 | -65.8539 | -0.18768 | -0.082397 | -0.23804 | 12.3779 | 68.573 | -0.21973 | 68.7607 | -0.032043 | -0.10071 | -0.10986 | -0.14648 | 1.7395 | 0.60425 | 0.41199 | 0.70496 | 0.51269 | 12.5656 | 122.4152 | 1.8402 | 122.4197 | 122.5708 | 122.4564 | 122.3831 | 122.3557 | -122.6532 | -122.5662 | 122.2275 | 122.319 | 65.4694 | 54.8859
2424.7656 | 122.5525 | -66.5359 | 55.9113 | -0.12505 | -0.00065152 | 0.069502 | 0.13769 | 0.0033753 | -0.0031402 | -0.00074776 | -0.091858 | -0.0024096 | 0.064179 | 0.065749 | -0.028713 | 0.0052593 | 0.00074769 | -0.98419 | 55.8655 | -66.7099 | 55.7098 | -54.039 | -66.7831 | 2.0004 | -11.5768 | 55.8792 | -66.5909 | 55.8197 | -64.801 | -66.0828 | -66.0324 | -0.17395 | -0.045776 | -0.20142 | 12.4969 | 68.5364 | -0.24719 | 68.7103 | -0.073242 | -0.054931 | -0.032044 | -0.091553 | 1.7349 | 0.50354 | 0.45319 | 0.55847 | 0.50812 | 12.6709 | 122.4197 | 1.7899 | 122.4106 | 122.5754 | 122.4701 | 122.4014 | 122.4152 | -122.6212 | -122.5021 | 122.2458 | 122.3557 | 65.5518 | 54.9591
2425.8281 | 122.6303 | -66.6229 | 55.8105 | -0.1403 | 0.0014847 | 0.068434 | 0.13534 | 0.0010253 | -0.0018586 | -0.0024566 | -0.076599 | -0.0060412 | 0.06482 | 0.065749 | -0.028713 | 0.0048321 | 0.0039521 | -0.99335 | 55.7785 | -66.7923 | 55.6366 | -54.1443 | -66.8289 | 2.1698 | -11.4853 | 55.7877 | -66.6595 | 55.806 | -64.8193 | -66.0873 | -66.0553 | -0.16937 | -0.032044 | -0.17395 | 12.4786 | 68.7927 | -0.20599 | 68.9621 | -0.036621 | -0.036621 | -0.022888 | -0.004578 | 1.8036 | 0.56763 | 0.53558 | 0.60425 | 0.57221 | 12.648 | 122.4289 | 1.8402 | 122.4655 | 122.5708 | 122.4472 | 122.4014 | 122.4106 | -122.6028 | -122.4701 | 122.2595 | 122.4289 | 65.6296 | 55.1376
2426.7656 | 122.731 | -66.5955 | 55.7098 | -0.17082 | -0.0019333 | 0.069929 | 0.13513 | 0.00038452 | -0.0022858 | -0.00074776 | -0.036926 | -0.0034778 | 0.063111 | 0.065749 | -0.028072 | 0.0022687 | 0.0011749 | -0.93842 | 55.7373 | -66.7831 | 55.7144 | -54.0298 | -66.7648 | 2.1652 | -11.7416 | 55.6961 | -66.7053 | 55.8884 | -64.7278 | -66.1011 | -66.037 | -0.18768 | 0.027466 | 0.004578 | 12.5656 | 68.7607 | -0.16937 | 68.9484 | 0.01831 | -0.10986 | -0.013733 | 0.17853 | 1.8677 | 0.55847 | 0.49439 | 0.66833 | 0.60425 | 12.7533 | 122.4976 | 1.9775 | 122.5937 | 122.5204 | 122.4014 | 122.3328 | 122.2916 | -122.493 | -122.4152 | 122.3099 | 122.4838 | 65.657 | 54.8538
2427.8281 | 122.5662 | -66.5817 | 55.8563 | -0.1403 | -1.0718e-05 | 0.067366 | 0.13748 | -0.00046988 | -0.0042084 | -0.0020294 | -0.085754 | -0.0028368 | 0.066529 | 0.068312 | -0.030636 | 0.0039777 | 0.0033111 | -0.94299 | 55.8014 | -66.774 | 55.687 | -53.9291 | -66.774 | 2.1103 | -12.3688 | 55.8014 | -66.6504 | 55.806 | -64.7827 | -66.1011 | -66.0324 | -0.19226 | -0.054931 | -0.16937 | 12.6526 | 68.692 | -0.19226 | 68.8843 | 0 | -0.068665 | -0.054931 | -0.050354 | 1.799 | 0.54932 | 0.48065 | 0.61798 | 0.54932 | 12.8448 | 122.4609 | 1.8677 | 122.4564 | 122.5754 | 122.4518 | 122.3831 | 122.3831 | -122.6303 | -122.5067 | 122.2687 | 122.3877 | 65.6387 | 54.213
2428.7812 | 122.7036 | -66.6504 | 55.6915 | -0.12505 | -0.0044967 | 0.063948 | 0.13363 | -0.0019653 | -0.0031402 | -0.0043792 | 0.066834 | -0.0030506 | 0.067169 | 0.061263 | -0.027859 | 0.0033367 | 0.0037385 | -0.68207 | 55.751 | -66.806 | 55.6274 | -53.7918 | -66.7419 | 2.3026 | -11.8835 | 55.6458 | -66.7419 | 55.7831 | -64.7461 | -66.0461 | -66.0553 | -0.15564 | 0.05951 | -0.064087 | 12.8586 | 68.9529 | -0.091552 | 69.1086 | 0.064087 | -0.091552 | -0.045776 | 0.091553 | 1.9043 | 0.59509 | 0.60425 | 0.68665 | 0.6958 | 13.0142 | 122.4335 | 1.9958 | 122.525 | 122.5571 | 122.3877 | 122.4014 | 122.2961 | -122.4976 | -122.4335 | 122.2778 | 122.4335 | 65.9683 | 54.7668
2429.7656 | 122.6715 | -66.687 | 55.7327 | -0.079269 | -0.0012923 | 0.067366 | 0.1362 | -0.0026063 | -0.0037812 | -0.00010676 | -0.079651 | -0.0030506 | 0.064392 | 0.067031 | -0.030422 | 0.0056867 | 0.0039521 | -0.93384 | 55.6503 | -66.9022 | 55.6091 | -53.9246 | -66.8289 | 2.2614 | -12.0255 | 55.6595 | -66.7969 | 55.7007 | -64.856 | -66.1743 | -66.1469 | -0.21515 | -0.082397 | -0.1236 | 12.7625 | 68.9484 | -0.14191 | 69.1635 | 0.073243 | -0.10986 | -0.073242 | -0.032043 | 1.8311 | 0.54016 | 0.5127 | 0.65002 | 0.62256 | 12.9776 | 122.5113 | 1.9409 | 122.4976 | 122.5525 | 122.4564 | 122.3373 | 122.3465 | -122.6349 | -122.5296 | 122.2961 | 122.3877 | 65.7532 | 54.6616
2430.7656 | 122.6166 | -66.9617 | 55.4855 | -0.18608 | -0.00043792 | 0.067152 | 0.13662 | 0.0018799 | -0.0031402 | -0.0018158 | -0.064392 | -0.0041186 | 0.066315 | 0.064681 | -0.028927 | 0.0046185 | 0.0026703 | -0.88806 | 55.481 | -67.1173 | 55.3757 | -54.1809 | -67.099 | 2.1103 | -12.3688 | 55.4306 | -66.9937 | 55.481 | -65.0848 | -66.394 | -66.3712 | -0.15564 | -0.004578 | -0.10986 | 12.7808 | 69.072 | -0.13733 | 69.2276 | 0.018311 | -0.032043 | -0.054932 | -0.004578 | 1.8768 | 0.59051 | 0.56763 | 0.62256 | 0.59967 | 12.9364 | 122.493 | 1.9089 | 122.4747 | 122.5983 | 122.4243 | 122.4426 | 122.3923 | -122.6028 | -122.4792 | 122.3373 | 122.4426 | 66.0736 | 54.5929
2431.7656 | 122.7081 | -66.98 | 55.3574 | -0.16319 | -0.0012923 | 0.068221 | 0.13705 | 0.0020935 | 0.0011322 | -0.0037384 | -0.027771 | -0.0026232 | 0.063111 | 0.060622 | -0.027431 | 0.0039777 | 0.0043793 | -0.85144 | 55.3528 | -67.1768 | 55.307 | -54.0161 | -67.0212 | 2.092 | -12.0071 | 55.307 | -67.0578 | 55.4764 | -65.0665 | -66.3757 | -66.3712 | -0.19684 | -0.004578 | -0.050354 | 12.9639 | 69.072 | -0.041199 | 69.2688 | 0.15564 | -0.07782 | -0.050354 | 0.11902 | 1.9135 | 0.60882 | 0.60425 | 0.68664 | 0.68207 | 13.1607 | 122.4838 | 1.9913 | 122.5342 | 122.5296 | 122.3648 | 122.3328 | 122.287 | -122.5342 | -122.4152 | 122.287 | 122.4564 | 66.1285 | 54.9728
2432.7656 | 122.6166 | -67.099 | 55.2979 | -0.13267 | -1.0718e-05 | 0.068221 | 0.1379 | 0.00038452 | -0.0054902 | 0.00032044 | -0.064392 | -0.0043322 | 0.065674 | 0.067671 | -0.02914 | 0.0044049 | 0.0030975 | -0.95215 | 55.2979 | -67.2821 | 55.1422 | -54.3182 | -67.3416 | 1.9821 | -12.3047 | 55.275 | -67.1722 | 55.2841 | -65.2634 | -66.6046 | -66.5771 | -0.1831 | 0 | -0.15564 | 12.7808 | 69.0811 | -0.24262 | 69.2642 | -0.05951 | -0.073242 | -0.022889 | -0.013733 | 1.8356 | 0.52185 | 0.49439 | 0.59509 | 0.56763 | 12.9639 | 122.4243 | 1.9089 | 122.4564 | 122.58 | 122.4472 | 122.3969 | 122.374 | -122.58 | -122.4701 | 122.2412 | 122.3831 | 66.1469 | 54.7943
2433.8438 | 122.6761 | -67.2226 | 55.1468 | -0.11742 | -0.00065152 | 0.066298 | 0.13577 | -0.00046988 | -0.0022858 | -0.0026704 | 0.042419 | -0.0047594 | 0.065247 | 0.067458 | -0.028927 | 0.0029095 | -0.00053411 | -0.90637 | 55.1559 | -67.4194 | 55.0507 | -54.277 | -67.2318 | 2.1744 | -12.1719 | 55.1193 | -67.3004 | 55.1743 | -65.3 | -66.6321 | -66.6229 | -0.19684 | 0.009155 | -0.096131 | 12.9456 | 69.397 | -0.009155 | 69.5938 | 0.18768 | -0.07782 | -0.027466 | 0.027465 | 1.9226 | 0.59967 | 0.59051 | 0.67749 | 0.66833 | 13.1424 | 122.4701 | 2.0004 | 122.4747 | 122.5754 | 122.4197 | 122.3785 | 122.3419 | -122.5662 | -122.4472 | 122.2733 | 122.3969 | 66.3162 | 55.0507
2434.7656 | 122.58 | -67.2729 | 55.1559 | -0.048752 | -0.00086512 | 0.068861 | 0.13812 | -0.0017517 | -0.004422 | -0.0024566 | -0.079651 | -0.0068958 | 0.06482 | 0.069594 | -0.030209 | 0.0033367 | 0.0043793 | -0.94299 | 55.1239 | -67.4606 | 54.9683 | -54.4327 | -67.4973 | 1.918 | -12.41 | 55.1056 | -67.2958 | 55.1331 | -65.4327 | -66.7831 | -66.7282 | -0.18768 | -0.032044 | -0.18768 | 12.8403 | 69.191 | -0.2243 | 69.3787 | -0.036621 | -0.022888 | -0.050354 | -0.022888 | 1.8402 | 0.54474 | 0.48981 | 0.56763 | 0.5127 | 13.028 | 122.4289 | 1.8631 | 122.4289 | 122.5845 | 122.4014 | 122.3969 | 122.3785 | -122.6166 | -122.4518 | 122.2412 | 122.406 | 66.33 | 54.863
2435.8281 | 122.5845 | -67.2455 | 55.1926 | -0.17082 | 0.00020288 | 0.066512 | 0.13833 | 0.0057251 | -0.0007904 | -0.00032036 | -0.06134 | -0.0024096 | 0.063324 | 0.064894 | -0.028927 | 0.0029095 | 0.0013885 | -0.97504 | 55.1788 | -67.4332 | 54.9911 | -54.0894 | -67.305 | 1.8539 | -12.204 | 55.1788 | -67.3279 | 55.1285 | -65.3961 | -66.7191 | -66.6962 | -0.18768 | -0.013733 | -0.20142 | 13.1561 | 69.0994 | -0.05951 | 69.2871 | 0.12817 | -0.082398 | -0.013733 | -0.064087 | 1.8494 | 0.54932 | 0.52643 | 0.63171 | 0.60883 | 13.3438 | 122.4243 | 1.9318 | 122.4564 | 122.612 | 122.5067 | 122.4243 | 122.4243 | -122.6257 | -122.5204 | 122.2366 | 122.374 | 66.2704 | 55.0415
2436.7656 | 122.6303 | -67.2546 | 55.188 | -0.11742 | 0.0021255 | 0.068434 | 0.13812 | 0.0035889 | -0.0031402 | -0.0018158 | -0.082703 | -0.0034778 | 0.06546 | 0.06639 | -0.029354 | 0.0046185 | -0.00074771 | -0.86517 | 55.1743 | -67.3874 | 55.0598 | -54.3365 | -67.4057 | 2.0279 | -12.0804 | 55.1468 | -67.3233 | 55.1788 | -65.3458 | -66.6321 | -66.655 | -0.13275 | -0.013733 | -0.12817 | 12.9181 | 69.2825 | -0.15106 | 69.4153 | -0.018311 | -0.068664 | -0.041198 | -0.009155 | 1.9089 | 0.59967 | 0.62256 | 0.66833 | 0.69122 | 13.0508 | 122.4472 | 1.9775 | 122.5021 | 122.5616 | 122.4701 | 122.4289 | 122.4014 | -122.5754 | -122.5113 | 122.3145 | 122.4335 | 66.3895 | 55.1743
2437.8281 | 122.6898 | -67.1768 | 55.1514 | -0.2166 | 0.00020288 | 0.070143 | 0.1347 | -0.0032471 | -0.0037812 | -0.0035248 | -0.0094604 | -0.0036914 | 0.06546 | 0.069167 | -0.0285 | 0.0035503 | 0.0026703 | -0.85602 | 55.1331 | -67.3691 | 55.1834 | -54.1992 | -67.3325 | 2.0737 | -12.085 | 55.1193 | -67.2821 | 55.2475 | -65.2084 | -66.6092 | -66.5359 | -0.19226 | -0.01831 | 0.032044 | 12.9776 | 69.2505 | -0.15564 | 69.4427 | 0.036622 | -0.10529 | -0.032043 | 0.096131 | 1.9684 | 0.64087 | 0.56763 | 0.74615 | 0.67291 | 13.1699 | 122.5525 | 2.0737 | 122.5296 | 122.5021 | 122.4014 | 122.3099 | 122.2961 | -122.5204 | -122.4335 | 122.3602 | 122.4243 | 66.3208 | 55.0919
2438.7656 | 122.58 | -67.2958 | 55.1651 | -0.07164 | -0.0012923 | 0.067793 | 0.1379 | -4.2682e-05 | -0.0029266 | -0.0041656 | 0.036316 | -0.0028368 | 0.066315 | 0.069808 | -0.0285 | 0.0037641 | 0.0043793 | -0.95215 | 55.1651 | -67.392 | 55.1559 | -54.3549 | -67.7032 | 1.9501 | -12.323 | 55.1514 | -67.3279 | 55.101 | -65.3458 | -66.6733 | -66.7145 | -0.096131 | 0 | -0.009155 | 12.941 | 69.2459 | -0.40741 | 69.342 | -0.31128 | -0.032044 | -0.013733 | -0.064087 | 1.9501 | 0.58136 | 0.62256 | 0.6134 | 0.6546 | 13.0371 | 122.5479 | 1.9821 | 122.4289 | 122.5571 | 122.4792 | 122.4609 | 122.4472 | -122.5571 | -122.493 | 122.4518 | 122.3969 | 66.3437 | 54.9728
2439.8281 | 122.6807 | -67.392 | 54.9408 | -0.15556 | 0.00041648 | 0.067152 | 0.13769 | 0.0010253 | -0.0048492 | -0.0035248 | -0.049133 | -0.002196 | 0.06546 | 0.064894 | -0.029568 | 0.0041913 | 0.0024567 | -0.90179 | 54.9271 | -67.5934 | 54.8492 | -54.4098 | -67.5751 | 1.8951 | -12.5107 | 54.9362 | -67.4973 | 55.014 | -65.4327 | -66.806 | -66.7648 | -0.20142 | -0.013733 | -0.091553 | 12.9822 | 69.2871 | -0.1831 | 69.4885 | 0.018311 | -0.10528 | -0.004578 | 0.073242 | 1.9592 | 0.62714 | 0.58594 | 0.73242 | 0.69122 | 13.1836 | 122.4426 | 2.0645 | 122.5113 | 122.5204 | 122.4335 | 122.319 | 122.3282 | -122.5342 | -122.438 | 122.2412 | 122.406 | 66.4902 | 54.8813
2440.7656 | 122.6257 | -67.3233 | 55.0644 | -0.10979 | 0.0010575 | 0.068007 | 0.1362 | 0.0044433 | -0.0046356 | -0.0030976 | -0.070496 | -0.0028368 | 0.06546 | 0.068312 | -0.029354 | 0.0046185 | 0.0033111 | -0.90637 | 55.0644 | -67.5201 | 54.9088 | -54.3045 | -67.5522 | 1.9226 | -12.7075 | 55.0186 | -67.4332 | 55.0598 | -65.3824 | -66.7374 | -66.7328 | -0.19684 | 0 | -0.15564 | 13.0188 | 69.2459 | -0.22888 | 69.4427 | -0.032043 | -0.10986 | -0.045776 | -0.004578 | 1.9409 | 0.59051 | 0.58594 | 0.70038 | 0.6958 | 13.2156 | 122.4289 | 2.0508 | 122.493 | 122.5845 | 122.4518 | 122.3877 | 122.3419 | -122.5845 | -122.4976 | 122.2321 | 122.3831 | 66.4169 | 54.6158
2441.8281 | 122.5433 | -67.4194 | 55.0003 | -0.15556 | 0.0023391 | 0.068648 | 0.13919 | 0.0031617 | -0.0020722 | -0.0043792 | -0.085754 | -0.0032642 | 0.063751 | 0.066176 | -0.031277 | 0.0054729 | 0.0050201 | -0.89264 | 54.9911 | -67.6025 | 54.8126 | -54.4098 | -67.6346 | 2.0187 | -12.7441 | 54.9408 | -67.5201 | 54.9179 | -65.5518 | -66.8884 | -66.8701 | -0.1831 | -0.009155 | -0.18768 | 13.0096 | 69.4382 | -0.21515 | 69.6213 | -0.032044 | -0.10071 | -0.059509 | -0.082397 | 1.8677 | 0.54932 | 0.53101 | 0.65003 | 0.63171 | 13.1927 | 122.4152 | 1.9684 | 122.4381 | 122.5937 | 122.4609 | 122.4106 | 122.3602 | -122.6028 | -122.5204 | 122.2321 | 122.3373 | 66.5268 | 54.6753
2442.7656 | 122.5891 | -67.3462 | 55.0827 | -0.094528 | 0.0021255 | 0.066939 | 0.13748 | -0.0047425 | -0.0048492 | -0.0018158 | -0.11017 | -0.0030506 | 0.066529 | 0.065322 | -0.028713 | 0.0048321 | 0.0026703 | -0.88806 | 55.0598 | -67.511 | 54.95 | -54.1306 | -67.5018 | 2.0233 | -12.5198 | 55.0278 | -67.4149 | 55.0507 | -65.3595 | -66.7236 | -66.7465 | -0.16479 | -0.022889 | -0.13275 | 13.2156 | 69.3695 | -0.15564 | 69.5343 | 0.009155 | -0.068665 | -0.054932 | -0.032044 | 1.9867 | 0.59967 | 0.62256 | 0.66833 | 0.69122 | 13.3804 | 122.4609 | 2.0554 | 122.4655 | 122.5708 | 122.4426 | 122.406 | 122.374 | -122.5937 | -122.4976 | 122.2961 | 122.3969 | 66.4581 | 54.8264
2443.8281 | 122.699 | -67.4973 | 54.8401 | -0.27 | 0.0016983 | 0.069075 | 0.13684 | -4.2682e-05 | -0.0005768 | -0.0037384 | 0.0027466 | -0.003905 | 0.061402 | 0.062972 | -0.029781 | 0.0046185 | 0.0026703 | -0.7782 | 54.8126 | -67.6666 | 54.8355 | -54.1855 | -67.5842 | 2.0737 | -12.4558 | 54.808 | -67.5751 | 54.9591 | -65.4373 | -66.7923 | -66.8152 | -0.16937 | -0.027466 | -0.004578 | 13.3118 | 69.5709 | -0.086976 | 69.7403 | 0.082397 | -0.07782 | -0.032044 | 0.11902 | 2.0599 | 0.68207 | 0.70496 | 0.75989 | 0.78278 | 13.4811 | 122.5021 | 2.1378 | 122.5342 | 122.4792 | 122.3831 | 122.3099 | 122.3053 | -122.5067 | -122.4152 | 122.3328 | 122.4564 | 66.7191 | 55.0415
2444.7656 | 122.6166 | -67.5018 | 54.9271 | -0.14793 | -0.00022432 | 0.068007 | 0.13855 | 0.00059812 | -0.0024994 | -0.0024566 | -0.070496 | -0.0026232 | 0.063538 | 0.067671 | -0.028927 | 0.0056867 | 0.0069427 | -0.93384 | 54.9133 | -67.662 | 54.744 | -54.1809 | -67.6666 | 2.0508 | -12.7213 | 54.8996 | -67.5476 | 54.8859 | -65.5197 | -66.8701 | -66.8976 | -0.16022 | -0.013733 | -0.1831 | 13.3209 | 69.5526 | -0.16479 | 69.7128 | -0.004578 | -0.045776 | -0.027466 | -0.041199 | 1.9821 | 0.60425 | 0.63171 | 0.65002 | 0.67749 | 13.4811 | 122.406 | 2.0279 | 122.4335 | 122.5754 | 122.4472 | 122.4152 | 122.4014 | -122.5891 | -122.4747 | 122.2458 | 122.3877 | 66.568 | 54.7806
2445.8281 | 122.6807 | -67.6117 | 54.7302 | -0.13267 | -0.00022432 | 0.068007 | 0.1394 | -0.00068368 | -0.0014312 | -0.00074776 | 0.011902 | -0.0032642 | 0.066101 | 0.060195 | -0.029354 | 0.0037641 | 0.0022431 | -0.89264 | 54.7211 | -67.7765 | 54.7073 | -54.5197 | -67.7582 | 2.1835 | -12.3779 | 54.6433 | -67.7124 | 54.8172 | -65.5609 | -66.9022 | -66.9342 | -0.16479 | -0.009156 | -0.022889 | 13.092 | 69.7952 | -0.14648 | 69.96 | 0.01831 | -0.10071 | -0.086975 | 0.086975 | 2.0508 | 0.67749 | 0.70953 | 0.7782 | 0.81024 | 13.2568 | 122.4838 | 2.1515 | 122.5296 | 122.4976 | 122.3557 | 122.3328 | 122.2549 | -122.5067 | -122.4426 | 122.319 | 122.4289 | 66.7191 | 55.2338
2446.7656 | 122.6852 | -67.63 | 54.7073 | -0.086899 | 0.00041648 | 0.06758 | 0.13748 | -0.0032471 | -0.0035674 | -0.003952 | -0.14374 | -0.002196 | 0.061615 | 0.058699 | -0.030209 | 0.0048321 | -0.00096131 | -0.87433 | 54.7302 | -67.7994 | 54.7119 | -54.1351 | -67.3004 | 2.2385 | -12.2543 | 54.657 | -67.7216 | 54.7806 | -65.5334 | -66.861 | -66.9754 | -0.16937 | 0.022889 | 0.004578 | 13.4949 | 69.8685 | 0.32959 | 70.0378 | 0.49896 | -0.091553 | -0.050354 | 0.073243 | 2.0966 | 0.6546 | 0.76904 | 0.74616 | 0.8606 | 13.6642 | 122.5113 | 2.1881 | 122.5021 | 122.5296 | 122.3785 | 122.3602 | 122.287 | -122.5067 | -122.4289 | 122.3419 | 122.4106 | 66.7557 | 55.3757
2447.8281 | 122.5845 | -67.4377 | 55.0278 | -0.033493 | 0.0012711 | 0.068648 | 0.14004 | 0.0038025 | -0.0033538 | -0.0018158 | -0.082703 | -0.0024096 | 0.063751 | 0.067885 | -0.028927 | 0.0048321 | 0.0026703 | -0.97961 | 55.0003 | -67.5934 | 54.8584 | -53.5629 | -67.598 | 2.124 | -12.7945 | 54.982 | -67.4652 | 54.9591 | -65.4327 | -66.7831 | -66.8198 | -0.15564 | -0.027466 | -0.16937 | 13.8748 | 69.5618 | -0.16022 | 69.7174 | -0.004577 | -0.027466 | -0.045776 | -0.068665 | 2.005 | 0.61798 | 0.6546 | 0.64545 | 0.68207 | 14.0305 | 122.4518 | 2.0325 | 122.4243 | 122.5937 | 122.4472 | 122.438 | 122.4197 | -122.6212 | -122.493 | 122.2961 | 122.3969 | 66.4581 | 54.6432
2448.7656 | 122.6257 | -67.2958 | 55.1285 | -0.13267 | -1.0718e-05 | 0.070784 | 0.13812 | 0.0014527 | -0.0022858 | -0.0041656 | -0.088806 | -0.0028368 | 0.065247 | 0.065108 | -0.030209 | 0.0044049 | 0.0026703 | -0.94757 | 55.1331 | -67.4652 | 55.0095 | -53.0273 | -67.4835 | 2.1652 | -12.7716 | 55.1147 | -67.3279 | 55.1331 | -65.2634 | -66.5909 | -66.655 | -0.16937 | 0.004578 | -0.11902 | 14.2685 | 69.4611 | -0.18768 | 69.6304 | -0.018311 | -0.032044 | -0.013733 | 0.004578 | 2.0325 | 0.64087 | 0.70496 | 0.67291 | 0.737 | 14.4379 | 122.4747 | 2.0645 | 122.4609 | 122.5983 | 122.4426 | 122.4289 | 122.4106 | -122.5937 | -122.4564 | 122.3053 | 122.4289 | 66.3483 | 54.5242
2449.8281 | 122.5342 | -67.3828 | 55.0507 | -0.12505 | 0.0014847 | 0.069289 | 0.14047 | -0.0013245 | -0.0003632 | -0.0030976 | -0.070496 | -0.0041186 | 0.06546 | 0.062117 | -0.030422 | 0.0048321 | 0.0018159 | -0.90637 | 55.0278 | -67.5705 | 54.863 | -53.1006 | -67.6071 | 2.2247 | -12.9593 | 54.9911 | -67.4561 | 54.9637 | -65.4282 | -66.774 | -66.8152 | -0.18768 | -0.022888 | -0.18768 | 14.2822 | 69.6075 | -0.22431 | 69.7952 | -0.036621 | -0.073243 | -0.059509 | -0.086975 | 1.9547 | 0.56763 | 0.60882 | 0.64087 | 0.68207 | 14.4699 | 122.4335 | 2.0279 | 122.4197 | 122.5983 | 122.4472 | 122.4106 | 122.374 | -122.6212 | -122.5067 | 122.2458 | 122.3465 | 66.4764 | 54.4235
2450.7656 | 122.6028 | -67.4881 | 54.9179 | -0.14793 | -0.00043792 | 0.069929 | 0.14004 | -0.0021789 | -0.0029266 | -0.00074776 | -0.036926 | -0.0019824 | 0.066101 | 0.070235 | -0.02914 | 0.0056867 | 0.00032049 | -0.92468 | 54.9316 | -67.6483 | 54.7623 | -53.1097 | -67.6254 | 2.243 | -13.0096 | 54.8996 | -67.5568 | 54.9316 | -65.451 | -66.7419 | -66.8564 | -0.16022 | 0.013733 | -0.15564 | 14.3784 | 69.7311 | -0.13733 | 69.8914 | 0.022888 | -0.068665 | -0.018311 | 0.013733 | 2.037 | 0.63171 | 0.74615 | 0.70038 | 0.81482 | 14.5386 | 122.4106 | 2.1057 | 122.4884 | 122.58 | 122.4564 | 122.4197 | 122.3877 | -122.5662 | -122.4747 | 122.2504 | 122.4197 | 66.5634 | 54.4785
2451.8281 | 122.6578 | -67.5476 | 54.8676 | -0.14793 | -1.0718e-05 | 0.06758 | 0.13726 | 0.0035889 | -0.0018586 | -0.0024566 | -0.0033568 | -0.0043322 | 0.065888 | 0.063185 | -0.028286 | 0.0031231 | 0.0050201 | -0.85144 | 54.7852 | -67.6712 | 54.7897 | -52.8992 | -67.6529 | 2.4124 | -12.9181 | 54.8035 | -67.598 | 54.8859 | -65.4419 | -66.7603 | -66.861 | -0.1236 | -0.082398 | -0.07782 | 14.6484 | 69.96 | -0.10529 | 70.0836 | 0.018311 | -0.050354 | -0.064087 | 0.01831 | 2.1057 | 0.68664 | 0.78735 | 0.737 | 0.83771 | 14.772 | 122.4609 | 2.1561 | 122.4838 | 122.4564 | 122.4014 | 122.3328 | 122.3511 | -122.5388 | -122.4655 | 122.3373 | 122.4335 | 66.6962 | 54.6295
2452.7656 | 122.5754 | -67.5934 | 54.8492 | -0.14793 | -0.0010787 | 0.066512 | 0.13812 | 0.0010253 | -0.0024994 | 0.00010684 | -0.22614 | -0.0028368 | 0.062683 | 0.066603 | -0.029995 | 0.0054729 | 0.0043793 | -0.93842 | 54.8264 | -67.7765 | 54.6478 | -53.0136 | -67.7948 | 2.3346 | -13.0646 | 54.8218 | -67.6163 | 54.7897 | -65.5518 | -66.8655 | -66.9662 | -0.1831 | -0.022888 | -0.20142 | 14.5798 | 69.928 | -0.20142 | 70.1111 | -0.018311 | -0.022888 | -0.027466 | -0.059509 | 2.0416 | 0.62714 | 0.72784 | 0.65002 | 0.75073 | 14.7629 | 122.4243 | 2.0645 | 122.406 | 122.6028 | 122.438 | 122.4197 | 122.4152 | -122.6257 | -122.4655 | 122.2412 | 122.3831 | 66.655 | 54.5288
2453.7656 | 122.58 | -67.7353 | 54.7165 | -0.094528 | -0.0012923 | 0.068648 | 0.13983 | 0.0029479 | -0.0039948 | -0.00074776 | -0.082703 | -0.0043322 | 0.066101 | 0.065749 | -0.029568 | 0.0046185 | 0.0045929 | -0.92926 | 54.6616 | -67.9138 | 54.5471 | -53.0411 | -67.9138 | 2.3895 | -12.9089 | 54.6433 | -67.7948 | 54.6341 | -65.6708 | -67.067 | -67.1173 | -0.17853 | -0.054932 | -0.16937 | 14.6942 | 70.1248 | -0.17853 | 70.3033 | 0 | -0.059509 | -0.073242 | -0.082398 | 2.0645 | 0.61798 | 0.66833 | 0.67749 | 0.72784 | 14.8727 | 122.4609 | 2.124 | 122.4289 | 122.5754 | 122.4381 | 122.3969 | 122.3785 | -122.6303 | -122.5113 | 122.2824 | 122.3694 | 66.806 | 54.8264
2454.7656 | 122.6166 | -67.7582 | 54.6341 | -0.1403 | 0.0034073 | 0.070784 | 0.14025 | -0.0017517 | -0.0018586 | 0.00010684 | -0.076599 | -0.0019824 | 0.063324 | 0.068312 | -0.027218 | 0.0067547 | -0.00010671 | -0.95215 | 54.6112 | -67.9596 | 54.4739 | -53.0502 | -67.9642 | 2.3483 | -12.8586 | 54.6112 | -67.8406 | 54.6066 | -65.7211 | -67.0624 | -67.1494 | -0.20142 | -0.022888 | -0.16022 | 14.7079 | 70.1065 | -0.20599 | 70.3079 | -0.004577 | -0.082397 | -0.022888 | -0.027466 | 2.037 | 0.60883 | 0.6958 | 0.69122 | 0.7782 | 14.9094 | 122.4335 | 2.1194 | 122.4472 | 122.5708 | 122.4518 | 122.3694 | 122.3694 | -122.5937 | -122.4747 | 122.2321 | 122.3648 | 66.806 | 54.8996
2455.8281 | 122.6028 | -67.7536 | 54.6204 | -0.20897 | 0.0014847 | 0.068648 | 0.13748 | 0.0014527 | -0.0031402 | 0.0013886 | -0.064392 | -0.0026232 | 0.068665 | 0.065322 | -0.02914 | 0.0059003 | 0.0060883 | -0.93384 | 54.6249 | -67.9596 | 54.451 | -53.1464 | -68.0008 | 2.2705 | -12.7533 | 54.57 | -67.8726 | 54.6112 | -65.6891 | -67.0395 | -67.1677 | -0.20599 | 0.004578 | -0.16937 | 14.6072 | 70.0241 | -0.24719 | 70.2301 | -0.041198 | -0.11902 | -0.050354 | -0.009155 | 2.0645 | 0.58594 | 0.71411 | 0.70496 | 0.83313 | 14.8132 | 122.4106 | 2.1835 | 122.4838 | 122.5845 | 122.4426 | 122.3785 | 122.3236 | -122.58 | -122.493 | 122.2046 | 122.3648 | 66.8198 | 55.0003
2456.7656 | 122.699 | -67.9138 | 54.4418 | -0.15556 | -0.00043792 | 0.069502 | 0.13684 | -0.0041015 | 6.4004e-05 | -0.004593 | 0.033264 | -0.003905 | 0.065033 | 0.058913 | -0.028927 | 0.0039777 | 0.0024567 | -0.88806 | 54.4235 | -68.0878 | 54.3686 | -53.0594 | -68.0237 | 2.2797 | -12.822 | 54.3686 | -68.0008 | 54.5013 | -65.7394 | -67.0761 | -67.2363 | -0.17395 | -0.01831 | -0.073242 | 14.8544 | 70.1935 | -0.10986 | 70.3674 | 0.064087 | -0.086975 | -0.073242 | 0.05951 | 2.1744 | 0.67749 | 0.83771 | 0.76447 | 0.92468 | 15.0284 | 122.4564 | 2.2614 | 122.5021 | 122.5113 | 122.3694 | 122.3373 | 122.2824 | -122.5296 | -122.4426 | 122.2824 | 122.4152 | 67.0258 | 55.0919
2457.8281 | 122.7081 | -67.9825 | 54.364 | -0.13267 | 0.0014847 | 0.069929 | 0.14004 | -0.0030335 | -0.0012176 | -0.0013886 | -0.024719 | -0.0049732 | 0.062256 | 0.068312 | -0.030636 | 0.0035503 | 0.0024567 | -0.91553 | 54.3457 | -68.1427 | 54.3411 | -53.0411 | -68.0695 | 2.1515 | -13.0142 | 54.3182 | -68.0374 | 54.4647 | -65.7715 | -67.1265 | -67.2913 | -0.16022 | -0.018311 | -0.022889 | 14.9414 | 70.134 | -0.086975 | 70.2942 | 0.073242 | -0.054932 | -0.045777 | 0.10071 | 2.211 | 0.69122 | 0.85602 | 0.74616 | 0.91095 | 15.1016 | 122.4838 | 2.2659 | 122.5021 | 122.4884 | 122.3557 | 122.3282 | 122.3007 | -122.5067 | -122.4014 | 122.3236 | 122.4472 | 67.067 | 54.9683
2458.7656 | 122.58 | -67.9504 | 54.4556 | -0.11742 | 0.00020288 | 0.069716 | 0.13961 | 0.00081172 | -0.004422 | -0.0030976 | -0.11322 | -0.0030506 | 0.064179 | 0.067244 | -0.029995 | 0.0067547 | -0.0016021 | -0.93842 | 54.4281 | -68.1381 | 54.2816 | -53.0457 | -68.1244 | 2.1332 | -13.2019 | 54.4144 | -68.0374 | 54.3915 | -65.8722 | -67.2226 | -67.3508 | -0.18768 | -0.027465 | -0.17395 | 14.9048 | 70.0836 | -0.17395 | 70.2713 | 0.013733 | -0.086976 | -0.041198 | -0.064087 | 2.0782 | 0.59967 | 0.72784 | 0.68665 | 0.81482 | 15.0925 | 122.4197 | 2.1652 | 122.4289 | 122.5662 | 122.4518 | 122.3785 | 122.3648 | -122.5937 | -122.493 | 122.2321 | 122.3419 | 67.012 | 54.7485
2459.8281 | 122.7493 | -68.0786 | 54.2953 | -0.16319 | 0.0012711 | 0.06758 | 0.1394 | 0.0020935 | -0.0029266 | -0.0020294 | -0.052185 | -0.0034778 | 0.065247 | 0.060195 | -0.028713 | 0.0041913 | 0.0020295 | -0.87891 | 54.3091 | -68.2297 | 54.2725 | -52.8854 | -68.1335 | 2.243 | -12.9822 | 54.2633 | -68.1381 | 54.4647 | -66.0416 | -67.337 | -67.3508 | -0.15106 | 0.013733 | -0.022888 | 15.1932 | 70.3217 | -0.054932 | 70.4727 | 0.09613 | -0.05951 | -0.032043 | 0.16937 | 2.037 | 0.72784 | 0.74158 | 0.78735 | 0.80109 | 15.3442 | 122.5021 | 2.0966 | 122.6028 | 122.5388 | 122.4014 | 122.3877 | 122.3419 | -122.525 | -122.4335 | 122.3511 | 122.5433 | 67.1997 | 55.0964
2460.7656 | 122.699 | -68.1793 | 54.1763 | -0.094528 | -0.0027877 | 0.07057 | 0.14025 | 0.0014527 | -0.0005768 | -0.00053396 | -0.04303 | -0.0041186 | 0.063324 | 0.070876 | -0.028927 | 0.0071819 | 0.0016021 | -0.94757 | 54.1763 | -68.3487 | 54.126 | -52.9907 | -68.2755 | 2.2247 | -12.9913 | 54.158 | -68.2526 | 54.277 | -65.9363 | -67.2546 | -67.4606 | -0.16937 | 0 | -0.050354 | 15.1886 | 70.4041 | -0.096131 | 70.5734 | 0.073242 | -0.073242 | -0.018311 | 0.10071 | 2.243 | 0.71869 | 0.92468 | 0.79193 | 0.99792 | 15.358 | 122.4747 | 2.3163 | 122.5296 | 122.525 | 122.4106 | 122.3557 | 122.3373 | -122.525 | -122.4289 | 122.3053 | 122.4564 | 67.2318 | 55.188
2461.8281 | 122.6624 | -68.2571 | 54.0985 | -0.10979 | 0.0012711 | 0.069502 | 0.13855 | -0.0028199 | -0.0046356 | -0.0041656 | -0.0064086 | -0.0028368 | 0.065888 | 0.065322 | -0.028286 | 0.0073955 | 0.0020295 | -0.93842 | 54.1306 | -68.4128 | 54.0298 | -53.2013 | -68.4357 | 2.2156 | -13.2523 | 54.0253 | -68.3578 | 54.1351 | -66.0324 | -67.2043 | -67.5751 | -0.15564 | 0.032043 | -0.068665 | 15.0558 | 70.4727 | -0.17853 | 70.6284 | -0.022888 | -0.10071 | -0.073242 | 0.036621 | 2.2247 | 0.68207 | 1.0529 | 0.78278 | 1.1536 | 15.2115 | 122.4426 | 2.3254 | 122.493 | 122.5433 | 122.3831 | 122.3877 | 122.2824 | -122.5113 | -122.4564 | 122.287 | 122.3923 | 67.3187 | 55.0049
2462.7656 | 122.7219 | -72.67 | 49.585 | -0.17082 | 0.00041648 | 0.068648 | 0.13769 | 0.00059812 | -0.0012176 | -0.003952 | -0.070496 | -0.0041186 | 0.064179 | 0.16209 | -0.029354 | 0.10224 | -0.00053411 | -0.94757 | 49.5667 | -72.9538 | 49.5621 | -56.1813 | -72.8165 | 1.8539 | 0.25635 | 49.5346 | -72.8073 | 49.5392 | -70.2896 | 47.0856 | -71.814 | -0.28381 | -0.018311 | -0.022888 | 16.4886 | 74.5239 | -0.14648 | 74.8077 | 0.13733 | -0.13733 | -0.050354 | -0.045776 | 2.3804 | 0.85602 | 119.7556 | 0.99335 | 119.8929 | 16.7725 | 122.5159 | 2.5177 | 122.3465 | 122.5204 | 122.3419 | 122.2366 | 122.2046 | -122.5388 | -122.3923 | 122.2321 | 122.2092 | 71.7224 | 72.9263
2463.8281 | 122.6761 | -72.3267 | 49.9649 | -0.10979 | 0.0021255 | 0.070784 | 0.13961 | 0.0020935 | -0.001004 | -0.004593 | -0.055237 | -0.0034778 | 0.065247 | 0.16188 | -0.029354 | 0.10224 | 0.0056611 | -0.89264 | 49.9237 | -72.5601 | 49.942 | -55.8701 | -72.4411 | 1.973 | 0.54932 | 49.9146 | -72.4319 | 49.9924 | -69.9783 | 47.1909 | -71.5805 | -0.23346 | -0.041199 | -0.022888 | 16.4566 | 74.2996 | -0.11444 | 74.5331 | 0.11902 | -0.10529 | -0.050354 | 0.027466 | 2.3483 | 0.74616 | 119.5175 | 0.85144 | 119.6228 | 16.6901 | 122.5021 | 2.4536 | 122.4243 | 122.4838 | 122.3465 | 122.2504 | 122.2412 | -122.525 | -122.3969 | 122.2687 | 122.319 | 71.434 | 72.876
2464.7656 | 122.6944 | -72.3129 | 49.9695 | -0.12505 | -0.00065152 | 0.069716 | 0.13726 | 0.0023071 | -0.0024994 | -0.0037384 | -0.088806 | -0.0051868 | 0.063111 | 0.16487 | -0.028927 | 0.09904 | 0.0041657 | -0.88806 | 49.9878 | -72.5052 | 49.9924 | -55.7098 | -72.3862 | 1.7395 | 0.74616 | 49.9558 | -72.4182 | 50.0656 | -69.8868 | 47.2366 | -71.5256 | -0.19226 | 0.018311 | 0.022889 | 16.6031 | 74.0524 | -0.073242 | 74.2447 | 0.11902 | -0.10529 | -0.013732 | 0.096131 | 2.4261 | 0.78735 | 119.5496 | 0.89264 | 119.6548 | 16.7953 | 122.4976 | 2.5314 | 122.4838 | 122.493 | 122.374 | 122.3007 | 122.2687 | -122.4747 | -122.3877 | 122.3053 | 122.3785 | 71.4249 | 73.0591
2465.8281 | 122.6807 | -72.0886 | 50.2121 | -0.094528 | -0.0019333 | 0.070784 | 0.13919 | -0.00089728 | -0.0018586 | -0.0054474 | -0.10712 | -0.0045458 | 0.066315 | 0.16658 | -0.02914 | 0.097331 | 0.0011749 | -0.88348 | 50.2304 | -72.2992 | 50.1984 | -55.426 | -72.1436 | 2.0462 | 0.95215 | 50.1938 | -72.171 | 50.3036 | -69.6533 | 47.4976 | -71.283 | -0.21057 | 0.018311 | -0.013733 | 16.6626 | 74.1348 | -0.054932 | 74.3454 | 0.15564 | -0.082398 | -0.01831 | 0.091553 | 2.4353 | 0.80566 | 119.5862 | 0.88806 | 119.6686 | 16.8732 | 122.4976 | 2.5177 | 122.4747 | 122.5296 | 122.3648 | 122.319 | 122.2824 | -122.5113 | -122.3831 | 122.287 | 122.3923 | 71.2051 | 73.0408
2466.7656 | 122.6898 | -72.0566 | 50.2716 | -0.14793 | -0.0012923 | 0.069502 | 0.13876 | 0.0010253 | -0.0016448 | -0.00096136 | -0.10406 | -0.0051868 | 0.063324 | 0.16743 | -0.031704 | 0.09904 | 0.0041657 | -0.89722 | 50.2579 | -72.2488 | 50.2167 | -55.394 | -72.1115 | 2.0966 | 1.2314 | 50.2121 | -72.1573 | 50.3494 | -69.5938 | 47.525 | -71.2555 | -0.19226 | -0.013732 | -0.054931 | 16.6626 | 74.1531 | -0.054931 | 74.3454 | 0.13733 | -0.10071 | -0.059509 | 0.07782 | 2.4628 | 0.80109 | 119.5816 | 0.90179 | 119.6823 | 16.8549 | 122.4655 | 2.5635 | 122.5067 | 122.5067 | 122.3694 | 122.3145 | 122.2687 | -122.5204 | -122.4289 | 122.2733 | 122.406 | 71.1594 | 73.288
2467.8281 | 122.6395 | -72.0566 | 50.2945 | -0.1403 | -0.00086512 | 0.072066 | 0.13726 | -0.0021789 | 0.0002778 | -0.0030976 | -0.046081 | -0.0036914 | 0.065888 | 0.16124 | -0.028927 | 0.09904 | 0.0095063 | -0.8606 | 50.3082 | -72.1939 | 50.2441 | -55.2658 | -72.0703 | 2.3392 | 1.1902 | 50.2167 | -72.1527 | 50.3036 | -69.5618 | 47.5616 | -71.2692 | -0.13733 | 0.013733 | -0.050354 | 16.7908 | 74.3958 | -0.013732 | 74.5331 | 0.1236 | -0.09613 | -0.07782 | 0.009155 | 2.4948 | 0.78735 | 119.6182 | 0.88348 | 119.7144 | 16.9281 | 122.4381 | 2.5909 | 122.4564 | 122.5021 | 122.3694 | 122.3648 | 122.2733 | -122.4884 | -122.4472 | 122.3007 | 122.3602 | 71.196 | 73.2468
2468.7656 | 122.6624 | -71.8643 | 50.4593 | -0.26237 | -0.00065152 | 0.071211 | 0.13769 | 0.0010253 | -0.001004 | 0.00074764 | -0.091858 | -0.0041186 | 0.06247 | 0.16572 | -0.029995 | 0.098613 | 0.0026703 | -0.82398 | 50.4181 | -72.0245 | 50.4684 | -54.9683 | -71.9147 | 2.2842 | 1.1078 | 50.4089 | -71.9238 | 50.5508 | -69.3649 | 47.7585 | -71.0495 | -0.16022 | -0.041199 | 0.009155 | 16.8961 | 74.1486 | -0.050354 | 74.3088 | 0.10986 | -0.059509 | -0.050354 | 0.091552 | 2.4994 | 0.81482 | 119.6228 | 0.87433 | 119.6823 | 17.0563 | 122.493 | 2.5589 | 122.4747 | 122.4426 | 122.3328 | 122.2824 | 122.2733 | -122.4838 | -122.3831 | 122.3328 | 122.4152 | 71.0403 | 72.9721
2469.8281 | 122.6532 | -71.8277 | 50.5005 | -0.079269 | 0.0010575 | 0.068861 | 0.13555 | -0.0026063 | -0.0050628 | -0.0020294 | -0.018616 | -0.0045458 | 0.063324 | 0.16145 | -0.031277 | 0.095836 | -0.00010671 | -0.87433 | 50.4913 | -72.0016 | 50.4547 | -54.8996 | -71.9009 | 2.33 | 1.387 | 50.4501 | -71.8872 | 50.56 | -69.31 | 47.818 | -71.022 | -0.17395 | -0.009155 | -0.045776 | 16.9281 | 74.1577 | -0.073242 | 74.3317 | 0.10071 | -0.059509 | -0.050354 | 0.05951 | 2.5177 | 0.80566 | 119.6457 | 0.86517 | 119.7052 | 17.1021 | 122.4564 | 2.5772 | 122.4472 | 122.493 | 122.3373 | 122.319 | 122.2778 | -122.5021 | -122.3877 | 122.2824 | 122.3877 | 70.9534 | 73.2147
2470.7656 | 122.6532 | -71.7957 | 50.5188 | -0.17845 | -0.00086512 | 0.072066 | 0.13641 | 0.0010253 | -0.0029266 | -0.0035248 | -0.088806 | -0.0045458 | 0.06482 | 0.16872 | -0.030849 | 0.10139 | -0.00010671 | -0.84228 | 50.4822 | -71.9879 | 50.5051 | -54.8447 | -71.9055 | 2.3163 | 1.767 | 50.4593 | -71.8597 | 50.5966 | -69.2917 | 47.8134 | -70.9808 | -0.19226 | -0.036621 | -0.013733 | 16.951 | 74.1119 | -0.10986 | 74.3042 | 0.082397 | -0.064087 | -0.059509 | 0.07782 | 2.504 | 0.81482 | 119.6091 | 0.87891 | 119.6732 | 17.1432 | 122.493 | 2.5681 | 122.4564 | 122.4701 | 122.319 | 122.2778 | 122.2549 | -122.5067 | -122.3785 | 122.3007 | 122.3923 | 70.9534 | 73.5626
2471.8281 | 122.6669 | -71.7316 | 50.5737 | -0.20897 | 0.0010575 | 0.07057 | 0.13833 | 0.0020935 | -0.0005768 | 0.0024566 | -0.16205 | -0.0047594 | 0.062683 | 0.16829 | -0.029995 | 0.099681 | 0.0024567 | -0.8194 | 50.5417 | -71.8964 | 50.4364 | -54.6021 | -71.5164 | 2.3254 | 1.0849 | 50.5371 | -71.8094 | 50.6653 | -69.191 | 47.8958 | -70.8984 | -0.16479 | -0.032043 | -0.13733 | 17.1295 | 74.057 | 0.21515 | 74.2218 | 0.37994 | -0.07782 | -0.036621 | 0.091553 | 2.5406 | 0.83313 | 119.6274 | 0.91095 | 119.7052 | 17.2943 | 122.3328 | 2.6184 | 122.4747 | 122.438 | 122.3465 | 122.2733 | 122.2687 | -122.4701 | -122.3831 | 122.168 | 122.3969 | 70.9122 | 72.8165
2472.7656 | 122.6212 | -71.7911 | 50.5142 | -0.16319 | 0.0010575 | 0.069502 | 0.13684 | -0.00025628 | -0.0074128 | -0.00074776 | -0.055237 | -0.0047594 | 0.065247 | 0.15889 | -0.030209 | 0.097117 | 0.0028839 | -0.86975 | 50.5188 | -71.965 | 50.4868 | -54.9179 | -71.8964 | 2.2705 | 1.4191 | 50.4684 | -71.8735 | 50.5554 | -69.2963 | 47.818 | -71.0083 | -0.17395 | 0.004578 | -0.027466 | 16.8732 | 74.0616 | -0.10528 | 74.2355 | 0.068665 | -0.082397 | -0.045776 | 0.041199 | 2.4948 | 0.78278 | 119.6091 | 0.86517 | 119.6915 | 17.0471 | 122.4518 | 2.5772 | 122.4289 | 122.4838 | 122.3419 | 122.3099 | 122.2595 | -122.4792 | -122.3877 | 122.2778 | 122.3465 | 70.9213 | 73.2101
2473.8281 | 122.6807 | -71.8002 | 50.5371 | -0.1403 | 0.0014847 | 0.068434 | 0.13748 | -0.00046988 | -0.0031402 | -0.00096136 | -0.039978 | -0.0058276 | 0.063751 | 0.1685 | -0.027645 | 0.098399 | 0.00074769 | -0.7782 | 50.5096 | -71.9376 | 50.56 | -54.5288 | -71.7316 | 2.3849 | 0.97504 | 50.5005 | -71.8506 | 50.6653 | -69.2642 | 47.8363 | -70.9488 | -0.13733 | -0.027465 | 0.022889 | 17.2714 | 74.1852 | 0.068665 | 74.3225 | 0.20599 | -0.050354 | -0.036621 | 0.12817 | 2.536 | 0.85144 | 119.6365 | 0.90179 | 119.6869 | 17.4088 | 122.4976 | 2.5864 | 122.5159 | 122.4472 | 122.3511 | 122.3099 | 122.3007 | -122.4747 | -122.3877 | 122.3602 | 122.4655 | 71.022 | 72.7753
2474.7656 | 122.6166 | -71.8185 | 50.5096 | -0.13267 | 0.00020288 | 0.070998 | 0.13897 | -0.0013245 | -0.0048492 | -0.004593 | -0.058289 | -0.0068958 | 0.063324 | 0.16145 | -0.029568 | 0.098399 | 0.0035247 | -0.88806 | 50.4868 | -72.0108 | 50.4318 | -54.538 | -71.933 | 2.2247 | 0.98877 | 50.441 | -71.8826 | 50.5142 | -69.2963 | 47.7539 | -71.0403 | -0.19226 | -0.022889 | -0.07782 | 17.2806 | 74.0433 | -0.11444 | 74.2355 | 0.07782 | -0.064087 | -0.068665 | 0.004577 | 2.5223 | 0.7782 | 119.5724 | 0.84228 | 119.6365 | 17.4728 | 122.4426 | 2.5864 | 122.3969 | 122.4976 | 122.3236 | 122.3053 | 122.2595 | -122.5204 | -122.3923 | 122.2504 | 122.3328 | 70.9305 | 72.8073
2475.8281 | 122.6807 | -71.7773 | 50.528 | -0.17082 | -0.00065152 | 0.070784 | 0.13748 | 0.0020935 | -0.0050628 | -0.0016022 | -0.14069 | -0.0060412 | 0.062683 | 0.17213 | -0.029781 | 0.10075 | 0.0041657 | -0.86975 | 50.5371 | -71.9467 | 50.5554 | -54.2816 | -71.8231 | 2.3209 | 1.1398 | 50.5188 | -71.8369 | 50.6149 | -69.4153 | 47.9462 | -70.816 | -0.16937 | 0.009155 | 0.027466 | 17.4957 | 74.0982 | -0.045776 | 74.2676 | 0.1236 | -0.059509 | -0.009155 | 0.086975 | 2.3621 | 0.9613 | 119.7235 | 1.0208 | 119.783 | 17.6651 | 122.5021 | 2.4216 | 122.4518 | 122.4838 | 122.3557 | 122.3145 | 122.2961 | -122.4747 | -122.3648 | 122.3328 | 122.3923 | 70.9076 | 72.9172
2476.7656 | 122.6486 | -71.7041 | 50.6058 | -0.15556 | 0.00020288 | 0.069289 | 0.1394 | -0.0015381 | -0.0022858 | -0.0060882 | -0.055237 | -0.0036914 | 0.064179 | 0.16807 | -0.030849 | 0.098185 | 0.0058747 | -0.90637 | 50.6149 | -71.8735 | 50.5646 | -54.1214 | -71.7773 | 2.3621 | 1.1993 | 50.6012 | -71.7682 | 50.6653 | -69.1177 | 47.9507 | -70.8755 | -0.16937 | 0.009155 | -0.041199 | 17.5827 | 74.0662 | -0.073242 | 74.2355 | 0.09613 | -0.064086 | -0.004578 | 0.059509 | 2.5864 | 0.82855 | 119.6548 | 0.89264 | 119.7189 | 17.7521 | 122.438 | 2.6505 | 122.4335 | 122.4884 | 122.3694 | 122.319 | 122.3053 | -122.4792 | -122.374 | 122.2687 | 122.3694 | 70.7977 | 72.9034
2477.8281 | 122.644 | -71.7773 | 50.4913 | 0.18013 | 0.00020288 | 0.075056 | 0.14047 | 0.00038452 | -0.0029266 | -0.0016022 | -0.030823 | -0.0064684 | 0.063751 | 0.16102 | -0.029354 | 0.099467 | 0.0020295 | -1.0162 | 50.4456 | -72.0016 | 50.5325 | -54.0802 | -71.8048 | 2.3163 | 1.0712 | 50.4547 | -71.8597 | 50.5829 | -69.1635 | 47.8729 | -70.9488 | -0.2243 | -0.045776 | 0.041199 | 17.6971 | 74.0936 | -0.027466 | 74.3179 | 0.19684 | -0.082397 | -0.036621 | 0.091553 | 2.6138 | 0.82855 | 119.6503 | 0.91095 | 119.7327 | 17.9214 | 122.5342 | 2.6962 | 122.4426 | 122.4472 | 122.3145 | 122.2229 | 122.2321 | -122.493 | -122.3511 | 122.3099 | 122.3602 | 70.7611 | 72.8485
2478.7656 | 122.6486 | -71.7819 | 50.4868 | -0.1403 | 0.00020288 | 0.069502 | 0.1394 | -0.0015381 | -0.0003632 | -0.0048066 | -0.04303 | -0.0047594 | 0.061829 | 0.16957 | -0.028072 | 0.097331 | -0.00010671 | -0.83313 | 50.4959 | -71.9879 | 50.4959 | -54.0619 | -71.7957 | 2.3529 | 1.1581 | 50.473 | -71.8735 | 50.5966 | -69.1452 | 47.8592 | -70.9396 | -0.20599 | 0.009156 | 0.009156 | 17.72 | 74.1348 | -0.013733 | 74.3408 | 0.19226 | -0.091553 | -0.013733 | 0.10986 | 2.6367 | 0.84229 | 119.6411 | 0.93384 | 119.7327 | 17.926 | 122.4838 | 2.7283 | 122.4701 | 122.4838 | 122.3465 | 122.2778 | 122.2549 | -122.4747 | -122.3602 | 122.2778 | 122.3785 | 70.9488 | 72.9401
2479.8281 | 122.6578 | -71.7957 | 50.5005 | -0.10979 | 0.00020288 | 0.069716 | 0.1379 | -0.0030335 | -0.0054902 | -0.0013886 | -0.076599 | -0.0060412 | 0.061829 | 0.16807 | -0.030209 | 0.09669 | 0.0018159 | -0.82855 | 50.4822 | -71.9879 | 50.4776 | -53.9246 | -71.8369 | 2.3254 | 1.4282 | 50.4913 | -71.8918 | 50.5783 | -69.1452 | 47.8638 | -70.9534 | -0.19226 | -0.01831 | -0.022888 | 17.8711 | 74.1211 | -0.041199 | 74.3134 | 0.15106 | -0.096131 | -0.009155 | 0.07782 | 2.6505 | 0.84229 | 119.6594 | 0.93842 | 119.7556 | 18.0634 | 122.4655 | 2.7466 | 122.4701 | 122.4701 | 122.3831 | 122.2778 | 122.287 | -122.4884 | -122.3923 | 122.2733 | 122.374 | 70.9671 | 73.2239
2480.7656 | 122.6898 | -71.8048 | 50.5234 | -0.12505 | -0.0017197 | 0.070357 | 0.13833 | 0.00081172 | -0.0052764 | -0.002884 | -0.049133 | -0.0032642 | 0.063111 | 0.16359 | -0.027218 | 0.097545 | 0.0052337 | -0.80109 | 50.4776 | -71.9925 | 50.4913 | -53.7689 | -71.7865 | 2.3712 | 1.3458 | 50.4227 | -71.8735 | 50.5646 | -69.1223 | 47.8729 | -70.9396 | -0.18768 | -0.045776 | -0.032043 | 18.0359 | 74.176 | 0.018311 | 74.3637 | 0.20599 | -0.068664 | -0.10071 | 0.041199 | 2.6825 | 0.86517 | 119.6777 | 0.93384 | 119.7464 | 18.2236 | 122.4838 | 2.7512 | 122.438 | 122.4701 | 122.2961 | 122.2824 | 122.2275 | -122.5159 | -122.3969 | 122.2961 | 122.3694 | 71.0037 | 73.1506
2481.8281 | 122.6257 | -71.9925 | 50.3311 | -0.17845 | 0.00084388 | 0.070143 | 0.13919 | -0.00068368 | -0.0042084 | -0.003952 | -0.097961 | -0.0054004 | 0.062683 | 0.16167 | -0.02914 | 0.097117 | 0.00096129 | -0.86975 | 50.2853 | -72.2168 | 50.2441 | -54.1855 | -72.0291 | 2.3026 | 1.149 | 50.2853 | -72.0795 | 50.3494 | -69.3466 | 47.6395 | -71.1731 | -0.2243 | -0.045777 | -0.086975 | 17.807 | 74.295 | -0.036621 | 74.5193 | 0.18768 | -0.086975 | -0.045777 | 0.01831 | 2.6459 | 0.8194 | 119.632 | 0.90637 | 119.7189 | 18.0313 | 122.4609 | 2.7328 | 122.4289 | 122.5021 | 122.3648 | 122.2778 | 122.2778 | -122.5479 | -122.4106 | 122.2366 | 122.3419 | 71.1227 | 73.1415
2482.7656 | 122.6395 | -71.9376 | 50.3815 | -0.27 | 0.00063028 | 0.071425 | 0.13769 | 0.0023071 | -0.0037812 | -0.0033112 | -0.067444 | -0.003905 | 0.060761 | 0.16914 | -0.031277 | 0.098185 | 0.0018159 | -0.83771 | 50.3128 | -72.1756 | 50.3128 | -53.9978 | -72.0062 | 2.3575 | 1.1261 | 50.3357 | -72.0154 | 50.386 | -69.278 | 47.6761 | -71.1044 | -0.23804 | -0.068665 | -0.068665 | 17.9398 | 74.295 | -0.068665 | 74.5331 | 0.16937 | -0.07782 | -0.045777 | 0.004577 | 2.6596 | 0.83313 | 119.6136 | 0.91095 | 119.6915 | 18.1778 | 122.4884 | 2.7374 | 122.4014 | 122.4884 | 122.3511 | 122.2504 | 122.2733 | -122.5571 | -122.3969 | 122.2504 | 122.3236 | 71.0999 | 73.0637
2483.8281 | 122.5296 | -72.1344 | 50.2579 | 0.035172 | -0.0027877 | 0.072066 | 0.13983 | -0.0028199 | -0.0024994 | -0.00010676 | -0.14069 | -0.0036914 | 0.063751 | 0.16487 | -0.027431 | 0.099681 | 0.0060883 | -0.91553 | 50.2853 | -72.2443 | 50.1297 | -54.2908 | -72.226 | 2.1149 | 1.1902 | 50.2029 | -72.1893 | 50.1892 | -69.4977 | 47.4609 | -71.3333 | -0.10986 | 0.027465 | -0.12817 | 17.8436 | 74.2493 | -0.091553 | 74.3591 | 0.018311 | -0.054932 | -0.054932 | -0.068665 | 2.6367 | 0.80109 | 119.5953 | 0.85602 | 119.6503 | 17.9535 | 122.374 | 2.6916 | 122.3785 | 122.5296 | 122.3923 | 122.4197 | 122.3373 | -122.5021 | -122.4472 | 122.2641 | 122.3236 | 71.2189 | 73.3246
2484.7656 | 122.6166 | -72.1344 | 50.1846 | -0.11742 | 0.00020288 | 0.071638 | 0.13897 | -0.0019653 | -0.0020722 | -0.004593 | -0.079651 | -0.0030506 | 0.064179 | 0.16615 | -0.028713 | 0.098613 | 0.0030975 | -0.8194 | 50.1297 | -72.3175 | 50.1343 | -54.1122 | -72.1893 | 2.2202 | 1.236 | 50.0931 | -72.2305 | 50.2029 | -69.4382 | 47.4976 | -71.283 | -0.18311 | -0.054931 | -0.050354 | 18.0222 | 74.3546 | -0.054932 | 74.5377 | 0.12817 | -0.096131 | -0.091552 | 0.018311 | 2.6962 | 0.85144 | 119.632 | 0.94757 | 119.7281 | 18.2053 | 122.4518 | 2.7924 | 122.4335 | 122.4472 | 122.3236 | 122.2641 | 122.2275 | -122.5021 | -122.4152 | 122.2687 | 122.3373 | 71.315 | 73.3704
2485.8281 | 122.5983 | -71.9971 | 50.3906 | -0.086899 | -0.00022432 | 0.067366 | 0.1409 | -0.0015381 | -0.0050628 | -0.00096136 | -0.10101 | -0.0049732 | 0.063751 | 0.16102 | -0.02914 | 0.097545 | 0.0052337 | -0.81482 | 50.3082 | -72.2031 | 50.1892 | -53.9246 | -72.084 | 2.0966 | 1.1627 | 50.2808 | -72.1252 | 50.2625 | -69.4061 | 47.5204 | -71.1594 | -0.20599 | -0.082397 | -0.20142 | 18.0725 | 74.0936 | -0.086975 | 74.2996 | 0.11902 | -0.12817 | -0.10986 | -0.12817 | 2.5909 | 0.83771 | 119.5175 | 0.96588 | 119.6457 | 18.2785 | 122.3923 | 2.7191 | 122.3877 | 122.5113 | 122.406 | 122.3053 | 122.2778 | -122.5937 | -122.5159 | 122.1863 | 122.2595 | 71.1823 | 73.1598
2486.7656 | 122.5204 | -72.2168 | 50.1709 | -0.1403 | -1.0718e-05 | 0.069289 | 0.13983 | 0.0010253 | -0.0054902 | -0.0026704 | -0.09491 | -0.002196 | 0.065674 | 0.1638 | -0.0285 | 0.099254 | -0.00032051 | -0.81482 | 50.1434 | -72.345 | 50.0565 | -54.0939 | -72.2122 | 2.0416 | 1.4877 | 50.1251 | -72.2809 | 50.0977 | -69.5435 | 47.3557 | -71.402 | -0.12817 | -0.027465 | -0.11444 | 18.1229 | 74.2584 | 0.004578 | 74.3866 | 0.13275 | -0.064087 | -0.045776 | -0.073242 | 2.6733 | 0.81482 | 119.5724 | 0.87891 | 119.6365 | 18.251 | 122.4014 | 2.7374 | 122.3785 | 122.4884 | 122.406 | 122.3602 | 122.3419 | -122.5159 | -122.4518 | 122.2733 | 122.3145 | 71.402 | 73.7045
2487.7656 | 122.644 | -72.0932 | 50.1755 | -0.17082 | 0.0021255 | 0.069502 | 0.1379 | 0.0010253 | -0.001004 | -0.002884 | -0.049133 | -0.0030506 | 0.065247 | 0.16209 | -0.0285 | 0.099681 | 0.0050201 | -0.82398 | 50.1572 | -72.3175 | 50.1801 | -53.9429 | -72.0978 | 2.2064 | 1.4969 | 50.1343 | -72.1939 | 50.2716 | -69.3512 | 47.5845 | -71.2051 | -0.2243 | -0.01831 | 0.004578 | 18.1503 | 74.2996 | -0.004577 | 74.5239 | 0.21973 | -0.10071 | -0.041199 | 0.09613 | 2.742 | 0.88806 | 119.6777 | 0.98877 | 119.7784 | 18.3746 | 122.4976 | 2.8427 | 122.4655 | 122.4747 | 122.3282 | 122.2504 | 122.2275 | -122.493 | -122.3694 | 122.2733 | 122.3648 | 71.2692 | 73.5901
2488.7656 | 122.5662 | -72.2397 | 50.1251 | -0.10979 | -0.00065152 | 0.072279 | 0.13876 | 0.0048705 | -0.0014312 | -0.0018158 | -0.13763 | -0.0024096 | 0.063538 | 0.16444 | -0.031277 | 0.099681 | 0.0026703 | -0.80566 | 50.1114 | -72.4319 | 49.9969 | -54.071 | -72.2534 | 2.2156 | 1.2039 | 50.0931 | -72.2809 | 50.0748 | -69.5297 | 47.3557 | -71.3791 | -0.19226 | -0.013733 | -0.12817 | 18.1686 | 74.4553 | -0.013733 | 74.6475 | 0.17853 | -0.041199 | -0.032043 | -0.050354 | 2.71 | 0.8606 | 119.5953 | 0.9018 | 119.6365 | 18.3609 | 122.4289 | 2.7512 | 122.3557 | 122.5433 | 122.374 | 122.3511 | 122.3328 | -122.5571 | -122.406 | 122.2366 | 122.3145 | 71.434 | 73.4436
2489.8281 | 122.5571 | -72.345 | 50.0427 | -0.094528 | -0.00086512 | 0.068648 | 0.14004 | 0.0025207 | -0.0024994 | -0.00053396 | -0.097961 | -0.0041186 | 0.062683 | 0.16893 | -0.031277 | 0.09669 | 0.0052337 | -0.85602 | 50.0427 | -72.5006 | 49.8871 | -54.071 | -72.3633 | 2.005 | 1.1307 | 49.9969 | -72.4228 | 50.0015 | -69.7632 | 47.3007 | -71.4523 | -0.15564 | 0 | -0.15564 | 18.2739 | 74.35 | -0.01831 | 74.5056 | 0.13733 | -0.07782 | -0.045777 | -0.041199 | 2.5818 | 0.89264 | 119.6457 | 0.97046 | 119.7235 | 18.4296 | 122.3877 | 2.6596 | 122.4243 | 122.5433 | 122.4197 | 122.3877 | 122.3419 | -122.5433 | -122.4655 | 122.2321 | 122.3465 | 71.489 | 73.4756
2490.7656 | 122.6578 | -72.3907 | 49.8917 | -0.12505 | 0.00063028 | 0.070998 | 0.1394 | 0.00059812 | -0.0037812 | -0.00032036 | -0.033874 | -0.0043322 | 0.063538 | 0.16102 | -0.029568 | 0.096904 | 0.0050201 | -0.80109 | 49.9008 | -72.5739 | 49.8962 | -54.0298 | -72.3541 | 2.0737 | 1.1032 | 49.8322 | -72.4869 | 49.9695 | -69.5572 | 47.287 | -71.4706 | -0.18311 | 0.009155 | 0.004577 | 18.3609 | 74.4644 | 0.036621 | 74.6475 | 0.21973 | -0.09613 | -0.05951 | 0.077819 | 2.8336 | 0.92011 | 119.6777 | 1.0162 | 119.7739 | 18.544 | 122.4701 | 2.9297 | 122.4564 | 122.4747 | 122.319 | 122.2916 | 122.2229 | -122.4655 | -122.3785 | 122.287 | 122.3602 | 71.5897 | 73.494
2491.7656 | 122.5571 | -72.4319 | 49.9191 | -0.10979 | 0.0010575 | 0.07292 | 0.14111 | 0.0065795 | -0.0031402 | -0.002884 | -0.17426 | -0.0032642 | 0.064606 | 0.17256 | -0.028286 | 0.098399 | 0.0045929 | -0.7782 | 49.9008 | -72.5967 | 49.8276 | -53.8971 | -72.4503 | 1.9455 | 1.3184 | 49.8871 | -72.5006 | 49.9054 | -69.6854 | 47.1634 | -71.5622 | -0.16479 | -0.01831 | -0.091552 | 18.5349 | 74.3774 | -0.01831 | 74.5422 | 0.14648 | -0.068664 | -0.032043 | -0.013732 | 2.7466 | 0.86975 | 119.5953 | 0.93841 | 119.664 | 18.6996 | 122.4243 | 2.8152 | 122.406 | 122.4976 | 122.3877 | 122.3328 | 122.319 | -122.5159 | -122.4197 | 122.2595 | 122.3373 | 71.6537 | 73.7503
2492.8438 | 122.5433 | -72.3679 | 49.9603 | -0.14793 | -0.00065152 | 0.071852 | 0.14111 | 0.0010253 | -0.0012176 | -0.00096136 | -0.16205 | -0.00070063 | 0.063751 | 0.16081 | -0.029568 | 0.098826 | 0.0054475 | -0.8194 | 49.8962 | -72.5876 | 49.8505 | -53.6957 | -72.4274 | 1.9318 | 1.2314 | 49.9191 | -72.4457 | 49.9237 | -69.6625 | 47.1771 | -71.5393 | -0.21973 | -0.064087 | -0.10986 | 18.6722 | 74.2996 | -0.059509 | 74.5193 | 0.16022 | -0.07782 | -0.041199 | -0.036621 | 2.7054 | 0.82855 | 119.545 | 0.90637 | 119.6228 | 18.8919 | 122.438 | 2.7832 | 122.3694 | 122.4838 | 122.3648 | 122.2641 | 122.287 | -122.5479 | -122.406 | 122.2183 | 122.2916 | 71.5485 | 73.5992
2493.7656 | 122.5388 | -72.4091 | 49.9878 | -0.094528 | 0.0014847 | 0.071425 | 0.13812 | -0.0017517 | -0.0024994 | -0.0037384 | -0.06134 | -0.003905 | 0.063751 | 0.16508 | -0.028072 | 0.098826 | 0.0067291 | -0.8606 | 49.9558 | -72.5418 | 49.8596 | -53.5538 | -72.377 | 1.9684 | 1.0025 | 49.9237 | -72.4548 | 49.91 | -69.6121 | 47.2046 | -71.5164 | -0.13275 | -0.032043 | -0.12817 | 18.8553 | 74.3774 | 0.032044 | 74.5102 | 0.16479 | -0.045776 | -0.064087 | -0.07782 | 2.7969 | 0.89264 | 119.6136 | 0.93842 | 119.6594 | 18.988 | 122.4014 | 2.8427 | 122.3648 | 122.4976 | 122.3785 | 122.3648 | 122.3328 | -122.5296 | -122.4426 | 122.2687 | 122.319 | 71.5485 | 73.4116
2494.8281 | 122.5891 | -72.5464 | 49.8367 | -0.086899 | -0.00043792 | 0.070357 | 0.13855 | 0.0018799 | -0.0020722 | -0.0037384 | -0.13458 | -0.0013416 | 0.065674 | 0.16658 | -0.029568 | 0.097545 | 0.0033111 | -0.9201 | 49.7772 | -72.7753 | 49.6445 | -53.8742 | -72.5693 | 1.9226 | 1.1581 | 49.7452 | -72.6425 | 49.7726 | -69.7495 | 47.0489 | -71.6446 | -0.22888 | -0.059509 | -0.19226 | 18.6722 | 74.469 | -0.022888 | 74.6979 | 0.20599 | -0.09613 | -0.091553 | -0.064087 | 2.7969 | 0.90179 | 119.5953 | 0.99792 | 119.6915 | 18.9011 | 122.4197 | 2.8931 | 122.4152 | 122.5525 | 122.3877 | 122.3236 | 122.2916 | -122.612 | -122.4792 | 122.1909 | 122.319 | 71.6263 | 73.7045
2495.7656 | 122.6395 | -72.5098 | 49.8093 | -0.11742 | 0.0025529 | 0.071638 | 0.13833 | -0.0011109 | -0.0035674 | -0.0065156 | -0.024719 | -0.0019824 | 0.066315 | 0.16316 | -0.029781 | 0.097545 | 0.0054475 | -0.79193 | 49.7772 | -72.6517 | 49.7818 | -53.6041 | -72.4548 | 2.0966 | 1.3412 | 49.7452 | -72.6196 | 49.8413 | -69.635 | 47.1542 | -71.5759 | -0.14191 | -0.032043 | -0.027466 | 18.9056 | 74.6063 | 0.054932 | 74.7482 | 0.19684 | -0.10986 | -0.064087 | 0.032044 | 2.8748 | 0.93384 | 119.664 | 1.0437 | 119.7739 | 19.0475 | 122.4335 | 2.9846 | 122.4609 | 122.4289 | 122.3648 | 122.287 | 122.2549 | -122.4609 | -122.4289 | 122.2916 | 122.3511 | 71.7178 | 73.851
2496.7656 | 122.5708 | -72.6974 | 49.6857 | -0.06401 | 0.00020288 | 0.072493 | 0.14047 | 0.0012391 | -0.0033538 | -0.0033112 | -0.12238 | -0.0026232 | 0.066101 | 0.17042 | -0.029995 | 0.099467 | 0.0013885 | -0.83771 | 49.6353 | -72.9172 | 49.53 | -53.8193 | -72.702 | 1.9958 | 1.4282 | 49.6033 | -72.7661 | 49.617 | -69.873 | 46.8933 | -71.7865 | -0.21973 | -0.050354 | -0.15564 | 18.8782 | 74.6933 | -0.004577 | 74.913 | 0.21515 | -0.068664 | -0.082398 | -0.068665 | 2.8244 | 0.91095 | 119.5908 | 0.97961 | 119.6594 | 19.0979 | 122.4472 | 2.8931 | 122.3831 | 122.5525 | 122.3694 | 122.3328 | 122.3007 | -122.6028 | -122.4518 | 122.2275 | 122.3145 | 71.8597 | 74.1257
2497.8281 | 122.5525 | -72.7432 | 49.6216 | -0.07164 | -0.00065152 | 0.068861 | 0.14047 | 0.0027343 | -0.0012176 | -0.002243 | -0.067444 | -0.0026232 | 0.066315 | 0.16295 | -0.029354 | 0.096904 | 0.0054475 | -0.87891 | 49.6033 | -72.9401 | 49.4934 | -53.8239 | -72.8531 | 1.9501 | 1.4648 | 49.5667 | -72.8531 | 49.5209 | -69.9509 | 46.8063 | -71.9009 | -0.19684 | -0.018311 | -0.12817 | 18.9194 | 74.6933 | -0.10986 | 74.8901 | 0.086975 | -0.10986 | -0.054932 | -0.10071 | 2.7924 | 0.84228 | 119.5496 | 0.95215 | 119.6594 | 19.1162 | 122.4335 | 2.9022 | 122.374 | 122.5433 | 122.4197 | 122.3465 | 122.3099 | -122.5616 | -122.4747 | 122.2366 | 122.2641 | 71.8643 | 74.2081
2498.7656 | 122.6303 | -72.6837 | 49.6307 | -0.15556 | 0.00063028 | 0.071638 | 0.13833 | -0.00025628 | -0.0031402 | -0.003952 | -0.0033568 | -0.0047594 | 0.065033 | 0.16337 | -0.028072 | 0.097117 | 0.0026703 | -0.82855 | 49.5712 | -72.8668 | 49.5621 | -53.6545 | -72.6746 | 2.0004 | 1.6159 | 49.5438 | -72.7798 | 49.6628 | -69.8227 | 46.9757 | -71.7178 | -0.1831 | -0.059509 | -0.068664 | 19.0292 | 74.6841 | 0.009155 | 74.8672 | 0.19226 | -0.09613 | -0.086975 | 0.032044 | 2.861 | 0.96588 | 119.6594 | 1.062 | 119.7556 | 19.2123 | 122.4289 | 2.9572 | 122.4426 | 122.438 | 122.3236 | 122.2549 | 122.2275 | -122.4976 | -122.4106 | 122.2458 | 122.3465 | 71.8552 | 74.2996
2499.7656 | 122.6578 | -72.7798 | 49.5255 | -0.033493 | 0.0012711 | 0.07292 | 0.1409 | -0.0021789 | -0.0039948 | -0.00053396 | -0.030823 | -0.0028368 | 0.061615 | 0.15932 | -0.030849 | 0.097545 | 0.0037385 | -0.85602 | 49.4751 | -72.9492 | 49.5071 | -53.6591 | -72.7066 | 2.0279 | 1.7624 | 49.4431 | -72.8668 | 49.5712 | -69.8914 | 46.8796 | -71.8185 | -0.16937 | -0.050354 | -0.018311 | 19.1208 | 74.8077 | 0.073242 | 74.9771 | 0.24262 | -0.086975 | -0.082398 | 0.045776 | 2.8885 | 0.9613 | 119.6594 | 1.0483 | 119.7464 | 19.2902 | 122.4564 | 2.9755 | 122.438 | 122.4243 | 122.3099 | 122.2549 | 122.2229 | -122.4747 | -122.3923 | 122.287 | 122.3511 | 71.9238 | 74.5422
2500.8281 | 122.5342 | -72.8165 | 49.585 | -0.16319 | -0.00022432 | 0.071425 | 0.14154 | 0.0012391 | -0.0001496 | -0.0026704 | -0.091858 | -0.0043322 | 0.067597 | 0.16807 | -0.030636 | 0.096904 | 0.0060883 | -0.85602 | 49.5804 | -72.9813 | 49.4339 | -53.7003 | -73.0087 | 1.9363 | 1.6251 | 49.53 | -72.8668 | 49.4888 | -69.9738 | 46.7972 | -71.8826 | -0.16479 | -0.004578 | -0.15106 | 19.1162 | 74.7528 | -0.19226 | 74.9176 | -0.027466 | -0.050354 | -0.054932 | -0.09613 | 2.8427 | 0.93384 | 119.6136 | 0.98419 | 119.664 | 19.281 | 122.4152 | 2.8931 | 122.3557 | 122.5616 | 122.3969 | 122.3969 | 122.3465 | -122.5662 | -122.4518 | 122.2504 | 122.3053 | 71.9604 | 74.4415
2501.7656 | 122.5479 | -72.6883 | 49.6536 | -0.12505 | -0.00043792 | 0.070784 | 0.14025 | -0.00068368 | -0.0031402 | -0.0020294 | -0.030823 | -0.0032642 | 0.064606 | 0.16231 | -0.02914 | 0.096904 | 0.0035247 | -0.78278 | 49.6078 | -72.8577 | 49.5758 | -53.4302 | -72.6608 | 2.0782 | 1.7532 | 49.585 | -72.7661 | 49.6216 | -69.809 | 46.9391 | -71.7453 | -0.16937 | -0.045776 | -0.077819 | 19.2581 | 74.7665 | 0.027465 | 74.9359 | 0.19684 | -0.07782 | -0.068664 | -0.032043 | 2.8793 | 0.94299 | 119.6274 | 1.0208 | 119.7052 | 19.4275 | 122.4335 | 2.9572 | 122.3877 | 122.4655 | 122.3511 | 122.2961 | 122.2733 | -122.5113 | -122.4197 | 122.2641 | 122.3099 | 71.9055 | 74.4415
2502.7656 | 122.5342 | -72.7249 | 49.6536 | -0.0029755 | -0.00065152 | 0.071425 | 0.14196 | 0.0018799 | -0.0022858 | -0.004593 | -0.10712 | -0.0032642 | 0.066315 | 0.16167 | -0.0285 | 0.098826 | 0.0043793 | -0.85144 | 49.6674 | -72.8668 | 49.5026 | -53.4622 | -72.7707 | 1.9089 | 1.5701 | 49.649 | -72.757 | 49.5895 | -69.8273 | 46.8704 | -71.7957 | -0.14191 | 0.013733 | -0.15106 | 19.2627 | 74.6338 | -0.045776 | 74.7757 | 0.09613 | -0.032043 | -0.004577 | -0.064086 | 2.8976 | 0.92926 | 119.5953 | 0.9613 | 119.6274 | 19.4046 | 122.3694 | 2.9297 | 122.3465 | 122.5342 | 122.406 | 122.3923 | 122.374 | -122.5204 | -122.4106 | 122.2275 | 122.3145 | 71.8735 | 74.295
2503.7656 | 122.6028 | -72.6883 | 49.6582 | -0.086899 | 0.0010575 | 0.07292 | 0.14154 | 0.0016663 | -0.0020722 | -0.0018158 | -0.049133 | -0.0058276 | 0.067383 | 0.16722 | -0.028713 | 0.098399 | 0.0039521 | -0.75073 | 49.6033 | -72.821 | 49.617 | -53.1647 | -72.6151 | 2.0645 | 1.6479 | 49.5987 | -72.7524 | 49.6674 | -69.722 | 46.9803 | -71.7041 | -0.13275 | -0.054932 | -0.041199 | 19.5236 | 74.7528 | 0.073242 | 74.8856 | 0.20599 | -0.064087 | -0.059509 | 0.009155 | 2.9663 | 0.98419 | 119.6686 | 1.0483 | 119.7327 | 19.6564 | 122.438 | 3.0304 | 122.4197 | 122.4243 | 122.3511 | 122.2916 | 122.287 | -122.4792 | -122.4106 | 122.3053 | 122.3557 | 71.9376 | 74.3362
2504.7656 | 122.6028 | -72.5647 | 49.6857 | -0.20134 | -0.0021469 | 0.073561 | 0.14004 | 0.0012391 | -0.0014312 | -0.0041656 | -0.058289 | -0.0047594 | 0.066529 | 0.16893 | -0.028286 | 0.09669 | 0.0050201 | -0.78278 | 49.6536 | -72.789 | 49.6445 | -53.0182 | -72.6608 | 1.9592 | 1.5015 | 49.6399 | -72.6837 | 49.7269 | -69.6671 | 47.0078 | -71.6492 | -0.2243 | -0.032044 | -0.041199 | 19.5465 | 74.5239 | -0.096131 | 74.7482 | 0.12817 | -0.11902 | -0.045776 | 0.041199 | 2.8976 | 0.91553 | 119.5724 | 1.0345 | 119.6915 | 19.7708 | 122.4335 | 3.0167 | 122.4106 | 122.4426 | 122.3236 | 122.2183 | 122.2046 | -122.4747 | -122.3694 | 122.2092 | 122.2916 | 71.7819 | 74.0662
2505.8281 | 122.5204 | -72.7524 | 49.6078 | -0.094528 | -0.0017197 | 0.070357 | 0.14047 | 0.0020935 | -0.0029266 | -0.0035248 | -0.10712 | -0.0047594 | 0.063965 | 0.16423 | -0.027859 | 0.099467 | 0.0052337 | -0.82398 | 49.6124 | -72.9034 | 49.4522 | -53.1876 | -72.7753 | 1.9638 | 1.4008 | 49.6033 | -72.8256 | 49.5483 | -69.8044 | 46.8338 | -71.8094 | -0.15106 | 0.004578 | -0.15564 | 19.5648 | 74.7162 | -0.022889 | 74.8672 | 0.12817 | -0.073243 | -0.004578 | -0.059509 | 2.948 | 0.94299 | 119.5862 | 1.0162 | 119.6594 | 19.7159 | 122.3557 | 3.0212 | 122.374 | 122.5159 | 122.4289 | 122.3648 | 122.3557 | -122.5113 | -122.4335 | 122.2046 | 122.3007 | 71.9284 | 74.1531
2506.7656 | 122.5616 | -72.6654 | 49.6628 | 0.073319 | 0.00063028 | 0.073347 | 0.14282 | -0.0019653 | -0.0018586 | -0.0050202 | -0.14069 | -0.0036914 | 0.064392 | 0.16295 | -0.030422 | 0.097758 | 0.0050201 | -0.737 | 49.7086 | -72.8073 | 49.585 | -52.9953 | -72.6654 | 2.0004 | 1.3962 | 49.6262 | -72.7295 | 49.6628 | -69.7357 | 46.9391 | -71.727 | -0.14191 | 0.045776 | -0.07782 | 19.6701 | 74.6658 | 0 | 74.8077 | 0.14191 | -0.064087 | -0.036621 | 0 | 2.9297 | 0.93842 | 119.6045 | 1.0025 | 119.6686 | 19.812 | 122.3923 | 2.9938 | 122.3923 | 122.5159 | 122.3557 | 122.374 | 122.2916 | -122.4701 | -122.3923 | 122.2504 | 122.3282 | 71.9284 | 74.0616
2507.7656 | 122.6166 | -72.6379 | 49.6628 | -0.1403 | -0.00022432 | 0.070357 | 0.1409 | -0.0011109 | -0.0007904 | -0.0060882 | -0.0064086 | -0.0028368 | 0.066101 | 0.16252 | -0.029781 | 0.10054 | 0.0052337 | -0.74158 | 49.6536 | -72.7936 | 49.6674 | -52.7618 | -72.5647 | 2.0462 | 1.6342 | 49.617 | -72.6837 | 49.6216 | -69.5114 | 47.113 | -71.608 | -0.15564 | -0.009156 | 0.004577 | 19.8761 | 74.6841 | 0.073242 | 74.8398 | 0.22888 | -0.045777 | -0.045777 | -0.041199 | 3.1265 | 1.03 | 119.751 | 1.0757 | 119.7968 | 20.0317 | 122.4609 | 3.1723 | 122.3053 | 122.4472 | 122.3007 | 122.2916 | 122.2549 | -122.4564 | -122.3465 | 122.3053 | 122.2595 | 71.8964 | 74.2722
2508.7656 | 122.5571 | -72.6288 | 49.7314 | -0.12505 | 0.00041648 | 0.070357 | 0.13961 | -0.0017517 | -0.0016448 | -0.002243 | -0.049133 | -0.0047594 | 0.065247 | 0.17021 | -0.028286 | 0.096477 | 0.0041657 | -0.73242 | 49.6902 | -72.789 | 49.6399 | -52.6016 | -72.5601 | 2.0874 | 1.6022 | 49.6536 | -72.6974 | 49.6765 | -69.6121 | 46.9849 | -71.6812 | -0.16022 | -0.041198 | -0.091552 | 20.0272 | 74.7162 | 0.068664 | 74.8764 | 0.22888 | -0.068665 | -0.07782 | -0.054931 | 3.0167 | 0.94757 | 119.6136 | 1.0162 | 119.6823 | 20.1874 | 122.4289 | 3.0853 | 122.374 | 122.4792 | 122.3511 | 122.319 | 122.2824 | -122.5204 | -122.4289 | 122.2687 | 122.3053 | 71.8964 | 74.231
2509.8438 | 122.4472 | -72.6654 | 49.6445 | -0.13267 | -0.0010787 | 0.073775 | 0.14196 | 0.0018799 | -0.0035674 | -0.00010676 | -0.15289 | -0.00027343 | 0.06546 | 0.16423 | -0.030209 | 0.098613 | 0.0056611 | -0.79651 | 49.6399 | -72.908 | 49.498 | -52.6566 | -72.757 | 1.9089 | 1.5976 | 49.6582 | -72.7798 | 49.5941 | -69.7495 | 46.8292 | -71.6263 | -0.24261 | -0.004577 | -0.14648 | 20.0089 | 74.5743 | -0.091553 | 74.8169 | 0.15106 | -0.11444 | 0.013733 | -0.050354 | 2.916 | 1.0391 | 119.4946 | 1.1536 | 119.6091 | 20.2515 | 122.406 | 3.0304 | 122.374 | 122.5479 | 122.438 | 122.3053 | 122.3236 | -122.5525 | -122.4243 | 122.1634 | 122.2595 | 71.8689 | 74.263
2510.7656 | 122.5204 | -71.9513 | 50.4272 | -0.10216 | -0.00086512 | 0.071211 | 0.14175 | -0.0043151 | -0.0014312 | -0.0030976 | -0.10406 | -0.0030506 | 0.06546 | 0.15974 | -0.027645 | 0.096477 | 0.0063019 | -0.92468 | 50.4227 | -72.0886 | 50.267 | -52.0248 | -71.8369 | 2.2476 | 1.9363 | 50.3906 | -72.0337 | 50.3311 | -68.9484 | 47.6349 | -70.9808 | -0.13733 | -0.004578 | -0.16022 | 19.9265 | 74.1989 | 0.11444 | 74.3362 | 0.25177 | -0.082397 | -0.036621 | -0.09613 | 3.0029 | 0.97046 | 119.5862 | 1.0529 | 119.6686 | 20.0638 | 122.3557 | 3.0853 | 122.3648 | 122.5113 | 122.4243 | 122.374 | 122.3419 | -122.5159 | -122.4609 | 122.2183 | 122.2824 | 71.0266 | 73.8876
2511.7656 | 122.5159 | -71.9925 | 50.4181 | -0.10216 | 0.0014847 | 0.07292 | 0.14389 | 0.0012391 | -0.0003632 | -0.0041656 | -0.036926 | -0.001128 | 0.063751 | 0.16637 | -0.028713 | 0.098613 | 0.0054475 | -0.92468 | 50.3632 | -72.1573 | 50.2121 | -51.9287 | -71.8735 | 2.2568 | 1.9638 | 50.3036 | -72.0932 | 50.267 | -68.9987 | 47.5754 | -71.1411 | -0.16479 | -0.054932 | -0.20599 | 20.0638 | 74.2493 | 0.11902 | 74.4141 | 0.28381 | -0.10071 | -0.11444 | -0.15106 | 2.9938 | 0.85144 | 119.5679 | 0.95215 | 119.6686 | 20.2286 | 122.3694 | 3.0945 | 122.3602 | 122.5204 | 122.3969 | 122.3557 | 122.2961 | -122.5754 | -122.5113 | 122.2046 | 122.2595 | 71.0678 | 73.9563
2512.7656 | 122.644 | -71.933 | 50.3311 | -0.07164 | -0.00065152 | 0.070357 | 0.14282 | 0.0040161 | -0.0014312 | -0.0030976 | -0.00030524 | -0.0058276 | 0.066529 | 0.16038 | -0.028072 | 0.097758 | 0.0035247 | -0.85144 | 50.3174 | -72.1207 | 50.3906 | -51.6403 | -71.8506 | 2.2888 | 1.9913 | 50.2991 | -72.0337 | 50.4089 | -68.8431 | 47.7356 | -70.9167 | -0.18768 | -0.013733 | 0.059509 | 20.2927 | 74.2218 | 0.082397 | 74.4095 | 0.27008 | -0.10071 | -0.032044 | 0.07782 | 3.0899 | 1.0162 | 119.6686 | 1.1169 | 119.7693 | 20.4803 | 122.5113 | 3.1906 | 122.4426 | 122.4381 | 122.3328 | 122.2504 | 122.2321 | -122.4518 | -122.3648 | 122.3236 | 122.3419 | 71.0815 | 73.9243
2513.7656 | 122.5159 | -71.8597 | 50.5371 | -0.15556 | 0.0023391 | 0.073347 | 0.14218 | 0.0010253 | -0.0018586 | -0.0030976 | -0.052185 | -0.0028368 | 0.066101 | 0.15996 | -0.028286 | 0.095408 | 0.0041657 | -0.86517 | 50.4913 | -71.9788 | 50.3998 | -51.4664 | -71.6446 | 2.1973 | 1.8951 | 50.4913 | -71.9055 | 50.4547 | -68.779 | 47.7631 | -70.8984 | -0.11902 | -0.045776 | -0.13733 | 20.3934 | 74.057 | 0.21515 | 74.176 | 0.33417 | -0.045777 | -0.045776 | -0.082397 | 3.0807 | 0.9613 | 119.6228 | 1.0071 | 119.6686 | 20.5124 | 122.3785 | 3.1265 | 122.3602 | 122.4701 | 122.3969 | 122.3511 | 122.3511 | -122.5159 | -122.4426 | 122.2595 | 122.3145 | 70.9946 | 73.7549
2514.8438 | 122.6349 | -71.7499 | 50.5417 | -0.18608 | -0.0021469 | 0.073775 | 0.14239 | 0.0040161 | 0.0002778 | -0.0026704 | -0.082703 | -0.0047594 | 0.065033 | 0.16679 | -0.031063 | 0.098185 | 0.0033111 | -1.0162 | 50.473 | -71.9788 | 50.5234 | -51.2741 | -71.5622 | 2.2705 | 1.918 | 50.4959 | -71.814 | 50.6287 | -68.6279 | 47.8867 | -70.7108 | -0.22888 | -0.068665 | -0.018311 | 20.4758 | 74.0204 | 0.18768 | 74.2493 | 0.41656 | -0.064087 | -0.045776 | 0.086975 | 3.1219 | 1.0391 | 119.6365 | 1.1032 | 119.7006 | 20.7047 | 122.5021 | 3.186 | 122.4426 | 122.4518 | 122.3099 | 122.2229 | 122.2458 | -122.5204 | -122.3557 | 122.2733 | 122.3785 | 70.7336 | 73.6679
2515.7656 | 122.5754 | -71.7728 | 50.5829 | -0.10979 | -0.0019333 | 0.073988 | 0.14282 | -0.00089728 | -0.0037812 | -0.0048066 | -0.11322 | -0.0032642 | 0.064392 | 0.16572 | -0.0285 | 0.098185 | 0.0020295 | -0.92468 | 50.5829 | -71.9604 | 50.4456 | -51.3474 | -71.5897 | 2.2751 | 1.8539 | 50.5554 | -71.8323 | 50.5463 | -68.6508 | 47.8317 | -70.7932 | -0.18768 | 0 | -0.13733 | 20.4254 | 74.0479 | 0.1831 | 74.2355 | 0.37079 | -0.059509 | -0.027466 | -0.036621 | 3.1219 | 0.97961 | 119.6045 | 1.0391 | 119.664 | 20.6131 | 122.406 | 3.1815 | 122.3785 | 122.5433 | 122.3877 | 122.3557 | 122.3282 | -122.5433 | -122.4152 | 122.2183 | 122.319 | 70.8481 | 73.6267
2516.7656 | 122.5067 | -71.6446 | 50.7385 | -0.12505 | -0.00065152 | 0.073988 | 0.14239 | -0.0021789 | -0.0018586 | -0.0037384 | -0.11017 | -0.0034778 | 0.065888 | 0.16786 | -0.027004 | 0.099254 | 0.0041657 | -0.97961 | 50.7111 | -71.8094 | 50.4547 | -51.2375 | -71.3608 | 2.3529 | 1.7944 | 50.6927 | -71.6995 | 50.6378 | -68.5593 | 47.9416 | -70.6604 | -0.16479 | -0.027465 | -0.28381 | 20.4071 | 73.9975 | 0.28381 | 74.1623 | 0.44861 | -0.054932 | -0.045776 | -0.10071 | 3.0853 | 0.98419 | 119.5862 | 1.0391 | 119.6411 | 20.5719 | 122.2641 | 3.1403 | 122.3373 | 122.5204 | 122.3923 | 122.3557 | 122.3373 | -122.5479 | -122.438 | 122.0993 | 122.2824 | 70.665 | 73.439
2517.7656 | 122.5021 | -70.5276 | 51.8372 | -0.11742 | 0.00041648 | 0.074202 | 0.14282 | -0.0011109 | 0.000705 | -0.0075836 | -0.064392 | -0.002196 | 0.066529 | 0.16423 | -0.030209 | 0.09669 | 0.0071563 | -0.85602 | 51.8097 | -70.6879 | 51.7914 | -50.0473 | -70.4453 | 2.5131 | 2.1011 | 51.8143 | -70.5826 | 51.7502 | -67.4698 | 49.0448 | -69.5663 | -0.16022 | -0.027466 | -0.045776 | 20.4803 | 73.0408 | 0.082398 | 73.201 | 0.24262 | -0.054932 | -0.022888 | -0.086975 | 3.0579 | 0.9613 | 119.5724 | 1.0162 | 119.6274 | 20.6406 | 122.4792 | 3.1128 | 122.3328 | 122.4976 | 122.3969 | 122.3373 | 122.3419 | -122.525 | -122.4197 | 122.319 | 122.2778 | 69.6716 | 72.6288
2518.8281 | 122.612 | -69.8639 | 52.4597 | -0.086899 | -0.0017197 | 0.074202 | 0.14517 | -0.00025628 | -0.0003632 | -0.0060882 | -0.039978 | -0.0041186 | 0.065247 | 0.16658 | -0.028072 | 0.095836 | 0.0054475 | -0.70496 | 52.4094 | -70.0378 | 52.4185 | -49.6948 | -69.6304 | 2.9251 | 2.3438 | 52.4048 | -69.9371 | 52.4689 | -66.7374 | 49.8047 | -68.8477 | -0.17395 | -0.050354 | -0.041199 | 20.1691 | 72.789 | 0.23346 | 72.963 | 0.40741 | -0.073242 | -0.054932 | 0.009155 | 3.1265 | 1.0162 | 119.6686 | 1.0895 | 119.7418 | 20.343 | 122.4564 | 3.1998 | 122.406 | 122.4472 | 122.3419 | 122.2733 | 122.2687 | -122.4976 | -122.3969 | 122.2824 | 122.3328 | 69.1589 | 72.2076
2519.7656 | 122.58 | -69.5526 | 52.7985 | -0.10979 | 0.0021255 | 0.076125 | 0.1488 | 0.0052979 | -0.0012176 | -0.0020294 | -0.15289 | -0.0045458 | 0.066101 | 0.1732 | -0.029781 | 0.099681 | 0.0028839 | -0.70496 | 52.7756 | -69.7311 | 52.7618 | -49.4339 | -69.1727 | 2.8564 | 2.4765 | 52.7893 | -69.6075 | 52.7802 | -66.4948 | 50.061 | -68.5638 | -0.17853 | -0.022888 | -0.036621 | 20.1187 | 72.4091 | 0.37994 | 72.5876 | 0.55847 | -0.054932 | -0.009155 | -0.018311 | 3.0579 | 0.98877 | 119.6136 | 1.0437 | 119.6686 | 20.2972 | 122.493 | 3.1128 | 122.3877 | 122.5067 | 122.3969 | 122.3282 | 122.3419 | -122.5296 | -122.406 | 122.3145 | 122.3328 | 68.8477 | 72.0291
2520.7656 | 122.5433 | -69.1956 | 53.2288 | -0.11742 | -0.0010787 | 0.075911 | 0.14431 | 0.0046569 | -0.0031402 | -0.00096136 | -0.06134 | -0.0032642 | 0.067169 | 0.16295 | -0.02914 | 0.094768 | 0.0054475 | -0.72327 | 53.1509 | -69.3512 | 53.0045 | -49.1638 | -69.0765 | 2.7969 | 1.9547 | 53.1006 | -69.2734 | 53.183 | -66.1652 | 50.1984 | -68.3395 | -0.15564 | -0.07782 | -0.2243 | 20.0317 | 71.9925 | 0.11902 | 72.1481 | 0.27466 | -0.077819 | -0.12817 | -0.045777 | 3.0304 | 0.85602 | 119.3939 | 0.93384 | 119.4717 | 20.1874 | 122.3557 | 3.1082 | 122.4564 | 122.5021 | 122.374 | 122.3465 | 122.2961 | -122.58 | -122.5021 | 122.2 | 122.3785 | 68.4723 | 71.1502
2521.8281 | 122.5433 | -69.0857 | 53.2928 | -0.079269 | 0.00084388 | 0.077834 | 0.14688 | -0.0038879 | -0.0024994 | -0.0054474 | -0.082703 | -0.0026232 | 0.065674 | 0.16444 | -0.031063 | 0.097117 | 0.0052337 | -0.68665 | 53.3157 | -69.2413 | 53.1372 | -49.0173 | -68.8431 | 2.8381 | 2.1561 | 53.2379 | -69.1498 | 53.2104 | -66.0095 | 50.5005 | -68.1198 | -0.15564 | 0.022888 | -0.15564 | 20.0684 | 71.9238 | 0.24261 | 72.0795 | 0.39825 | -0.064087 | -0.054932 | -0.082398 | 3.0762 | 0.96588 | 119.5862 | 1.03 | 119.6503 | 20.224 | 122.3785 | 3.1403 | 122.3602 | 122.5571 | 122.3877 | 122.4014 | 122.3236 | -122.5342 | -122.4426 | 122.2229 | 122.2961 | 68.399 | 71.2418
2522.7656 | 122.5891 | -68.9346 | 53.4027 | -0.14793 | 0.0027665 | 0.078047 | 0.14688 | 0.0033753 | -0.0007904 | -0.0037384 | -0.018616 | -0.0066822 | 0.066101 | 0.16252 | -0.02615 | 0.098826 | 0.00032049 | -0.60425 | 53.3752 | -69.0811 | 53.3569 | -48.7518 | -68.6691 | 3.0212 | 2.449 | 53.334 | -68.9941 | 53.4164 | -65.7715 | 50.7431 | -67.9047 | -0.14648 | -0.027466 | -0.045776 | 20.1828 | 71.9559 | 0.2655 | 72.1024 | 0.41199 | -0.05951 | -0.068665 | 0.013733 | 3.1631 | 1.03 | 119.6777 | 1.0895 | 119.7372 | 20.3293 | 122.4381 | 3.2227 | 122.4106 | 122.4564 | 122.3282 | 122.3099 | 122.2687 | -122.4838 | -122.3969 | 122.2916 | 122.3511 | 68.3304 | 71.3837
2523.7656 | 122.5616 | -68.7332 | 53.6362 | -0.07164 | -0.0015061 | 0.079543 | 0.1473 | 0.0050843 | 6.4004e-05 | -0.002243 | -0.10712 | -0.0017688 | 0.066315 | 0.16872 | -0.02914 | 0.096904 | 0.0037385 | -0.6546 | 53.6133 | -68.9072 | 53.4805 | -48.7244 | -68.573 | 2.98 | 2.4765 | 53.5812 | -68.8202 | 53.5675 | -65.6479 | 50.8621 | -67.7353 | -0.17395 | -0.022888 | -0.15564 | 20.0089 | 71.7133 | 0.16022 | 71.8872 | 0.33417 | -0.086975 | -0.054931 | -0.068664 | 3.0853 | 0.99792 | 119.5953 | 1.0849 | 119.6823 | 20.1828 | 122.3877 | 3.1723 | 122.3877 | 122.5204 | 122.4014 | 122.3465 | 122.3145 | -122.5433 | -122.4564 | 122.2137 | 122.3007 | 68.0786 | 71.2097
2524.8438 | 122.6166 | -68.486 | 53.7781 | -0.22423 | -0.00065152 | 0.079756 | 0.14794 | 0.0029479 | -0.0003632 | 0.00074764 | -0.11017 | -0.0045458 | 0.064606 | 0.16145 | -0.030636 | 0.097331 | 0.0043793 | -0.57678 | 53.7186 | -68.7103 | 53.5538 | -48.6923 | -68.1061 | 3.1723 | 2.7969 | 53.7003 | -68.6142 | 53.8376 | -65.3824 | 51.1322 | -67.4515 | -0.2243 | -0.059509 | -0.2243 | 19.7937 | 71.6583 | 0.37994 | 71.8826 | 0.60425 | -0.12817 | -0.07782 | 0.059509 | 3.1036 | 1.0345 | 119.6182 | 1.1627 | 119.7464 | 20.018 | 122.2641 | 3.2318 | 122.4518 | 122.4289 | 122.3145 | 122.2046 | 122.1863 | -122.4884 | -122.3923 | 122.0398 | 122.3236 | 67.9092 | 71.283
2525.7656 | 122.5433 | -68.2983 | 54.0115 | -0.13267 | 0.0010575 | 0.078047 | 0.15029 | -0.0030335 | -0.001004 | -0.003952 | -0.012512 | -0.0041186 | 0.06546 | 0.16487 | -0.028927 | 0.097117 | 0.0045929 | -0.59509 | 54.0115 | -68.4494 | 53.9474 | -48.3032 | -68.0832 | 3.1128 | 2.9388 | 53.9658 | -68.3807 | 53.9658 | -65.213 | 51.2787 | -67.3508 | -0.15106 | 0 | -0.064087 | 19.9951 | 71.4111 | 0.21515 | 71.5622 | 0.36621 | -0.082397 | -0.045777 | -0.045777 | 3.0853 | 0.94757 | 119.577 | 1.03 | 119.6594 | 20.1462 | 122.3969 | 3.1677 | 122.3465 | 122.4609 | 122.3465 | 122.3099 | 122.2641 | -122.4609 | -122.3923 | 122.2458 | 122.2641 | 67.7032 | 71.2372
2526.7656 | 122.5204 | -68.1107 | 54.2633 | -0.13267 | -0.00043792 | 0.081892 | 0.15072 | 0.0010253 | -0.001004 | -0.0020294 | -0.055237 | -0.0043322 | 0.063965 | 0.16637 | -0.0285 | 0.096263 | 0.0063019 | -0.64087 | 54.213 | -68.3166 | 54.071 | -48.2941 | -67.9779 | 3.1403 | 3.0624 | 54.213 | -68.1702 | 54.1809 | -65.0299 | 51.4343 | -67.1494 | -0.20599 | -0.050354 | -0.19226 | 19.8166 | 71.2509 | 0.13275 | 71.4569 | 0.33874 | -0.059509 | -0.050354 | -0.082398 | 3.0808 | 0.9613 | 119.545 | 1.0208 | 119.6045 | 20.0226 | 122.3877 | 3.1403 | 122.3511 | 122.5296 | 122.3831 | 122.3236 | 122.3236 | -122.58 | -122.4335 | 122.1817 | 122.2916 | 67.4698 | 71.1731
2527.7656 | 122.5296 | -68.0557 | 54.2908 | -0.086899 | -0.00022432 | 0.081465 | 0.14965 | -0.00046988 | 0.0019866 | -0.0024566 | -0.039978 | -0.003905 | 0.064606 | 0.16594 | -0.0285 | 0.095836 | 0.0043793 | -0.53558 | 54.245 | -68.161 | 54.245 | -48.0789 | -67.8268 | 3.1906 | 3.2181 | 54.2404 | -68.1015 | 54.2908 | -64.8834 | 51.5991 | -67.0212 | -0.10529 | -0.045776 | -0.045776 | 19.9768 | 71.2463 | 0.22888 | 71.3516 | 0.33417 | -0.045776 | -0.050354 | 0 | 3.1723 | 1.0345 | 119.6548 | 1.0803 | 119.7006 | 20.0821 | 122.406 | 3.2181 | 122.3923 | 122.406 | 122.3419 | 122.3007 | 122.2961 | -122.4518 | -122.3923 | 122.3007 | 122.3465 | 67.5201 | 71.2738
2528.7656 | 122.4243 | -67.8909 | 54.4693 | -0.10216 | -0.00086512 | 0.081679 | 0.15094 | 0.0018799 | 0.0002778 | -0.0041656 | -0.079651 | -0.0030506 | 0.064606 | 0.15697 | -0.028713 | 0.095195 | 0.0041657 | -0.59052 | 54.4189 | -68.0969 | 54.2816 | -48.0103 | -67.7536 | 3.1631 | 3.273 | 54.3777 | -68.0145 | 54.3228 | -64.5355 | 51.828 | -66.9434 | -0.20599 | -0.050354 | -0.18768 | 19.8807 | 71.0541 | 0.13733 | 71.2601 | 0.34332 | -0.1236 | -0.091552 | -0.14648 | 3.3554 | 0.94757 | 119.7189 | 1.0712 | 119.8425 | 20.0867 | 122.3785 | 3.479 | 122.3373 | 122.5159 | 122.3923 | 122.3099 | 122.2687 | -122.5662 | -122.4838 | 122.1725 | 122.2137 | 67.3004 | 71.1639
2529.8281 | 122.6349 | -67.9871 | 54.2999 | -0.15556 | 0.00020288 | 0.081038 | 0.15072 | 0.00081172 | -0.0012176 | -0.004593 | -0.018616 | -0.0045458 | 0.062897 | 0.16359 | -0.028713 | 0.096477 | 0.0056611 | -0.57678 | 54.277 | -68.1564 | 54.2496 | -47.9233 | -67.7628 | 3.2639 | 3.2913 | 54.2633 | -68.0786 | 54.3365 | -64.7552 | 51.6769 | -66.9296 | -0.16937 | -0.022888 | -0.050354 | 20.0638 | 71.2509 | 0.22431 | 71.4203 | 0.39368 | -0.091552 | -0.036621 | 0.036621 | 3.2318 | 1.0574 | 119.664 | 1.149 | 119.7556 | 20.2332 | 122.406 | 3.3234 | 122.4152 | 122.4335 | 122.3419 | 122.2641 | 122.2504 | -122.4564 | -122.3785 | 122.2366 | 122.3236 | 67.4103 | 71.2784
2530.7656 | 122.5159 | -68.042 | 54.3274 | 0.065689 | -0.0023605 | 0.08531 | 0.15435 | -0.0023925 | -0.0012176 | -0.0024566 | -0.10406 | -0.0024096 | 0.067383 | 0.16679 | -0.029354 | 0.095836 | 0.0033111 | -0.63629 | 54.364 | -68.1793 | 54.1672 | -48.0148 | -67.8772 | 3.1265 | 3.0762 | 54.277 | -68.0923 | 54.2404 | -64.8468 | 51.5442 | -67.0303 | -0.13733 | 0.036621 | -0.16022 | 20.0272 | 71.1685 | 0.16479 | 71.3058 | 0.30212 | -0.050354 | -0.050354 | -0.086976 | 3.1952 | 1.0117 | 119.5862 | 1.062 | 119.6365 | 20.1645 | 122.3465 | 3.2455 | 122.3328 | 122.5433 | 122.3694 | 122.406 | 122.319 | -122.5067 | -122.4197 | 122.2092 | 122.2824 | 67.4057 | 71.1182
2531.7656 | 122.5342 | -67.923 | 54.4006 | 0.012284 | -1.0718e-05 | 0.084456 | 0.15478 | 0.00081172 | -0.0014312 | 0.0020294 | -0.13153 | -0.003905 | 0.063538 | 0.16765 | -0.030422 | 0.096904 | 0.0016021 | -0.55389 | 54.4235 | -68.0969 | 54.3045 | -47.818 | -67.7582 | 3.1174 | 3.3096 | 54.3686 | -68.0145 | 54.3915 | -64.7369 | 51.6586 | -66.8976 | -0.17395 | 0.022888 | -0.096131 | 20.105 | 71.0403 | 0.16479 | 71.2143 | 0.33875 | -0.091552 | -0.032044 | -0.009156 | 3.186 | 1.0254 | 119.5816 | 1.1169 | 119.6732 | 20.2789 | 122.4014 | 3.2776 | 122.406 | 122.5204 | 122.3831 | 122.3465 | 122.2916 | -122.4976 | -122.4152 | 122.2275 | 122.3145 | 67.3691 | 71.2326
2532.7656 | 122.5525 | -67.9138 | 54.4098 | -0.086899 | -0.0015061 | 0.084883 | 0.1535 | -0.00025628 | -0.001004 | -0.002884 | -0.10101 | -0.0017688 | 0.06482 | 0.16786 | -0.028927 | 0.097972 | 0.0071563 | -0.62714 | 54.4235 | -68.0969 | 54.3091 | -47.7356 | -67.6895 | 3.1769 | 3.3691 | 54.3457 | -67.9871 | 54.4235 | -64.6957 | 51.6907 | -66.8655 | -0.18311 | 0.013733 | -0.10071 | 20.1782 | 71.0907 | 0.2243 | 71.2738 | 0.40741 | -0.073243 | -0.064087 | 0.013733 | 3.2181 | 1.0483 | 119.6045 | 1.1215 | 119.6777 | 20.3613 | 122.406 | 3.2913 | 122.4106 | 122.5204 | 122.3328 | 122.3373 | 122.2595 | -122.5067 | -122.3969 | 122.2229 | 122.3373 | 67.2867 | 71.283
2533.8281 | 122.5113 | -67.6895 | 54.657 | -0.13267 | -0.00043792 | 0.08531 | 0.15649 | -0.00025628 | -0.0018586 | -0.0035248 | -0.079651 | -0.0026232 | 0.064392 | 0.16658 | -0.028072 | 0.096477 | 0.0077973 | -0.48523 | 54.6707 | -67.8406 | 54.5197 | -47.5708 | -67.4698 | 3.3417 | 3.3279 | 54.6524 | -67.7582 | 54.5792 | -64.4852 | 51.8829 | -66.6824 | -0.15106 | 0.013733 | -0.13733 | 20.1187 | 71.0312 | 0.21973 | 71.1823 | 0.37079 | -0.068665 | -0.004577 | -0.077819 | 3.2043 | 1.0071 | 119.5724 | 1.0757 | 119.6411 | 20.2698 | 122.3602 | 3.273 | 122.3373 | 122.5113 | 122.4106 | 122.3602 | 122.3419 | -122.4976 | -122.4152 | 122.2092 | 122.2687 | 67.2043 | 71.0175
2534.7656 | 122.6349 | -67.8085 | 54.4647 | -0.10979 | -0.00086512 | 0.087233 | 0.15435 | 0.0027343 | -0.0020722 | -0.0041656 | 0.0057984 | -0.0049732 | 0.064179 | 0.16252 | -0.030422 | 0.096263 | 0.0028839 | -0.5722 | 54.4556 | -67.9779 | 54.451 | -47.5616 | -67.5201 | 3.3691 | 3.5843 | 54.4144 | -67.8818 | 54.5151 | -64.5035 | 51.8417 | -66.7145 | -0.16937 | -0.009156 | -0.013733 | 20.2469 | 71.1777 | 0.28839 | 71.347 | 0.45776 | -0.073242 | -0.050354 | 0.050354 | 3.3051 | 1.0941 | 119.6503 | 1.1673 | 119.7235 | 20.4163 | 122.4289 | 3.3783 | 122.3969 | 122.4335 | 122.2961 | 122.2641 | 122.2229 | -122.4426 | -122.3465 | 122.2595 | 122.3236 | 67.2363 | 71.3928
2535.7656 | 122.5433 | -67.9779 | 54.3549 | -0.15556 | 0.00063028 | 0.086592 | 0.15692 | 0.0025207 | 6.4004e-05 | -0.0024566 | -0.04303 | -0.0041186 | 0.063751 | 0.16508 | -0.030209 | 0.098826 | 0.00096129 | -0.59509 | 54.2953 | -68.1427 | 54.2542 | -47.612 | -67.6849 | 3.3875 | 3.6255 | 54.2908 | -68.0511 | 54.2908 | -64.7095 | 51.6266 | -66.9434 | -0.16479 | -0.059509 | -0.10071 | 20.3659 | 71.3654 | 0.29297 | 71.5302 | 0.45776 | -0.073242 | -0.064087 | -0.064087 | 3.2684 | 1.0345 | 119.6045 | 1.1078 | 119.6777 | 20.5307 | 122.3969 | 3.3417 | 122.3419 | 122.438 | 122.3419 | 122.2733 | 122.2687 | -122.4976 | -122.406 | 122.2321 | 122.2687 | 67.3828 | 71.6034
2536.7656 | 122.5571 | -68.1473 | 54.1901 | -0.14793 | 0.0014847 | 0.089796 | 0.1582 | 0.0033753 | 0.0009186 | -0.0024566 | -0.12238 | -0.0034778 | 0.065033 | 0.16872 | -0.029568 | 0.097545 | 0.0052337 | -0.64087 | 54.1397 | -68.3395 | 54.0527 | -47.7173 | -67.9138 | 3.2867 | 3.6392 | 54.1901 | -68.161 | 54.1809 | -64.8514 | 51.4526 | -67.0761 | -0.19226 | -0.050354 | -0.13733 | 20.43 | 71.434 | 0.23346 | 71.6263 | 0.42572 | -0.013733 | 0 | -0.009155 | 3.2959 | 1.0712 | 119.5999 | 1.0849 | 119.6136 | 20.6223 | 122.3923 | 3.3096 | 122.3419 | 122.4792 | 122.3511 | 122.287 | 122.3373 | -122.5296 | -122.3511 | 122.2 | 122.3282 | 67.5064 | 71.7865
2537.8281 | 122.4792 | -68.2388 | 54.1534 | -0.06401 | -0.0012923 | 0.086592 | 0.15863 | -0.0038879 | -0.0016448 | -0.00074776 | -0.070496 | -0.0045458 | 0.06546 | 0.1606 | -0.029568 | 0.094768 | 0.0043793 | -0.69122 | 54.0939 | -68.4128 | 53.9474 | -47.7356 | -68.0649 | 3.2364 | 3.5843 | 54.1351 | -68.2434 | 54.0115 | -64.9704 | 51.3565 | -67.1951 | -0.17395 | -0.059509 | -0.20599 | 20.5032 | 71.4752 | 0.17395 | 71.6492 | 0.3479 | -0.004577 | -0.01831 | -0.14191 | 3.2684 | 1.0437 | 119.5953 | 1.0483 | 119.5999 | 20.6772 | 122.3602 | 3.273 | 122.2549 | 122.5067 | 122.3785 | 122.3328 | 122.374 | -122.5662 | -122.3969 | 122.1863 | 122.2504 | 67.5476 | 71.8231
2538.7656 | 122.5067 | -68.0054 | 54.3457 | -0.10216 | -0.00022432 | 0.088942 | 0.16119 | 0.0044433 | -0.0001496 | -0.0026704 | -0.070496 | -0.00091423 | 0.066529 | 0.1685 | -0.029995 | 0.096904 | 0.0060883 | -0.64545 | 54.3732 | -68.1793 | 54.1672 | -47.525 | -67.7856 | 3.2547 | 3.4836 | 54.3137 | -68.0923 | 54.2633 | -64.7141 | 51.5671 | -66.9571 | -0.17395 | 0.027466 | -0.17853 | 20.4803 | 71.2601 | 0.21973 | 71.434 | 0.39368 | -0.086975 | -0.032043 | -0.082397 | 3.2913 | 1.0483 | 119.5724 | 1.1353 | 119.6594 | 20.6543 | 122.3465 | 3.3783 | 122.3557 | 122.5525 | 122.406 | 122.3785 | 122.319 | -122.525 | -122.438 | 122.1725 | 122.2687 | 67.3599 | 71.489
2539.7656 | 122.4838 | -67.6712 | 54.7165 | -0.018234 | -1.0718e-05 | 0.091505 | 0.1614 | -0.0032471 | -0.0003632 | -0.0048066 | -0.097961 | -0.0034778 | 0.065674 | 0.16252 | -0.029568 | 0.097972 | 0.0058747 | -0.99792 | 54.689 | -67.8223 | 54.5288 | -47.3419 | -67.3096 | 3.5248 | 3.5934 | 54.6295 | -67.7399 | 54.5883 | -64.3707 | 51.9104 | -66.6046 | -0.15106 | -0.027466 | -0.18768 | 20.3293 | 71.196 | 0.36163 | 71.347 | 0.5127 | -0.068664 | -0.086975 | -0.12817 | 3.3005 | 1.0666 | 119.5816 | 1.1353 | 119.6503 | 20.4803 | 122.3511 | 3.3691 | 122.3282 | 122.5113 | 122.3694 | 122.3602 | 122.3007 | -122.5388 | -122.4564 | 122.2 | 122.2595 | 66.6733 | 71.2646
2540.7656 | 122.5296 | -66.6458 | 55.6641 | -0.14793 | -0.00043792 | 0.089369 | 0.18277 | 0.0014527 | 0.0032684 | -0.002243 | -0.033874 | -0.0032642 | 0.065247 | 0.16017 | -0.028286 | 0.097117 | 0.0092927 | -2.4353 | 55.6366 | -66.8289 | 55.5222 | -46.6553 | -65.918 | 3.8589 | 3.6987 | 55.6503 | -66.7328 | 55.5817 | -63.3957 | 52.8992 | -65.657 | -0.1831 | -0.027465 | -0.14191 | 19.9905 | 70.5048 | 0.72784 | 70.6879 | 0.91095 | -0.086975 | -0.013732 | -0.082397 | 3.2501 | 0.98877 | 119.545 | 1.0757 | 119.632 | 20.1736 | 122.3511 | 3.3371 | 122.3145 | 122.4655 | 122.3831 | 122.2824 | 122.2961 | -122.493 | -122.3969 | 122.168 | 122.2275 | 64.2105 | 70.3445
2541.7656 | 122.5525 | -67.0212 | 55.2887 | -0.13267 | 0.0021255 | 0.092574 | 0.1802 | 0.00059812 | 0.0047638 | -0.00053396 | -0.13763 | -0.0036914 | 0.065888 | 0.16893 | -0.029354 | 0.096904 | 0.0016021 | -2.7786 | 55.2658 | -67.218 | 55.1605 | -46.9025 | -66.2888 | 3.6621 | 3.6484 | 55.2795 | -67.1265 | 55.2292 | -63.7619 | 52.4826 | -65.9958 | -0.19684 | -0.022888 | -0.12817 | 20.1187 | 70.6833 | 0.73242 | 70.8801 | 0.92926 | -0.10529 | -0.009155 | -0.059509 | 3.2593 | 1.0254 | 119.5038 | 1.1307 | 119.6091 | 20.3156 | 122.3785 | 3.3646 | 122.3557 | 122.4838 | 122.406 | 122.287 | 122.3007 | -122.5067 | -122.4152 | 122.1817 | 122.2504 | 64.2426 | 70.6696
2542.7656 | 122.5937 | -67.0303 | 55.2933 | -0.20897 | 0.0016983 | 0.093214 | 0.17593 | 0.0018799 | 0.0009186 | -0.0030976 | -0.11932 | -0.0017688 | 0.06546 | 0.17064 | -0.027859 | 0.09904 | 0.0067291 | -2.7466 | 55.2383 | -67.2821 | 55.1376 | -46.8292 | -66.2842 | 3.7949 | 3.7811 | 55.2063 | -67.1356 | 55.2246 | -63.739 | 52.533 | -65.9958 | -0.25177 | -0.054932 | -0.15564 | 20.2011 | 70.8252 | 0.74615 | 71.077 | 0.99792 | -0.10529 | -0.086975 | -0.068665 | 3.2913 | 1.0345 | 119.5633 | 1.1398 | 119.6686 | 20.4529 | 122.4197 | 3.3966 | 122.3602 | 122.5204 | 122.3419 | 122.2687 | 122.2366 | -122.5754 | -122.4289 | 122.168 | 122.2549 | 64.2838 | 70.8115
2543.8281 | 122.5021 | -67.2272 | 55.1239 | -0.16319 | 0.0014847 | 0.096846 | 0.17999 | 0.0025207 | 0.0032684 | -0.001175 | -0.13458 | -0.0026232 | 0.062897 | 0.1685 | -0.029995 | 0.097331 | 0.0080109 | -2.8473 | 55.0919 | -67.4149 | 54.95 | -46.9528 | -66.4078 | 3.5889 | 3.8177 | 55.0781 | -67.3187 | 55.0507 | -63.9267 | 52.3224 | -66.1789 | -0.18768 | -0.032043 | -0.17395 | 20.2744 | 70.816 | 0.8194 | 71.0037 | 1.0071 | -0.091553 | -0.045776 | -0.073242 | 3.3005 | 1.0483 | 119.5496 | 1.1398 | 119.6411 | 20.462 | 122.3648 | 3.392 | 122.3694 | 122.5067 | 122.3969 | 122.319 | 122.3053 | -122.5388 | -122.4426 | 122.1771 | 122.2778 | 64.3799 | 71.0449
2544.7656 | 122.5204 | -67.2546 | 55.1239 | -0.094528 | 0.0010575 | 0.095564 | 0.17935 | -0.00046988 | 0.0032684 | -0.0016022 | -0.064392 | -0.0017688 | 0.069733 | 0.16487 | -0.026363 | 0.096904 | 0.0048065 | -2.6825 | 55.188 | -67.3599 | 54.9179 | -46.8384 | -66.3986 | 3.7308 | 3.9185 | 55.0873 | -67.3141 | 55.0507 | -63.8763 | 52.3407 | -66.1697 | -0.10529 | 0.064087 | -0.20599 | 20.4163 | 70.9854 | 0.85602 | 71.0907 | 0.9613 | -0.059509 | -0.036621 | -0.073242 | 3.3783 | 1.0849 | 119.5953 | 1.1444 | 119.6548 | 20.5215 | 122.2778 | 3.4378 | 122.3648 | 122.5479 | 122.4014 | 122.4426 | 122.3419 | -122.4838 | -122.438 | 122.1725 | 122.3053 | 64.5721 | 71.1731
2545.7656 | 122.5159 | -66.9891 | 55.3619 | -0.14793 | -0.00065152 | 0.10048 | 0.18212 | 0.0023071 | 0.0036956 | -0.0037384 | -0.055237 | -0.0030506 | 0.065674 | 0.16615 | -0.031063 | 0.098613 | 0.0026703 | -2.7054 | 55.4352 | -67.0944 | 55.1651 | -46.6919 | -66.1606 | 3.9139 | 3.9917 | 55.3299 | -67.0715 | 55.2795 | -63.62 | 52.5925 | -65.9271 | -0.10528 | 0.073243 | -0.19684 | 20.2972 | 70.903 | 0.82855 | 71.0083 | 0.93384 | -0.082397 | -0.032043 | -0.082397 | 3.3691 | 1.062 | 119.5816 | 1.1444 | 119.664 | 20.4025 | 122.2595 | 3.4515 | 122.3511 | 122.5296 | 122.4014 | 122.4243 | 122.319 | -122.4564 | -122.4335 | 122.1542 | 122.2687 | 64.2838 | 70.9808
2546.7656 | 122.493 | -67.0532 | 55.2979 | -0.17845 | 0.0014847 | 0.1056 | 0.18554 | 0.0063659 | 0.0019866 | -0.0020294 | -0.11932 | -0.0034778 | 0.066956 | 0.16936 | -0.029781 | 0.098613 | 0.0039521 | -2.8427 | 55.2795 | -67.2226 | 55.1331 | -46.7514 | -66.188 | 3.7994 | 4.0649 | 55.2429 | -67.1265 | 55.2063 | -63.6887 | 52.4826 | -65.9729 | -0.16937 | -0.018311 | -0.16479 | 20.3018 | 70.8527 | 0.86517 | 71.022 | 1.0345 | -0.073242 | -0.054932 | -0.091553 | 3.3646 | 1.0803 | 119.5358 | 1.1536 | 119.6091 | 20.4712 | 122.3557 | 3.4378 | 122.3328 | 122.5021 | 122.3694 | 122.3328 | 122.2961 | -122.5204 | -122.4243 | 122.1863 | 122.2595 | 64.2105 | 71.1182
2547.8281 | 122.4976 | -66.9022 | 55.4031 | -0.12505 | 0.0025529 | 0.1086 | 0.18682 | -0.00089728 | 0.0045502 | -0.0041656 | -0.036926 | -0.0036914 | 0.065247 | 0.16936 | -0.027645 | 0.095195 | 0.0077973 | -2.8473 | 55.3665 | -67.1265 | 55.188 | -46.6599 | -66.0645 | 4.1016 | 3.923 | 55.2979 | -67.0532 | 55.2704 | -63.588 | 52.8488 | -65.7394 | -0.2243 | -0.036621 | -0.21515 | 20.2423 | 71.0037 | 0.83771 | 71.228 | 1.062 | -0.15106 | -0.10529 | -0.13275 | 3.3142 | 1.1627 | 119.751 | 1.3138 | 119.902 | 20.4666 | 122.3145 | 3.4653 | 122.3236 | 122.493 | 122.3511 | 122.2687 | 122.2 | -122.5296 | -122.4564 | 122.0901 | 122.1725 | 64.0549 | 70.8252
2548.7656 | 122.4976 | -66.893 | 55.4398 | -0.10979 | 0.00084388 | 0.10774 | 0.18917 | -0.0030335 | 0.003482 | -0.0035248 | -0.021667 | -0.0054004 | 0.066956 | 0.17107 | -0.029781 | 0.097545 | 0.0041657 | -2.7557 | 55.4169 | -67.0029 | 55.3436 | -46.3394 | -65.9225 | 4.0833 | 3.9963 | 55.4123 | -66.9525 | 55.3711 | -63.4506 | 52.7161 | -65.8173 | -0.10986 | -0.022888 | -0.09613 | 20.5536 | 70.9763 | 0.97046 | 71.0861 | 1.0803 | -0.05951 | -0.027466 | -0.068664 | 3.4424 | 1.0757 | 119.6091 | 1.1353 | 119.6686 | 20.6635 | 122.3465 | 3.5019 | 122.3236 | 122.4197 | 122.3648 | 122.3099 | 122.3053 | -122.4426 | -122.3923 | 122.2366 | 122.2641 | 64.1373 | 70.8893
2549.7656 | 122.5113 | -65.4602 | 56.8863 | -0.15556 | -0.0015061 | 0.11714 | 0.19751 | 0.00017092 | 0.0026276 | -0.0065156 | -0.024719 | -0.0017688 | 0.06546 | 0.17213 | -0.02914 | 0.095622 | 0.0065155 | -2.6871 | 56.8726 | -65.6158 | 56.8817 | -45.5521 | -64.7919 | 4.4998 | 4.248 | 56.868 | -65.506 | 56.7993 | -62.0682 | 54.1031 | -64.3845 | -0.15564 | -0.013733 | -0.004578 | 19.9081 | 69.96 | 0.66833 | 70.1157 | 0.82397 | -0.045776 | -0.018311 | -0.086976 | 3.392 | 1.0757 | 119.5633 | 1.1215 | 119.6091 | 20.0638 | 122.4976 | 3.4378 | 122.3053 | 122.4884 | 122.374 | 122.3328 | 122.3282 | -122.5021 | -122.3923 | 122.3419 | 122.2595 | 62.7731 | 69.7083
2550.8281 | 122.6395 | -86.0596 | 36.1816 | -0.14793 | 0.0031937 | 0.076979 | 0.16824 | 0.0029479 | 0.0098908 | -0.001175 | 0.0057984 | -0.0051868 | 0.066315 | 0.16337 | -0.030636 | 0.096049 | 0.0086517 | -4.6921 | 36.1633 | -86.2747 | 36.1725 | -57.9529 | -84.3201 | -0.60425 | -1.6754 | 36.113 | -86.2015 | 36.2137 | -81.7017 | 33.5495 | -84.7824 | -0.21515 | -0.018311 | -0.009156 | 28.1067 | 85.4553 | 1.7395 | 85.6705 | 1.9547 | -0.14191 | -0.068665 | 0.032043 | 4.3579 | 1.2772 | 119.6091 | 1.4191 | 119.751 | 28.3218 | 122.4472 | 4.4998 | 122.4152 | 122.438 | 122.3145 | 122.2229 | 122.1725 | -122.4564 | -122.3831 | 122.2321 | 122.2733 | 81.3675 | 84.3842
2551.7656 | 122.5204 | -83.5007 | 38.8275 | -0.10979 | 0.00084388 | 0.079329 | 0.17059 | 0.0033753 | 0.010532 | 0.0013886 | -0.12238 | -0.0024096 | 0.064606 | 0.16701 | -0.030422 | 0.096263 | 0.010574 | -4.4861 | 38.8504 | -83.6792 | 38.7497 | -55.7602 | -81.2668 | -0.10071 | -0.91553 | 38.7863 | -83.5922 | 38.7817 | -79.3167 | 36.0535 | -82.2464 | -0.17853 | 0.022888 | -0.07782 | 27.7405 | 83.4 | 2.2339 | 83.5785 | 2.4124 | -0.091553 | -0.041199 | -0.045777 | 4.184 | 1.2543 | 119.5541 | 1.3458 | 119.6457 | 27.919 | 122.4289 | 4.2755 | 122.374 | 122.5296 | 122.3785 | 122.3511 | 122.287 | -122.5067 | -122.4197 | 122.2504 | 122.2824 | 79.0146 | 82.5851
2552.7656 | 122.5021 | -80.7175 | 41.6611 | -0.10979 | -0.00043792 | 0.079329 | 0.17187 | 0.0033753 | 0.01694 | -0.0020294 | -0.076599 | -0.0019824 | 0.067383 | 0.16273 | -0.029568 | 0.099467 | 0.0099335 | -4.1748 | 41.6656 | -80.8319 | 41.4963 | -53.7003 | -77.7969 | 0.71869 | -0.28839 | 41.6336 | -80.7678 | 41.6016 | -76.5747 | 38.9099 | -79.4449 | -0.11444 | 0.004577 | -0.16479 | 27.0172 | 81.4362 | 2.9205 | 81.5506 | 3.035 | -0.050354 | -0.027466 | -0.05951 | 4.1428 | 1.2726 | 119.6274 | 1.3229 | 119.6777 | 27.1317 | 122.3282 | 4.1931 | 122.3694 | 122.4976 | 122.4014 | 122.3831 | 122.3511 | -122.493 | -122.4289 | 122.2137 | 122.319 | 76.5427 | 80.4291
2553.8281 | 122.5616 | -88.0325 | 34.2728 | -0.079269 | 0.00041648 | 0.079115 | 0.16589 | 0.0014527 | -0.0012176 | -0.004593 | -0.085754 | -0.0028368 | 0.06482 | 0.16615 | -0.027859 | 0.097331 | 0.0026703 | -4.7745 | 34.0759 | -88.4125 | 34.1995 | -58.1589 | -86.3983 | -1.4236 | -2.5589 | 34.2682 | -88.1744 | 34.4009 | -83.4549 | 31.5445 | -86.7096 | -0.37994 | -0.19684 | -0.073242 | 29.8737 | 86.6089 | 1.6342 | 86.9888 | 2.0142 | -0.14191 | -0.004578 | 0.12817 | 4.5776 | 1.3229 | 119.577 | 1.4648 | 119.7189 | 30.2536 | 122.612 | 4.7195 | 122.5754 | 122.4884 | 122.4426 | 122.1085 | 122.3007 | -122.6852 | -122.4472 | 122.2321 | 122.4335 | 83.2581 | 85.4736
2554.7656 | 122.4884 | -75.0916 | 47.3053 | -0.10216 | 0.00041648 | 0.07762 | 0.18148 | 0.0029479 | 0.028476 | -0.0020294 | -0.024719 | -0.0026232 | 0.066956 | 0.16102 | -0.028072 | 0.097758 | 0.0088653 | -3.7262 | 47.2733 | -75.2197 | 47.3236 | -49.6353 | -70.4132 | 1.9363 | 1.1261 | 47.3007 | -75.0961 | 47.2183 | -71.1319 | 44.5404 | -73.8327 | -0.12817 | -0.032044 | 0.01831 | 25.4562 | 77.0279 | 4.6783 | 77.1561 | 4.8065 | -0.004577 | -0.004578 | -0.086975 | 3.9597 | 1.2589 | 119.632 | 1.2634 | 119.6365 | 25.5844 | 122.5433 | 3.9642 | 122.3145 | 122.493 | 122.3969 | 122.3648 | 122.3923 | -122.525 | -122.4014 | 122.4152 | 122.3099 | 71.3654 | 76.2177
2555.7656 | 122.5113 | -70.8069 | 51.5213 | -0.13267 | 0.00063028 | 0.076125 | 0.18917 | 0.00017092 | 0.037235 | -0.0030976 | -0.079651 | -0.0030506 | 0.063751 | 0.16316 | -0.027431 | 0.096477 | 0.0054475 | -3.3783 | 51.4709 | -71.0312 | 51.384 | -47.081 | -64.3616 | 3.3691 | 2.5864 | 51.4481 | -70.8801 | 51.4984 | -67.0303 | 48.8159 | -69.5847 | -0.2243 | -0.050354 | -0.13733 | 23.7259 | 74.176 | 6.4453 | 74.4003 | 6.6696 | -0.073242 | -0.073242 | -0.022888 | 3.7766 | 1.2222 | 119.6228 | 1.2955 | 119.696 | 23.9502 | 122.4152 | 3.8498 | 122.3785 | 122.5021 | 122.3282 | 122.2778 | 122.2549 | -122.5525 | -122.4014 | 122.1909 | 122.3053 | 67.4286 | 73.3932
2556.8281 | 122.5021 | -65.4327 | 56.9046 | -0.19371 | 0.00084388 | 0.07527 | 0.20605 | 0.0016663 | 0.059451 | 0.0016022 | -0.097961 | -0.0041186 | 0.067383 | 0.17192 | -0.029995 | 0.097117 | 0.0043793 | -2.6917 | 56.8405 | -65.6158 | 56.9458 | -44.0643 | -55.2567 | 4.6509 | 4.4037 | 56.8771 | -65.4648 | 56.8726 | -61.8942 | 54.1534 | -64.2654 | -0.18311 | -0.064087 | 0.041199 | 21.3684 | 70.0836 | 10.1761 | 70.2667 | 10.3592 | -0.032044 | -0.027466 | -0.032043 | 3.5385 | 1.1673 | 119.5862 | 1.1993 | 119.6182 | 21.5515 | 122.5616 | 3.5706 | 122.3373 | 122.4564 | 122.3419 | 122.2733 | 122.3099 | -122.5204 | -122.3694 | 122.3785 | 122.3053 | 62.7411 | 69.8364
2557.7656 | 122.4838 | -62.2742 | 60.141 | -0.13267 | 0.0029801 | 0.071211 | 0.22805 | 0.0016663 | 0.085941 | -0.0016022 | -0.0064086 | -0.0024096 | 0.063324 | 0.16872 | -0.02914 | 0.097117 | 0.0077973 | -2.2293 | 60.0769 | -62.3611 | 59.9487 | -43.5562 | -48.5413 | 5.7541 | 5.4245 | 60.0632 | -62.2696 | 60.0128 | -58.8547 | 57.3486 | -61.1435 | -0.086975 | -0.064087 | -0.19226 | 18.718 | 68.0283 | 13.7329 | 68.1152 | 13.8199 | 0.004578 | -0.07782 | -0.12817 | 3.4195 | 1.1307 | 119.6228 | 1.1261 | 119.6182 | 18.8049 | 122.3099 | 3.4149 | 122.2824 | 122.438 | 122.3328 | 122.3511 | 122.3373 | -122.5021 | -122.4106 | 122.2229 | 122.287 | 60.0449 | 67.6987
2558.7656 | 122.4747 | -61.496 | 60.9009 | -0.19371 | 0.00020288 | 0.073347 | 0.25775 | -0.00068368 | 0.11628 | -0.0058746 | -0.058289 | -0.0015552 | 0.066742 | 0.16551 | -0.029354 | 0.095408 | 0.0028839 | -2.0828 | 60.8597 | -61.6333 | 60.6766 | -41.9861 | -42.9382 | 6.4819 | 5.3284 | 60.8597 | -61.528 | 60.7636 | -58.1406 | 58.0994 | -60.379 | -0.13733 | -0.041199 | -0.2243 | 19.5099 | 67.9779 | 18.5577 | 68.1152 | 18.6951 | -0.032043 | -0.041199 | -0.13733 | 3.3554 | 1.1169 | 119.5953 | 1.149 | 119.6274 | 19.6472 | 122.3099 | 3.3875 | 122.2916 | 122.493 | 122.3877 | 122.3557 | 122.3557 | -122.5342 | -122.4289 | 122.1725 | 122.2595 | 59.4131 | 66.8243
2559.7656 | 121.9208 | -9.3704 | 113.1226 | -0.07164 | 0.0021255 | 0.060103 | 0.13021 | 0.00017092 | 0.016299 | -0.0043792 | -0.10101 | -0.0036914 | 0.061829 | 0.16872 | -0.030209 | 0.09669 | 0.0048065 | 2.3621 | 113.0951 | -9.4666 | 112.825 | -6.8069 | -6.5186 | 15.7379 | 20.9061 | 113.0402 | -9.4345 | 112.9715 | -8.0658 | 110.2066 | -8.5052 | -0.096131 | -0.027466 | -0.29755 | 2.5635 | 25.1083 | 2.8519 | 25.2045 | 2.948 | -0.064087 | -0.082398 | -0.15106 | 1.3046 | 0.86517 | 119.577 | 0.92926 | 119.6411 | 2.6596 | 122.2916 | 1.3687 | 122.406 | 122.5616 | 122.4747 | 122.4655 | 122.4106 | -122.5891 | -122.5571 | 122.1954 | 122.3419 | 11.7325 | 30.2765
2560.8281 | 122.4518 | -9.5947 | 112.8891 | -0.094528 | 0.0019119 | 0.061598 | 0.1268 | 0.0029479 | 0.015659 | -0.0043792 | -0.10712 | -0.00070063 | 0.062256 | 0.17491 | -0.031063 | 0.097972 | 0.0056611 | 2.2888 | 112.8387 | -9.6863 | 112.619 | -7.7316 | -6.6742 | 15.4404 | 21.4554 | 112.8296 | -9.6634 | 112.7472 | -8.2855 | 109.9503 | -8.7341 | -0.091552 | -0.050354 | -0.27008 | 1.8631 | 25.0351 | 2.9205 | 25.1266 | 3.0121 | -0.068664 | -0.059509 | -0.14191 | 1.3092 | 0.8606 | 119.545 | 0.92926 | 119.6136 | 1.9547 | 122.3053 | 1.3779 | 122.4106 | 122.525 | 122.493 | 122.4335 | 122.4243 | -122.5754 | -122.5525 | 122.2137 | 122.3419 | 11.8835 | 31.0501
2561.7656 | 122.4838 | -9.6039 | 112.8387 | -0.10216 | 0.0012711 | 0.062025 | 0.12829 | 0.00081172 | 0.017368 | -0.0035248 | -0.085754 | -0.0017688 | 0.06546 | 0.17256 | -0.02914 | 0.099254 | 0.0054475 | 2.33 | 112.8204 | -9.7504 | 112.5549 | -8.2672 | -6.6696 | 15.3488 | 21.579 | 112.7563 | -9.7137 | 112.6968 | -8.2947 | 109.9319 | -8.7753 | -0.14648 | -0.01831 | -0.28381 | 1.3367 | 24.9527 | 2.9343 | 25.0992 | 3.0807 | -0.10986 | -0.082397 | -0.14191 | 1.3092 | 0.82855 | 119.5358 | 0.93841 | 119.6457 | 1.4832 | 122.3053 | 1.4191 | 122.4106 | 122.5708 | 122.4701 | 122.4243 | 122.3602 | -122.5891 | -122.5525 | 122.1588 | 122.3007 | 11.9339 | 31.1829
2562.7656 | 122.4518 | -9.6542 | 112.8799 | -0.11742 | 0.0023391 | 0.062453 | 0.12573 | 0.00038452 | 0.017154 | -0.0058746 | -0.027771 | -0.0024096 | 0.06482 | 0.17107 | -0.028927 | 0.097117 | 0.0069427 | 2.179 | 112.7655 | -9.7687 | 112.5229 | -8.194 | -6.6925 | 15.4312 | 21.4142 | 112.7335 | -9.7504 | 112.619 | -8.3633 | 109.8679 | -8.8303 | -0.11444 | -0.11444 | -0.35706 | 1.4603 | 25.0854 | 2.9617 | 25.1999 | 3.0762 | -0.09613 | -0.14648 | -0.26093 | 1.2909 | 0.82397 | 119.5221 | 0.9201 | 119.6182 | 1.5747 | 122.2916 | 1.387 | 122.3694 | 122.5342 | 122.4838 | 122.4197 | 122.3877 | -122.6486 | -122.6303 | 122.1771 | 122.2733 | 11.8332 | 31.0684
2563.8281 | 122.4518 | -9.5947 | 112.8891 | -0.10216 | 0.0027665 | 0.062453 | 0.12359 | 0.0012391 | 0.016299 | -0.0033112 | -0.027771 | -0.0026232 | 0.066742 | 0.1732 | -0.029781 | 0.09669 | 0.0050201 | 2.0279 | 112.8479 | -9.6817 | 112.587 | -7.5623 | -6.6605 | 15.5319 | 21.2723 | 112.8021 | -9.6771 | 112.6923 | -8.2901 | 109.9457 | -8.7708 | -0.086975 | -0.041199 | -0.30212 | 2.0325 | 25.1266 | 2.9343 | 25.2136 | 3.0212 | -0.082397 | -0.086975 | -0.19684 | 1.3046 | 0.82398 | 119.5404 | 0.90637 | 119.6228 | 2.1194 | 122.2687 | 1.387 | 122.3694 | 122.5296 | 122.4792 | 122.4426 | 122.3969 | -122.5708 | -122.5662 | 122.1817 | 122.287 | 11.6226 | 30.867
2564.7656 | 122.493 | -9.8145 | 112.6419 | -0.033493 | 0.0010575 | 0.062239 | 0.12722 | 0.00081172 | 0.012027 | -0.0030976 | -0.079651 | -0.0024096 | 0.064606 | 0.17406 | -0.030422 | 0.098399 | 0.0060883 | 2.1423 | 112.6144 | -9.9564 | 112.3535 | -7.7087 | -6.9855 | 15.3992 | 20.787 | 112.5504 | -9.9152 | 112.4908 | -8.5098 | 109.7122 | -8.9722 | -0.14191 | -0.027466 | -0.28839 | 2.1057 | 25.2136 | 2.829 | 25.3555 | 2.9709 | -0.10071 | -0.091553 | -0.15106 | 1.3046 | 0.84229 | 119.5267 | 0.94299 | 119.6274 | 2.2476 | 122.3099 | 1.4053 | 122.406 | 122.5708 | 122.4655 | 122.4289 | 122.3648 | -122.5983 | -122.5571 | 122.168 | 122.3053 | 11.9568 | 30.6015
2565.8281 | 122.5891 | -10.0525 | 112.3352 | -0.16319 | 0.0010575 | 0.061598 | 0.12359 | 0.00038452 | 0.015018 | -0.0033112 | 0.024109 | -0.0041186 | 0.062683 | 0.16273 | -0.029995 | 0.095836 | 0.0045929 | 2.211 | 112.2803 | -10.231 | 112.1567 | -8.0383 | -7.1594 | 15.3305 | 20.961 | 112.2253 | -10.1761 | 112.2574 | -8.6746 | 109.5337 | -9.1461 | -0.17853 | -0.054932 | -0.17853 | 2.0142 | 25.383 | 2.8931 | 25.5615 | 3.0716 | -0.1236 | -0.10986 | -0.07782 | 1.3779 | 0.90637 | 119.5862 | 1.03 | 119.7098 | 2.1927 | 122.3877 | 1.5015 | 122.4335 | 122.5113 | 122.4014 | 122.3328 | 122.2778 | -122.5662 | -122.5113 | 122.2092 | 122.3099 | 12.2635 | 31.0135
2566.7656 | 122.4838 | -10.1532 | 112.3398 | -0.094528 | 0.0019119 | 0.059462 | 0.12701 | -0.0036743 | 0.015872 | -0.0052338 | 0.042419 | -0.00048703 | 0.065247 | 0.17341 | -0.028927 | 0.094981 | 0.0077973 | 1.9958 | 112.2986 | -10.2493 | 111.9781 | -8.6517 | -7.2922 | 15.2206 | 20.8511 | 112.2574 | -10.1898 | 112.1567 | -8.8348 | 109.4055 | -9.3063 | -0.096131 | -0.041199 | -0.36163 | 1.5015 | 25.3738 | 2.861 | 25.47 | 2.9572 | -0.036621 | -0.082398 | -0.18311 | 1.3184 | 0.84686 | 119.5587 | 0.88348 | 119.5953 | 1.5976 | 122.2275 | 1.355 | 122.3465 | 122.5479 | 122.4472 | 122.4518 | 122.4106 | -122.5891 | -122.5296 | 122.1313 | 122.3099 | 12.149 | 31.0043
2567.7656 | 122.58 | -29.2419 | 93.1641 | -0.086899 | -0.00065152 | 0.071211 | 0.12573 | 0.0010253 | -0.0012176 | -0.00096136 | -0.049133 | -0.0028368 | 0.06482 | 0.16978 | -0.030422 | 0.095195 | 0.0097199 | 0.8194 | 93.1 | -29.425 | 92.8711 | -22.8333 | -29.3884 | 10.6339 | 15.1291 | 93.0496 | -29.3655 | 92.9581 | -27.3239 | 90.239 | -28.5004 | -0.18311 | -0.064086 | -0.29297 | 6.4087 | 39.8758 | -0.14649 | 40.0589 | 0.036621 | -0.1236 | -0.11444 | -0.20599 | 1.918 | 0.74158 | 119.4809 | 0.86517 | 119.6045 | 6.5918 | 122.2961 | 2.0416 | 122.3236 | 122.525 | 122.4152 | 122.3419 | 122.2916 | -122.5891 | -122.5296 | 122.113 | 122.2 | 30.0613 | 44.371
2568.8281 | 122.5708 | -29.0359 | 93.3289 | -0.10216 | 0.0012711 | 0.072707 | 0.12616 | 0.0018799 | 0.0013458 | -0.0026704 | -0.12238 | -0.0060412 | 0.065674 | 0.17128 | -0.030636 | 0.098826 | 0.0056611 | 0.87433 | 93.3014 | -29.2053 | 93.132 | -22.5952 | -29.1595 | 10.7117 | 15.3992 | 93.251 | -29.1275 | 93.251 | -27.1042 | 90.4541 | -28.244 | -0.16937 | -0.027465 | -0.19684 | 6.4407 | 39.7476 | -0.1236 | 39.917 | 0.045776 | -0.091552 | -0.077819 | -0.077819 | 1.9318 | 0.79193 | 119.4901 | 0.88348 | 119.5816 | 6.6101 | 122.3373 | 2.0233 | 122.3785 | 122.5067 | 122.3785 | 122.3373 | 122.287 | -122.5342 | -122.4564 | 122.168 | 122.287 | 29.9103 | 44.4351
2569.7656 | 122.4884 | -10.144 | 112.3535 | -0.094528 | 0.00063028 | 0.062453 | 0.1253 | 0.0018799 | 0.016299 | -0.0043792 | -0.067444 | -0.0024096 | 0.064179 | 0.16551 | -0.0285 | 0.095622 | 0.0037385 | 1.8082 | 112.3398 | -10.2448 | 112.0239 | -8.5052 | -7.2281 | 15.3214 | 21.4005 | 112.2757 | -10.2036 | 112.175 | -8.7799 | 109.4055 | -9.2743 | -0.10071 | -0.013733 | -0.32959 | 1.6388 | 25.4654 | 2.916 | 25.5661 | 3.0167 | -0.059509 | -0.07782 | -0.17853 | 1.3641 | 0.86975 | 119.5496 | 0.92926 | 119.6091 | 1.7395 | 122.2687 | 1.4236 | 122.3785 | 122.5845 | 122.4792 | 122.4838 | 122.4197 | -122.5983 | -122.5571 | 122.168 | 122.319 | 11.9522 | 31.5445
2570.7656 | 122.612 | -10.144 | 112.2528 | -0.06401 | 0.00041648 | 0.061812 | 0.12551 | 0.00059812 | 0.015231 | -0.003952 | 0.16754 | -0.002196 | 0.065033 | 0.16316 | -0.030209 | 0.094768 | 0.0067291 | 1.8127 | 112.2208 | -10.2631 | 112.0972 | -8.3542 | -7.1548 | 15.4221 | 21.2128 | 112.1384 | -10.2631 | 112.2391 | -8.6792 | 109.4559 | -9.1919 | -0.11902 | -0.032044 | -0.15564 | 1.7899 | 25.5661 | 2.9892 | 25.6851 | 3.1082 | -0.11902 | -0.11444 | -0.013733 | 1.4648 | 0.95215 | 119.5999 | 1.0712 | 119.7189 | 1.9089 | 122.3602 | 1.5839 | 122.5021 | 122.4838 | 122.4014 | 122.3648 | 122.2824 | -122.5159 | -122.5159 | 122.2412 | 122.3831 | 11.9568 | 31.3568
2571.7656 | 122.4976 | -10.2173 | 112.2391 | -0.06401 | 0.0016983 | 0.06053 | 0.12637 | -0.0038879 | 0.016299 | -0.0013886 | -0.09491 | -0.002196 | 0.063538 | 0.17235 | -0.030849 | 0.098185 | 0.0022431 | 1.9913 | 112.2437 | -10.3546 | 111.9324 | -8.6517 | -7.3288 | 15.184 | 21.3409 | 112.2025 | -10.3226 | 112.0651 | -8.8577 | 109.3048 | -9.3613 | -0.13733 | 0.004577 | -0.3067 | 1.5656 | 25.4013 | 2.8885 | 25.5386 | 3.0258 | -0.10529 | -0.036621 | -0.17395 | 1.3596 | 0.85602 | 119.5221 | 0.9613 | 119.6274 | 1.7029 | 122.287 | 1.4648 | 122.3877 | 122.5983 | 122.525 | 122.4609 | 122.4197 | -122.5937 | -122.5616 | 122.1497 | 122.2824 | 12.2086 | 31.5582
2572.8281 | 122.5571 | -10.405 | 112.0239 | -0.14793 | 0.0012711 | 0.059462 | 0.12637 | 0.0029479 | 0.016086 | -0.0037384 | -0.033874 | -0.0036914 | 0.064392 | 0.16743 | -0.031063 | 0.097758 | 0.0024567 | 1.9913 | 111.9965 | -10.5194 | 111.8225 | -9.4025 | -7.3746 | 15.2206 | 21.5927 | 111.9781 | -10.4736 | 111.9186 | -8.9584 | 109.1675 | -9.4711 | -0.11444 | -0.027466 | -0.20142 | 1.0025 | 25.6256 | 3.0304 | 25.7401 | 3.1448 | -0.068665 | -0.045777 | -0.10529 | 1.4465 | 0.93384 | 119.5724 | 1.0025 | 119.6411 | 1.1169 | 122.3419 | 1.5152 | 122.3923 | 122.5159 | 122.4518 | 122.4014 | 122.3831 | -122.5433 | -122.4976 | 122.2275 | 122.3236 | 12.3962 | 31.9977
2573.7656 | 122.6074 | -10.3592 | 112.0239 | -0.094528 | 0.0012711 | 0.060103 | 0.12487 | -0.00068368 | 0.016513 | -0.0033112 | -0.015564 | -0.003905 | 0.062683 | 0.16872 | -0.029995 | 0.097331 | 0.0077973 | 1.9455 | 112.0102 | -10.4919 | 111.8362 | -9.407 | -7.37 | 15.2252 | 21.5927 | 111.9781 | -10.4599 | 111.9827 | -8.9127 | 109.2545 | -9.4162 | -0.13275 | -0.013733 | -0.18768 | 0.95215 | 25.5844 | 2.9892 | 25.7172 | 3.1219 | -0.10071 | -0.045777 | -0.041199 | 1.4465 | 0.94299 | 119.6136 | 1.0437 | 119.7144 | 1.0849 | 122.3282 | 1.5472 | 122.4426 | 122.5021 | 122.438 | 122.3694 | 122.3373 | -122.5159 | -122.4838 | 122.1954 | 122.3419 | 12.3047 | 31.9519
2574.7656 | 122.5937 | -10.2173 | 112.1521 | -0.17845 | -0.00065152 | 0.061385 | 0.12338 | 0.0023071 | 0.016727 | -0.00074776 | -0.036926 | -0.0030506 | 0.062683 | 0.17107 | -0.027431 | 0.096049 | 0.0052337 | 1.9226 | 112.1841 | -10.3271 | 111.9736 | -9.1324 | -7.2235 | 15.2161 | 21.6431 | 112.1338 | -10.3043 | 112.1155 | -8.7616 | 109.3689 | -9.2743 | -0.10986 | 0.032043 | -0.17853 | 1.0849 | 25.4333 | 2.9938 | 25.5432 | 3.1036 | -0.086975 | -0.018311 | -0.036621 | 1.4557 | 0.94299 | 119.5862 | 1.03 | 119.6732 | 1.1948 | 122.3007 | 1.5427 | 122.4197 | 122.5113 | 122.438 | 122.4014 | 122.3511 | -122.4792 | -122.4564 | 122.1909 | 122.3328 | 12.1399 | 31.8604
2575.7656 | 122.5937 | -10.4462 | 111.9415 | -0.079269 | 0.00063028 | 0.060103 | 0.12445 | 0.0023071 | 0.016299 | -0.0050202 | -0.027771 | -0.0032642 | 0.062256 | 0.17491 | -0.030849 | 0.096263 | 0.0073701 | 1.9226 | 111.8866 | -10.6064 | 111.7767 | -8.9584 | -7.5119 | 15.2298 | 21.6568 | 111.9049 | -10.5148 | 111.9278 | -8.963 | 109.1537 | -9.4711 | -0.16022 | -0.054931 | -0.1648 | 1.4877 | 25.676 | 2.9343 | 25.8362 | 3.0945 | -0.068665 | -0.036621 | -0.013733 | 1.4832 | 0.97504 | 119.5999 | 1.0437 | 119.6686 | 1.6479 | 122.3831 | 1.5518 | 122.4426 | 122.493 | 122.4197 | 122.3328 | 122.3511 | -122.5479 | -122.4564 | 122.2229 | 122.374 | 12.3688 | 32.103
2576.7656 | 122.5891 | -10.5698 | 111.7996 | -0.079269 | 0.0016983 | 0.060744 | 0.12616 | 0.0016663 | 0.014377 | -0.0013886 | -0.021667 | -0.0041186 | 0.063538 | 0.17619 | -0.03149 | 0.096904 | 0.0063019 | 1.9363 | 111.7996 | -10.7208 | 111.6211 | -9.7092 | -7.608 | 15.2115 | 21.9772 | 111.763 | -10.643 | 111.7722 | -9.0958 | 109.0118 | -9.6222 | -0.15106 | 0 | -0.17853 | 0.8606 | 25.7812 | 2.9617 | 25.9323 | 3.1128 | -0.073242 | -0.036622 | -0.027466 | 1.474 | 0.94757 | 119.5816 | 1.0208 | 119.6548 | 1.0117 | 122.3419 | 1.5472 | 122.4152 | 122.5204 | 122.406 | 122.3694 | 122.3328 | -122.5204 | -122.4426 | 122.1909 | 122.3419 | 12.5061 | 32.547
2577.7656 | 122.6028 | -10.6064 | 111.7859 | -0.12505 | 0.0019119 | 0.060103 | 0.12423 | -0.00089728 | 0.015659 | -0.0030976 | -0.039978 | -0.0036914 | 0.062256 | 0.17854 | -0.032772 | 0.095836 | 0.0043793 | 1.9089 | 111.763 | -10.7346 | 111.6257 | -9.6863 | -7.5806 | 15.1062 | 22.0642 | 111.6943 | -10.675 | 111.7355 | -9.1141 | 108.9798 | -9.6588 | -0.12817 | -0.022889 | -0.16022 | 0.9201 | 25.7126 | 3.0258 | 25.8408 | 3.154 | -0.068665 | -0.091553 | -0.050354 | 1.4923 | 0.94757 | 119.5862 | 1.0162 | 119.6548 | 1.0483 | 122.3602 | 1.561 | 122.4106 | 122.4976 | 122.3694 | 122.3694 | 122.3007 | -122.5204 | -122.4609 | 122.2321 | 122.3419 | 12.5153 | 32.6706
2578.7656 | 122.5891 | -10.6522 | 111.7538 | -0.11742 | 0.0025529 | 0.062025 | 0.12423 | -0.00025628 | 0.017154 | -0.0058746 | -0.064392 | -0.003905 | 0.063111 | 0.16807 | -0.028927 | 0.097545 | -0.0013885 | 1.9226 | 111.7722 | -10.7437 | 111.5341 | -9.7046 | -7.7133 | 15.2115 | 21.9269 | 111.676 | -10.7483 | 111.6852 | -9.169 | 108.8882 | -9.7046 | -0.091552 | 0.018311 | -0.21973 | 0.94757 | 25.8636 | 2.9388 | 25.9552 | 3.0304 | -0.09613 | -0.07782 | -0.068664 | 1.4832 | 0.94757 | 119.5404 | 1.0437 | 119.6365 | 1.0391 | 122.2778 | 1.5793 | 122.4335 | 122.5159 | 122.4243 | 122.4243 | 122.3282 | -122.4976 | -122.5021 | 122.1863 | 122.3373 | 12.5748 | 32.579
2579.7656 | 122.4884 | -10.6842 | 111.7218 | -0.1403 | 0.0012711 | 0.06053 | 0.12295 | -0.0047425 | 0.012027 | -0.002884 | -0.085754 | -0.0047594 | 0.065033 | 0.17256 | -0.030209 | 0.095408 | 0.0035247 | 1.9135 | 111.7264 | -10.7986 | 111.4792 | -9.7366 | -7.7179 | 15.2756 | 22.0688 | 111.7035 | -10.7666 | 111.5936 | -9.2743 | 108.8242 | -9.8053 | -0.11444 | 0.004577 | -0.24262 | 0.94757 | 25.9598 | 2.9663 | 26.0742 | 3.0807 | -0.082398 | -0.018311 | -0.12817 | 1.4099 | 0.87891 | 119.5084 | 0.9613 | 119.5908 | 1.062 | 122.2778 | 1.4923 | 122.3602 | 122.525 | 122.4701 | 122.4106 | 122.3877 | -122.5204 | -122.4884 | 122.1634 | 122.2778 | 12.5977 | 32.753
2580.7656 | 122.6028 | -10.6476 | 111.7126 | -0.12505 | 0.0012711 | 0.063521 | 0.12338 | -0.00089728 | 0.015659 | -0.0020294 | -0.10406 | -0.0034778 | 0.060974 | 0.17641 | -0.028713 | 0.09669 | -0.0013885 | 1.8448 | 111.676 | -10.7895 | 111.5341 | -9.6359 | -7.663 | 15.2847 | 22.2107 | 111.6302 | -10.7666 | 111.731 | -9.1461 | 108.9111 | -9.668 | -0.14191 | -0.036621 | -0.17853 | 1.0117 | 25.9323 | 2.9846 | 26.0742 | 3.1265 | -0.11902 | -0.082397 | 0.018311 | 1.5015 | 0.97961 | 119.5587 | 1.0986 | 119.6777 | 1.1536 | 122.3236 | 1.6205 | 122.4976 | 122.4655 | 122.3969 | 122.3236 | 122.2778 | -122.5021 | -122.4792 | 122.1817 | 122.3785 | 12.4924 | 32.8583
2581.7656 | 122.6486 | -10.6842 | 111.6852 | -0.12505 | 0.0021255 | 0.060103 | 0.12445 | -0.00025628 | 0.015659 | -0.0037384 | -0.046081 | -0.0032642 | 0.065247 | 0.16978 | -0.029781 | 0.096049 | 0.0090789 | 1.8951 | 111.7126 | -10.7941 | 111.5616 | -9.6588 | -7.6401 | 15.3946 | 22.2839 | 111.6714 | -10.7391 | 111.7218 | -9.1141 | 108.9615 | -9.6359 | -0.10986 | 0.027465 | -0.1236 | 1.0254 | 26.0788 | 3.0441 | 26.1887 | 3.154 | -0.054932 | -0.013733 | 0.036621 | 1.5701 | 1.0483 | 119.6457 | 1.1032 | 119.7006 | 1.1353 | 122.3557 | 1.6251 | 122.4609 | 122.5067 | 122.4106 | 122.3969 | 122.3557 | -122.4792 | -122.4243 | 122.2458 | 122.406 | 12.5793 | 32.9681
2582.8281 | 122.5845 | -10.7574 | 111.644 | -0.10216 | 0.0023391 | 0.060744 | 0.12402 | 0.0014527 | 0.014377 | -0.0041656 | -0.039978 | -0.0017688 | 0.062256 | 0.17448 | -0.030209 | 0.096477 | 0.0058747 | 1.8127 | 111.6348 | -10.8765 | 111.4609 | -9.9564 | -7.7454 | 15.2161 | 22.2107 | 111.5936 | -10.8398 | 111.6165 | -9.2148 | 108.847 | -9.7504 | -0.11902 | -0.009155 | -0.18311 | 0.80109 | 25.9735 | 3.0121 | 26.0925 | 3.1311 | -0.082398 | -0.050354 | -0.027466 | 1.5427 | 1.0071 | 119.6045 | 1.0895 | 119.6869 | 0.9201 | 122.3373 | 1.6251 | 122.4564 | 122.5113 | 122.4335 | 122.3923 | 122.3511 | -122.5204 | -122.4838 | 122.2183 | 122.374 | 12.5702 | 32.9681
2583.7656 | 122.5983 | -10.7529 | 111.6211 | -0.15556 | 0.0012711 | 0.063734 | 0.12402 | 0.0040161 | 0.016727 | -0.0026704 | -0.11932 | -0.0034778 | 0.062897 | 0.17235 | -0.030209 | 0.096904 | 0.0048065 | 1.7166 | 111.5524 | -10.8856 | 111.4929 | -9.906 | -7.7454 | 15.1382 | 22.1466 | 111.5753 | -10.8215 | 111.6486 | -9.2239 | 108.847 | -9.7366 | -0.13275 | -0.068665 | -0.12817 | 0.84686 | 25.8911 | 3.0075 | 26.0239 | 3.1403 | -0.068664 | -0.045777 | 0.027466 | 1.5289 | 1.0162 | 119.5999 | 1.0849 | 119.6686 | 0.97961 | 122.3785 | 1.5976 | 122.4701 | 122.438 | 122.3969 | 122.3053 | 122.3282 | -122.5067 | -122.4426 | 122.2458 | 122.4014 | 12.4695 | 32.8995
2584.7656 | 122.5845 | -10.7712 | 111.5936 | -0.15556 | 0.0044755 | 0.062666 | 0.12338 | 0.00081172 | 0.017368 | 0.00010684 | -0.10101 | -0.0041186 | 0.060547 | 0.16978 | -0.029995 | 0.095622 | 0.0069427 | 1.9638 | 111.5936 | -10.8902 | 111.4471 | -9.9518 | -7.7499 | 15.2435 | 22.2977 | 111.5845 | -10.8627 | 111.6119 | -9.2331 | 108.7784 | -9.7687 | -0.11902 | 0 | -0.14648 | 0.8194 | 26.0147 | 3.0212 | 26.1337 | 3.1403 | -0.091553 | -0.009155 | 0.01831 | 1.5381 | 1.0025 | 119.5496 | 1.0941 | 119.6411 | 0.93842 | 122.3373 | 1.6296 | 122.4747 | 122.4838 | 122.4472 | 122.3648 | 122.3557 | -122.4838 | -122.4564 | 122.2183 | 122.3831 | 12.735 | 33.0688
2585.7656 | 122.5616 | -10.7162 | 111.676 | -0.11742 | 0.0031937 | 0.063307 | 0.12295 | 0.0012391 | 0.014377 | -0.003952 | -0.079651 | -0.0013416 | 0.061829 | 0.17256 | -0.028927 | 0.096263 | 0.0020295 | 1.9958 | 111.6806 | -10.8215 | 111.4929 | -9.9014 | -7.7271 | 15.2847 | 22.3114 | 111.6531 | -10.7941 | 111.6486 | -9.1965 | 108.8379 | -9.7046 | -0.10529 | 0.004578 | -0.1831 | 0.81482 | 26.001 | 2.9892 | 26.1063 | 3.0945 | -0.077819 | -0.022888 | -0.027465 | 1.5198 | 1.0117 | 119.5541 | 1.0895 | 119.632 | 0.92011 | 122.3145 | 1.5976 | 122.4426 | 122.5021 | 122.4472 | 122.3969 | 122.3694 | -122.4976 | -122.4701 | 122.2092 | 122.3648 | 12.7121 | 33.0276
2586.8438 | 122.5388 | -10.6293 | 111.7905 | -0.07164 | 0.00041648 | 0.062025 | 0.12423 | 0.0010253 | 0.015231 | -0.004593 | -0.070496 | -0.0026232 | 0.061829 | 0.17598 | -0.027859 | 0.097331 | 0.0050201 | 2.0599 | 111.7905 | -10.7254 | 111.6074 | -9.7458 | -7.5806 | 15.2802 | 22.4075 | 111.7264 | -10.7025 | 111.7493 | -9.0866 | 108.9478 | -9.6222 | -0.096131 | 0 | -0.1831 | 0.88348 | 25.9094 | 3.0487 | 26.0056 | 3.1448 | -0.073243 | -0.064087 | -0.041198 | 1.5427 | 1.0071 | 119.577 | 1.0803 | 119.6503 | 0.97961 | 122.3328 | 1.6159 | 122.4518 | 122.5159 | 122.4289 | 122.4197 | 122.3557 | -122.5159 | -122.493 | 122.2366 | 122.3785 | 12.6892 | 33.0368
2587.7656 | 122.5937 | -10.6567 | 111.7355 | -0.17082 | 0.0016983 | 0.06053 | 0.12466 | 0.00038452 | 0.016299 | 0.0013886 | -0.091858 | -0.0032642 | 0.060761 | 0.16914 | -0.029995 | 0.096477 | 0.0056611 | 2.179 | 111.7218 | -10.7986 | 111.5753 | -9.7733 | -7.6447 | 15.1657 | 22.6227 | 111.6531 | -10.73 | 111.7447 | -9.1003 | 108.934 | -9.613 | -0.14191 | -0.013733 | -0.16022 | 0.88348 | 25.8224 | 3.0121 | 25.9644 | 3.154 | -0.073242 | -0.082398 | 0.009155 | 1.5564 | 1.0437 | 119.5908 | 1.1169 | 119.664 | 1.0254 | 122.374 | 1.6296 | 122.4747 | 122.5204 | 122.3831 | 122.3785 | 122.3099 | -122.5342 | -122.4655 | 122.2321 | 122.4014 | 12.8357 | 33.2794
2588.7656 | 122.5616 | -10.6247 | 111.731 | -0.10216 | 0.0012711 | 0.061385 | 0.12381 | 0.00081172 | 0.015445 | -0.0048066 | -0.11017 | -0.0034778 | 0.060974 | 0.17149 | -0.028927 | 0.096477 | 0.0028839 | 2.0508 | 111.7401 | -10.762 | 111.5707 | -9.7229 | -7.6263 | 15.2435 | 22.6639 | 111.6714 | -10.7117 | 111.7355 | -9.0958 | 108.9111 | -9.6268 | -0.13733 | 0.009155 | -0.16022 | 0.90179 | 25.8682 | 2.9984 | 26.0056 | 3.1357 | -0.086975 | -0.059509 | 0.004578 | 1.5289 | 0.99792 | 119.5358 | 1.0849 | 119.6228 | 1.0391 | 122.3328 | 1.6159 | 122.4472 | 122.5021 | 122.3831 | 122.3648 | 122.2961 | -122.493 | -122.4426 | 122.1954 | 122.3602 | 12.6755 | 33.2886
2589.7656 | 122.5754 | -10.6155 | 111.7355 | -0.17845 | 0.0021255 | 0.064589 | 0.12252 | -4.2682e-05 | 0.017154 | -0.0037384 | -0.10712 | -0.0024096 | 0.059052 | 0.1732 | -0.030422 | 0.096263 | 0.0045929 | 2.1469 | 111.7447 | -10.7346 | 111.5753 | -9.6863 | -7.6035 | 15.303 | 22.5677 | 111.7035 | -10.6842 | 111.7401 | -9.0591 | 108.9432 | -9.5993 | -0.11902 | 0.009155 | -0.16022 | 0.92926 | 25.9186 | 3.0121 | 26.0376 | 3.1311 | -0.068664 | -0.032044 | 0.004577 | 1.5564 | 1.0162 | 119.5587 | 1.0849 | 119.6274 | 1.0483 | 122.3099 | 1.6251 | 122.4243 | 122.4792 | 122.3877 | 122.3602 | 122.319 | -122.4701 | -122.4197 | 122.1909 | 122.3557 | 12.7625 | 33.1833
2590.7656 | 122.4518 | -10.6339 | 111.7905 | -0.094528 | -0.0015061 | 0.058394 | 0.12231 | -4.2682e-05 | 0.012881 | -0.003952 | -0.085754 | -0.0028368 | 0.059479 | 0.17256 | -0.030209 | 0.094554 | 0.0033111 | 2.0966 | 111.7859 | -10.7803 | 111.5112 | -9.819 | -7.6584 | 15.3854 | 22.6501 | 111.7447 | -10.7437 | 111.795 | -9.0271 | 108.6777 | -9.819 | -0.14648 | -0.004577 | -0.27924 | 0.81482 | 26.0193 | 2.9755 | 26.1658 | 3.1219 | -0.10986 | -0.045776 | 0.004578 | 1.6067 | 0.81482 | 119.3115 | 0.92468 | 119.4214 | 0.9613 | 122.2916 | 1.7166 | 122.5388 | 122.5662 | 122.4884 | 122.4197 | 122.3785 | -122.5708 | -122.5342 | 122.1451 | 122.4289 | 12.7304 | 33.284
2591.7656 | 122.5708 | -10.6064 | 111.7676 | -0.10216 | 0.0010575 | 0.060103 | 0.12295 | 0.00081172 | 0.016513 | -0.0030976 | -0.067444 | -0.0043322 | 0.062897 | 0.17576 | -0.031063 | 0.09669 | 0.0060883 | 2.1469 | 111.7767 | -10.73 | 111.4471 | -9.7595 | -7.5806 | 15.2206 | 22.6776 | 111.676 | -10.73 | 111.7218 | -9.0546 | 108.9294 | -9.5993 | -0.1236 | 0.009155 | -0.32043 | 0.84686 | 25.827 | 3.0258 | 25.9506 | 3.1494 | -0.1236 | -0.091553 | -0.045776 | 1.5518 | 1.0071 | 119.5358 | 1.1307 | 119.6594 | 0.97046 | 122.1771 | 1.6754 | 122.4518 | 122.5067 | 122.406 | 122.3831 | 122.2824 | -122.4976 | -122.4976 | 122.0535 | 122.3282 | 12.7533 | 33.284
2592.8281 | 122.6257 | -10.5881 | 111.7676 | -0.086899 | 0.00020288 | 0.06288 | 0.1221 | -0.0017517 | 0.015872 | -0.002243 | -0.064392 | -0.0034778 | 0.062042 | 0.1732 | -0.030849 | 0.096049 | 0.0084381 | 2.2842 | 111.7859 | -10.7437 | 111.6028 | -9.6313 | -7.5302 | 15.477 | 22.8104 | 111.7126 | -10.7117 | 111.7676 | -9.0088 | 108.9844 | -9.5398 | -0.15564 | 0.018311 | -0.16479 | 0.95673 | 26.0651 | 3.0579 | 26.2207 | 3.2135 | -0.1236 | -0.054932 | 0 | 1.5793 | 1.0483 | 119.5724 | 1.1719 | 119.696 | 1.1124 | 122.3465 | 1.7029 | 122.4792 | 122.5296 | 122.4243 | 122.374 | 122.3007 | -122.5113 | -122.4792 | 122.1909 | 122.3557 | 12.8723 | 33.3984
2593.7656 | 122.5891 | -10.675 | 111.7035 | -0.17845 | 0.00063028 | 0.064162 | 0.12188 | 0.0057251 | 0.018222 | -0.0018158 | -0.12848 | -0.0032642 | 0.061829 | 0.1747 | -0.027859 | 0.097758 | 0.0048065 | 2.3071 | 111.6943 | -10.7849 | 111.557 | -9.6634 | -7.6263 | 15.4175 | 22.9752 | 111.6211 | -10.7483 | 111.7172 | -9.0729 | 108.902 | -9.5856 | -0.10986 | -0.009155 | -0.14648 | 1.0117 | 26.0925 | 3.0487 | 26.2024 | 3.1586 | -0.073242 | -0.082397 | 0.013733 | 1.6022 | 1.0895 | 119.577 | 1.1627 | 119.6503 | 1.1215 | 122.3419 | 1.6754 | 122.4655 | 122.4792 | 122.3694 | 122.3694 | 122.2961 | -122.4884 | -122.4518 | 122.2321 | 122.3923 | 12.9822 | 33.6502
2594.7656 | 122.5662 | -10.6567 | 111.7264 | -0.15556 | 0.0031937 | 0.062239 | 0.12252 | -0.0043151 | 0.012454 | -0.0030976 | -0.11932 | -0.0036914 | 0.063538 | 0.17299 | -0.029995 | 0.096049 | 0.0060883 | 2.4033 | 111.7355 | -10.7941 | 111.5204 | -9.6359 | -7.6309 | 15.4907 | 23.0621 | 111.7035 | -10.7346 | 111.6852 | -9.1095 | 108.8791 | -9.6359 | -0.13733 | 0.009156 | -0.20599 | 1.0208 | 26.1475 | 3.0258 | 26.2848 | 3.1631 | -0.07782 | -0.022888 | -0.041198 | 1.5472 | 1.0208 | 119.5358 | 1.0986 | 119.6136 | 1.1581 | 122.3145 | 1.6251 | 122.4197 | 122.5296 | 122.438 | 122.3923 | 122.3602 | -122.5204 | -122.4609 | 122.1771 | 122.3419 | 13.06 | 33.7189
2595.8281 | 122.5891 | -10.4462 | 111.9141 | -0.10216 | 0.00063028 | 0.061171 | 0.12359 | -0.00068368 | 0.014804 | -0.0026704 | -0.046081 | -0.0036914 | 0.06247 | 0.17448 | -0.028927 | 0.097117 | 0.0060883 | 2.5314 | 111.9278 | -10.5515 | 111.795 | -9.3567 | -7.2968 | 15.6509 | 23.172 | 111.882 | -10.5286 | 111.969 | -8.9355 | 109.4925 | -9.2514 | -0.10529 | 0.013733 | -0.11902 | 1.0895 | 26.0971 | 3.1494 | 26.2024 | 3.2547 | -0.082397 | -0.032043 | 0.054932 | 1.5106 | 1.1948 | 119.9387 | 1.2772 | 120.0211 | 1.1948 | 122.3465 | 1.593 | 122.4976 | 122.4792 | 122.4106 | 122.374 | 122.3282 | -122.4655 | -122.4426 | 122.2412 | 122.4152 | 12.9776 | 33.6182
2596.7656 | 122.5937 | -10.3775 | 112.0148 | -0.17082 | 0.0016983 | 0.061385 | 0.12252 | 0.00017092 | 0.018649 | -0.004593 | -0.10406 | -0.003905 | 0.060547 | 0.16701 | -0.029781 | 0.095836 | 0.0045929 | 2.5589 | 111.9553 | -10.5011 | 111.8408 | -9.4299 | -7.2739 | 15.6097 | 23.1766 | 111.9553 | -10.4874 | 112.0056 | -8.7891 | 109.1629 | -9.2972 | -0.1236 | -0.05951 | -0.17395 | 0.94757 | 25.9872 | 3.1036 | 26.1108 | 3.2272 | -0.10986 | -0.05951 | -0.009156 | 1.5884 | 1.0803 | 119.5404 | 1.1902 | 119.6503 | 1.0712 | 122.3419 | 1.6983 | 122.493 | 122.4564 | 122.4426 | 122.3328 | 122.3328 | -122.5159 | -122.5021 | 122.2183 | 122.3831 | 12.9364 | 33.5541
2597.7656 | 122.5479 | -10.3683 | 112.0285 | -0.1403 | 0.0019119 | 0.061171 | 0.12146 | -0.00068368 | 0.017368 | -0.0035248 | -0.10101 | -0.0041186 | 0.062683 | 0.17491 | -0.029995 | 0.098185 | 0.0056611 | 2.5818 | 111.9919 | -10.5057 | 111.8088 | -9.4528 | -7.2876 | 15.5914 | 23.1354 | 111.9507 | -10.4599 | 111.9644 | -8.8028 | 109.1309 | -9.3292 | -0.13733 | -0.036621 | -0.21973 | 0.91553 | 25.9598 | 3.0807 | 26.0971 | 3.2181 | -0.091553 | -0.077819 | -0.064086 | 1.5656 | 1.0391 | 119.4992 | 1.1307 | 119.5908 | 1.0529 | 122.3145 | 1.6571 | 122.4243 | 122.4976 | 122.4106 | 122.3602 | 122.319 | -122.5342 | -122.4884 | 122.1771 | 122.3328 | 12.9501 | 33.5037
2598.8281 | 122.5937 | -10.3867 | 111.9507 | -0.12505 | 0.0025529 | 0.06288 | 0.12466 | 0.0038025 | 0.015018 | -0.0024566 | -0.13763 | -0.0028368 | 0.061829 | 0.17641 | -0.029354 | 0.096904 | 0.0058747 | 2.6413 | 111.969 | -10.5331 | 111.8637 | -9.5123 | -7.2968 | 15.5731 | 23.2727 | 111.9186 | -10.4965 | 112.001 | -8.7982 | 109.14 | -9.3109 | -0.14648 | 0.01831 | -0.086976 | 0.87433 | 25.9598 | 3.0899 | 26.1063 | 3.2364 | -0.10986 | -0.032044 | 0.050354 | 1.5884 | 1.0757 | 119.5267 | 1.1856 | 119.6365 | 1.0208 | 122.3969 | 1.6983 | 122.4976 | 122.5021 | 122.4152 | 122.3557 | 122.3053 | -122.4838 | -122.4472 | 122.2504 | 122.3877 | 13.028 | 33.6594
2599.7656 | 122.5525 | -10.3546 | 112.001 | -0.12505 | -0.00086512 | 0.062453 | 0.12466 | 0.0010253 | 0.018222 | -0.00032036 | -0.088806 | -0.0017688 | 0.061829 | 0.18367 | -0.03149 | 0.097758 | 0.0067291 | 2.5635 | 112.0193 | -10.4691 | 111.8317 | -9.4757 | -7.2739 | 15.4999 | 23.5931 | 111.9919 | -10.4691 | 111.9781 | -8.7936 | 109.1766 | -9.2789 | -0.11444 | 0.01831 | -0.16937 | 0.87891 | 25.8545 | 3.0807 | 25.9689 | 3.1952 | -0.11444 | -0.009156 | -0.022889 | 1.561 | 1.0757 | 119.5312 | 1.1902 | 119.6457 | 0.99335 | 122.3007 | 1.6754 | 122.4472 | 122.4884 | 122.4609 | 122.374 | 122.3465 | -122.4701 | -122.4701 | 122.1863 | 122.3328 | 12.9181 | 33.9478
2600.8438 | 122.4655 | -10.437 | 112.0285 | -0.16319 | 0.00063028 | 0.060744 | 0.12423 | 0.0010253 | 0.017368 | 0.00032044 | -0.18646 | -0.0015552 | 0.064179 | 0.17769 | -0.030636 | 0.09904 | 0.0063019 | 2.6688 | 111.9965 | -10.5835 | 111.6898 | -9.5398 | -7.4066 | 15.3214 | 23.1995 | 111.9781 | -10.524 | 111.8683 | -8.9355 | 109.0164 | -9.4116 | -0.14648 | -0.032043 | -0.33875 | 0.89722 | 25.7584 | 3.0304 | 25.9048 | 3.1769 | -0.086975 | -0.050354 | -0.16022 | 1.5015 | 1.0254 | 119.4534 | 1.1124 | 119.5404 | 1.0437 | 122.2733 | 1.5884 | 122.3923 | 122.58 | 122.5021 | 122.4335 | 122.4152 | -122.612 | -122.5525 | 122.1268 | 122.3053 | 13.1058 | 33.6365
2601.7656 | 122.6166 | -10.3912 | 111.9553 | -0.07164 | 0.00041648 | 0.059035 | 0.12231 | 0.00017092 | 0.01694 | -0.003952 | -0.055237 | -0.0032642 | 0.06247 | 0.17064 | -0.0285 | 0.09434 | 0.0060883 | 2.7832 | 111.9965 | -10.5194 | 111.8042 | -9.3567 | -7.2235 | 15.4083 | 23.4467 | 111.9141 | -10.4874 | 111.9965 | -8.7204 | 109.227 | -9.2743 | -0.12817 | 0.041199 | -0.15106 | 1.0345 | 25.7996 | 3.1677 | 25.9277 | 3.2959 | -0.096131 | -0.041199 | 0.041199 | 1.6708 | 1.1169 | 119.6182 | 1.2131 | 119.7144 | 1.1627 | 122.3236 | 1.767 | 122.4838 | 122.5159 | 122.4014 | 122.3877 | 122.3053 | -122.4747 | -122.4426 | 122.1954 | 122.3877 | 13.1744 | 33.8379
2602.7656 | 122.6166 | -10.3912 | 111.969 | -0.086899 | 0.0019119 | 0.061171 | 0.12188 | 0.0025207 | 0.017795 | -0.0033112 | -0.067444 | -0.0015552 | 0.063965 | 0.16872 | -0.030636 | 0.09669 | 0.0058747 | 2.861 | 111.9919 | -10.5331 | 111.8088 | -9.3292 | -7.2098 | 15.5319 | 23.4879 | 111.9278 | -10.4645 | 111.9965 | -8.7112 | 109.2178 | -9.2514 | -0.14191 | 0.022888 | -0.16022 | 1.062 | 25.9232 | 3.1815 | 26.0651 | 3.3234 | -0.073243 | -0.041199 | 0.027466 | 1.68 | 1.1398 | 119.6091 | 1.2131 | 119.6823 | 1.2039 | 122.3419 | 1.7532 | 122.4609 | 122.525 | 122.3923 | 122.3831 | 122.319 | -122.5021 | -122.4335 | 122.2 | 122.3877 | 13.2523 | 33.8791
2603.7656 | 122.58 | -10.4324 | 111.9598 | -0.12505 | 0.00020288 | 0.063521 | 0.12167 | 0.00017092 | 0.018649 | -0.0041656 | -0.079651 | -0.0068958 | 0.062256 | 0.17534 | -0.030636 | 0.099467 | 0.0060883 | 2.8702 | 111.9553 | -10.5469 | 111.7401 | -9.3796 | -7.3242 | 15.4816 | 22.1237 | 111.8591 | -10.5606 | 111.8912 | -8.8028 | 109.0942 | -9.3292 | -0.11444 | -0.004578 | -0.21973 | 1.0529 | 25.914 | 3.1082 | 26.0284 | 3.2227 | -0.12817 | -0.10071 | -0.068665 | 1.6296 | 1.1032 | 119.5267 | 1.2314 | 119.6548 | 1.1673 | 122.287 | 1.7578 | 122.4518 | 122.5021 | 122.4197 | 122.3877 | 122.2916 | -122.5067 | -122.5204 | 122.1725 | 122.3236 | 13.3026 | 32.5562
2604.8281 | 122.5113 | -10.4965 | 111.9507 | -0.14793 | 0.0027665 | 0.06053 | 0.12316 | -0.0023925 | 0.01694 | -0.0058746 | -0.14984 | -0.002196 | 0.06247 | 0.1732 | -0.029995 | 0.096904 | 0.0073701 | 2.9114 | 111.9827 | -10.6247 | 111.6623 | -9.5398 | -7.402 | 15.3534 | 22.1832 | 111.9232 | -10.5789 | 111.8225 | -8.8852 | 109.0164 | -9.4208 | -0.12817 | 0.032043 | -0.28839 | 0.95673 | 25.8499 | 3.0945 | 25.9781 | 3.2227 | -0.082397 | -0.027466 | -0.12817 | 1.6113 | 1.0757 | 119.5129 | 1.1581 | 119.5953 | 1.0849 | 122.287 | 1.6937 | 122.4014 | 122.6074 | 122.5021 | 122.4792 | 122.4197 | -122.5754 | -122.5296 | 122.1588 | 122.319 | 13.4079 | 32.6797
2605.7656 | 122.5388 | -10.5194 | 111.9415 | -0.041122 | 0.0019119 | 0.060316 | 0.12381 | 0.00017092 | 0.017368 | -0.0041656 | -0.16205 | -0.001128 | 0.063324 | 0.17726 | -0.029354 | 0.09904 | 0.0073701 | 3.0029 | 111.9324 | -10.6293 | 111.6577 | -9.4849 | -7.3792 | 15.4678 | 23.5474 | 111.9049 | -10.5789 | 111.8317 | -8.8715 | 109.0073 | -9.4025 | -0.10986 | -0.009155 | -0.28381 | 1.0345 | 25.9872 | 3.1403 | 26.0971 | 3.2501 | -0.059509 | -0.036621 | -0.10986 | 1.6479 | 1.1169 | 119.5267 | 1.1765 | 119.5862 | 1.1444 | 122.287 | 1.7075 | 122.4106 | 122.5616 | 122.4838 | 122.4518 | 122.4243 | -122.5708 | -122.5204 | 122.1771 | 122.3511 | 13.5223 | 34.0668
2606.7656 | 122.6303 | -10.4965 | 111.8683 | -0.079269 | 0.0012711 | 0.062239 | 0.12274 | -0.00025628 | 0.015445 | -0.009079 | -0.055237 | -0.001128 | 0.064179 | 0.16914 | -0.029568 | 0.097331 | 0.0037385 | 3.154 | 111.9141 | -10.5927 | 111.7905 | -9.1324 | -7.4615 | 15.239 | 22.2153 | 111.8179 | -10.5789 | 111.9049 | -8.7433 | 109.1034 | -9.3201 | -0.09613 | 0.045776 | -0.07782 | 1.3641 | 25.7355 | 3.035 | 25.8316 | 3.1311 | -0.082397 | -0.050354 | 0.036621 | 1.7532 | 1.1765 | 119.5999 | 1.2589 | 119.6823 | 1.4603 | 122.3831 | 1.8356 | 122.4838 | 122.5067 | 122.3969 | 122.4106 | 122.3145 | -122.4609 | -122.4472 | 122.287 | 122.4014 | 13.6505 | 32.7118
2607.8281 | 122.4472 | -10.5743 | 111.9049 | -0.16319 | 0.0010575 | 0.062239 | 0.12466 | 0.0031617 | 0.017368 | 0.00032044 | -0.18646 | -0.0034778 | 0.063324 | 0.17406 | -0.024013 | 0.10011 | 0.0082245 | 3.1448 | 111.8729 | -10.6934 | 111.5662 | -9.6359 | -7.5119 | 15.4678 | 22.0367 | 111.85 | -10.675 | 111.7081 | -8.6975 | 108.8974 | -9.5352 | -0.11902 | -0.032043 | -0.33874 | 0.93842 | 26.0422 | 3.0624 | 26.1612 | 3.1815 | -0.10071 | -0.054931 | -0.19684 | 1.8768 | 1.0391 | 119.4717 | 1.1398 | 119.5724 | 1.0574 | 122.2595 | 1.9775 | 122.3831 | 122.5662 | 122.525 | 122.4472 | 122.4243 | -122.5983 | -122.58 | 122.1405 | 122.2824 | 13.7192 | 32.6111
2608.7656 | 122.5479 | -10.5423 | 111.8546 | -0.19371 | 0.00063028 | 0.060744 | 0.1221 | -0.00025628 | 0.017795 | -0.0018158 | -0.064392 | -0.0026232 | 0.061615 | 0.1747 | -0.028072 | 0.09669 | 0.0075837 | 3.2043 | 111.8362 | -10.6293 | 111.644 | -9.5078 | -7.3837 | 15.6601 | 23.8724 | 111.8088 | -10.6201 | 111.8179 | -8.8943 | 108.9844 | -9.3613 | -0.086975 | -0.01831 | -0.21057 | 1.0345 | 26.2024 | 3.1586 | 26.2894 | 3.2455 | -0.07782 | -0.045776 | -0.036621 | 1.6479 | 1.181 | 119.5267 | 1.2589 | 119.6045 | 1.1215 | 122.2733 | 1.7258 | 122.438 | 122.4655 | 122.4289 | 122.3785 | 122.3511 | -122.4838 | -122.4747 | 122.1863 | 122.3602 | 13.7466 | 34.4147
2609.7656 | 122.5616 | -10.5743 | 111.8088 | -0.17082 | 0.0025529 | 0.063094 | 0.1221 | -0.0017517 | 0.017581 | -0.0041656 | -0.064392 | -0.0015552 | 0.063965 | 0.17235 | -0.028072 | 0.097331 | 0.0077973 | 3.3234 | 111.8591 | -10.6842 | 111.5891 | -9.5123 | -7.4112 | 15.7242 | 23.9731 | 111.7813 | -10.6476 | 111.7172 | -8.8715 | 108.9615 | -9.4391 | -0.10986 | 0.050354 | -0.21973 | 1.062 | 26.2985 | 3.1631 | 26.4084 | 3.273 | -0.073242 | -0.027466 | -0.091553 | 1.7029 | 1.1353 | 119.5358 | 1.2085 | 119.6091 | 1.1719 | 122.2733 | 1.7761 | 122.3648 | 122.5433 | 122.4289 | 122.4335 | 122.3557 | -122.493 | -122.4564 | 122.1634 | 122.2916 | 13.8977 | 34.5474
2610.8438 | 122.5296 | -10.611 | 111.8546 | -0.12505 | 0.0016983 | 0.061385 | 0.12231 | -0.0015381 | 0.015659 | -0.0013886 | -0.14374 | -0.0030506 | 0.062256 | 0.18239 | -0.030636 | 0.098613 | 0.0039521 | 3.1494 | 111.8454 | -10.7162 | 111.5524 | -9.5993 | -7.457 | 15.7745 | 22.4487 | 111.8088 | -10.6705 | 111.7218 | -8.9172 | 108.8928 | -9.4391 | -0.10529 | -0.009155 | -0.30212 | 1.0117 | 26.3855 | 3.154 | 26.4908 | 3.2593 | -0.059509 | -0.045776 | -0.13275 | 1.6937 | 1.1719 | 119.5038 | 1.2314 | 119.5633 | 1.1169 | 122.2687 | 1.7532 | 122.3923 | 122.5616 | 122.4792 | 122.4564 | 122.4197 | -122.5708 | -122.525 | 122.1634 | 122.3328 | 13.7604 | 33.0597
2611.7656 | 122.5891 | -10.6155 | 111.7859 | -0.16319 | 0.00041648 | 0.061385 | 0.12295 | 0.0020935 | 0.014804 | -0.0026704 | -0.046081 | -0.0024096 | 0.063965 | 0.17854 | -0.028927 | 0.097331 | 0.0069427 | 3.3783 | 111.7676 | -10.7391 | 111.5616 | -9.5718 | -7.4112 | 15.8478 | 22.4716 | 111.7355 | -10.7071 | 111.7126 | -8.876 | 108.9752 | -9.3979 | -0.1236 | -0.018311 | -0.22431 | 1.0437 | 26.4633 | 3.2043 | 26.5869 | 3.3279 | -0.091552 | -0.050354 | -0.073243 | 1.7395 | 1.2177 | 119.5908 | 1.3092 | 119.6823 | 1.1673 | 122.3007 | 1.8311 | 122.4197 | 122.5067 | 122.4426 | 122.3831 | 122.3511 | -122.525 | -122.493 | 122.1771 | 122.3282 | 13.9938 | 33.0872
2612.7656 | 122.5845 | -10.6339 | 111.7584 | -0.12505 | 0.0023391 | 0.062239 | 0.12231 | -0.00046988 | 0.018008 | -0.0041656 | -0.052185 | -0.0017688 | 0.063111 | 0.17363 | -0.029354 | 0.096263 | 0.0067291 | 3.6438 | 111.7676 | -10.73 | 111.6028 | -9.5215 | -7.3929 | 15.9302 | 24.115 | 111.7126 | -10.7025 | 111.7172 | -8.8715 | 108.9661 | -9.3979 | -0.09613 | 0.009155 | -0.15564 | 1.1124 | 26.564 | 3.241 | 26.6602 | 3.3371 | -0.068665 | -0.045777 | -0.041199 | 1.7624 | 1.236 | 119.5999 | 1.3046 | 119.6686 | 1.2085 | 122.3328 | 1.8311 | 122.4197 | 122.4976 | 122.4152 | 122.4014 | 122.3465 | -122.4884 | -122.4609 | 122.2366 | 122.3511 | 14.2776 | 34.7488
2613.8281 | 122.5754 | -10.6567 | 111.7401 | -0.13267 | -0.0012923 | 0.064375 | 0.12338 | -0.0015381 | 0.017368 | -0.0052338 | -0.06134 | -0.002196 | 0.06247 | 0.17876 | -0.030209 | 0.095836 | 0.010361 | 3.7949 | 111.7447 | -10.7391 | 111.5707 | -9.5169 | -7.4112 | 15.8112 | 22.3892 | 111.6852 | -10.7483 | 111.7172 | -8.876 | 108.9203 | -9.4208 | -0.082398 | 0.004578 | -0.16937 | 1.1398 | 26.4679 | 3.2455 | 26.5503 | 3.3279 | -0.091553 | -0.054931 | -0.022888 | 1.7807 | 1.236 | 119.577 | 1.3275 | 119.6686 | 1.2222 | 122.3099 | 1.8723 | 122.4655 | 122.4838 | 122.4335 | 122.4014 | 122.3419 | -122.4792 | -122.4884 | 122.2275 | 122.374 | 14.4516 | 33.046
2614.7656 | 122.58 | -10.6567 | 111.7355 | -0.094528 | -1.0718e-05 | 0.061171 | 0.12017 | -0.0021789 | 0.015231 | -0.004593 | -0.033874 | -0.0017688 | 0.062256 | 0.17235 | -0.029568 | 0.093699 | 0.0097199 | 3.8635 | 111.7126 | -10.8124 | 111.5295 | -9.5352 | -7.4524 | 15.6967 | 22.3618 | 111.6623 | -10.7346 | 111.6989 | -8.876 | 108.9249 | -9.3933 | -0.15564 | -0.022889 | -0.20599 | 1.1215 | 26.3535 | 3.2043 | 26.5091 | 3.36 | -0.07782 | -0.073243 | -0.036621 | 1.7807 | 1.2634 | 119.5816 | 1.3412 | 119.6594 | 1.2772 | 122.3419 | 1.8585 | 122.4335 | 122.525 | 122.3969 | 122.3694 | 122.319 | -122.5479 | -122.4701 | 122.1863 | 122.3557 | 14.5203 | 33.0185
2615.7656 | 122.5479 | -10.6796 | 111.6943 | -0.1403 | 0.0016983 | 0.062453 | 0.12188 | -0.00046988 | 0.017368 | 0.001175 | -0.085754 | -0.0015552 | 0.064606 | 0.1732 | -0.029995 | 0.097545 | 0.010147 | 3.9871 | 111.6898 | -10.7941 | 111.5158 | -9.5261 | -7.5027 | 15.8249 | 22.1512 | 111.644 | -10.7666 | 111.6714 | -8.9355 | 108.847 | -9.4345 | -0.11444 | -0.004578 | -0.17853 | 1.1536 | 26.5045 | 3.1769 | 26.619 | 3.2913 | -0.086976 | -0.050354 | -0.022888 | 1.7441 | 1.2451 | 119.5267 | 1.3321 | 119.6136 | 1.268 | 122.3099 | 1.8311 | 122.4381 | 122.4838 | 122.4106 | 122.3694 | 122.3236 | -122.4884 | -122.4609 | 122.1954 | 122.3511 | 14.6667 | 32.8308
2616.7656 | 122.5479 | -10.7346 | 111.6852 | -0.10216 | -0.0010787 | 0.060744 | 0.12146 | -0.0011109 | 0.016727 | -0.002884 | -0.091858 | -0.0030506 | 0.064606 | 0.17811 | -0.02914 | 0.094981 | 0.0043793 | 4.0878 | 111.6714 | -10.8078 | 111.4746 | -9.5489 | -7.5302 | 15.7654 | 23.9731 | 111.6165 | -10.8124 | 111.644 | -9.0225 | 108.8333 | -9.4482 | -0.073242 | -0.013733 | -0.21057 | 1.1856 | 26.4999 | 3.2043 | 26.5732 | 3.2776 | -0.07782 | -0.068665 | -0.041199 | 1.712 | 1.2863 | 119.5679 | 1.3641 | 119.6457 | 1.2589 | 122.2824 | 1.7899 | 122.4564 | 122.4792 | 122.4289 | 122.406 | 122.3511 | -122.493 | -122.4976 | 122.2092 | 122.3785 | 14.8224 | 34.7076
2617.7656 | 122.5891 | -10.7483 | 111.644 | -0.14793 | 0.00063028 | 0.064803 | 0.12103 | 0.0010253 | 0.018649 | 0.00010684 | -0.082703 | -0.0032642 | 0.063965 | 0.17107 | -0.030209 | 0.098185 | 0.0092927 | 4.0512 | 111.644 | -10.881 | 111.4197 | -9.7321 | -7.5485 | 15.7516 | 24.4034 | 111.5616 | -10.8353 | 111.6119 | -8.9722 | 108.8013 | -9.4437 | -0.13275 | 0 | -0.2243 | 1.0162 | 26.4999 | 3.1998 | 26.6327 | 3.3325 | -0.086975 | -0.082398 | -0.032044 | 1.7761 | 1.3046 | 119.5496 | 1.3916 | 119.6365 | 1.149 | 122.3007 | 1.8631 | 122.4472 | 122.525 | 122.3969 | 122.3923 | 122.3099 | -122.525 | -122.4792 | 122.168 | 122.3602 | 14.7995 | 35.1517
2618.7656 | 122.5983 | -10.7574 | 111.6211 | -0.17082 | 0.0019119 | 0.061171 | 0.12316 | -0.0038879 | 0.018436 | -0.0037384 | -0.055237 | -0.0028368 | 0.06247 | 0.17021 | -0.030209 | 0.095408 | 0.0052337 | 4.454 | 111.6531 | -10.849 | 111.4563 | -9.6542 | -7.5119 | 15.921 | 24.3896 | 111.5799 | -10.8078 | 111.6211 | -8.9355 | 108.8425 | -9.4025 | -0.091553 | 0.032043 | -0.16479 | 1.1032 | 26.6785 | 3.2455 | 26.77 | 3.3371 | -0.050354 | -0.041199 | 0 | 1.8219 | 1.355 | 119.5999 | 1.4053 | 119.6503 | 1.1948 | 122.3053 | 1.8723 | 122.4289 | 122.5021 | 122.3877 | 122.4106 | 122.3373 | -122.4701 | -122.4289 | 122.2137 | 122.3785 | 15.2115 | 35.1471
2619.7656 | 122.58 | -10.7574 | 111.6669 | -0.16319 | 0.0021255 | 0.063094 | 0.12124 | -0.00025628 | 0.016299 | -0.0043792 | -0.079651 | -0.0034778 | 0.06247 | 0.17534 | -0.030636 | 0.096477 | 0.0077973 | 4.4174 | 111.6577 | -10.881 | 111.4334 | -9.6542 | -7.5302 | 15.8752 | 24.4492 | 111.5799 | -10.8398 | 111.6074 | -8.9401 | 108.8333 | -9.3933 | -0.1236 | -0.009155 | -0.23346 | 1.1032 | 26.6327 | 3.2272 | 26.7563 | 3.3508 | -0.082398 | -0.086975 | -0.059509 | 1.8173 | 1.3641 | 119.5908 | 1.4465 | 119.6732 | 1.2268 | 122.3145 | 1.8997 | 122.4472 | 122.5388 | 122.4197 | 122.4152 | 122.3373 | -122.5479 | -122.5067 | 122.1909 | 122.3648 | 15.1749 | 35.2066
2620.7656 | 122.58 | -10.7895 | 111.5845 | -0.10216 | -0.00065152 | 0.06288 | 0.12252 | -0.0019653 | 0.016513 | -0.0018158 | -0.046081 | -0.0030506 | 0.064606 | 0.17534 | -0.029354 | 0.09434 | 0.0058747 | 4.6783 | 111.6028 | -10.9039 | 111.3968 | -9.668 | -7.5668 | 15.8249 | 24.3622 | 111.5616 | -10.881 | 111.5616 | -8.9813 | 108.7875 | -9.407 | -0.11444 | 0.01831 | -0.18768 | 1.1215 | 26.6144 | 3.2227 | 26.7288 | 3.3371 | -0.091552 | -0.022889 | -0.022889 | 1.8082 | 1.3824 | 119.577 | 1.474 | 119.6686 | 1.236 | 122.3007 | 1.8997 | 122.4426 | 122.5067 | 122.4426 | 122.3923 | 122.3511 | -122.4884 | -122.4655 | 122.1863 | 122.3511 | 15.4678 | 35.1517
2621.8281 | 122.5067 | -10.8444 | 111.6028 | -0.07164 | 0.00084388 | 0.061598 | 0.12338 | -0.0034607 | 0.017795 | -0.0033112 | -0.13458 | -0.0030506 | 0.062683 | 0.17747 | -0.027859 | 0.095622 | 0.0086517 | 4.8798 | 111.6257 | -10.9177 | 111.3556 | -9.6817 | -7.5851 | 15.8203 | 24.3439 | 111.5891 | -10.8948 | 111.47 | -9.0546 | 108.6685 | -9.4849 | -0.073243 | 0.022888 | -0.24719 | 1.1627 | 26.6647 | 3.2593 | 26.738 | 3.3325 | -0.050354 | -0.013733 | -0.13275 | 1.7899 | 1.3596 | 119.5129 | 1.4099 | 119.5633 | 1.236 | 122.2733 | 1.8402 | 122.3648 | 122.5433 | 122.4838 | 122.4701 | 122.4335 | -122.5204 | -122.4976 | 122.2 | 122.3145 | 15.7242 | 35.1883
2622.7656 | 122.5525 | -10.8353 | 111.5387 | -0.14793 | 0.00020288 | 0.063307 | 0.12381 | 0.00038452 | 0.015018 | -0.00096136 | -0.10101 | -0.0036914 | 0.063111 | 0.17341 | -0.02914 | 0.096904 | 0.0060883 | 4.6005 | 111.5662 | -10.9543 | 111.3373 | -9.7046 | -7.608 | 15.7242 | 22.467 | 111.5067 | -10.9039 | 111.5067 | -9.0042 | 108.6914 | -9.3933 | -0.11902 | 0.027466 | -0.20142 | 1.1307 | 26.5594 | 3.2272 | 26.6785 | 3.3463 | -0.068665 | -0.032043 | -0.032043 | 1.8311 | 1.442 | 119.5267 | 1.5106 | 119.5953 | 1.2497 | 122.2916 | 1.8997 | 122.4106 | 122.5204 | 122.4106 | 122.4014 | 122.3419 | -122.493 | -122.4426 | 122.1725 | 122.3419 | 15.4358 | 33.3023
2623.7656 | 122.5571 | -10.8398 | 111.5479 | -0.13267 | 0.0027665 | 0.062666 | 0.1221 | 0.0010253 | 0.018222 | -0.0016022 | -0.09491 | -0.0036914 | 0.062683 | 0.17662 | -0.0285 | 0.095195 | 0.0092927 | 5.2277 | 111.5433 | -10.9726 | 111.351 | -9.6359 | -7.6126 | 15.8066 | 22.4442 | 111.47 | -10.9177 | 111.5112 | -8.9905 | 108.6868 | -9.3384 | -0.13275 | -0.004578 | -0.19684 | 1.2039 | 26.6464 | 3.2272 | 26.7792 | 3.36 | -0.07782 | -0.07782 | -0.036622 | 1.8494 | 1.5015 | 119.5267 | 1.5793 | 119.6045 | 1.3367 | 122.3236 | 1.9272 | 122.4289 | 122.5159 | 122.3877 | 122.3831 | 122.3099 | -122.5204 | -122.4655 | 122.1909 | 122.3511 | 16.0675 | 33.284
2624.8281 | 122.612 | -10.9177 | 111.4609 | -0.14793 | 0.0019119 | 0.061598 | 0.12146 | -0.00025628 | 0.015231 | -0.010574 | -0.04303 | -0.0034778 | 0.062042 | 0.18089 | -0.030636 | 0.096904 | 0.011642 | 5.4291 | 111.4609 | -11.0184 | 111.4059 | -9.5261 | -7.8644 | 15.8524 | 22.4533 | 111.4059 | -11.0229 | 111.4746 | -8.9813 | 108.6731 | -9.2056 | -0.10071 | 0 | -0.054931 | 1.3916 | 26.77 | 3.0533 | 26.8707 | 3.154 | -0.10529 | -0.054931 | 0.013733 | 1.9363 | 1.712 | 119.5908 | 1.8173 | 119.696 | 1.4923 | 122.4243 | 2.0416 | 122.4976 | 122.4792 | 122.4289 | 122.3785 | 122.3236 | -122.4792 | -122.4838 | 122.3236 | 122.3923 | 16.3467 | 33.371
2625.7656 | 122.5708 | -11.467 | 110.8749 | -0.1403 | 0.0010575 | 0.061171 | 0.12295 | 0.0018799 | 0.019931 | -0.0024566 | -0.30548 | -0.0024096 | 0.063965 | 0.64616 | -0.030636 | 0.094127 | 0.47478 | 5.5161 | 110.8795 | -11.5952 | 110.7422 | -10.2951 | -8.0246 | 16.6946 | 22.7783 | 110.82 | -11.4944 | 110.8063 | -8.2947 | 108.078 | 68.541 | -0.12817 | 0.004578 | -0.13275 | 1.1719 | 28.1616 | 3.4424 | 28.2898 | 3.5706 | -0.027466 | -0.054932 | -0.068665 | 3.1723 | 80.0079 | 119.545 | 80.0354 | 119.5724 | 1.3 | 122.3373 | 3.1998 | 122.3007 | 122.4747 | 122.3145 | 122.3465 | 122.287 | -122.4701 | -122.3694 | 122.2092 | 122.2733 | 16.983 | 34.2453
2626.7656 | 122.5159 | -11.673 | 110.6689 | -0.10979 | 0.0027665 | 0.06053 | 0.12316 | -0.0021789 | 0.018222 | -0.0018158 | -0.30548 | -0.0032642 | 0.065033 | 0.74785 | -0.031277 | 0.093486 | 0.58031 | 5.5298 | 110.7193 | -11.7554 | 110.4904 | -10.5011 | -8.2031 | 16.7725 | 22.4854 | 110.5911 | -11.7004 | 110.5179 | -8.2535 | 107.8171 | 83.6563 | -0.082397 | 0.050354 | -0.17853 | 1.1719 | 28.4454 | 3.4698 | 28.5278 | 3.5522 | -0.027465 | -0.07782 | -0.15106 | 3.4195 | 95.3293 | 119.4901 | 95.3568 | 119.5175 | 1.2543 | 122.2458 | 3.447 | 122.2183 | 122.4747 | 122.2916 | 122.3923 | 122.2641 | -122.4243 | -122.3694 | 122.1634 | 122.1909 | 17.2028 | 34.1583
2627.7656 | 122.5525 | -11.6684 | 110.6369 | -0.16319 | 0.0014847 | 0.06288 | 0.12103 | -0.0015381 | 0.020999 | -0.0013886 | -0.32684 | -0.002196 | 0.064179 | 0.77241 | -0.032558 | 0.093059 | 0.59911 | 5.9143 | 110.6689 | -11.7554 | 110.4446 | -10.5148 | -8.1757 | 16.832 | 22.7966 | 110.5911 | -11.6684 | 110.527 | -8.1299 | 107.8033 | 87.4283 | -0.086975 | 0.032043 | -0.19226 | 1.1536 | 28.5004 | 3.4927 | 28.5873 | 3.5797 | 0 | -0.045777 | -0.10986 | 3.5385 | 99.0967 | 119.4717 | 99.0967 | 119.4717 | 1.2405 | 122.2 | 3.5385 | 122.1954 | 122.4243 | 122.2595 | 122.3373 | 122.2595 | -122.3923 | -122.3053 | 122.113 | 122.1954 | 17.5827 | 34.465
2628.8281 | 122.5754 | -11.7096 | 110.5545 | -0.14793 | 0.00020288 | 0.062239 | 0.12338 | -0.0028199 | 0.018222 | -0.0041656 | -0.31158 | -0.002196 | 0.060974 | 0.78459 | -0.03384 | 0.093059 | 0.61769 | 6.2119 | 110.6369 | -11.7416 | 110.4218 | -10.4874 | -8.1757 | 16.8823 | 22.8745 | 110.527 | -11.7004 | 110.4904 | -8.139 | 107.7484 | 90.0925 | -0.032043 | 0.082398 | -0.13275 | 1.2222 | 28.5919 | 3.5339 | 28.624 | 3.566 | 0.009156 | -0.027465 | -0.064087 | 3.5706 | 101.8021 | 119.458 | 101.7929 | 119.4489 | 1.2543 | 122.1634 | 3.5614 | 122.1909 | 122.3785 | 122.2275 | 122.3465 | 122.2366 | -122.2961 | -122.2549 | 122.1313 | 122.2 | 17.9214 | 34.584
2629.7656 | 122.4792 | -11.7142 | 110.5545 | -0.1403 | 0.0010575 | 0.063307 | 0.1221 | 0.0020935 | 0.019717 | -0.0013886 | -0.4184 | -0.0015552 | 0.064392 | 0.80147 | -0.035549 | 0.095195 | 0.62837 | 6.4362 | 110.5911 | -11.8103 | 110.4126 | -10.3958 | -8.1757 | 16.8549 | 22.9019 | 110.4721 | -11.7325 | 110.4034 | -7.9834 | 107.8079 | 92.189 | -0.096131 | 0.036621 | -0.14191 | 1.3184 | 28.569 | 3.5385 | 28.6652 | 3.6346 | -0.018311 | -0.082397 | -0.15106 | 3.7308 | 103.9032 | 119.5221 | 103.9215 | 119.5404 | 1.4145 | 122.2229 | 3.7491 | 122.1359 | 122.4014 | 122.2046 | 122.3053 | 122.1863 | -122.3648 | -122.287 | 122.1268 | 122.1176 | 18.1503 | 34.6161
2630.7656 | 122.4792 | -11.0779 | 111.1725 | -0.056381 | 0.00041648 | 0.065016 | 0.12081 | 0.0038025 | 0.020572 | -0.0018158 | -0.36041 | -0.0032642 | 0.063751 | 0.80574 | -0.031063 | 0.093272 | 0.63286 | 6.6147 | 111.1588 | -11.2152 | 111.0214 | -9.8282 | -7.4249 | 17.1707 | 22.8287 | 111.0718 | -11.1282 | 111.1038 | -7.4707 | 108.3344 | 94.043 | -0.13733 | -0.013733 | -0.15106 | 1.2497 | 28.2486 | 3.653 | 28.3859 | 3.7903 | -0.050354 | -0.10071 | -0.068664 | 3.6072 | 105.1209 | 119.4122 | 105.1712 | 119.4626 | 1.387 | 122.2366 | 3.6575 | 122.2321 | 122.374 | 122.2 | 122.2366 | 122.1497 | -122.3877 | -122.3007 | 122.0993 | 122.1817 | 17.6926 | 33.9066
2631.7656 | 122.4518 | -10.881 | 111.3693 | -0.16319 | 0.0019119 | 0.060103 | 0.12081 | -0.0019653 | 0.018649 | -0.0026704 | -0.29938 | -0.0032642 | 0.064179 | 0.81044 | -0.032345 | 0.09135 | 0.64012 | 7.0404 | 111.4014 | -11.0138 | 111.1862 | -9.6817 | -7.1823 | 17.3584 | 22.7509 | 111.2686 | -10.9222 | 111.2457 | -7.2372 | 108.5449 | 95.1508 | -0.13275 | 0.032043 | -0.18311 | 1.1993 | 28.2394 | 3.6987 | 28.3722 | 3.8315 | -0.041199 | -0.10071 | -0.1236 | 3.6438 | 106.0318 | 119.426 | 106.073 | 119.4672 | 1.3321 | 122.2 | 3.685 | 122.168 | 122.4152 | 122.1909 | 122.2824 | 122.1497 | -122.3831 | -122.2916 | 122.0673 | 122.1268 | 17.9214 | 33.6319
2632.8281 | 122.5433 | -10.9222 | 111.3098 | -0.094528 | 0.00041648 | 0.062025 | 0.12081 | -0.0015381 | 0.02164 | -0.0041656 | -0.31464 | -0.0047594 | 0.063111 | 0.81001 | -0.032131 | 0.092418 | 0.63841 | 7.2784 | 111.3327 | -11.0046 | 111.1908 | -9.6268 | -7.1594 | 17.5232 | 23.0301 | 111.2045 | -10.9451 | 111.2503 | -7.1594 | 108.7234 | 95.9839 | -0.082398 | 0.022889 | -0.11902 | 1.2955 | 28.4454 | 3.7628 | 28.5278 | 3.8452 | -0.022888 | -0.10529 | -0.059509 | 3.7628 | 106.9061 | 119.6457 | 106.929 | 119.6686 | 1.3779 | 122.1954 | 3.7857 | 122.1954 | 122.3373 | 122.1497 | 122.2549 | 122.1268 | -122.3145 | -122.2549 | 122.113 | 122.1725 | 18.2007 | 33.9523
2633.7656 | 122.4747 | -10.9451 | 111.2595 | -0.12505 | 0.0029801 | 0.061812 | 0.12146 | 0.0018799 | 0.021213 | -0.0016022 | -0.38788 | -0.0015552 | 0.062897 | 0.81364 | -0.032772 | 0.093059 | 0.64354 | 7.2098 | 111.2457 | -11.087 | 111.1267 | -9.6954 | -7.2372 | 17.4957 | 23.2864 | 111.1771 | -10.9909 | 111.1954 | -7.2647 | 108.4351 | 96.1166 | -0.14191 | -0.013732 | -0.13275 | 1.2497 | 28.4409 | 3.7079 | 28.5828 | 3.8498 | -0.045777 | -0.082397 | -0.064086 | 3.6804 | 107.0618 | 119.3802 | 107.1075 | 119.426 | 1.3916 | 122.2137 | 3.7262 | 122.1863 | 122.3328 | 122.168 | 122.1909 | 122.1222 | -122.3465 | -122.2504 | 122.0718 | 122.1405 | 18.1549 | 34.2316
2634.7656 | 122.4243 | -11.3159 | 110.9024 | -0.17082 | 0.0034073 | 0.062025 | 0.12103 | -0.0015381 | 0.018649 | -0.0041656 | -0.36652 | -0.0026232 | 0.066956 | 0.81621 | -0.034054 | 0.094127 | 0.64333 | 7.5943 | 110.8749 | -11.4532 | 110.7285 | -10.0388 | -7.6721 | 17.4866 | 22.8836 | 110.788 | -11.3571 | 110.7925 | -7.608 | 108.0368 | 96.1578 | -0.13733 | -0.027466 | -0.17395 | 1.2772 | 28.8025 | 3.6438 | 28.9398 | 3.7811 | -0.041199 | -0.11444 | -0.10986 | 3.7079 | 107.4738 | 119.3527 | 107.515 | 119.3939 | 1.4145 | 122.1817 | 3.7491 | 122.1497 | 122.3282 | 122.1451 | 122.1909 | 122.1039 | -122.3557 | -122.2595 | 122.0444 | 122.1085 | 18.9102 | 34.1995
2635.7656 | 122.4335 | -11.3937 | 110.7971 | -0.14793 | 0.00041648 | 0.063307 | 0.12103 | -0.00068368 | 0.019504 | 0.00032044 | -0.38177 | -0.0034778 | 0.062256 | 0.81322 | -0.032131 | 0.09434 | 0.63863 | 7.7225 | 110.7788 | -11.5219 | 110.6461 | -10.1303 | -7.7271 | 17.6376 | 22.9431 | 110.7239 | -11.4349 | 110.7193 | -7.6584 | 107.9727 | 96.3638 | -0.12817 | -0.01831 | -0.15106 | 1.2634 | 29.0314 | 3.6667 | 29.1595 | 3.7949 | -0.041199 | -0.073242 | -0.07782 | 3.7354 | 107.7576 | 119.3665 | 107.7988 | 119.4077 | 1.3916 | 122.168 | 3.7766 | 122.1542 | 122.3007 | 122.1588 | 122.1725 | 122.1176 | -122.319 | -122.2321 | 122.0398 | 122.113 | 19.1162 | 34.3369
2636.7656 | 122.3831 | -11.4578 | 110.7559 | -0.13267 | 0.0016983 | 0.061385 | 0.12551 | 0.0010253 | 0.019931 | -0.002884 | -0.43671 | -0.0024096 | 0.064179 | 0.81642 | -0.032558 | 0.093699 | 0.64119 | 8.2443 | 110.7651 | -11.5997 | 110.495 | -10.3958 | -7.869 | 17.569 | 22.9477 | 110.701 | -11.5173 | 110.5957 | -7.7545 | 107.8125 | 96.5881 | -0.14191 | 0.009156 | -0.26093 | 1.062 | 29.0268 | 3.5889 | 29.1687 | 3.7308 | -0.059509 | -0.054931 | -0.16022 | 3.7033 | 108.046 | 119.2703 | 108.1055 | 119.3298 | 1.2039 | 122.0947 | 3.7628 | 122.113 | 122.3648 | 122.2183 | 122.2229 | 122.1588 | -122.3557 | -122.2733 | 121.9528 | 122.0535 | 19.7021 | 34.4055
2637.7656 | 122.4243 | -11.5082 | 110.701 | -0.16319 | 0.0023391 | 0.064589 | 0.12124 | 0.0023071 | 0.023135 | -0.0030976 | -0.40924 | -0.0032642 | 0.062683 | 0.81215 | -0.03149 | 0.094981 | 0.64418 | 8.4183 | 110.701 | -11.6135 | 110.3302 | -10.5057 | -7.5714 | 17.8207 | 23.3093 | 110.5682 | -11.5402 | 110.6186 | -7.663 | 107.8583 | 96.8491 | -0.10529 | 0 | -0.37079 | 1.0025 | 29.3289 | 3.9368 | 29.4342 | 4.0421 | -0.032043 | -0.13275 | -0.082398 | 3.8452 | 108.3572 | 119.3665 | 108.3893 | 119.3985 | 1.1078 | 121.9437 | 3.8773 | 122.1588 | 122.3145 | 122.1085 | 122.2092 | 122.0764 | -122.3145 | -122.2412 | 121.8384 | 122.1268 | 19.9265 | 34.8175
2638.7656 | 122.4014 | -11.5265 | 110.7101 | -0.14793 | 0.0019119 | 0.062453 | 0.12274 | 0.0033753 | 0.020786 | -0.0035248 | -0.41229 | -0.0015552 | 0.064392 | 0.82219 | -0.031917 | 0.093486 | 0.64204 | 8.8211 | 110.7285 | -11.6501 | 110.4492 | -10.2814 | -7.8873 | 17.7704 | 23.053 | 110.6461 | -11.5402 | 110.5682 | -7.7087 | 107.7988 | 97.023 | -0.1236 | 0.018311 | -0.26093 | 1.2451 | 29.2969 | 3.6392 | 29.4205 | 3.7628 | -0.013733 | -0.064087 | -0.14191 | 3.8177 | 108.5495 | 119.3253 | 108.5632 | 119.339 | 1.3687 | 122.0993 | 3.8315 | 122.1085 | 122.3785 | 122.1863 | 122.2549 | 122.1725 | -122.3602 | -122.2504 | 121.9757 | 122.0947 | 20.3476 | 34.5795
2639.7656 | 122.4197 | -11.5311 | 110.6644 | -0.10979 | 0.00084388 | 0.064803 | 0.12167 | 0.0012391 | 0.018222 | -0.0026704 | -0.36957 | -0.0045458 | 0.065247 | 0.8192 | -0.03149 | 0.093486 | 0.64461 | 8.7616 | 110.6735 | -11.6821 | 110.4584 | -10.3088 | -7.8598 | 17.775 | 23.1354 | 110.5682 | -11.5768 | 110.5637 | -7.6492 | 107.8171 | 97.2427 | -0.15106 | 0.009155 | -0.20599 | 1.2222 | 29.306 | 3.6713 | 29.4571 | 3.8223 | -0.045776 | -0.096131 | -0.10071 | 3.8818 | 108.7738 | 119.3481 | 108.8196 | 119.3939 | 1.3733 | 122.1405 | 3.9276 | 122.1405 | 122.3557 | 122.1451 | 122.2046 | 122.0993 | -122.3465 | -122.2412 | 121.9894 | 122.0947 | 20.2927 | 34.6664
2640.7656 | 122.3694 | -11.5677 | 110.6323 | -0.14793 | 0.00063028 | 0.062025 | 0.12124 | -0.0017517 | 0.020786 | -0.002884 | -0.31769 | -0.0030506 | 0.063751 | 0.80958 | -0.031063 | 0.093059 | 0.63948 | 9.3704 | 110.5957 | -11.6959 | 110.4172 | -10.318 | -7.8461 | 17.7841 | 23.1628 | 110.5408 | -11.5906 | 110.4813 | -7.6996 | 107.7484 | 97.3343 | -0.12817 | -0.036621 | -0.21515 | 1.2497 | 29.3518 | 3.7216 | 29.48 | 3.8498 | -0.022888 | -0.091553 | -0.15106 | 3.8681 | 108.902 | 119.3161 | 108.9249 | 119.339 | 1.3779 | 122.113 | 3.891 | 122.0718 | 122.2916 | 122.1313 | 122.1634 | 122.1085 | -122.3282 | -122.2229 | 121.9849 | 122.049 | 20.9381 | 34.7305
2641.8281 | 122.319 | -11.6043 | 110.614 | -0.29289 | 0.0023391 | 0.063094 | 0.1221 | -0.0021789 | 0.02164 | -0.0024566 | -0.4184 | -0.00070063 | 0.062042 | 0.813 | -0.031063 | 0.09434 | 0.63713 | 9.993 | 110.6827 | -11.7004 | 110.3943 | -10.3088 | -7.8918 | 17.7429 | 23.3917 | 110.5499 | -11.6364 | 110.4492 | -7.7591 | 107.6797 | 97.467 | -0.09613 | 0.068664 | -0.21973 | 1.2955 | 29.3472 | 3.7125 | 29.4434 | 3.8086 | -0.032044 | -0.064087 | -0.16479 | 3.8452 | 109.0713 | 119.2841 | 109.1034 | 119.3161 | 1.3916 | 122.0947 | 3.8773 | 122.0856 | 122.3831 | 122.1863 | 122.287 | 122.1542 | -122.3145 | -122.2504 | 121.9986 | 122.0535 | 21.5973 | 34.996
2642.7656 | 122.3969 | -11.6409 | 110.5453 | -0.12505 | 0.00020288 | 0.06288 | 0.12081 | -0.0019653 | 0.02164 | -0.00010676 | -0.40009 | -0.0024096 | 0.065247 | 0.8098 | -0.031917 | 0.094554 | 0.6382 | 10.3683 | 110.5865 | -11.792 | 110.3531 | -10.35 | -7.9239 | 17.7887 | 23.4146 | 110.4767 | -11.6592 | 110.4492 | -7.6355 | 107.7118 | 97.641 | -0.15106 | 0.041199 | -0.19226 | 1.2909 | 29.4296 | 3.717 | 29.5807 | 3.8681 | -0.018311 | -0.068664 | -0.09613 | 4.0054 | 109.2819 | 119.3527 | 109.3002 | 119.371 | 1.442 | 122.1451 | 4.0237 | 122.1085 | 122.3785 | 122.1359 | 122.2275 | 122.1176 | -122.3373 | -122.2046 | 121.994 | 122.0901 | 22.0093 | 35.0555
2643.7656 | 122.3007 | -11.7004 | 110.5545 | -0.23949 | 0.0014847 | 0.060957 | 0.12359 | -0.0013245 | 0.023135 | -0.0033112 | -0.40619 | -0.001128 | 0.064392 | 0.80852 | -0.030636 | 0.094768 | 0.63969 | 10.0708 | 110.5774 | -11.8103 | 110.2249 | -10.4416 | -8.0292 | 17.7658 | 23.259 | 110.4355 | -11.7325 | 110.3165 | -7.8049 | 107.5516 | 97.6501 | -0.10986 | 0.022889 | -0.32959 | 1.2588 | 29.4662 | 3.6713 | 29.5761 | 3.7811 | -0.032044 | -0.11902 | -0.23804 | 3.8956 | 109.3506 | 119.252 | 109.3826 | 119.2841 | 1.3687 | 122.0352 | 3.9276 | 122.049 | 122.3877 | 122.168 | 122.2778 | 122.1359 | -122.3648 | -122.287 | 121.9254 | 122.0169 | 21.7712 | 34.9594
2644.7656 | 122.3373 | -11.7188 | 110.527 | -0.10216 | 0.0019119 | 0.065871 | 0.12146 | -0.00089728 | 0.020358 | -0.002243 | -0.40314 | 0.00036737 | 0.06482 | 0.81087 | -0.028927 | 0.093699 | 0.64333 | 11.0825 | 110.5453 | -11.8423 | 110.2203 | -10.3867 | -8.0383 | 17.7933 | 22.9706 | 110.4309 | -11.7279 | 110.3119 | -7.7545 | 107.5699 | 97.76 | -0.1236 | 0.01831 | -0.3067 | 1.3321 | 29.512 | 3.6804 | 29.6356 | 3.804 | -0.009155 | -0.096131 | -0.21515 | 3.9642 | 109.4788 | 119.2886 | 109.4879 | 119.2978 | 1.4557 | 122.0627 | 3.9734 | 122.0398 | 122.3877 | 122.1588 | 122.2641 | 122.1497 | -122.3694 | -122.2549 | 121.9391 | 122.0306 | 22.8012 | 34.6893
2645.7656 | 122.4152 | -11.705 | 110.4401 | -0.14793 | 0.0019119 | 0.062025 | 0.11996 | 0.0046569 | 0.019504 | 0.0018158 | -0.35431 | -0.0024096 | 0.065033 | 0.80574 | -0.030849 | 0.091136 | 0.64055 | 10.9726 | 110.4492 | -11.8332 | 110.0739 | -10.524 | -7.695 | 18.1183 | 23.1125 | 110.3394 | -11.7554 | 110.3622 | -7.7133 | 107.6202 | 97.9111 | -0.12817 | 0.009156 | -0.36621 | 1.181 | 29.8233 | 4.01 | 29.9515 | 4.1382 | -0.050354 | -0.10071 | -0.077819 | 3.9917 | 109.6161 | 119.3253 | 109.6664 | 119.3756 | 1.3092 | 121.907 | 4.0421 | 122.1176 | 122.2824 | 122.0947 | 122.1542 | 122.0444 | -122.2733 | -122.1954 | 121.7789 | 122.0673 | 22.6776 | 34.8175
2646.8281 | 122.2595 | -11.7325 | 110.5087 | -0.1403 | 0.0016983 | 0.063948 | 0.12167 | -0.0028199 | 0.020358 | -0.0041656 | -0.40009 | 0.00015377 | 0.063965 | 0.81172 | -0.034267 | 0.092631 | 0.63948 | 11.5723 | 110.4996 | -11.8607 | 110.17 | -10.4736 | -8.0383 | 17.8986 | 22.8561 | 110.4401 | -11.7508 | 110.257 | -7.8461 | 107.5974 | 98.0072 | -0.12817 | -0.009155 | -0.33875 | 1.2589 | 29.631 | 3.6942 | 29.7592 | 3.8223 | -0.01831 | -0.068665 | -0.25177 | 3.8864 | 109.7397 | 119.3298 | 109.758 | 119.3481 | 1.387 | 122.0306 | 3.9047 | 122.0078 | 122.3602 | 122.1909 | 122.2321 | 122.1725 | -122.3694 | -122.2595 | 121.9025 | 121.9894 | 23.3047 | 34.5886
2647.7656 | 122.2824 | -11.7874 | 110.4355 | -0.094528 | 0.0016983 | 0.063521 | 0.12274 | 0.0048705 | 0.023135 | -0.0048066 | -0.32074 | -0.0028368 | 0.066101 | 0.80788 | -0.034054 | 0.092204 | 0.63564 | 12.5427 | 110.4813 | -11.9064 | 110.3119 | -10.3317 | -8.1207 | 17.926 | 22.6318 | 110.3806 | -11.8149 | 110.2386 | -7.8186 | 107.4234 | 97.9843 | -0.11902 | 0.045776 | -0.1236 | 1.4557 | 29.7134 | 3.6667 | 29.8325 | 3.7857 | -0.027465 | -0.054932 | -0.19684 | 3.9688 | 109.7717 | 119.2108 | 109.7992 | 119.2383 | 1.5747 | 122.2183 | 3.9963 | 122.0535 | 122.3877 | 122.1954 | 122.2687 | 122.168 | -122.3419 | -122.2504 | 122.0993 | 122.0261 | 24.3301 | 34.4193
2648.7656 | 122.2916 | -11.6913 | 110.5133 | -0.10979 | 0.00063028 | 0.061598 | 0.12039 | -0.00068368 | 0.01929 | -0.0037384 | -0.29327 | -0.00091423 | 0.061615 | 0.61326 | -0.030422 | 0.097331 | 0.44273 | 12.8998 | 110.614 | -11.7599 | 110.2798 | -10.437 | -7.9376 | 17.514 | 22.5952 | 110.5453 | -11.6684 | 110.3531 | -8.2443 | 107.6935 | 65.9134 | -0.068665 | 0.10071 | -0.23346 | 1.2543 | 29.2053 | 3.7537 | 29.274 | 3.8223 | 0.022888 | 0.032043 | -0.16022 | 3.447 | 77.6047 | 119.3848 | 77.5818 | 119.3619 | 1.3229 | 122.0398 | 3.4241 | 122.0215 | 122.374 | 122.2137 | 122.3053 | 122.2366 | -122.2733 | -122.1817 | 121.9711 | 122.0444 | 24.5911 | 34.2865
2649.7656 | 122.3831 | -16.7679 | 105.3818 | -0.18608 | 0.021565 | 0.064589 | 0.1221 | 0.0014527 | 0.034885 | -0.00053396 | -0.26886 | -0.0026232 | 0.066742 | 0.59105 | -0.030636 | 0.096049 | 0.42201 | 98.1033 | 105.368 | -17.0013 | 104.9973 | -15.2847 | -11.2015 | 16.3422 | 21.1029 | 105.2582 | -16.9006 | 105.2353 | -13.1561 | 102.7771 | 57.6782 | -0.23346 | -0.013733 | -0.38452 | 1.4832 | 33.11 | 5.5664 | 33.3435 | 5.7999 | -0.13275 | -0.1236 | -0.14648 | 3.6118 | 74.4461 | 119.545 | 74.5789 | 119.6777 | 1.7166 | 121.9986 | 3.7445 | 122.1359 | 122.3694 | 122.1588 | 122.1359 | 122.0261 | -122.3831 | -122.2824 | 121.7651 | 122.0032 | 114.8712 | 37.8708
2650.8281 | 122.4609 | -25.8911 | 96.2128 | -0.17082 | 0.052754 | 0.068648 | 0.11996 | -0.00046988 | 0.057956 | -0.0024566 | -0.15289 | -0.0024096 | 0.06482 | 0.56071 | -0.032345 | 0.092631 | 0.3998 | 91.713 | 96.3547 | -25.9644 | 96.1395 | -22.9568 | -16.3971 | 13.6551 | 18.1595 | 96.2036 | -25.9048 | 96.1716 | -21.7896 | 93.6813 | 47.5204 | -0.073242 | 0.14191 | -0.073243 | 2.9343 | 39.5462 | 9.494 | 39.6194 | 9.5673 | -0.013733 | -0.009156 | -0.041199 | 4.1016 | 73.4116 | 119.5724 | 73.4253 | 119.5862 | 3.0075 | 122.1039 | 4.1153 | 122.0764 | 122.319 | 122.1085 | 122.2458 | 122.0947 | -122.1771 | -122.1176 | 122.0306 | 122.0627 | 117.6041 | 44.0506
2651.7656 | 122.3328 | -47.1725 | 74.9634 | -0.26237 | 0.17067 | 0.081465 | 0.12338 | 0.0055115 | 0.15708 | -0.001175 | -0.29327 | 0.14905 | 0.06781 | 0.446 | -0.031704 | 0.09669 | 0.42564 | 71.4798 | 74.9268 | -47.3694 | 74.7208 | -40.8508 | -18.3334 | 7.2235 | 10.6384 | 74.9268 | -47.2092 | 74.8077 | -41.9907 | 72.3358 | 24.9481 | -0.19684 | -0.036621 | -0.24262 | 6.3217 | 54.3961 | 28.8391 | 54.5929 | 29.0359 | -0.036621 | -0.036621 | -0.15564 | 5.1819 | 72.1207 | 119.5084 | 72.1573 | 119.545 | 6.5186 | 122.0901 | 5.2185 | 122.0169 | 122.2961 | 122.1359 | 122.0993 | 122.0993 | -122.3328 | -122.1725 | 121.8933 | 121.9803 | 118.6523 | 57.811
2652.7656 | 122.3923 | -71.4981 | 50.5783 | -0.52177 | 0.45501 | 0.10347 | 0.12188 | 0.0048705 | 0.40638 | -0.00074776 | -0.13153 | -0.0019824 | 0.068238 | 0.17042 | -0.028072 | 0.098613 | 0.0060883 | 47.4884 | 50.5463 | -71.6949 | 50.3632 | -58.4518 | -6.7108 | -0.7782 | 1.6983 | 50.5646 | -71.6583 | 50.528 | -66.0004 | 48.0469 | -70.166 | -0.19684 | -0.032043 | -0.21515 | 13.0463 | 70.7199 | 64.7873 | 70.9167 | 64.9841 | -0.16022 | -0.013733 | -0.050354 | 5.4977 | 1.3321 | 119.545 | 1.4923 | 119.7052 | 13.2431 | 122.0581 | 5.658 | 122.1863 | 122.2412 | 122.2229 | 122.0444 | 122.0627 | -122.2733 | -122.2366 | 121.8613 | 122.0261 | 118.9865 | 73.1964
2653.7656 | 122.3236 | -39.1067 | 83.0933 | -0.15556 | 0.015156 | 0.08296 | 0.12616 | 0.0052979 | -0.0042084 | -0.0041656 | -0.079651 | -0.0017688 | 0.066101 | 0.17876 | -0.027645 | 0.098613 | 0.0063019 | 81.5323 | 83.1116 | -39.2166 | 83.0154 | -30.7297 | -39.1937 | 9.1278 | 12.8906 | 83.0841 | -39.1479 | 83.0521 | -35.4767 | 80.484 | -38.0539 | -0.10986 | 0.01831 | -0.07782 | 8.3771 | 48.2346 | -0.086976 | 48.3444 | 0.022888 | -0.041199 | -0.009156 | -0.041199 | 3.6301 | 1.0529 | 119.5908 | 1.0941 | 119.632 | 8.4869 | 122.2321 | 3.6713 | 122.2 | 122.3282 | 122.2321 | 122.2183 | 122.1909 | -122.3099 | -122.2412 | 122.1222 | 122.1588 | 120.639 | 51.9974
2654.8281 | 122.3694 | -41.4505 | 80.7678 | -0.17845 | 0.019643 | 0.084669 | 0.12316 | 0.0029479 | 0.002414 | -0.0016022 | -0.088806 | -0.0028368 | 0.066101 | 0.17192 | -0.03149 | 0.098613 | 0.0073701 | 79.3167 | 80.809 | -41.5741 | 80.5527 | -32.6935 | -41.2903 | 8.3588 | 11.7783 | 80.7404 | -41.478 | 80.7495 | -37.6007 | 78.186 | -40.3107 | -0.1236 | 0.041199 | -0.21515 | 8.757 | 49.8093 | 0.16022 | 49.9329 | 0.28381 | -0.027466 | -0.027466 | -0.01831 | 3.8498 | 1.1398 | 119.6365 | 1.1673 | 119.664 | 8.8806 | 122.1268 | 3.8773 | 122.2275 | 122.3831 | 122.2183 | 122.2595 | 122.1909 | -122.3419 | -122.2458 | 122.0032 | 122.2 | 120.7672 | 53.2288
2655.7656 | 122.374 | -42.9794 | 79.2297 | -0.23186 | 0.022206 | 0.087019 | 0.12103 | -0.00025628 | -0.001004 | -0.00010676 | -0.13153 | -0.0028368 | 0.066315 | 0.17534 | -0.027218 | 0.097758 | 0.0095063 | 77.7466 | 79.2526 | -43.1122 | 79.0146 | -33.815 | -42.8192 | 7.8415 | 11.1786 | 79.1885 | -43.0435 | 79.1702 | -39.0701 | 76.6251 | -41.835 | -0.13275 | 0.022889 | -0.21515 | 9.1644 | 50.8209 | 0.16022 | 50.9537 | 0.29297 | -0.064087 | -0.041198 | -0.059509 | 3.9093 | 1.1444 | 119.6045 | 1.2085 | 119.6686 | 9.2972 | 122.1268 | 3.9734 | 122.2137 | 122.3648 | 122.2321 | 122.2321 | 122.168 | -122.3419 | -122.2733 | 121.994 | 122.1497 | 120.726 | 54.158
2656.7656 | 122.4197 | -44.2703 | 77.916 | -0.1403 | 0.023915 | 0.089156 | 0.12231 | 0.0018799 | 0.0013458 | 0.00053404 | -0.20477 | -0.0013416 | 0.065033 | 0.17811 | -0.029354 | 0.098399 | 0.0063019 | 76.4099 | 77.9114 | -44.4305 | 77.7512 | -34.6893 | -44.0277 | 7.5256 | 10.881 | 77.9663 | -44.3161 | 77.8656 | -40.1733 | 75.3754 | -43.1488 | -0.16022 | -0.004578 | -0.16479 | 9.581 | 51.796 | 0.24262 | 51.9562 | 0.40283 | -0.045776 | 0.050354 | -0.050354 | 4.097 | 1.1215 | 119.6457 | 1.1673 | 119.6915 | 9.7412 | 122.1817 | 4.1428 | 122.1817 | 122.3419 | 122.2824 | 122.1817 | 122.2366 | -122.3465 | -122.2321 | 122.0215 | 122.1359 | 120.6802 | 55.1514
2657.7656 | 122.4243 | -46.0464 | 76.1765 | -0.10216 | 0.028615 | 0.089369 | 0.12188 | 0.0033753 | 0.001773 | -0.0035248 | -0.091858 | -0.002196 | 0.067169 | 0.17876 | -0.031063 | 0.099681 | 0.0056611 | 74.6567 | 76.2085 | -46.1792 | 76.0208 | -36.0031 | -45.6985 | 6.9901 | 10.0479 | 76.1215 | -46.0922 | 76.1353 | -41.8167 | 73.6176 | -44.8975 | -0.13275 | 0.032043 | -0.15564 | 10.0433 | 53.0365 | 0.3479 | 53.1692 | 0.48065 | -0.045776 | -0.054932 | -0.041199 | 4.2297 | 1.149 | 119.664 | 1.1948 | 119.7098 | 10.1761 | 122.2 | 4.2755 | 122.2275 | 122.3877 | 122.2137 | 122.2549 | 122.168 | -122.3557 | -122.2687 | 122.0673 | 122.1817 | 120.7031 | 56.0944
2658.8281 | 122.5296 | -47.9141 | 74.2218 | -0.19371 | 0.031819 | 0.095137 | 0.12338 | 0.0016663 | 0.0019866 | -0.002884 | 0.0057984 | -0.0017688 | 0.066956 | 0.17149 | -0.030422 | 0.097545 | 0.010147 | 72.6059 | 74.2584 | -48.0377 | 74.1074 | -37.5366 | -47.6578 | 6.5186 | 9.407 | 74.0662 | -48.0927 | 74.3271 | -43.4692 | 71.8094 | -46.7056 | -0.1236 | 0.036621 | -0.11444 | 10.3775 | 54.4327 | 0.25635 | 54.5563 | 0.37994 | -0.17853 | -0.15564 | 0.10529 | 4.4449 | 1.2085 | 119.7235 | 1.387 | 119.902 | 10.5011 | 122.1451 | 4.6234 | 122.4197 | 122.2961 | 122.1588 | 122.1725 | 121.9803 | -122.2595 | -122.3145 | 122.0215 | 122.2412 | 120.52 | 57.3212
2659.7656 | 122.406 | -49.5575 | 72.6334 | -0.15556 | 0.038014 | 0.099409 | 0.12295 | 0.0025207 | -0.0012176 | -0.002884 | -0.11932 | -0.00070063 | 0.067169 | 0.17534 | -0.029995 | 0.097972 | 0.010788 | 70.871 | 72.6608 | -49.7086 | 72.5098 | -38.4293 | -49.1409 | 5.9006 | 8.7112 | 72.5922 | -49.6857 | 72.6059 | -45.0485 | 70.0882 | -48.4039 | -0.15106 | 0.027466 | -0.1236 | 11.1282 | 55.4581 | 0.41657 | 55.6091 | 0.56763 | -0.12817 | -0.041199 | -0.027466 | 4.509 | 1.1536 | 119.6457 | 1.2817 | 119.7739 | 11.2793 | 122.2183 | 4.6371 | 122.2916 | 122.3694 | 122.2778 | 122.2183 | 122.1497 | -122.3419 | -122.319 | 122.0673 | 122.1634 | 120.4285 | 58.2687
2660.7656 | 122.4472 | -52.0294 | 70.1843 | -0.13267 | 0.045918 | 0.1024 | 0.12146 | -0.00046988 | 0.0015594 | -0.0033112 | -0.088806 | -0.0015552 | 0.06781 | 0.17256 | -0.030209 | 0.097331 | 0.010361 | 68.2892 | 70.1981 | -52.1576 | 70.0424 | -40.0864 | -51.4801 | 5.246 | 7.9605 | 70.1614 | -52.0889 | 70.1385 | -47.3236 | 67.6392 | -50.8026 | -0.12817 | 0.013733 | -0.14191 | 11.9431 | 57.2754 | 0.54932 | 57.4036 | 0.67749 | -0.059509 | -0.022888 | -0.045776 | 4.7058 | 1.2268 | 119.6686 | 1.2863 | 119.7281 | 12.0712 | 122.2 | 4.7653 | 122.2275 | 122.3557 | 122.2504 | 122.2275 | 122.1909 | -122.3419 | -122.2733 | 122.0718 | 122.168 | 120.3186 | 59.9899
2661.8281 | 122.438 | -54.5609 | 67.6529 | -0.079269 | 0.04955 | 0.10774 | 0.12295 | -0.00046988 | 0.004123 | -0.0037384 | -0.052185 | -0.0026232 | 0.068238 | 0.17042 | -0.028927 | 0.096477 | 0.010574 | 65.8127 | 67.717 | -54.7028 | 67.4377 | -41.8671 | -53.9291 | 4.4998 | 6.9305 | 67.6163 | -54.6524 | 67.5705 | -49.6628 | 65.1031 | -53.3203 | -0.14191 | 0.064087 | -0.21515 | 12.6938 | 59.0607 | 0.63171 | 59.2026 | 0.77362 | -0.091553 | -0.036621 | -0.082397 | 4.8981 | 1.2405 | 119.664 | 1.3321 | 119.7556 | 12.8357 | 122.1405 | 4.9896 | 122.2229 | 122.4197 | 122.2687 | 122.2778 | 122.1771 | -122.3557 | -122.3053 | 121.9986 | 122.1313 | 120.3735 | 61.4914
2662.7656 | 122.4564 | -58.4564 | 63.7299 | -0.17845 | 0.064717 | 0.11885 | 0.12188 | 0.0025207 | 0.0039094 | -0.0020294 | -0.012512 | -0.0034778 | 0.07016 | 0.17128 | -0.0285 | 0.097117 | 0.0088653 | 61.9904 | 63.7527 | -58.6121 | 63.6154 | -44.0872 | -58.548 | 3.3417 | 5.5435 | 63.7482 | -58.4885 | 63.7573 | -53.2654 | 61.2442 | -57.1335 | -0.15564 | 0.022889 | -0.11444 | 14.3692 | 61.7981 | -0.091553 | 61.9537 | 0.064087 | -0.032043 | 0.018311 | 0.027466 | 5.191 | 1.3229 | 119.7006 | 1.355 | 119.7327 | 14.5248 | 122.2275 | 5.2231 | 122.2458 | 122.3648 | 122.2366 | 122.2092 | 122.2046 | -122.3419 | -122.2183 | 122.0718 | 122.2137 | 120.4468 | 63.9999
2663.7656 | 122.4335 | -71.0815 | 51.1047 | -0.2166 | 0.1036 | 0.15837 | 0.12381 | -0.00046988 | -0.0035674 | -0.002243 | -0.10101 | -0.001128 | 0.069519 | 0.16957 | -0.029781 | 0.096049 | 0.0082245 | 49.2142 | 51.1505 | -71.2372 | 50.9537 | -52.6154 | -70.8755 | -0.70953 | 0.67291 | 51.0818 | -71.1594 | 51.0544 | -65.0894 | 48.5687 | -69.6579 | -0.15564 | 0.045777 | -0.15106 | 18.4662 | 70.372 | 0.20599 | 70.5276 | 0.36163 | -0.07782 | -0.022888 | -0.050354 | 5.9921 | 1.4236 | 119.6503 | 1.5015 | 119.7281 | 18.6218 | 122.1909 | 6.0699 | 122.2137 | 122.3877 | 122.2412 | 122.2321 | 122.1634 | -122.3419 | -122.2641 | 122.0352 | 122.1359 | 120.2957 | 71.7545
2664.8281 | 122.4014 | -48.0103 | 74.2493 | -0.3463 | 0.21938 | 0.28206 | 0.11975 | 0.0023071 | -0.0029266 | -0.002884 | -0.088806 | -0.0013416 | 0.068878 | 0.17598 | -0.029568 | 0.096904 | 0.0048065 | 71.5897 | 74.1394 | -48.2117 | 73.9197 | -35.2158 | -50.2304 | 6.6696 | 9.1507 | 74.1165 | -48.1476 | 74.1714 | -43.428 | 71.6629 | -46.7743 | -0.20142 | -0.10986 | -0.32959 | 12.7945 | 54.6799 | -2.2202 | 54.8813 | -2.0187 | -0.13733 | -0.13275 | -0.07782 | 4.5822 | 1.236 | 119.6732 | 1.3733 | 119.8105 | 12.9959 | 122.1313 | 4.7195 | 122.319 | 122.3511 | 122.2641 | 122.1497 | 122.1268 | -122.4609 | -122.3969 | 121.9299 | 122.1817 | 119.5999 | 57.1609
2665.7656 | 122.3923 | -59.4589 | 62.9654 | -0.10216 | 0.016865 | 0.061171 | 0.12231 | 0.0057251 | -0.0001496 | -0.002884 | -0.10101 | -0.0017688 | 0.068238 | 0.17662 | -0.031063 | 0.097972 | 0.0050201 | 67.0898 | 66.3666 | -56.282 | 64.3021 | -40.1505 | -55.101 | 7.5668 | 4.4449 | 64.4302 | -58.9188 | 62.5488 | -55.1926 | 59.9213 | -57.9346 | 3.1769 | 3.4012 | 1.3367 | 19.3085 | 67.0258 | 4.3579 | 63.8489 | 1.181 | 0.54016 | 1.4648 | -0.41656 | 4.2664 | 1.5244 | 119.3802 | 0.98419 | 118.84 | 16.1316 | 120.5841 | 3.7262 | 121.4676 | 122.6486 | 123.349 | 125.8255 | 123.8892 | -119.2474 | -121.8842 | 123.761 | 122.0078 | 126.5488 | 63.9038
2666.7656 | 122.4243 | -59.7885 | 62.4252 | -0.10216 | 0.01537 | 0.075484 | 0.12274 | 0.0014527 | 0.0002778 | 0.00032044 | -0.11627 | -0.0013416 | 0.068238 | 0.17641 | -0.029354 | 0.098399 | 0.0058747 | 61.116 | 62.5992 | -59.8526 | 62.1048 | -43.4555 | -59.3399 | 3.2043 | 4.8569 | 62.3566 | -59.8892 | 62.7045 | -54.0985 | 59.9579 | -58.5617 | -0.064087 | 0.17395 | -0.32044 | 16.333 | 62.9929 | 0.44861 | 63.0569 | 0.5127 | -0.10071 | -0.068665 | 0.27924 | 5.69 | 1.2268 | 119.7464 | 1.3275 | 119.8471 | 16.3971 | 121.9574 | 5.7907 | 122.5937 | 122.4518 | 122.2458 | 122.3877 | 122.1451 | -122.2778 | -122.3145 | 121.8933 | 122.493 | 120.9045 | 64.6454
2667.7656 | 122.4518 | -60.7224 | 61.3174 | -0.12505 | 0.017293 | 0.076979 | 0.12081 | -0.0017517 | -0.0012176 | -0.00096136 | -0.0064086 | -0.002196 | 0.068878 | 0.17 | -0.030422 | 0.097758 | 0.011215 | 60.5667 | 61.8256 | -60.6033 | 61.4731 | -43.6935 | -60.3699 | 3.0167 | 4.5868 | 61.6974 | -60.5713 | 61.8851 | -55.0873 | 58.786 | -59.4315 | 0.11902 | 0.50812 | 0.15564 | 17.0288 | 63.739 | 0.35248 | 63.62 | 0.23346 | 0.15106 | 0.37994 | 0.56763 | 5.6351 | 1.2909 | 119.5084 | 1.1398 | 119.3573 | 16.9098 | 122.0764 | 5.484 | 122.4564 | 122.4289 | 122.2687 | 122.5479 | 122.4197 | -121.9208 | -121.8887 | 122.1954 | 122.6074 | 121.2891 | 65.3091
2668.7656 | 122.3785 | -60.7819 | 61.5189 | -0.10979 | 0.019643 | 0.075484 | 0.11996 | 0.0014527 | 0.0019866 | -0.0048066 | -0.088806 | -0.0034778 | 0.068451 | 0.17662 | -0.028713 | 0.098399 | 0.0067291 | 61.3266 | 62.0178 | -60.4248 | 61.5509 | -43.9362 | -60.1089 | 3.4058 | 4.866 | 62.1323 | -60.1273 | 61.8713 | -54.8492 | 58.5388 | -59.7336 | 0.35706 | 0.49896 | 0.032043 | 16.8457 | 64.1876 | 0.67291 | 63.8306 | 0.31586 | 0.6546 | 0.6134 | 0.35248 | 5.9326 | 1.0483 | 119.3207 | 0.39368 | 118.6661 | 16.4886 | 121.9757 | 5.278 | 121.9986 | 122.4426 | 122.2595 | 122.7997 | 122.9141 | -121.9437 | -121.6461 | 122.3328 | 122.6532 | 122.1085 | 65.6479
2669.7656 | 122.4289 | -64.9109 | 57.3029 | -0.1403 | 0.021779 | 0.078261 | 0.12039 | 0.0035889 | 0.0002778 | -0.0024566 | -0.11322 | -0.0019824 | 0.069306 | 0.16658 | -0.029354 | 0.097972 | 0.0099335 | 56.012 | 57.2754 | -65.1443 | 56.7535 | -46.5454 | -64.8605 | 1.8173 | 2.7283 | 57.2662 | -65.0391 | 57.0786 | -59.1385 | 54.5059 | -63.6017 | -0.23346 | -0.027465 | -0.54932 | 18.3655 | 66.7282 | 0.050354 | 66.9617 | 0.28381 | -0.12817 | -0.036621 | -0.2243 | 5.7724 | 1.3092 | 119.4168 | 1.4374 | 119.545 | 18.5989 | 121.8979 | 5.9006 | 122.1176 | 122.4197 | 122.3053 | 122.1863 | 122.1771 | -122.4472 | -122.3419 | 121.6644 | 121.9894 | 120.9229 | 67.6392
2670.7656 | 122.4472 | -67.2501 | 55.0644 | -0.010605 | 0.022847 | 0.076979 | 0.12124 | -4.2682e-05 | 0.0022004 | -0.003952 | -0.085754 | -0.0030506 | 0.068878 | 0.17042 | -0.029781 | 0.096049 | 0.0099335 | 55.5588 | 56.4926 | -65.7578 | 56.2271 | -46.843 | -65.4327 | 0.79651 | 1.7532 | 55.0827 | -67.5476 | 54.8676 | -61.4914 | 52.3865 | -65.7028 | 1.4923 | 1.4282 | 1.1627 | 20.4071 | 68.0466 | 1.8173 | 66.5543 | 0.32501 | -0.29755 | 0.018311 | -0.19684 | 5.7587 | 1.5472 | 119.6365 | 1.8448 | 119.9341 | 18.9148 | 121.9849 | 6.0562 | 122.4152 | 122.2504 | 122.6303 | 123.7427 | 122.3328 | -120.8221 | -122.612 | 123.4772 | 122.1176 | 122.8088 | 69.0033
2671.7656 | 122.438 | -66.156 | 56.0486 | -0.1403 | 0.024556 | 0.079115 | 0.12081 | 0.0012391 | 0.0019866 | -0.002884 | -0.064392 | -0.0034778 | 0.06781 | 0.17299 | -0.029781 | 0.097758 | 0.0056611 | 52.3407 | 53.8101 | -68.6829 | 56.0028 | -46.5866 | -68.3716 | 1.5015 | 2.4582 | 56.0852 | -66.1285 | 56.2454 | -59.9808 | 53.5355 | -64.6591 | -2.5269 | -2.2385 | -0.045776 | 19.5694 | 67.6575 | -2.2156 | 70.1843 | 0.31128 | 0.027466 | 0.036621 | 0.19684 | 6.1752 | 1.4969 | 119.6915 | 1.4694 | 119.664 | 22.0963 | 124.6857 | 6.1478 | 122.374 | 122.493 | 122.2137 | 119.9661 | 122.2412 | -124.7314 | -122.1771 | 122.1588 | 122.4014 | 118.4967 | 68.6142
2672.8281 | 122.5388 | -66.6183 | 55.4993 | -0.22423 | 0.024342 | 0.078261 | 0.12252 | 0.0027343 | 0.0030548 | -0.00032036 | -0.015564 | -0.003905 | 0.068878 | 0.17064 | -0.030209 | 0.097545 | 0.0099335 | 54.4601 | 55.4443 | -66.8793 | 55.5771 | -46.6507 | -66.4444 | 0.96588 | 2.4399 | 55.545 | -66.4764 | 55.5817 | -60.4294 | 53.2883 | -65.0711 | -0.26093 | -0.054932 | 0.077819 | 19.9677 | 67.5842 | 0.17395 | 67.8452 | 0.43488 | 0.14191 | 0.045776 | 0.082397 | 6.189 | 1.5472 | 119.9066 | 1.4053 | 119.7647 | 20.2286 | 122.4564 | 6.0471 | 122.0581 | 122.3236 | 122.0215 | 122.0627 | 122.1634 | -122.3785 | -121.9757 | 122.1954 | 122.2 | 121.0785 | 69.0582
2673.7656 | 122.4747 | -66.6824 | 55.5496 | -0.094528 | 0.02477 | 0.079115 | 0.1221 | 0.0010253 | 0.0004914 | -0.0016022 | -0.088806 | -0.0017688 | 0.069519 | 0.16679 | -0.030209 | 0.097331 | 0.0088653 | 54.4281 | 55.4581 | -66.9342 | 55.3116 | -46.6278 | -66.4307 | 1.0345 | 2.2018 | 55.4581 | -66.7923 | 55.4306 | -60.5438 | 53.1235 | -65.1443 | -0.25177 | -0.091553 | -0.23804 | 20.0546 | 67.717 | 0.25177 | 67.9688 | 0.50354 | -0.10986 | -0.091553 | -0.11902 | 6.1386 | 1.5381 | 119.8059 | 1.6479 | 119.9158 | 20.3064 | 122.2458 | 6.2485 | 122.2229 | 122.3923 | 122.2504 | 122.1405 | 122.1405 | -122.4838 | -122.3419 | 121.994 | 122.113 | 121.1105 | 68.8843
2674.7656 | 122.493 | -68.6554 | 53.7415 | -0.1403 | 0.02541 | 0.079329 | 0.12188 | -0.0017517 | 0.0047638 | -0.0018158 | -0.088806 | -0.0019824 | 0.069733 | 0.1747 | -0.030849 | 0.094127 | 0.010147 | 53.7003 | 54.6433 | -67.7261 | 54.4052 | -47.2092 | -68.7057 | 0.43488 | 1.5656 | 53.8742 | -68.5547 | 53.1967 | -62.7365 | 50.322 | -67.3187 | 0.92926 | 0.90179 | 0.66376 | 21.4462 | 69.0903 | -0.050354 | 68.161 | -0.97961 | 0.10071 | 0.13275 | -0.54474 | 5.9189 | 1.3367 | 118.9774 | 1.236 | 118.8766 | 20.517 | 122.1313 | 5.8182 | 121.7514 | 122.3694 | 122.4289 | 123.2986 | 122.5296 | -121.4676 | -122.2961 | 123.0606 | 121.8521 | 122.3557 | 70.2209
2675.8281 | 122.5159 | -67.9276 | 54.2587 | -0.19371 | 0.026265 | 0.080397 | 0.11953 | -0.0013245 | 0.0011322 | -0.0048066 | 0.0057984 | -0.002196 | 0.06781 | 0.17042 | -0.031063 | 0.096904 | 0.0084381 | 53.2516 | 54.2038 | -68.1793 | 54.2816 | -46.8658 | -66.1423 | 0.62714 | 1.8539 | 54.3274 | -67.8726 | 54.3915 | -61.5463 | 51.8967 | -66.4444 | -0.25177 | -0.054932 | 0.022888 | 21.0617 | 68.5547 | 1.7853 | 68.8065 | 2.037 | 0.054931 | 0.068665 | 0.13275 | 6.3812 | 1.4832 | 119.8242 | 1.4282 | 119.7693 | 21.3135 | 122.4609 | 6.3263 | 122.2641 | 122.3831 | 122.2 | 122.1313 | 122.2549 | -122.438 | -122.1313 | 122.2092 | 122.319 | 121.1792 | 69.7815
2676.7656 | 122.5296 | -67.7948 | 54.5746 | -0.11742 | 0.028401 | 0.08232 | 0.12081 | 0.0031617 | 6.4004e-05 | -0.0018158 | -0.10101 | -0.0013416 | 0.070587 | 0.17085 | -0.032345 | 0.097758 | 0.0060883 | 53.0045 | 53.9978 | -68.3762 | 54.0665 | -46.9482 | -67.63 | 0.58136 | 1.7212 | 54.039 | -68.1931 | 54.4556 | -61.3541 | 52.0615 | -66.0507 | -0.58136 | -0.57678 | -0.50812 | 20.8466 | 68.3762 | 0.16479 | 68.9575 | 0.74616 | -0.39825 | -0.53558 | -0.11902 | 6.4407 | 1.7441 | 119.8563 | 2.1423 | 120.2545 | 21.4279 | 122.4426 | 6.839 | 122.6486 | 122.374 | 122.2321 | 121.7926 | 121.8338 | -122.9507 | -122.7676 | 121.8613 | 122.2504 | 120.7993 | 69.516
2677.7656 | 122.5571 | -68.2755 | 53.9108 | -0.15556 | 0.029469 | 0.082533 | 0.12146 | -0.00089728 | -0.0016448 | -0.00053396 | -0.067444 | -0.0019824 | 0.068665 | 0.17 | -0.029354 | 0.097331 | 0.0080109 | 54.0802 | 55.0095 | -67.3599 | 55.0781 | -46.1975 | -67.424 | 0.7782 | 1.8448 | 55.0552 | -66.6138 | 53.6819 | -62.6495 | 50.7339 | -66.6595 | 0.91553 | 1.0986 | 1.1673 | 22.0779 | 69.0537 | 0.85144 | 68.1381 | -0.064087 | 1.6617 | 1.1444 | -0.22888 | 5.6259 | 1.6159 | 119.0094 | -0.045776 | 117.3477 | 21.1624 | 122.438 | 3.9642 | 120.2957 | 122.3694 | 121.669 | 123.2849 | 123.3307 | -121.2708 | -120.5246 | 123.3536 | 121.9574 | 122.3557 | 70.1202
2678.7656 | 122.4152 | -69.2505 | 53.096 | -0.10979 | 0.027119 | 0.081252 | 0.12081 | 0.0020935 | -0.0005768 | -0.00053396 | -0.052185 | -0.0032642 | 0.07251 | 0.17427 | -0.028713 | 0.096904 | 0.0077973 | 51.8692 | 52.7573 | -69.6579 | 52.4231 | -47.374 | -69.4748 | -0.20142 | 1.1032 | 52.8397 | -69.4748 | 53.6682 | -63.1714 | 50.2258 | -67.5659 | -0.40741 | -0.33874 | -0.67291 | 21.8765 | 69.0491 | -0.2243 | 69.4565 | 0.18311 | -0.2243 | -0.25635 | 0.57221 | 6.0791 | 1.6846 | 119.4763 | 1.9089 | 119.7006 | 22.2839 | 122.081 | 6.3034 | 123.143 | 122.4152 | 122.3145 | 122.0078 | 122.0901 | -122.7539 | -122.5708 | 121.6736 | 122.9187 | 121.1197 | 70.3537
2679.7656 | 122.4014 | -71.3928 | 50.8575 | -0.13267 | 0.03011 | 0.082747 | 0.11761 | 0.0023071 | 0.0013458 | -0.0030976 | -0.11932 | -0.0032642 | 0.069306 | 0.16978 | -0.031277 | 0.095622 | 0.011642 | 50.6424 | 51.3565 | -71.0815 | 50.9766 | -48.2529 | -70.6238 | -0.37994 | 0.44861 | 51.0681 | -71.1548 | 50.6241 | -65.0208 | 48.1018 | -69.8502 | 0.31128 | 0.49896 | 0.11902 | 23.14 | 71.0129 | 0.76904 | 70.7016 | 0.45776 | 0.23804 | 0.21057 | -0.23346 | 6.3721 | 1.5427 | 119.4946 | 1.3046 | 119.2566 | 22.8287 | 122.0581 | 6.134 | 121.7789 | 122.438 | 122.2229 | 122.7493 | 122.4609 | -121.9391 | -122.0123 | 122.3694 | 122.0169 | 122.0352 | 71.8414
2680.7656 | 122.4518 | -72.0062 | 50.2213 | -0.10216 | 0.035237 | 0.084883 | 0.1221 | 0.0027343 | -0.0001496 | -0.0016022 | -0.088806 | -0.0045458 | 0.071442 | 0.17576 | -0.029995 | 0.097117 | 0.01271 | 49.9466 | 50.235 | -72.0932 | 50.3082 | -48.6511 | -71.5256 | -0.78735 | 0.13733 | 50.2304 | -72.0566 | 50.2487 | -65.1306 | 47.818 | -70.4498 | -0.086975 | 0.013733 | 0.086976 | 23.3551 | 71.2189 | 0.48065 | 71.3058 | 0.56763 | -0.050354 | 0.009156 | 0.027466 | 6.8756 | 1.5564 | 119.8242 | 1.6068 | 119.8746 | 23.4421 | 122.4014 | 6.926 | 122.3053 | 122.3282 | 122.287 | 122.2412 | 122.2366 | -122.3145 | -122.2778 | 122.3145 | 122.2549 | 121.9528 | 72.1436
2681.7656 | 122.4701 | -72.4274 | 49.7543 | -0.14793 | 0.039937 | 0.08531 | 0.12338 | 0.0050843 | 0.0036956 | -0.002884 | -0.10712 | 0.0010084 | 0.070374 | 0.17149 | -0.029568 | 0.097331 | 0.0052337 | 50.1938 | 50.4959 | -71.7636 | 50.528 | -48.143 | -81.7245 | -0.33875 | 0.018311 | 50.2396 | -72.1252 | 49.8047 | -65.4556 | 47.3648 | -70.903 | 0.66376 | 0.74158 | 0.77362 | 24.2844 | 72.0886 | -9.2972 | 71.4249 | -9.9609 | 0.30212 | 0.48523 | 0.050354 | 6.9717 | 1.5244 | 119.7922 | 1.2222 | 119.4901 | 23.6206 | 122.2916 | 6.6696 | 121.9299 | 122.2595 | 122.3648 | 122.9233 | 122.6669 | -121.5179 | -121.8796 | 122.9553 | 122.2321 | 122.6212 | 72.4457
2682.7656 | 122.4472 | -73.7457 | 48.5046 | -0.18608 | 0.038014 | 0.089156 | 0.12039 | 0.0025207 | 0.000705 | -0.0026704 | -0.067444 | -0.0024096 | 0.068878 | 0.17085 | -0.028713 | 0.09669 | 0.010361 | 47.8317 | 48.4039 | -73.97 | 48.0789 | -49.5255 | -74.8764 | -1.2131 | -0.53101 | 48.3582 | -73.8556 | 48.4406 | -66.9067 | 45.9595 | -72.1619 | -0.2243 | -0.10071 | -0.42572 | 24.2203 | 72.5327 | -1.1307 | 72.757 | -0.90637 | -0.10986 | -0.14648 | -0.064087 | 6.839 | 1.5839 | 119.7052 | 1.6937 | 119.8151 | 24.4446 | 122.049 | 6.9489 | 122.2961 | 122.374 | 122.2137 | 122.1497 | 122.1039 | -122.4747 | -122.3602 | 121.8246 | 122.1863 | 121.5775 | 73.2147
2683.7656 | 122.4838 | -74.2538 | 48.0103 | -0.19371 | 0.040578 | 0.091933 | 0.11975 | 0.0050843 | 0.0028412 | -0.0041656 | -0.11932 | -0.0030506 | 0.07016 | 0.1685 | -0.030422 | 0.095195 | 0.0088653 | 47.5616 | 48.848 | -73.8144 | 48.5962 | -48.6237 | -73.2605 | -1.2177 | -1.1261 | 48.0515 | -74.4278 | 47.6212 | -67.1127 | 45.7764 | -72.5327 | 0.43945 | 0.83771 | 0.58594 | 25.6302 | 73.0362 | 0.99335 | 72.5967 | 0.55389 | -0.17395 | 0.041199 | -0.3891 | 7.1411 | 1.7212 | 120.0302 | 1.8951 | 120.2042 | 25.1907 | 122.4106 | 7.3151 | 122.049 | 122.6624 | 122.4792 | 123.1018 | 122.3053 | -121.8246 | -122.438 | 122.85 | 121.875 | 121.8155 | 73.1277
2684.7656 | 122.4655 | -75.1694 | 47.0627 | -0.086899 | 0.043355 | 0.090865 | 0.12124 | 0.0027343 | 0.0019866 | -0.0018158 | -0.049133 | -0.0032642 | 0.070801 | 0.16637 | -0.029995 | 0.097331 | 0.010574 | 45.0623 | 46.6782 | -76.0483 | 46.907 | -49.4385 | -74.3362 | -1.355 | -1.0757 | 46.9849 | -75.2747 | 46.8842 | -68.0008 | 44.7235 | -73.4985 | -0.87891 | -0.38452 | -0.15564 | 25.7309 | 73.8144 | 0.83313 | 74.6933 | 1.712 | -0.10529 | -0.07782 | -0.17853 | 7.1686 | 1.6708 | 119.8929 | 1.7761 | 119.9982 | 26.6098 | 122.9553 | 7.2739 | 122.1588 | 122.7264 | 122.2595 | 121.8475 | 122.1542 | -123.111 | -122.3373 | 122.0764 | 122.0535 | 120.2316 | 74.0936
2685.7656 | 122.4884 | -75.0092 | 47.2733 | -0.12505 | 0.045918 | 0.095137 | 0.12295 | 0.0025207 | 0.005191 | -0.0020294 | -0.064392 | -0.0019824 | 0.071869 | 0.16743 | -0.029781 | 0.098826 | 0.011642 | 46.0052 | 46.6965 | -75.7095 | 46.8201 | -49.2188 | -75.6912 | -1.4786 | -1.1719 | 46.9849 | -75.2838 | 47.1313 | -67.7444 | 44.7693 | -73.3704 | -0.70038 | -0.57678 | -0.45319 | 25.7904 | 73.5306 | -0.68207 | 74.231 | 0.018311 | -0.27466 | -0.28839 | -0.14191 | 7.2647 | 1.6388 | 119.7784 | 1.9135 | 120.0531 | 26.4908 | 122.5296 | 7.5394 | 122.4152 | 122.406 | 122.2687 | 121.7056 | 121.994 | -122.9828 | -122.5571 | 121.8292 | 122.1405 | 121.0144 | 73.8373
2686.7656 | 122.5479 | -76.9547 | 45.1813 | -0.51414 | 0.22109 | 0.10005 | 0.11825 | 0.0052979 | 0.17374 | -0.00053396 | -0.055237 | -0.0015552 | 0.071442 | 0.17235 | -0.032131 | 0.09434 | 0.0099335 | 42.7917 | 45.2728 | -77.0279 | 45.2866 | -49.7589 | -23.7717 | -1.799 | -1.6663 | 45.1904 | -77.0279 | 45.3049 | -69.5663 | 42.8284 | -75.2472 | -0.073242 | 0.091553 | 0.10529 | 27.1957 | 75.1556 | 53.183 | 75.2289 | 53.2562 | -0.073242 | 0.009156 | 0.1236 | 7.3883 | 1.7075 | 119.783 | 1.7807 | 119.8563 | 27.269 | 122.3145 | 7.4615 | 122.3328 | 122.3007 | 122.2183 | 122.2275 | 122.1451 | -122.2092 | -122.2092 | 122.2412 | 122.2595 | 119.7464 | 75.2884
2687.7656 | 122.5113 | -77.1469 | 45.0485 | -0.094528 | 0.063435 | 0.10069 | 0.12381 | 0.00038452 | 0.0090362 | -0.0016022 | -0.079651 | 0.00079477 | 0.072937 | 0.17277 | -0.031277 | 0.096049 | 0.0069427 | 43.3548 | 45.2179 | -77.211 | 45.2637 | -49.4431 | -75.0961 | -2.0187 | -1.6113 | 45.369 | -76.9363 | 45.0348 | -69.7174 | 42.6315 | -75.4623 | -0.064087 | 0.16937 | 0.21515 | 27.7039 | 75.1282 | 2.0508 | 75.1923 | 2.1149 | 0.21057 | 0.32043 | -0.013733 | 7.4295 | 1.6846 | 119.7784 | 1.474 | 119.5679 | 27.7679 | 122.4747 | 7.2189 | 121.9711 | 122.4289 | 122.3053 | 122.3648 | 122.5159 | -122.2595 | -121.9849 | 122.4106 | 122.1817 | 120.5017 | 75.5356
2688.7656 | 122.4564 | -78.5843 | 43.6478 | -0.17845 | 0.061513 | 0.10475 | 0.12081 | 0.0048705 | 0.0049774 | -0.0054474 | -0.10101 | -0.00070063 | 0.072724 | 0.18111 | -0.030422 | 0.097117 | 0.02211 | 40.5441 | 43.6249 | -78.7674 | 43.4875 | -50.0977 | -77.6367 | -2.7283 | -2.4307 | 43.5562 | -78.7354 | 43.6111 | -71.0724 | 41.1392 | -75.444 | -0.1831 | -0.022888 | -0.16022 | 28.4866 | 75.856 | 0.94757 | 76.0391 | 1.1307 | -0.15106 | -0.091553 | -0.036621 | 7.5119 | 3.1403 | 119.7235 | 3.2913 | 119.8746 | 28.6697 | 122.2549 | 7.663 | 122.3465 | 122.3923 | 122.2916 | 122.2092 | 122.1405 | -122.4152 | -122.3831 | 122.0718 | 122.1954 | 119.1284 | 76.1536
2689.7656 | 122.438 | -79.0924 | 43.1717 | -0.17845 | 0.068562 | 0.11415 | 0.12231 | 0.0027343 | 0.005191 | -0.0030976 | -0.11017 | -0.00091423 | 0.073578 | 0.17363 | -0.030849 | 0.097758 | 0.010147 | 40.3793 | 43.2724 | -79.1748 | 43.0573 | -49.498 | -78.0533 | -2.7969 | -2.3666 | 43.364 | -78.9551 | 42.9474 | -71.5988 | 40.7318 | -77.2751 | -0.082398 | 0.10071 | -0.11444 | 29.5944 | 76.2955 | 1.0391 | 76.3779 | 1.1215 | 0.13733 | 0.19226 | -0.2243 | 7.4936 | 1.8173 | 119.8242 | 1.68 | 119.6869 | 29.6768 | 122.2321 | 7.3563 | 121.9025 | 122.4472 | 122.319 | 122.3648 | 122.4564 | -122.3465 | -122.1268 | 122.1497 | 122.0398 | 119.4717 | 76.7258
2690.8281 | 122.4884 | -80.2094 | 42.0044 | -0.19371 | 0.093983 | 0.12718 | 0.12274 | 0.00017092 | 0.014163 | -0.0058746 | -0.085754 | -0.00070063 | 0.073151 | 0.16551 | -0.029995 | 0.095622 | 0.0099335 | 39.299 | 42.1005 | -80.3055 | 41.9724 | -49.6674 | -77.8976 | -3.2043 | -3.2364 | 42.0914 | -79.9393 | 42.0044 | -72.4777 | 39.4821 | -78.4149 | -0.09613 | 0.09613 | -0.032044 | 30.542 | 77.005 | 2.3117 | 77.1011 | 2.4078 | 0.27008 | 0.086975 | 0 | 7.7316 | 1.7944 | 119.6915 | 1.5244 | 119.4214 | 30.6381 | 122.2778 | 7.4615 | 121.9437 | 122.406 | 122.0306 | 122.3099 | 122.3007 | -122.3099 | -121.9437 | 122.1817 | 122.2137 | 119.5084 | 76.973
2691.7656 | 122.5342 | -78.9597 | 43.19 | -0.43022 | 0.15102 | 0.19554 | 0.12188 | 0.00081172 | 0.0071136 | -0.00010676 | -0.058289 | -0.0045458 | 0.069519 | 0.1685 | -0.029995 | 0.096049 | 0.010361 | 39.5325 | 43.0801 | -79.2435 | 43.1625 | -48.2986 | -77.774 | -2.7191 | -2.6917 | 43.1122 | -79.0741 | 43.3044 | -71.1594 | 40.8142 | -77.1469 | -0.28381 | -0.10986 | -0.027465 | 30.661 | 76.2405 | 1.1856 | 76.5244 | 1.4694 | -0.11444 | -0.077819 | 0.11444 | 7.8003 | 1.8127 | 119.7739 | 1.9272 | 119.8883 | 30.9448 | 122.406 | 7.9147 | 122.3785 | 122.3236 | 122.1863 | 122.0398 | 122.0718 | -122.4335 | -122.2641 | 122.1222 | 122.2641 | 118.4921 | 76.268
2692.7656 | 122.4426 | -61.1343 | 61.1069 | -0.094528 | 0.027333 | 0.080824 | 0.12081 | 0.0016663 | 0.0030548 | -0.00053396 | -0.10406 | -0.0017688 | 0.070587 | 0.16722 | -0.032558 | 0.095836 | 0.0095063 | 60.1959 | 61.2213 | -61.2854 | 59.491 | -38.3652 | -60.6125 | 3.2822 | 4.9301 | 61.6287 | -60.8047 | 60.5988 | -55.0186 | 58.9096 | -59.0836 | -0.15106 | 0.11444 | -1.6159 | 22.7692 | 64.4165 | 0.52185 | 64.5676 | 0.67291 | 0.32959 | 0.52185 | -0.50812 | 6.1157 | 2.0508 | 120.0439 | 1.7212 | 119.7144 | 22.9202 | 120.7764 | 5.7861 | 121.4035 | 122.5067 | 122.4335 | 122.3557 | 122.7631 | -122.3923 | -121.9116 | 120.6253 | 121.7331 | 121.3303 | 66.0645
2693.7656 | 122.5616 | -107.2586 | 14.9689 | -0.22423 | 0.069417 | 0.096632 | 0.12359 | 0.0031617 | 0.011172 | -0.002884 | -0.10101 | -0.0036914 | 0.076996 | 0.16978 | -0.030422 | 0.097117 | 0.0086517 | 11.8103 | 14.9048 | -106.7139 | 14.4928 | -62.3795 | -106.4713 | -12.2086 | -14.4653 | 14.7629 | -107.4509 | 14.859 | -97.1237 | 12.4603 | -105.1575 | 0.54474 | -0.064087 | -0.47607 | 44.8792 | 95.05 | 0.78735 | 94.5053 | 0.24261 | -0.19226 | -0.20599 | -0.10986 | 10.1349 | 2.1011 | 119.7189 | 2.2934 | 119.9112 | 44.3344 | 121.2067 | 10.3271 | 122.3099 | 121.6187 | 122.2137 | 122.1634 | 122.0215 | -121.6827 | -122.4197 | 121.7514 | 122.1176 | 119.0689 | 92.7933
2694.7656 | 122.4792 | -108.2291 | 9.375 | -0.36919 | 0.24587 | 0.26091 | 0.12124 | -0.0015381 | 0.013522 | -0.0013886 | -0.085754 | -0.0028368 | 0.074005 | 0.17042 | -0.029781 | 0.098185 | 0.012924 | 32.1259 | 44.5541 | -76.2314 | 45.369 | -44.8746 | -84.6313 | -7.3242 | -16.658 | 34.8862 | -100.9598 | 13.5452 | -98.3551 | 11.1649 | -105.899 | 31.9977 | 35.1791 | 35.994 | 63.3545 | 100.9048 | 23.5977 | 68.9072 | -8.4 | 7.2693 | 25.5112 | 4.1702 | 9.874 | 2.33 | 119.3939 | -4.9393 | 112.1246 | 31.3568 | 121.6003 | 2.6047 | 114.505 | 120.7855 | 135.8459 | 152.7832 | 143.1152 | -85.6064 | -110.3348 | 153.598 | 121.7743 | 140.3549 | 91.571
2695.7656 | 122.5113 | -107.3822 | 14.8544 | -0.20134 | 0.096547 | 0.0977 | 0.12252 | -0.0015381 | 0.032535 | -0.0030976 | -0.088806 | -0.0024096 | 0.07251 | 0.17213 | -0.029354 | 0.097117 | 0.0071563 | 10.3867 | 14.9323 | -107.4829 | 14.7217 | -58.7448 | -101.4359 | -11.7874 | -14.566 | 14.9048 | -107.428 | 14.7903 | -97.2702 | 12.3642 | -105.2399 | -0.10071 | 0.07782 | -0.13275 | 48.6374 | 95.5948 | 5.9464 | 95.6955 | 6.0471 | -0.045777 | 0.050354 | -0.064087 | 10.112 | 2.1423 | 119.7464 | 2.1881 | 119.7922 | 48.7381 | 122.2046 | 10.1578 | 122.2183 | 122.4152 | 122.3328 | 122.3145 | 122.287 | -122.3373 | -122.2824 | 122.1039 | 122.1725 | 117.7689 | 92.8162
2696.7656 | 122.5845 | -108.5495 | 13.8748 | -0.30052 | 0.15957 | 0.10304 | 0.12124 | 0.0010253 | 0.084659 | -0.0026704 | 0.014954 | -0.001128 | 0.076355 | 0.16487 | -0.029781 | 0.096904 | 0.011215 | 4.6783 | 10.3546 | -112.0148 | 10.1669 | -59.7748 | -97.8058 | -12.941 | -16.2781 | 10.2997 | -111.9644 | 12.6205 | -98.8495 | 10.8994 | -106.5674 | -3.4653 | -3.5202 | -3.7079 | 48.7747 | 95.6085 | 10.7437 | 99.0738 | 14.209 | -3.4149 | -3.5751 | -1.2543 | 9.7 | 1.9821 | 119.4489 | 5.397 | 122.8638 | 52.24 | 122.1817 | 13.1149 | 124.585 | 122.3694 | 122.2641 | 118.9041 | 118.8492 | -125.8896 | -125.8392 | 118.7164 | 121.17 | 113.2278 | 92.2714
2697.7656 | 122.6166 | -113.3011 | 9.0225 | -0.23949 | 0.17751 | 0.11287 | 0.12167 | 0.0023071 | 0.088931 | -0.0013886 | -0.088806 | -0.0019824 | 0.073792 | 0.17021 | -0.029781 | 0.095836 | 0.01271 | 4.6143 | 9.2743 | -109.8221 | 8.9264 | -58.8318 | -110.2203 | -13.2797 | -16.8869 | 9.1049 | -113.2645 | 8.8348 | -102.562 | 6.4178 | -111.1542 | 3.479 | 0.25177 | -0.09613 | 54.4693 | 100.0214 | 3.0807 | 96.5424 | -0.39825 | 0.036621 | 0.082397 | -0.18768 | 10.7391 | 2.1469 | 119.7189 | 2.1103 | 119.6823 | 50.9903 | 118.7485 | 10.7025 | 122.0993 | 119.0964 | 122.3694 | 122.5754 | 122.406 | -118.8446 | -122.287 | 122.2275 | 122.1359 | 117.9153 | 96.4142
2698.7656 | 122.4243 | -108.5037 | 13.765 | -0.6591 | 0.52721 | 0.11159 | 0.11996 | -0.00089728 | 0.44867 | 0.0024566 | -0.070496 | -0.0034778 | 0.075073 | 0.17064 | -0.029568 | 0.099681 | 0.010361 | 10.9177 | 13.829 | -108.5083 | 13.5956 | -65.181 | -37.088 | -12.4649 | -15.2939 | 13.7558 | -108.5587 | 13.6871 | -98.0301 | 11.2885 | -106.2561 | -0.004578 | 0.064087 | -0.16937 | 43.3228 | 96.0388 | 71.4157 | 96.0434 | 71.4203 | -0.054932 | -0.009156 | -0.07782 | 10.4736 | 2.2476 | 119.7922 | 2.3026 | 119.8471 | 43.3273 | 122.1039 | 10.5286 | 122.2458 | 122.3373 | 122.3145 | 122.3328 | 122.2595 | -122.2733 | -122.3236 | 122.0993 | 122.1909 | 119.4214 | 93.2098
2699.8281 | 122.4655 | -108.3847 | 13.7833 | -0.77354 | 0.61202 | 0.12996 | 0.11889 | 0.0027343 | 0.51575 | -0.0026704 | -0.058289 | -0.0015552 | 0.074433 | 0.16167 | -0.029354 | 0.097331 | 0.0097199 | 11.1557 | 13.7329 | -108.5449 | 13.5773 | -54.2999 | -27.0447 | -11.2335 | -15.4083 | 13.765 | -108.4808 | 13.7558 | -97.879 | 11.3525 | -106.1508 | -0.16022 | -0.050354 | -0.20599 | 54.0848 | 97.1512 | 81.34 | 97.3114 | 81.5002 | -0.09613 | -0.01831 | -0.027466 | 10.5057 | 2.2339 | 119.7372 | 2.33 | 119.8334 | 54.245 | 122.1222 | 10.6018 | 122.2366 | 122.2778 | 122.2458 | 122.1176 | 122.1497 | -122.3282 | -122.2641 | 121.962 | 122.1405 | 119.5404 | 92.9764
2700.7656 | 122.3694 | -110.9756 | 11.2564 | -0.75066 | 0.61544 | 0.093855 | 0.12124 | -0.0032471 | 0.55463 | 0.00010684 | -0.088806 | -0.0032642 | 0.073578 | 0.16615 | -0.02914 | 0.096477 | 0.0092927 | 8.6655 | 11.1923 | -111.0809 | 11.0092 | -54.3961 | -23.2773 | -11.9659 | -16.3284 | 11.2335 | -111.0489 | 11.1008 | -100.2136 | 8.6838 | -108.7189 | -0.10529 | -0.064087 | -0.24719 | 56.5796 | 99.0097 | 87.6984 | 99.115 | 87.8037 | -0.073242 | -0.022888 | -0.15564 | 10.762 | 2.2568 | 119.6594 | 2.33 | 119.7327 | 56.6849 | 122.0901 | 10.8353 | 122.1497 | 122.2733 | 122.2824 | 122.168 | 122.2092 | -122.3373 | -122.3053 | 121.9849 | 122.0764 | 119.6411 | 94.6472
2701.7656 | 122.4014 | -111.4609 | 10.7529 | -0.78117 | 0.63872 | 0.097273 | 0.11975 | -0.00025628 | 0.57791 | -0.0041656 | 0.0057984 | -0.0017688 | 0.07251 | 0.1653 | -0.031277 | 0.096477 | 0.013779 | 8.2214 | 10.6934 | -111.438 | 10.5469 | -53.627 | -19.5511 | -12.0438 | -16.4474 | 10.7208 | -111.4883 | 10.643 | -100.5157 | 8.2809 | -109.1125 | 0.022888 | -0.05951 | -0.20599 | 57.8339 | 99.4171 | 91.9098 | 99.3942 | 91.8869 | -0.027466 | -0.032044 | -0.10986 | 10.9451 | 2.3483 | 119.7418 | 2.3758 | 119.7693 | 57.811 | 121.9849 | 10.9726 | 122.1313 | 122.1313 | 122.2092 | 122.1542 | 122.1817 | -122.1909 | -122.2412 | 122.0078 | 122.1039 | 119.6823 | 95.0134
2702.8281 | 122.374 | -111.5112 | 10.7117 | -0.81169 | 0.65004 | 0.093428 | 0.12081 | -0.0013245 | 0.58731 | -0.00053396 | -0.10406 | -0.0013416 | 0.073792 | 0.17 | -0.029995 | 0.096477 | 0.014206 | 8.3359 | 10.6293 | -111.6486 | 10.3867 | -53.0869 | -17.276 | -12.1307 | -16.5573 | 10.6796 | -111.5707 | 10.5331 | -100.5432 | 8.1573 | -109.2087 | -0.13733 | -0.082398 | -0.32501 | 58.4244 | 99.3805 | 94.2352 | 99.5178 | 94.3726 | -0.05951 | -0.032044 | -0.17853 | 10.968 | 2.3026 | 119.6686 | 2.3621 | 119.7281 | 58.5617 | 122.0352 | 11.0275 | 122.1039 | 122.2778 | 122.2504 | 122.1405 | 122.1909 | -122.3602 | -122.2824 | 121.8979 | 122.0444 | 119.8471 | 94.9539
2703.7656 | 122.3007 | -112.4817 | 9.6954 | -0.81169 | 0.70302 | 0.095351 | 0.12338 | 0.0040161 | 0.64115 | -0.00096136 | -0.10406 | -0.00070063 | 0.07721 | 0.16978 | -0.02914 | 0.097117 | 0.011856 | 7.3151 | 9.6268 | -112.5458 | 9.3933 | -53.0319 | -10.3638 | -12.355 | -16.7404 | 9.6634 | -112.5641 | 9.5123 | -101.3947 | 7.1777 | -110.1974 | -0.064087 | -0.068665 | -0.30212 | 59.4498 | 100.1266 | 102.1179 | 100.1907 | 102.182 | -0.082398 | -0.032044 | -0.18311 | 11.087 | 2.2842 | 119.6594 | 2.3666 | 119.7418 | 59.5139 | 121.9391 | 11.1694 | 122.0764 | 122.1725 | 122.2275 | 122.1085 | 122.1451 | -122.2412 | -122.2595 | 121.875 | 121.994 | 119.7968 | 95.7413
2704.7656 | 122.319 | -112.674 | 9.5169 | -0.7888 | 0.70495 | 0.094923 | 0.1221 | 0.0044433 | 0.64243 | -0.004593 | -0.10406 | -0.0013416 | 0.075287 | 0.17512 | -0.031704 | 0.096904 | 0.01207 | 7.077 | 9.4528 | -112.738 | 9.2285 | -52.6382 | -10.0296 | -12.1765 | -16.8961 | 9.4757 | -112.7197 | 9.3521 | -101.5503 | 6.9717 | -110.3577 | -0.064087 | -0.064087 | -0.28839 | 60.0357 | 100.4974 | 102.6443 | 100.5615 | 102.7084 | -0.045777 | -0.041199 | -0.16479 | 11.1237 | 2.3163 | 119.6457 | 2.3621 | 119.6915 | 60.0998 | 121.9666 | 11.1694 | 122.0718 | 122.1909 | 122.1954 | 122.1268 | 122.1497 | -122.2549 | -122.2366 | 121.9025 | 122.0261 | 119.751 | 95.7779
2705.7656 | 122.3373 | -112.706 | 9.4574 | -0.7888 | 0.70409 | 0.098128 | 0.12188 | 0.0016663 | 0.64392 | -0.00096136 | -0.14984 | -0.0032642 | 0.077423 | 0.16658 | -0.030849 | 0.098399 | 0.0075837 | 6.9672 | 9.3842 | -112.8479 | 9.1827 | -51.9516 | -9.6497 | -12.1078 | -16.8182 | 9.3979 | -112.8159 | 9.2789 | -101.5091 | 6.8985 | -110.408 | -0.14191 | -0.073242 | -0.27466 | 60.7544 | 100.5981 | 103.0563 | 100.7401 | 103.1982 | -0.10986 | -0.059509 | -0.17853 | 11.1969 | 2.298 | 119.6045 | 2.4078 | 119.7144 | 60.8963 | 122.0306 | 11.3068 | 122.0947 | 122.2321 | 122.2137 | 122.0901 | 122.1039 | -122.3053 | -122.2733 | 121.8887 | 121.9849 | 119.6732 | 95.8878
2706.7656 | 122.2183 | -84.3201 | 37.8296 | -2.6122 | 2.5487 | 1.9981 | 0.12017 | 0.0023071 | 0.5463 | -0.005661 | -0.10406 | -0.0034778 | 0.072083 | 0.17448 | -0.030422 | 0.097758 | 0.01207 | 33.5632 | 37.5229 | -84.4528 | 37.4359 | -39.4135 | 2.9388 | -2.8381 | -5.5069 | 37.532 | -84.5993 | 37.7838 | -75.5402 | 34.9182 | -82.3608 | -0.13275 | -0.3067 | -0.39368 | 44.9066 | 81.4819 | 87.2589 | 81.6147 | 87.3917 | -0.27924 | -0.29755 | -0.045777 | 8.7799 | 1.9592 | 119.2383 | 2.2385 | 119.5175 | 45.0394 | 121.8887 | 9.0591 | 122.3831 | 121.9757 | 122.1313 | 121.843 | 121.8521 | -122.2824 | -122.4289 | 121.756 | 122.1039 | 117.8833 | 78.8132
2707.7656 | 122.3007 | -113.8504 | 8.1985 | -0.88799 | 0.73272 | 0.10603 | 0.11911 | -0.0017517 | 0.6576 | -0.0048066 | -0.082703 | -0.0026232 | 0.075928 | 0.16679 | -0.029995 | 0.094127 | 0.010788 | 5.8365 | 8.1024 | -114.0976 | 7.8918 | -51.329 | -7.8827 | -12.4329 | -17.0334 | 8.2443 | -113.9877 | 8.075 | -102.562 | 5.6808 | -111.5524 | -0.24719 | -0.09613 | -0.3067 | 62.5214 | 101.4175 | 105.9677 | 101.6647 | 106.2149 | -0.13733 | 0.045777 | -0.1236 | 11.2885 | 2.298 | 119.5312 | 2.4353 | 119.6686 | 62.7686 | 121.9894 | 11.4258 | 122.0627 | 122.2 | 122.2321 | 121.9528 | 122.0947 | -122.2961 | -122.1863 | 121.7422 | 121.9254 | 119.6869 | 96.817
2708.7656 | 122.3145 | -113.9328 | 8.1894 | -0.7888 | 0.73079 | 0.10133 | 0.11911 | -0.00068368 | 0.65973 | -0.0035248 | -0.079651 | -0.0017688 | 0.077637 | 0.17021 | -0.029354 | 0.10096 | 0.015488 | 5.6717 | 8.0521 | -114.1022 | 7.8644 | -50.1801 | -7.3837 | -12.3734 | -16.983 | 8.1345 | -114.0518 | 8.1116 | -102.4887 | 5.722 | -111.5433 | -0.16937 | -0.13733 | -0.32501 | 63.7527 | 101.5594 | 106.5491 | 101.7288 | 106.7184 | -0.11902 | -0.054932 | -0.07782 | 11.4441 | 2.3895 | 119.6548 | 2.5085 | 119.7739 | 63.9221 | 121.9666 | 11.5631 | 122.1634 | 122.1542 | 122.1863 | 121.9849 | 122.0673 | -122.2916 | -122.2412 | 121.7972 | 122.0444 | 119.6045 | 96.9498
2709.7656 | 122.3099 | -113.9832 | 8.1436 | -0.79643 | 0.73656 | 0.10304 | 0.11868 | -0.00089728 | 0.65845 | -0.00074776 | -0.06134 | -0.0026232 | 0.076782 | 0.16978 | -0.03149 | 0.097758 | 0.0065155 | 5.6442 | 8.0704 | -114.1159 | 7.8506 | -49.3469 | -6.9855 | -12.2681 | -17.0883 | 8.1116 | -114.0747 | 7.9697 | -102.4246 | 5.5893 | -111.5753 | -0.13275 | -0.073242 | -0.29297 | 64.6362 | 101.7151 | 106.9977 | 101.8478 | 107.1304 | -0.091553 | -0.032044 | -0.17395 | 11.5585 | 2.4078 | 119.5724 | 2.4994 | 119.664 | 64.769 | 121.9666 | 11.6501 | 122.0444 | 122.1863 | 122.1863 | 122.0535 | 122.0947 | -122.2595 | -122.2183 | 121.8338 | 121.9528 | 119.6274 | 96.8948
2710.7656 | 122.3053 | -114.006 | 8.1116 | -0.87273 | 0.73635 | 0.10261 | 0.12188 | 0.0072205 | 0.65824 | -0.00032036 | -0.06134 | -0.0019824 | 0.075287 | 0.17064 | -0.030636 | 0.096263 | 0.01506 | 5.571 | 8.0338 | -114.1525 | 7.901 | -48.4817 | -6.8298 | -12.2726 | -15.8295 | 8.107 | -114.0564 | 7.9605 | -102.2781 | 5.5893 | -111.5753 | -0.14649 | -0.07782 | -0.21057 | 65.5243 | 101.7334 | 107.1762 | 101.8799 | 107.3227 | -0.050354 | -0.004577 | -0.15106 | 11.7279 | 2.4307 | 119.5953 | 2.4811 | 119.6457 | 65.6708 | 122.0535 | 11.7783 | 122.0169 | 122.1863 | 122.1634 | 122.0398 | 122.113 | -122.2641 | -122.168 | 121.907 | 121.9666 | 119.577 | 98.1766
2711.7656 | 122.2595 | -114.0701 | 8.0521 | -0.83458 | 0.73485 | 0.10496 | 0.12081 | 0.0020935 | 0.66037 | 0.00010684 | -0.079651 | -0.00091423 | 0.07721 | 0.16786 | -0.028927 | 0.096049 | 0.013138 | 5.4199 | 8.0612 | -114.2029 | 7.663 | -48.3856 | -6.7657 | -12.3825 | -16.0217 | 7.9926 | -114.1983 | 7.8461 | -102.2644 | 5.4657 | -111.6486 | -0.13275 | 0.009155 | -0.3891 | 65.6845 | 101.6876 | 107.3044 | 101.8204 | 107.4371 | -0.12817 | -0.059509 | -0.20599 | 11.8057 | 2.4216 | 119.5358 | 2.5497 | 119.664 | 65.8173 | 121.8658 | 11.9339 | 122.0444 | 122.2641 | 122.1909 | 122.1313 | 122.0627 | -122.2549 | -122.2504 | 121.7331 | 121.9162 | 119.4901 | 98.0484
2712.7656 | 122.2824 | -114.1205 | 8.02 | -0.89561 | 0.7528 | 0.12269 | 0.11718 | -0.00046988 | 0.65995 | -0.0024566 | -0.06134 | -0.001128 | 0.076569 | 0.16359 | -0.029995 | 0.097117 | 0.014419 | 5.4428 | 7.9605 | -114.2258 | 7.6859 | -48.0103 | -6.5826 | -12.2543 | -15.9027 | 8.0292 | -114.0976 | 7.814 | -102.2141 | 5.4703 | -111.6623 | -0.10529 | -0.05951 | -0.33417 | 66.1102 | 101.8661 | 107.5378 | 101.9714 | 107.6431 | 0.022888 | 0.009155 | -0.20599 | 11.9064 | 2.4582 | 119.5908 | 2.4353 | 119.5679 | 66.2155 | 121.9116 | 11.8835 | 121.9116 | 122.1863 | 122.1268 | 122.081 | 122.1497 | -122.2458 | -122.1176 | 121.8063 | 121.9345 | 119.5633 | 98.2178
2713.8281 | 122.2366 | -114.3539 | 7.7728 | -0.82695 | 0.73784 | 0.10582 | 0.12252 | 0.0020935 | 0.65888 | -0.002884 | -0.10406 | -0.0028368 | 0.07721 | 0.16786 | -0.02914 | 0.096904 | 0.013138 | 5.2002 | 7.7087 | -114.4409 | 7.4615 | -47.4655 | -6.5506 | -12.236 | -16.2323 | 7.7774 | -114.4226 | 7.5394 | -102.4567 | 5.159 | -111.9095 | -0.086975 | -0.064087 | -0.31128 | 66.8884 | 102.1179 | 107.8033 | 102.2049 | 107.8903 | -0.068664 | 0.004578 | -0.23346 | 11.8973 | 2.4445 | 119.5129 | 2.5131 | 119.5816 | 66.9754 | 121.9025 | 11.9659 | 121.962 | 122.1497 | 122.2 | 122.0627 | 122.1313 | -122.2137 | -122.1954 | 121.8155 | 121.8933 | 119.5541 | 98.1216
2714.7656 | 122.2687 | -114.7247 | 7.4432 | -0.88036 | 0.78975 | 0.15901 | 0.11889 | -0.00025628 | 0.66016 | -0.0016022 | -0.06134 | -0.00091423 | 0.07721 | 0.16701 | -0.027859 | 0.098399 | 0.013138 | 5.2826 | 7.9605 | -114.4821 | 7.0679 | -46.8201 | -6.4682 | -12.3413 | -16.4062 | 7.3654 | -114.8163 | 7.1823 | -102.6718 | 4.8248 | -112.2482 | 0.24261 | 0.51727 | -0.37537 | 67.9047 | 102.3834 | 108.2565 | 102.1408 | 108.0139 | -0.091553 | -0.07782 | -0.26093 | 12.0529 | 2.4765 | 119.5496 | 2.5681 | 119.6411 | 67.662 | 121.55 | 12.1445 | 121.9986 | 122.4426 | 122.1817 | 122.6852 | 122.0901 | -121.9254 | -122.2595 | 121.7926 | 121.907 | 120.0073 | 98.3185
2715.7656 | 122.2595 | -114.2807 | 7.7408 | -0.8651 | 0.73656 | 0.10603 | 0.12017 | 0.0016663 | 0.65567 | -0.0024566 | -0.058289 | -0.0015552 | 0.076996 | 0.15611 | -0.030849 | 0.098613 | 0.012283 | 4.8431 | 7.3563 | -114.8163 | 7.1182 | -46.225 | -6.4224 | -12.2131 | -15.8936 | 7.4432 | -114.7522 | 7.2052 | -102.5711 | 4.9576 | -111.5936 | -0.53558 | -0.38452 | -0.62256 | 68.0557 | 102.0676 | 107.8583 | 102.6031 | 108.3939 | -0.4715 | -0.29755 | -0.53558 | 11.7096 | 2.6871 | 119.2383 | 3.1586 | 119.7098 | 68.5913 | 121.9345 | 12.1811 | 121.9574 | 122.1725 | 122.1954 | 121.637 | 121.7239 | -122.5571 | -122.493 | 121.3989 | 121.4859 | 119.1238 | 98.3871
2716.7656 | 122.2641 | -114.7614 | 7.3517 | -0.81932 | 0.73592 | 0.10475 | 0.11889 | 0.0016663 | 0.65738 | -0.0035248 | -0.079651 | -0.002196 | 0.076355 | 0.16722 | -0.030849 | 0.097758 | 0.011429 | 4.7882 | 7.2556 | -114.798 | 7.045 | -45.7672 | -6.3171 | -12.204 | -15.7928 | 7.3563 | -114.8209 | 7.1732 | -102.5299 | 4.7974 | -112.2482 | -0.036621 | -0.096131 | -0.3067 | 68.9941 | 102.5574 | 108.4442 | 102.594 | 108.4808 | -0.059509 | 0.004577 | -0.17853 | 12.2314 | 2.5131 | 119.5587 | 2.5726 | 119.6182 | 69.0308 | 121.843 | 12.291 | 121.994 | 122.0535 | 122.1771 | 122.0169 | 122.1176 | -122.1497 | -122.1725 | 121.8063 | 121.9345 | 119.5496 | 98.9685
2717.7656 | 122.2321 | -114.6423 | 7.5027 | -0.8651 | 0.7325 | 0.10646 | 0.1206 | 0.00038452 | 0.65418 | -0.00032036 | -0.04303 | 0.0010084 | 0.076569 | 0.16337 | -0.02914 | 0.096904 | 0.010574 | 4.7882 | 7.4158 | -114.7339 | 7.1457 | -45.3918 | -6.3354 | -12.1353 | -15.8569 | 7.4844 | -114.7156 | 7.2647 | -102.3926 | 4.8981 | -112.1155 | -0.091553 | -0.086976 | -0.35706 | 69.2505 | 102.507 | 108.3069 | 102.5986 | 108.3984 | -0.073242 | -0.018311 | -0.23804 | 12.2498 | 2.5269 | 119.5404 | 2.6001 | 119.6136 | 69.342 | 121.8796 | 12.323 | 121.9803 | 122.1497 | 122.2 | 122.0581 | 122.1268 | -122.2366 | -122.2183 | 121.788 | 121.907 | 119.4305 | 98.7854
2718.7656 | 122.7356 | -114.6973 | 7.4615 | -0.85747 | 0.7372 | 0.10454 | 0.12017 | 0.0025207 | 0.65311 | -0.0018158 | -0.058289 | -0.0024096 | 0.076996 | 0.16701 | -0.030209 | 0.094981 | 0.013138 | 4.7699 | 7.3883 | -114.7842 | 7.0999 | -44.9753 | -6.3126 | -12.1353 | -15.9348 | 7.4249 | -114.7476 | 7.2189 | -102.4155 | 4.866 | -112.1475 | -0.086975 | -0.073242 | -0.36163 | 69.722 | 102.562 | 108.3847 | 102.6489 | 108.4717 | -0.050354 | -0.036621 | -0.24261 | 12.2818 | 2.5497 | 119.5633 | 2.6001 | 119.6136 | 69.809 | 121.8842 | 12.3322 | 121.9666 | 122.1725 | 122.1725 | 122.0856 | 122.1222 | -122.2458 | -122.2092 | 121.7972 | 121.9162 | 119.4672 | 98.7625
2719.7656 | 122.2595 | -115.4938 | 6.6742 | -0.83458 | 0.73742 | 0.1056 | 0.11911 | -0.00068368 | 0.65375 | -0.0037384 | 0.033264 | -0.00091423 | 0.079346 | 0.1732 | -0.029781 | 0.096049 | 0.015701 | 4.0283 | 6.6055 | -115.5762 | 6.2988 | -44.8975 | -6.4178 | -12.1353 | -16.3971 | 6.6925 | -115.5075 | 6.3995 | -103.0975 | 4.0466 | -112.9669 | -0.082398 | -0.068664 | -0.37537 | 70.5963 | 103.3585 | 109.0759 | 103.4409 | 109.1583 | -0.013733 | 0.018311 | -0.27466 | 12.3962 | 2.5269 | 119.5404 | 2.5406 | 119.5541 | 70.6787 | 121.875 | 12.41 | 121.907 | 122.1817 | 122.2 | 122.0993 | 122.1863 | -122.2504 | -122.1817 | 121.7926 | 121.8933 | 119.5221 | 99.0967
2720.7656 | 122.2733 | -111.6074 | 10.4233 | -0.77354 | 0.72439 | 0.12141 | 0.11889 | -0.0032471 | 0.62662 | -0.0033112 | -0.030823 | 0.00058097 | 0.075928 | 0.16466 | -0.029781 | 0.095408 | 0.012497 | 5.1865 | 10.2676 | -111.8408 | 10.0708 | -45.4102 | -6.7474 | -11.4029 | -14.653 | 10.3592 | -111.7584 | 10.1212 | -99.8474 | 7.7316 | -109.0805 | -0.23346 | -0.15564 | -0.35248 | 66.1972 | 100.2045 | 104.8599 | 100.4379 | 105.0934 | -0.15106 | -0.064087 | -0.30212 | 11.7599 | 2.5269 | 119.339 | 2.6779 | 119.4901 | 66.4307 | 121.9116 | 11.911 | 121.8796 | 122.1085 | 122.1176 | 121.875 | 121.9666 | -122.2641 | -122.1817 | 121.6782 | 121.7285 | 116.7938 | 96.9543
2721.7656 | 122.1863 | -113.7405 | 8.3313 | -0.84984 | 0.74169 | 0.12227 | 0.1206 | -0.0045289 | 0.64115 | 0.00010684 | -0.067444 | -0.0017688 | 0.079132 | 0.16508 | -0.029995 | 0.097117 | 0.01506 | 4.097 | 8.2626 | -113.8779 | 7.9147 | -44.8151 | -6.2302 | -12.085 | -15.5823 | 8.3084 | -113.8367 | 8.0978 | -101.6418 | 5.722 | -111.2457 | -0.13733 | -0.068665 | -0.41656 | 68.9255 | 101.6556 | 107.5104 | 101.7929 | 107.6477 | -0.09613 | -0.022888 | -0.23346 | 12.0987 | 2.4948 | 119.4626 | 2.5909 | 119.5587 | 69.0628 | 121.7926 | 12.1948 | 121.9345 | 122.1405 | 122.1451 | 122.0032 | 122.049 | -122.2092 | -122.168 | 121.6553 | 121.8384 | 117.8375 | 98.1583
2722.7656 | 122.2137 | -113.9328 | 8.1757 | -0.81169 | 0.74212 | 0.12227 | 0.11996 | -0.0013245 | 0.64414 | -0.0020294 | -0.06134 | -0.0024096 | 0.07721 | 0.16637 | -0.032131 | 0.097117 | 0.016342 | 4.2206 | 8.1116 | -114.0747 | 7.8461 | -44.1788 | -6.4178 | -12.117 | -17.157 | 8.1757 | -114.0152 | 7.9422 | -101.5961 | 5.5756 | -111.3647 | -0.14191 | -0.064087 | -0.32959 | 69.754 | 101.8158 | 107.515 | 101.9577 | 107.6569 | -0.082398 | 0 | -0.23346 | 12.3367 | 2.5681 | 119.5084 | 2.6505 | 119.5908 | 69.8959 | 121.9208 | 12.4191 | 121.9574 | 122.1863 | 122.1909 | 122.0444 | 122.1085 | -122.2504 | -122.1909 | 121.7789 | 121.875 | 118.1534 | 96.7758
2723.7656 | 122.2137 | -113.9236 | 8.1757 | -0.91087 | 0.73998 | 0.12077 | 0.11932 | 0.0010253 | 0.64328 | -0.0026704 | -0.06134 | 0.00036737 | 0.076569 | 0.16658 | -0.029568 | 0.09434 | 0.012924 | 4.1565 | 8.1573 | -114.0427 | 7.8506 | -43.6203 | -6.3675 | -12.1124 | -15.7333 | 8.1665 | -113.9969 | 7.9285 | -101.3626 | 5.5801 | -111.3419 | -0.11902 | -0.01831 | -0.32501 | 70.3033 | 101.8112 | 107.5562 | 101.9302 | 107.6752 | -0.073242 | -0.009155 | -0.24719 | 12.561 | 2.5818 | 119.5038 | 2.655 | 119.577 | 70.4224 | 121.8933 | 12.6343 | 121.9254 | 122.2 | 122.1634 | 122.081 | 122.0901 | -122.2183 | -122.1725 | 121.7743 | 121.8521 | 118.0801 | 98.1903
2724.7656 | 122.2412 | -114.1113 | 8.0154 | -0.84221 | 0.73998 | 0.11885 | 0.12017 | -0.0047425 | 0.64093 | -0.0043792 | -0.046081 | -0.00070063 | 0.078278 | 0.17042 | -0.028072 | 0.094554 | 0.014206 | 4.1061 | 7.9376 | -114.2029 | 7.7042 | -43.4189 | -6.3766 | -12.1033 | -15.8157 | 8.0109 | -114.1388 | 7.7591 | -101.3763 | 5.4153 | -111.4838 | -0.091553 | -0.07782 | -0.31128 | 70.6924 | 102.0081 | 107.7347 | 102.0996 | 107.8262 | -0.027466 | -0.004578 | -0.25635 | 12.735 | 2.6276 | 119.5267 | 2.655 | 119.5541 | 70.784 | 121.907 | 12.7625 | 121.8979 | 122.1405 | 122.1497 | 122.049 | 122.1222 | -122.2183 | -122.1542 | 121.8155 | 121.8704 | 118.2175 | 98.2956
2725.8281 | 122.2275 | -114.2029 | 7.9102 | -1.0863 | 0.74212 | 0.12013 | 0.11953 | 0.0018799 | 0.64072 | -0.00074776 | -0.11322 | 0.0018628 | 0.076142 | 0.1732 | -0.030636 | 0.095622 | 0.01207 | 4.2252 | 7.901 | -114.2395 | 7.6309 | -42.7505 | -6.2439 | -12.1628 | -15.8981 | 7.8827 | -114.2761 | 7.7225 | -101.3763 | 5.3192 | -111.5524 | -0.036621 | -0.009155 | -0.27924 | 71.4523 | 102.0401 | 107.959 | 102.0767 | 107.9956 | -0.073242 | -0.027466 | -0.18768 | 12.8265 | 2.6505 | 119.5221 | 2.7237 | 119.5953 | 71.489 | 121.8704 | 12.8998 | 121.9986 | 122.1405 | 122.1588 | 122.1039 | 122.0856 | -122.1497 | -122.1863 | 121.8338 | 121.9254 | 118.428 | 98.3047
2726.7656 | 122.2778 | -114.2899 | 7.7911 | -0.87273 | 0.73977 | 0.1212 | 0.11846 | 0.0027343 | 0.64243 | -0.00074776 | -0.0033568 | -0.0013416 | 0.078705 | 0.16679 | -0.031277 | 0.094981 | 0.019333 | 4.1519 | 7.6996 | -114.3723 | 7.5714 | -42.3889 | -6.1523 | -12.1628 | -15.9851 | 7.7408 | -114.3631 | 7.6218 | -101.2894 | 5.2734 | -111.6074 | -0.082397 | -0.091553 | -0.21973 | 71.9009 | 102.1271 | 108.1375 | 102.2095 | 108.2199 | -0.073242 | -0.050354 | -0.16937 | 13.0005 | 2.6825 | 119.5633 | 2.7557 | 119.6365 | 71.9833 | 121.9437 | 13.0737 | 121.9849 | 122.0718 | 122.1039 | 121.9894 | 122.0306 | -122.1634 | -122.1542 | 121.8613 | 121.9116 | 118.4418 | 98.3047
2727.7656 | 122.1771 | -114.4272 | 7.6767 | -0.80406 | 0.74041 | 0.12077 | 0.1206 | -0.00068368 | 0.64093 | -0.0050202 | -0.085754 | -0.00027343 | 0.079346 | 0.16722 | -0.030849 | 0.097117 | 0.014847 | 4.0741 | 7.5806 | -114.4913 | 7.3746 | -42.1463 | -6.2851 | -12.3184 | -16.2369 | 7.6675 | -114.4913 | 7.4249 | -101.3626 | 5.072 | -111.7859 | -0.064087 | -0.096131 | -0.30212 | 72.2809 | 102.1088 | 108.1421 | 102.1729 | 108.2062 | -0.064087 | -0.009155 | -0.25177 | 13.0646 | 2.6413 | 119.4992 | 2.7054 | 119.5633 | 72.345 | 121.8658 | 13.1287 | 121.9162 | 122.0718 | 122.1588 | 122.0078 | 122.0947 | -122.168 | -122.168 | 121.8018 | 121.8521 | 118.5013 | 98.1903
2728.7656 | 122.319 | -114.4501 | 7.6218 | -0.88799 | 0.74041 | 0.12184 | 0.11718 | 0.00038452 | 0.63752 | -0.0016022 | -0.00030524 | -0.0024096 | 0.077423 | 0.17363 | -0.030636 | 0.095195 | 0.011642 | 4.1748 | 7.5256 | -114.5416 | 7.4249 | -41.4093 | -6.1432 | -12.2314 | -16.2048 | 7.5668 | -114.4959 | 7.489 | -101.2115 | 5.1315 | -111.6714 | -0.091553 | -0.09613 | -0.19684 | 73.0408 | 102.2186 | 108.3069 | 102.3102 | 108.3984 | -0.045777 | -0.054932 | -0.13275 | 13.2385 | 2.7786 | 119.5816 | 2.8244 | 119.6274 | 73.1323 | 121.9666 | 13.2843 | 121.9849 | 122.0673 | 122.0627 | 121.9757 | 122.0169 | -122.1634 | -122.1176 | 121.875 | 121.9391 | 118.6249 | 98.2452
2729.7656 | 122.2321 | -114.6011 | 7.5439 | -0.85747 | 0.73934 | 0.1244 | 0.1221 | -0.0021789 | 0.63752 | -0.0030976 | -0.06134 | -0.0015552 | 0.078705 | 0.17021 | -0.031063 | 0.094768 | 0.010361 | 4.0375 | 7.4249 | -114.7293 | 7.1915 | -41.3818 | -6.2073 | -12.3917 | -16.4749 | 7.4524 | -114.679 | 7.3563 | -101.3535 | 4.7241 | -111.9553 | -0.12817 | -0.11902 | -0.35248 | 73.2193 | 102.2095 | 108.3939 | 102.3376 | 108.522 | -0.07782 | -0.091552 | -0.18768 | 13.2477 | 2.6459 | 119.3253 | 2.7237 | 119.4031 | 73.3475 | 121.9208 | 13.3255 | 122.0352 | 122.1542 | 122.1313 | 122.0261 | 122.0535 | -122.2733 | -122.2229 | 121.7926 | 121.9574 | 118.6386 | 98.1262
2730.7656 | 122.2961 | -114.6561 | 7.3975 | -0.87273 | 0.73934 | 0.12141 | 0.11868 | 0.0031617 | 0.63794 | -0.0026704 | -0.00030524 | 0.00015377 | 0.078491 | 0.16765 | -0.031704 | 0.096049 | 0.011642 | 4.1016 | 7.3059 | -114.7659 | 7.1869 | -41.1987 | -6.0654 | -12.3093 | -16.4841 | 7.37 | -114.7247 | 7.2418 | -101.2665 | 4.8706 | -111.9553 | -0.10986 | -0.091553 | -0.21057 | 73.4573 | 102.3468 | 108.5907 | 102.4567 | 108.7006 | -0.068664 | -0.027466 | -0.15564 | 13.3896 | 2.7008 | 119.5267 | 2.7695 | 119.5953 | 73.5672 | 121.9528 | 13.4583 | 121.9666 | 122.0718 | 122.0947 | 121.962 | 122.0261 | -122.1634 | -122.1222 | 121.843 | 121.8979 | 118.7576 | 98.172
2731.7656 | 122.1588 | -114.7888 | 7.3013 | -0.85747 | 0.73955 | 0.12291 | 0.11868 | 0.0010253 | 0.63901 | 0.00096124 | -0.036926 | -0.0017688 | 0.077637 | 0.16594 | -0.02914 | 0.097758 | 0.0069427 | 4.0649 | 7.2144 | -114.8666 | 7.0358 | -41.0522 | -6.0516 | -12.4237 | -16.658 | 7.283 | -114.8254 | 7.0908 | -101.2985 | 4.7104 | -112.0148 | -0.07782 | -0.086976 | -0.2655 | 73.7366 | 102.3651 | 108.7372 | 102.4429 | 108.815 | -0.036621 | -0.018311 | -0.21057 | 13.4903 | 2.774 | 119.4992 | 2.8107 | 119.5358 | 73.8144 | 121.9025 | 13.5269 | 121.9162 | 122.081 | 122.1085 | 122.0032 | 122.0718 | -122.168 | -122.1268 | 121.8246 | 121.8796 | 118.8538 | 98.1308
2732.7656 | 122.4792 | -114.7659 | 7.3196 | -0.88036 | 0.74083 | 0.12334 | 0.12146 | -0.0011109 | 0.63452 | -0.0043792 | -0.024719 | -0.00070063 | 0.076782 | 0.16102 | -0.030849 | 0.095408 | 0.016128 | 4.1702 | 7.2144 | -114.7842 | 7.1091 | -40.9927 | -6.015 | -12.355 | -16.6489 | 7.2876 | -114.7888 | 7.2281 | -101.0101 | 4.866 | -111.8546 | -0.018311 | -0.10529 | -0.21057 | 73.7732 | 102.4109 | 108.7509 | 102.4292 | 108.7692 | -0.022888 | -0.032043 | -0.091553 | 13.7558 | 2.9114 | 119.632 | 2.9343 | 119.6548 | 73.7915 | 121.8933 | 13.7787 | 122.0169 | 121.9986 | 122.0764 | 121.9803 | 122.0535 | -122.1039 | -122.1085 | 121.875 | 121.994 | 118.9362 | 98.1171
2733.7656 | 122.3145 | -114.7842 | 7.2464 | -0.79643 | 0.73998 | 0.12739 | 0.12188 | 0.0025207 | 0.63666 | -0.0020294 | 0.0027466 | -0.0017688 | 0.079346 | 0.1732 | -0.032345 | 0.094127 | 0.01741 | 4.184 | 7.1503 | -114.8529 | 7.1182 | -40.8188 | -6.0883 | -12.4695 | -16.8137 | 7.2327 | -114.8483 | 7.1457 | -101.0147 | 4.7836 | -111.9415 | -0.068664 | -0.09613 | -0.12817 | 73.9655 | 102.3148 | 108.696 | 102.3834 | 108.7646 | -0.064087 | -0.013733 | -0.10071 | 13.7695 | 2.8427 | 119.5679 | 2.9068 | 119.632 | 74.0341 | 121.9711 | 13.8336 | 121.994 | 122.0032 | 122.081 | 121.9345 | 122.0169 | -122.0993 | -122.0947 | 121.9025 | 121.9299 | 118.9682 | 97.9706
2734.7656 | 122.2824 | -114.9536 | 7.0999 | -0.85747 | 0.73784 | 0.12184 | 0.12039 | 0.0014527 | 0.63602 | -0.0041656 | -0.070496 | -0.0017688 | 0.077637 | 0.17299 | -0.03149 | 0.095836 | 0.0095063 | 4.0375 | 7.0084 | -115.0589 | 6.8939 | -40.8829 | -5.9052 | -12.4924 | -16.9739 | 7.0587 | -115.0223 | 6.9534 | -101.1017 | 4.6051 | -112.0743 | -0.10529 | -0.091553 | -0.20599 | 74.0707 | 102.4612 | 109.0485 | 102.5665 | 109.1537 | -0.068665 | -0.041199 | -0.14649 | 13.8519 | 2.8793 | 119.5587 | 2.948 | 119.6274 | 74.176 | 121.9528 | 13.9206 | 121.9757 | 122.0673 | 122.081 | 121.962 | 122.0123 | -122.1588 | -122.1222 | 121.8475 | 121.907 | 118.9911 | 97.9797
2735.7656 | 122.2733 | -114.9994 | 7.0496 | -0.88799 | 0.73763 | 0.12227 | 0.11975 | 0.0014527 | 0.63623 | 0.00053404 | -0.046081 | -0.00048703 | 0.078919 | 0.16914 | -0.029995 | 0.096904 | 0.011429 | 4.0421 | 6.9214 | -115.1047 | 6.8665 | -40.6403 | -5.864 | -12.5198 | -17.0563 | 7.0175 | -115.0589 | 6.926 | -101.0376 | 4.5685 | -112.0972 | -0.10528 | -0.12817 | -0.18311 | 74.3591 | 102.4796 | 109.1354 | 102.5848 | 109.2407 | -0.059509 | -0.032044 | -0.1236 | 13.9618 | 2.9022 | 119.5679 | 2.9617 | 119.6274 | 74.4644 | 121.9711 | 14.0213 | 121.9849 | 122.0261 | 122.0764 | 121.9208 | 122.0169 | -122.1542 | -122.1085 | 121.8658 | 121.9254 | 119.0414 | 97.9431
2736.7656 | 122.3236 | -115.0223 | 6.9901 | -0.82695 | 0.73913 | 0.12334 | 0.12039 | 0.00038452 | 0.63431 | -0.002884 | -0.067444 | -0.0015552 | 0.078064 | 0.16444 | -0.02914 | 0.095195 | 0.015701 | 3.9825 | 6.8756 | -115.1367 | 6.8665 | -40.3564 | -5.7907 | -12.4558 | -17.0929 | 6.9534 | -115.123 | 6.8985 | -101.0056 | 4.5319 | -112.1429 | -0.11444 | -0.11444 | -0.1236 | 74.6658 | 102.5665 | 109.2316 | 102.681 | 109.346 | -0.10071 | -0.036621 | -0.091552 | 14.0167 | 2.8793 | 119.5541 | 2.98 | 119.6548 | 74.7803 | 122.0032 | 14.1174 | 122.0215 | 122.0123 | 122.0764 | 121.8979 | 121.9757 | -122.1268 | -122.113 | 121.8887 | 121.9208 | 119.0048 | 97.9294
2737.8281 | 122.3328 | -115.0223 | 6.9809 | -0.84984 | 0.73763 | 0.12184 | 0.12081 | 0.00081172 | 0.63559 | 0.0013886 | -0.046081 | -0.0015552 | 0.07956 | 0.16615 | -0.03149 | 0.095836 | 0.017837 | 4.0604 | 6.9031 | -115.004 | 6.8115 | -40.1779 | -5.8136 | -12.4374 | -17.157 | 6.9443 | -115.1138 | 6.9077 | -100.8728 | 4.5776 | -112.1017 | 0.018311 | -0.07782 | -0.16937 | 74.8444 | 102.5848 | 109.2087 | 102.5665 | 109.1904 | -0.091553 | -0.036621 | -0.073242 | 14.1495 | 2.9205 | 119.5999 | 3.0121 | 119.6915 | 74.8261 | 121.8155 | 14.241 | 122.0215 | 121.907 | 122.0581 | 121.9254 | 121.9666 | -121.9849 | -122.0947 | 121.8338 | 121.9299 | 119.0826 | 97.8653
2738.7656 | 122.287 | -114.9628 | 7.0084 | -0.9185 | 0.73571 | 0.11992 | 0.12039 | 0.0016663 | 0.6341 | -0.00074776 | -0.039978 | -0.0026232 | 0.081909 | 0.16444 | -0.031704 | 0.097972 | 0.011856 | 4.0146 | 6.9122 | -115.0543 | 6.8665 | -40.0406 | -5.7358 | -12.4237 | -17.0975 | 6.9901 | -115.0955 | 6.926 | -100.8087 | 4.5456 | -112.0743 | -0.091552 | -0.096131 | -0.14191 | 74.9222 | 102.5391 | 109.227 | 102.6306 | 109.3185 | -0.13275 | -0.018311 | -0.082398 | 14.1541 | 2.8885 | 119.5084 | 3.0212 | 119.6411 | 75.0137 | 121.9208 | 14.2868 | 122.0215 | 121.9666 | 122.0856 | 121.875 | 121.9528 | -122.0627 | -122.1039 | 121.8292 | 121.8887 | 118.9774 | 97.8653
2739.7656 | 122.1268 | -80.9326 | 41.0431 | -1.0482 | 0.93117 | 0.45381 | 0.11996 | 0.0014527 | 0.47516 | -0.00053396 | -0.085754 | 0.00015377 | 0.073364 | 0.17897 | -0.031704 | 0.096263 | 0.013992 | 20.137 | 45.8038 | -76.1398 | 46.0876 | -27.9053 | -5.2689 | 2.2751 | -2.4811 | 43.1396 | -79.9576 | 40.9286 | -70.4178 | 38.6353 | -78.2227 | 4.7928 | 4.7607 | 5.0446 | 53.0273 | 83.2077 | 75.6638 | 78.4149 | 70.871 | 0.97504 | 2.0966 | -0.11444 | 10.5148 | 2.71 | 119.5679 | 1.7349 | 118.5928 | 48.2346 | 122.2275 | 9.5398 | 120.8862 | 121.9437 | 123.0972 | 126.7364 | 124.0723 | -117.1829 | -121.0007 | 127.0203 | 121.8613 | 101.0696 | 78.4515
2740.7656 | 122.2092 | -106.0043 | 15.8066 | -1.3992 | 1.2655 | 0.73707 | 0.11825 | 0.00017092 | 0.57813 | -0.0065156 | -0.082703 | -0.0024096 | 0.081269 | 0.17149 | -0.030849 | 0.094981 | 0.013138 | 8.7845 | 15.596 | -106.0913 | 16.571 | -38.3514 | -6.4453 | -9.1827 | -13.2294 | 16.626 | -105.3909 | 15.7654 | -93.0405 | 13.3942 | -103.1067 | -0.086976 | -0.21057 | 0.76447 | 67.6529 | 96.8216 | 99.559 | 96.9086 | 99.646 | 0.6134 | 0.8194 | -0.041199 | 12.9639 | 2.8976 | 119.3985 | 2.2842 | 118.7851 | 67.7399 | 122.6624 | 12.3505 | 121.1563 | 121.6873 | 122.0169 | 121.6003 | 122.6303 | -121.8979 | -121.1975 | 122.5754 | 121.7697 | 114.7888 | 92.775
2741.7656 | 122.2641 | -108.3939 | 13.5498 | -0.7888 | 0.68358 | 0.11928 | 0.11932 | 0.00081172 | 0.59052 | -0.00032036 | -0.067444 | -0.00070063 | 0.078919 | 0.17277 | -0.031704 | 0.096049 | 0.016556 | 7.7545 | 13.4583 | -108.5907 | 13.4537 | -39.4638 | -6.5643 | -10.35 | -14.8499 | 13.5178 | -108.5037 | 13.5086 | -95.2332 | 11.0687 | -105.574 | -0.19684 | -0.091553 | -0.096131 | 68.9301 | 98.0438 | 101.8295 | 98.2407 | 102.0264 | -0.10986 | -0.032044 | -0.041199 | 13.1607 | 2.8198 | 119.4626 | 2.9297 | 119.5724 | 69.1269 | 122.0444 | 13.2706 | 122.0123 | 122.049 | 122.0215 | 121.8521 | 121.9116 | -122.1405 | -122.0535 | 121.8475 | 121.9025 | 116.1484 | 93.544
2742.7656 | 122.3557 | -109.5566 | 12.3596 | -0.84221 | 0.6917 | 0.1197 | 0.12081 | -4.2682e-05 | 0.59479 | -0.001175 | -0.052185 | -0.00070063 | 0.078278 | 0.16893 | -0.029568 | 0.095195 | 0.013138 | 6.7062 | 12.2223 | -109.8084 | 12.2086 | -38.9877 | -6.5689 | -10.3912 | -15.4999 | 12.3093 | -109.6939 | 12.3734 | -96.0571 | 9.9701 | -106.6818 | -0.25177 | -0.13733 | -0.15106 | 70.5688 | 99.1653 | 102.9877 | 99.4171 | 103.2394 | -0.13733 | -0.050354 | 0.013733 | 13.4995 | 2.8748 | 119.5267 | 3.0121 | 119.664 | 70.8206 | 122.0169 | 13.6368 | 122.0673 | 122.0306 | 122.0032 | 121.7789 | 121.8658 | -122.168 | -122.0535 | 121.7651 | 121.9299 | 116.2628 | 94.0567
2743.7656 | 122.3785 | -110.3622 | 11.618 | -0.80406 | 0.69384 | 0.12013 | 0.11825 | 0.0063659 | 0.59436 | -0.0016022 | -0.049133 | -0.0024096 | 0.075287 | 0.17576 | -0.031917 | 0.094981 | 0.019119 | 6.1935 | 11.6226 | -110.408 | 11.5402 | -39.0427 | -6.5506 | -10.6659 | -15.8936 | 11.6318 | -110.4355 | 11.6318 | -96.666 | 9.2102 | -107.373 | -0.045776 | 0.004578 | -0.07782 | 71.3196 | 99.6964 | 103.8116 | 99.7421 | 103.8574 | -0.073242 | 0.013733 | 0.013733 | 13.6963 | 2.9892 | 119.5724 | 3.0624 | 119.6457 | 71.3654 | 121.9482 | 13.7695 | 122.0673 | 122.0306 | 122.0673 | 121.9849 | 121.994 | -122.0261 | -122.0535 | 121.9025 | 121.994 | 116.5558 | 94.4687
2744.7656 | 122.3877 | -92.3355 | 29.6402 | -1.1474 | 0.99697 | 0.52922 | 0.11782 | -4.2682e-05 | 0.49332 | -0.0018158 | -0.073547 | 0.001222 | 0.079346 | 0.17427 | -0.030636 | 0.094768 | 0.013779 | 21.6751 | 28.3081 | -93.5577 | 28.8712 | -34.0027 | -5.4611 | -4.5136 | -8.1116 | 29.0909 | -92.8482 | 29.7638 | -80.2368 | 27.3468 | -89.5752 | -1.2222 | -1.3321 | -0.76904 | 58.3328 | 87.822 | 86.8744 | 89.0442 | 88.0966 | -0.5127 | -0.54932 | 0.1236 | 12.0987 | 2.7603 | 119.6823 | 3.273 | 120.195 | 59.5551 | 122.4289 | 12.6114 | 122.612 | 121.8658 | 121.9391 | 120.6436 | 121.4264 | -123.1979 | -122.4884 | 121.2067 | 122.0993 | 114.0106 | 84.2239
2745.7656 | 122.3557 | -110.9802 | 10.9863 | -0.88036 | 0.6996 | 0.12056 | 0.11911 | -0.0026063 | 0.5965 | -0.002243 | -0.067444 | -0.0026232 | 0.079346 | 0.16893 | -0.031704 | 0.095195 | 0.013779 | 5.7175 | 10.968 | -111.0855 | 10.8948 | -39.267 | -6.6605 | -10.8673 | -16.127 | 10.968 | -111.0535 | 11.0092 | -96.7163 | 8.5876 | -107.9453 | -0.10528 | -0.01831 | -0.091553 | 71.7133 | 100.1129 | 104.3198 | 100.2182 | 104.425 | -0.073242 | -0.01831 | 0.022888 | 14.2639 | 3.035 | 119.5679 | 3.1082 | 119.6411 | 71.8185 | 121.9803 | 14.3372 | 122.0627 | 122.0535 | 122.0215 | 121.9482 | 121.9482 | -122.0718 | -122.0398 | 121.875 | 121.9894 | 116.6977 | 94.8532
2746.7656 | 122.3328 | -112.4634 | 9.5078 | -0.85747 | 0.71264 | 0.12291 | 0.11932 | 0.0018799 | 0.60868 | -0.0030976 | -0.073547 | -0.00027343 | 0.080841 | 0.16423 | -0.03149 | 0.095836 | 0.013992 | 4.4449 | 9.4894 | -112.5961 | 9.3521 | -39.0152 | -6.2073 | -11.348 | -16.8549 | 9.4803 | -112.5412 | 9.4711 | -97.9431 | 7.0496 | -109.4193 | -0.13275 | -0.01831 | -0.15564 | 73.4482 | 101.1154 | 106.2561 | 101.2482 | 106.3889 | -0.07782 | -0.027465 | -0.036621 | 14.5203 | 3.0441 | 119.5129 | 3.1219 | 119.5908 | 73.5809 | 121.9482 | 14.5981 | 122.0123 | 122.0856 | 122.0215 | 121.9528 | 121.9437 | -122.1039 | -122.049 | 121.8155 | 121.9345 | 116.9083 | 95.6085
2747.7656 | 122.1542 | -112.8159 | 9.169 | -0.8651 | 0.71242 | 0.1197 | 0.11697 | 0.0027343 | 0.61124 | -0.0013886 | -0.058289 | -0.001128 | 0.082123 | 0.17256 | -0.031704 | 0.096477 | 0.015488 | 4.1885 | 9.0775 | -112.9898 | 9.0225 | -38.7726 | -6.0562 | -11.4853 | -17.0654 | 9.1278 | -112.9166 | 9.1187 | -98.1537 | 6.7062 | -109.7534 | -0.17395 | -0.091552 | -0.14648 | 74.0433 | 101.3306 | 106.7596 | 101.5045 | 106.9336 | -0.10071 | -0.041198 | -0.050354 | 14.6622 | 3.0624 | 119.5221 | 3.1631 | 119.6228 | 74.2172 | 122.0123 | 14.7629 | 122.0352 | 122.0673 | 122.0444 | 121.8933 | 121.9437 | -122.1588 | -122.0856 | 121.8384 | 121.9345 | 117.0044 | 95.7504
2748.7656 | 122.2366 | -112.9623 | 9.0179 | -0.80406 | 0.71264 | 0.12163 | 0.12039 | -0.0021789 | 0.60868 | -0.0033112 | -0.09491 | -0.00048703 | 0.074219 | 0.17641 | -0.032558 | 0.097545 | 0.013992 | 4.2892 | 8.9447 | -113.0814 | 8.8943 | -38.4705 | -5.9601 | -11.5082 | -17.2897 | 8.9813 | -113.118 | 8.9813 | -98.41 | 6.5735 | -109.877 | -0.11902 | -0.073242 | -0.1236 | 74.4919 | 101.4542 | 107.0023 | 101.5732 | 107.1213 | -0.15564 | -0.036621 | -0.036621 | 14.5523 | 3.0853 | 119.5358 | 3.241 | 119.6915 | 74.6109 | 121.9757 | 14.7079 | 122.0993 | 122.0261 | 122.0993 | 121.907 | 121.9437 | -122.0993 | -122.1359 | 121.8567 | 121.9437 | 117.2516 | 95.6726
2749.8281 | 122.3053 | -113.1042 | 8.8852 | -0.87273 | 0.71178 | 0.12163 | 0.11996 | 0.0029479 | 0.61039 | -0.0030976 | -0.13763 | 0.00015377 | 0.081269 | 0.17299 | -0.031063 | 0.096049 | 0.017837 | 4.2572 | 8.8211 | -113.2462 | 8.7662 | -38.6719 | -5.8594 | -11.4532 | -17.5507 | 8.8348 | -113.1866 | 8.8531 | -98.378 | 6.4453 | -109.9777 | -0.14191 | -0.064087 | -0.11902 | 74.4324 | 101.651 | 107.2449 | 101.7929 | 107.3868 | -0.082398 | -0.050354 | -0.032044 | 14.7263 | 3.1265 | 119.5496 | 3.2089 | 119.632 | 74.5743 | 122.0123 | 14.8087 | 122.0398 | 122.0673 | 122.0215 | 121.9254 | 121.9391 | -122.1313 | -122.0718 | 121.8704 | 121.9574 | 117.3615 | 95.5536
2750.7656 | 122.2916 | -113.1821 | 8.8577 | -0.87273 | 0.71264 | 0.12291 | 0.11932 | 0.0033753 | 0.60868 | -0.0013886 | -0.067444 | 0.00079477 | 0.07956 | 0.16572 | -0.032131 | 0.093913 | 0.015701 | 4.2709 | 8.7753 | -113.2462 | 8.7112 | -38.7131 | -5.8731 | -11.6776 | -17.5552 | 8.8211 | -113.2004 | 8.8028 | -98.2864 | 6.3904 | -109.9457 | -0.064087 | -0.082397 | -0.14648 | 74.469 | 101.5045 | 107.309 | 101.5686 | 107.373 | -0.01831 | -0.036621 | -0.054932 | 14.8956 | 3.2364 | 119.5724 | 3.2547 | 119.5908 | 74.5331 | 121.9574 | 14.9139 | 122.0032 | 122.0215 | 122.0215 | 121.9574 | 122.0032 | -122.1039 | -122.0581 | 121.8933 | 121.9849 | 117.453 | 95.6268
2751.7656 | 122.2092 | -93.5303 | 28.3401 | -1.7654 | 1.7184 | 1.2017 | 0.11846 | 0.0046569 | 0.50486 | -0.00074776 | -0.097961 | -0.0013416 | 0.079987 | 0.17641 | -0.030636 | 0.095622 | 0.014419 | 7.5851 | 28.6423 | -93.0313 | 28.83 | -33.5083 | -4.184 | -4.2984 | -8.0246 | 29.2007 | -92.5232 | 28.6057 | -80.7083 | 25.9964 | -90.5777 | 0.49896 | 0.30212 | 0.48981 | 60.022 | 89.2319 | 89.3463 | 88.7329 | 88.8474 | 1.0071 | 0.8606 | 0.2655 | 12.822 | 2.9526 | 119.5267 | 1.9455 | 118.5196 | 59.523 | 121.8613 | 11.8149 | 121.1288 | 121.6736 | 121.7239 | 122.1725 | 122.731 | -121.3715 | -120.8633 | 122.3602 | 122.1359 | 101.1154 | 85.5057
2752.7656 | 122.1909 | -91.4383 | 30.4138 | -0.68199 | 0.58361 | 0.11287 | 0.11953 | -0.0045289 | 0.5087 | 0.00010684 | -0.36346 | -5.9826e-05 | 0.078919 | 0.73759 | -0.032345 | 0.093486 | 0.57945 | 3.6575 | 30.0705 | -91.9601 | 30.1025 | -33.1238 | -4.8386 | -1.8448 | -7.3883 | 30.4184 | -91.3742 | 30.4825 | -76.4969 | 27.7954 | 5.3009 | -0.52185 | -0.34332 | -0.31128 | 58.3145 | 89.5935 | 86.5997 | 90.1154 | 87.1216 | 0.064086 | 0.004578 | 0.068665 | 14.9414 | 96.7392 | 119.2337 | 96.6751 | 119.1696 | 58.8364 | 122.0627 | 14.8773 | 121.8567 | 122.0306 | 121.7926 | 121.5088 | 121.8567 | -122.374 | -121.788 | 121.5408 | 121.9208 | 95.0958 | 84.05
2753.7656 | 122.2 | -99.2294 | 22.5861 | -0.72777 | 0.58339 | 0.11821 | 0.11975 | -0.00089728 | 0.50208 | -0.0035248 | -0.27802 | 0.25223 | 0.081269 | 0.44322 | -0.030209 | 0.090495 | 0.54207 | 3.4195 | 22.8287 | -99.1562 | 22.6822 | -35.3851 | -4.8798 | -4.9347 | -11.1877 | 22.6135 | -99.2523 | 22.3755 | -83.7662 | 20.0867 | -8.5327 | 0.073242 | 0.24261 | 0.09613 | 63.8443 | 94.2947 | 94.3497 | 94.2215 | 94.2764 | -0.022888 | 0.027465 | -0.21057 | 15.4633 | 90.6967 | 119.3161 | 90.7196 | 119.339 | 63.7711 | 121.8384 | 15.4861 | 121.6278 | 121.9849 | 121.8658 | 122.0581 | 121.843 | -121.7422 | -121.8384 | 121.9116 | 121.6049 | 102.6489 | 88.0417
2754.7656 | 122.1039 | -95.6909 | 26.2939 | -0.78117 | 0.59984 | 0.11564 | 0.11868 | -4.2682e-05 | 0.51532 | -0.001175 | -0.29938 | -0.0019824 | 0.07956 | 0.64723 | -0.031063 | 0.092204 | 0.48759 | 3.2913 | 26.4267 | -95.2423 | 26.619 | -33.8608 | -5.0903 | -3.8498 | -10.0433 | 26.4999 | -95.3888 | 25.7812 | -79.0833 | 24.5682 | -10.1303 | 0.44861 | 0.13275 | 0.32501 | 61.8301 | 91.8411 | 90.6006 | 91.3925 | 90.152 | 0.30212 | 0.20599 | -0.5127 | 16.6077 | 85.5606 | 120.2591 | 85.2585 | 119.957 | 61.3815 | 121.8613 | 16.3055 | 121.17 | 121.669 | 121.8887 | 122.1176 | 122.1909 | -121.5363 | -121.6827 | 122.3099 | 121.4722 | 98.9822 | 85.6476
2755.7656 | 122.1405 | -94.249 | 27.5208 | -0.77354 | 0.5772 | 0.11436 | 0.11996 | 0.00038452 | 0.50315 | -0.0018158 | -0.19867 | 0.26782 | 0.078491 | 0.45241 | -0.030636 | 0.091136 | 0.56514 | 3.1906 | 27.4933 | -94.4183 | 27.8778 | -33.9981 | -5.0125 | -3.1906 | -9.1141 | 27.7405 | -94.0063 | 27.7267 | -78.7949 | 25.3967 | -1.8951 | -0.16937 | -0.027466 | 0.35706 | 60.2509 | 91.0583 | 89.2365 | 91.2277 | 89.4058 | 0.24261 | 0.21973 | 0.20599 | 15.4541 | 92.3538 | 119.6457 | 92.1112 | 119.4031 | 60.4202 | 122.2961 | 15.2115 | 121.7331 | 121.9116 | 121.7468 | 121.7422 | 121.9894 | -121.9391 | -121.5271 | 122.1268 | 121.9757 | 97.4396 | 85.1349
2756.7656 | 122.2137 | -75.4669 | 46.3669 | -0.6591 | 0.48 | 0.10454 | 0.1174 | -0.00068368 | 0.42432 | -0.004593 | -0.15594 | 0.27551 | 0.075928 | 0.4193 | -0.03149 | 0.090068 | 0.53673 | 2.5589 | 44.9615 | -76.2634 | 46.4035 | -27.6993 | -4.5319 | 3.653 | -1.0757 | 45.0256 | -76.1124 | 46.431 | -62.0773 | 44.3848 | 15.6967 | -0.79651 | -1.4053 | 0.036621 | 47.7676 | 79.1199 | 70.9351 | 79.9164 | 71.7316 | -0.64545 | -1.3412 | 0.064087 | 13.3896 | 91.1636 | 119.8517 | 91.8091 | 120.4971 | 48.5641 | 122.6669 | 14.035 | 122.5433 | 121.225 | 121.138 | 120.4285 | 120.4926 | -122.6303 | -122.4792 | 121.8704 | 121.8979 | 78.0258 | 74.3912
2757.7656 | 122.3053 | -95.723 | 26.0422 | -0.70488 | 0.58382 | 0.11415 | 0.11825 | -0.0015381 | 0.50806 | -0.0024566 | -0.12848 | 0.27551 | 0.082123 | 0.38426 | -0.031063 | 0.091136 | 0.50255 | 2.1881 | 25.7401 | -96.1853 | 25.7721 | -34.964 | -5.3925 | -3.978 | -10.1578 | 25.4242 | -95.9015 | 25.9872 | -80.5756 | 23.7534 | -9.4437 | -0.46234 | -0.30212 | -0.27008 | 60.759 | 91.745 | 90.3305 | 92.2073 | 90.7928 | -0.17853 | -0.61798 | -0.054931 | 15.1474 | 86.2793 | 119.4763 | 86.4578 | 119.6548 | 61.2213 | 121.9574 | 15.3259 | 121.8887 | 121.9254 | 121.3257 | 121.463 | 121.1472 | -122.2275 | -121.9437 | 121.4951 | 121.7102 | 97.9111 | 85.5652
2758.7656 | 122.3053 | -92.8116 | 28.6423 | -0.66673 | 0.54003 | 0.11116 | 0.11654 | 0.0023071 | 0.47324 | -0.0043792 | 0.085144 | 0.23514 | 0.081482 | 0.43553 | -0.02914 | 0.092418 | 0.51942 | 2.1973 | 29.5578 | -92.1021 | 29.4113 | -33.49 | -5.2917 | -3.0212 | -10.3958 | 28.7018 | -91.6306 | 29.1504 | -77.4765 | 26.207 | -8.8303 | 0.70953 | 0.91553 | 0.76904 | 59.3216 | 89.7903 | 87.5198 | 89.0808 | 86.8103 | 1.181 | 0.059509 | 0.50812 | 15.3351 | 83.9813 | 119.0186 | 82.8003 | 117.8375 | 58.6121 | 121.5134 | 14.1541 | 120.7809 | 121.6599 | 120.3323 | 122.3694 | 121.5134 | -120.7443 | -120.2728 | 122.2229 | 121.962 | 95.0088 | 82.4158
2759.8281 | 112.0468 | 6.0974 | 97.7188 | -0.39207 | 0.021352 | 0.075056 | -1.4542 | 0.020465 | 0.054965 | 0.0026702 | -0.31464 | 0.16635 | 0.06781 | 0.48659 | -0.03149 | 0.092418 | 0.48653 | 0.073242 | 97.0963 | -110.9436 | 129.657 | 1.2772 | 0.086975 | 10.2905 | 35.0601 | 128.5538 | 5.2551 | 126.9928 | 11.5265 | 109.4147 | 80.7541 | -117.041 | -0.62256 | 31.9382 | -4.8203 | 4.1931 | -6.0104 | 121.2341 | 111.0306 | -0.84229 | 30.835 | 29.274 | 5.4291 | 74.6567 | 103.3173 | 75.499 | 104.1595 | 112.2208 | 240.6006 | 6.2714 | 121.7377 | 208.0399 | 123.2986 | 90.9988 | 122.4564 | -208.6624 | -92.4637 | 123.5596 | 120.8954 | -6.0242 | 28.9627
2760.7656 | 116.6748 | -6.8939 | 96.8262 | -0.39207 | 0.015797 | 0.076338 | 0.1253 | -0.0017517 | 0.031467 | -0.0024566 | -0.18951 | 0.17105 | 0.067169 | 0.42143 | -0.029568 | 0.09434 | 0.42052 | -0.21973 | 114.5142 | -7.1274 | 113.9832 | -3.2913 | -1.5244 | 28.1158 | 28.0014 | 97.4625 | -7.4615 | 114.0289 | -0.65918 | 104.9561 | 62.1735 | -0.23346 | 17.688 | 17.157 | 3.6026 | 35.0098 | 5.3696 | 35.2432 | 5.603 | -0.56763 | 0.63629 | 17.2028 | 6.2347 | 69.0674 | 111.85 | 69.635 | 112.4176 | 3.8361 | 121.1105 | 6.8024 | 121.4905 | 121.6415 | 104.924 | 121.4081 | 104.3564 | -103.9536 | -104.2877 | 120.8771 | 120.9229 | 6.6742 | 34.8953
2761.8281 | 121.9482 | -6.7886 | 104.2648 | -0.31578 | 0.016865 | 0.07762 | 0.1268 | -4.2682e-05 | 0.033389 | -0.0043792 | -0.20477 | 0.2142 | 0.068024 | 0.40178 | -0.030849 | 0.092631 | 0.44829 | -0.21973 | 114.6652 | -7.1869 | 114.0747 | -3.4149 | -1.3779 | 28.3173 | 28.1387 | 104.924 | -7.338 | 114.2487 | -0.47607 | 112.262 | 68.0283 | -0.39825 | 10.4004 | 9.8099 | 3.3737 | 35.1059 | 5.4108 | 35.5042 | 5.809 | -0.54932 | 0.65918 | 9.9838 | 6.3126 | 74.8169 | 119.0506 | 75.3662 | 119.5999 | 3.772 | 121.2616 | 6.8619 | 121.5866 | 121.8521 | 112.262 | 121.4539 | 111.7126 | -111.4517 | -111.6028 | 120.8633 | 121.0373 | 6.5689 | 34.9274
2762.7656 | 122.3877 | 1.3641 | 114.7842 | -0.17082 | 0.014516 | 0.079543 | 0.1221 | 0.0023071 | 0.029544 | -0.0020294 | -0.14374 | 0.097993 | 0.067169 | 0.58528 | -0.03619 | 0.090922 | 0.53181 | -0.059509 | 113.4338 | -4.5731 | 115.0452 | -2.8885 | -0.72784 | 28.1891 | 28.7247 | 114.7934 | -2.2247 | 115.7913 | 0.49439 | 113.2874 | 79.7516 | -5.9372 | -1.3504 | 0.26093 | -4.2526 | 26.825 | -2.092 | 32.7621 | 3.8452 | -3.5889 | 0.009155 | 1.0071 | -0.86975 | 78.3875 | 111.9232 | 81.9763 | 115.5121 | 1.6846 | 119.6182 | 2.7191 | 118.0161 | 118.0069 | 117.0181 | 112.0697 | 113.4293 | -119.3573 | -117.009 | 113.681 | 114.4272 | -1.4236 | 27.3605
2763.7656 | 122.287 | -6.5506 | 114.7614 | -0.16319 | 0.016865 | 0.076338 | 0.12188 | 0.00038452 | 0.030826 | -0.003952 | 0.027161 | 0.0050672 | 0.066742 | 0.18986 | -0.029995 | 0.094127 | 0.028305 | -0.07782 | 115.5762 | -6.5643 | 115.2283 | -2.8107 | -0.78278 | 26.564 | 28.2486 | 114.8666 | -6.427 | 115.4755 | -1.7303 | 112.738 | -1.0849 | -0.013733 | 0.81482 | 0.46692 | 3.7399 | 33.1146 | 5.7678 | 33.1284 | 5.7816 | 0.1236 | 0.10528 | 0.71411 | 4.8203 | 5.4657 | 119.2886 | 5.3421 | 119.165 | 3.7537 | 121.7926 | 4.6967 | 121.9025 | 122.1405 | 121.2936 | 122.1268 | 121.4172 | -121.3257 | -121.1884 | 121.7789 | 122.0261 | 6.4728 | 34.7992
2764.7656 | 121.8246 | -6.2164 | 102.4841 | -0.15556 | 0.018361 | 0.079329 | 0.12466 | -0.00068368 | 0.028476 | -0.0043792 | 0.014954 | 0.0018628 | 0.064179 | 0.18068 | -0.029995 | 0.094554 | 0.018906 | -0.027466 | 115.274 | -6.1157 | 115.1871 | -2.861 | -0.91095 | 26.4313 | 27.9968 | 109.877 | -6.5094 | 115.3931 | -1.7075 | 112.2757 | -3.8132 | 0.10071 | 12.7899 | 12.7029 | 3.3554 | 32.6477 | 5.3055 | 32.547 | 5.2048 | -0.29297 | 7.3929 | 12.9089 | 4.509 | 2.4033 | 118.4921 | 2.6962 | 118.7851 | 3.2547 | 121.3028 | 4.8019 | 121.9025 | 121.3898 | 116.3864 | 121.4905 | 116.0934 | -108.5999 | -108.9935 | 121.4035 | 121.6095 | 6.189 | 34.2133
2765.7656 | 121.962 | -6.5872 | 114.7247 | -0.18608 | 0.015156 | 0.075911 | 0.12188 | -0.0017517 | 0.03403 | -0.003952 | 0.036316 | 0.0031446 | 0.068878 | 0.18538 | -0.031917 | 0.096904 | 0.017624 | -0.082397 | 115.5716 | -6.5323 | 115.3244 | -2.8244 | -0.70038 | 26.6373 | 28.0792 | 114.7659 | -6.4041 | 115.4892 | -1.7441 | 112.706 | -4.0283 | 0.054931 | 0.84686 | 0.59967 | 3.7628 | 33.2245 | 5.8868 | 33.1696 | 5.8319 | 0.18311 | 0.041199 | 0.76447 | 4.8431 | 2.5589 | 119.2932 | 2.3758 | 119.1101 | 3.7079 | 121.8567 | 4.66 | 121.8933 | 122.1039 | 121.17 | 122.1588 | 121.3531 | -121.257 | -121.1288 | 121.9116 | 122.0764 | 6.5048 | 34.6664
2766.7656 | 121.9666 | -6.4453 | 114.8529 | -0.20897 | 0.014729 | 0.078047 | 0.12124 | 0.00059812 | 0.029544 | -0.004593 | 0.014954 | 0.0018628 | 0.067169 | 0.17982 | -0.026791 | 0.094981 | 0.020401 | -0.064087 | 115.6631 | -6.5094 | 115.448 | -2.8427 | -0.66834 | 26.8158 | 28.2486 | 115.1459 | -6.3583 | 115.6174 | -1.5244 | 112.8983 | -3.804 | -0.064087 | 0.81024 | 0.59509 | 3.6026 | 33.2611 | 5.777 | 33.3252 | 5.8411 | 0.086975 | 0.29297 | 0.76447 | 4.921 | 2.6413 | 119.3436 | 2.5543 | 119.2566 | 3.6667 | 121.9574 | 4.834 | 121.9757 | 122.1725 | 121.5042 | 122.1085 | 121.5912 | -121.3623 | -121.2112 | 121.8933 | 122.0627 | 6.3812 | 34.6939
2767.8281 | 121.9849 | -6.1569 | 115.0406 | -0.19371 | 0.017079 | 0.078474 | 0.12252 | -0.00025628 | 0.032535 | -0.0041656 | 0.0088502 | 0.0014356 | 0.066956 | 0.18965 | -0.02914 | 0.094768 | 0.013779 | -0.027466 | 115.7959 | -6.2714 | 115.5624 | -2.9114 | -0.88806 | 26.7151 | 28.2944 | 114.9628 | -6.0425 | 115.3976 | -1.5747 | 112.3444 | -3.8773 | -0.11444 | 0.75531 | 0.52185 | 3.2455 | 32.872 | 5.2689 | 32.9865 | 5.3833 | 0.11444 | -0.077819 | 0.35706 | 4.5822 | 2.2797 | 118.5013 | 2.1652 | 118.3868 | 3.36 | 121.8338 | 4.4678 | 121.4401 | 122.0673 | 121.0052 | 121.9528 | 121.1197 | -121.3119 | -121.0831 | 121.7194 | 121.5546 | 6.1295 | 34.4513
2768.7656 | 122.0398 | -5.1544 | 116.2216 | -0.13267 | 0.015156 | 0.083815 | 0.12124 | -0.0011109 | 0.025912 | -0.002243 | 0.024109 | 0.003999 | 0.067597 | 0.19179 | -0.02914 | 0.095195 | 0.01741 | -0.082397 | 117.041 | -5.1773 | 116.7435 | -2.2018 | -0.57678 | 27.5299 | 28.8208 | 116.3635 | -5.0674 | 116.9266 | -0.2655 | 114.2212 | -2.4353 | -0.022888 | 0.8194 | 0.52185 | 2.9526 | 32.6843 | 4.5776 | 32.7072 | 4.6005 | 0.086975 | 0.14191 | 0.70496 | 4.8889 | 2.7191 | 119.3756 | 2.6321 | 119.2886 | 2.9755 | 121.9208 | 4.8019 | 121.994 | 122.2183 | 121.431 | 122.1954 | 121.5179 | -121.3989 | -121.2891 | 121.8979 | 122.081 | 5.072 | 33.9752
2769.8281 | 121.9208 | -6.752 | 114.8849 | -0.17082 | 0.017079 | 0.075911 | 0.11953 | 0.0016663 | 0.032535 | -0.0024566 | 0.033264 | 0.003999 | 0.06482 | 0.18922 | -0.029568 | 0.093486 | 0.015701 | -0.059509 | 115.4297 | -6.8344 | 115.2054 | -2.9846 | -0.65918 | 27.0309 | 28.0289 | 115.004 | -6.6605 | 115.3336 | -1.7166 | 112.5916 | -3.9688 | -0.082398 | 0.54474 | 0.32043 | 3.7674 | 33.783 | 6.0928 | 33.8654 | 6.1752 | 0.091553 | 0.11902 | 0.44861 | 5.0354 | 2.7832 | 119.3436 | 2.6916 | 119.252 | 3.8498 | 122.0398 | 4.9438 | 121.994 | 122.2641 | 121.6644 | 122.1817 | 121.756 | -121.7194 | -121.5454 | 121.9574 | 122.0856 | 6.6925 | 34.7809
2770.7656 | 121.907 | -6.34 | 114.9994 | -0.18608 | 0.016865 | 0.076552 | 0.12188 | 0.00038452 | 0.032748 | -0.0018158 | 0.036316 | 0.001222 | 0.065033 | 0.18602 | -0.0285 | 0.095408 | 0.017624 | -0.032043 | 115.8096 | -6.4224 | 115.6174 | -2.7969 | -0.61798 | 27.1591 | 28.2806 | 115.3793 | -6.2485 | 115.7867 | -1.2726 | 112.9715 | -3.4836 | -0.082397 | 0.81024 | 0.61798 | 3.5431 | 33.4991 | 5.722 | 33.5815 | 5.8044 | 0.091553 | 0.37994 | 0.78735 | 5.0674 | 2.8564 | 119.3115 | 2.7649 | 119.22 | 3.6255 | 122.0398 | 4.9759 | 122.0352 | 122.2321 | 121.6278 | 122.1497 | 121.7194 | -121.4218 | -121.2479 | 121.9574 | 122.1268 | 6.308 | 34.6207
2771.7656 | 121.9437 | -6.5735 | 115.155 | -0.1403 | 0.018147 | 0.079115 | 0.12103 | 0.00017092 | 0.032535 | -0.0024566 | 0.021057 | 0.0027174 | 0.068024 | 0.19072 | -0.027859 | 0.096049 | 0.022324 | -0.082397 | 115.6265 | -6.5323 | 115.3931 | -2.9709 | -0.71411 | 27.1454 | 27.9282 | 115.1825 | -6.459 | 115.5487 | -1.5427 | 112.8204 | -3.7262 | 0.041198 | 0.4715 | 0.23804 | 3.6026 | 33.7189 | 5.8594 | 33.6777 | 5.8182 | 0.11444 | 0.027466 | 0.39368 | 5.0308 | 2.8473 | 119.3939 | 2.7328 | 119.2795 | 3.5614 | 121.9254 | 4.9164 | 122.0078 | 122.1588 | 121.6415 | 122.2 | 121.756 | -121.6873 | -121.6141 | 121.9666 | 122.1222 | 6.4911 | 34.5016
2772.8281 | 149.9954 | -0.082397 | 74.176 | -0.40733 | 0.014729 | 0.072279 | 0.12188 | -0.0013245 | 0.037235 | -0.00053396 | 0.030212 | 0.0031446 | 0.06781 | 0.19243 | -0.029995 | 0.094554 | 0.021683 | 0.032043 | 110.2203 | -13.0463 | 108.7784 | -4.1885 | -0.89722 | 25.8408 | 23.7808 | 108.6777 | -11.673 | 101.0284 | -3.4424 | 116.9403 | -2.2614 | -12.9639 | 36.0443 | 34.6024 | -4.1061 | 25.9232 | -0.81482 | 38.887 | 12.149 | -11.5906 | 34.5016 | 26.8524 | -3.36 | -2.179 | 117.0227 | 9.4116 | 128.6133 | 8.8577 | 121.8246 | 8.2306 | 112.7014 | 123.2666 | 120.3506 | 110.3027 | 108.7601 | -87.2223 | -85.849 | 108.8608 | 101.1108 | 0.11444 | 23.8632
2773.7656 | 122.2961 | -6.2897 | 115.448 | -0.13267 | 0.016865 | 0.078261 | 0.11996 | -0.0030335 | 0.027621 | -0.0030976 | 0.0027466 | 0.0027174 | 0.065247 | 0.18815 | -0.0285 | 0.093913 | 0.020615 | -0.068665 | 115.8737 | -6.2622 | 115.6082 | -2.8702 | -0.7782 | 27.4933 | 28.331 | 115.2878 | -6.2164 | 115.7913 | -1.1398 | 113.0905 | -3.1631 | 0.027466 | 0.42572 | 0.16022 | 3.4195 | 33.783 | 5.5115 | 33.7555 | 5.484 | 0.073242 | -0.16022 | 0.34332 | 5.1498 | 3.1265 | 119.3802 | 3.0533 | 119.3069 | 3.392 | 121.8704 | 5.0766 | 122.0078 | 122.1359 | 121.5042 | 122.1634 | 121.5775 | -121.7102 | -121.6644 | 121.8979 | 122.081 | 6.221 | 34.6207
2774.7656 | 123.9578 | -12.8998 | 20.7413 | 149.1059 | 0.15764 | 0.11372 | 1.7884 | 0.27062 | 3.3471 | 0.046677 | 50.5276 | 0.029634 | 0.012909 | 0.36461 | -0.026577 | 0.089854 | 0.034286 | 0.082397 | 149.9954 | -3.4561 | 76.8265 | 0.8606 | 0.091553 | 116.7252 | 2.1973 | 80.7861 | -0.07782 | 81.0104 | 0.068665 | 91.0904 | -7.251 | 9.4437 | 129.2541 | 56.0852 | 13.7604 | 129.6249 | 12.9913 | 120.1813 | 3.5477 | 12.822 | 60.0449 | 60.2692 | 12.9684 | 5.6488 | 103.9902 | -7.1732 | 91.1682 | 4.3167 | 80.2826 | 0.14649 | 81.0883 | 153.4515 | 80.864 | 162.8952 | 93.6859 | -24.1974 | -20.8191 | 89.7263 | 93.9102 | 12.9822 | 15.097
2775.8281 | 122.2916 | -94.5053 | 27.3743 | -2.6962 | 2.5481 | 2.1733 | 0.12081 | 0.0016663 | 0.50913 | -0.00032036 | 0.054627 | 0.002931 | 0.079987 | 0.17683 | -0.0285 | 0.094768 | 0.022537 | 11.0825 | 27.2552 | -94.3634 | 26.9623 | -42.6865 | -4.541 | -6.7795 | -11.1099 | 27.1866 | -94.6793 | 27.7817 | -80.0217 | 25.1312 | -90.8936 | 0.14191 | -0.11902 | -0.41199 | 51.8188 | 87.7258 | 89.9643 | 87.5839 | 89.8224 | -0.17395 | -0.18768 | 0.40741 | 14.4836 | 3.6118 | 119.6365 | 3.7857 | 119.8105 | 51.6769 | 121.3257 | 14.6576 | 122.4609 | 121.6187 | 121.8658 | 121.7606 | 121.6919 | -121.7377 | -122.0535 | 121.4676 | 122.287 | 105.5878 | 83.3954
2776.7656 | 122.4014 | -73.3475 | 48.5229 | 48.169 | 0.44774 | 0.10112 | 0.12487 | 0.0014527 | 0.39868 | -0.00010676 | 0.0027466 | 0.0061352 | 0.079132 | 0.1826 | -0.027431 | 0.094981 | 0.017624 | 1.4969 | 42.3019 | -73.4711 | 47.5708 | -31.6223 | -4.7974 | 1.7212 | -1.6846 | 47.3053 | -73.0774 | 48.4406 | -61.1069 | 45.6528 | -69.7128 | -0.1236 | -6.221 | -0.95215 | 41.7252 | 75.0687 | 68.5501 | 75.1923 | 68.6737 | 0.27008 | -1.2177 | -0.082397 | 12.2406 | 3.6346 | 119.0002 | 3.3646 | 118.7302 | 41.8488 | 121.0419 | 11.9705 | 121.5179 | 115.773 | 120.3827 | 115.6494 | 120.6528 | -121.994 | -121.6003 | 120.9183 | 121.788 | 74.8444 | 71.6629
2777.7656 | 121.962 | -6.5414 | 114.8117 | -0.20897 | 0.014943 | 0.078261 | 0.12594 | -0.0023925 | 0.032321 | 0.00010684 | 0.011902 | 0.00229 | 0.066101 | 0.18239 | -0.028927 | 0.09669 | 0.016769 | -0.082397 | 115.6311 | -6.5186 | 115.3702 | -2.8976 | -0.63171 | 27.887 | 28.1479 | 114.8392 | -6.4362 | 115.5441 | -1.2543 | 112.793 | -3.978 | 0.022888 | 0.8194 | 0.55847 | 3.6438 | 34.4284 | 5.9097 | 34.4055 | 5.8868 | 0.10529 | 0.027465 | 0.73242 | 5.2872 | 2.5635 | 119.3344 | 2.4582 | 119.2291 | 3.6209 | 121.8887 | 5.1819 | 121.9803 | 122.1497 | 121.2753 | 122.1725 | 121.3806 | -121.3303 | -121.2479 | 121.9116 | 122.0856 | 6.459 | 34.6893
2778.8281 | 121.8613 | -6.6422 | 115.2924 | -0.15556 | 0.016011 | 0.077406 | 0.12231 | 0.00017092 | 0.032321 | -0.0033112 | 0.021057 | 0.0027174 | 0.065247 | 0.1841 | -0.030209 | 0.093913 | 0.023178 | -0.032043 | 115.5075 | -6.6879 | 115.3198 | -2.7237 | -0.5127 | 27.9282 | 28.3127 | 114.9399 | -6.5231 | 115.5212 | -1.2497 | 112.6465 | -3.9917 | -0.045776 | 0.21515 | 0.027466 | 3.9185 | 34.5703 | 6.1295 | 34.6161 | 6.1752 | 0.11902 | -0.35248 | 0.22888 | 5.3925 | 2.6505 | 119.2886 | 2.5314 | 119.1696 | 3.9642 | 122.0078 | 5.2734 | 122.0444 | 122.1954 | 121.463 | 122.1497 | 121.582 | -121.9803 | -121.8155 | 121.962 | 122.1634 | 6.6101 | 34.9548
2779.7656 | 122.0032 | -6.5094 | 115.3519 | -0.18608 | 0.016865 | 0.076338 | 0.12338 | -0.0013245 | 0.032962 | -0.0052338 | 0.0088502 | 0.003999 | 0.066101 | 0.17961 | -0.028927 | 0.093486 | 0.014633 | -0.07782 | 115.7501 | -6.5643 | 115.4388 | -2.7786 | -0.55389 | 28.0838 | 28.2944 | 115.3702 | -6.4453 | 115.6128 | -1.1444 | 112.9349 | -3.9185 | -0.054932 | 0.39825 | 0.086975 | 3.7308 | 34.5932 | 5.9555 | 34.6481 | 6.0104 | 0.064087 | 0.01831 | 0.26093 | 5.365 | 2.5909 | 119.4443 | 2.5269 | 119.3802 | 3.7857 | 122.0032 | 5.3009 | 122.0581 | 122.3145 | 121.8155 | 122.2595 | 121.8796 | -121.9162 | -121.7972 | 121.9482 | 122.1222 | 6.4316 | 34.8038
2780.8281 | 121.8063 | -6.5094 | 115.1505 | -0.27763 | 0.017506 | 0.078261 | 0.12316 | -4.2682e-05 | 0.033176 | -0.0030976 | -0.04303 | 0.0054944 | 0.067169 | 0.18089 | -0.0285 | 0.094768 | 0.016556 | -0.027466 | 115.4663 | -6.5918 | 115.3748 | -2.8244 | -0.64545 | 27.681 | 28.3264 | 114.9445 | -6.4545 | 115.567 | -1.181 | 112.5229 | -3.9551 | -0.082398 | 0.31586 | 0.2243 | 3.685 | 34.1904 | 5.864 | 34.2728 | 5.9463 | 0.054931 | -0.20599 | 0.41657 | 5.3284 | 2.5543 | 119.0323 | 2.4994 | 118.9774 | 3.7674 | 121.9666 | 5.2734 | 122.0215 | 122.0581 | 121.3989 | 121.9757 | 121.4539 | -121.7422 | -121.6049 | 121.8842 | 122.0764 | 6.4819 | 34.8358
2781.7656 | 121.6644 | -6.4865 | 114.7385 | -0.37682 | 0.017079 | 0.07997 | 0.12381 | 0.00038452 | 0.034457 | -0.0037384 | -0.067444 | 0.0027174 | 0.065247 | 0.19221 | -0.029354 | 0.097545 | 0.01741 | -0.009155 | 115.5441 | -6.6055 | 115.3793 | -2.829 | -0.70496 | 27.4429 | 28.5324 | 114.9673 | -6.5552 | 115.5533 | -1.1261 | 112.4451 | -3.9322 | -0.11902 | 0.80566 | 0.64087 | 3.6575 | 33.9294 | 5.7816 | 34.0485 | 5.9006 | -0.068665 | 0.22888 | 0.81482 | 5.3604 | 2.5543 | 118.9316 | 2.623 | 119.0002 | 3.7766 | 121.9849 | 5.4291 | 122.1085 | 122.1497 | 121.5225 | 122.0306 | 121.4539 | -121.344 | -121.2936 | 121.8658 | 122.0398 | 6.4774 | 35.0189
2782.7656 | 122.1039 | -5.484 | 115.9241 | -0.18608 | 0.016438 | 0.08296 | 0.12487 | -0.0026063 | 0.02933 | -0.0033112 | 0.039368 | 0.0042126 | 0.067597 | 0.19008 | -0.0285 | 0.093272 | 0.019546 | -0.068665 | 116.716 | -5.5847 | 116.4642 | -2.33 | -0.42114 | 28.4592 | 28.9261 | 116.5741 | -5.4932 | 116.6794 | -0.082397 | 114.0289 | -2.7695 | -0.10071 | 0.79193 | 0.54016 | 3.154 | 33.9432 | 5.0629 | 34.0439 | 5.1636 | -0.009155 | 0.65002 | 0.75531 | 5.4016 | 2.7145 | 119.5129 | 2.7237 | 119.5221 | 3.2547 | 122.0489 | 5.4108 | 122.1725 | 122.3007 | 122.0673 | 122.2 | 122.0581 | -121.5088 | -121.4172 | 121.9482 | 122.1634 | 5.4153 | 34.4101
2783.8281 | 121.7514 | -6.5735 | 115.1138 | -0.22423 | 0.017934 | 0.080397 | 0.12402 | 0.0027343 | 0.032535 | -0.0037384 | -0.10406 | 0.0089124 | 0.066956 | 0.1873 | -0.030849 | 0.093486 | 0.013351 | 0.004578 | 115.2924 | -6.7886 | 115.3427 | -2.9114 | -0.6546 | 27.7313 | 28.6743 | 115.0177 | -6.601 | 115.4984 | -1.0986 | 112.4084 | -4.0833 | -0.21515 | 0.17853 | 0.22888 | 3.6621 | 34.3048 | 5.9189 | 34.52 | 6.134 | -0.027466 | -0.096131 | 0.38452 | 5.4749 | 2.4902 | 118.9819 | 2.5177 | 119.0094 | 3.8773 | 122.1313 | 5.5023 | 122.0993 | 122.081 | 121.6187 | 121.8658 | 121.5912 | -121.9025 | -121.7148 | 121.9162 | 122.0718 | 6.5781 | 35.2478
2784.7656 | 122.406 | -5.6305 | 116.3132 | -0.10216 | 0.015584 | 0.083815 | 0.12316 | -0.00046988 | 0.028049 | -0.002243 | -0.027771 | 0.0050672 | 0.06546 | 0.19264 | -0.031277 | 0.095408 | 0.020187 | -0.032043 | 116.1896 | -5.5206 | 116.3681 | -2.3392 | -0.64087 | 28.4271 | 29.1367 | 115.7227 | -5.452 | 116.5512 | -0.064087 | 113.5574 | -3.0258 | 0.10986 | -0.1236 | 0.054932 | 3.2913 | 34.0576 | 4.9896 | 33.9478 | 4.8798 | 0.17853 | -0.59051 | 0.23804 | 5.5664 | 2.6047 | 119.1879 | 2.4261 | 119.0094 | 3.1815 | 121.8887 | 5.3879 | 122.0032 | 121.7102 | 121.1746 | 121.8201 | 121.3531 | -121.8338 | -121.7651 | 121.9986 | 122.1817 | 5.5985 | 34.7672
2785.8438 | 116.3727 | -6.4453 | 102.0767 | -0.48363 | 0.018361 | 0.074843 | 0.1221 | 0.0016663 | 0.033389 | -0.0013886 | -0.027771 | 0.006349 | 0.068451 | 0.18217 | -0.026577 | 0.09669 | 0.016556 | -0.12817 | 115.4709 | -6.4041 | 115.2878 | -3.0579 | -0.97046 | 28.656 | 28.8437 | 115.7089 | -6.3034 | 114.7476 | -1.1581 | 107.1762 | -4.0283 | 0.041198 | 13.3942 | 13.2111 | 3.3875 | 35.1013 | 5.4749 | 35.0601 | 5.4337 | 0.14191 | 13.6322 | 12.6709 | 5.2872 | 2.417 | 113.6215 | 2.2751 | 113.4796 | 3.3463 | 121.6919 | 5.1453 | 121.051 | 121.875 | 122.0123 | 121.9162 | 122.1542 | -108.4808 | -108.3801 | 121.7331 | 121.1929 | 6.3171 | 35.289
2786.7656 | 122.0169 | -6.7932 | 115.0681 | -0.15556 | 0.017079 | 0.076125 | 0.12316 | -0.0017517 | 0.034885 | -0.0026704 | 0.0027466 | 0.0072034 | 0.069306 | 0.18794 | -0.031277 | 0.095836 | 0.018265 | -0.059509 | 115.4572 | -6.7245 | 115.1916 | -3.0167 | -0.58594 | 28.3768 | 28.8437 | 114.9078 | -6.6559 | 115.3336 | -1.0757 | 112.5687 | -3.8727 | 0.068665 | 0.3891 | 0.1236 | 3.7765 | 35.17 | 6.2073 | 35.1013 | 6.1386 | 0.13733 | -0.16022 | 0.2655 | 5.7175 | 2.9205 | 119.3619 | 2.7832 | 119.2245 | 3.7079 | 121.9162 | 5.5801 | 121.9894 | 122.1817 | 121.5637 | 122.2504 | 121.701 | -121.7926 | -121.7239 | 121.9849 | 122.1268 | 6.7337 | 35.6369
2787.7656 | 97.7783 | -5.4245 | 96.3638 | -0.65147 | 0.010884 | 0.076338 | 0.086635 | -0.0047425 | 0.029544 | -0.006302 | -0.22308 | -0.005614 | 0.06012 | 0.1873 | -0.037044 | 0.085582 | 0.0024567 | -0.082397 | 114.743 | -6.4636 | 114.7202 | -3.2547 | 0.086975 | 13.5635 | 28.6606 | 107.0663 | -6.9809 | 99.9756 | -1.0208 | 87.6709 | 0.050354 | -1.0391 | 18.3792 | 18.3563 | 2.1698 | 18.988 | 5.5115 | 20.0272 | 6.5506 | -1.5564 | 10.7025 | 3.6118 | 4.4037 | 5.4749 | 93.0954 | 7.0312 | 94.6518 | 3.2089 | 121.1838 | 5.9601 | 106.9565 | 121.2067 | 114.0472 | 120.1675 | 112.4908 | -102.8275 | -103.3447 | 120.1447 | 105.4001 | 5.3421 | 34.0851
2788.8281 | 122.2733 | -6.5414 | 114.8712 | -0.23186 | 0.017293 | 0.080824 | 0.12124 | -0.0013245 | 0.032108 | -0.0016022 | -0.018616 | 0.0048536 | 0.066956 | 0.18516 | -0.028927 | 0.093913 | 0.018478 | -0.036621 | 115.6403 | -6.5918 | 115.4572 | -2.8564 | -0.54474 | 28.5828 | 29.155 | 115.0818 | -6.4224 | 115.6174 | -0.66834 | 112.7151 | -3.4973 | -0.050354 | 0.76904 | 0.58594 | 3.685 | 35.1242 | 5.9967 | 35.1746 | 6.0471 | 0.11902 | 0.21057 | 0.74616 | 5.8731 | 3.0441 | 119.2566 | 2.9251 | 119.1376 | 3.7354 | 122.049 | 5.7541 | 122.0398 | 122.2321 | 121.5042 | 122.1817 | 121.6232 | -121.463 | -121.2936 | 121.9986 | 122.1588 | 6.5048 | 35.6964
2789.7656 | 122.4564 | -108.7006 | 13.3209 | -1.773 | 1.5742 | 0.92464 | 0.12274 | 0.0025207 | 0.67533 | -0.001175 | 0.011902 | 0.0052808 | 0.083832 | 0.18004 | -0.0285 | 0.097331 | 0.02446 | 0.64087 | 13.028 | -108.7097 | 13.1287 | -48.2849 | 9.1324 | -12.2589 | -17.8711 | 13.2477 | -108.8882 | 13.2614 | -92.0929 | 10.9314 | -104.512 | -0.009155 | -0.29297 | -0.19226 | 60.4157 | 96.4417 | 117.8329 | 96.4508 | 117.8421 | -0.18768 | -0.073242 | -0.059509 | 16.6077 | 4.1885 | 119.632 | 4.3762 | 119.8196 | 60.4248 | 121.8384 | 16.7953 | 122.1497 | 121.7377 | 122.1359 | 121.7285 | 121.9482 | -122.0306 | -122.2092 | 121.8292 | 121.962 | 109.3414 | 90.8295
2790.7656 | 122.1863 | -93.2739 | 28.6331 | -2.8182 | 2.6861 | 2.0551 | 0.12359 | -0.00068368 | 0.67426 | 0.0016022 | -0.012512 | 0.0065626 | 0.081696 | 0.17406 | -0.028927 | 0.096049 | 0.022537 | 1.0666 | 28.7247 | -92.8848 | 28.6423 | -37.9028 | 24.2661 | -5.3146 | -9.906 | 28.83 | -93.1503 | 28.7338 | -78.2867 | 26.239 | -89.3188 | 0.3891 | 0.091552 | 0.009155 | 55.3711 | 87.9593 | 117.54 | 87.5702 | 117.1509 | 0.1236 | 0.19684 | 0.10071 | 14.9872 | 3.9551 | 119.5129 | 3.8315 | 119.3893 | 54.982 | 121.5271 | 14.8636 | 121.8842 | 121.6095 | 121.9803 | 121.9986 | 122.1039 | -121.5179 | -121.7834 | 121.9162 | 122.0078 | 94.3405 | 83.3679
2791.8281 | 122.1451 | -119.7006 | 2.1881 | -0.10216 | 0.057881 | 0.0024246 | 0.056941 | 0.0025207 | -0.0020722 | -0.00032036 | -0.10406 | 0.0016492 | 0.083405 | 0.16743 | -0.028927 | 0.093913 | 0.024033 | -0.064087 | 2.211 | -0.13733 | 1.8631 | -0.10529 | 0.43945 | -7.8415 | -20.3156 | 2.1835 | -119.8425 | 1.9089 | -101.7609 | -0.31586 | -106.1096 | 119.5633 | 0.022889 | -0.32501 | 119.5953 | 111.8591 | 120.1401 | -7.7042 | 0.57678 | -0.14191 | -0.004577 | -0.27923 | 17.9398 | 13.591 | 119.3848 | 13.7329 | 119.5267 | 0.032043 | 2.0004 | 18.0817 | 121.7514 | 2.3483 | 122.0261 | 121.9116 | 121.8842 | -2.3254 | -122.0306 | 121.5637 | 121.6095 | 119.6365 | 99.3851
2792.7656 | 122.2137 | -119.1834 | 2.8198 | -0.079269 | 0.057454 | -0.00035239 | 0.047969 | 0.00038452 | 0.001773 | -0.0013886 | -0.29022 | -0.010527 | 0.083405 | 0.17747 | -0.03149 | 0.083873 | 0.011429 | -0.050354 | 2.8015 | -0.054932 | 2.5269 | 0.032043 | 0.99792 | -7.5531 | -20.1096 | 2.8015 | -119.2795 | 2.5955 | -101.1703 | 0.31128 | -101.4862 | 119.1284 | -0.01831 | -0.29297 | 119.2154 | 111.6302 | 120.1813 | -7.4982 | 1.0529 | -0.09613 | -0.01831 | -0.2243 | 18.013 | 17.6971 | 119.4946 | 17.7933 | 119.5908 | 0.086975 | 2.5818 | 18.1091 | 121.875 | 2.8564 | 122.081 | 121.9849 | 121.9849 | -2.8748 | -122.0993 | 121.7102 | 121.7789 | 119.133 | 99.0738
2793.8281 | 122.3419 | -118.8171 | 3.1677 | -0.11742 | 0.058736 | -0.002275 | 0.059291 | 0.00017092 | 0.0036956 | -0.0041656 | 0.13702 | 0.0016492 | 0.084259 | 0.17149 | -0.028927 | 0.094768 | 0.022751 | 0.009155 | 3.1677 | 0.10986 | 3.0029 | 0.064087 | 1.3916 | -6.6971 | -20.3705 | 3.1174 | -118.9224 | 3.0533 | -100.8774 | 0.80566 | -114.5096 | 118.927 | 0 | -0.16479 | 118.8812 | 112.1201 | 120.2087 | -6.8069 | 1.2817 | -0.10529 | -0.050354 | -0.11444 | 17.9398 | 4.3076 | 119.6228 | 4.4128 | 119.7281 | -0.045776 | 2.8931 | 18.045 | 121.9757 | 3.0579 | 122.0398 | 121.9849 | 121.9345 | -3.0579 | -122.0901 | 121.8201 | 121.8704 | 118.8263 | 98.4467
2794.7656 | 122.287 | -118.8217 | 3.2089 | -0.19371 | 0.057881 | 0.0011428 | 0.059932 | 0.00038452 | 0.0054046 | 0.00074764 | -0.033874 | 0.0033582 | 0.087677 | 0.1747 | -0.029781 | 0.097545 | 0.019974 | -0.004578 | 3.2043 | 0.15106 | 3.0304 | 0.11444 | 1.2863 | -6.8024 | -20.4712 | 3.1906 | -118.8492 | 3.0899 | -100.6119 | 0.82855 | -114.418 | 118.9728 | -0.004577 | -0.17853 | 118.9362 | 112.0193 | 120.108 | -6.9534 | 1.1353 | -0.027466 | -0.01831 | -0.11902 | 18.2098 | 4.4037 | 119.6503 | 4.4312 | 119.6777 | -0.036621 | 2.8793 | 18.2373 | 121.9391 | 3.0533 | 122.0398 | 122.0261 | 122.0123 | -3.0579 | -122.0581 | 121.8521 | 121.9116 | 118.8171 | 98.3505
2795.7656 | 122.3099 | -118.6523 | 3.3875 | -0.20897 | 0.057454 | 0.00071561 | 0.061214 | 0.0025207 | 0.0019866 | -0.002243 | -0.046081 | 0.0027174 | 0.086182 | 0.17619 | -0.029568 | 0.096477 | 0.022324 | 0.009155 | 3.3646 | 0.33875 | 3.2043 | 0.14191 | 1.4557 | -6.7429 | -20.6818 | 3.3646 | -118.7256 | 3.273 | -100.2136 | 0.99335 | -114.1983 | 118.9911 | -0.022888 | -0.1831 | 118.7943 | 111.9095 | 120.108 | -7.0816 | 1.1169 | -0.073242 | -0.022888 | -0.11444 | 18.4387 | 4.454 | 119.6457 | 4.5273 | 119.7189 | -0.19684 | 2.8656 | 18.512 | 121.9986 | 3.0258 | 122.0901 | 122.0169 | 122.0169 | -3.0487 | -122.113 | 121.8567 | 121.9254 | 118.6615 | 97.9706
2796.7656 | 122.2824 | -118.6523 | 3.4378 | -0.19371 | 0.058949 | -0.001207 | 0.059932 | -0.00025628 | 0.0047638 | -0.0024566 | -0.055237 | 0.0033582 | 0.088959 | 0.17299 | -0.030209 | 0.095408 | 0.022324 | -0.032043 | 3.4241 | 0.34332 | 3.2227 | -0.07782 | 1.4145 | -6.7932 | -20.8282 | 3.3325 | -118.7302 | 3.241 | -100.0351 | 1.0071 | -114.1708 | 118.9957 | -0.013733 | -0.21515 | 118.5745 | 111.8591 | 120.0668 | -7.1365 | 1.0712 | -0.07782 | -0.10528 | -0.19684 | 18.6172 | 4.4815 | 119.6594 | 4.5593 | 119.7372 | -0.42114 | 2.8793 | 18.6951 | 121.9711 | 3.0807 | 122.0627 | 122.0764 | 121.9849 | -3.0945 | -122.168 | 121.875 | 121.8933 | 118.6203 | 97.8241
2797.7656 | 122.3053 | -118.6066 | 3.4927 | -0.10979 | 0.058308 | -0.001207 | 0.060359 | -0.0028199 | 0.004123 | -0.0033112 | 0.0088502 | 0.00229 | 0.088104 | 0.16701 | -0.029568 | 0.096049 | 0.025101 | 0.027466 | 3.4607 | 0.33875 | 3.3142 | 0.24719 | 1.5427 | -6.6376 | -20.9335 | 3.4744 | -118.6478 | 3.3325 | -99.765 | 1.0666 | -114.2532 | 118.9453 | -0.032044 | -0.17853 | 118.8538 | 111.969 | 120.1492 | -6.9763 | 1.2039 | -0.041199 | -0.018311 | -0.16022 | 18.8416 | 4.3533 | 119.6732 | 4.3945 | 119.7144 | -0.091553 | 2.9755 | 18.8828 | 121.9803 | 3.1219 | 122.1222 | 122.0673 | 122.081 | -3.154 | -122.1405 | 121.9208 | 121.9391 | 118.634 | 97.673
2798.7656 | 122.3053 | -118.6386 | 3.4744 | -0.20134 | 0.061085 | -0.0020614 | 0.060786 | 0.0038025 | 0.002414 | -0.003952 | -0.039978 | 0.0037854 | 0.087036 | 0.17363 | -0.031063 | 0.095195 | 0.02681 | 0 | 3.4287 | 0.32044 | 3.273 | 0.17853 | 1.4786 | -6.6742 | -21.0846 | 3.4424 | -118.689 | 3.3051 | -99.7055 | 1.0254 | -114.2303 | 118.959 | -0.045776 | -0.20142 | 118.8171 | 111.9644 | 120.1172 | -6.9946 | 1.1581 | -0.050354 | -0.032043 | -0.16937 | 18.9331 | 4.4083 | 119.664 | 4.4586 | 119.7144 | -0.14191 | 2.9526 | 18.9835 | 121.994 | 3.1082 | 122.1313 | 122.0673 | 122.081 | -3.154 | -122.1634 | 121.9116 | 121.9437 | 118.6386 | 97.554
2799.7656 | 122.3053 | -118.5974 | 3.4836 | -0.16319 | 0.061085 | -0.00077979 | 0.059932 | 0.0016663 | 0.0022004 | 0.00010684 | -0.055237 | 0.0025036 | 0.086395 | 0.16829 | -0.0285 | 0.095622 | 0.025101 | -0.013733 | 3.4607 | 0.31586 | 3.273 | 0.086975 | 1.4557 | -6.6833 | -21.2814 | 3.4698 | -118.6752 | 3.2913 | -99.5544 | 1.0345 | -114.1983 | 118.9133 | -0.022889 | -0.21057 | 118.6844 | 111.9141 | 120.0531 | -6.9992 | 1.1398 | -0.07782 | -0.013733 | -0.19226 | 19.043 | 4.3991 | 119.632 | 4.4769 | 119.7098 | -0.22888 | 2.9572 | 19.1208 | 121.9666 | 3.1448 | 122.1451 | 122.0581 | 122.0673 | -3.1677 | -122.1588 | 121.8704 | 121.8887 | 118.5837 | 97.316
2800.7656 | 122.3007 | -118.6249 | 3.4927 | -0.11742 | 0.061085 | 0.00071561 | 0.059505 | -4.2682e-05 | 0.003482 | -0.0013886 | -0.024719 | 0.0014356 | 0.087677 | 0.17641 | -0.030422 | 0.097117 | 0.024673 | -0.004578 | 3.4698 | 0.31586 | 3.2867 | 0.07782 | 1.4648 | -6.6513 | -21.3867 | 3.4607 | -118.6707 | 3.3005 | -99.4263 | 1.0483 | -114.1479 | 118.9407 | -0.022888 | -0.20599 | 118.7027 | 111.9736 | 120.0897 | -6.9672 | 1.149 | -0.045776 | -0.032044 | -0.19226 | 19.1986 | 4.4769 | 119.6732 | 4.5227 | 119.7189 | -0.23804 | 2.9709 | 19.2444 | 121.9711 | 3.154 | 122.1313 | 122.0947 | 122.0856 | -3.1769 | -122.1634 | 121.9116 | 121.9254 | 118.6203 | 97.2382
2801.7656 | 122.3099 | -118.6066 | 3.4744 | -0.22423 | 0.061299 | -0.00013879 | 0.059505 | 0.0010253 | 0.0054046 | -0.001175 | -0.079651 | 0.0037854 | 0.088959 | 0.17363 | -0.030636 | 0.096477 | 0.027664 | -0.009155 | 3.4653 | 0.29755 | 3.3096 | 0.14648 | 1.474 | -6.6147 | -21.4828 | 3.479 | -118.689 | 3.3188 | -99.2661 | 1.03 | -113.0951 | 118.9041 | -0.009155 | -0.16479 | 118.7531 | 111.9919 | 120.0806 | -6.9122 | 1.1765 | -0.082398 | 0.004578 | -0.15564 | 19.3405 | 5.5115 | 119.6365 | 5.5939 | 119.7189 | -0.15106 | 3.0121 | 19.4229 | 122.0078 | 3.1677 | 122.168 | 122.0718 | 122.0856 | -3.1769 | -122.1634 | 121.9162 | 121.9254 | 118.5974 | 97.1237
2802.7656 | 122.3007 | -118.5425 | 3.5522 | -0.14793 | 0.061085 | -0.00035239 | 0.060573 | 0.0014527 | 0.0049774 | -0.002884 | -0.3421 | -0.003905 | 0.0896 | 0.214 | -0.033199 | 0.09135 | 0.066757 | -0.009155 | 3.4149 | 0.21973 | 3.1769 | 0.091553 | 1.4053 | -7.0953 | -21.8216 | 3.4012 | -118.7576 | 3.3051 | -101.5686 | 1.062 | -150 | 118.7622 | -0.13733 | -0.37537 | 118.634 | 111.4471 | 119.9478 | -7.3151 | 1.1856 | -0.21515 | -0.15106 | -0.24719 | 16.9739 | -31.4575 | 119.6045 | -31.2424 | 119.8196 | -0.12817 | 2.9572 | 17.189 | 122.0627 | 3.1952 | 122.1588 | 121.9574 | 121.9437 | -3.3325 | -122.3099 | 121.7194 | 121.8475 | 118.5333 | 96.7209
2803.8281 | 122.4106 | -118.7439 | 3.4378 | -0.18608 | 0.061513 | 0.0013564 | 0.059718 | -0.0011109 | 0.004123 | -0.0035248 | -0.049133 | 0.0042126 | 0.092591 | 0.16786 | -0.028927 | 0.096477 | 0.024887 | -0.018311 | 3.479 | 0.46234 | 3.2593 | 0.23346 | 1.4328 | -6.6513 | -21.9131 | 3.4653 | -118.7119 | 3.2913 | -99.9435 | 0.95215 | -114.1708 | 119.2062 | 0.041199 | -0.17853 | 118.9774 | 112.0926 | 120.1767 | -7.1136 | 0.97046 | 0.032043 | 0.027466 | -0.14648 | 18.8004 | 4.5731 | 119.696 | 4.541 | 119.664 | -0.22888 | 2.7969 | 18.7683 | 122.0032 | 3.0167 | 122.1771 | 122.2229 | 122.2092 | -2.9755 | -122.1497 | 122.0032 | 122.0352 | 118.7256 | 96.8307
2804.7656 | 122.3877 | -118.634 | 3.4561 | -0.19371 | 0.060872 | 0.0019974 | 0.060359 | 0.00081172 | 0.0030548 | -0.0026704 | -0.13458 | 0.0059216 | 0.087464 | 0.1794 | -0.028713 | 0.098185 | 0.031296 | -0.004578 | 3.4607 | 0.44403 | 3.3371 | 0.28381 | 1.474 | -6.7154 | -21.9955 | 3.479 | -118.6844 | 3.2684 | -99.9435 | 1.2085 | -113.7131 | 119.0781 | 0.004577 | -0.11902 | 118.9178 | 111.9186 | 120.108 | -7.1594 | 1.03 | -0.050354 | 0.022888 | -0.18768 | 18.6905 | 4.921 | 119.8425 | 4.9713 | 119.8929 | -0.16022 | 2.8931 | 18.7408 | 121.9528 | 3.0167 | 122.1634 | 122.0947 | 122.113 | -3.0121 | -122.1405 | 121.9711 | 121.9025 | 118.6295 | 96.6385
2805.7656 | 122.3648 | -118.5745 | 3.5202 | -0.22423 | 0.061513 | 0.0011428 | 0.057582 | -0.00068368 | 0.0054046 | -0.0016022 | -0.097961 | 0.0033582 | 0.091522 | 0.17 | -0.03149 | 0.096263 | 0.028305 | -0.15106 | 3.4653 | 0.42114 | 3.3325 | 0.21057 | 1.4832 | -6.6971 | -22.0734 | 3.4744 | -118.689 | 3.392 | -99.6597 | 1.1215 | -113.7451 | 118.9957 | -0.054932 | -0.18768 | 118.7851 | 111.8774 | 120.0577 | -7.1182 | 1.062 | -0.11444 | -0.045777 | -0.12817 | 18.9148 | 4.8294 | 119.696 | 4.9438 | 119.8105 | -0.21057 | 2.9114 | 19.0292 | 122.081 | 3.0441 | 122.1634 | 122.0398 | 122.0489 | -3.0991 | -122.2092 | 121.907 | 121.9666 | 118.4235 | 96.5012
2806.7656 | 122.3557 | -118.5745 | 3.5522 | -0.19371 | 0.060231 | 0.00028841 | 0.059077 | 0.0018799 | 0.0036956 | -0.0043792 | -0.10406 | 0.0054944 | 0.089173 | 0.17726 | -0.031277 | 0.096049 | 0.028091 | -0.013733 | 3.5248 | 0.46234 | 3.3875 | 0.19684 | 1.5198 | -6.6971 | -22.2061 | 3.5294 | -118.634 | 3.4241 | -99.5316 | 1.149 | -113.3972 | 119.0369 | -0.027466 | -0.16479 | 118.7714 | 111.8774 | 120.0943 | -7.1594 | 1.0574 | -0.059509 | -0.022888 | -0.12817 | 19.043 | 5.1773 | 119.7235 | 5.2368 | 119.783 | -0.2655 | 2.9251 | 19.1025 | 122.0581 | 3.0624 | 122.1634 | 122.0993 | 122.1039 | -3.0899 | -122.1863 | 121.962 | 121.9986 | 118.5608 | 96.3684
2807.7656 | 122.3877 | -118.5654 | 3.5477 | -0.36156 | 0.062154 | 7.4814e-05 | 0.058864 | -0.0028199 | 0.0030548 | -0.0033112 | -0.12848 | 0.0061352 | 0.089386 | 0.17747 | -0.029354 | 0.098399 | 0.026596 | 0.082397 | 3.4653 | 0.40741 | 3.3737 | 0.19684 | 1.506 | -6.6925 | -22.348 | 3.4882 | -118.6661 | 3.4149 | -99.4949 | 1.1307 | -113.1409 | 118.9728 | -0.082397 | -0.17395 | 118.7622 | 111.8729 | 120.0714 | -7.0999 | 1.0986 | -0.10071 | -0.059509 | -0.13275 | 19.0704 | 5.4245 | 119.696 | 5.5252 | 119.7968 | -0.21057 | 2.9663 | 19.1711 | 122.081 | 3.0579 | 122.1542 | 122.0306 | 122.0535 | -3.1403 | -122.2137 | 121.9391 | 121.9803 | 118.6478 | 96.2173
2808.7656 | 122.3602 | -118.5699 | 3.5568 | -0.17845 | 0.062794 | 0.00092921 | 0.060146 | -0.0019653 | 0.0043366 | -0.0067292 | -0.16815 | 0.0054944 | 0.088959 | 0.17555 | -0.029354 | 0.098826 | 0.02681 | -0.064087 | 3.5522 | 0.4303 | 3.3279 | 0.10071 | 1.4374 | -6.6833 | -22.5082 | 3.5477 | -118.6615 | 3.4103 | -98.735 | 1.1261 | -113.5757 | 119.0002 | -0.004578 | -0.22888 | 118.6707 | 111.8866 | 120.0073 | -7.1136 | 1.0071 | -0.091553 | -0.009156 | -0.14649 | 19.8349 | 4.9942 | 119.696 | 5.0858 | 119.7876 | -0.32959 | 2.8976 | 19.9265 | 122.0718 | 3.1219 | 122.2092 | 122.1222 | 122.1176 | -3.1265 | -122.2183 | 121.8979 | 121.9803 | 118.5059 | 96.0617
2809.7656 | 122.3785 | -118.5654 | 3.5568 | -0.19371 | 0.063435 | -0.00077979 | 0.058223 | 0.0063659 | 0.002414 | -0.0033112 | -0.15594 | 0.0048536 | 0.090668 | 0.18089 | -0.031277 | 0.097972 | 0.0298 | -0.032043 | 3.5568 | 0.42114 | 3.3691 | 0.16479 | 1.4832 | -6.6376 | -21.2265 | 3.5385 | -118.6386 | 3.4424 | -98.6618 | 1.1673 | -113.4567 | 118.9865 | 0 | -0.18768 | 118.7302 | 111.9278 | 120.0485 | -7.0587 | 1.062 | -0.073242 | -0.018311 | -0.11444 | 19.9036 | 5.1086 | 119.7327 | 5.1819 | 119.8059 | -0.25635 | 2.948 | 19.9768 | 122.081 | 3.1357 | 122.1771 | 122.1222 | 122.1039 | -3.1357 | -122.1954 | 121.9345 | 122.0078 | 118.5333 | 97.3389
2810.7656 | 122.287 | -118.6295 | 3.5568 | -0.20897 | 0.060658 | -0.00035239 | 0.060786 | 0.0012391 | 0.0036956 | -0.00096136 | -0.20782 | 0.074067 | 0.090882 | 0.18132 | -0.030209 | 0.097331 | 0.094314 | -0.050354 | 3.5706 | 0.40283 | 3.2501 | 0.013733 | 1.387 | -6.5002 | -22.7921 | 3.5339 | -118.7027 | 3.3096 | -98.1857 | 1.0117 | -101.2619 | 119.0323 | 0.013733 | -0.3067 | 118.6432 | 112.1292 | 120.0165 | -6.9031 | 0.98419 | -0.073242 | -0.022888 | -0.24719 | 20.4437 | 17.3676 | 119.6411 | 17.4408 | 119.7144 | -0.3891 | 2.8473 | 20.517 | 122.0123 | 3.1677 | 122.2366 | 122.2 | 122.1634 | -3.154 | -122.2595 | 121.8796 | 121.9391 | 118.5791 | 95.8374
2811.7656 | 122.3465 | -118.5287 | 3.5889 | -0.22423 | 0.062367 | 0.00028841 | 0.059077 | -0.0021789 | 0.0047638 | -0.00074776 | -0.11627 | 0.0048536 | 0.092163 | 0.17363 | -0.02914 | 0.095622 | 0.029159 | -0.009155 | 3.5477 | 0.44403 | 3.3783 | 0.17853 | 1.5015 | -6.4774 | -22.7783 | 3.5522 | -118.6203 | 3.4378 | -97.9523 | 1.1581 | -113.0173 | 118.9728 | -0.041199 | -0.21057 | 118.7073 | 112.0514 | 120.0302 | -6.9214 | 1.0574 | -0.091552 | -0.036621 | -0.15106 | 20.5765 | 5.5115 | 119.6869 | 5.603 | 119.7784 | -0.2655 | 2.9343 | 20.668 | 122.0581 | 3.1036 | 122.1725 | 122.0764 | 122.081 | -3.1448 | -122.2092 | 121.907 | 121.9666 | 118.5196 | 95.7504
2812.7656 | 122.3511 | -118.5928 | 3.5568 | -0.15556 | 0.061513 | -0.0014206 | 0.059291 | -0.0013245 | 0.002414 | -0.00010676 | -0.159 | 0.0061352 | 0.092591 | 0.20546 | -0.028927 | 0.097972 | 0.04924 | -0.054932 | 3.5477 | 0.36163 | 3.3142 | 0.050354 | 1.4099 | -6.5277 | -22.8928 | 3.5248 | -118.6844 | 3.392 | -97.8424 | 1.1169 | -109.6298 | 118.9545 | -0.009156 | -0.24262 | 118.6432 | 112.0651 | 120.0027 | -6.8893 | 1.0483 | -0.091553 | -0.032044 | -0.1648 | 20.7504 | 8.963 | 119.7098 | 9.0546 | 119.8013 | -0.31128 | 2.9526 | 20.842 | 122.0764 | 3.186 | 122.2092 | 122.1405 | 122.1176 | -3.1952 | -122.2412 | 121.907 | 121.9849 | 118.5379 | 95.7001
2813.7656 | 122.2916 | -118.5699 | 3.6026 | -0.17845 | 0.062154 | 0.00028841 | 0.059291 | 0.0020935 | 0.0039094 | -0.0037384 | -0.16815 | 0.0044262 | 0.094086 | 0.19115 | -0.030422 | 0.096477 | 0.039413 | -0.059509 | 3.5843 | 0.3479 | 3.2959 | 0.018311 | 1.3824 | -6.5643 | -23.0072 | 3.5797 | -118.6661 | 3.3646 | -98.291 | 1.0757 | -111.5891 | 118.9178 | -0.01831 | -0.3067 | 118.5883 | 112.0056 | 119.9524 | -6.9122 | 1.0345 | -0.096131 | -0.022888 | -0.23804 | 20.2789 | 6.9809 | 119.6457 | 7.077 | 119.7418 | -0.32959 | 2.948 | 20.3751 | 122.0306 | 3.2364 | 122.2458 | 122.1542 | 122.1497 | -3.2547 | -122.2687 | 121.8658 | 121.9345 | 118.5104 | 95.5627
2814.7656 | 122.2916 | -118.5928 | 3.5751 | -0.17082 | 0.063222 | -0.00056619 | 0.061214 | 0.0018799 | 0.0043366 | -0.0024566 | -0.1651 | 0.0052808 | 0.092591 | 0.19264 | -0.030849 | 0.096049 | 0.038559 | -0.059509 | 3.5843 | 0.34332 | 3.2684 | -0.018311 | 1.3733 | -6.5552 | -23.1171 | 3.5614 | -118.6981 | 3.3188 | -98.2498 | 1.0391 | -111.5616 | 118.9362 | 0.009156 | -0.3067 | 118.5745 | 112.0377 | 119.9661 | -6.8985 | 1.03 | -0.10529 | -0.013733 | -0.25635 | 20.343 | 7.0312 | 119.632 | 7.1365 | 119.7372 | -0.36163 | 2.9251 | 20.4483 | 122.0169 | 3.241 | 122.2595 | 122.1771 | 122.1542 | -3.2318 | -122.2733 | 121.8613 | 121.9116 | 118.5333 | 95.4758
2815.7656 | 122.2687 | -118.6523 | 3.5889 | -0.16319 | 0.065144 | 0.00050201 | 0.058864 | 0.00038452 | 0.005191 | -0.0037384 | -0.14679 | 0.0089124 | 0.093018 | 0.18922 | -0.030209 | 0.09669 | 0.043472 | -0.082397 | 3.6072 | 0.33875 | 3.3005 | 0.1831 | 1.4282 | -6.6193 | -23.2407 | 3.5751 | -118.6798 | 3.3142 | -97.9706 | 0.98419 | -106.2332 | 118.9911 | 0.018311 | -0.28839 | 118.8354 | 112.0331 | 120.0806 | -6.958 | 1.0895 | -0.027466 | -0.013733 | -0.27466 | 20.6818 | 12.4191 | 119.6365 | 12.4466 | 119.664 | -0.15564 | 2.9617 | 20.7092 | 121.994 | 3.2684 | 122.2549 | 122.2595 | 122.2275 | -3.2501 | -122.2687 | 121.9528 | 121.9666 | 118.5699 | 95.4117
2816.7656 | 122.438 | -118.6111 | 3.5934 | -0.14793 | 0.063222 | -0.0018478 | 0.059932 | -0.00025628 | 0.002414 | -0.0013886 | -0.18951 | 0.007417 | 0.093659 | 0.1905 | -0.031063 | 0.097117 | 0.037491 | -0.082397 | 3.5797 | 0.30212 | 3.2181 | -0.059509 | 1.3092 | -6.4362 | -23.3597 | 3.5202 | -118.7531 | 3.3051 | -98.1491 | 0.84686 | -104.9103 | 118.9133 | -0.013733 | -0.37537 | 118.5516 | 112.175 | 119.9203 | -6.7383 | 1.0071 | -0.14191 | -0.073242 | -0.28839 | 20.462 | 13.7009 | 119.458 | 13.8428 | 119.5999 | -0.36163 | 2.916 | 20.6039 | 122.0581 | 3.2776 | 122.2733 | 122.1909 | 122.1313 | -3.2913 | -122.3465 | 121.8292 | 121.9162 | 118.5287 | 95.2515
2817.7656 | 122.2687 | -118.5791 | 3.6667 | -0.1403 | 0.062794 | 0.0028518 | 0.057368 | -0.00025628 | 0.0026276 | -0.00074776 | -0.1651 | 0.014253 | 0.093231 | 0.19563 | -0.029995 | 0.096904 | 0.044327 | -0.045776 | 3.5294 | 0.28839 | 3.2776 | -0.032043 | 1.3779 | -6.5231 | -23.4695 | 3.5568 | -118.7164 | 3.3508 | -98.735 | 1.0757 | -133.7448 | 118.8675 | -0.13733 | -0.3891 | 118.5471 | 112.056 | 119.957 | -6.8115 | 1.0895 | -0.13733 | -0.10986 | -0.31586 | 19.8441 | -15.1657 | 119.6548 | -15.0284 | 119.7922 | -0.32043 | 2.9892 | 19.9814 | 122.0673 | 3.241 | 122.2733 | 122.1085 | 122.1359 | -3.3783 | -122.3831 | 121.8567 | 121.9299 | 118.5333 | 95.1096
2818.7656 | 122.287 | -118.634 | 3.5706 | -0.11742 | 0.06429 | -0.00056619 | 0.057155 | 0.00059812 | 0.0045502 | -0.0016022 | -0.14679 | 0.0099804 | 0.092163 | 0.18922 | -0.032345 | 0.098399 | 0.046249 | -0.032043 | 3.5843 | 0.32501 | 3.3325 | 0.018311 | 1.4099 | -6.5643 | -23.5153 | 3.5568 | -118.6752 | 3.3188 | -97.6364 | 0.99335 | -107.2769 | 118.959 | 0.013733 | -0.23804 | 118.6523 | 112.0697 | 120.0439 | -6.8893 | 1.0849 | -0.041199 | -0.013733 | -0.25177 | 20.9976 | 11.3571 | 119.6274 | 11.3983 | 119.6686 | -0.3067 | 3.0075 | 21.0388 | 121.994 | 3.2593 | 122.2321 | 122.2183 | 122.1909 | -3.2455 | -122.2458 | 121.9666 | 121.9528 | 118.602 | 95.1187
2819.7656 | 122.2824 | -118.5745 | 3.6346 | -0.11742 | 0.065785 | -0.00013879 | 0.059077 | 0.0040161 | 0.0030548 | -0.0030976 | -0.159 | 0.010194 | 0.095581 | 0.18303 | -0.029354 | 0.096904 | 0.030014 | -0.064087 | 3.6072 | 0.31128 | 3.3051 | -0.018311 | 1.3824 | -6.5094 | -23.6252 | 3.6026 | -118.6523 | 3.3417 | -97.6868 | 1.03 | -115.6403 | 118.8858 | -0.027466 | -0.32959 | 118.5562 | 112.0651 | 119.957 | -6.8207 | 1.0712 | -0.07782 | -0.032044 | -0.29297 | 20.8878 | 2.9343 | 119.6045 | 3.0121 | 119.6823 | -0.32959 | 2.9938 | 20.9656 | 121.994 | 3.2959 | 122.2549 | 122.1817 | 122.1771 | -3.3234 | -122.287 | 121.8796 | 121.9162 | 118.5104 | 94.9493
2820.7656 | 122.3465 | -118.5699 | 3.653 | -0.13267 | 0.064931 | -0.00035239 | 0.0563 | -0.0030335 | 0.0039094 | -0.0041656 | -0.12848 | 0.013612 | 0.093231 | 0.17897 | -0.031063 | 0.098185 | 0.030228 | -0.045776 | 3.6209 | 0.31128 | 3.3737 | 0.009155 | 1.4282 | -6.4682 | -23.6343 | 3.6438 | -118.6203 | 3.4058 | -97.5632 | 1.1124 | -113.9511 | 118.8812 | -0.032043 | -0.27924 | 118.5791 | 112.1017 | 119.9982 | -6.7795 | 1.1169 | -0.050354 | -0.009155 | -0.24719 | 21.0068 | 4.6188 | 119.6823 | 4.6692 | 119.7327 | -0.30212 | 3.0624 | 21.0571 | 122.0261 | 3.3096 | 122.2641 | 122.1909 | 122.2137 | -3.3417 | -122.2733 | 121.9437 | 121.9757 | 118.5242 | 94.9356
2821.7656 | 122.2961 | -118.5516 | 3.6575 | -0.1403 | 0.067067 | 0.00050201 | 0.058864 | 0.0035889 | 0.0036956 | -0.0013886 | -0.11322 | 0.0065626 | 0.096222 | 0.17897 | -0.02914 | 0.097758 | 0.029587 | -0.027466 | 3.6484 | 0.30212 | 3.3875 | 0 | 1.4603 | -6.4774 | -23.6893 | 3.6301 | -118.6066 | 3.4012 | -97.673 | 1.1169 | -104.6173 | 118.8538 | -0.009156 | -0.27008 | 118.5516 | 112.0743 | 120.0119 | -6.7795 | 1.1581 | -0.054931 | -0.027466 | -0.25635 | 20.8786 | 13.9343 | 119.6686 | 13.9893 | 119.7235 | -0.30212 | 3.0853 | 20.9335 | 122.0078 | 3.3463 | 122.2366 | 122.2 | 122.1817 | -3.3554 | -122.2641 | 121.9391 | 121.9528 | 118.5242 | 94.8624
2822.7656 | 122.3099 | -118.5425 | 3.6896 | -0.13267 | 0.065572 | -0.00099339 | 0.05865 | -0.0028199 | 0.0032684 | -0.0071564 | -0.10406 | 0.0065626 | 0.098145 | 0.17811 | -0.029995 | 0.095622 | 0.027237 | -0.022888 | 3.6575 | 0.33417 | 3.4287 | 0.027466 | 1.4969 | -6.4636 | -23.7579 | 3.6438 | -118.5883 | 3.447 | -97.4396 | 1.149 | -113.4247 | 118.8766 | -0.032043 | -0.26092 | 118.5699 | 112.0789 | 120.0394 | -6.7978 | 1.1627 | -0.045777 | -0.045776 | -0.24262 | 21.1029 | 5.1178 | 119.6915 | 5.1636 | 119.7372 | -0.3067 | 3.0945 | 21.1487 | 122.0352 | 3.3234 | 122.2321 | 122.2 | 122.1863 | -3.3554 | -122.2778 | 121.9711 | 121.9894 | 118.5196 | 94.7845
2823.8281 | 122.2824 | -118.5471 | 3.6896 | -0.18608 | 0.06664 | 0.00050201 | 0.059718 | 0.0044433 | 0.0060456 | -0.0024566 | -0.12543 | 0.0065626 | 0.09494 | 0.17726 | -0.029354 | 0.097117 | 0.029159 | -0.050354 | 3.6667 | 0.31586 | 3.392 | -0.032043 | 1.4145 | -6.4636 | -23.9365 | 3.6392 | -118.602 | 3.3966 | -97.3663 | 1.1124 | -113.063 | 118.8629 | -0.022888 | -0.29755 | 118.515 | 112.0834 | 119.9615 | -6.7795 | 1.0986 | -0.054932 | -0.050354 | -0.29297 | 21.1807 | 5.484 | 119.6594 | 5.5389 | 119.7144 | -0.3479 | 3.0762 | 21.2357 | 121.9986 | 3.3508 | 122.2412 | 122.2137 | 122.1863 | -3.3737 | -122.2916 | 121.9391 | 121.9437 | 118.4967 | 94.6106
2824.7656 | 122.3511 | -118.5242 | 3.685 | -0.086899 | 0.064717 | -0.00099339 | 0.059505 | 0.0025207 | 0.004123 | -0.0026704 | -0.091858 | 0.0031446 | 0.095581 | 0.17982 | -0.030209 | 0.097758 | 0.030228 | -0.059509 | 3.6667 | 0.27924 | 3.3829 | -0.009155 | 1.4877 | -6.4362 | -23.996 | 3.6484 | -118.5745 | 3.4332 | -97.2565 | 1.1719 | -112.8891 | 118.8034 | -0.018311 | -0.30212 | 118.515 | 112.088 | 120.0119 | -6.7154 | 1.2085 | -0.050354 | -0.036622 | -0.25177 | 21.2677 | 5.6351 | 119.696 | 5.6854 | 119.7464 | -0.28839 | 3.1036 | 21.3181 | 122.0078 | 3.3875 | 122.2229 | 122.1909 | 122.1725 | -3.4058 | -122.2595 | 121.907 | 121.9574 | 118.4647 | 94.5282
2825.7656 | 122.2733 | -118.4006 | 3.7445 | -0.12505 | 0.064931 | -0.0020614 | 0.057155 | 0.00017092 | 0.0022004 | -0.0020294 | -0.11017 | 0.0061352 | 0.095795 | 0.18217 | -0.030849 | 0.096904 | 0.031509 | -0.032043 | 3.6713 | 0.27924 | 3.4149 | 0.050354 | 1.5015 | -6.4041 | -24.0005 | 3.6575 | -118.5974 | 3.4698 | -97.1466 | 1.1856 | -112.4313 | 118.6798 | -0.073242 | -0.32959 | 118.4509 | 111.9965 | 119.902 | -6.6833 | 1.2222 | -0.19684 | -0.086975 | -0.27466 | 21.254 | 5.9692 | 119.5862 | 6.1661 | 119.783 | -0.22888 | 3.1357 | 21.4508 | 122.0673 | 3.392 | 122.2549 | 122.0718 | 122.0581 | -3.4653 | -122.3419 | 121.8155 | 121.8704 | 118.3685 | 94.4
2826.7656 | 122.3557 | -118.5242 | 3.6804 | -0.10979 | 0.065144 | 0.00028841 | 0.05865 | 0.0018799 | 0.0043366 | -0.0026704 | -0.11322 | 0.0050672 | 0.098572 | 0.1779 | -0.029781 | 0.096049 | 0.032577 | -0.036621 | 3.6575 | 0.27466 | 3.3966 | 0.054932 | 1.4786 | -6.395 | -24.1562 | 3.6438 | -118.6111 | 3.4653 | -97.0413 | 1.1856 | -113.0081 | 118.7988 | -0.022888 | -0.28381 | 118.5791 | 112.1292 | 120.0027 | -6.6696 | 1.2039 | -0.086975 | -0.036621 | -0.21515 | 21.4828 | 5.5161 | 119.7098 | 5.603 | 119.7968 | -0.21973 | 3.1219 | 21.5698 | 122.0764 | 3.3829 | 122.2549 | 122.1817 | 122.168 | -3.4058 | -122.2916 | 121.9208 | 121.9894 | 118.4875 | 94.368
2827.7656 | 122.2961 | -118.8126 | 3.4058 | -0.17845 | 0.064931 | 7.4814e-05 | 0.059932 | 0.00038452 | 0.001773 | -0.0050202 | -0.2597 | 0.0018628 | 0.099213 | 0.52525 | -0.031704 | 0.092204 | 0.37352 | -0.059509 | 3.3966 | 0.25635 | 3.0853 | 0.050354 | 1.2772 | -5.2002 | -24.1562 | 3.3554 | -118.84 | 3.0579 | -94.2719 | 0.75073 | -40.7272 | 119.0689 | -0.009156 | -0.32044 | 118.8629 | 113.6124 | 120.0897 | -5.4565 | 1.0208 | -0.027466 | -0.050354 | -0.3479 | 24.5407 | 78.0853 | 119.5633 | 78.1128 | 119.5908 | -0.20599 | 2.829 | 24.5682 | 121.8979 | 3.1403 | 122.1954 | 122.2092 | 122.168 | -3.1494 | -122.2458 | 121.8979 | 121.8704 | 118.7531 | 94.6564
2828.7656 | 122.3373 | -118.5883 | 3.6255 | -0.15556 | 0.064717 | -0.00013879 | 0.057368 | -0.0060241 | 0.0039094 | -0.0035248 | -0.067444 | 0.0078442 | 0.098572 | 0.17747 | -0.030849 | 0.097117 | 0.030441 | -0.050354 | 3.5751 | 0.26093 | 3.3371 | 0.14191 | 1.4328 | -6.2668 | -24.3393 | 3.598 | -118.6569 | 3.3508 | -96.7484 | 1.0986 | -120.6436 | 118.8492 | -0.050354 | -0.28839 | 118.7302 | 112.3215 | 120.0211 | -6.5277 | 1.1719 | -0.068664 | -0.027466 | -0.27466 | 21.8399 | -2.0554 | 119.6869 | -1.9867 | 119.7556 | -0.11902 | 3.0762 | 21.9086 | 122.0078 | 3.3142 | 122.2549 | 122.1634 | 122.1863 | -3.3646 | -122.2824 | 121.9254 | 121.9391 | 118.5379 | 94.249
2829.7656 | 122.3145 | -118.602 | 3.6163 | -0.086899 | 0.067067 | -0.0018478 | 0.058864 | -0.00068368 | 0.0026276 | -0.006302 | -0.079651 | 0.0076306 | 0.098145 | 0.17107 | -0.029995 | 0.09434 | 0.02446 | -0.041199 | 3.6209 | 0.2655 | 3.3234 | 0.091553 | 1.442 | -6.34 | -24.4492 | 3.598 | -118.634 | 3.3325 | -96.7438 | 1.0941 | -114.299 | 118.8675 | 0.004578 | -0.29297 | 118.6935 | 112.262 | 120.0439 | -6.6055 | 1.1765 | -0.032043 | -0.018311 | -0.28381 | 21.8582 | 4.303 | 119.696 | 4.335 | 119.7281 | -0.17395 | 3.0579 | 21.8903 | 121.9666 | 3.3554 | 122.2321 | 122.2229 | 122.2 | -3.3508 | -122.2504 | 121.9254 | 121.9345 | 118.5608 | 94.1528
2830.8281 | 122.3511 | -118.5654 | 3.6392 | -0.14793 | 0.068135 | -0.00099339 | 0.056728 | 0.0010253 | 0.005191 | -0.0035248 | -0.091858 | 0.006349 | 0.10007 | 0.17406 | -0.029781 | 0.095408 | 0.025101 | -0.009155 | 3.6026 | 0.28381 | 3.4698 | 0.25635 | 1.4648 | -6.3034 | -24.614 | 3.653 | -118.6157 | 3.4287 | -96.5836 | 1.1261 | -113.7497 | 118.8492 | -0.036621 | -0.16937 | 118.8217 | 112.262 | 120.0302 | -6.5872 | 1.181 | -0.050354 | 0.013733 | -0.21057 | 21.9818 | 4.8157 | 119.6915 | 4.866 | 119.7418 | -0.027465 | 3.186 | 22.0322 | 122.0444 | 3.3188 | 122.2687 | 122.168 | 122.2183 | -3.3554 | -122.2549 | 122.0352 | 121.994 | 118.5562 | 93.9514
2831.7656 | 122.3282 | -118.5608 | 3.6621 | -0.11742 | 0.065572 | -0.0016342 | 0.055873 | 0.00017092 | 0.0060456 | -0.002884 | -0.024719 | 0.005708 | 0.098999 | 0.16679 | -0.032772 | 0.096263 | 0.0298 | 0.068665 | 3.6758 | 0.30212 | 3.3325 | 0.12817 | 1.442 | -6.3126 | -24.7787 | 3.6484 | -118.6615 | 3.3646 | -96.524 | 1.0941 | -113.7405 | 118.8629 | 0.013733 | -0.32959 | 118.689 | 112.2482 | 120.0027 | -6.6147 | 1.1398 | -0.10071 | -0.013733 | -0.29755 | 22.0367 | 4.8203 | 119.6548 | 4.921 | 119.7556 | -0.17395 | 3.0304 | 22.1375 | 122.0261 | 3.3737 | 122.3099 | 122.2366 | 122.2092 | -3.36 | -122.3236 | 121.8933 | 121.9254 | 118.6295 | 93.782
2832.7656 | 122.3328 | -118.5791 | 3.6713 | -0.086899 | 0.066853 | -0.00035239 | 0.058223 | -0.0017517 | 0.0036956 | -0.0043792 | -0.067444 | 0.0059216 | 0.098572 | 0.17171 | -0.029568 | 0.095195 | 0.023178 | -0.054932 | 3.6713 | 0.25635 | 3.3783 | 0.082397 | 1.4465 | -6.3171 | -24.8749 | 3.6301 | -118.6295 | 3.3875 | -96.4096 | 1.1215 | -113.6719 | 118.8355 | 0 | -0.29297 | 118.6615 | 112.262 | 120.0256 | -6.5735 | 1.1902 | -0.050354 | -0.041199 | -0.28381 | 22.1695 | 4.9072 | 119.7006 | 4.9576 | 119.751 | -0.17395 | 3.1219 | 22.2198 | 122.0169 | 3.4149 | 122.2595 | 122.2504 | 122.2092 | -3.4149 | -122.3007 | 121.9574 | 121.9666 | 118.5242 | 93.7042
2833.7656 | 122.3511 | -118.5196 | 3.7033 | -0.11742 | 0.067494 | -0.00013879 | 0.056514 | -4.2682e-05 | 0.0028412 | -0.006302 | -0.070496 | 0.0065626 | 0.098999 | 0.1685 | -0.029354 | 0.095195 | 0.024246 | -0.036621 | 3.6896 | 0.25635 | 3.3783 | 0.068665 | 1.4694 | -6.2622 | -24.8795 | 3.6484 | -118.6066 | 3.447 | -96.3181 | 1.1719 | -114.917 | 118.7759 | -0.013733 | -0.32501 | 118.5883 | 112.2574 | 119.989 | -6.5186 | 1.2131 | -0.086975 | -0.054932 | -0.25635 | 22.2015 | 3.6026 | 119.6915 | 3.6896 | 119.7784 | -0.18768 | 3.1219 | 22.2885 | 122.0535 | 3.4332 | 122.2549 | 122.2092 | 122.168 | -3.447 | -122.3099 | 121.8979 | 121.9666 | 118.483 | 93.6401
2834.8281 | 122.3007 | -108.4808 | 13.7009 | -0.3997 | 0.33367 | -0.020647 | 0.061427 | 0.0023071 | 0.02399 | -0.0035248 | -0.12238 | 0.009126 | 0.37457 | 0.18046 | -0.031704 | 0.097331 | 0.029159 | -0.009155 | 13.6139 | 1.474 | 13.4903 | 0.9613 | 6.2668 | -2.7557 | -20.0317 | 13.6505 | -108.522 | 13.5635 | -88.1699 | 11.1832 | -103.6469 | 109.9548 | -0.086975 | -0.21057 | 109.4421 | 105.7251 | 114.7476 | -4.2297 | 4.7928 | -0.041199 | -0.050354 | -0.13733 | 20.311 | 4.834 | 119.664 | 4.8752 | 119.7052 | -0.5127 | 12.0163 | 20.3522 | 122.0856 | 12.1399 | 122.1725 | 122.0947 | 122.1313 | -12.2269 | -122.2229 | 121.9711 | 122.0444 | 108.4717 | 88.4491
2835.7656 | 122.1954 | -70.1157 | 51.9379 | -4.1305 | 3.8194 | -0.16228 | 0.080012 | 0.0012391 | 0.17096 | -0.004593 | -0.070496 | 0.0084852 | 3.9062 | 0.18346 | -0.032131 | 0.096049 | 0.025528 | 0.018311 | 51.709 | 4.9164 | 52.4231 | 3.5385 | 33.9706 | 11.6821 | 0.004578 | 51.709 | -70.079 | 51.5945 | -52.7664 | 49.2462 | -65.538 | 75.032 | -0.22888 | 0.48523 | 73.6542 | 81.7978 | 104.0863 | 6.7657 | 29.0543 | 0.036621 | -0.22888 | -0.34332 | 17.3492 | 4.5776 | 119.3619 | 4.541 | 119.3253 | -1.3779 | 47.5067 | 17.3126 | 121.6736 | 46.7926 | 121.788 | 121.8246 | 121.8246 | -47.0215 | -122.0169 | 122.5388 | 121.7102 | 70.134 | 70.1202
2836.7656 | 121.4905 | -50.2121 | 71.283 | -17.0318 | 7.0235 | -0.34172 | 0.088344 | 0.00017092 | 0.35083 | -0.0048066 | -0.027771 | 0.0099804 | 7.0093 | 0.18303 | -0.030636 | 0.093913 | 0.028091 | 33.9752 | 70.2667 | 7.1686 | 69.9554 | 4.8157 | 68.2846 | 17.9031 | 10.6705 | 71.4432 | -48.0835 | 71.0037 | -44.7281 | 68.6508 | -44.7372 | 57.3807 | -1.0162 | -1.3275 | 55.0278 | 68.1152 | 118.4967 | 10.7346 | 61.116 | 2.1286 | 0.16022 | -0.27924 | 5.484 | 5.4749 | 118.8629 | 3.3463 | 116.7343 | -2.3529 | 62.7869 | 3.3554 | 119.0872 | 63.0981 | 119.5267 | 120.4788 | 121.6553 | -64.1144 | -119.3665 | 120.1675 | 121.2158 | 84.1873 | 60.8826
2837.7656 | 121.9025 | -84.4025 | 37.2574 | -5.2978 | 5.1716 | -0.18578 | 0.072749 | -0.0019653 | 0.1904 | -0.0048066 | -0.033874 | 0.007417 | 5.3612 | 0.18388 | -0.030636 | 0.094127 | 0.027023 | 1.062 | 35.9665 | 3.7262 | 35.8612 | 2.3209 | 35.3577 | 3.9963 | -7.3288 | 36.7126 | -84.5032 | 36.9736 | -79.5502 | 34.877 | -79.4266 | 88.1287 | -1.2909 | -1.3962 | 86.7233 | 88.3987 | 119.7601 | 0.27008 | 31.6315 | -0.10071 | -0.54474 | -0.28381 | 4.8523 | 4.9759 | 119.2795 | 5.0766 | 119.3802 | -1.4053 | 32.135 | 4.953 | 121.4767 | 32.2403 | 121.2158 | 120.369 | 121.1151 | -33.5312 | -121.7606 | 120.2637 | 121.376 | 85.4645 | 77.0737
2838.7656 | 121.701 | -0.49439 | 121.3486 | -0.18608 | 0.022633 | 0.0054154 | 0.055232 | -4.2682e-05 | -0.0022858 | -0.00096136 | -0.13458 | 0.010835 | 0.12762 | 0.19884 | -0.030849 | 0.095195 | 0.022751 | -0.032043 | 0.25635 | -0.11444 | -0.086975 | 0.091553 | -0.09613 | 1.8951 | 5.9784 | 120.9869 | -0.36621 | 120.9366 | -0.14191 | 117.9062 | 3.0487 | 0.37994 | -121.0922 | -121.4355 | 0.58594 | 2.3895 | 0.39826 | 2.0096 | 0.018311 | 0.12817 | -0.36163 | -0.41199 | 0.35248 | 3.5431 | 118.4006 | 3.4149 | 118.2724 | 0.20599 | 0.027466 | 0.2243 | 121.3028 | 0.37079 | 121.3531 | 0.75073 | 121.4813 | -121.463 | -121.7148 | 0.40741 | 121.431 | 0.46234 | 6.4728
2839.8281 | 121.2296 | -0.4715 | 121.4951 | -0.15556 | 0.021565 | 0.0043472 | 0.057796 | -0.0015381 | -0.0052764 | -0.0050202 | -0.12848 | 0.010621 | 0.13104 | 0.20097 | -0.031063 | 0.095836 | 0.023178 | -0.050354 | 0.19684 | -0.15564 | -0.10071 | 0.059509 | -0.10986 | 1.9226 | 7.6767 | 121.3348 | -0.53101 | 121.0419 | -0.24719 | 118.1168 | 3.1219 | 0.31586 | -121.2982 | -121.5958 | 0.53101 | 2.3941 | 0.36163 | 2.0782 | 0.045777 | -0.059509 | -0.16022 | -0.45319 | 0.22431 | 3.5934 | 118.5883 | 3.653 | 118.6478 | 0.21515 | 0.054932 | 0.28381 | 121.5729 | 0.35248 | 121.8658 | 0.66834 | 121.8063 | -121.6507 | -122.0261 | 0.37079 | 121.5134 | 0.42114 | 8.1482
2840.7656 | 121.55 | -0.59052 | 121.4996 | -0.12505 | 0.024129 | 0.004988 | 0.056087 | -0.0023925 | -0.0046356 | -0.0054474 | -0.070496 | 0.009126 | 0.13553 | 0.20161 | -0.029995 | 0.094554 | 0.020615 | -0.054932 | 0.21515 | -0.13275 | -0.12817 | 0.054932 | -0.10071 | 1.918 | 7.9559 | 121.4218 | -0.6958 | 121.3165 | -0.25635 | 118.4647 | 3.1448 | 0.45776 | -121.2845 | -121.6278 | 0.64545 | 2.5085 | 0.48981 | 2.0508 | 0.032043 | -0.10529 | -0.07782 | -0.18311 | 0.33417 | 3.7354 | 119.0552 | 3.8406 | 119.1605 | 0.18768 | 0.004577 | 0.43945 | 122.0123 | 0.3479 | 122.1176 | 0.80566 | 122.0123 | -121.6324 | -122.1954 | 0.46234 | 121.907 | 0.53558 | 8.5464
2841.7656 | 121.3852 | -0.5722 | 121.4539 | -0.14793 | 0.023701 | 0.0045608 | 0.057155 | 0.00038452 | -0.0035674 | -0.0041656 | -0.10406 | 0.0097668 | 0.13382 | 0.21016 | -0.030209 | 0.095195 | 0.024887 | -0.050354 | 0.19684 | -0.17853 | -0.10529 | 0.041199 | -0.12817 | 1.9226 | 7.9605 | 121.3806 | -0.75989 | 120.9274 | -0.28839 | 118.1351 | 3.1723 | 0.39368 | -121.257 | -121.5591 | 0.6134 | 2.4948 | 0.44403 | 2.1011 | 0.050354 | -0.18768 | -0.073242 | -0.52643 | 0.28381 | 3.7445 | 118.7073 | 3.9322 | 118.895 | 0.21973 | 0.073242 | 0.4715 | 121.6873 | 0.37537 | 122.1405 | 0.76904 | 121.9528 | -121.6324 | -122.2137 | 0.46692 | 121.4996 | 0.52185 | 8.5327
2842.8281 | 121.2204 | -0.65002 | 121.4355 | -0.15556 | 0.024556 | 0.0081924 | 0.052669 | -0.015851 | -0.0057038 | -0.0097198 | -0.15289 | 0.010408 | 0.13104 | 0.19862 | -0.034267 | 0.085582 | 0.020401 | -0.054932 | 0.17853 | -0.17395 | -0.11902 | 0.022888 | -0.15564 | 1.8951 | 7.7728 | 121.3852 | -0.79651 | 120.6528 | -0.27466 | 118.0527 | 2.9572 | 0.47607 | -121.257 | -121.5546 | 0.67291 | 2.5452 | 0.49438 | 2.0691 | 0.01831 | -0.14648 | -0.050354 | -0.78278 | 0.37537 | 3.6072 | 118.7027 | 3.7537 | 118.8492 | 0.19684 | 0.054931 | 0.52185 | 121.4493 | 0.35248 | 122.1817 | 0.82855 | 122.0352 | -121.6095 | -122.2321 | 0.53101 | 121.3028 | 0.59509 | 8.4229
2843.7656 | 121.5408 | -0.63629 | 120.8267 | -0.16319 | 0.026692 | 0.0075516 | 0.055019 | 0.0020935 | -0.0024994 | -0.0030976 | -0.13153 | 0.010621 | 0.13318 | 0.20524 | -0.034054 | 0.083232 | 0.018906 | 0.018311 | 0.22888 | -0.086975 | -0.045776 | 0.11902 | -0.068665 | 1.9867 | 10.2905 | 121.376 | -0.79651 | 120.488 | -0.20142 | 118.0023 | 3.186 | 0.54932 | -120.5978 | -120.8725 | 0.75531 | 2.623 | 0.56763 | 2.0737 | 0.01831 | -0.16022 | 0.54932 | -0.33875 | 0.43488 | 3.8223 | 118.6386 | 3.9825 | 118.7988 | 0.20599 | 0.041199 | 0.59509 | 121.2845 | 0.31586 | 122.1725 | 0.86517 | 122.0123 | -120.9137 | -121.6232 | 0.59052 | 121.1243 | 0.6546 | 10.9268
2844.7656 | 121.9254 | -0.74158 | 121.1838 | -0.16319 | 0.023701 | 0.0075516 | 0.055446 | 0.00017092 | -0.0018586 | -0.0035248 | -0.027771 | 0.011049 | 0.13831 | 0.20759 | -0.028072 | 0.095408 | 0.02446 | -0.013733 | 0.17395 | -0.11902 | -0.032043 | 0.12817 | -0.050354 | 2.0187 | 3.0121 | 121.3303 | -0.81024 | 121.2662 | -0.22888 | 118.5699 | 3.1815 | 0.62256 | -121.0098 | -121.2158 | 0.86975 | 2.7603 | 0.69122 | 2.1378 | 0.068665 | -0.068665 | 0.14648 | 0.082397 | 0.5127 | 3.923 | 119.3115 | 3.9917 | 119.3802 | 0.24719 | 0.086976 | 0.58136 | 122.0764 | 0.29297 | 122.1405 | 0.91553 | 122.0718 | -121.3028 | -121.994 | 0.70953 | 122.0078 | 0.72784 | 3.7537
2845.7656 | 121.4081 | -0.67291 | 121.2891 | -0.13267 | 0.023701 | 0.0034928 | 0.055232 | -0.0023925 | -0.0035674 | -0.0054474 | -0.17731 | 0.010408 | 0.13617 | 0.20824 | -0.030209 | 0.086436 | 0.020615 | 0 | 0.19226 | -0.14191 | -0.073242 | 0.068665 | -0.082397 | 2.037 | 2.2797 | 121.4264 | -0.77362 | 120.6207 | -0.20599 | 118.0435 | 3.2547 | 0.53101 | -121.0968 | -121.3623 | 0.74158 | 2.71 | 0.59052 | 2.179 | 0.05951 | -0.10071 | 0.13733 | -0.66833 | 0.46692 | 3.9276 | 118.7164 | 4.0283 | 118.8171 | 0.21057 | 0.068665 | 0.56763 | 121.3943 | 0.33417 | 122.2 | 0.86517 | 122.0993 | -121.431 | -122.0627 | 0.59967 | 121.2936 | 0.67291 | 2.9526
2846.7656 | 122.1725 | -0.75073 | 121.3852 | -0.17845 | 0.026478 | 0.005629 | 0.054164 | -0.00025628 | -0.0039948 | -0.003952 | -0.04303 | 0.0076306 | 0.13788 | 0.20845 | -0.029995 | 0.094768 | 0.022324 | -0.004578 | 0.17395 | -0.12817 | -0.036621 | 0.14191 | -0.004578 | 2.037 | 1.9135 | 121.2982 | -0.84686 | 121.2708 | -0.30212 | 118.5425 | 3.4424 | 0.62256 | -121.2112 | -121.4218 | 0.89264 | 2.7878 | 0.74615 | 2.1652 | 0.1236 | -0.096131 | -0.086975 | -0.11444 | 0.44861 | 4.1931 | 119.2932 | 4.2892 | 119.3893 | 0.27008 | 0.091553 | 0.54474 | 122.1176 | 0.30212 | 122.1451 | 0.92468 | 122.049 | -121.5134 | -122.2321 | 0.71411 | 122.0215 | 0.74615 | 2.6642
2847.7656 | 121.8567 | -0.8194 | 121.3989 | -0.23186 | 0.021352 | 0.006697 | 0.055232 | 0.00081172 | -0.0048492 | -0.0013886 | -0.079651 | 0.011689 | 0.13702 | 0.21443 | -0.031063 | 0.094768 | 0.022324 | -0.045776 | 0.24719 | -0.1236 | -0.11444 | 0.022888 | -0.1236 | 1.8768 | 2.3117 | 121.2936 | -0.89722 | 121.1975 | -0.4303 | 118.3365 | 3.4012 | 0.6958 | -121.1517 | -121.5134 | 0.84229 | 2.6962 | 0.6958 | 2.0004 | 0 | -0.07782 | -0.10529 | -0.20142 | 0.3891 | 4.2206 | 119.1559 | 4.2984 | 119.2337 | 0.14648 | 0.009155 | 0.46692 | 122.0947 | 0.37079 | 122.1909 | 1.0666 | 122.113 | -121.5225 | -122.2961 | 0.70496 | 122.0169 | 0.77362 | 3.1311
2848.7656 | 121.9437 | -0.82398 | 121.3898 | 0.13435 | 0.024129 | 0.0054154 | 0.056087 | 0.00059812 | -0.0024994 | -0.0071564 | -0.091858 | 0.010835 | 0.13767 | 0.20567 | -0.030636 | 0.093272 | 0.02745 | -0.059509 | 0.24261 | -0.10986 | -0.11444 | 0.032043 | -0.14191 | 1.8539 | 2.1561 | 121.3348 | -0.90637 | 121.1792 | -0.43488 | 118.3731 | 3.4103 | 0.71411 | -121.1472 | -121.5042 | 0.85602 | 2.6779 | 0.68207 | 1.9638 | -0.032044 | -0.082397 | -0.054932 | -0.21057 | 0.3891 | 4.2343 | 119.1971 | 4.3167 | 119.2795 | 0.14191 | -0.004578 | 0.4715 | 122.0856 | 0.35248 | 122.2412 | 1.0666 | 122.1588 | -121.4996 | -122.2961 | 0.70953 | 122.0032 | 0.76447 | 2.98
2849.7656 | 122.0169 | -0.83313 | 121.3669 | -0.1403 | 0.02541 | 0.004988 | 0.057368 | 0.0027343 | -0.0022858 | -0.0013886 | -0.091858 | 0.0084852 | 0.13937 | 0.21229 | -0.0285 | 0.093272 | 0.02745 | -0.064087 | 0.22888 | -0.15564 | -0.068665 | 0.064087 | -0.15564 | 1.8494 | 7.8278 | 121.2936 | -0.90637 | 121.1792 | -0.43488 | 118.4097 | 3.4882 | 0.67749 | -121.138 | -121.4355 | 0.89722 | 2.6825 | 0.67749 | 2.005 | 0 | -0.073242 | -0.073242 | -0.18768 | 0.39826 | 4.3213 | 119.2429 | 4.3945 | 119.3161 | 0.21973 | 0.086975 | 0.4715 | 122.0856 | 0.38452 | 122.2 | 1.062 | 122.1268 | -121.5225 | -122.2733 | 0.76447 | 122.0123 | 0.76904 | 8.6609
2850.7656 | 122.1817 | -0.83771 | 121.3715 | -0.1403 | 0.026265 | 0.0026382 | 0.05395 | 0.0012391 | -0.0005768 | -0.0033112 | -0.055237 | 0.010408 | 0.14023 | 0.21336 | -0.02914 | 0.093272 | 0.02446 | -0.004578 | 0.18768 | -0.13275 | -0.064087 | 0.10071 | -0.059509 | 1.8768 | 3.0487 | 121.2845 | -0.90179 | 121.1884 | -0.45319 | 118.4555 | 3.5706 | 0.70496 | -121.1838 | -121.4355 | 0.93842 | 2.7145 | 0.7782 | 2.0096 | 0.073242 | -0.064086 | -0.086975 | -0.18311 | 0.38452 | 4.4083 | 119.2932 | 4.4724 | 119.3573 | 0.23346 | 0.068664 | 0.44861 | 122.0901 | 0.32043 | 122.1863 | 1.0254 | 122.1222 | -121.5042 | -122.2733 | 0.77362 | 122.0261 | 0.83313 | 3.8864
2851.7656 | 121.9528 | -0.84228 | 121.3486 | -0.20134 | 0.022847 | 0.004988 | 0.0563 | -0.0030335 | -0.0031402 | -0.002884 | -0.13763 | 0.011049 | 0.13745 | 0.21507 | -0.030209 | 0.093699 | 0.027023 | -0.022888 | 0.1831 | -0.16022 | -0.086975 | 0.054932 | -0.10071 | 1.8494 | 3.2501 | 121.2799 | -0.93384 | 121.0373 | -0.44861 | 118.158 | 3.6575 | 0.68207 | -121.1655 | -121.4355 | 0.89722 | 2.6917 | 0.74158 | 2.0096 | 0.059509 | -0.091553 | -0.068665 | -0.31128 | 0.39368 | 4.4998 | 119.0002 | 4.5914 | 119.0918 | 0.21515 | 0.073242 | 0.48523 | 121.9711 | 0.34332 | 122.2137 | 1.0254 | 122.1222 | -121.5088 | -122.2824 | 0.75531 | 121.8796 | 0.8194 | 4.0924
2852.8281 | 122.3694 | -0.85144 | 121.2982 | -0.22423 | 0.023915 | 0.0064834 | 0.056941 | 0.0044433 | -0.0003632 | -0.00053396 | -0.12543 | 0.011262 | 0.13895 | 0.21828 | -0.032345 | 0.096477 | 0.023819 | -0.013733 | 0.15564 | -0.13275 | -0.022888 | 0.13275 | -0.054932 | 1.8723 | 2.7191 | 121.257 | -0.93384 | 121.1884 | -0.64087 | 118.5287 | 3.8315 | 0.71869 | -121.1426 | -121.3211 | 0.98419 | 2.7237 | 0.79651 | 2.005 | 0.077819 | -0.082398 | -0.041199 | -0.10986 | 0.21057 | 4.6829 | 119.3802 | 4.7653 | 119.4626 | 0.2655 | 0.10986 | 0.29297 | 122.1222 | 0.28839 | 122.1909 | 1.0071 | 122.1085 | -121.431 | -122.2321 | 0.82855 | 122.0398 | 0.83771 | 3.5706
2853.7656 | 122.1634 | -0.85144 | 121.3486 | -0.12505 | 0.024129 | 0.0058426 | 0.055232 | -0.0019653 | -0.0012176 | -0.005661 | -0.088806 | 0.014039 | 0.1366 | 0.21187 | -0.031704 | 0.094554 | 0.030441 | -0.059509 | 0.19684 | -0.14648 | -0.1236 | 0.041199 | -0.13275 | 1.8265 | 4.2435 | 121.3531 | -0.92468 | 121.1746 | -0.52185 | 118.428 | 3.7262 | 0.70496 | -121.1517 | -121.4722 | 0.89264 | 2.6779 | 0.71869 | 1.973 | 0.013733 | -0.073243 | 0.004577 | -0.17395 | 0.32959 | 4.5776 | 119.2795 | 4.6509 | 119.3527 | 0.18768 | 0.022888 | 0.40283 | 122.0993 | 0.34332 | 122.2778 | 1.0483 | 122.2046 | -121.4951 | -122.2733 | 0.72784 | 122.0261 | 0.79193 | 5.0949
2854.7656 | 122.1542 | -0.89264 | 121.3165 | -0.13267 | 0.024129 | 0.00392 | 0.055659 | 0.0014527 | -0.0024994 | -0.0058746 | -0.14069 | 0.011476 | 0.14322 | 0.21529 | -0.029781 | 0.096049 | 0.029159 | -0.050354 | 0.21515 | -0.16937 | -0.11902 | 0.018311 | -0.13275 | 1.799 | 2.9617 | 121.257 | -0.98419 | 121.1517 | -0.49439 | 118.3594 | 3.8086 | 0.72327 | -121.1014 | -121.4355 | 0.91095 | 2.6917 | 0.75989 | 1.9684 | 0.036622 | -0.091553 | -0.059509 | -0.1648 | 0.39825 | 4.7012 | 119.252 | 4.7928 | 119.3436 | 0.18768 | 0.050354 | 0.48981 | 122.1359 | 0.38452 | 122.2412 | 1.1078 | 122.1497 | -121.4859 | -122.3007 | 0.77362 | 122.0444 | 0.84228 | 3.8544
2855.7656 | 122.168 | -0.92926 | 121.312 | -0.13267 | 0.023915 | 0.0047744 | 0.058009 | 0.0023071 | -0.0020722 | -0.0020294 | -0.11932 | 0.01233 | 0.14151 | 0.22148 | -0.028286 | 0.096263 | 0.031937 | -0.068665 | 0.21973 | -0.15106 | -0.10986 | 0.032043 | -0.11444 | 1.7807 | 3.3966 | 121.2662 | -1.0025 | 121.1197 | -0.53101 | 118.3411 | 3.8589 | 0.7782 | -121.0922 | -121.4218 | 0.9613 | 2.71 | 0.81482 | 1.9318 | 0.036621 | -0.073242 | -0.045777 | -0.19226 | 0.39825 | 4.7882 | 119.2703 | 4.8614 | 119.3436 | 0.18311 | 0.041199 | 0.4715 | 122.1222 | 0.37079 | 122.2687 | 1.149 | 122.1954 | -121.463 | -122.3145 | 0.8194 | 122.049 | 0.86059 | 4.3259
2856.7656 | 122.1725 | -0.92926 | 121.3165 | -0.056381 | 0.022847 | 0.0062698 | 0.055446 | -0.0019653 | -0.002713 | -0.0024566 | -0.10406 | 0.011049 | 0.1413 | 0.21422 | -0.029781 | 0.095195 | 0.028091 | -0.068665 | 0.23346 | -0.11902 | -0.11444 | 0.032043 | -0.11444 | 1.7853 | 3.2318 | 121.2433 | -1.0162 | 121.1197 | -0.54016 | 118.3365 | 3.8956 | 0.81024 | -121.0831 | -121.431 | 0.9613 | 2.7145 | 0.81482 | 1.9043 | 0.004578 | -0.086975 | -0.073242 | -0.19684 | 0.3891 | 4.8248 | 119.2657 | 4.9118 | 119.3527 | 0.15106 | 0.004578 | 0.47607 | 122.1359 | 0.35248 | 122.2595 | 1.1627 | 122.1725 | -121.4355 | -122.3328 | 0.81482 | 122.049 | 0.86059 | 4.1611
2857.7656 | 121.9711 | -0.90637 | 121.312 | -0.18608 | 0.019856 | 0.0013564 | 0.058009 | -0.010083 | -0.0063446 | -0.015488 | -0.18036 | 0.011903 | 0.13361 | 0.21742 | -0.0285 | 0.087932 | 0.029373 | 0.009155 | 0.23346 | -0.10986 | -0.068665 | 0.091553 | -0.082397 | 1.7761 | 2.6733 | 121.2479 | -0.99792 | 120.8679 | -0.51727 | 118.1808 | 4.0146 | 0.79651 | -121.0785 | -121.3806 | 0.99792 | 2.6825 | 0.82397 | 1.886 | 0.027466 | -0.091553 | -0.064087 | -0.44403 | 0.3891 | 4.921 | 119.0872 | 5.0125 | 119.1788 | 0.20142 | 0.041198 | 0.48065 | 121.8658 | 0.34332 | 122.2458 | 1.1398 | 122.1542 | -121.4218 | -122.3099 | 0.83771 | 121.7743 | 0.91553 | 3.5797
2858.7656 | 122.2687 | -0.90179 | 121.2708 | -0.17845 | 0.023488 | 0.0041336 | 0.055019 | -0.0053833 | -0.0029266 | 0.0016022 | -0.058289 | 0.011903 | 0.14023 | 0.21763 | -0.03149 | 0.096049 | 0.027664 | 0 | 0.17395 | -0.09613 | -0.009155 | 0.16479 | 0.009155 | 1.886 | 2.6093 | 121.2021 | -0.98877 | 121.2021 | -0.45319 | 118.4052 | 4.1336 | 0.80566 | -121.0968 | -121.2799 | 1.0666 | 2.7878 | 0.91095 | 1.9821 | 0.10528 | -0.086976 | -0.068665 | -0.068665 | 0.44861 | 5.0354 | 119.3069 | 5.1224 | 119.3939 | 0.26092 | 0.086975 | 0.53558 | 122.1909 | 0.27008 | 122.1909 | 1.0757 | 122.1039 | -121.3669 | -122.2595 | 0.89264 | 122.1039 | 0.90179 | 3.511
2859.7656 | 122.1954 | -0.95215 | 121.2891 | -0.17845 | 0.022633 | 0.0030654 | 0.0563 | -0.0030335 | -0.0033538 | -0.0054474 | -0.11322 | 0.012544 | 0.14343 | 0.21913 | -0.030209 | 0.094127 | 0.030655 | -0.059509 | 0.20142 | -0.15564 | -0.050354 | -0.082397 | -0.17853 | 1.8402 | 2.3621 | 121.2524 | -0.99792 | 121.1151 | -0.5722 | 118.3182 | 4.129 | 0.79651 | -121.0876 | -121.3394 | 0.86975 | 2.7924 | 0.77362 | 1.9958 | -0.022888 | -0.045777 | -0.036621 | -0.17395 | 0.37994 | 5.0812 | 119.2703 | 5.127 | 119.3161 | 0.073243 | 0.10529 | 0.42572 | 122.113 | 0.35706 | 122.2504 | 1.1536 | 122.2046 | -121.4447 | -122.287 | 0.90179 | 122.0673 | 0.89264 | 3.3142
2860.7656 | 122.2 | -0.95673 | 121.2753 | -0.094528 | 0.025197 | 0.003279 | 0.057368 | -0.0058105 | -0.0035674 | -0.0037384 | -0.015564 | 0.011689 | 0.14407 | 0.21998 | -0.02914 | 0.095836 | 0.031509 | -0.064087 | 0.18768 | -0.16479 | -0.1236 | 0.041199 | -0.11902 | 1.9363 | 2.2064 | 121.2662 | -1.0117 | 121.106 | -0.5722 | 118.3044 | 4.2068 | 0.79193 | -121.0876 | -121.3989 | 0.99792 | 2.8931 | 0.83771 | 2.1011 | 0.045776 | -0.054932 | -0.009156 | -0.16937 | 0.38452 | 5.1636 | 119.2612 | 5.2185 | 119.3161 | 0.20599 | 0.041199 | 0.43945 | 122.1176 | 0.35248 | 122.2778 | 1.1444 | 122.2229 | -121.4401 | -122.287 | 0.83313 | 122.0627 | 0.89264 | 3.1631
2861.7656 | 122.2366 | -0.98419 | 121.2799 | -0.1403 | 0.023701 | 0.0052018 | 0.055232 | -0.00025628 | -0.0007904 | -0.0037384 | -0.12848 | 0.013185 | 0.14536 | 0.22276 | -0.030849 | 0.093913 | 0.030441 | -0.054932 | 0.20599 | -0.16479 | -0.10986 | 0.032043 | -0.10986 | 1.7624 | 2.3895 | 121.2341 | -1.0574 | 121.0968 | -0.5722 | 118.2953 | 4.3167 | 0.8194 | -121.0739 | -121.3898 | 1.0162 | 2.7466 | 0.87433 | 1.9272 | 0.054932 | -0.073242 | -0.045776 | -0.1831 | 0.41199 | 5.3009 | 119.2795 | 5.3741 | 119.3527 | 0.19684 | 0.054932 | 0.48523 | 122.1542 | 0.37079 | 122.2916 | 1.1902 | 122.2183 | -121.4447 | -122.3373 | 0.87433 | 122.081 | 0.92926 | 3.3737
2862.8281 | 122.1405 | -0.98419 | 121.2708 | -0.16319 | 0.024342 | 0.005629 | 0.055873 | -0.01756 | -0.009549 | -0.013779 | -0.18036 | 0.014467 | 0.13788 | 0.22639 | -0.027218 | 0.091777 | 0.033646 | -0.013733 | 0.1831 | -0.15106 | -0.068665 | 0.073242 | -0.1236 | 1.7349 | 2.4902 | 121.2158 | -1.0574 | 121.0007 | -0.59052 | 118.2678 | 4.3945 | 0.83313 | -121.0876 | -121.3394 | 1.0574 | 2.7191 | 0.8606 | 1.886 | 0.027466 | -0.073242 | -0.054932 | -0.27008 | 0.39368 | 5.3787 | 119.252 | 5.452 | 119.3253 | 0.2243 | 0.082397 | 0.46692 | 122.0581 | 0.33417 | 122.2733 | 1.1673 | 122.2 | -121.4218 | -122.3282 | 0.91553 | 121.9849 | 0.97046 | 3.4744
2863.7656 | 122.2046 | -0.97961 | 121.2616 | -0.26237 | 0.024129 | 0.002211 | 0.055659 | 0.0014527 | -0.0031402 | -0.0052338 | -0.12238 | 0.01233 | 0.14386 | 0.22255 | -0.029995 | 0.09434 | 0.035995 | -0.041199 | 0.25177 | -0.11902 | -0.1236 | 0.018311 | -0.10071 | 1.7441 | 2.4994 | 121.2112 | -1.0666 | 121.106 | -0.59967 | 118.2632 | 4.5136 | 0.86059 | -121.0098 | -121.3852 | 0.99792 | 2.7237 | 0.87891 | 1.8631 | 0.018311 | -0.086975 | -0.050354 | -0.15564 | 0.37994 | 5.4932 | 119.2429 | 5.5801 | 119.3298 | 0.13733 | -0.004577 | 0.46692 | 122.1725 | 0.37079 | 122.2778 | 1.2314 | 122.1909 | -121.3806 | -122.3282 | 0.85602 | 122.0856 | 0.93841 | 3.479
2864.7656 | 122.2046 | -0.97504 | 121.2616 | -0.18608 | 0.023915 | 0.0060562 | 0.055019 | 0.0014527 | 6.4004e-05 | -0.003952 | -0.073547 | 0.015962 | 0.14621 | 0.22639 | -0.030849 | 0.095408 | 0.033859 | -0.013733 | 0.19226 | -0.14191 | -0.07782 | 0.086975 | -0.10529 | 1.7303 | 2.4261 | 121.2067 | -1.0757 | 121.0739 | -0.60883 | 118.277 | 4.5502 | 0.83313 | -121.0693 | -121.3394 | 1.062 | 2.7054 | 0.86975 | 1.8723 | 0.036621 | -0.10071 | -0.054932 | -0.18768 | 0.36621 | 5.5252 | 119.252 | 5.6259 | 119.3527 | 0.22888 | 0.064087 | 0.46692 | 122.1497 | 0.33417 | 122.2824 | 1.1673 | 122.1817 | -121.4035 | -122.3373 | 0.89722 | 122.049 | 0.9613 | 3.4012
2865.7656 | 122.319 | -0.95673 | 121.2479 | -0.16319 | 0.02242 | 0.0047744 | 0.0563 | 0.0057251 | -0.0007904 | -0.005661 | -0.055237 | 0.01233 | 0.14386 | 0.21977 | -0.030209 | 0.093486 | 0.033432 | 0.027466 | 0.16937 | -0.1236 | 0.018311 | 0.18768 | 0 | 1.8265 | 2.3392 | 121.1563 | -1.0483 | 121.1517 | -0.48065 | 118.3777 | 4.7333 | 0.83313 | -121.0785 | -121.2296 | 1.1444 | 2.7832 | 0.95673 | 1.9501 | 0.1236 | -0.091553 | -0.091553 | -0.096131 | 0.47607 | 5.69 | 119.3344 | 5.7816 | 119.426 | 0.31128 | 0.14191 | 0.56763 | 122.2 | 0.29297 | 122.2046 | 1.1261 | 122.113 | -121.3715 | -122.2961 | 0.97504 | 122.1085 | 0.98419 | 3.2959
2866.7656 | 122.2504 | -1.0117 | 121.2341 | -0.15556 | 0.022633 | 0.0054154 | 0.055659 | -0.0023925 | -0.0029266 | -0.0033112 | -0.12543 | 0.012758 | 0.14664 | 0.22832 | -0.032986 | 0.09669 | 0.033005 | -0.036621 | 0.20599 | -0.17395 | -0.11902 | 0.032043 | -0.11902 | 1.712 | 2.5406 | 121.2067 | -1.0757 | 121.0739 | -0.61798 | 118.2404 | 4.7699 | 0.83771 | -121.0281 | -121.3531 | 1.0437 | 2.7237 | 0.89264 | 1.886 | 0.054931 | -0.064087 | -0.027466 | -0.16022 | 0.39368 | 5.7816 | 119.252 | 5.8456 | 119.3161 | 0.20599 | 0.054931 | 0.45776 | 122.1497 | 0.37994 | 122.2824 | 1.2177 | 122.2183 | -121.4081 | -122.3099 | 0.89264 | 122.0856 | 0.97504 | 3.5522
2867.7656 | 122.2046 | -0.98419 | 121.2845 | -0.14793 | 0.02242 | 0.003279 | 0.053523 | -0.00089728 | -0.0035674 | -0.0030976 | -0.091858 | 0.014039 | 0.14578 | 0.22426 | -0.029354 | 0.094554 | 0.038986 | -0.045776 | 0.20599 | -0.14191 | -0.10071 | 0.032043 | -0.11444 | 1.7258 | 1.2177 | 121.1975 | -1.0941 | 121.1929 | -0.39368 | 118.1259 | 4.8477 | 0.84228 | -121.0785 | -121.3852 | 1.0162 | 2.71 | 0.86975 | 1.8677 | 0.027466 | -0.10986 | -0.086975 | -0.091553 | 0.59051 | 5.8319 | 119.1101 | 5.9418 | 119.22 | 0.17395 | 0.041199 | 0.70038 | 122.287 | 0.3479 | 122.2916 | 1.1902 | 122.1817 | -121.4264 | -122.3785 | 0.88348 | 122.1771 | 0.93842 | 2.2018
2868.7656 | 122.2183 | -1.0162 | 121.2387 | -0.33867 | 0.025838 | 0.00392 | 0.055873 | 0.0040161 | -0.0024994 | -0.0030976 | -0.12543 | 0.012544 | 0.14514 | 0.22917 | -0.030422 | 0.096263 | 0.03685 | -0.009155 | 0.23804 | -0.091553 | -0.1236 | 0.036621 | -0.10529 | 1.7441 | 2.4216 | 121.2112 | -1.0986 | 121.0648 | -0.63171 | 118.2312 | 5.0812 | 0.92468 | -121.0007 | -121.3623 | 1.0529 | 2.7603 | 0.91095 | 1.8356 | -0.013733 | -0.082398 | -0.027465 | -0.17395 | 0.38452 | 6.0974 | 119.2474 | 6.1798 | 119.3298 | 0.12817 | -0.032043 | 0.46692 | 122.1634 | 0.32959 | 122.3099 | 1.2543 | 122.2275 | -121.3303 | -122.3373 | 0.89264 | 122.081 | 1.0071 | 3.4378
2869.8281 | 122.2412 | -1.0391 | 121.2341 | -0.018234 | 0.025197 | 0.0043472 | 0.056087 | 0.0020935 | -0.0035674 | -0.0030976 | -0.12848 | 0.015748 | 0.14642 | 0.23045 | -0.032131 | 0.09434 | 0.044327 | -0.086975 | 0.22888 | -0.12817 | -0.10986 | 0.045776 | -0.1236 | 1.7349 | 2.3941 | 121.1929 | -1.1353 | 121.0556 | -0.6134 | 118.2312 | 5.6992 | 0.91095 | -121.0052 | -121.344 | 1.0849 | 2.774 | 0.91553 | 1.8631 | 0.004578 | -0.09613 | -0.041199 | -0.17853 | 0.42572 | 6.7383 | 119.2703 | 6.8344 | 119.3665 | 0.17395 | 0.018311 | 0.52185 | 122.1909 | 0.35706 | 122.3282 | 1.268 | 122.2321 | -121.3623 | -122.3694 | 0.92926 | 122.0947 | 0.95215 | 3.4332
2870.7656 | 122.2641 | -1.0208 | 121.2158 | -0.14793 | 0.021352 | 0.006697 | 0.054805 | 0.0012391 | -0.0022858 | -0.0026704 | -0.055237 | 0.013612 | 0.14664 | 0.23152 | -0.029995 | 0.093913 | 0.04454 | 0.009155 | 0.16479 | -0.13733 | -0.041199 | 0.11444 | -0.050354 | 1.8036 | 2.449 | 121.1792 | -1.0574 | 121.0968 | -0.58136 | 118.2678 | 5.7404 | 0.88348 | -121.051 | -121.257 | 1.1353 | 2.8244 | 0.97046 | 1.9409 | 0.086975 | -0.036621 | -0.036621 | -0.11902 | 0.43945 | 6.7612 | 119.2886 | 6.7978 | 119.3253 | 0.25177 | 0.09613 | 0.47607 | 122.1542 | 0.30212 | 122.2366 | 1.1856 | 122.2 | -121.3531 | -122.2733 | 0.97961 | 122.1176 | 1.03 | 3.4698
2871.7656 | 122.3236 | -1.0986 | 121.1472 | -0.16319 | 0.023701 | 0.0054154 | 0.054378 | -0.00068368 | -0.0016448 | -0.0048066 | -0.09491 | 0.074708 | 0.15561 | 0.214 | -0.032772 | 0.093272 | 0.082779 | 0.022888 | 0.16937 | -0.13275 | -0.022888 | 0.16479 | -0.036621 | 2.6459 | 2.33 | 121.0464 | -1.1856 | 121.0007 | -0.55389 | 118.1946 | 51.1688 | 0.96588 | -120.9778 | -121.17 | 1.2634 | 3.7445 | 1.062 | 2.7786 | 0.09613 | -0.086975 | -0.10071 | -0.14648 | 0.54474 | 52.2675 | 119.2932 | 52.3544 | 119.3802 | 0.29755 | 0.10986 | 0.63171 | 122.1863 | 0.30212 | 122.2321 | 1.268 | 122.1451 | -121.2799 | -122.3328 | 1.0757 | 122.0993 | 1.1215 | 3.4286
2872.7656 | 122.3145 | -1.1765 | 121.0007 | -0.17082 | 0.023701 | 0.004988 | 0.054591 | 0.0014527 | -0.0035674 | -0.0058746 | -0.29327 | 0.53784 | 0.15668 | 0.22191 | -0.033626 | 0.09135 | 0.54549 | 0.022888 | 0.17853 | -0.11444 | 0 | 0.17853 | 0 | 2.9755 | 2.2476 | 120.9 | -1.1993 | 120.8817 | -0.53101 | 118.0618 | 92.2806 | 1.062 | -120.8221 | -121.0007 | 1.355 | 4.1519 | 1.1765 | 3.0899 | 0.11444 | -0.022888 | -0.10071 | -0.11902 | 0.64545 | 93.457 | 119.2383 | 93.4799 | 119.2612 | 0.29297 | 0.11444 | 0.66834 | 122.081 | 0.29297 | 122.0993 | 1.355 | 122.0764 | -121.1151 | -122.2 | 1.1765 | 122.0581 | 1.1993 | 3.4241
2873.7656 | 122.2183 | -1.1856 | 121.0464 | -0.13267 | 0.020924 | 0.0058426 | 0.054378 | 0.0035889 | -0.0037812 | -0.0035248 | -0.26581 | 0.45667 | 0.15668 | 0.25374 | -0.032558 | 0.091777 | 0.49742 | 0.004578 | 0.16937 | -0.12817 | -0.059509 | 0.1236 | -0.064087 | 2.7969 | 2.3209 | 120.9457 | -1.2039 | 120.8405 | -0.60883 | 118.0023 | 81.8344 | 1.0574 | -120.8771 | -121.106 | 1.3092 | 3.9825 | 1.1215 | 2.9251 | 0.064087 | -0.01831 | -0.10071 | -0.20599 | 0.57678 | 83.02 | 119.1879 | 83.0383 | 119.2062 | 0.25177 | 0.068665 | 0.59509 | 122.0444 | 0.29755 | 122.1497 | 1.355 | 122.1313 | -121.1746 | -122.2504 | 1.1261 | 122.0261 | 1.1902 | 3.5065
2874.7656 | 122.2 | -1.0208 | 121.2433 | -0.1403 | 0.023701 | 0.0037064 | 0.056087 | 0.00038452 | -0.0039948 | -0.0052338 | -0.13458 | 0.02408 | 0.14728 | 0.24348 | -0.030636 | 0.092845 | 0.065262 | -0.059509 | 0.20142 | -0.16022 | -0.11444 | 0.036621 | -0.11444 | 1.2405 | 2.3712 | 121.2387 | -1.0574 | 121.051 | -0.65918 | 118.1946 | -6.2256 | 0.8606 | -121.0419 | -121.3577 | 1.0574 | 2.2614 | 0.90637 | 1.4008 | 0.045776 | -0.036621 | -0.004578 | -0.19226 | 0.36163 | -5.2048 | 119.2154 | -5.1682 | 119.252 | 0.19684 | 0.045776 | 0.39825 | 122.1085 | 0.36163 | 122.2961 | 1.2222 | 122.2595 | -121.4035 | -122.3007 | 0.90637 | 122.0718 | 0.9613 | 3.392
2875.7656 | 122.2641 | -1.0345 | 121.2616 | -0.17082 | 0.02242 | 0.0041336 | 0.051387 | 0.00038452 | -0.0001496 | 0.00010684 | -0.09491 | 0.013612 | 0.14749 | 0.22362 | -0.029354 | 0.096904 | 0.030655 | -0.036621 | 0.20142 | -0.13733 | -0.091553 | 0.054932 | -0.10071 | 1.7624 | 2.3163 | 121.1563 | -1.1215 | 121.0373 | -0.62714 | 118.1213 | 1.7853 | 0.89722 | -121.0602 | -121.3531 | 1.0895 | 2.7969 | 0.93384 | 1.8997 | 0.036621 | -0.086975 | -0.10529 | -0.22431 | 0.40741 | 2.8198 | 119.1559 | 2.9068 | 119.2429 | 0.19226 | 0.045776 | 0.49438 | 122.1588 | 0.33875 | 122.2778 | 1.236 | 122.1909 | -121.3989 | -122.3831 | 0.94299 | 122.0718 | 0.99792 | 3.3508
2876.7656 | 122.2458 | -1.0437 | 121.1975 | -0.14793 | 0.020711 | 0.0017838 | 0.056087 | 0.00017092 | -0.0031402 | -0.003952 | -0.079651 | 0.017457 | 0.14792 | 0.22191 | -0.031277 | 0.095195 | 0.028732 | -0.004578 | 0.19226 | -0.14191 | -0.068665 | 0.10071 | -0.082397 | 1.767 | 2.33 | 121.1563 | -1.1215 | 121.0373 | -0.61798 | 118.1763 | 4.4632 | 0.90179 | -121.0052 | -121.2662 | 1.1444 | 2.8107 | 0.9613 | 1.9089 | 0.05951 | -0.07782 | -0.041199 | -0.16022 | 0.42572 | 5.5069 | 119.22 | 5.5847 | 119.2978 | 0.24262 | 0.073242 | 0.50354 | 122.1588 | 0.33417 | 122.2778 | 1.236 | 122.2 | -121.3394 | -122.319 | 0.97504 | 122.081 | 1.0391 | 3.3737
2877.7656 | 122.2092 | -1.0666 | 121.1838 | -0.17082 | 0.024983 | 0.0034928 | 0.055446 | 0.0014527 | -0.0031402 | -0.0054474 | -0.10406 | 0.015748 | 0.1507 | 0.23109 | -0.031063 | 0.096477 | 0.032791 | 0.004578 | 0.16937 | -0.13733 | -0.054932 | 0.11902 | -0.050354 | 1.7395 | 2.4445 | 121.1334 | -1.1215 | 121.0602 | -0.62256 | 118.19 | 6.6605 | 0.92926 | -121.0144 | -121.2387 | 1.1856 | 2.8061 | 1.0162 | 1.8768 | 0.086975 | -0.054932 | -0.050354 | -0.1236 | 0.44403 | 7.7271 | 119.2566 | 7.782 | 119.3115 | 0.25635 | 0.082397 | 0.49896 | 122.1817 | 0.3067 | 122.2549 | 1.236 | 122.2 | -121.3211 | -122.3053 | 1.0117 | 122.1268 | 1.0712 | 3.511
2878.7656 | 122.2275 | -1.0666 | 121.1792 | -0.58281 | 0.0091751 | -0.0014206 | 0.055019 | -0.01521 | -0.0082672 | -0.018692 | -0.22003 | 0.012117 | 0.14044 | 0.22682 | -0.03149 | 0.092418 | 0.03685 | -0.041199 | 0.17395 | -0.16937 | -0.11902 | 0.013733 | -0.16479 | 1.6479 | 2.3804 | 121.1197 | -1.149 | 121.0236 | -0.68207 | 118.0984 | 4.6234 | 0.89722 | -121.0052 | -121.2982 | 1.0803 | 2.7145 | 0.90179 | 1.8173 | 0.004578 | -0.082398 | -0.059509 | -0.15564 | 0.38452 | 5.69 | 119.165 | 5.7724 | 119.2474 | 0.18311 | 0.050354 | 0.46692 | 122.1725 | 0.34332 | 122.2687 | 1.2405 | 122.1863 | -121.3486 | -122.3282 | 0.94757 | 122.0901 | 1.0254 | 3.447
2879.7656 | 122.2504 | -1.0712 | 121.2662 | -0.20134 | 0.026051 | 0.0058426 | 0.052455 | 0.00017092 | -0.0005768 | -0.0035248 | -0.11627 | 0.017885 | 0.14984 | 0.22661 | -0.028713 | 0.094981 | 0.040481 | -0.041199 | 0.19226 | -0.1236 | -0.091553 | 0.07782 | -0.11444 | 1.7166 | 2.3849 | 121.1334 | -1.149 | 121.019 | -0.63629 | 118.1534 | 4.5273 | 0.94757 | -121.0739 | -121.3577 | 1.149 | 2.7878 | 0.95673 | 1.8402 | 0.009155 | -0.07782 | -0.13275 | -0.24719 | 0.43488 | 5.5984 | 119.2245 | 5.6763 | 119.3024 | 0.20142 | 0.032043 | 0.5127 | 122.168 | 0.31586 | 122.2824 | 1.2634 | 122.2046 | -121.3898 | -122.4152 | 0.97961 | 122.0901 | 1.03 | 3.4561
2880.7656 | 122.2916 | -1.0574 | 121.2021 | -0.17082 | 0.023274 | 0.0026382 | 0.052882 | 0.00081172 | -0.0003632 | -0.0054474 | -0.067444 | 0.014253 | 0.14941 | 0.22618 | -0.0285 | 0.095195 | 0.031296 | 0.036621 | 0.14648 | -0.10986 | 0.013733 | 0.19226 | -0.004578 | 1.8173 | 2.5864 | 121.0922 | -1.1215 | 121.106 | -0.54474 | 118.2907 | 4.9026 | 0.94757 | -121.0556 | -121.1884 | 1.2497 | 2.8748 | 1.0529 | 1.9272 | 0.10529 | -0.064087 | -0.10986 | -0.09613 | 0.5127 | 5.9601 | 119.3481 | 6.0242 | 119.4122 | 0.30212 | 0.1236 | 0.57678 | 122.2275 | 0.25635 | 122.2137 | 1.2039 | 122.1497 | -121.312 | -122.3236 | 1.0712 | 122.1634 | 1.0941 | 3.6438
2881.7656 | 122.3007 | -1.0529 | 121.1929 | -0.20897 | 0.02477 | 0.005629 | 0.056941 | -0.0032471 | -0.0031402 | -0.0030976 | -0.082703 | 0.015962 | 0.15091 | 0.22746 | -0.030209 | 0.094127 | 0.039627 | -0.004578 | 0.18768 | -0.13275 | -0.054932 | 0.11444 | -0.054932 | 1.7944 | 2.5589 | 121.1243 | -1.1536 | 121.0281 | -0.62714 | 118.1625 | 2.861 | 0.9201 | -121.0052 | -121.2479 | 1.1673 | 2.8473 | 0.99792 | 1.9272 | 0.077819 | -0.10071 | -0.068664 | -0.16479 | 0.42572 | 3.9139 | 119.2154 | 4.0146 | 119.3161 | 0.24719 | 0.077819 | 0.52643 | 122.1817 | 0.32043 | 122.2778 | 1.2405 | 122.1771 | -121.3257 | -122.3465 | 0.99792 | 122.081 | 1.0483 | 3.6118
2882.7656 | 122.2549 | -1.0712 | 121.1884 | -0.13267 | 0.023061 | 0.005629 | 0.055019 | 0.00017092 | -0.0022858 | -0.002884 | -0.085754 | 0.018312 | 0.15241 | 0.22917 | -0.030422 | 0.095408 | 0.035568 | 0.018311 | 0.16022 | -0.12817 | -0.036621 | 0.12817 | -0.050354 | 1.8082 | 2.6047 | 121.138 | -1.149 | 121.0693 | -0.59967 | 118.1854 | 4.715 | 0.94299 | -121.0281 | -121.225 | 1.1993 | 2.8793 | 1.0208 | 1.9363 | 0.07782 | -0.07782 | -0.050354 | -0.11902 | 0.4715 | 5.7861 | 119.2566 | 5.864 | 119.3344 | 0.25635 | 0.091553 | 0.54932 | 122.2183 | 0.28839 | 122.287 | 1.2314 | 122.2092 | -121.3165 | -122.3373 | 1.0345 | 122.1405 | 1.0895 | 3.6758
2883.7656 | 122.2046 | -1.0757 | 121.1746 | -0.31578 | 0.016225 | 0.00092921 | 0.057368 | -0.013928 | -0.0076264 | -0.020187 | -0.19257 | 0.015321 | 0.14664 | 0.22703 | -0.029995 | 0.092631 | 0.037064 | -0.050354 | 0.17395 | -0.17853 | -0.1236 | 0.022888 | -0.17853 | 1.6891 | 2.536 | 121.1334 | -1.1902 | 121.0236 | -0.70496 | 118.0801 | 4.7791 | 0.89722 | -121.0007 | -121.2982 | 1.0986 | 2.7649 | 0.89722 | 1.8677 | 0 | -0.11444 | -0.041199 | -0.15106 | 0.37079 | 5.8548 | 119.1559 | 5.9692 | 119.2703 | 0.20142 | 0.054932 | 0.48523 | 122.2137 | 0.35248 | 122.3236 | 1.2497 | 122.2092 | -121.3531 | -122.3648 | 0.95215 | 122.0993 | 1.0254 | 3.6118
2884.7656 | 122.2595 | -1.0574 | 121.1929 | -0.14793 | 0.022633 | 0.0045608 | 0.054378 | -0.00046988 | -0.0003632 | -0.0024566 | -0.091858 | 0.016603 | 0.15155 | 0.22832 | -0.030422 | 0.092204 | 0.033432 | -0.045776 | 0.19684 | -0.15106 | -0.11444 | 0.059509 | -0.11902 | 1.7578 | 2.4765 | 121.1288 | -1.1673 | 121.1014 | -0.79651 | 118.1625 | 4.8477 | 0.90637 | -120.9961 | -121.3074 | 1.1169 | 2.8152 | 0.93841 | 1.9089 | 0.032043 | -0.10986 | -0.064087 | -0.091553 | 0.26092 | 5.9052 | 119.22 | 6.015 | 119.3298 | 0.21057 | 0.036621 | 0.37079 | 122.2687 | 0.3479 | 122.2961 | 1.2543 | 122.1863 | -121.344 | -122.3602 | 0.94299 | 122.1588 | 1.0117 | 3.5339
2885.8281 | 122.2778 | -1.0849 | 121.1563 | -0.18608 | 0.024556 | 0.0041336 | 0.05395 | -0.0017517 | -0.0020722 | -0.0043792 | -0.09491 | 0.016603 | 0.15219 | 0.22789 | -0.031917 | 0.095622 | 0.037704 | 0.004578 | 0.18768 | -0.1236 | -0.018311 | 0.15106 | -0.036621 | 1.8082 | 2.6688 | 121.1151 | -1.1536 | 121.0419 | -0.62256 | 118.1717 | 4.9026 | 0.9613 | -120.9686 | -121.1746 | 1.236 | 2.8931 | 1.0483 | 1.9318 | 0.086975 | -0.068664 | -0.041199 | -0.11444 | 0.46234 | 5.9875 | 119.2566 | 6.0562 | 119.3253 | 0.27466 | 0.10528 | 0.53101 | 122.1954 | 0.31128 | 122.2687 | 1.2726 | 122.2 | -121.2799 | -122.3099 | 1.0666 | 122.1268 | 1.0895 | 3.7537
2886.7656 | 122.3694 | -1.0666 | 121.1609 | -0.1403 | 0.020283 | 0.0030654 | 0.054591 | -0.0043151 | 0.0026276 | -0.0013886 | -0.067444 | 0.017244 | 0.15198 | 0.22746 | -0.030849 | 0.095195 | 0.034927 | 0.036621 | 0.16022 | -0.10529 | -0.10986 | 0.23346 | 0.059509 | 1.7624 | 2.6138 | 121.106 | -1.1673 | 121.1014 | -0.51727 | 118.2541 | 5.127 | 0.9613 | -121.0007 | -121.2708 | 1.3 | 2.829 | 1.1261 | 1.8677 | 0.16479 | -0.10071 | -0.054932 | -0.05951 | 0.54932 | 6.1935 | 119.3207 | 6.2942 | 119.4214 | 0.33875 | -0.004577 | 0.65002 | 122.2687 | 0.2655 | 122.2733 | 1.2268 | 122.1725 | -121.2662 | -122.3282 | 0.95673 | 122.168 | 1.1032 | 3.6804
2887.7656 | 122.3511 | -1.0849 | 121.1792 | -0.20134 | 0.023274 | 0.004988 | 0.054164 | 0.00017092 | -0.0016448 | -0.0018158 | -0.091858 | 0.016176 | 0.15305 | 0.23259 | -0.030422 | 0.094554 | 0.039627 | 0.027466 | 0.14648 | -0.10071 | 0.022888 | 0.18768 | 0.004578 | 1.8311 | 2.6001 | 121.0922 | -1.1536 | 121.0739 | -0.57678 | 118.2358 | 5.159 | 0.98419 | -121.0327 | -121.1563 | 1.2726 | 2.916 | 1.0895 | 1.9318 | 0.10529 | -0.068664 | -0.086975 | -0.10528 | 0.50812 | 6.2439 | 119.3207 | 6.3126 | 119.3893 | 0.28839 | 0.1236 | 0.57678 | 122.2275 | 0.24719 | 122.2458 | 1.2314 | 122.1771 | -121.2799 | -122.3328 | 1.1078 | 122.1588 | 1.1124 | 3.685
2888.7656 | 122.2778 | -1.0941 | 121.1517 | -0.17082 | 0.025197 | 0.0037064 | 0.056728 | 0.0010253 | -0.0057038 | -0.0058746 | -0.1712 | 0.016816 | 0.15134 | 0.23707 | -0.030636 | 0.094768 | 0.035995 | -0.022888 | 0.18768 | -0.16022 | -0.054932 | 0.086975 | -0.10071 | 1.7487 | 2.4078 | 121.0968 | -1.1948 | 121.0648 | -0.62256 | 118.1259 | 5.3375 | 0.93384 | -120.964 | -121.2067 | 1.181 | 2.8427 | 0.99335 | 1.9089 | 0.059509 | -0.10071 | -0.054931 | -0.086975 | 0.4715 | 6.4316 | 119.22 | 6.5323 | 119.3207 | 0.24719 | 0.10528 | 0.5722 | 122.2595 | 0.3479 | 122.2916 | 1.2817 | 122.1909 | -121.3119 | -122.3465 | 1.0391 | 122.1588 | 1.0712 | 3.5019
2889.7656 | 122.2412 | -1.1353 | 121.1838 | -0.16319 | 0.02242 | 0.0037064 | 0.05331 | 0.0010253 | -0.0022858 | -0.0024566 | 0.011902 | 0.017885 | 0.15839 | 0.23707 | -0.028286 | 0.097758 | 0.040268 | -0.059509 | 0.19684 | -0.15564 | -0.12817 | 0.045776 | -0.12817 | 1.7624 | 2.4216 | 121.1563 | -1.1536 | 121.0052 | -0.67749 | 118.0893 | 5.6122 | 0.97961 | -120.9869 | -121.312 | 1.181 | 2.8976 | 1.0071 | 1.918 | 0.027466 | -0.01831 | -0.027466 | -0.17853 | 0.45776 | 6.7474 | 119.2245 | 6.7657 | 119.2429 | 0.20142 | 0.027466 | 0.47607 | 122.1588 | 0.35248 | 122.3099 | 1.3321 | 122.2916 | -121.3394 | -122.3373 | 1.0071 | 122.1405 | 1.0757 | 3.5568
2890.7656 | 122.287 | -1.1215 | 121.138 | -0.16319 | 0.023274 | 0.005629 | 0.055232 | 0.0018799 | -0.0005768 | -0.0033112 | -0.082703 | 0.017457 | 0.15369 | 0.23643 | -0.029354 | 0.093913 | 0.043686 | 0.013733 | 0.16937 | -0.11444 | -0.022888 | 0.15564 | -0.032043 | 1.8265 | 2.4857 | 121.0968 | -1.1719 | 121.0281 | -0.63629 | 118.1488 | 6.1844 | 1.0071 | -120.9686 | -121.1609 | 1.2772 | 2.948 | 1.0895 | 1.9409 | 0.082398 | -0.050354 | -0.041198 | -0.10986 | 0.48523 | 7.3059 | 119.2703 | 7.3563 | 119.3207 | 0.27008 | 0.091553 | 0.53558 | 122.2 | 0.28381 | 122.2687 | 1.2909 | 122.2183 | -121.2524 | -122.3099 | 1.0986 | 122.1497 | 1.1353 | 3.6072
2891.7656 | 122.2961 | -1.2451 | 120.9915 | -0.17845 | 0.023488 | 0.003279 | 0.055019 | 0.0018799 | -0.0039948 | -0.0026704 | -0.22919 | 0.016176 | 0.16309 | 0.59297 | -0.032558 | 0.091777 | 0.38762 | 0.018311 | 0.16479 | -0.12817 | -0.027466 | 0.16479 | -0.027466 | 2.5314 | 2.0462 | 120.9183 | -1.2772 | 120.8176 | -0.61798 | 117.9382 | 63.1302 | 1.1169 | -120.8267 | -121.019 | 1.4099 | 3.7765 | 1.2177 | 2.6596 | 0.10071 | -0.032044 | -0.073242 | -0.17395 | 0.62714 | 64.3753 | 119.1833 | 64.4073 | 119.2154 | 0.29297 | 0.10071 | 0.65918 | 122.0947 | 0.29297 | 122.1954 | 1.4099 | 122.1634 | -121.1197 | -122.2687 | 1.2177 | 122.0627 | 1.2634 | 3.2913
2892.7656 | 122.2916 | -2.3117 | 119.8059 | -0.22423 | 0.021992 | 0.0062698 | 0.053096 | 0.00017092 | -0.0033538 | -0.0026704 | -0.95551 | 1.1977 | 2.0079 | 1.2298 | -0.031917 | 0.090495 | 0.37138 | 0.041199 | 0.13733 | -0.1236 | 0.018311 | 0.23346 | 0.009155 | 2.8885 | 0.80566 | 119.5633 | -2.1652 | 119.5221 | 15.5823 | 116.6245 | 41.9449 | 2.1881 | -119.6686 | -119.7876 | 2.5452 | 5.2002 | 2.3209 | 3.0121 | 0.13275 | 0.14649 | -0.24262 | -0.28381 | 17.894 | 44.2566 | 118.9362 | 44.1101 | 118.7897 | 0.35706 | 0.14191 | 17.7475 | 121.6873 | 0.26093 | 121.7285 | 2.449 | 121.875 | -119.9295 | -121.9711 | 2.33 | 121.8338 | 2.3529 | 3.1174
2893.7656 | 122.2687 | -0.33417 | 121.9254 | -0.23949 | 0.016011 | 0.0011428 | 0.055232 | -0.0060241 | -0.0022858 | -0.0088654 | -0.10406 | 0.014253 | 0.021668 | 0.0080707 | -0.031277 | -0.0015765 | -0.00032051 | -0.045776 | 0.19226 | -0.15106 | -0.15106 | -0.059509 | -0.073242 | -0.091553 | -0.25635 | 0.050354 | -0.41657 | -0.21973 | -0.20142 | -0.2655 | -0.2243 | 0.1831 | -121.7331 | -122.0764 | 0.27466 | 0.24261 | 0.26092 | 0.059509 | 0.07782 | -0.082398 | -121.875 | -122.1451 | 0.13275 | 0.10986 | 0.068664 | 0.19226 | 0.15106 | 0.091553 | 0 | 0.21515 | 0.19684 | 0.34332 | 0.46692 | 0.52643 | 0.38452 | -122.0764 | -122.3419 | 0.1831 | 0.11444 | 0.28839 | 0.077819
2894.7656 | 122.3282 | -0.32959 | 121.9208 | -0.17082 | 0.023701 | 0.0060562 | 0.054805 | -0.0013245 | -0.004422 | -0.001175 | 0.021057 | 0.013185 | 0.021027 | 0.0023029 | -0.031063 | -0.0013629 | 0.0030975 | 0.009155 | 0.16479 | -0.1236 | -0.036621 | 0.10986 | -0.027466 | 0.050354 | -0.16022 | 0.036621 | -0.3891 | -0.18768 | -0.11444 | -0.1831 | -0.16937 | 0.20599 | -121.756 | -121.9574 | 0.43945 | 0.37994 | 0.30212 | 0.17395 | 0.09613 | -0.059509 | -121.8842 | -122.1085 | 0.21515 | 0.16022 | 0.14649 | 0.21973 | 0.20599 | 0.23346 | 0.086975 | 0.27466 | 0.20142 | 0.28839 | 0.42572 | 0.49438 | 0.36621 | -122.0444 | -122.3099 | 0.29297 | 0.14191 | 0.33875 | 0.16937
2895.7656 | 122.3145 | -0.33417 | 121.9711 | -0.086899 | 0.026906 | 0.0086196 | 0.055873 | -0.0013245 | -0.0033538 | -0.0020294 | -0.073547 | 0.014894 | 0.019745 | 0.0059345 | -0.029781 | -0.00050847 | 0.0020295 | -0.045776 | 0.16022 | -0.16022 | -0.091553 | -0.004578 | -0.10986 | -0.018311 | -0.21515 | 0.045776 | -0.41199 | -0.20599 | -0.13275 | -0.21973 | -0.19226 | 0.17395 | -121.8109 | -122.0627 | 0.32959 | 0.31586 | 0.2243 | 0.14191 | 0.050354 | -0.07782 | -121.9254 | -122.1771 | 0.20142 | 0.14191 | 0.11444 | 0.21973 | 0.19226 | 0.15564 | 0.068664 | 0.27924 | 0.20599 | 0.32043 | 0.45776 | 0.49438 | 0.37994 | -122.1313 | -122.3831 | 0.24261 | 0.12817 | 0.28839 | 0.11902
2896.8281 | 122.4426 | -0.29755 | 121.9391 | -0.11742 | 0.025197 | 0.004988 | 0.053737 | 0.0025207 | -0.0018586 | -0.0035248 | 0.072937 | 0.015107 | 0.020172 | 0.0029437 | -0.029995 | -0.0039265 | -0.00010671 | 0.009155 | 0.16937 | -0.11444 | 0.036621 | 0.19684 | 0.027466 | 0.091553 | -0.17853 | 0.027466 | -0.3891 | -0.086975 | -0.073242 | -0.13733 | -0.11902 | 0.1831 | -121.7697 | -121.9025 | 0.49438 | 0.3891 | 0.32501 | 0.20599 | 0.14191 | -0.091553 | -121.9116 | -122.0261 | 0.2243 | 0.17853 | 0.16022 | 0.27008 | 0.25177 | 0.31128 | 0.15106 | 0.31586 | 0.30212 | 0.28381 | 0.41656 | 0.46692 | 0.32501 | -122.0535 | -122.3282 | 0.33417 | 0.21057 | 0.3067 | 0.11902
2897.7656 | 122.3419 | -0.32501 | 121.9711 | -0.079269 | 0.026692 | 0.005629 | 0.053096 | -4.2682e-05 | -0.0046356 | -0.0048066 | 0.014954 | 0.014894 | 0.018463 | 0.0091389 | -0.030422 | 0.0014141 | 0.0054475 | 0.027466 | 0.17395 | -0.12817 | -0.018311 | 0.10529 | -0.036621 | 0.054932 | -0.16022 | 0.022888 | -0.38452 | -0.20599 | -0.10071 | -0.19684 | -0.16937 | 0.19684 | -121.7972 | -121.9894 | 0.4303 | 0.37994 | 0.28839 | 0.18311 | 0.091553 | -0.059509 | -121.9482 | -122.1771 | 0.2243 | 0.15564 | 0.12817 | 0.21515 | 0.18768 | 0.23346 | 0.10986 | 0.28381 | 0.17853 | 0.30212 | 0.40741 | 0.49896 | 0.3479 | -122.0993 | -122.3557 | 0.3067 | 0.11902 | 0.35248 | 0.1648
2898.7656 | 122.4289 | -0.3067 | 121.9482 | -0.1403 | 0.022847 | 0.0058426 | 0.054164 | -0.00089728 | -0.0031402 | 0.00053404 | -0.033874 | 0.014253 | 0.018036 | 0.0050801 | -0.030636 | 0.0012005 | -0.0016021 | 0.050354 | 0.10071 | -0.14648 | -0.004578 | 0.12817 | -0.07782 | 0.041199 | -0.11902 | -0.018311 | -0.37537 | -0.1236 | -0.050354 | -0.14191 | -0.10529 | 0.16022 | -121.8475 | -121.9528 | 0.43488 | 0.3479 | 0.22888 | 0.18768 | 0.068664 | -0.068664 | -121.9666 | -122.0718 | 0.25635 | 0.20142 | 0.16479 | 0.27008 | 0.23346 | 0.27466 | 0.14191 | 0.32501 | 0.25177 | 0.24719 | 0.35705 | 0.40741 | 0.28839 | -122.0947 | -122.3236 | 0.30212 | 0.18311 | 0.35706 | 0.18768
2899.7656 | 122.3969 | -0.32044 | 121.962 | -0.11742 | 0.023701 | 0.005629 | 0.055659 | -0.0011109 | -0.0035674 | -0.00032036 | 0.018005 | 0.015321 | 0.018463 | 0.0020893 | -0.030636 | -0.00029487 | 0.0024567 | -0.036621 | 0.15106 | -0.1236 | 0.018311 | 0.15106 | -0.009155 | 0.091553 | -0.086975 | 0.018311 | -0.36621 | -0.14191 | -0.022888 | -0.12817 | -0.10071 | 0.19684 | -121.8109 | -121.9437 | 0.4715 | 0.41199 | 0.31128 | 0.21515 | 0.11444 | -0.045776 | -121.9437 | -122.1039 | 0.29755 | 0.21973 | 0.19226 | 0.2655 | 0.23804 | 0.27466 | 0.14191 | 0.34332 | 0.2243 | 0.27466 | 0.38452 | 0.4715 | 0.33875 | -122.0856 | -122.3282 | 0.33875 | 0.17853 | 0.28381 | 0.23346
2900.7656 | 122.3328 | -0.31586 | 122.0169 | -0.094528 | 0.024983 | 0.0043472 | 0.056087 | -0.0019653 | -0.0007904 | -0.005661 | -0.0064086 | 0.016816 | 0.018891 | -0.0019695 | -0.030422 | -0.0041401 | -0.00010671 | -0.041199 | 0.19684 | -0.16022 | -0.11902 | 0 | -0.1236 | -0.027466 | -0.23804 | 0.032043 | -0.42572 | -0.13733 | -0.27466 | -0.3067 | -0.23346 | 0.15564 | -121.8201 | -122.1359 | 0.31586 | 0.28839 | 0.19226 | 0.13275 | 0.036621 | -0.10986 | -121.9849 | -122.1542 | 0.041199 | 0.082398 | 0.009155 | 0.19226 | 0.11902 | 0.16022 | 0.041198 | 0.15106 | 0.28839 | 0.35706 | 0.45776 | 0.5127 | 0.3479 | -122.1771 | -122.4426 | 0.19684 | 0.17853 | 0.27466 | 0.07782
2901.7656 | 122.3465 | -0.34332 | 121.9849 | -0.1403 | 0.025624 | 0.0041336 | 0.055659 | -0.0019653 | -0.0050628 | -0.0050202 | -0.039978 | 0.015748 | 0.019959 | -0.00090154 | -0.030636 | -8.1274e-05 | 0.00032049 | -0.036621 | 0.21973 | -0.14191 | -0.11444 | -0.004578 | -0.1236 | -0.032043 | -0.25635 | 0.054932 | -0.40741 | -0.27924 | -0.15564 | -0.26093 | -0.21515 | 0.20142 | -121.7651 | -122.0993 | 0.33874 | 0.31128 | 0.21973 | 0.10986 | 0.018311 | -0.064087 | -121.9299 | -122.2641 | 0.18768 | 0.12817 | 0.082398 | 0.19226 | 0.14648 | 0.13733 | 0.027466 | 0.25177 | 0.12817 | 0.36163 | 0.46234 | 0.56305 | 0.39825 | -122.1268 | -122.3923 | 0.22888 | 0.064087 | 0.3067 | 0.086975
2902.7656 | 122.3236 | -0.34332 | 121.9803 | -0.17082 | 0.023701 | 0.0045608 | 0.056514 | -0.0015381 | -0.0020722 | -0.0033112 | -0.033874 | 0.014894 | 0.01825 | 0.0023029 | -0.029995 | -0.00093567 | 0.0022431 | -0.059509 | 0.20142 | -0.11902 | -0.11444 | 0.004578 | -0.11902 | -0.036621 | -0.25177 | 0.041199 | -0.39825 | -0.25177 | -0.15106 | -0.26093 | -0.2243 | 0.2243 | -121.7789 | -122.0947 | 0.3479 | 0.3067 | 0.2243 | 0.082398 | 0 | -0.054931 | -121.9391 | -122.2321 | 0.19226 | 0.11902 | 0.082398 | 0.17395 | 0.13733 | 0.1236 | 0.004578 | 0.24719 | 0.14648 | 0.32044 | 0.43945 | 0.54474 | 0.38452 | -122.0993 | -122.3785 | 0.22888 | 0.091553 | 0.28381 | 0.091553
2903.7656 | 122.3007 | -0.36621 | 121.994 | -0.079269 | 0.023488 | 0.0054154 | 0.055659 | -0.00068368 | -0.0016448 | -0.0020294 | -0.036926 | 0.015321 | 0.018891 | 0.0037983 | -0.029781 | -0.0020039 | -0.0013885 | -0.045776 | 0.23346 | -0.1236 | -0.1236 | -0.013733 | -0.10986 | -0.050354 | -0.24719 | 0.032043 | -0.41199 | -0.26093 | -0.16022 | -0.26093 | -0.20142 | 0.24262 | -121.7606 | -122.1176 | 0.35248 | 0.31586 | 0.25635 | 0.073242 | 0.013733 | -0.045776 | -121.962 | -122.2549 | 0.20599 | 0.16479 | 0.10529 | 0.21057 | 0.15106 | 0.10986 | 0 | 0.25177 | 0.15106 | 0.35706 | 0.44403 | 0.59967 | 0.39825 | -122.1176 | -122.406 | 0.24262 | 0.10529 | 0.32044 | 0.11902
2904.7656 | 122.3007 | -0.3479 | 122.0215 | -0.18608 | 0.023915 | 0.0052018 | 0.056941 | -0.0011109 | -0.0020722 | -0.0035248 | 0.021057 | 0.015535 | 0.02124 | 0.0027301 | -0.028927 | -0.0022175 | 0.0011749 | -0.032043 | 0.17853 | -0.14648 | -0.10529 | 0.036621 | -0.12817 | -0.018311 | -0.21973 | 0.036621 | -0.41657 | -0.27008 | -0.16022 | -0.24719 | -0.21973 | 0.20142 | -121.843 | -122.1268 | 0.38452 | 0.32959 | 0.21973 | 0.12817 | 0.01831 | -0.068665 | -121.9849 | -122.2916 | 0.18768 | 0.12817 | 0.10071 | 0.19684 | 0.16937 | 0.18311 | 0.041198 | 0.25635 | 0.14648 | 0.32501 | 0.45319 | 0.52643 | 0.38452 | -122.168 | -122.438 | 0.24261 | 0.077819 | 0.31586 | 0.12817
2905.7656 | 122.3007 | -0.35706 | 122.0032 | -0.18608 | 0.022206 | 0.0062698 | 0.052882 | -4.2682e-05 | -0.0033538 | -0.0037384 | 0.0027466 | 0.015321 | 0.018677 | 0.0012347 | -0.029354 | -0.0015765 | 0.0039521 | -0.018311 | 0.16937 | -0.14191 | -0.09613 | 0.041199 | -0.09613 | -0.018311 | -0.23346 | 0.045776 | -0.41199 | -0.27466 | -0.14191 | -0.25635 | -0.21057 | 0.21515 | -121.8338 | -122.0993 | 0.39825 | 0.33874 | 0.26093 | 0.1236 | 0.045777 | -0.054931 | -121.9574 | -122.2778 | 0.21515 | 0.14648 | 0.10071 | 0.20142 | 0.15564 | 0.18311 | 0.045777 | 0.27008 | 0.13733 | 0.31128 | 0.45776 | 0.52643 | 0.40283 | -122.1451 | -122.4152 | 0.26093 | 0.082398 | 0.33874 | 0.1236
2906.7656 | 122.3099 | -0.34332 | 122.0352 | -0.086899 | 0.023488 | 0.003279 | 0.055232 | -0.0011109 | -0.002713 | -0.002243 | -0.027771 | 0.014467 | 0.020813 | 0.0059345 | -0.029568 | -0.0017901 | -0.0018157 | 0.1236 | 0.20142 | -0.14191 | -0.1236 | -0.036621 | -0.091553 | -0.027466 | -0.22888 | 0.064087 | -0.40283 | -0.2655 | -0.15564 | -0.26093 | -0.21973 | 0.20142 | -121.8338 | -122.1588 | 0.3067 | 0.31586 | 0.25177 | 0.11444 | 0.050354 | -0.059509 | -121.9711 | -122.3007 | 0.18768 | 0.1236 | 0.082398 | 0.18311 | 0.14191 | 0.10529 | 0.018311 | 0.24719 | 0.13733 | 0.34332 | 0.46692 | 0.54474 | 0.40741 | -122.1771 | -122.438 | 0.21973 | 0.07782 | 0.46692 | 0.11444
2907.8281 | 122.319 | -0.32959 | 121.994 | -0.12505 | 0.022206 | 0.00392 | 0.056514 | -0.0038879 | -0.0022858 | -0.0080108 | -0.058289 | 0.01703 | 0.019318 | 0.0046527 | -0.031063 | -0.0013629 | 0.00010689 | -0.009155 | 0.19684 | -0.13733 | -0.064087 | 0.045776 | -0.10071 | -0.018311 | -0.18768 | 0.022888 | -0.40283 | -0.21973 | -0.13733 | -0.25177 | -0.17853 | 0.19226 | -121.7972 | -122.0581 | 0.37537 | 0.31128 | 0.22888 | 0.11902 | 0.036621 | -0.073242 | -121.9711 | -122.2137 | 0.19226 | 0.15106 | 0.07782 | 0.2243 | 0.15106 | 0.18311 | 0.073242 | 0.2655 | 0.18311 | 0.33417 | 0.42572 | 0.52643 | 0.35248 | -122.1313 | -122.3969 | 0.2655 | 0.10986 | 0.32043 | 0.14191
2908.7656 | 122.3419 | -0.33875 | 122.0078 | -0.10979 | 0.024129 | 0.0062698 | 0.054378 | 0.0029479 | -0.0039948 | -0.001175 | 0.030212 | 0.014039 | 0.019531 | 0.0082843 | -0.029568 | -0.0015765 | 0.00096129 | 0 | 0.16937 | -0.13733 | -0.045776 | 0.064087 | -0.068665 | 0.022888 | -0.20599 | 0.032043 | -0.38452 | -0.2655 | -0.13733 | -0.25177 | -0.20599 | 0.20142 | -121.8384 | -122.0535 | 0.40283 | 0.36163 | 0.27008 | 0.16022 | 0.068664 | -0.045776 | -121.9757 | -122.2733 | 0.20142 | 0.13275 | 0.086975 | 0.17853 | 0.13275 | 0.20142 | 0.091553 | 0.24719 | 0.11902 | 0.3067 | 0.41656 | 0.50812 | 0.37079 | -122.1451 | -122.3923 | 0.29297 | 0.073242 | 0.33875 | 0.13275
2909.7656 | 122.3465 | -0.36163 | 122.0123 | -0.17082 | 0.023061 | 0.004988 | 0.054805 | 0.0031617 | -0.0039948 | -0.0033112 | -0.021667 | 0.016816 | 0.0206 | 0.0070027 | -0.03149 | 0.0012005 | 0.0013885 | -0.050354 | 0.19684 | -0.16479 | -0.10986 | -0.009155 | -0.12817 | -0.041199 | -0.25177 | 0.018311 | -0.42114 | -0.25177 | -0.14191 | -0.23804 | -0.20142 | 0.19684 | -121.8155 | -122.1222 | 0.35248 | 0.32043 | 0.23346 | 0.1236 | 0.036621 | -0.05951 | -121.994 | -122.2641 | 0.21973 | 0.16022 | 0.1236 | 0.21973 | 0.18311 | 0.15564 | 0.054932 | 0.27924 | 0.16937 | 0.36163 | 0.43945 | 0.55847 | 0.37994 | -122.1771 | -122.4335 | 0.25177 | 0.10986 | 0.31128 | 0.10986
2910.7656 | 122.3465 | -0.35248 | 122.0352 | -0.14793 | 0.023061 | 0.004988 | 0.055873 | 0.0014527 | -0.004422 | -0.0043792 | -0.0064086 | 0.015321 | 0.018677 | 0.0023029 | -0.031277 | -8.1274e-05 | 0.0037385 | -0.036621 | 0.18768 | -0.16937 | -0.1236 | -0.009155 | -0.11444 | -0.036621 | -0.2655 | 0.013733 | -0.42114 | -0.2655 | -0.14648 | -0.25635 | -0.20599 | 0.18311 | -121.8475 | -122.1588 | 0.34332 | 0.31586 | 0.23804 | 0.13275 | 0.054932 | -0.068665 | -122.0215 | -122.3007 | 0.20599 | 0.14648 | 0.09613 | 0.21515 | 0.16479 | 0.16022 | 0.045777 | 0.27466 | 0.15564 | 0.35706 | 0.43488 | 0.54016 | 0.36621 | -122.2046 | -122.4564 | 0.22888 | 0.086975 | 0.31586 | 0.086975
2911.7656 | 122.3602 | -0.36163 | 122.0535 | -0.17082 | 0.026478 | 0.0043472 | 0.057368 | 0.0010253 | -0.0022858 | -0.0020294 | -0.018616 | 0.015107 | 0.019531 | 0.0040119 | -0.029995 | 0.00013253 | 0.00096129 | -0.032043 | 0.17853 | -0.16479 | -0.1236 | -0.009155 | -0.10986 | -0.022888 | -0.23804 | 0.027466 | -0.42114 | -0.27466 | -0.15106 | -0.27924 | -0.21515 | 0.19684 | -121.875 | -122.1771 | 0.35248 | 0.33874 | 0.25177 | 0.14191 | 0.054932 | -0.05951 | -122.0261 | -122.3282 | 0.21057 | 0.14648 | 0.082397 | 0.20599 | 0.14191 | 0.15564 | 0.041199 | 0.27008 | 0.14648 | 0.34332 | 0.44861 | 0.54016 | 0.3891 | -122.2183 | -122.4747 | 0.23804 | 0.086975 | 0.32959 | 0.1236
2912.7656 | 122.3511 | -0.31128 | 122.0535 | -0.15556 | 0.022633 | 0.0052018 | 0.055019 | 0.0035889 | -0.0014312 | -0.0013886 | -0.00030524 | 0.015535 | 0.020813 | -0.0017559 | -0.030849 | -0.0047809 | 0.0039521 | -0.045776 | 0.19226 | -0.14648 | -0.10986 | 0.013733 | -0.11902 | -0.018311 | -0.23804 | 0.036621 | -0.41199 | -0.16479 | -0.068665 | -0.40741 | -0.28839 | 0.16479 | -121.8613 | -122.1634 | 0.32501 | 0.29297 | 0.19226 | 0.12817 | 0.027465 | -0.10071 | -122.0169 | -122.2183 | 0.24261 | 0.022888 | -0.096131 | 0.1236 | 0.004577 | 0.16022 | 0.036621 | 0.34332 | 0.24719 | 0.33874 | 0.44861 | 0.50354 | 0.3479 | -122.2 | -122.4655 | 0.20142 | 0.14648 | 0.2655 | 0.073242
2913.7656 | 122.3602 | -0.33875 | 122.0993 | -0.13267 | 0.023061 | 0.0060562 | 0.052669 | -4.2682e-05 | -0.0033538 | -0.00737 | 0.033264 | 0.01468 | 0.021027 | 0.0046527 | -0.029568 | -0.0017901 | 0.0052337 | -0.036621 | 0.17853 | -0.14191 | -0.10071 | 0.013733 | -0.11902 | -0.013733 | -0.24261 | 0.054932 | -0.39825 | -0.28381 | -0.15106 | -0.27924 | -0.1236 | 0.19684 | -121.9208 | -122.2 | 0.35248 | 0.32501 | 0.21973 | 0.12817 | 0.022888 | -0.059509 | -122.0444 | -122.3831 | 0.18768 | 0.21515 | 0.059509 | 0.27466 | 0.11902 | 0.15564 | 0.041199 | 0.24719 | 0.11444 | 0.32044 | 0.45319 | 0.51727 | 0.39368 | -122.2412 | -122.4976 | 0.23804 | 0.054932 | 0.30212 | 0.09613
2914.7656 | 122.3419 | -0.33417 | 122.0215 | -0.048752 | 0.023274 | 0.0062698 | 0.05395 | -0.0036743 | -0.0029266 | -0.004593 | 0.0057984 | 0.016176 | 0.019959 | -0.0023969 | -0.029781 | -0.0020039 | 0.0030975 | -0.14191 | 0.21973 | -0.10529 | -0.11444 | -0.004578 | -0.1236 | -0.018311 | -0.24719 | 0.027466 | -0.41199 | -0.27008 | -0.14191 | -0.2655 | -0.21057 | 0.22888 | -121.8018 | -122.1359 | 0.32959 | 0.31586 | 0.21057 | 0.086975 | -0.01831 | -0.07782 | -121.994 | -122.2916 | 0.19226 | 0.1236 | 0.068664 | 0.20142 | 0.14648 | 0.10071 | -0.009155 | 0.27008 | 0.14191 | 0.32501 | 0.43945 | 0.55389 | 0.36163 | -122.1268 | -122.4335 | 0.21973 | 0.064086 | 0.19226 | 0.086975
2915.7656 | 122.3145 | -0.36621 | 122.0352 | -0.07164 | 0.022847 | 0.0054154 | 0.052669 | 0.00017092 | -0.0007904 | -0.0020294 | -0.00030524 | 0.01703 | 0.020172 | 0.0020893 | -0.028713 | -0.00072207 | 0.0043793 | -0.064087 | 0.18768 | -0.16479 | -0.14648 | 0.032043 | -0.086975 | -0.054932 | -0.24261 | 0.050354 | -0.37079 | -0.2655 | -0.15564 | -0.25177 | -0.21515 | 0.20142 | -121.8475 | -122.1817 | 0.39825 | 0.31128 | 0.27924 | 0.10986 | 0.07782 | -0.004578 | -121.9849 | -122.3007 | 0.21057 | 0.15106 | 0.11444 | 0.15564 | 0.11902 | 0.19684 | 0.018311 | 0.21515 | 0.10529 | 0.35248 | 0.42114 | 0.55389 | 0.41657 | -122.2 | -122.406 | 0.21973 | 0.10071 | 0.30212 | 0.1236
2916.7656 | 122.3694 | -0.36163 | 122.0169 | -0.16319 | 0.023915 | 0.0060562 | 0.055232 | 0.00059812 | -0.0054902 | -0.0035248 | -0.018616 | 0.016603 | 0.017822 | 0.0059345 | -0.030209 | -8.1274e-05 | 0.0013885 | -0.054932 | 0.16022 | -0.16022 | -0.1236 | -0.009155 | -0.11444 | -0.027466 | -0.25635 | 0.013733 | -0.40283 | -0.27008 | -0.15564 | -0.27924 | -0.21515 | 0.20142 | -121.8567 | -122.1405 | 0.35248 | 0.33417 | 0.24719 | 0.13275 | 0.045776 | -0.041199 | -122.0032 | -122.287 | 0.20599 | 0.14648 | 0.082397 | 0.18768 | 0.1236 | 0.15106 | 0.036621 | 0.24719 | 0.13275 | 0.32043 | 0.41657 | 0.52185 | 0.37537 | -122.1771 | -122.4197 | 0.23804 | 0.091552 | 0.3067 | 0.10528
2917.7656 | 122.3694 | -0.35248 | 122.0398 | -0.14793 | 0.023488 | 0.0062698 | 0.055446 | -0.0019653 | -0.002713 | -0.0052338 | -0.021667 | 0.015107 | 0.017609 | 0.0046527 | -0.030636 | -0.0013629 | 0.0045929 | -0.054932 | 0.19226 | -0.16022 | -0.13275 | -0.004578 | -0.1236 | -0.036621 | -0.24261 | 0.036621 | -0.39368 | -0.26093 | -0.15564 | -0.25177 | -0.21057 | 0.19226 | -121.8475 | -122.1725 | 0.3479 | 0.31586 | 0.22888 | 0.1236 | 0.036621 | -0.041199 | -122.0032 | -122.3007 | 0.19684 | 0.14191 | 0.10071 | 0.18311 | 0.14191 | 0.15564 | 0.027466 | 0.23804 | 0.13275 | 0.35248 | 0.4303 | 0.54474 | 0.3891 | -122.2 | -122.4335 | 0.21973 | 0.091553 | 0.29755 | 0.10986
2918.7656 | 122.3648 | -0.3479 | 122.0444 | -0.1403 | 0.022847 | 0.0043472 | 0.057155 | 0.0033753 | -0.0054902 | -0.0018158 | -0.018616 | 0.016603 | 0.0206 | 0.00059386 | -0.030209 | -0.0015765 | 0.0016021 | -0.041199 | 0.21973 | -0.11902 | -0.11444 | -0.009155 | -0.11902 | -0.041199 | -0.24719 | 0.009155 | -0.40283 | -0.27466 | -0.16022 | -0.27008 | -0.21515 | 0.22888 | -121.8246 | -122.1588 | 0.33874 | 0.3067 | 0.22888 | 0.07782 | 0 | -0.054932 | -122.0352 | -122.319 | 0.18768 | 0.13275 | 0.077819 | 0.18768 | 0.13275 | 0.10986 | 0.004578 | 0.24262 | 0.12817 | 0.33875 | 0.41199 | 0.56763 | 0.35706 | -122.1634 | -122.4472 | 0.23346 | 0.073242 | 0.3067 | 0.10071
2919.7656 | 122.3419 | -0.36163 | 122.0535 | -0.17082 | 0.023488 | 0.005629 | 0.056514 | -0.00089728 | -0.0033538 | -0.0041656 | 0.021057 | 0.015321 | 0.019318 | 0.00038026 | -0.028713 | -0.0015765 | 0.0039521 | -0.013733 | 0.18768 | -0.13275 | -0.073242 | 0.050354 | -0.073242 | 0 | -0.21973 | 0.032043 | -0.39825 | -0.27008 | -0.15564 | -0.25635 | -0.21973 | 0.22888 | -121.8658 | -122.1268 | 0.41199 | 0.36163 | 0.28839 | 0.13275 | 0.059509 | -0.036621 | -122.0215 | -122.3236 | 0.20599 | 0.14191 | 0.10528 | 0.17853 | 0.14191 | 0.18311 | 0.059509 | 0.24261 | 0.12817 | 0.32043 | 0.4303 | 0.54932 | 0.39368 | -122.1863 | -122.4518 | 0.28839 | 0.091552 | 0.3479 | 0.14191
2920.7656 | 122.3328 | -0.32501 | 122.0306 | -0.10216 | 0.024342 | 0.0062698 | 0.054378 | 0.0029479 | -0.0035674 | -0.001175 | -0.027771 | 0.013612 | 0.020386 | 0.0050801 | -0.029568 | -0.0015765 | -0.00010671 | -0.064087 | 0.18768 | -0.16937 | -0.059509 | 0.25177 | -0.036621 | -0.15564 | -0.20599 | 0.073242 | -0.37537 | -0.27924 | -0.16022 | -0.2655 | -0.21515 | 0.15564 | -121.843 | -122.0901 | 0.57678 | 0.16937 | 0.28839 | 0.013733 | 0.13275 | -0.050354 | -121.9574 | -122.3099 | 0.1648 | 0.10986 | 0.059509 | 0.16022 | 0.10986 | 0.42114 | 0.10986 | 0.21515 | 0.09613 | 0.35706 | 0.44861 | 0.5127 | 0.39825 | -122.2 | -122.406 | 0.2655 | 0.045776 | 0.26093 | 0.11902
2921.7656 | 122.3511 | -0.33875 | 122.0581 | -0.15556 | 0.024129 | 0.005629 | 0.054591 | -0.00068368 | -0.0024994 | -0.0052338 | 0.0088502 | 0.014039 | 0.019104 | 0.0044391 | -0.028927 | 0.0014141 | -0.00032051 | -0.050354 | 0.19684 | -0.15106 | -0.11444 | 0.004578 | -0.11902 | -0.032043 | -0.23346 | 0.041199 | -0.42572 | -0.3067 | -0.086975 | -0.25177 | -0.21973 | 0.18768 | -121.8613 | -122.1725 | 0.34332 | 0.3067 | 0.21973 | 0.11902 | 0.032043 | -0.086975 | -122.0169 | -122.3648 | 0.25177 | 0.11902 | 0.086975 | 0.20599 | 0.17395 | 0.15564 | 0.036621 | 0.33874 | 0.11902 | 0.3479 | 0.46692 | 0.53558 | 0.37994 | -122.2092 | -122.4838 | 0.2243 | 0.032043 | 0.28839 | 0.10529
2922.7656 | 122.3648 | -0.35248 | 122.0718 | -0.16319 | 0.02477 | 0.0045608 | 0.0563 | 0.00059812 | -0.002713 | -0.0037384 | -0.0033568 | 0.017457 | 0.0206 | -0.0011151 | -0.030636 | 0.00055973 | 0.0013885 | -0.036621 | 0.23804 | -0.1236 | -0.11444 | 0.004578 | -0.12817 | -0.036621 | -0.24719 | 0.036621 | -0.42114 | -0.27008 | -0.17395 | -0.27008 | -0.2243 | 0.22888 | -121.8338 | -122.1863 | 0.35706 | 0.31586 | 0.2243 | 0.086975 | -0.004578 | -0.068665 | -122.0352 | -122.3419 | 0.17853 | 0.12817 | 0.082397 | 0.19684 | 0.15106 | 0.12817 | 0.009155 | 0.24719 | 0.15106 | 0.36163 | 0.45776 | 0.59052 | 0.3891 | -122.1954 | -122.493 | 0.23804 | 0.082397 | 0.31586 | 0.10529
2923.8281 | 122.3877 | -0.32044 | 122.0444 | -0.16319 | 0.023915 | 0.0037064 | 0.055019 | -0.00025628 | -0.0042084 | -0.00010676 | -0.021667 | 0.015748 | 0.016541 | 0.0020893 | -0.030636 | 0.00034613 | -0.0013885 | -0.054932 | 0.19226 | -0.1831 | -0.10529 | -0.018311 | -0.10986 | -0.041199 | -0.24261 | -0.004578 | -0.41657 | -0.25635 | -0.14191 | -0.25177 | -0.1831 | 0.13733 | -121.8521 | -122.1497 | 0.30212 | 0.27924 | 0.21057 | 0.14191 | 0.073242 | -0.09613 | -122.049 | -122.3007 | 0.17853 | 0.13733 | 0.068665 | 0.23346 | 0.1648 | 0.16479 | 0.077819 | 0.27466 | 0.16022 | 0.37537 | 0.41199 | 0.5127 | 0.31586 | -122.2275 | -122.4609 | 0.21515 | 0.064087 | 0.2655 | 0.07782
2924.7656 | 122.3694 | -0.32501 | 122.0764 | -0.094528 | 0.023701 | 0.0047744 | 0.055232 | -0.0019653 | -0.0031402 | -0.0026704 | 0.0088502 | 0.015962 | 0.01825 | 0.0031573 | -0.028286 | -0.0020039 | 0.0073701 | -0.068665 | 0.18768 | -0.15564 | -0.11444 | -0.004578 | -0.11902 | -0.032043 | -0.25635 | 0.027466 | -0.39368 | -0.25177 | -0.13275 | -0.28839 | -0.2243 | 0.16937 | -121.8887 | -122.1909 | 0.32043 | 0.29297 | 0.20599 | 0.1236 | 0.036621 | -0.068665 | -122.0489 | -122.3282 | 0.19226 | 0.10071 | 0.036621 | 0.16937 | 0.10529 | 0.15106 | 0.041199 | 0.26093 | 0.14191 | 0.34332 | 0.42114 | 0.5127 | 0.35248 | -122.2321 | -122.4701 | 0.21057 | 0.073242 | 0.25635 | 0.068664
2925.7656 | 122.2733 | -0.33875 | 122.1313 | -0.13267 | 0.023274 | 0.006697 | 0.053523 | -0.00068368 | -0.0046356 | -0.00053396 | 0.011902 | 0.015321 | 0.02124 | 0.00059386 | -0.029568 | -0.0017901 | 0.00053409 | -0.027466 | 0.18768 | -0.14648 | -0.10529 | 0.032043 | -0.13275 | -0.041199 | -0.23804 | 0.013733 | -0.41199 | -0.27924 | -0.17395 | -0.25635 | -0.21057 | 0.19226 | -121.9437 | -122.2366 | 0.37079 | 0.29755 | 0.20599 | 0.10529 | 0.013733 | -0.073242 | -122.1176 | -122.4106 | 0.1648 | 0.12817 | 0.082397 | 0.20142 | 0.15564 | 0.17853 | 0.041198 | 0.23804 | 0.13275 | 0.33417 | 0.42572 | 0.52643 | 0.35248 | -122.2778 | -122.5433 | 0.23346 | 0.059509 | 0.31128 | 0.10071
2926.7656 | 122.3694 | -0.34332 | 122.0718 | -0.11742 | 0.026051 | 0.004988 | 0.053523 | -0.0019653 | -0.0020722 | -0.0018158 | 0.011902 | 0.015535 | 0.019745 | 0.0018757 | -0.030849 | -0.0011493 | 0.00096129 | -0.004578 | 0.16022 | -0.13733 | -0.068665 | 0.050354 | -0.073242 | 0 | -0.21057 | 0.018311 | -0.40741 | -0.2655 | -0.13733 | -0.25635 | -0.19226 | 0.20599 | -121.9116 | -122.1405 | 0.39368 | 0.34332 | 0.27008 | 0.13733 | 0.064087 | -0.064087 | -122.0535 | -122.3373 | 0.20599 | 0.15106 | 0.086975 | 0.21515 | 0.15106 | 0.18768 | 0.068664 | 0.27008 | 0.14191 | 0.29755 | 0.42572 | 0.50354 | 0.36163 | -122.2092 | -122.4792 | 0.27466 | 0.07782 | 0.33874 | 0.13275
2927.7656 | 122.4564 | -0.29755 | 122.0306 | -0.19371 | 0.023274 | 0.0086196 | 0.055446 | -0.0015381 | -0.0007904 | -0.003952 | 0.036316 | 0.014253 | 0.020813 | 0.0067889 | -0.031277 | 0.00013253 | 0.00010689 | 0.004578 | 0.15106 | -0.1236 | 0 | 0.15106 | 0 | 0.073242 | -0.086975 | -0.009155 | -0.37537 | -0.16022 | -0.041199 | -0.13275 | -0.10986 | 0.17395 | -121.8796 | -122.0306 | 0.44861 | 0.37079 | 0.29755 | 0.19684 | 0.1236 | -0.07782 | -122.0398 | -122.1909 | 0.25635 | 0.18768 | 0.16479 | 0.2655 | 0.24261 | 0.27466 | 0.1236 | 0.33417 | 0.21515 | 0.27466 | 0.36621 | 0.44861 | 0.28839 | -122.1542 | -122.406 | 0.29755 | 0.13733 | 0.30212 | 0.21057
2928.7656 | 122.438 | -0.30212 | 122.049 | -0.19371 | 0.023061 | 0.0045608 | 0.054805 | -0.0032471 | -0.0050628 | -0.0020294 | 0.021057 | 0.015107 | 0.019318 | 0.00059386 | -0.029995 | -0.00029487 | 0.0052337 | 0.022888 | 0.13275 | -0.10986 | -0.032043 | 0.1236 | -0.018311 | 0.054932 | -0.1236 | 0.013733 | -0.36621 | -0.21057 | -0.091553 | -0.1831 | -0.14191 | 0.19226 | -121.9162 | -122.081 | 0.42572 | 0.35706 | 0.28381 | 0.16479 | 0.091552 | -0.064087 | -122.0352 | -122.2595 | 0.21057 | 0.16022 | 0.11902 | 0.2243 | 0.18311 | 0.23346 | 0.07782 | 0.27466 | 0.15564 | 0.24261 | 0.37994 | 0.43488 | 0.31586 | -122.1588 | -122.4152 | 0.27008 | 0.091553 | 0.32501 | 0.17853
2929.7656 | 122.4335 | -0.31586 | 122.0764 | -0.16319 | 0.023488 | 0.0092606 | 0.054591 | 0.00017092 | 6.4004e-05 | -0.0048066 | 0.042419 | 0.015107 | 0.01825 | 0.00016666 | -0.033199 | -8.1274e-05 | 0.00010689 | 0.027466 | 0.15564 | -0.12817 | 0 | 0.1236 | -0.004578 | 0.07782 | -0.11444 | 0.009155 | -0.36621 | -0.18768 | -0.068665 | -0.15106 | -0.11444 | 0.18768 | -121.9208 | -122.0764 | 0.43945 | 0.39368 | 0.31128 | 0.20599 | 0.1236 | -0.050354 | -122.0673 | -122.2641 | 0.24719 | 0.20142 | 0.16479 | 0.25177 | 0.21515 | 0.25177 | 0.12817 | 0.29755 | 0.17853 | 0.28381 | 0.37537 | 0.4715 | 0.32501 | -122.2046 | -122.4426 | 0.31586 | 0.12817 | 0.34332 | 0.20142
2930.7656 | 122.3831 | -0.33417 | 122.113 | -0.16319 | 0.024983 | 0.0034928 | 0.054378 | 0.0010253 | -0.0048492 | -0.00053396 | 0.018005 | 0.013398 | 0.019318 | -0.0011151 | -0.029354 | -0.00072207 | 0.0058747 | 0.022888 | 0.15564 | -0.11444 | -0.036621 | 0.082397 | -0.045776 | 0.041199 | -0.17395 | 0.009155 | -0.40283 | -0.24719 | -0.13275 | -0.24261 | -0.1831 | 0.21973 | -121.9574 | -122.1497 | 0.41656 | 0.37537 | 0.28839 | 0.15564 | 0.068665 | -0.068665 | -122.1039 | -122.3602 | 0.20142 | 0.15106 | 0.091552 | 0.21973 | 0.16022 | 0.19684 | 0.07782 | 0.27008 | 0.15564 | 0.27008 | 0.41199 | 0.48981 | 0.34332 | -122.2275 | -122.5159 | 0.29755 | 0.086975 | 0.35706 | 0.16022
2931.7656 | 122.4289 | -0.32044 | 122.113 | -0.18608 | 0.024342 | 0.0041336 | 0.053737 | -0.00025628 | -0.0057038 | -0.0035248 | 0.021057 | 0.014467 | 0.017822 | 0.00080746 | -0.029781 | -0.00050847 | 0.0043793 | 0.018311 | 0.13275 | -0.13733 | 0 | 0.11902 | -0.036621 | 0.045776 | -0.13733 | -0.004578 | -0.37079 | -0.20142 | -0.091553 | -0.18768 | -0.13733 | 0.18311 | -121.9803 | -122.113 | 0.43945 | 0.36621 | 0.28381 | 0.18311 | 0.10071 | -0.050354 | -122.1176 | -122.3145 | 0.22888 | 0.18311 | 0.13275 | 0.23346 | 0.18311 | 0.25635 | 0.13733 | 0.27924 | 0.16937 | 0.27008 | 0.36621 | 0.45319 | 0.31586 | -122.2504 | -122.4838 | 0.32044 | 0.11902 | 0.33875 | 0.18311
2932.7656 | 122.4564 | -0.32044 | 122.0764 | -0.18608 | 0.024556 | 0.0052018 | 0.05395 | -0.0011109 | -0.002713 | -0.00074776 | 0.021057 | 0.013826 | 0.019318 | 0.0046527 | -0.03149 | -0.00093567 | 0.00074769 | 0.022888 | 0.12817 | -0.10529 | 0.004578 | 0.11902 | -0.013733 | 0.059509 | -0.10986 | -0.013733 | -0.36621 | -0.1831 | -0.059509 | -0.15564 | -0.12817 | 0.21515 | -121.9482 | -122.0718 | 0.43945 | 0.37994 | 0.3067 | 0.16479 | 0.091553 | -0.045776 | -122.0901 | -122.2595 | 0.26093 | 0.19226 | 0.1648 | 0.23804 | 0.21057 | 0.22431 | 0.10986 | 0.3067 | 0.18311 | 0.23346 | 0.35248 | 0.44861 | 0.3067 | -122.1817 | -122.4426 | 0.32501 | 0.13733 | 0.34332 | 0.21057
2933.7656 | 122.5479 | -0.31586 | 122.0444 | -0.16319 | 0.021565 | 0.0058426 | 0.055019 | -0.00068368 | -0.0048492 | -0.0033112 | 0.036316 | 0.014253 | 0.017395 | 0.011275 | -0.029781 | -0.0058491 | 0.0099335 | 0.013733 | 0.14191 | -0.09613 | 0.032043 | 0.16937 | 0.018311 | 0.10529 | -0.045776 | -0.022888 | -0.35706 | -0.018311 | -0.25177 | -0.17853 | -0.091553 | 0.21973 | -121.9025 | -122.0123 | 0.48523 | 0.42114 | 0.33417 | 0.20142 | 0.11444 | -0.041199 | -122.0673 | -122.0627 | 0.064087 | 0.2243 | 0.13733 | 0.2655 | 0.17853 | 0.2655 | 0.12817 | 0.10529 | 0.33874 | 0.23804 | 0.33417 | 0.45776 | 0.29297 | -122.1405 | -122.4014 | 0.3479 | 0.29755 | 0.32959 | 0.27008
2934.7656 | 122.5296 | -0.31128 | 122.0673 | -0.20897 | 0.023061 | 0.0071244 | 0.056087 | 0.0014527 | -0.004422 | -0.0035248 | 0.042419 | 0.01468 | 0.017609 | -0.00047414 | -0.029781 | -0.0032855 | 0.0018159 | 0.009155 | 0.15106 | -0.10986 | 0.032043 | 0.16937 | 0.004578 | 0.082397 | -0.050354 | -0.013733 | -0.36621 | -0.11444 | -0.009155 | -0.09613 | -0.086975 | 0.20142 | -121.9162 | -122.0352 | 0.48065 | 0.39368 | 0.31586 | 0.19226 | 0.11444 | -0.054932 | -122.081 | -122.1817 | 0.30212 | 0.2243 | 0.21515 | 0.27924 | 0.27008 | 0.27924 | 0.14191 | 0.35706 | 0.25177 | 0.26093 | 0.35248 | 0.46234 | 0.29755 | -122.1771 | -122.4335 | 0.34332 | 0.19684 | 0.32043 | 0.26092
2935.7656 | 122.5021 | -0.29297 | 122.0581 | -0.20897 | 0.02242 | 0.0054154 | 0.054591 | -0.0013245 | -0.0029266 | -0.0024566 | -0.073547 | 0.014253 | 0.019318 | 0.0055073 | -0.030849 | -0.0011493 | -0.0030975 | 0.045776 | 0.14648 | -0.11444 | -0.11902 | 0.27466 | 0.073242 | -0.13275 | -0.004578 | -0.027466 | -0.37537 | -0.15106 | -0.009155 | -0.1236 | -0.10071 | 0.17853 | -121.9116 | -122.1771 | 0.56763 | 0.16022 | 0.36621 | -0.01831 | 0.18768 | -0.082397 | -122.0856 | -122.2092 | 0.28381 | 0.19226 | 0.16937 | 0.27466 | 0.25177 | 0.3891 | -0.004578 | 0.36621 | 0.2243 | 0.26093 | 0.3479 | 0.43945 | 0.2655 | -122.1725 | -122.4335 | 0.17395 | 0.14191 | 0.33874 | 0.28839
2936.8281 | 122.4197 | -0.33417 | 122.1313 | -0.10979 | 0.02242 | 0.0054154 | 0.057582 | 0.0020935 | -0.0016448 | -0.001175 | -0.097961 | 0.013398 | 0.017822 | 0.0050801 | -0.032986 | 0.00034613 | -0.00010671 | -0.009155 | 0.16937 | -0.16479 | -0.045776 | 0.059509 | -0.10529 | -0.018311 | -0.1831 | 0.009155 | -0.39825 | -0.20142 | -0.11902 | -0.22888 | -0.16479 | 0.16937 | -121.962 | -122.1771 | 0.39368 | 0.31586 | 0.22888 | 0.14648 | 0.059509 | -0.064087 | -122.1222 | -122.3328 | 0.21515 | 0.16937 | 0.10528 | 0.23346 | 0.16937 | 0.2243 | 0.11902 | 0.27924 | 0.19684 | 0.33417 | 0.40741 | 0.50354 | 0.34332 | -122.2961 | -122.5296 | 0.28839 | 0.13275 | 0.32501 | 0.15106
2937.7656 | 122.525 | -0.27924 | 122.0581 | -0.10216 | 0.026692 | 0.0058426 | 0.053096 | -0.0015381 | -0.002713 | -0.0058746 | -0.00030524 | 0.015962 | 0.018891 | 0.0012347 | -0.029354 | -0.0022175 | 0.0020295 | -0.082397 | 0.11902 | -0.14648 | 0.022888 | 0.13275 | 0.009155 | 0.09613 | -0.09613 | -0.009155 | -0.36621 | -0.14648 | -0.022888 | -0.13275 | -0.10071 | 0.13275 | -121.9391 | -122.0352 | 0.41199 | 0.37537 | 0.28839 | 0.24261 | 0.15564 | -0.086975 | -122.0673 | -122.2046 | 0.25635 | 0.17853 | 0.14648 | 0.2655 | 0.23346 | 0.27924 | 0.16937 | 0.34332 | 0.21973 | 0.2655 | 0.35706 | 0.39825 | 0.27008 | -122.2046 | -122.4243 | 0.30212 | 0.13275 | 0.19684 | 0.18311
2938.7656 | 122.374 | -0.32044 | 122.0856 | -0.15556 | 0.023274 | 0.0071244 | 0.055446 | -0.0023925 | -0.0003632 | -0.0048066 | -0.030823 | 0.015962 | 0.018677 | 0.0035847 | -0.03149 | -0.0015765 | 0.00010689 | -0.009155 | 0.17853 | -0.13275 | -0.073242 | 0.032043 | -0.09613 | -0.004578 | -0.22888 | 0.032043 | -0.39368 | -0.2655 | -0.14648 | -0.25177 | -0.21515 | 0.18768 | -121.907 | -122.1588 | 0.35248 | 0.31586 | 0.22431 | 0.12817 | 0.036621 | -0.073242 | -122.0535 | -122.3511 | 0.17395 | 0.10529 | 0.068665 | 0.17853 | 0.14191 | 0.16479 | 0.059509 | 0.24719 | 0.12817 | 0.31128 | 0.42572 | 0.49896 | 0.35248 | -122.2183 | -122.4792 | 0.24719 | 0.054932 | 0.31128 | 0.091553
2939.8281 | 122.4564 | -0.3067 | 122.0535 | -0.18608 | 0.023701 | 0.0047744 | 0.054164 | 0.00017092 | -0.0007904 | -0.0052338 | 0.036316 | 0.013612 | 0.018891 | 0.0010211 | -0.032131 | -0.0022175 | -0.00096131 | 0.027466 | 0.15106 | -0.12817 | -0.009155 | 0.12817 | -0.013733 | 0.073242 | -0.1236 | -0.004578 | -0.36621 | -0.17395 | -0.068665 | -0.15564 | -0.13275 | 0.17853 | -121.9025 | -122.0627 | 0.43488 | 0.37994 | 0.29297 | 0.20142 | 0.11444 | -0.059509 | -122.0581 | -122.2275 | 0.23804 | 0.17395 | 0.15106 | 0.23346 | 0.21057 | 0.25635 | 0.11902 | 0.29755 | 0.19226 | 0.27924 | 0.36163 | 0.45776 | 0.30212 | -122.1817 | -122.4197 | 0.29755 | 0.13275 | 0.33417 | 0.18311
2940.7656 | 122.4701 | -0.31586 | 122.1039 | -0.16319 | 0.02477 | 0.0088332 | 0.052882 | -0.0032471 | -0.002713 | 0.00010684 | 0.027161 | 0.015535 | 0.01825 | -0.0023969 | -0.03149 | -0.00029487 | 0.0052337 | -0.19684 | 0.14191 | -0.15106 | -0.09613 | 0.045776 | -0.091553 | 0 | -0.19684 | -0.027466 | -0.39368 | -0.20599 | -0.091553 | -0.17853 | -0.1236 | 0.16479 | -121.962 | -122.2 | 0.36163 | 0.31586 | 0.2243 | 0.15106 | 0.059509 | -0.07782 | -122.1313 | -122.3099 | 0.2243 | 0.19226 | 0.13733 | 0.27008 | 0.21515 | 0.19684 | 0.054932 | 0.30212 | 0.18768 | 0.29297 | 0.36621 | 0.45776 | 0.28839 | -122.2549 | -122.4976 | 0.21973 | 0.10986 | 0.11902 | 0.11902
2941.7656 | 122.4884 | -0.28839 | 122.0673 | -0.15556 | 0.023915 | 0.0058426 | 0.05331 | -0.0011109 | -0.0022858 | -0.0033112 | 0.011902 | 0.014039 | 0.021668 | 0.0014485 | -0.030636 | -0.0037129 | 0.00074769 | -0.022888 | 0.15106 | -0.12817 | -0.036621 | 0.07782 | -0.050354 | 0.045776 | -0.14191 | 0.004578 | -0.37537 | -0.16022 | -0.036621 | -0.14191 | -0.10071 | 0.16022 | -121.9162 | -122.1039 | 0.36621 | 0.33417 | 0.23804 | 0.17395 | 0.07782 | -0.086975 | -122.0627 | -122.2275 | 0.25177 | 0.18768 | 0.14648 | 0.27466 | 0.23346 | 0.20599 | 0.091553 | 0.33874 | 0.21515 | 0.27924 | 0.37994 | 0.43945 | 0.29297 | -122.1954 | -122.4426 | 0.25177 | 0.12817 | 0.2655 | 0.14648
2942.7656 | 122.5113 | -0.29755 | 122.0581 | -0.14793 | 0.024983 | 0.0043472 | 0.055019 | -0.00089728 | -0.0016448 | -0.0088654 | 0.091248 | 0.018098 | 0.020172 | 0.0027301 | -0.029568 | -0.0011493 | 0.00096129 | 0.027466 | 0.14191 | -0.10986 | 0.059509 | 0.28381 | -0.37537 | -0.036621 | -0.13275 | -0.032043 | -0.38452 | -0.14191 | -0.018311 | -0.1236 | -0.086975 | 0.18768 | -121.9162 | -121.9986 | 0.58136 | 0.26092 | -0.07782 | 0.073242 | -0.2655 | -0.086975 | -122.0901 | -122.2 | 0.27923 | 0.21057 | 0.17395 | 0.29755 | 0.26093 | 0.39368 | 0.16937 | 0.36621 | 0.24261 | 0.25177 | 0.35248 | 0.43945 | 0.2655 | -122.168 | -122.4426 | 0.35705 | 0.15564 | 0.32501 | 0.16479
2943.7656 | 122.5067 | -0.30212 | 122.049 | -0.16319 | 0.022847 | 0.003279 | 0.054164 | -0.00089728 | -0.0007904 | -0.0018158 | 0.021057 | 0.015748 | 0.016754 | 0.00059386 | -0.031063 | -0.0026447 | -0.00032051 | 0.018311 | 0.14648 | -0.11444 | 0.036621 | 0.20599 | 0.032043 | 0.09613 | -0.009155 | -0.013733 | -0.3891 | -0.16022 | -0.009155 | -0.086975 | -0.091553 | 0.18768 | -121.9025 | -122.0123 | 0.50812 | 0.39825 | 0.33417 | 0.21057 | 0.14648 | -0.086975 | -122.0627 | -122.2092 | 0.29297 | 0.21057 | 0.21515 | 0.29755 | 0.30212 | 0.32044 | 0.15106 | 0.37994 | 0.22888 | 0.26093 | 0.37537 | 0.44861 | 0.28839 | -122.1634 | -122.438 | 0.33875 | 0.14191 | 0.32044 | 0.29297
2944.7656 | 122.5525 | -0.31586 | 122.0535 | -0.14793 | 0.025838 | 0.0047744 | 0.052455 | 0.00081172 | -0.0016448 | -0.0033112 | 0.014954 | 0.015321 | 0.017182 | 0.0029437 | -0.032131 | -0.0026447 | 0.0048065 | 0.022888 | 0.14191 | -0.082397 | 0.027466 | 0.18768 | 0.004578 | 0.10071 | -0.050354 | -0.009155 | -0.35248 | -0.059509 | -0.25177 | -0.12817 | -0.073242 | 0.23346 | -121.9116 | -122.0261 | 0.50354 | 0.41657 | 0.32044 | 0.18311 | 0.086975 | -0.036621 | -122.0627 | -122.113 | 0.064087 | 0.24261 | 0.18768 | 0.27924 | 0.2243 | 0.27008 | 0.10986 | 0.10071 | 0.29297 | 0.2243 | 0.34332 | 0.45776 | 0.3067 | -122.1359 | -122.406 | 0.34332 | 0.25635 | 0.33875 | 0.2655
2945.7656 | 122.4976 | -0.3067 | 122.0673 | -0.23186 | 0.024556 | 0.0047744 | 0.05395 | -0.0030335 | -0.0035674 | -0.003952 | 0.0027466 | 0.013612 | 0.019104 | 0.0050801 | -0.031063 | 0.00098693 | -0.0030975 | -0.013733 | 0.13275 | -0.13275 | 0.022888 | 0.13275 | 0.013733 | 0.068665 | -0.10529 | -0.022888 | -0.35248 | -0.16022 | -0.027466 | -0.12817 | -0.10529 | 0.17395 | -121.9345 | -122.0444 | 0.43945 | 0.37537 | 0.32043 | 0.20142 | 0.14648 | -0.045776 | -122.0901 | -122.2275 | 0.27924 | 0.20142 | 0.17853 | 0.24719 | 0.2243 | 0.2655 | 0.15564 | 0.32501 | 0.19226 | 0.2655 | 0.32959 | 0.43945 | 0.28381 | -122.2 | -122.4197 | 0.32959 | 0.14648 | 0.29297 | 0.20142
2946.7656 | 122.5479 | -0.30212 | 122.0673 | -0.20897 | 0.022847 | 0.0054154 | 0.053737 | -0.0028199 | -0.002713 | -0.006302 | -0.0033568 | 0.013612 | 0.018036 | -0.0032513 | -0.033199 | 0.0012005 | 0.0020295 | 0 | 0.15564 | -0.09613 | 0.027466 | 0.15564 | 0.004578 | 0.09613 | -0.068665 | 0 | -0.35248 | -0.12817 | 0 | -0.086975 | -0.073242 | 0.20599 | -121.9116 | -122.0398 | 0.45776 | 0.39825 | 0.3067 | 0.19226 | 0.10071 | -0.050354 | -122.0673 | -122.1954 | 0.30212 | 0.22888 | 0.21515 | 0.27924 | 0.2655 | 0.25177 | 0.1236 | 0.35248 | 0.2243 | 0.25177 | 0.35248 | 0.45776 | 0.30212 | -122.1634 | -122.4197 | 0.32959 | 0.17395 | 0.30212 | 0.23346
2947.8281 | 122.3877 | -0.31586 | 122.1359 | -0.12505 | 0.02242 | 0.0034928 | 0.054805 | -0.00089728 | -0.0031402 | -0.0026704 | -0.024719 | 0.014253 | 0.019745 | 0.0061481 | -0.029568 | 0.0022687 | 0.00053409 | -0.064087 | 0.1831 | -0.15564 | -0.10529 | 0.009155 | -0.10986 | -0.036621 | -0.25635 | 0.022888 | -0.39825 | -0.3067 | -0.091553 | -0.26093 | -0.21515 | 0.16022 | -121.9528 | -122.2412 | 0.32501 | 0.27924 | 0.20599 | 0.11902 | 0.045777 | -0.082397 | -122.113 | -122.4426 | 0.2243 | 0.10071 | 0.054932 | 0.1831 | 0.13733 | 0.16479 | 0.050354 | 0.3067 | 0.091552 | 0.33874 | 0.42114 | 0.49896 | 0.33875 | -122.2916 | -122.5342 | 0.21057 | 0.009155 | 0.25177 | 0.059509
2948.7656 | 122.4838 | -0.33875 | 122.0718 | -0.17082 | 0.023915 | 0.0045608 | 0.054164 | -0.0011109 | -0.004422 | -0.0041656 | -0.015564 | 0.010835 | 0.016968 | 0.0010211 | -0.03149 | -0.00029487 | -0.00010671 | -0.036621 | 0.15564 | -0.10986 | -0.054932 | 0.068665 | -0.082397 | 0.032043 | -0.26093 | -0.032043 | -0.45319 | -0.23804 | -0.10986 | -0.21973 | -0.15564 | 0.22888 | -121.9162 | -122.1268 | 0.40741 | 0.37079 | 0.25635 | 0.14191 | 0.027466 | -0.11444 | -122.1039 | -122.3099 | 0.22888 | 0.18311 | 0.11902 | 0.29755 | 0.23346 | 0.17853 | 0.054931 | 0.34332 | 0.21515 | 0.2655 | 0.42114 | 0.49439 | 0.3067 | -122.1817 | -122.525 | 0.28381 | 0.10071 | 0.30212 | 0.07782
2949.7656 | 122.406 | -0.34332 | 122.1039 | -0.11742 | 0.025197 | 0.00392 | 0.054805 | -0.0030335 | -0.0012176 | -0.0033112 | -0.033874 | 0.01468 | 0.017822 | 0.0040119 | -0.030209 | -0.0013629 | 0.00010689 | -0.009155 | 0.15564 | -0.10986 | -0.050354 | 0.064087 | -0.068665 | 0 | -0.20142 | 0.018311 | -0.38452 | -0.2655 | -0.15106 | -0.23346 | -0.21057 | 0.23346 | -121.9482 | -122.1542 | 0.40741 | 0.34332 | 0.27466 | 0.10986 | 0.041198 | -0.041198 | -122.0856 | -122.3694 | 0.19226 | 0.13275 | 0.10986 | 0.17395 | 0.15106 | 0.17395 | 0.059509 | 0.23346 | 0.11902 | 0.2655 | 0.40283 | 0.49896 | 0.36163 | -122.2137 | -122.4884 | 0.29297 | 0.07782 | 0.33417 | 0.14191
2950.7656 | 122.5113 | -0.32501 | 122.0718 | -0.18608 | 0.023488 | 0.0058426 | 0.054591 | -0.0019653 | -0.0050628 | -0.0048066 | 0.0027466 | 0.015107 | 0.019104 | 0.0035847 | -0.034481 | -0.00093567 | 0.0020295 | 0.018311 | 0.17395 | -0.09613 | 0.032043 | 0.17853 | 0.018311 | 0.10071 | -0.054932 | -0.013733 | -0.37079 | -0.13733 | -0.24261 | -0.068665 | -0.045776 | 0.22888 | -121.8979 | -122.0398 | 0.50354 | 0.42572 | 0.34332 | 0.19684 | 0.11444 | -0.045777 | -122.0856 | -122.2092 | 0.082397 | 0.27924 | 0.25635 | 0.32501 | 0.30212 | 0.27466 | 0.12817 | 0.12817 | 0.23346 | 0.27008 | 0.35706 | 0.49896 | 0.31128 | -122.168 | -122.4426 | 0.35706 | 0.18768 | 0.34332 | 0.27008
2951.7656 | 122.5983 | -0.3067 | 122.0581 | -0.18608 | 0.024342 | 0.0047744 | 0.055446 | -4.2682e-05 | -0.0022858 | -0.0035248 | 0.014954 | 0.01468 | 0.018891 | -0.0043195 | -0.031917 | -0.0015765 | -0.0011749 | 0.022888 | 0.15564 | -0.09613 | 0.032043 | 0.17395 | -0.004578 | 0.10071 | -0.07782 | -0.032043 | -0.36621 | -0.1236 | -0.004578 | -0.10529 | -0.10071 | 0.21057 | -121.9025 | -122.0261 | 0.48065 | 0.40741 | 0.30212 | 0.19684 | 0.091552 | -0.059509 | -122.0901 | -122.1817 | 0.30212 | 0.20599 | 0.20142 | 0.2655 | 0.26093 | 0.27008 | 0.12817 | 0.36163 | 0.24262 | 0.25177 | 0.33417 | 0.46234 | 0.27466 | -122.1542 | -122.4243 | 0.33874 | 0.18311 | 0.32959 | 0.22888
2952.7656 | 122.5433 | -0.28381 | 122.1039 | -0.16319 | 0.024983 | 0.0045608 | 0.05395 | 0.0040161 | -0.0022858 | -0.0037384 | 0.014954 | 0.014894 | 0.019745 | -0.00068794 | -0.03149 | -0.00093567 | 0.0037385 | 0.013733 | 0.15564 | -0.10986 | 0.022888 | 0.15106 | -0.004578 | 0.09613 | -0.068665 | -0.009155 | -0.36621 | -0.12817 | -0.004578 | -0.10529 | -0.10071 | 0.17395 | -121.9482 | -122.081 | 0.43488 | 0.37994 | 0.27923 | 0.20599 | 0.10529 | -0.082398 | -122.113 | -122.2321 | 0.27923 | 0.1831 | 0.17853 | 0.2655 | 0.26093 | 0.26093 | 0.13275 | 0.36163 | 0.23804 | 0.2655 | 0.35706 | 0.43945 | 0.27466 | -122.2137 | -122.4701 | 0.3067 | 0.15564 | 0.29755 | 0.21515
2953.7656 | 122.5388 | -0.29297 | 122.0901 | -0.18608 | 0.024129 | 0.0045608 | 0.054164 | -0.0019653 | -0.0014312 | -0.0016022 | 0.0057984 | 0.015962 | 0.018891 | 0.0061481 | -0.032772 | -0.0017901 | 0.0024567 | 0.013733 | 0.16022 | -0.10529 | 0.022888 | 0.16479 | 0 | 0.086975 | -0.068665 | -0.004578 | -0.37079 | -0.13275 | -0.013733 | -0.10529 | -0.07782 | 0.18768 | -121.9299 | -122.0673 | 0.45776 | 0.37994 | 0.29297 | 0.19226 | 0.10529 | -0.07782 | -122.0947 | -122.2229 | 0.27924 | 0.21515 | 0.18768 | 0.29297 | 0.2655 | 0.27008 | 0.12817 | 0.35706 | 0.23804 | 0.2655 | 0.36621 | 0.45319 | 0.28839 | -122.1954 | -122.4609 | 0.31586 | 0.16022 | 0.3067 | 0.2243
2954.7656 | 122.4976 | -0.29755 | 122.1039 | -0.17082 | 0.02477 | 0.0047744 | 0.05331 | -0.0019653 | -0.0022858 | -0.0033112 | -0.0094604 | 0.013185 | 0.022736 | 0.0012347 | -0.030422 | -0.0026447 | 0.00053409 | -0.027466 | 0.11444 | -0.14191 | -0.045776 | 0.073242 | -0.07782 | 0.027466 | -0.16022 | -0.013733 | -0.37537 | -0.17853 | -0.064087 | -0.15564 | -0.11902 | 0.15564 | -121.9894 | -122.1497 | 0.37079 | 0.32501 | 0.21973 | 0.16937 | 0.064087 | -0.07782 | -122.1176 | -122.2824 | 0.23346 | 0.17853 | 0.14191 | 0.25635 | 0.21973 | 0.21515 | 0.096131 | 0.31128 | 0.19684 | 0.25635 | 0.36163 | 0.41199 | 0.28381 | -122.2458 | -122.4792 | 0.25177 | 0.11902 | 0.27008 | 0.13733
2955.7656 | 122.5067 | -0.30212 | 122.0993 | -0.19371 | 0.021992 | 0.0062698 | 0.054378 | 0.0025207 | -0.0033538 | -0.005661 | -0.0033568 | 0.013612 | 0.019104 | 0.0031573 | -0.029995 | -0.0024311 | -0.00032051 | -0.073242 | 0.10529 | -0.16479 | -0.045776 | 0.068665 | -0.07782 | 0.013733 | -0.17395 | -0.018311 | -0.37537 | -0.18768 | -0.086975 | -0.16479 | -0.13733 | 0.13733 | -121.994 | -122.1451 | 0.37079 | 0.31586 | 0.2243 | 0.17853 | 0.086975 | -0.073242 | -122.1176 | -122.287 | 0.21515 | 0.16479 | 0.13733 | 0.23804 | 0.21057 | 0.23346 | 0.11902 | 0.28839 | 0.18768 | 0.27008 | 0.35705 | 0.40741 | 0.28381 | -122.2641 | -122.4747 | 0.25635 | 0.11444 | 0.22888 | 0.12817
2956.7656 | 122.5113 | -0.29297 | 122.0901 | -0.1403 | 0.02242 | 0.0019974 | 0.053096 | 0.0010253 | -0.0007904 | -0.0043792 | -0.018616 | 0.014467 | 0.017822 | 0.0046527 | -0.029781 | -0.00050847 | 0.0020295 | -0.018311 | 0.15106 | -0.11902 | -0.022888 | 0.10529 | -0.032043 | 0.059509 | -0.13733 | 0.009155 | -0.38452 | -0.15106 | -0.036621 | -0.15106 | -0.10529 | 0.17395 | -121.9391 | -122.113 | 0.39825 | 0.35248 | 0.26093 | 0.17853 | 0.086976 | -0.091552 | -122.081 | -122.2412 | 0.25635 | 0.18768 | 0.14191 | 0.27924 | 0.23346 | 0.22431 | 0.096131 | 0.3479 | 0.23346 | 0.27008 | 0.39368 | 0.44403 | 0.30212 | -122.2092 | -122.4747 | 0.27008 | 0.14191 | 0.27466 | 0.15564
2957.7656 | 122.5708 | -0.29755 | 122.0764 | -0.17082 | 0.025624 | 0.0058426 | 0.054164 | -0.0011109 | -0.0005768 | -0.0026704 | -0.015564 | 0.014253 | 0.017395 | -4.6942e-05 | -0.032131 | -0.00029487 | -0.0026703 | 0.004578 | 0.15564 | -0.10529 | 0.027466 | 0.16479 | 0.009155 | 0.086975 | -0.059509 | -0.022888 | -0.35706 | -0.13275 | 0.004578 | -0.086975 | -0.07782 | 0.19226 | -121.9208 | -122.0489 | 0.46234 | 0.38452 | 0.3067 | 0.19226 | 0.11444 | -0.05951 | -122.0993 | -122.2092 | 0.30212 | 0.21973 | 0.21057 | 0.27924 | 0.27008 | 0.27008 | 0.13275 | 0.36163 | 0.2243 | 0.26093 | 0.33417 | 0.45319 | 0.27466 | -122.1817 | -122.4335 | 0.32501 | 0.16479 | 0.30212 | 0.23804
2958.7656 | 122.5571 | -0.30212 | 122.0718 | -0.13267 | 0.021138 | 0.0058426 | 0.052669 | 0.00059812 | -0.0054902 | -0.002884 | 0.014954 | 0.015107 | 0.017395 | 0.0016621 | -0.033626 | -0.0013629 | 0.00010689 | 0.009155 | 0.14648 | -0.11902 | 0.022888 | 0.16022 | 0 | 0.10071 | -0.086975 | -0.004578 | -0.35706 | -0.11902 | -0.004578 | -0.10071 | -0.07782 | 0.18311 | -121.9254 | -122.049 | 0.46234 | 0.40283 | 0.30212 | 0.21973 | 0.11902 | -0.054932 | -122.0764 | -122.1909 | 0.29755 | 0.2243 | 0.20142 | 0.27924 | 0.25635 | 0.27924 | 0.14191 | 0.35248 | 0.23804 | 0.2655 | 0.35248 | 0.44861 | 0.29755 | -122.1909 | -122.4289 | 0.32501 | 0.18311 | 0.31128 | 0.21515
2959.7656 | 122.5342 | -0.3067 | 122.0718 | -0.1403 | 0.023488 | 0.0047744 | 0.054591 | 0.00038452 | -0.0022858 | -0.0037384 | -0.015564 | 0.013826 | 0.016968 | 0.0037983 | -0.030209 | -0.0015765 | 0.0016021 | 0.009155 | 0.16479 | -0.086975 | 0.022888 | 0.14191 | -0.004578 | 0.082397 | -0.073242 | -0.013733 | -0.36163 | -0.13275 | -0.004578 | -0.10529 | -0.086975 | 0.21973 | -121.907 | -122.049 | 0.44861 | 0.3891 | 0.30212 | 0.16937 | 0.082397 | -0.054931 | -122.0856 | -122.2046 | 0.30212 | 0.21973 | 0.20142 | 0.27466 | 0.25635 | 0.22888 | 0.10986 | 0.35705 | 0.22888 | 0.25177 | 0.3479 | 0.4715 | 0.29297 | -122.1588 | -122.4335 | 0.32959 | 0.17395 | 0.31586 | 0.23346
2960.7656 | 122.5342 | -0.3067 | 122.1085 | -0.16319 | 0.02477 | 0.006697 | 0.053737 | -0.0013245 | -0.006131 | -0.00096136 | 0.0057984 | 0.015107 | 0.01825 | 0.0065753 | -0.030422 | -0.0017901 | 0.0022431 | 0.022888 | 0.14648 | -0.10986 | 0.022888 | 0.14191 | -0.004578 | 0.082397 | -0.07782 | -0.009155 | -0.37079 | -0.11902 | -0.022888 | -0.11902 | -0.082397 | 0.19684 | -121.962 | -122.0856 | 0.44861 | 0.3891 | 0.30212 | 0.19226 | 0.10529 | -0.064087 | -122.1176 | -122.2275 | 0.28381 | 0.2243 | 0.18768 | 0.28839 | 0.25177 | 0.25177 | 0.13275 | 0.3479 | 0.25177 | 0.25635 | 0.36163 | 0.45319 | 0.29755 | -122.2183 | -122.4792 | 0.32959 | 0.18768 | 0.32959 | 0.22888
2961.7656 | 122.4976 | -0.3067 | 122.1039 | -0.12505 | 0.024129 | 0.004988 | 0.055446 | -4.2682e-05 | -0.0048492 | -0.0030976 | -0.015564 | 0.013398 | 0.019104 | 0.0063617 | -0.031277 | -0.00072207 | 0.00096129 | 0.013733 | 0.14191 | -0.11902 | 0.018311 | 0.13275 | -0.009155 | 0.068665 | -0.11902 | 0.009155 | -0.36621 | -0.17395 | -0.054932 | -0.15564 | -0.1236 | 0.18768 | -121.962 | -122.0856 | 0.43945 | 0.37537 | 0.29755 | 0.18768 | 0.10986 | -0.059509 | -122.0947 | -122.2778 | 0.25177 | 0.18311 | 0.15106 | 0.24262 | 0.21057 | 0.25177 | 0.13733 | 0.31128 | 0.19226 | 0.26093 | 0.37537 | 0.44861 | 0.31586 | -122.2229 | -122.4701 | 0.32501 | 0.13275 | 0.32043 | 0.18768
2962.7656 | 122.525 | -0.31128 | 122.1085 | -0.13267 | 0.022633 | 0.0075516 | 0.054378 | -0.0015381 | -0.0024994 | -0.0048066 | -0.012512 | 0.014253 | 0.020386 | 0.0014485 | -0.030849 | -0.0030719 | 0.00010689 | -0.032043 | 0.14191 | -0.13733 | -0.027466 | 0.082397 | -0.068665 | 0.036621 | -0.16479 | -0.004578 | -0.36621 | -0.17853 | -0.045776 | -0.16479 | -0.10529 | 0.17395 | -121.9666 | -122.1359 | 0.39368 | 0.3479 | 0.24261 | 0.17395 | 0.068664 | -0.054932 | -122.113 | -122.287 | 0.2655 | 0.20599 | 0.14648 | 0.26093 | 0.20142 | 0.21973 | 0.10986 | 0.32044 | 0.18768 | 0.27924 | 0.36163 | 0.45319 | 0.3067 | -122.2458 | -122.4747 | 0.28381 | 0.13275 | 0.27924 | 0.14648
2963.7812 | 122.525 | -0.28381 | 122.1039 | -0.17082 | 0.02242 | 0.0071244 | 0.054164 | -0.00089728 | -0.002713 | -0.0018158 | -0.0094604 | 0.014039 | 0.0206 | 0.0093525 | -0.029354 | 0.0014141 | 0.0020295 | -0.022888 | 0.16479 | -0.10986 | -0.022888 | 0.09613 | -0.041199 | 0.041199 | -0.13733 | -0.009155 | -0.39368 | -0.15106 | -0.050354 | -0.13733 | -0.11444 | 0.17395 | -121.9391 | -122.1268 | 0.37994 | 0.32501 | 0.24261 | 0.15106 | 0.068664 | -0.10986 | -122.113 | -122.2549 | 0.23346 | 0.16937 | 0.14648 | 0.27924 | 0.25635 | 0.20599 | 0.086975 | 0.34332 | 0.24261 | 0.27466 | 0.38452 | 0.44861 | 0.27466 | -122.2137 | -122.4976 | 0.26092 | 0.13275 | 0.26092 | 0.14648
2965.3125 | 122.5616 | -0.29297 | 122.1039 | -0.2166 | 0.020283 | 0.0060562 | 0.055019 | -0.0034607 | -0.0018586 | -0.0013886 | -0.0033568 | 0.013826 | 0.018677 | 0.00038026 | -0.029995 | 0.00013253 | 0.0024567 | -0.022888 | 0.15564 | -0.10529 | 0.022888 | 0.14648 | -0.004578 | 0.086975 | -0.091553 | 0.004578 | -0.3479 | -0.13733 | -0.009155 | -0.10071 | -0.091553 | 0.18768 | -121.9482 | -122.081 | 0.43945 | 0.37994 | 0.28839 | 0.19226 | 0.10071 | -0.054931 | -122.0993 | -122.2412 | 0.28381 | 0.20142 | 0.19226 | 0.25635 | 0.24719 | 0.25177 | 0.12817 | 0.33874 | 0.21057 | 0.26093 | 0.35248 | 0.44861 | 0.29755 | -122.2092 | -122.4518 | 0.31586 | 0.15564 | 0.27008 | 0.20142
2966.1562 | 122.5067 | -0.3067 | 122.0764 | -0.19371 | 0.024342 | 0.0052018 | 0.054164 | -0.00068368 | -0.0018586 | -0.00096136 | -0.06134 | 0.013826 | 0.017182 | 0.0089253 | -0.032131 | -0.0017901 | -0.0011749 | 0 | 0.15564 | -0.11902 | 0 | 0.11444 | -0.064087 | 0.022888 | -0.14191 | -0.004578 | -0.36621 | -0.16937 | -0.068665 | -0.1831 | -0.13733 | 0.18768 | -121.9208 | -122.0764 | 0.42114 | 0.32959 | 0.24261 | 0.14191 | 0.054932 | -0.059509 | -122.081 | -122.2458 | 0.23804 | 0.16937 | 0.1236 | 0.22888 | 0.18311 | 0.23346 | 0.11902 | 0.29755 | 0.19684 | 0.27466 | 0.36163 | 0.46234 | 0.30212 | -122.1954 | -122.4426 | 0.3067 | 0.13733 | 0.3067 | 0.16479
2967.3906 | 122.5159 | -0.30212 | 122.081 | -0.2166 | 0.024342 | 0.0062698 | 0.053523 | -0.00089728 | -0.0048492 | -0.0020294 | -0.058289 | 0.016176 | 0.02124 | 0.0059345 | -0.030636 | -0.00072207 | -0.0011749 | -0.009155 | 0.14648 | -0.10071 | -0.004578 | 0.13733 | -0.054932 | 0.041199 | -0.11902 | 0 | -0.37537 | -0.14191 | -0.064087 | -0.16937 | -0.11444 | 0.20142 | -121.9345 | -122.0856 | 0.43945 | 0.34332 | 0.24719 | 0.14191 | 0.045776 | -0.073242 | -122.081 | -122.2229 | 0.23804 | 0.18768 | 0.13275 | 0.26092 | 0.20599 | 0.23804 | 0.09613 | 0.31128 | 0.23346 | 0.24719 | 0.37537 | 0.44861 | 0.30212 | -122.1817 | -122.4564 | 0.29755 | 0.16022 | 0.29297 | 0.18311
2969.0938 | 122.4335 | -0.33875 | 122.1634 | -0.12505 | 0.022847 | 0.004988 | 0.055019 | -0.0034607 | -0.0035674 | 0.00053404 | -0.070496 | 0.016176 | 0.020172 | 0.0044391 | -0.031917 | 0.00034613 | 0.00032049 | -0.073242 | 0.20142 | -0.16022 | -0.13275 | 0.073242 | -0.10986 | -0.068665 | -0.26093 | 0.041199 | -0.3891 | -0.27008 | -0.14648 | -0.27008 | -0.2243 | 0.17853 | -121.962 | -122.2961 | 0.41199 | 0.27008 | 0.22888 | 0.091552 | 0.050354 | -0.050354 | -122.1222 | -122.4335 | 0.19226 | 0.11444 | 0.068664 | 0.16479 | 0.11902 | 0.23346 | 0.027466 | 0.24261 | 0.11902 | 0.36163 | 0.4303 | 0.54016 | 0.37994 | -122.3236 | -122.5525 | 0.20599 | 0.068664 | 0.2655 | 0.07782
2970.3125 | 122.525 | -0.32044 | 122.1313 | -0.12505 | 0.021352 | 0.0037064 | 0.054164 | 0.00081172 | -0.0031402 | -0.0030976 | -0.0094604 | 0.014039 | 0.018463 | 0.0023029 | -0.031704 | -0.00029487 | 0.0013885 | 0.004578 | 0.14191 | -0.10071 | 0.004578 | 0.11902 | -0.022888 | 0.050354 | -0.13275 | -0.004578 | -0.3891 | -0.20142 | -0.059509 | -0.17395 | -0.14648 | 0.21973 | -121.9894 | -122.1268 | 0.43945 | 0.37079 | 0.29755 | 0.15106 | 0.07782 | -0.068664 | -122.1359 | -122.3328 | 0.26093 | 0.17395 | 0.14649 | 0.24261 | 0.21515 | 0.21973 | 0.10529 | 0.32959 | 0.18768 | 0.24262 | 0.38452 | 0.46234 | 0.31586 | -122.2321 | -122.5204 | 0.32501 | 0.11902 | 0.32501 | 0.18768
2971.0312 | 122.438 | -0.34332 | 122.1542 | -0.12505 | 0.025197 | 0.0064834 | 0.056087 | 0.00081172 | -0.0046356 | 0.001175 | -0.14679 | 0.016389 | 0.019745 | 0.0033711 | -0.030209 | -0.0069171 | 0.0022431 | -0.009155 | 0.16937 | -0.15106 | -0.073242 | 0.036621 | -0.13733 | -0.054932 | -0.21515 | -0.004578 | -0.39825 | -0.22888 | -0.16022 | -0.28839 | -0.20599 | 0.19226 | -121.9849 | -122.2275 | 0.37994 | 0.28839 | 0.20599 | 0.09613 | 0.013733 | -0.054931 | -122.1588 | -122.3831 | 0.18311 | 0.13733 | 0.054932 | 0.19226 | 0.10986 | 0.18768 | 0.07782 | 0.23804 | 0.16937 | 0.32044 | 0.39368 | 0.5127 | 0.33874 | -122.3053 | -122.5525 | 0.27008 | 0.11444 | 0.33417 | 0.12817
2972.4688 | 122.4792 | -0.33417 | 122.1359 | -0.18608 | 0.023488 | 0.0052018 | 0.052028 | 0.0025207 | -0.0033538 | -0.0013886 | -0.024719 | 0.012758 | 0.019959 | 0.0031573 | -0.031277 | -0.00093567 | 0.0024567 | 0.009155 | 0.15106 | -0.13275 | -0.032043 | 0.10529 | -0.032043 | 0.045776 | -0.16479 | 0.018311 | -0.37994 | -0.2243 | -0.10529 | -0.21057 | -0.1831 | 0.20142 | -121.9849 | -122.168 | 0.43945 | 0.37994 | 0.30212 | 0.17853 | 0.10071 | -0.045777 | -122.1176 | -122.3602 | 0.22888 | 0.15106 | 0.1236 | 0.19684 | 0.16937 | 0.23804 | 0.10071 | 0.27466 | 0.15564 | 0.28381 | 0.39826 | 0.48523 | 0.35248 | -122.2687 | -122.5159 | 0.30212 | 0.10986 | 0.34332 | 0.16937
2976.3281 | 122.4655 | -0.35248 | 122.1176 | -0.11742 | 0.021992 | 0.0060562 | 0.055232 | -0.00046988 | -0.0033538 | -0.003952 | -0.10712 | 0.015962 | 0.019745 | 0.0087115 | -0.03149 | -0.0011493 | 0.0020295 | -0.068665 | 0.17853 | -0.16479 | -0.11444 | -0.013733 | -0.16479 | -0.068665 | -0.2243 | 0 | -0.42572 | -0.2243 | -0.15106 | -0.2655 | -0.19226 | 0.18768 | -121.9391 | -122.2321 | 0.33875 | 0.28381 | 0.18768 | 0.09613 | 0 | -0.073242 | -122.1176 | -122.3419 | 0.20142 | 0.16022 | 0.086975 | 0.23346 | 0.16022 | 0.15106 | 0.050354 | 0.27466 | 0.20142 | 0.34332 | 0.42572 | 0.53101 | 0.35248 | -122.2824 | -122.5433 | 0.23804 | 0.12817 | 0.28381 | 0.12817
2976.8906 | 122.4838 | -0.32501 | 122.1313 | -0.11742 | 0.02242 | 0.005629 | 0.054378 | 0.0018799 | -0.002713 | -0.0030976 | -0.076599 | 0.015962 | 0.019531 | 0.0025165 | -0.030209 | -8.1274e-05 | 0.00074769 | -0.036621 | 0.17395 | -0.13733 | -0.07782 | 0.022888 | -0.10529 | -0.022888 | -0.1831 | -0.004578 | -0.37994 | -0.21515 | -0.10529 | -0.21973 | -0.1831 | 0.18768 | -121.9574 | -122.2092 | 0.3479 | 0.30212 | 0.21973 | 0.11444 | 0.032043 | -0.054932 | -122.1359 | -122.3465 | 0.21973 | 0.14191 | 0.10529 | 0.19684 | 0.16022 | 0.16022 | 0.059509 | 0.27466 | 0.16479 | 0.31128 | 0.37537 | 0.49896 | 0.32043 | -122.2687 | -122.5113 | 0.24719 | 0.10986 | 0.28839 | 0.14191
2977.7656 | 122.4838 | -0.32044 | 122.168 | -0.18608 | 0.023061 | 0.003279 | 0.055019 | 0.00081172 | -0.0014312 | -0.0024566 | 0.018005 | 0.014467 | 0.018463 | 0.0044391 | -0.031277 | 0.0014141 | 0.0039521 | 0.004578 | 0.16937 | -0.13275 | -0.027466 | 0.11902 | -0.041199 | 0.045776 | -0.16479 | 0 | -0.37994 | -0.21973 | -0.10071 | -0.19226 | -0.15564 | 0.18768 | -121.9986 | -122.1954 | 0.43945 | 0.36621 | 0.27924 | 0.17853 | 0.091552 | -0.059509 | -122.168 | -122.3877 | 0.21973 | 0.1648 | 0.12817 | 0.2243 | 0.18768 | 0.25177 | 0.10529 | 0.27924 | 0.16022 | 0.30212 | 0.37994 | 0.48981 | 0.32044 | -122.3007 | -122.5479 | 0.29297 | 0.10071 | 0.32501 | 0.15564
2978.7656 | 122.438 | -0.31586 | 122.1863 | -0.16319 | 0.021352 | 0.0047744 | 0.053096 | -0.00046988 | -0.0042084 | -0.003952 | 0.0027466 | 0.014039 | 0.02124 | -4.6942e-05 | -0.031277 | 0.00077333 | 0.0033111 | -0.068665 | 0.17853 | -0.16022 | -0.1236 | 0.004578 | -0.11444 | -0.027466 | -0.24261 | 0.018311 | -0.40741 | -0.32044 | -0.09613 | -0.23804 | -0.19226 | 0.15564 | -122.0078 | -122.3099 | 0.32044 | 0.28839 | 0.20142 | 0.13275 | 0.045776 | -0.091553 | -122.168 | -122.5067 | 0.21973 | 0.1236 | 0.07782 | 0.21515 | 0.16937 | 0.16479 | 0.036621 | 0.31128 | 0.086975 | 0.33874 | 0.42572 | 0.49438 | 0.33417 | -122.3465 | -122.5937 | 0.19226 | -0.004578 | 0.24719 | 0.073242
2979.8438 | 122.5662 | -0.32044 | 122.1359 | -0.14793 | 0.022206 | 0.0043472 | 0.05331 | -4.2682e-05 | -0.0042084 | -0.0035248 | 0.039368 | 0.014039 | 0.01825 | 0.0037983 | -0.030209 | -0.0017901 | 0.0033111 | -0.018311 | 0.16479 | -0.1236 | -0.050354 | 0.091553 | -0.050354 | 0.036621 | -0.13275 | -0.013733 | -0.36621 | -0.15106 | -0.036621 | -0.13275 | -0.10071 | 0.19684 | -121.9711 | -122.1863 | 0.41199 | 0.35706 | 0.27008 | 0.16022 | 0.073242 | -0.045776 | -122.1497 | -122.287 | 0.28381 | 0.21973 | 0.18768 | 0.2655 | 0.23346 | 0.21515 | 0.073242 | 0.32959 | 0.21515 | 0.28839 | 0.35248 | 0.48523 | 0.3067 | -122.2595 | -122.5021 | 0.27008 | 0.16937 | 0.30212 | 0.18768
2980.7656 | 122.4472 | -0.32501 | 122.1542 | -0.17845 | 0.023274 | 0.0045608 | 0.05395 | 0.0048705 | -0.002713 | -0.00074776 | 0.082092 | 0.015321 | 0.021668 | 0.0023029 | -0.030422 | -0.00029487 | 0.00074769 | -0.068665 | 0.17853 | -0.14648 | -0.1236 | -0.004578 | -0.1236 | -0.027466 | -0.29755 | 0.054932 | -0.3479 | -0.24719 | -0.16479 | -0.27466 | -0.21515 | 0.17853 | -121.9757 | -122.2778 | 0.32043 | 0.29755 | 0.20142 | 0.11902 | 0.022888 | -0.022888 | -122.0993 | -122.4014 | 0.16022 | 0.10986 | 0.050354 | 0.13275 | 0.073242 | 0.14191 | 0.022888 | 0.1831 | 0.10071 | 0.32501 | 0.40283 | 0.50354 | 0.37994 | -122.3007 | -122.5021 | 0.20142 | 0.07782 | 0.25635 | 0.027466
2981.7656 | 122.493 | -0.35706 | 122.113 | -0.11742 | 0.023488 | 0.0060562 | 0.05395 | 0.0023071 | -0.0020722 | -0.0020294 | -0.033874 | 0.016603 | 0.019318 | 0.0078571 | -0.031277 | 0.00055973 | 0.0030975 | -0.054932 | 0.17853 | -0.16479 | -0.10529 | 0.004578 | -0.10986 | -0.036621 | -0.25177 | 0.018311 | -0.41199 | -0.2655 | -0.15106 | -0.26093 | -0.20599 | 0.19226 | -121.9345 | -122.2183 | 0.36163 | 0.32043 | 0.24719 | 0.12817 | 0.054932 | -0.054931 | -122.0947 | -122.3785 | 0.20599 | 0.15106 | 0.096131 | 0.20599 | 0.15106 | 0.16937 | 0.059509 | 0.26092 | 0.14648 | 0.34332 | 0.4303 | 0.53558 | 0.37537 | -122.2778 | -122.525 | 0.25177 | 0.091553 | 0.30212 | 0.10529
2982.8281 | 122.4976 | -0.3479 | 122.1634 | -0.18608 | 0.022633 | 0.0069106 | 0.054164 | 0.00059812 | -0.0052764 | -0.002884 | -0.073547 | 0.01703 | 0.019104 | 0.0093525 | -0.028713 | -0.00029487 | 0.0030975 | -0.009155 | 0.1831 | -0.10529 | -0.059509 | 0.059509 | -0.10071 | -0.027466 | -0.17853 | 0.009155 | -0.3891 | -0.21973 | -0.13733 | -0.25177 | -0.1831 | 0.24261 | -121.9803 | -122.2229 | 0.40741 | 0.32043 | 0.24719 | 0.07782 | 0.004578 | -0.041199 | -122.1542 | -122.3831 | 0.21057 | 0.16479 | 0.09613 | 0.20599 | 0.13733 | 0.16479 | 0.045777 | 0.25177 | 0.16937 | 0.28839 | 0.39825 | 0.531 | 0.35706 | -122.2687 | -122.5525 | 0.28839 | 0.12817 | 0.33874 | 0.16937
2983.7656 | 122.5067 | -0.37079 | 122.1451 | -0.12505 | 0.022633 | 0.0054154 | 0.052028 | -4.2682e-05 | -0.0029266 | -0.005661 | -0.018616 | 0.014253 | 0.019318 | 0.0084979 | -0.030636 | -0.00029487 | 0.0024567 | -0.054932 | 0.17395 | -0.13733 | -0.11444 | -0.004578 | -0.12817 | -0.032043 | -0.26093 | -0.018311 | -0.40741 | -0.2655 | -0.14191 | -0.26093 | -0.19684 | 0.23346 | -121.9711 | -122.2595 | 0.36621 | 0.33875 | 0.24261 | 0.10529 | 0.009155 | -0.036621 | -122.1634 | -122.4106 | 0.22888 | 0.17395 | 0.10986 | 0.21057 | 0.14648 | 0.13275 | 0.022888 | 0.2655 | 0.14191 | 0.31128 | 0.3891 | 0.54474 | 0.35248 | -122.2824 | -122.5525 | 0.25635 | 0.10529 | 0.31586 | 0.10986
2984.8281 | 122.4838 | -0.34332 | 122.1725 | -0.17082 | 0.023701 | 0.0045608 | 0.056514 | 0.0044433 | -0.007199 | -0.0020294 | -0.073547 | 0.014894 | 0.021454 | 0.010848 | -0.033199 | -0.0011493 | -0.0020295 | -0.009155 | 0.19684 | -0.1236 | -0.073242 | 0.045776 | -0.10986 | -0.032043 | -0.1831 | -0.009155 | -0.3891 | -0.22888 | -0.13733 | -0.24719 | -0.19226 | 0.21973 | -121.9757 | -122.2458 | 0.3891 | 0.31128 | 0.23346 | 0.091553 | 0.013733 | -0.045776 | -122.1817 | -122.4014 | 0.20599 | 0.15106 | 0.096131 | 0.19684 | 0.14191 | 0.16937 | 0.050354 | 0.25177 | 0.16022 | 0.32043 | 0.37994 | 0.54016 | 0.33417 | -122.2961 | -122.5616 | 0.27008 | 0.11444 | 0.33417 | 0.16022
2985.7656 | 122.4701 | -0.35248 | 122.1542 | -0.14793 | 0.023915 | 0.0062698 | 0.052882 | -0.0030335 | -0.0022858 | -0.0030976 | -0.0064086 | 0.015748 | 0.021668 | 0.0074299 | -0.028286 | -0.0013629 | 0.0048065 | -0.059509 | 0.19226 | -0.14648 | -0.009155 | -0.082397 | -0.22888 | 0.004578 | -0.27008 | 0.068665 | -0.38452 | -0.27008 | -0.16479 | -0.25177 | -0.20599 | 0.20599 | -121.962 | -122.1634 | 0.27008 | 0.35706 | 0.1236 | 0.15106 | -0.082398 | -0.032043 | -122.0856 | -122.4243 | 0.18768 | 0.14648 | 0.10071 | 0.17853 | 0.13275 | 0.064087 | 0.13733 | 0.21973 | 0.11444 | 0.33874 | 0.45319 | 0.54474 | 0.42114 | -122.3007 | -122.5388 | 0.34332 | 0.082397 | 0.29297 | 0.082397
2986.7656 | 122.4838 | -0.35248 | 122.1771 | -0.1403 | 0.025838 | 0.003279 | 0.054591 | -0.00089728 | -0.0022858 | -0.0050202 | 0.051575 | 0.016603 | 0.019318 | -0.0017559 | -0.02914 | -0.0015765 | 0.0011749 | -0.064087 | 0.1831 | -0.16937 | 0.027466 | 0.022888 | -0.32044 | -0.027466 | -0.26093 | 0.050354 | -0.36163 | -0.27466 | -0.15564 | -0.2655 | -0.20599 | 0.18311 | -121.994 | -122.1497 | 0.37537 | 0.32501 | 0.032043 | 0.14191 | -0.15106 | -0.009155 | -122.1268 | -122.4518 | 0.19684 | 0.14648 | 0.086975 | 0.15564 | 0.09613 | 0.19226 | 0.19684 | 0.20599 | 0.086975 | 0.35248 | 0.41199 | 0.53558 | 0.40283 | -122.3465 | -122.5388 | 0.37994 | 0.07782 | 0.28839 | 0.091553
2987.7656 | 122.4884 | -0.35706 | 122.1863 | -0.11742 | 0.02242 | 0.004988 | 0.052669 | -0.0021789 | -0.0029266 | -0.0037384 | -0.0064086 | 0.017457 | 0.019531 | 0.0044391 | -0.031063 | -0.0024311 | -0.00074771 | -0.045776 | 0.16937 | -0.15564 | -0.11444 | -0.013733 | -0.11902 | -0.036621 | -0.25177 | 0.009155 | -0.40741 | -0.27008 | -0.15106 | -0.25177 | -0.19226 | 0.20142 | -122.0169 | -122.3007 | 0.34332 | 0.32043 | 0.23804 | 0.11902 | 0.036621 | -0.050354 | -122.1771 | -122.4564 | 0.20599 | 0.16479 | 0.10529 | 0.21515 | 0.15564 | 0.14191 | 0.041199 | 0.25635 | 0.13733 | 0.32501 | 0.41657 | 0.52643 | 0.36621 | -122.3419 | -122.5937 | 0.24261 | 0.086975 | 0.31128 | 0.10529
2988.8281 | 122.5296 | -0.2655 | 122.2321 | -0.10979 | 0.021565 | 0.0058426 | 0.0563 | 0.0046569 | -0.0039948 | -0.0024566 | -0.058289 | 0.014467 | 0.017182 | 0.0080707 | -0.032131 | 0.00055973 | 0.0045929 | -0.018311 | 0.15564 | -0.15106 | -0.07782 | 0.064087 | -0.09613 | -0.013733 | -0.17853 | -0.004578 | -0.37994 | 0.004578 | -0.091553 | -0.091553 | -0.091553 | 0.11444 | -122.0764 | -122.3099 | 0.32959 | 0.25177 | 0.16937 | 0.13733 | 0.054932 | -0.11444 | -122.2366 | -122.2275 | 0.17395 | 0.17395 | 0.17395 | 0.28839 | 0.28839 | 0.21515 | 0.073242 | 0.28839 | 0.38452 | 0.3067 | 0.37537 | 0.42114 | 0.26092 | -122.3831 | -122.612 | 0.18768 | 0.27008 | 0.24719 | 0.086975
2989.7656 | 122.493 | -0.34332 | 122.1909 | -0.16319 | 0.026051 | 0.0060562 | 0.053523 | 0.0016663 | -0.0016448 | -0.00010676 | 0.054627 | 0.018098 | 0.020172 | 0.0020893 | -0.029568 | -0.0015765 | 0.0013885 | -0.004578 | 0.16937 | -0.12817 | -0.054932 | 0.091553 | -0.045776 | 0.027466 | -0.21973 | 0.018311 | -0.3891 | -0.2655 | -0.14191 | -0.23804 | -0.19226 | 0.21515 | -122.0215 | -122.2458 | 0.43488 | 0.37079 | 0.29755 | 0.15564 | 0.082398 | -0.045776 | -122.1725 | -122.4564 | 0.20142 | 0.15106 | 0.10529 | 0.19684 | 0.15106 | 0.21973 | 0.073242 | 0.24719 | 0.1236 | 0.29755 | 0.40741 | 0.5127 | 0.36163 | -122.319 | -122.58 | 0.28839 | 0.07782 | 0.33874 | 0.1236
2990.7656 | 122.5067 | -0.35706 | 122.1771 | -0.16319 | 0.024129 | 0.0052018 | 0.05331 | 0.00059812 | -0.002713 | -0.0041656 | -0.0033568 | 0.015107 | 0.018036 | 0.00016666 | -0.031277 | -0.0015765 | 0.00074769 | -0.036621 | 0.17395 | -0.15564 | -0.10071 | -0.009155 | -0.14191 | -0.036621 | -0.26093 | 0.018311 | -0.42114 | -0.27466 | -0.15106 | -0.26093 | -0.21973 | 0.20142 | -122.0032 | -122.2778 | 0.3479 | 0.32043 | 0.21515 | 0.11902 | 0.013733 | -0.064087 | -122.1588 | -122.4518 | 0.20599 | 0.13733 | 0.096131 | 0.20142 | 0.16022 | 0.14649 | 0.054932 | 0.27008 | 0.14648 | 0.32959 | 0.43945 | 0.53101 | 0.37537 | -122.3328 | -122.5983 | 0.25635 | 0.082398 | 0.32043 | 0.096131
2991.8281 | 122.4747 | -0.33417 | 122.1588 | -0.12505 | 0.02541 | 0.0079788 | 0.05395 | -0.0013245 | -0.0018586 | -0.0030976 | -0.073547 | 0.017457 | 0.017609 | 0.0016621 | -0.029568 | 0.00034613 | -0.0020295 | -0.07782 | 0.1831 | -0.15106 | -0.14648 | -0.064087 | -0.21515 | -0.09613 | -0.27466 | 0.013733 | -0.37537 | -0.30212 | -0.11902 | -0.32501 | -0.23804 | 0.1831 | -121.9757 | -122.3053 | 0.27008 | 0.23804 | 0.11902 | 0.054932 | -0.064087 | -0.041199 | -122.1451 | -122.4609 | 0.21515 | 0.09613 | 0.009155 | 0.13733 | 0.050354 | 0.086975 | 0.004578 | 0.25635 | 0.073242 | 0.33417 | 0.3891 | 0.51727 | 0.3479 | -122.3099 | -122.5342 | 0.18768 | 0.032043 | 0.25635 | 0.059509
2992.7656 | 122.5296 | -0.33875 | 122.168 | -0.11742 | 0.025197 | 0.0041336 | 0.054805 | -0.00068368 | -0.0001496 | -0.0041656 | -0.015564 | 0.013826 | 0.020172 | 0.0012347 | -0.030209 | -0.0022175 | 0.0026703 | -0.022888 | 0.16022 | -0.13275 | -0.09613 | 0.036621 | -0.10529 | -0.022888 | -0.18768 | 0 | -0.41199 | -0.21973 | -0.1236 | -0.23804 | -0.17395 | 0.20599 | -122.0078 | -122.2641 | 0.37537 | 0.31586 | 0.23346 | 0.10986 | 0.027465 | -0.073242 | -122.168 | -122.3877 | 0.21515 | 0.1648 | 0.10071 | 0.23804 | 0.17395 | 0.16937 | 0.036621 | 0.28839 | 0.19226 | 0.29297 | 0.41199 | 0.49896 | 0.33875 | -122.3007 | -122.58 | 0.24262 | 0.11902 | 0.31586 | 0.15106
2993.7656 | 122.5113 | -0.32501 | 122.1909 | -0.15556 | 0.024983 | 0.0058426 | 0.055232 | 0.0040161 | -0.001004 | -0.0018158 | -0.021667 | 0.017671 | 0.016968 | 0.0037983 | -0.03149 | 0.00077333 | 0.0030975 | -0.041199 | 0.15564 | -0.16479 | -0.091553 | 0.045776 | -0.082397 | -0.018311 | -0.20142 | 0.009155 | -0.39368 | -0.2243 | -0.12817 | -0.2243 | -0.17395 | 0.16022 | -122.0352 | -122.2824 | 0.37079 | 0.3067 | 0.24262 | 0.14648 | 0.082398 | -0.068665 | -122.1817 | -122.4152 | 0.19684 | 0.15106 | 0.10071 | 0.21973 | 0.16937 | 0.21057 | 0.073242 | 0.2655 | 0.16937 | 0.32044 | 0.40283 | 0.48065 | 0.33417 | -122.3557 | -122.5845 | 0.23346 | 0.10071 | 0.28381 | 0.1236
2994.7656 | 122.5296 | -0.32501 | 122.1588 | -0.19371 | 0.024983 | 0.0054154 | 0.054805 | -4.2682e-05 | -0.0012176 | -0.0052338 | -0.024719 | 0.01468 | 0.022095 | 0.0050801 | -0.029995 | 0.00013253 | 0.00053409 | -0.032043 | 0.17853 | -0.14191 | -0.10986 | 0.032043 | -0.10529 | -0.022888 | -0.20142 | -0.013733 | -0.41199 | -0.22888 | -0.11444 | -0.22888 | -0.1831 | 0.18311 | -121.9803 | -122.2687 | 0.35706 | 0.30212 | 0.21973 | 0.11902 | 0.036621 | -0.086975 | -122.1725 | -122.3877 | 0.21057 | 0.14191 | 0.09613 | 0.22888 | 0.1831 | 0.17395 | 0.032044 | 0.29755 | 0.1831 | 0.32044 | 0.39825 | 0.50354 | 0.31128 | -122.3007 | -122.5708 | 0.21515 | 0.09613 | 0.29297 | 0.1236
2995.7656 | 122.5067 | -0.35706 | 122.1634 | -0.10979 | 0.023274 | 0.0045608 | 0.054378 | 0.0020935 | -0.0024994 | -0.0060882 | 0.018005 | 0.01468 | 0.019959 | 0.0057209 | -0.030636 | -0.0020039 | 0.0037385 | -0.059509 | 0.1831 | -0.15564 | -0.1236 | 0.009155 | -0.11444 | -0.041199 | -0.26093 | 0.004578 | -0.40741 | -0.27466 | -0.16937 | -0.26093 | -0.21515 | 0.20142 | -121.9803 | -122.287 | 0.36621 | 0.31586 | 0.24261 | 0.11444 | 0.041199 | -0.050354 | -122.1588 | -122.438 | 0.18768 | 0.14191 | 0.096131 | 0.19226 | 0.14648 | 0.16479 | 0.032044 | 0.23804 | 0.13275 | 0.33874 | 0.41199 | 0.54016 | 0.36163 | -122.319 | -122.5708 | 0.23346 | 0.082398 | 0.29755 | 0.096131
2996.7656 | 122.5067 | -0.36163 | 122.1542 | -0.12505 | 0.024556 | 0.0037064 | 0.053096 | 0.0012391 | -0.0059174 | -0.002884 | 0.024109 | 0.016176 | 0.018677 | 0.0065753 | -0.030636 | -0.0013629 | 0.00096129 | -0.059509 | 0.1831 | -0.17853 | -0.13275 | 0 | -0.11902 | -0.036621 | -0.2655 | 0.013733 | -0.39368 | -0.27466 | -0.15564 | -0.25177 | -0.21973 | 0.1831 | -121.9711 | -122.287 | 0.36163 | 0.32501 | 0.24261 | 0.14191 | 0.059509 | -0.032044 | -122.1405 | -122.4289 | 0.20599 | 0.14191 | 0.10986 | 0.17395 | 0.14191 | 0.17853 | 0.045777 | 0.23804 | 0.11902 | 0.36163 | 0.40741 | 0.54474 | 0.37537 | -122.3328 | -122.5479 | 0.22888 | 0.086975 | 0.30212 | 0.09613
2997.7656 | 122.5204 | -0.33875 | 122.1542 | -0.13267 | 0.021779 | 0.0058426 | 0.052882 | 0.00017092 | -0.0020722 | -0.0016022 | -0.033874 | 0.01703 | 0.018036 | 0.0012347 | -0.031277 | 0.0018413 | 0.0026703 | -0.022888 | 0.1831 | -0.15564 | -0.091553 | 0.032043 | -0.10529 | -0.032043 | -0.19226 | 0 | -0.39825 | -0.22888 | -0.10986 | -0.22888 | -0.16479 | 0.18311 | -121.9711 | -122.2458 | 0.37079 | 0.3067 | 0.23346 | 0.1236 | 0.050354 | -0.059509 | -122.1542 | -122.3831 | 0.22888 | 0.17395 | 0.10986 | 0.23346 | 0.16937 | 0.18768 | 0.064087 | 0.28839 | 0.16937 | 0.33874 | 0.39825 | 0.52185 | 0.33875 | -122.3099 | -122.5525 | 0.24719 | 0.10986 | 0.31586 | 0.14648
2998.7656 | 122.5204 | -0.35248 | 122.1954 | -0.15556 | 0.026265 | 0.0064834 | 0.054805 | 0.0040161 | -0.0020722 | -0.0020294 | -0.012512 | 0.016816 | 0.019104 | 0.0048663 | -0.032558 | 0.00055973 | 0.0030975 | 0.11444 | 0.19684 | -0.086975 | -0.027466 | 0.073242 | -0.07782 | 0.004578 | -0.16479 | 0.004578 | -0.36163 | -0.2243 | -0.13275 | -0.23804 | -0.17395 | 0.2655 | -121.9986 | -122.2229 | 0.42572 | 0.35706 | 0.27466 | 0.091553 | 0.009155 | -0.009155 | -122.1909 | -122.4197 | 0.21973 | 0.17853 | 0.11444 | 0.18768 | 0.1236 | 0.16022 | 0.059509 | 0.22888 | 0.13733 | 0.28381 | 0.36621 | 0.54932 | 0.35706 | -122.2824 | -122.5571 | 0.32501 | 0.12817 | 0.46692 | 0.18768
2999.7656 | 122.5296 | -0.32959 | 122.1771 | -0.1403 | 0.023061 | 0.007338 | 0.052882 | 0.0046569 | -0.0035674 | -0.0026704 | -0.024719 | 0.015748 | 0.018891 | -4.6942e-05 | -0.030209 | -0.00072207 | 0.00010689 | -0.004578 | 0.17395 | -0.14191 | -0.054932 | 0.10986 | -0.073242 | -0.004578 | -0.17395 | 0.022888 | -0.37079 | -0.20142 | -0.13733 | -0.21973 | -0.17395 | 0.18768 | -122.0032 | -122.2321 | 0.43945 | 0.32501 | 0.25635 | 0.13733 | 0.068665 | -0.041199 | -122.1542 | -122.3785 | 0.19226 | 0.15564 | 0.10986 | 0.19684 | 0.15106 | 0.25177 | 0.086975 | 0.23346 | 0.16937 | 0.31586 | 0.39368 | 0.50354 | 0.35248 | -122.319 | -122.5479 | 0.27466 | 0.12817 | 0.32501 | 0.15564
3000.7656 | 122.5433 | -0.31586 | 122.1909 | -0.17082 | 0.022633 | 0.0060562 | 0.05331 | 0.00059812 | -0.0024994 | -0.002884 | -0.021667 | 0.015962 | 0.019318 | 0.0035847 | -0.029781 | -0.0015765 | 0.00032049 | -0.018311 | 0.16937 | -0.14648 | -0.073242 | 0.091553 | -0.059509 | 0 | -0.16022 | 0.036621 | -0.35706 | -0.2243 | -0.11444 | -0.22888 | -0.17395 | 0.16937 | -122.0215 | -122.2641 | 0.40741 | 0.31586 | 0.25635 | 0.14648 | 0.086975 | -0.041199 | -122.1542 | -122.4152 | 0.20142 | 0.14191 | 0.086975 | 0.18311 | 0.12817 | 0.23804 | 0.073242 | 0.24261 | 0.13275 | 0.31586 | 0.39368 | 0.48523 | 0.35248 | -122.3373 | -122.5479 | 0.24261 | 0.091553 | 0.29755 | 0.15564
3001.7656 | 122.5113 | -0.33875 | 122.1909 | -0.12505 | 0.026051 | 0.005629 | 0.05331 | 0.0016663 | -0.0042084 | -0.0013886 | 0.0057984 | 0.015748 | 0.021668 | 0.0061481 | -0.031704 | 0.00013253 | -0.0011749 | -0.027466 | 0.16937 | -0.15106 | -0.07782 | 0.10529 | -0.059509 | 0 | -0.16479 | 0.036621 | -0.37079 | -0.21515 | -0.12817 | -0.21057 | -0.16937 | 0.18768 | -122.0215 | -122.2687 | 0.44403 | 0.33875 | 0.27924 | 0.15106 | 0.091553 | -0.032044 | -122.1542 | -122.406 | 0.21057 | 0.16937 | 0.12817 | 0.20142 | 0.16022 | 0.25635 | 0.073242 | 0.24261 | 0.15564 | 0.32044 | 0.40741 | 0.50812 | 0.37537 | -122.3419 | -122.5616 | 0.26093 | 0.1236 | 0.31128 | 0.17395
3002.7656 | 122.5479 | -0.3479 | 122.1863 | -0.15556 | 0.023488 | 0.004988 | 0.051387 | 0.0055115 | -0.0048492 | -0.0026704 | -0.0064086 | 0.015321 | 0.019531 | 0.0076435 | -0.030209 | 0.00055973 | 0.0024567 | -0.036621 | 0.16022 | -0.15564 | -0.10986 | 0.036621 | -0.10071 | -0.022888 | -0.20599 | -0.009155 | -0.41657 | -0.24261 | -0.11444 | -0.2243 | -0.16022 | 0.19226 | -122.0261 | -122.2961 | 0.38452 | 0.32501 | 0.24719 | 0.13275 | 0.054932 | -0.068665 | -122.1954 | -122.4289 | 0.23346 | 0.18768 | 0.1236 | 0.25635 | 0.19226 | 0.19226 | 0.045777 | 0.30212 | 0.17395 | 0.31586 | 0.40741 | 0.50812 | 0.33874 | -122.3419 | -122.6028 | 0.23804 | 0.10528 | 0.31128 | 0.14191
3003.7656 | 122.5388 | -0.32501 | 122.2092 | -0.10979 | 0.021779 | 0.0047744 | 0.05395 | 0.0029479 | -0.0037812 | -0.0035248 | 0.014954 | 0.016176 | 0.016114 | 0.0046527 | -0.033199 | 0.0012005 | 0.00032049 | -0.045776 | 0.16022 | -0.16022 | -0.082397 | 0.018311 | -0.10529 | -0.018311 | -0.20599 | -0.009155 | -0.40741 | -0.2243 | -0.11444 | -0.22888 | -0.16479 | 0.1648 | -122.0489 | -122.2916 | 0.34332 | 0.3067 | 0.21973 | 0.14191 | 0.054931 | -0.082398 | -122.2183 | -122.4335 | 0.21057 | 0.16022 | 0.09613 | 0.24261 | 0.17853 | 0.17853 | 0.07782 | 0.29297 | 0.18311 | 0.32043 | 0.39825 | 0.48523 | 0.31586 | -122.3694 | -122.6166 | 0.24262 | 0.10071 | 0.27924 | 0.11902
3004.7656 | 122.5204 | -0.3067 | 122.2 | -0.17845 | 0.023061 | 0.0069106 | 0.054591 | 0.0029479 | -0.0020722 | -0.0037384 | -0.021667 | 0.016816 | 0.018677 | -0.0017559 | -0.031063 | -0.0017901 | 0.0024567 | -0.013733 | 0.15564 | -0.14648 | -0.009155 | 0.20599 | -0.004578 | 0.073242 | -0.16937 | 0.050354 | -0.33417 | -0.21057 | -0.1236 | -0.23346 | -0.16479 | 0.16022 | -122.0444 | -122.2092 | 0.5127 | 0.37994 | 0.30212 | 0.21973 | 0.14191 | -0.027465 | -122.1497 | -122.4106 | 0.18311 | 0.14191 | 0.073243 | 0.16937 | 0.10071 | 0.35248 | 0.13733 | 0.21057 | 0.1236 | 0.30212 | 0.38452 | 0.46234 | 0.35706 | -122.3465 | -122.5342 | 0.29755 | 0.096131 | 0.29297 | 0.13733
3005.7656 | 122.525 | -0.3479 | 122.2092 | -0.15556 | 0.024556 | 0.0081924 | 0.0563 | 0.0031617 | -0.004422 | -0.001175 | -0.015564 | 0.015748 | 0.019104 | 0.0044391 | -0.031704 | 0.0014141 | 0.00096129 | -0.009155 | 0.16022 | -0.14191 | -0.086975 | 0.041199 | -0.11444 | -0.036621 | -0.20599 | -0.004578 | -0.39825 | -0.25177 | -0.16479 | -0.28381 | -0.19684 | 0.20599 | -122.0489 | -122.2961 | 0.3891 | 0.31128 | 0.23346 | 0.10529 | 0.027466 | -0.050354 | -122.2137 | -122.4609 | 0.1831 | 0.15106 | 0.064087 | 0.20142 | 0.11444 | 0.18311 | 0.054932 | 0.23346 | 0.14648 | 0.30212 | 0.39368 | 0.50812 | 0.34332 | -122.3511 | -122.6074 | 0.26092 | 0.09613 | 0.33874 | 0.14191
3006.8281 | 122.4655 | -0.34332 | 122.2458 | -0.1403 | 0.023061 | 0.0071244 | 0.055873 | 0.0035889 | -0.0059174 | -0.0035248 | -0.039978 | 0.014039 | 0.021454 | 0.0042255 | -0.029781 | 0.00013253 | 0.0013885 | -0.073242 | 0.15106 | -0.14648 | -0.13733 | -0.032043 | -0.1831 | -0.068665 | -0.29755 | -0.009155 | -0.39825 | -0.28839 | -0.2243 | -0.32501 | -0.22888 | 0.19684 | -122.0947 | -122.3831 | 0.31128 | 0.27466 | 0.16022 | 0.077819 | -0.036621 | -0.054931 | -122.2549 | -122.5342 | 0.11902 | 0.11444 | 0.018311 | 0.16937 | 0.073242 | 0.11444 | 0.009155 | 0.17395 | 0.10986 | 0.29755 | 0.3891 | 0.49438 | 0.33417 | -122.3923 | -122.644 | 0.20599 | 0.054932 | 0.27008 | 0.045777
3007.7656 | 122.5204 | -0.3479 | 122.2 | -0.18608 | 0.023915 | 0.0045608 | 0.054591 | 0.00081172 | -0.0037812 | 0.00053404 | -0.021667 | 0.015321 | 0.017395 | 0.00080746 | -0.030422 | -8.1274e-05 | 0.0045929 | -0.009155 | 0.19226 | -0.10986 | -0.091553 | 0.045776 | -0.09613 | -0.036621 | -0.19684 | -0.022888 | -0.3891 | -0.24261 | -0.14648 | -0.2655 | -0.1831 | 0.23804 | -122.0078 | -122.2916 | 0.39368 | 0.31128 | 0.25177 | 0.073242 | 0.013733 | -0.041199 | -122.2229 | -122.4426 | 0.20142 | 0.16479 | 0.082397 | 0.20599 | 0.1236 | 0.15564 | 0.01831 | 0.24261 | 0.14648 | 0.30212 | 0.36621 | 0.54016 | 0.32501 | -122.3099 | -122.5891 | 0.25635 | 0.10528 | 0.33874 | 0.15106
3008.7656 | 122.525 | -0.33875 | 122.2137 | -0.13267 | 0.023061 | 0.0052018 | 0.053096 | 0.0018799 | -0.0018586 | -0.003952 | -0.018616 | 0.014253 | 0.018891 | 0.0027301 | -0.031063 | -0.00050847 | 0.0022431 | 0 | 0.20599 | -0.091553 | -0.091553 | 0.059509 | -0.091553 | -0.027466 | -0.17853 | 0.004578 | -0.39825 | -0.22888 | -0.15564 | -0.25177 | -0.1831 | 0.24719 | -122.0078 | -122.3053 | 0.39825 | 0.31128 | 0.24719 | 0.064087 | 0 | -0.059509 | -122.2092 | -122.4426 | 0.18311 | 0.15564 | 0.086975 | 0.21515 | 0.14648 | 0.15106 | 0 | 0.24261 | 0.16937 | 0.29755 | 0.40283 | 0.54474 | 0.34332 | -122.3053 | -122.612 | 0.24719 | 0.10986 | 0.33875 | 0.16022
3009.7656 | 122.5571 | -0.32959 | 122.1954 | -0.14793 | 0.024556 | 0.0037064 | 0.053523 | 0.0027343 | -0.0024994 | -0.00096136 | 0.011902 | 0.014467 | 0.020172 | 0.0023029 | -0.032131 | -8.1274e-05 | 0.0022431 | -0.027466 | 0.15564 | -0.16022 | -0.086975 | 0.064087 | -0.082397 | -0.009155 | -0.1831 | -0.018311 | -0.39368 | -0.22888 | -0.12817 | -0.22888 | -0.16937 | 0.16937 | -122.0398 | -122.2824 | 0.39368 | 0.32043 | 0.24719 | 0.15106 | 0.07782 | -0.064087 | -122.2137 | -122.4243 | 0.20142 | 0.16022 | 0.10071 | 0.2243 | 0.16479 | 0.2243 | 0.073242 | 0.2655 | 0.16479 | 0.31586 | 0.37537 | 0.48523 | 0.31128 | -122.3557 | -122.5891 | 0.24261 | 0.10071 | 0.30212 | 0.14649
3010.7656 | 122.5525 | -0.3479 | 122.1817 | -0.13267 | 0.024129 | 0.004988 | 0.052882 | 0.0016663 | -0.0039948 | -0.0026704 | -0.0094604 | 0.014039 | 0.017609 | 0.0033711 | -0.031063 | -8.1274e-05 | 0.0022431 | -0.018311 | 0.16937 | -0.16022 | -0.11444 | 0.041199 | -0.10529 | -0.022888 | -0.19226 | -0.004578 | -0.3891 | -0.25635 | -0.13275 | -0.22888 | -0.17853 | 0.18768 | -122.0123 | -122.2961 | 0.3891 | 0.32501 | 0.24261 | 0.13733 | 0.054931 | -0.041199 | -122.1863 | -122.4381 | 0.21515 | 0.16937 | 0.11902 | 0.21057 | 0.16022 | 0.20142 | 0.045776 | 0.25635 | 0.13275 | 0.32959 | 0.38452 | 0.51727 | 0.34332 | -122.3419 | -122.5708 | 0.23346 | 0.091552 | 0.32959 | 0.15564
3011.7656 | 122.5159 | -0.35248 | 122.2 | -0.46074 | 0.025838 | 0.0026382 | 0.055232 | 0.00038452 | -0.0033538 | -0.0041656 | -0.039978 | 0.015748 | 0.019531 | 0.0052937 | -0.028072 | 0.0018413 | 0.0020295 | -0.045776 | 0.1831 | -0.12817 | -0.13275 | -0.059509 | -0.14648 | -0.054932 | -0.2655 | -0.004578 | -0.40283 | -0.27924 | -0.1831 | -0.29297 | -0.20599 | 0.2243 | -122.0169 | -122.3328 | 0.29297 | 0.29755 | 0.20599 | 0.073242 | -0.01831 | -0.050354 | -122.2046 | -122.4792 | 0.16937 | 0.14648 | 0.059509 | 0.19684 | 0.10986 | 0.068665 | -0.004577 | 0.21973 | 0.1236 | 0.31128 | 0.39825 | 0.53558 | 0.3479 | -122.3282 | -122.6028 | 0.21973 | 0.073242 | 0.3067 | 0.086975
3012.7656 | 122.5616 | -0.32044 | 122.2046 | -0.16319 | 0.02477 | 0.0058426 | 0.055019 | 0.00081172 | -0.0012176 | -0.004593 | 0.085144 | 0.014467 | 0.019745 | 0.0067889 | -0.029781 | -8.1274e-05 | 0.0011749 | -0.004578 | 0.17853 | -0.14648 | -0.068665 | 0.036621 | -0.036621 | 0.073242 | -0.16479 | 0.050354 | -0.33417 | -0.22888 | -0.11444 | -0.22888 | -0.16937 | 0.17395 | -122.0261 | -122.2733 | 0.35706 | 0.39368 | 0.28381 | 0.21973 | 0.10986 | -0.013732 | -122.1542 | -122.4335 | 0.20599 | 0.15106 | 0.091553 | 0.16479 | 0.10528 | 0.18311 | 0.077819 | 0.21973 | 0.10528 | 0.32501 | 0.38452 | 0.49896 | 0.37079 | -122.3511 | -122.5388 | 0.25177 | 0.091553 | 0.31586 | 0.15564
3013.7656 | 122.6074 | -0.29297 | 122.2 | -0.16319 | 0.023915 | 0.0069106 | 0.052882 | 0.0010253 | -0.0012176 | -0.0060882 | 0.069885 | 0.016389 | 0.018891 | -0.0028241 | -0.029781 | -0.0026447 | 0.0056611 | 0.004578 | 0.11902 | -0.11444 | -0.022888 | 0.12817 | -0.050354 | 0.041199 | -0.1236 | -0.013733 | -0.35248 | -0.18768 | -0.086975 | -0.17395 | -0.10986 | 0.17853 | -122.081 | -122.2229 | 0.42114 | 0.33417 | 0.24261 | 0.15564 | 0.064087 | -0.059509 | -122.2137 | -122.3877 | 0.20599 | 0.18311 | 0.11902 | 0.24262 | 0.17853 | 0.24262 | 0.091553 | 0.2655 | 0.1648 | 0.23346 | 0.33875 | 0.41199 | 0.27924 | -122.3145 | -122.5525 | 0.27008 | 0.10529 | 0.29755 | 0.16937
3014.8281 | 122.58 | -0.31586 | 122.0764 | -0.20897 | 0.024129 | 0.00392 | 0.054378 | 0.0010253 | -0.0031402 | -0.005661 | -0.0094604 | 0.01468 | 0.019318 | 0.010634 | -0.032772 | -0.00072207 | -0.00032051 | -0.013733 | 0.13275 | -0.12817 | -0.027466 | 0.11902 | -0.068665 | 0.009155 | -0.11902 | -0.045776 | -0.37079 | -0.15564 | -0.059509 | -0.16479 | -0.15106 | 0.18768 | -121.9437 | -122.1039 | 0.43488 | 0.32501 | 0.24719 | 0.13733 | 0.059509 | -0.054932 | -122.1222 | -122.2321 | 0.25635 | 0.16479 | 0.15106 | 0.21973 | 0.20599 | 0.24719 | 0.10071 | 0.31128 | 0.21515 | 0.26093 | 0.32501 | 0.44861 | 0.27008 | -122.2046 | -122.4472 | 0.28839 | 0.16022 | 0.30212 | 0.19684
3015.7656 | 122.5479 | -0.32501 | 122.2 | -0.14793 | 0.024556 | 0.006697 | 0.055019 | 0.00059812 | -0.0037812 | -0.003952 | -0.049133 | 0.017885 | 0.020172 | 0.0031573 | -0.033199 | -0.00050847 | -0.0013885 | -0.009155 | 0.18768 | -0.10529 | -0.068665 | 0.059509 | -0.09613 | -0.027466 | -0.20142 | -0.013733 | -0.39368 | -0.25177 | -0.15564 | -0.26093 | -0.19684 | 0.21973 | -122.0123 | -122.2687 | 0.38452 | 0.29755 | 0.22888 | 0.07782 | 0.009156 | -0.068665 | -122.2137 | -122.4518 | 0.16937 | 0.12817 | 0.064087 | 0.19684 | 0.13275 | 0.16479 | 0.036621 | 0.23804 | 0.14191 | 0.29297 | 0.37994 | 0.5127 | 0.31128 | -122.3053 | -122.5937 | 0.25635 | 0.073242 | 0.31586 | 0.1236
3016.7656 | 122.4609 | -0.31586 | 122.3007 | -0.17082 | 0.025197 | 0.0045608 | 0.054805 | 0.0020935 | -0.0031402 | -0.0030976 | -0.018616 | 0.014467 | 0.020172 | 0.0074299 | -0.030636 | -0.0028583 | 0.0024567 | -0.027466 | 0.15564 | -0.15564 | -0.091553 | 0.050354 | -0.09613 | -0.032043 | -0.18768 | -0.036621 | -0.39368 | -0.23346 | -0.12817 | -0.24261 | -0.09613 | 0.16022 | -122.1451 | -122.3923 | 0.36621 | 0.28381 | 0.21973 | 0.1236 | 0.05951 | -0.07782 | -122.3373 | -122.5342 | 0.18768 | 0.21973 | 0.073242 | 0.29755 | 0.15106 | 0.20599 | 0.064087 | 0.2655 | 0.16022 | 0.31128 | 0.35706 | 0.4715 | 0.27924 | -122.4564 | -122.6944 | 0.2243 | 0.082398 | 0.28839 | 0.12817
3017.7656 | 122.5479 | -0.33875 | 122.2275 | -0.10979 | 0.023488 | 0.004988 | 0.05395 | -0.0011109 | -0.0007904 | -0.0024566 | -0.00030524 | 0.012971 | 0.019318 | 0.0052937 | -0.031277 | 0.00055973 | 0.0035247 | -0.032043 | 0.16937 | -0.16022 | -0.091553 | 0.036621 | -0.086975 | -0.009155 | -0.20142 | -0.032043 | -0.39825 | -0.24261 | -0.11444 | -0.23804 | -0.16937 | 0.17853 | -122.0581 | -122.319 | 0.37537 | 0.32959 | 0.25177 | 0.15106 | 0.073242 | -0.059509 | -122.2595 | -122.4701 | 0.2243 | 0.16937 | 0.10071 | 0.22888 | 0.16022 | 0.19684 | 0.068664 | 0.28381 | 0.15564 | 0.32959 | 0.36621 | 0.50812 | 0.3067 | -122.3877 | -122.6257 | 0.24719 | 0.09613 | 0.3067 | 0.13733
3018.7656 | 122.5388 | -0.34332 | 122.2092 | -0.15556 | 0.023701 | 0.0058426 | 0.052455 | 0.0020935 | -0.0022858 | -0.0041656 | -0.033874 | 0.015107 | 0.018677 | 0.0031573 | -0.03149 | 0.00034613 | 0.0056611 | -0.059509 | 0.17853 | -0.1236 | -0.15564 | -0.045776 | -0.16022 | -0.073242 | -0.28839 | -0.013733 | -0.40283 | -0.28381 | -0.19226 | -0.31586 | -0.20142 | 0.21973 | -122.0306 | -122.3648 | 0.29755 | 0.27008 | 0.18311 | 0.050354 | -0.036621 | -0.059509 | -122.2229 | -122.493 | 0.15106 | 0.14191 | 0.027466 | 0.20142 | 0.086975 | 0.07782 | -0.032044 | 0.21057 | 0.11902 | 0.30212 | 0.3891 | 0.52185 | 0.32959 | -122.3328 | -122.612 | 0.18768 | 0.05951 | 0.28381 | 0.054932
3019.7656 | 122.5388 | -0.35248 | 122.2183 | -0.14793 | 0.021565 | 0.0069106 | 0.054164 | 0.0020935 | -0.002713 | -0.002884 | -0.030823 | 0.016389 | 0.022522 | 0.0072163 | -0.031063 | 0.00013253 | 0.0045929 | -0.027466 | 0.16022 | -0.14648 | -0.09613 | 0.022888 | -0.12817 | -0.027466 | -0.21973 | -0.022888 | -0.40283 | -0.2655 | -0.1831 | -0.28381 | -0.19684 | 0.20599 | -122.0581 | -122.3145 | 0.37537 | 0.32501 | 0.2243 | 0.11902 | 0.01831 | -0.050354 | -122.2412 | -122.4838 | 0.16937 | 0.15564 | 0.068665 | 0.20599 | 0.11902 | 0.16937 | 0.050354 | 0.21973 | 0.13733 | 0.3067 | 0.37994 | 0.5127 | 0.32959 | -122.3648 | -122.6212 | 0.25635 | 0.086975 | 0.32501 | 0.13275
3020.7656 | 122.5479 | -0.36621 | 122.2 | -0.12505 | 0.02477 | 0.0047744 | 0.054591 | 0.0012391 | -0.0024994 | -0.0052338 | -0.036926 | 0.015107 | 0.019104 | 0.0080707 | -0.031063 | 0.00034613 | 0.0020295 | -0.004578 | 0.15564 | -0.14191 | -0.091553 | 0.036621 | -0.11444 | -0.022888 | -0.20599 | -0.022888 | -0.3891 | -0.26093 | -0.16937 | -0.29755 | -0.20142 | 0.2243 | -122.0444 | -122.2916 | 0.40283 | 0.34332 | 0.25177 | 0.11902 | 0.027466 | -0.022888 | -122.2229 | -122.4609 | 0.19684 | 0.16479 | 0.068665 | 0.18768 | 0.091553 | 0.17853 | 0.050354 | 0.21973 | 0.12817 | 0.29755 | 0.36621 | 0.52185 | 0.34332 | -122.3419 | -122.5891 | 0.27466 | 0.10529 | 0.36163 | 0.16022
3021.7656 | 122.5525 | -0.3479 | 122.2 | -0.20134 | 0.023701 | 0.006697 | 0.055446 | -0.0013245 | -0.0020722 | -0.0067292 | -0.012512 | 0.014894 | 0.017395 | 0.0031573 | -0.032986 | -0.00029487 | 0.0033111 | -0.018311 | 0.19226 | -0.11902 | -0.068665 | 0.064087 | -0.10529 | -0.032043 | -0.20142 | -0.018311 | -0.40283 | -0.25635 | -0.15564 | -0.28381 | -0.17395 | 0.22888 | -122.0078 | -122.2687 | 0.41199 | 0.31586 | 0.24261 | 0.086976 | 0.013733 | -0.054932 | -122.2183 | -122.4564 | 0.19226 | 0.17395 | 0.064087 | 0.22888 | 0.11902 | 0.18311 | 0.050354 | 0.24719 | 0.14648 | 0.31128 | 0.38452 | 0.54016 | 0.32959 | -122.319 | -122.6028 | 0.27924 | 0.091552 | 0.32959 | 0.14648
3022.7656 | 122.5616 | -0.3479 | 122.2137 | -0.025863 | 0.025838 | 0.0058426 | 0.053737 | 0.0027343 | -0.0022858 | -0.0041656 | -0.024719 | 0.014253 | 0.019531 | 0.0080707 | -0.029568 | -0.00072207 | 0.00096129 | 0 | 0.21973 | -0.045776 | -0.064087 | 0.064087 | -0.10986 | -0.009155 | -0.17395 | -0.022888 | -0.39825 | -0.24719 | -0.14191 | -0.26093 | -0.1831 | 0.30212 | -121.994 | -122.2778 | 0.41199 | 0.33874 | 0.23804 | 0.036621 | -0.064087 | -0.050354 | -122.2366 | -122.4609 | 0.20599 | 0.16479 | 0.086975 | 0.21515 | 0.13733 | 0.10986 | -0.018311 | 0.25635 | 0.15106 | 0.2655 | 0.37537 | 0.56763 | 0.32501 | -122.2595 | -122.612 | 0.28381 | 0.10071 | 0.3479 | 0.17395
3023.7656 | 122.5616 | -0.3479 | 122.1909 | -0.079269 | 0.021992 | 0.004988 | 0.054591 | 0.0035889 | -0.0035674 | -0.001175 | 0.011902 | 0.01468 | 0.020813 | 0.0074299 | -0.030849 | -0.0013629 | 0.0043793 | -0.045776 | 0.17853 | -0.16022 | -0.10529 | 0.027466 | -0.10529 | -0.027466 | -0.20599 | -0.022888 | -0.39825 | -0.24261 | -0.14191 | -0.25177 | -0.17395 | 0.18768 | -122.0123 | -122.2961 | 0.37537 | 0.32043 | 0.24261 | 0.13275 | 0.054931 | -0.050354 | -122.2137 | -122.4335 | 0.20599 | 0.17395 | 0.09613 | 0.2243 | 0.14648 | 0.18768 | 0.054931 | 0.25635 | 0.15564 | 0.33874 | 0.37537 | 0.52643 | 0.32501 | -122.3511 | -122.5891 | 0.24261 | 0.10528 | 0.30212 | 0.14191
3024.7656 | 122.5616 | -0.33417 | 122.2092 | -0.13267 | 0.02477 | 0.0052018 | 0.052455 | -0.0017517 | -0.0016448 | -0.0035248 | -0.088806 | 0.014467 | 0.017395 | 0.0091389 | -0.030849 | -0.0013629 | 0.0016021 | -0.032043 | 0.16937 | -0.14648 | -0.086975 | 0.050354 | -0.10071 | 0.009155 | -0.09613 | 0.013733 | -0.32501 | -0.23346 | -0.10071 | -0.23804 | -0.16937 | 0.18768 | -122.0398 | -122.2961 | 0.38452 | 0.34332 | 0.23346 | 0.15564 | 0.045776 | 0.009155 | -122.1954 | -122.4426 | 0.23346 | 0.16479 | 0.09613 | 0.15564 | 0.086975 | 0.19684 | 0.059509 | 0.2243 | 0.091553 | 0.31586 | 0.33875 | 0.50354 | 0.3479 | -122.3557 | -122.5342 | 0.24719 | 0.10071 | 0.30212 | 0.23804
3025.8281 | 122.5342 | -0.35248 | 122.2229 | -0.13267 | 0.02242 | 0.0058426 | 0.054805 | 0.0023071 | -0.0033538 | -0.0026704 | -0.015564 | 0.017457 | 0.021027 | 0.0025165 | -0.031277 | 0.0012005 | 0.0024567 | -0.032043 | 0.13275 | -0.13733 | -0.091553 | 0.036621 | -0.11444 | -0.036621 | -0.21973 | -0.032043 | -0.39825 | -0.27466 | -0.16479 | -0.29297 | -0.19684 | 0.21515 | -122.0901 | -122.3145 | 0.3891 | 0.31586 | 0.23804 | 0.10071 | 0.022888 | -0.045776 | -122.2549 | -122.4976 | 0.18768 | 0.15564 | 0.059509 | 0.20142 | 0.10529 | 0.17395 | 0.045776 | 0.23346 | 0.1236 | 0.27008 | 0.36621 | 0.48523 | 0.32044 | -122.3602 | -122.6212 | 0.26093 | 0.07782 | 0.32044 | 0.13275
3026.7656 | 122.5754 | -0.3479 | 122.2229 | -0.11742 | 0.02477 | 0.0075516 | 0.051601 | 0.0038025 | -0.0029266 | -0.0024566 | -0.027771 | 0.015321 | 0.020172 | 0.0065753 | -0.030849 | -0.00050847 | 0.00010689 | -0.027466 | 0.16479 | -0.17853 | -0.10529 | 0.041199 | -0.086975 | -0.018311 | -0.18768 | -0.018311 | -0.40741 | -0.23804 | -0.1236 | -0.26093 | -0.17395 | 0.16937 | -122.0581 | -122.3282 | 0.3891 | 0.32959 | 0.26092 | 0.16022 | 0.091553 | -0.05951 | -122.2412 | -122.4609 | 0.2243 | 0.17395 | 0.086975 | 0.23346 | 0.14648 | 0.21973 | 0.073242 | 0.28381 | 0.16937 | 0.34332 | 0.3891 | 0.5127 | 0.32959 | -122.4014 | -122.6303 | 0.24261 | 0.10986 | 0.32043 | 0.16022
3027.7656 | 122.5616 | -0.35706 | 122.2183 | -0.15556 | 0.023701 | 0.0043472 | 0.054378 | -0.0030335 | -0.0016448 | -0.0026704 | -0.018616 | 0.015535 | 0.021668 | 0.0023029 | -0.030849 | 0.00034613 | 0.0030975 | -0.018311 | 0.14648 | -0.13275 | -0.07782 | 0.082397 | -0.041199 | -0.009155 | -0.17853 | -0.009155 | -0.37537 | -0.24261 | -0.14648 | -0.23804 | -0.16479 | 0.2243 | -122.0718 | -122.2961 | 0.43945 | 0.3479 | 0.31586 | 0.1236 | 0.091552 | -0.01831 | -122.2275 | -122.4609 | 0.21057 | 0.19226 | 0.11902 | 0.21057 | 0.13733 | 0.21515 | 0.054931 | 0.22888 | 0.13275 | 0.27924 | 0.36621 | 0.50354 | 0.3479 | -122.3511 | -122.5937 | 0.27924 | 0.11444 | 0.33874 | 0.17853
3028.7656 | 122.58 | -0.3067 | 122.2275 | -0.12505 | 0.023701 | 0.0041336 | 0.054591 | 0.00038452 | -0.0014312 | -0.0035248 | -0.055237 | 0.013398 | 0.017822 | 0.0087115 | -0.033626 | -0.00029487 | -0.00032051 | -0.009155 | 0.17853 | -0.14191 | -0.07782 | 0.036621 | -0.09613 | 0.036621 | -0.13275 | 0.004578 | -0.33417 | -0.23346 | -0.13275 | -0.24261 | -0.16022 | 0.16479 | -122.049 | -122.3053 | 0.34332 | 0.34332 | 0.21057 | 0.17853 | 0.045777 | -0.027465 | -122.2229 | -122.4609 | 0.17395 | 0.14648 | 0.064087 | 0.17395 | 0.091552 | 0.17853 | 0.064087 | 0.20142 | 0.10071 | 0.32044 | 0.33875 | 0.48523 | 0.31128 | -122.3694 | -122.5616 | 0.22888 | 0.073243 | 0.29755 | 0.17395
3029.8281 | 122.5479 | -0.37537 | 122.2321 | -0.20134 | 0.024129 | 0.0058426 | 0.053737 | -0.0019653 | -0.0022858 | -0.0030976 | -0.018616 | 0.015962 | 0.019531 | 0.0012347 | -0.031704 | -0.0013629 | 0.0026703 | 0.059509 | 0.18768 | -0.16937 | -0.19226 | 0.004578 | -0.11444 | -0.10529 | -0.28839 | -0.009155 | -0.40283 | -0.30212 | -0.18768 | -0.32959 | -0.21057 | 0.20599 | -122.0444 | -122.4243 | 0.37994 | 0.27008 | 0.26092 | 0.064087 | 0.054932 | -0.027466 | -122.2412 | -122.5342 | 0.18768 | 0.16479 | 0.045776 | 0.19226 | 0.073242 | 0.17395 | -0.022888 | 0.21515 | 0.10071 | 0.35706 | 0.39368 | 0.56305 | 0.36621 | -122.4014 | -122.6349 | 0.1831 | 0.073242 | 0.43487 | 0.086975
3030.7656 | 122.5342 | -0.3479 | 122.2504 | -0.18608 | 0.022633 | 0.0034928 | 0.054378 | -0.0013245 | -0.0050628 | -0.0041656 | 0.036316 | 0.015748 | 0.020386 | 0.0025165 | -0.029995 | -0.00093567 | 0.00074769 | -0.10986 | 0.19684 | -0.15564 | -0.09613 | 0.009155 | -0.15564 | -0.022888 | -0.27924 | 0.009155 | -0.39368 | -0.31128 | -0.16937 | -0.29297 | -0.21057 | 0.19226 | -122.0535 | -122.3465 | 0.35706 | 0.32501 | 0.19226 | 0.13275 | 0 | -0.045777 | -122.2412 | -122.5616 | 0.17853 | 0.13733 | 0.054931 | 0.18311 | 0.10071 | 0.16479 | 0.05951 | 0.2243 | 0.082398 | 0.35248 | 0.40283 | 0.54474 | 0.35706 | -122.406 | -122.644 | 0.25177 | 0.036621 | 0.23804 | 0.068664
3031.7656 | 122.5296 | -0.37079 | 122.2275 | -0.1403 | 0.021779 | 0.0030654 | 0.055446 | -0.00068368 | -0.0018586 | -0.002884 | 0.033264 | 0.015748 | 0.019745 | -4.6942e-05 | -0.031704 | -0.0011493 | 0.0026703 | -0.059509 | 0.1831 | -0.15564 | -0.13275 | -0.013733 | -0.12817 | -0.036621 | -0.27466 | -0.013733 | -0.4303 | -0.32044 | -0.17395 | -0.29297 | -0.20599 | 0.21515 | -122.0444 | -122.3602 | 0.35706 | 0.33417 | 0.24261 | 0.11902 | 0.027466 | -0.059509 | -122.2412 | -122.5479 | 0.19684 | 0.16479 | 0.07782 | 0.2243 | 0.13733 | 0.14191 | 0.022889 | 0.25635 | 0.10986 | 0.33874 | 0.41657 | 0.55389 | 0.35706 | -122.3831 | -122.6578 | 0.23804 | 0.050354 | 0.31128 | 0.096131
3032.8281 | 122.5708 | -0.3479 | 122.2229 | -0.20134 | 0.024983 | 0.0043472 | 0.052241 | 0.00059812 | -0.0042084 | -0.0060882 | -0.0064086 | 0.015321 | 0.019318 | 0.012984 | -0.031704 | 0.0016277 | 0.0050201 | -0.018311 | 0.15564 | -0.13733 | -0.073242 | 0.10529 | -0.082397 | -0.004578 | -0.19226 | 0.004578 | -0.36163 | -0.23346 | -0.14648 | -0.25177 | -0.17395 | 0.21057 | -122.0673 | -122.2961 | 0.45319 | 0.34332 | 0.2655 | 0.13275 | 0.054932 | -0.013733 | -122.2183 | -122.4564 | 0.20142 | 0.17395 | 0.09613 | 0.18768 | 0.10986 | 0.24262 | 0.064087 | 0.21515 | 0.12817 | 0.29297 | 0.36621 | 0.50354 | 0.35248 | -122.3602 | -122.5845 | 0.27466 | 0.11444 | 0.32959 | 0.15564
3033.7656 | 122.5754 | -0.35706 | 122.2229 | -0.094528 | 0.023274 | 0.0052018 | 0.051814 | -4.2682e-05 | -0.0042084 | -0.0026704 | 0.027161 | 0.017244 | 0.019318 | 0.0040119 | -0.032986 | -0.0026447 | 0.0043793 | -0.045776 | 0.17853 | -0.16022 | -0.13275 | -0.018311 | -0.11444 | -0.041199 | -0.27466 | -0.041199 | -0.41199 | -0.27466 | -0.15106 | -0.27466 | -0.17853 | 0.19684 | -122.0444 | -122.3557 | 0.33874 | 0.31586 | 0.24261 | 0.11902 | 0.045776 | -0.054931 | -122.2641 | -122.4976 | 0.20599 | 0.17853 | 0.082398 | 0.23346 | 0.13733 | 0.14191 | 0.027466 | 0.26092 | 0.13733 | 0.33874 | 0.37079 | 0.53558 | 0.31586 | -122.3831 | -122.6349 | 0.2243 | 0.082398 | 0.31128 | 0.082398
3034.7656 | 122.5845 | -0.36163 | 122.2412 | -0.10979 | 0.02477 | 0.007338 | 0.054378 | 0.0012391 | -0.0050628 | -0.0043792 | -0.030823 | 0.01703 | 0.018036 | 0.0084979 | -0.0285 | 0.00098693 | 0.0020295 | -0.027466 | 0.16022 | -0.16022 | -0.09613 | 0.041199 | -0.09613 | -0.013733 | -0.20142 | -0.022888 | -0.40741 | -0.25635 | -0.14191 | -0.2655 | -0.17395 | 0.20142 | -122.081 | -122.3373 | 0.40283 | 0.3479 | 0.2655 | 0.14648 | 0.064087 | -0.045777 | -122.2641 | -122.4976 | 0.21973 | 0.18768 | 0.09613 | 0.23346 | 0.14191 | 0.20142 | 0.064087 | 0.2655 | 0.15106 | 0.32043 | 0.38452 | 0.52185 | 0.33874 | -122.4014 | -122.6486 | 0.2655 | 0.10528 | 0.33417 | 0.16022
3035.7656 | 122.5983 | -0.34332 | 122.2183 | -0.14793 | 0.021352 | 0.0058426 | 0.053737 | -0.0038879 | -0.0048492 | -0.005661 | 0.0057984 | 0.014039 | 0.018463 | 0.0025165 | -0.03149 | -0.0015765 | 0.0037385 | -0.041199 | 0.17395 | -0.14648 | -0.11444 | 0.009155 | -0.091553 | -0.027466 | -0.22888 | -0.032043 | -0.39825 | -0.25635 | -0.14648 | -0.25177 | -0.16479 | 0.19684 | -122.0444 | -122.3328 | 0.35248 | 0.31586 | 0.25177 | 0.11902 | 0.054931 | -0.054931 | -122.2504 | -122.4747 | 0.19684 | 0.17853 | 0.091553 | 0.23346 | 0.14648 | 0.15564 | 0.032043 | 0.25177 | 0.14191 | 0.32043 | 0.36621 | 0.51727 | 0.31128 | -122.3648 | -122.6166 | 0.22888 | 0.086975 | 0.30212 | 0.11444
3036.7656 | 122.5891 | -0.35706 | 122.2366 | -0.094528 | 0.026051 | 0.004988 | 0.053523 | -0.0013245 | -0.002713 | -0.002243 | -0.0064086 | 0.016389 | 0.020172 | 0.0067889 | -0.032772 | -0.0024311 | 0.0022431 | -0.045776 | 0.16479 | -0.14648 | -0.11902 | 0.018311 | -0.1236 | -0.045776 | -0.23804 | -0.045776 | -0.42572 | -0.27924 | -0.14191 | -0.26093 | -0.18768 | 0.21057 | -122.0718 | -122.3557 | 0.37537 | 0.31128 | 0.23346 | 0.10071 | 0.022888 | -0.068664 | -122.2824 | -122.5159 | 0.21515 | 0.16937 | 0.096131 | 0.23804 | 0.16479 | 0.16479 | 0.027465 | 0.28381 | 0.14648 | 0.31128 | 0.37994 | 0.52185 | 0.31128 | -122.3831 | -122.6624 | 0.23804 | 0.07782 | 0.31128 | 0.11902
3037.7656 | 122.5708 | -0.33875 | 122.2412 | -0.1403 | 0.023915 | 0.0047744 | 0.053096 | 0.0033753 | -0.0003632 | -0.002243 | -0.021667 | 0.015107 | 0.018677 | 0.0031573 | -0.030849 | -0.00093567 | 0.0011749 | 0 | 0.21973 | -0.09613 | -0.091553 | 0.064087 | -0.086975 | -0.018311 | -0.20142 | -0.045776 | -0.39368 | -0.25635 | -0.16022 | -0.28381 | -0.18768 | 0.24262 | -122.0215 | -122.3328 | 0.40283 | 0.32043 | 0.25177 | 0.077819 | 0.009155 | -0.054932 | -122.287 | -122.4976 | 0.17853 | 0.15106 | 0.054932 | 0.20599 | 0.10986 | 0.16022 | 0.004577 | 0.23346 | 0.13733 | 0.31586 | 0.3479 | 0.55847 | 0.29297 | -122.3373 | -122.6349 | 0.24719 | 0.082397 | 0.33875 | 0.13733
3038.7656 | 122.58 | -0.34332 | 122.2321 | -0.10979 | 0.021992 | 0.0034928 | 0.051814 | 0.0014527 | -0.0024994 | -0.0054474 | 0.018005 | 0.016176 | 0.019531 | 0.00080746 | -0.031277 | -0.00029487 | 0.0022431 | -0.041199 | 0.1831 | -0.15106 | -0.11444 | -0.022888 | -0.11444 | -0.050354 | -0.2655 | -0.009155 | -0.39825 | -0.29755 | -0.1831 | -0.29297 | -0.21057 | 0.19226 | -122.049 | -122.3465 | 0.32043 | 0.29297 | 0.22888 | 0.10071 | 0.036621 | -0.054931 | -122.2412 | -122.5296 | 0.16022 | 0.13275 | 0.050354 | 0.18768 | 0.10529 | 0.12817 | 0.036621 | 0.21515 | 0.10071 | 0.33417 | 0.3891 | 0.52643 | 0.33417 | -122.3831 | -122.6303 | 0.22888 | 0.045777 | 0.30212 | 0.07782
3039.7656 | 122.5937 | -0.33875 | 122.2229 | -0.10216 | 0.023274 | 0.0052018 | 0.054378 | 0.0033753 | -0.0050628 | -0.006302 | 0.0057984 | 0.014894 | 0.020813 | 0.0025165 | -0.030849 | 0.00034613 | 0.0011749 | -0.045776 | 0.16479 | -0.15106 | -0.10071 | 0.022888 | -0.082397 | -0.018311 | -0.21973 | -0.054932 | -0.41199 | -0.27466 | -0.13733 | -0.2655 | -0.17395 | 0.18768 | -122.0581 | -122.3236 | 0.36163 | 0.32043 | 0.25635 | 0.13275 | 0.068665 | -0.073242 | -122.2778 | -122.4976 | 0.20142 | 0.1648 | 0.073242 | 0.23804 | 0.14648 | 0.17395 | 0.050354 | 0.27466 | 0.13733 | 0.31586 | 0.35706 | 0.50354 | 0.28381 | -122.374 | -122.6349 | 0.23804 | 0.064087 | 0.29297 | 0.11902
3040.7656 | 122.5983 | -0.34332 | 122.2458 | -0.18608 | 0.023274 | 0.004988 | 0.052455 | 0.0020935 | -0.0031402 | -0.0080108 | -0.0064086 | 0.016389 | 0.020172 | 0.0037983 | -0.030849 | -0.0022175 | 0.0026703 | -0.050354 | 0.16479 | -0.16937 | -0.13275 | 0.009155 | -0.10986 | -0.027466 | -0.23804 | -0.032043 | -0.40741 | -0.28381 | -0.14191 | -0.27466 | -0.17395 | 0.17395 | -122.081 | -122.3785 | 0.35248 | 0.31586 | 0.23346 | 0.14191 | 0.05951 | -0.064087 | -122.2778 | -122.5296 | 0.20142 | 0.16937 | 0.068665 | 0.23346 | 0.13275 | 0.17853 | 0.036622 | 0.2655 | 0.1236 | 0.33417 | 0.37537 | 0.50812 | 0.31128 | -122.4152 | -122.6532 | 0.21057 | 0.05951 | 0.29297 | 0.10529
3041.7656 | 122.5616 | -0.35706 | 122.2092 | -0.15556 | 0.023061 | 0.0052018 | 0.055019 | 0.00017092 | -0.0031402 | -0.0054474 | 0.011902 | 0.016176 | 0.0206 | 0.0037983 | -0.032558 | -0.0022175 | -0.00053411 | -0.050354 | 0.16937 | -0.14648 | -0.1236 | -0.013733 | -0.11444 | -0.050354 | -0.25177 | -0.036621 | -0.40283 | -0.27924 | -0.14191 | -0.2655 | -0.18768 | 0.21057 | -122.0398 | -122.3328 | 0.34332 | 0.3067 | 0.24261 | 0.09613 | 0.032043 | -0.045776 | -122.2458 | -122.4884 | 0.21515 | 0.16937 | 0.091553 | 0.21515 | 0.13733 | 0.13275 | 0.022888 | 0.26093 | 0.1236 | 0.31586 | 0.36621 | 0.52643 | 0.32043 | -122.3557 | -122.612 | 0.23346 | 0.07782 | 0.3067 | 0.10529
3042.7656 | 122.5891 | -0.36163 | 122.2321 | -0.18608 | 0.023701 | 0.0041336 | 0.053523 | 0.00059812 | -0.0016448 | -0.0043792 | 0.014954 | 0.01703 | 0.019959 | 0.0044391 | -0.032131 | -0.0011493 | 0.0013885 | -0.050354 | 0.16937 | -0.15564 | -0.13733 | -0.013733 | -0.1236 | -0.050354 | -0.25635 | -0.036621 | -0.44403 | -0.29755 | -0.15564 | -0.27008 | -0.20142 | 0.20599 | -122.0627 | -122.3694 | 0.3479 | 0.31128 | 0.23804 | 0.10529 | 0.032044 | -0.082398 | -122.2687 | -122.5296 | 0.20599 | 0.16022 | 0.091552 | 0.24261 | 0.17395 | 0.14191 | 0.018311 | 0.28839 | 0.14649 | 0.32501 | 0.40741 | 0.53101 | 0.32501 | -122.3877 | -122.6761 | 0.2243 | 0.064087 | 0.31128 | 0.10528
3043.7656 | 122.5708 | -0.35248 | 122.2458 | -0.11742 | 0.02477 | 0.004988 | 0.054591 | 0.0033753 | -0.0033538 | -0.0037384 | 0.018005 | 0.013612 | 0.019959 | 0.0048663 | -0.029995 | -0.0020039 | 0.0052337 | -0.050354 | 0.1831 | -0.15564 | -0.13275 | -0.013733 | -0.1236 | -0.036621 | -0.27466 | -0.027466 | -0.41199 | -0.31128 | -0.17853 | -0.27924 | -0.20599 | 0.19684 | -122.0627 | -122.3785 | 0.33875 | 0.31586 | 0.22888 | 0.11902 | 0.032044 | -0.059509 | -122.2733 | -122.5571 | 0.17395 | 0.14648 | 0.073242 | 0.20599 | 0.13275 | 0.14191 | 0.022889 | 0.23346 | 0.10071 | 0.33874 | 0.38452 | 0.53558 | 0.32501 | -122.4014 | -122.6578 | 0.21973 | 0.041199 | 0.30212 | 0.07782
3044.7656 | 122.525 | -0.3479 | 122.2687 | -0.086899 | 0.023488 | 0.0043472 | 0.052669 | 0.0016663 | -0.0035674 | -0.0043792 | -0.079651 | 0.015962 | 0.018891 | -0.00090154 | -0.030849 | -0.00093567 | 0.0016021 | -0.068665 | 0.18768 | -0.15106 | -0.11902 | 0.064087 | 0.21057 | 0.027466 | -0.20142 | 0.018311 | -0.38452 | -0.32044 | -0.16937 | -0.27924 | -0.19684 | 0.19684 | -122.081 | -122.3877 | 0.41199 | 0.37537 | 0.55847 | 0.17853 | 0.36163 | -0.036621 | -122.2504 | -122.5891 | 0.17853 | 0.15106 | 0.068664 | 0.18768 | 0.10529 | 0.21515 | 0.032043 | 0.21515 | 0.064086 | 0.33874 | 0.40283 | 0.53558 | 0.36621 | -122.4197 | -122.6532 | 0.22888 | 0.027465 | 0.27924 | 0.14648
3045.7656 | 122.5754 | -0.36621 | 122.2504 | -0.094528 | 0.02477 | 0.0043472 | 0.05331 | 0.0016663 | -0.0048492 | -0.0065156 | 0.0088502 | 0.015107 | 0.019531 | 0.0035847 | -0.031277 | -0.00072207 | 0.00032049 | -0.050354 | 0.17853 | -0.14648 | -0.1236 | 0 | -0.1236 | -0.032043 | -0.27466 | -0.009155 | -0.41199 | -0.30212 | -0.1831 | -0.29297 | -0.20599 | 0.21973 | -122.0718 | -122.374 | 0.36621 | 0.33417 | 0.24262 | 0.11444 | 0.022888 | -0.045776 | -122.2595 | -122.5525 | 0.18311 | 0.16022 | 0.073242 | 0.20599 | 0.11902 | 0.14648 | 0.022888 | 0.22888 | 0.10986 | 0.32501 | 0.40283 | 0.54474 | 0.35706 | -122.3969 | -122.6624 | 0.24262 | 0.064087 | 0.31586 | 0.091553
3046.7656 | 122.6395 | -0.29297 | 122.2092 | -0.23949 | 0.025197 | 0.0077652 | 0.052028 | -0.0013245 | -0.0003632 | -0.0020294 | 0.057678 | 0.015748 | 0.020172 | -4.6942e-05 | -0.03149 | -0.00029487 | -0.00032051 | 0.004578 | 0.12817 | -0.11902 | -0.027466 | 0.12817 | -0.050354 | 0.041199 | -0.13275 | -0.054932 | -0.37994 | -0.20599 | -0.091553 | -0.19226 | -0.11902 | 0.17395 | -122.081 | -122.2366 | 0.42114 | 0.33417 | 0.24261 | 0.16022 | 0.068665 | -0.086975 | -122.2641 | -122.4152 | 0.20142 | 0.17395 | 0.10071 | 0.26093 | 0.18768 | 0.24719 | 0.091553 | 0.28839 | 0.17395 | 0.24719 | 0.32501 | 0.42114 | 0.23804 | -122.3282 | -122.5891 | 0.2655 | 0.086975 | 0.29755 | 0.16022
3047.7656 | 122.5891 | -0.32044 | 122.2366 | -0.1403 | 0.024556 | 0.0041336 | 0.056514 | 0.0025207 | -0.0024994 | -0.0030976 | -0.058289 | 0.015962 | 0.016968 | 0.0070027 | -0.032558 | -0.0011493 | -0.00096131 | -0.004578 | 0.16022 | -0.13275 | -0.07782 | 0.054932 | -0.082397 | -0.013733 | -0.20599 | 0 | -0.32501 | -0.25177 | -0.1236 | -0.23346 | -0.1831 | 0.18768 | -122.0764 | -122.3145 | 0.37537 | 0.3067 | 0.23804 | 0.11902 | 0.050354 | -0.004577 | -122.2366 | -122.4884 | 0.19684 | 0.13733 | 0.086976 | 0.14191 | 0.091553 | 0.18768 | 0.054931 | 0.20142 | 0.073242 | 0.29297 | 0.32501 | 0.48065 | 0.32044 | -122.3694 | -122.5616 | 0.24262 | 0.068665 | 0.31586 | 0.11444
3048.8281 | 122.5983 | -0.33417 | 122.2229 | -0.13267 | 0.024129 | 0.0043472 | 0.054378 | 0.0027343 | -0.0042084 | -0.0033112 | -0.046081 | 0.015535 | 0.017609 | 0.0078571 | -0.032986 | -0.0020039 | -0.00032051 | -0.022888 | 0.16479 | -0.15564 | -0.036621 | 0.059509 | -0.050354 | 0.018311 | -0.16937 | 0 | -0.35248 | -0.24719 | -0.14648 | -0.25177 | -0.16937 | 0.17853 | -122.0581 | -122.2595 | 0.39368 | 0.35248 | 0.28381 | 0.17395 | 0.10529 | -0.018311 | -122.2229 | -122.4701 | 0.18768 | 0.16479 | 0.082397 | 0.18311 | 0.10071 | 0.21515 | 0.11902 | 0.20599 | 0.10529 | 0.32044 | 0.35248 | 0.49896 | 0.33417 | -122.3785 | -122.5754 | 0.29755 | 0.086975 | 0.31128 | 0.16479
3049.7656 | 122.5525 | -0.35706 | 122.2595 | -0.1403 | 0.021138 | 0.006697 | 0.054378 | -0.0036743 | -0.0018586 | -0.004593 | 0.014954 | 0.013185 | 0.019745 | 0.0048663 | -0.030422 | -0.0013629 | 0.0030975 | -0.054932 | 0.20599 | -0.13733 | -0.12817 | 0.004578 | -0.1236 | -0.045776 | -0.27924 | -0.022888 | -0.41657 | -0.31128 | -0.1831 | -0.30212 | -0.22888 | 0.21973 | -122.0535 | -122.3877 | 0.36163 | 0.31128 | 0.23346 | 0.091553 | 0.013733 | -0.059509 | -122.2824 | -122.5708 | 0.17395 | 0.12817 | 0.054932 | 0.18768 | 0.11444 | 0.14191 | 0.009155 | 0.23346 | 0.10529 | 0.34332 | 0.39368 | 0.56305 | 0.33417 | -122.3969 | -122.6761 | 0.22888 | 0.045777 | 0.30212 | 0.07782
3050.7656 | 122.612 | -0.35706 | 122.2549 | -0.20134 | 0.023701 | 0.0052018 | 0.053096 | -4.2682e-05 | -0.0029266 | -0.0037384 | -0.0094604 | 0.014467 | 0.019531 | -0.00068794 | -0.033626 | -0.00072207 | 0.0013885 | -0.045776 | 0.16937 | -0.14191 | -0.11444 | 0 | -0.11444 | -0.036621 | -0.24719 | -0.032043 | -0.41657 | -0.27008 | -0.13733 | -0.27008 | -0.17853 | 0.21515 | -122.0856 | -122.3694 | 0.35706 | 0.32043 | 0.24261 | 0.10529 | 0.027466 | -0.059509 | -122.287 | -122.525 | 0.21973 | 0.17853 | 0.086975 | 0.23804 | 0.14648 | 0.14191 | 0.027466 | 0.27924 | 0.14648 | 0.31128 | 0.38452 | 0.52643 | 0.32501 | -122.3969 | -122.6715 | 0.24261 | 0.086975 | 0.31128 | 0.10986
3051.7656 | 122.5433 | -0.37537 | 122.2595 | -0.15556 | 0.025838 | 0.0062698 | 0.05395 | 0.0067933 | -0.0033538 | 0.00010684 | -0.052185 | 0.01468 | 0.018891 | 0.0042255 | -0.032345 | -0.00072207 | 0.0041657 | -0.050354 | 0.15106 | -0.16022 | -0.1236 | -0.013733 | -0.14648 | -0.068665 | -0.27466 | -0.027466 | -0.41199 | -0.31586 | -0.19684 | -0.33875 | -0.23346 | 0.21515 | -122.1085 | -122.3831 | 0.36163 | 0.3067 | 0.22888 | 0.091552 | 0.013733 | -0.036621 | -122.287 | -122.5754 | 0.17853 | 0.14191 | 0.036621 | 0.17853 | 0.073242 | 0.14648 | 0.036621 | 0.21515 | 0.09613 | 0.31128 | 0.38452 | 0.52643 | 0.3479 | -122.4197 | -122.6715 | 0.25177 | 0.059509 | 0.32501 | 0.10071
3052.8281 | 122.5845 | -0.32959 | 122.2458 | -0.1403 | 0.023915 | 0.0071244 | 0.052669 | 0.0029479 | -0.0033538 | -0.0060882 | -0.052185 | 0.014039 | 0.019531 | 0.0033711 | -0.030422 | -0.00029487 | 0.0018159 | -0.018311 | 0.16022 | -0.15106 | 0.054932 | 0.07782 | 0.073242 | 0 | -0.14191 | 0.018311 | -0.35248 | -0.24261 | -0.14191 | -0.24719 | -0.16479 | 0.17853 | -122.0856 | -122.1909 | 0.40741 | 0.32959 | 0.40283 | 0.15106 | 0.2243 | -0.022888 | -122.2275 | -122.4884 | 0.18768 | 0.16479 | 0.082398 | 0.18768 | 0.10529 | 0.22888 | 0.20599 | 0.21057 | 0.10986 | 0.31128 | 0.37079 | 0.48981 | 0.3479 | -122.3969 | -122.5983 | 0.38452 | 0.086975 | 0.31128 | 0.18768
3053.7656 | 122.6166 | -0.36163 | 122.2504 | -0.12505 | 0.022847 | 0.0071244 | 0.052028 | 0.00081172 | -0.0020722 | -0.0026704 | 0.0088502 | 0.014467 | 0.018677 | 0.0046527 | -0.031277 | -0.00050847 | 0.00032049 | -0.045776 | 0.19226 | -0.15564 | -0.11902 | -0.009155 | -0.1236 | -0.036621 | -0.2655 | -0.050354 | -0.41199 | -0.28381 | -0.16022 | -0.27008 | -0.17853 | 0.20599 | -122.0581 | -122.3694 | 0.35248 | 0.32501 | 0.23804 | 0.11902 | 0.032044 | -0.050354 | -122.3007 | -122.5342 | 0.20142 | 0.1831 | 0.091552 | 0.23346 | 0.14191 | 0.14649 | 0.036621 | 0.25177 | 0.12817 | 0.3479 | 0.36163 | 0.55389 | 0.31128 | -122.406 | -122.6624 | 0.24261 | 0.07782 | 0.31586 | 0.09613
3054.7656 | 122.5754 | -0.27924 | 122.2687 | -0.15556 | 0.023488 | 0.005629 | 0.055019 | 0.0057251 | -0.002713 | -0.0024566 | -0.036926 | 0.013826 | 0.018463 | 0.0046527 | -0.027004 | -0.0011493 | 0.00074769 | -0.013733 | 0.16479 | -0.14191 | -0.07782 | 0.054932 | -0.10071 | -0.022888 | -0.18768 | -0.059509 | -0.3891 | -0.25177 | -0.073242 | -0.25177 | -0.1831 | 0.13733 | -122.1039 | -122.3465 | 0.33417 | 0.25635 | 0.17853 | 0.11902 | 0.041199 | -0.10986 | -122.3282 | -122.5204 | 0.20599 | 0.096131 | 0.027466 | 0.20599 | 0.13733 | 0.19684 | 0.064087 | 0.31586 | 0.13733 | 0.3067 | 0.32959 | 0.44403 | 0.21973 | -122.4106 | -122.6578 | 0.20142 | 0.027466 | 0.2655 | 0.091553
3055.7656 | 122.58 | -0.27466 | 122.3053 | -0.1403 | 0.024129 | 0.0064834 | 0.054164 | 0.0014527 | -0.0024994 | -0.0030976 | -0.0064086 | 0.016816 | 0.018677 | 0.01042 | -0.029354 | -0.0013629 | 0.0018159 | -0.018311 | 0.15564 | -0.14648 | -0.073242 | 0.054932 | -0.10529 | -0.013733 | -0.1831 | -0.032043 | -0.40283 | -0.17853 | -0.09613 | -0.1831 | -0.13733 | 0.12817 | -122.1497 | -122.3785 | 0.32959 | 0.26093 | 0.16937 | 0.13275 | 0.041198 | -0.12817 | -122.3373 | -122.4838 | 0.17853 | 0.13733 | 0.091553 | 0.2655 | 0.21973 | 0.20142 | 0.073242 | 0.3067 | 0.2243 | 0.30212 | 0.37079 | 0.4303 | 0.24262 | -122.4518 | -122.7081 | 0.20142 | 0.09613 | 0.25635 | 0.091553
3056.8438 | 122.6807 | -0.32959 | 122.2275 | -0.2166 | 0.02477 | 0.0034928 | 0.051387 | 0.0025207 | -0.001004 | -0.0037384 | 0.097351 | 0.014253 | 0.020813 | -0.0060283 | -0.029995 | -0.0015765 | -0.00053411 | -0.054932 | 0.11902 | -0.13733 | -0.086975 | 0.054932 | -0.07782 | 0.041199 | -0.21515 | -0.036621 | -0.39368 | -0.2243 | -0.086975 | -0.17853 | -0.10986 | 0.19226 | -122.1085 | -122.3145 | 0.38452 | 0.37079 | 0.25177 | 0.17853 | 0.059509 | -0.064087 | -122.2641 | -122.4518 | 0.24261 | 0.21973 | 0.15106 | 0.28381 | 0.21515 | 0.19226 | 0.050354 | 0.3067 | 0.16937 | 0.25635 | 0.35706 | 0.44861 | 0.29297 | -122.3648 | -122.6212 | 0.24261 | 0.10529 | 0.27466 | 0.11444
3057.7656 | 122.6074 | -0.36163 | 122.2458 | -0.16319 | 0.025197 | 0.0045608 | 0.052241 | -0.00025628 | -0.0042084 | 0.00010684 | -0.0064086 | 0.015748 | 0.019318 | 0.0037983 | -0.030209 | 0.00034613 | 0.0011749 | -0.041199 | 0.15564 | -0.15106 | -0.11902 | -0.022888 | -0.1236 | -0.032043 | -0.2655 | -0.045776 | -0.41657 | -0.27008 | -0.18768 | -0.2655 | -0.17853 | 0.21057 | -122.0901 | -122.3648 | 0.33874 | 0.32959 | 0.23804 | 0.11902 | 0.027466 | -0.054932 | -122.2916 | -122.5159 | 0.17395 | 0.1831 | 0.09613 | 0.23804 | 0.15106 | 0.12817 | 0.032043 | 0.22888 | 0.14648 | 0.3067 | 0.37079 | 0.51727 | 0.31586 | -122.3969 | -122.6624 | 0.24261 | 0.091552 | 0.32043 | 0.09613
3058.7656 | 122.6074 | -0.36621 | 122.2549 | -0.13267 | 0.02477 | 0.0047744 | 0.053737 | 0.00081172 | -0.0037812 | -0.0030976 | -0.0064086 | 0.016603 | 0.019531 | 0.0037983 | -0.031063 | -0.0015765 | 0.0018159 | -0.059509 | 0.16937 | -0.16479 | -0.11902 | 0 | -0.11902 | -0.050354 | -0.2655 | -0.027466 | -0.41657 | -0.28839 | -0.16479 | -0.27466 | -0.19684 | 0.20142 | -122.0856 | -122.374 | 0.36621 | 0.31586 | 0.24719 | 0.11444 | 0.045776 | -0.050354 | -122.2824 | -122.5433 | 0.20142 | 0.16937 | 0.091553 | 0.21973 | 0.14191 | 0.16479 | 0.045776 | 0.25177 | 0.12817 | 0.33417 | 0.3891 | 0.53558 | 0.33875 | -122.4197 | -122.6715 | 0.24719 | 0.07782 | 0.3067 | 0.10071
3059.7656 | 122.5342 | -0.31128 | 122.3053 | -0.13267 | 0.023701 | 0.003279 | 0.054591 | 0.0020935 | -0.0020722 | -0.0037384 | -0.036926 | 0.015535 | 0.022309 | 0.0065753 | -0.030209 | 0.0022687 | -0.00010671 | -0.036621 | 0.15564 | -0.13275 | -0.07782 | 0.045776 | -0.1236 | -0.032043 | -0.20142 | -0.022888 | -0.39825 | -0.2655 | -0.16937 | -0.26093 | -0.054932 | 0.17853 | -122.1497 | -122.3831 | 0.35705 | 0.27924 | 0.18768 | 0.10071 | 0.009155 | -0.086975 | -122.3282 | -122.5708 | 0.14191 | 0.25635 | 0.050354 | 0.34332 | 0.13733 | 0.17853 | 0.054931 | 0.22888 | 0.13275 | 0.28839 | 0.37537 | 0.46692 | 0.28839 | -122.438 | -122.7036 | 0.23346 | 0.045776 | 0.27466 | 0.10986
3060.8281 | 122.5937 | -0.35706 | 122.2641 | -0.20134 | 0.02477 | 0.0043472 | 0.055232 | 0.0016663 | -0.0042084 | -0.002884 | -0.04303 | 0.015535 | 0.017822 | 0.0055073 | -0.030422 | -0.0022175 | 0.00074769 | -0.036621 | 0.15106 | -0.15106 | -0.091553 | 0.027466 | -0.10071 | -0.041199 | -0.21973 | -0.022888 | -0.39368 | -0.27008 | -0.16022 | -0.30212 | -0.17853 | 0.20599 | -122.113 | -122.3557 | 0.38452 | 0.31586 | 0.25635 | 0.10986 | 0.050354 | -0.036621 | -122.287 | -122.5342 | 0.19684 | 0.17853 | 0.054932 | 0.21515 | 0.091553 | 0.17853 | 0.059509 | 0.23346 | 0.1236 | 0.30212 | 0.37079 | 0.50812 | 0.33417 | -122.4152 | -122.6578 | 0.2655 | 0.086975 | 0.32043 | 0.13733

## Thermal Data
Fire Time | North 25 C | Conduit Top | Conduit Bottom | TC Cable
-0.3396 | 22.6846 | 21.6321 | 21.7901 | 21.1644
0.6604 | 22.6873 | 21.6369 | 21.7847 | 21.1668
1.6604 | 22.6817 | 21.6332 | 21.7843 | 21.1679
2.6604 | 22.6992 | 21.6298 | 21.7876 | 21.1678
3.6604 | 22.9945 | 21.6183 | 21.7849 | 21.1587
4.6604 | 24.0273 | 21.6348 | 21.794 | 21.1626
5.6604 | 25.8174 | 21.6398 | 21.7952 | 21.1692
6.6604 | 28.2993 | 21.6481 | 21.8123 | 21.1666
7.6604 | 31.3431 | 21.6568 | 21.8205 | 21.163
8.6604 | 34.8504 | 21.6693 | 21.8368 | 21.1665
9.6604 | 38.741 | 21.6767 | 21.843 | 21.1566
10.6604 | 42.9438 | 21.6943 | 21.8663 | 21.1667
11.6604 | 47.406 | 21.7167 | 21.8875 | 21.1642
12.6604 | 52.1097 | 21.7445 | 21.912 | 21.1545
13.6604 | 57.0321 | 21.7685 | 21.9502 | 21.1682
14.6604 | 62.1167 | 21.7996 | 21.978 | 21.1613
15.6604 | 67.2934 | 21.8449 | 22.0062 | 21.1627
16.6604 | 72.6688 | 21.8976 | 22.0594 | 21.1673
17.6604 | 78.1532 | 21.9512 | 22.1037 | 21.1674
18.6604 | 83.6695 | 21.9996 | 22.1512 | 21.167
19.6604 | 89.3692 | 22.0856 | 22.1988 | 21.1654
20.6604 | 95.1808 | 22.1611 | 22.253 | 21.1654
21.6604 | 101.0199 | 22.248 | 22.3034 | 21.1686
22.6604 | 106.9128 | 22.3468 | 22.3767 | 21.1697
23.6604 | 112.9036 | 22.4875 | 22.4653 | 21.1655
24.6604 | 118.849 | 22.5468 | 22.5502 | 21.17
25.6604 | 124.873 | 22.6319 | 22.6218 | 21.1654
26.6604 | 131.0052 | 22.7191 | 22.7026 | 21.1709
27.6604 | 137.0631 | 22.8232 | 22.7866 | 21.1656
28.6604 | 143.0405 | 22.9802 | 22.8856 | 21.1696
29.6604 | 149.092 | 23.0909 | 22.997 | 21.1642
30.6604 | 155.0526 | 23.242 | 23.1545 | 21.175
31.6604 | 161.0397 | 23.3888 | 23.3151 | 21.1744
32.6604 | 167.0603 | 23.5132 | 23.4135 | 21.1725
33.6604 | 173.1312 | 23.7069 | 23.5498 | 21.1744
34.6604 | 179.1962 | 23.9221 | 23.6916 | 21.1734
35.6604 | 185.2764 | 24.1568 | 23.8372 | 21.1792
36.6604 | 191.3626 | 24.3443 | 24.0168 | 21.1821
37.6604 | 197.3549 | 24.5688 | 24.326 | 21.1832
38.6604 | 203.3895 | 24.7487 | 24.4646 | 21.1841
39.6604 | 209.4078 | 24.9606 | 24.6532 | 21.1818
40.6604 | 215.4289 | 25.1817 | 24.8904 | 21.1892
41.6604 | 221.3677 | 25.4806 | 25.1526 | 21.1986
42.6604 | 227.4127 | 25.7361 | 25.3858 | 21.2017
43.6604 | 233.3991 | 26.015 | 25.5555 | 21.2004
44.6604 | 239.3561 | 26.3318 | 25.786 | 21.2045
45.6604 | 245.2507 | 26.6472 | 26.0256 | 21.2079
46.6604 | 251.0422 | 26.9079 | 26.3688 | 21.2134
47.6604 | 256.8112 | 27.2246 | 26.7301 | 21.2204
48.6604 | 262.6555 | 27.5365 | 26.9336 | 21.2291
49.6604 | 268.4801 | 27.8504 | 27.173 | 21.2362
50.6604 | 274.218 | 28.1509 | 27.4174 | 21.239
51.6604 | 279.9712 | 28.5967 | 27.7363 | 21.2385
52.6604 | 285.642 | 29.0155 | 28.1734 | 21.2511
53.6604 | 291.3123 | 29.3682 | 28.679 | 21.2632
54.6604 | 297.0271 | 29.7495 | 29.0032 | 21.2705
55.6604 | 302.7197 | 30.1554 | 29.2988 | 21.2784
56.6604 | 308.3288 | 30.6901 | 29.762 | 21.2826
57.6604 | 313.9392 | 31.2405 | 30.1603 | 21.2996
58.6604 | 319.4296 | 31.5748 | 30.5176 | 21.3072
59.6604 | 324.9601 | 32.002 | 30.9119 | 21.324
60.6604 | 330.5603 | 32.4363 | 31.1548 | 21.3368
61.6604 | 336.171 | 32.9504 | 31.5371 | 21.3538
62.6604 | 341.8199 | 33.448 | 31.9343 | 21.3675
63.6604 | 347.1919 | 34.0209 | 32.2936 | 21.3768
64.6604 | 352.6572 | 34.6125 | 32.7293 | 21.3915
65.6604 | 358.0632 | 35.1755 | 33.2507 | 21.4098
66.6604 | 363.3963 | 35.7231 | 33.9899 | 21.4253
67.6604 | 368.656 | 36.3797 | 34.4204 | 21.445
68.6604 | 374.1597 | 36.9956 | 35.1192 | 21.463
69.6604 | 379.5488 | 37.6408 | 35.7003 | 21.4852
70.6604 | 384.7926 | 38.228 | 36.3334 | 21.5067
71.6604 | 390.0011 | 38.9494 | 36.7807 | 21.5256
72.6604 | 395.2088 | 39.6428 | 37.3037 | 21.553
73.6604 | 400.3563 | 40.376 | 37.9329 | 21.5764
74.6604 | 405.6622 | 41.1133 | 38.6758 | 21.5927
75.6604 | 410.8017 | 41.7318 | 39.3285 | 21.6278
76.6604 | 415.8708 | 42.6284 | 39.7827 | 21.6528
77.6604 | 420.9818 | 43.431 | 40.3072 | 21.6832
78.6604 | 425.9781 | 44.2959 | 41.0949 | 21.7283
79.6604 | 431.0287 | 45.1526 | 41.7708 | 21.7604
80.6604 | 436.1618 | 45.9682 | 42.4351 | 21.7927
81.6604 | 441.1378 | 46.7447 | 43.2797 | 21.8349
82.6604 | 446.068 | 47.6182 | 44.034 | 21.8715
83.6604 | 450.9395 | 48.4702 | 44.8291 | 21.9153
84.6604 | 455.7438 | 49.3863 | 45.9312 | 21.9628
85.6604 | 460.4977 | 50.3258 | 46.7653 | 22.0027
86.6604 | 465.2562 | 51.2901 | 47.3993 | 22.0474
87.6604 | 469.9978 | 52.346 | 48.3496 | 22.0982
88.6604 | 474.5317 | 53.3474 | 49.4585 | 22.1532
89.6604 | 478.6508 | 54.3584 | 50.0701 | 22.2011
90.6604 | 482.354 | 55.3901 | 51.2065 | 22.2624
91.6604 | 485.7615 | 56.3788 | 52.0829 | 22.323
92.6604 | 488.9498 | 57.5349 | 52.8499 | 22.3784
93.6604 | 491.8719 | 58.4754 | 53.7139 | 22.4434
94.6604 | 494.6444 | 59.6214 | 54.8363 | 22.5052
95.6604 | 497.4476 | 60.6024 | 55.7814 | 22.5828
96.6604 | 499.9529 | 61.811 | 56.6608 | 22.6618
97.6604 | 502.6005 | 62.9404 | 57.6705 | 22.7419
98.6604 | 505.215 | 63.9335 | 58.4736 | 22.8196
99.6604 | 507.5476 | 64.9327 | 59.661 | 22.9078
100.6604 | 509.8546 | 66.1346 | 60.7241 | 23.0081
101.6604 | 511.8928 | 67.208 | 61.7016 | 23.1082
102.6604 | 513.7313 | 68.3037 | 62.5267 | 23.2088
103.6604 | 515.4526 | 69.3564 | 63.5953 | 23.3216
104.6604 | 516.5829 | 70.3773 | 64.6864 | 23.4359
105.6604 | 517.4679 | 71.4527 | 65.6161 | 23.5676
106.6604 | 518.3012 | 72.492 | 66.1684 | 23.7006
107.6604 | 519.0851 | 73.5511 | 67.033 | 23.8317
108.6604 | 519.6987 | 74.6984 | 68.1528 | 23.9685
109.6604 | 520.0756 | 75.8659 | 68.9227 | 24.1251
110.6604 | 520.2468 | 76.826 | 70.3208 | 24.2673
111.6604 | 520.331 | 77.8865 | 71.2946 | 24.4152
112.6604 | 520.4845 | 79.0341 | 72.181 | 24.576
113.6604 | 520.6421 | 80.0689 | 72.9717 | 24.7375
114.6604 | 520.699 | 81.0736 | 73.9527 | 24.9007
115.6604 | 520.5378 | 82.0749 | 74.9227 | 25.068
116.6604 | 520.5311 | 83.1875 | 75.6212 | 25.2529
117.6604 | 520.5414 | 84.205 | 76.6109 | 25.428
118.6604 | 520.5027 | 85.2616 | 77.4156 | 25.6206
119.6604 | 520.5202 | 86.3032 | 78.5802 | 25.8194
120.6604 | 520.5199 | 87.3175 | 79.667 | 26.0052
121.6604 | 520.6053 | 88.4257 | 80.3662 | 26.1982
122.6604 | 520.6003 | 89.3904 | 81.3022 | 26.385
123.6604 | 520.5803 | 90.435 | 82.329 | 26.5848
124.6604 | 520.6416 | 91.4492 | 83.3288 | 26.7825
125.6604 | 520.6951 | 92.4139 | 84.1165 | 27.0017
126.6604 | 520.7623 | 93.4147 | 85.0089 | 27.2096
127.6604 | 520.9384 | 94.4389 | 85.5942 | 27.4144
128.6604 | 521.032 | 95.4186 | 86.4447 | 27.6197
129.6604 | 521.1732 | 96.4515 | 87.3416 | 27.8333
130.6604 | 521.4965 | 97.5 | 88.3929 | 28.0446
131.6604 | 521.7406 | 98.5355 | 89.2292 | 28.2631
132.6604 | 522.0836 | 99.564 | 90.1622 | 28.4755
133.6604 | 522.3323 | 100.4838 | 91.2729 | 28.6959
134.6604 | 522.5188 | 101.6305 | 92.3029 | 28.9266
135.6604 | 522.6438 | 102.5469 | 93.3101 | 29.1567
136.6604 | 522.8072 | 103.5789 | 94.1229 | 29.3888
137.6604 | 522.9825 | 104.6092 | 95.1176 | 29.6246
138.6604 | 523.1754 | 105.6728 | 96.0322 | 29.8571
139.6604 | 523.33 | 106.6966 | 96.8152 | 30.1004
140.6604 | 523.575 | 107.7308 | 97.4895 | 30.3454
141.6604 | 523.7898 | 108.6874 | 98.5958 | 30.5844
142.6604 | 523.9045 | 109.5902 | 99.5515 | 30.8218
143.6604 | 524.0071 | 110.6636 | 100.4867 | 31.0589
144.6604 | 524.0868 | 111.6966 | 101.3446 | 31.3081
145.6604 | 524.2168 | 112.5173 | 102.4243 | 31.5575
146.6604 | 524.2405 | 113.4235 | 103.1363 | 31.8088
147.6604 | 524.1623 | 114.4758 | 104.1917 | 32.0536
148.6604 | 524.143 | 115.4858 | 105.1878 | 32.3175
149.6604 | 524.1601 | 116.4195 | 105.8649 | 32.5612
150.6604 | 524.2818 | 117.4018 | 106.8313 | 32.8157
151.6604 | 524.4868 | 118.3157 | 107.7602 | 33.0696
152.6604 | 524.709 | 119.362 | 108.5734 | 33.334
153.6604 | 524.959 | 120.3142 | 109.5025 | 33.5858
154.6604 | 525.0995 | 121.3957 | 110.3426 | 33.849
155.6604 | 525.159 | 122.3941 | 110.9872 | 34.1123
156.6604 | 525.2806 | 123.3471 | 112.0385 | 34.364
157.6604 | 525.4406 | 124.4248 | 112.8489 | 34.6295
158.6604 | 525.4729 | 125.3788 | 113.8404 | 34.8884
159.6604 | 525.7108 | 126.2933 | 114.6925 | 35.1468
160.6604 | 525.8458 | 127.203 | 115.54 | 35.416
161.6604 | 526.0004 | 128.0644 | 116.564 | 35.688
162.6604 | 525.9388 | 129.1523 | 117.3459 | 35.9613
163.6604 | 525.956 | 130.0489 | 118.0035 | 36.2162
164.6604 | 525.9705 | 131.0082 | 118.9975 | 36.4988
165.6604 | 525.9355 | 131.8773 | 119.8798 | 36.7757
166.6604 | 525.9061 | 132.7842 | 120.7708 | 37.042
167.6604 | 525.8052 | 133.6907 | 121.5589 | 37.3068
168.6604 | 525.783 | 134.6294 | 122.2629 | 37.5667
169.6604 | 525.8555 | 135.5546 | 123.0875 | 37.8224
170.6604 | 525.9498 | 136.4809 | 123.9343 | 38.0898
171.6604 | 525.9014 | 137.3871 | 124.6821 | 38.3582
172.6604 | 525.9166 | 138.1848 | 125.5751 | 38.6301
173.6604 | 526.0044 | 139.1793 | 126.456 | 38.9109
174.6604 | 526.0334 | 140.1122 | 127.459 | 39.2015
175.6604 | 525.9963 | 141.1066 | 128.3899 | 39.5046
176.6604 | 526.0643 | 142.042 | 129.0812 | 39.8166
177.6604 | 526.2386 | 142.9519 | 129.8762 | 40.1326
178.6604 | 526.1492 | 143.8272 | 130.6624 | 40.4462
179.6604 | 526.2094 | 144.7406 | 131.6311 | 40.7538
180.6604 | 526.228 | 145.6136 | 132.4922 | 41.0508
181.6604 | 526.2881 | 146.5402 | 133.2718 | 41.3243
182.6604 | 526.3144 | 147.3835 | 134.1068 | 41.614
183.6604 | 526.3118 | 148.2064 | 135.036 | 41.8805
184.6604 | 526.1823 | 149.1467 | 135.9157 | 42.1527
185.6604 | 526.107 | 150.1508 | 136.592 | 42.4273
186.6604 | 525.9747 | 150.9884 | 137.2974 | 42.6958
187.6604 | 526.0331 | 151.8254 | 138.073 | 42.9707
188.6604 | 526.0708 | 152.6275 | 138.8352 | 43.2538
189.6604 | 525.9834 | 153.4562 | 139.6568 | 43.538
190.6604 | 525.9987 | 154.3632 | 140.2945 | 43.8281
191.6604 | 526.0308 | 155.1979 | 140.9958 | 44.1279
192.6604 | 525.9688 | 156.1275 | 141.6881 | 44.4186
193.6604 | 525.9926 | 156.9984 | 142.8228 | 44.7172
194.6604 | 526.1595 | 157.9387 | 143.7684 | 45.0103
195.6604 | 526.1533 | 158.7863 | 144.569 | 45.2921
196.6604 | 526.0873 | 159.6023 | 145.4735 | 45.5765
197.6604 | 526.0891 | 160.4948 | 146.2956 | 45.8495
198.6604 | 526.0784 | 161.4246 | 146.9482 | 46.1341
199.6604 | 526.0714 | 162.209 | 147.7778 | 46.3983
200.6604 | 525.9647 | 163.0536 | 148.6328 | 46.6707
201.6604 | 525.9202 | 163.8963 | 149.5171 | 46.9372
202.6604 | 526.0272 | 164.775 | 150.2669 | 47.2123
203.6604 | 526.0782 | 165.5305 | 151.0875 | 47.5006
204.6604 | 526.0855 | 166.3569 | 151.8493 | 47.7821
205.6604 | 526.1148 | 167.1735 | 152.6232 | 48.0566
206.6604 | 526.1979 | 168.038 | 153.4479 | 48.3292
207.6604 | 526.1758 | 168.8571 | 154.2781 | 48.5869
208.6604 | 526.2261 | 169.702 | 155.122 | 48.8442
209.6604 | 526.0926 | 170.5606 | 155.9875 | 49.0913
210.6604 | 526.0272 | 171.358 | 156.7506 | 49.3261
211.6604 | 525.831 | 172.1462 | 157.4478 | 49.5615
212.6604 | 525.8333 | 172.9477 | 158.1322 | 49.7846
213.6604 | 525.9435 | 173.7216 | 158.8633 | 50.001
214.6604 | 525.8485 | 174.5622 | 159.7254 | 50.2078
215.6604 | 525.7427 | 175.3423 | 160.5116 | 50.4189
216.6604 | 525.7571 | 176.0843 | 161.2697 | 50.6134
217.6604 | 525.7391 | 176.9001 | 162.0755 | 50.8119
218.6604 | 525.7717 | 177.7291 | 162.7084 | 51.0048
219.6604 | 525.8241 | 178.5411 | 163.5613 | 51.2012
220.6604 | 525.6812 | 179.3666 | 164.2279 | 51.3936
221.6604 | 525.6871 | 180.1423 | 164.992 | 51.5901
222.6604 | 525.7935 | 180.9104 | 165.7737 | 51.7911
223.6604 | 525.8749 | 181.7323 | 166.5413 | 51.9963
224.6604 | 525.8211 | 182.5019 | 167.3131 | 52.1989
225.6604 | 525.7634 | 183.3146 | 167.9536 | 52.4018
226.6604 | 525.8296 | 184.1408 | 168.6864 | 52.6078
227.6604 | 525.7167 | 184.8503 | 169.4791 | 52.8116
228.6604 | 525.5409 | 185.5777 | 170.2248 | 53.0139
229.6604 | 525.4952 | 186.3257 | 170.934 | 53.2122
230.6604 | 525.3878 | 187.1195 | 171.6374 | 53.4038
231.6604 | 525.3117 | 187.9181 | 172.3734 | 53.589
232.6604 | 525.474 | 188.6394 | 173.1618 | 53.7689
233.6604 | 525.6023 | 189.3714 | 173.877 | 53.9438
234.6604 | 525.6973 | 190.127 | 174.5956 | 54.1207
235.6604 | 525.6247 | 190.925 | 175.2902 | 54.2919
236.6604 | 525.6834 | 191.7191 | 175.9644 | 54.4732
237.6604 | 525.6587 | 192.4489 | 176.5922 | 54.6459
238.6604 | 525.6627 | 193.2261 | 177.4165 | 54.8097
239.6604 | 525.6921 | 194.0083 | 178.1802 | 54.9692
240.6604 | 525.6791 | 194.7411 | 178.8498 | 55.1214
241.6604 | 525.6843 | 195.4697 | 179.5639 | 55.2769
242.6604 | 525.696 | 196.1942 | 180.3734 | 55.4214
243.6604 | 525.7291 | 196.9127 | 181.0701 | 55.5842
244.6604 | 525.802 | 197.6555 | 181.8373 | 55.7313
245.6604 | 525.6698 | 198.331 | 182.5608 | 55.8746
246.6604 | 525.7012 | 199.1027 | 183.2284 | 56.0199
247.6604 | 525.7904 | 199.7992 | 183.8796 | 56.1602
248.6604 | 525.8331 | 200.5308 | 184.5442 | 56.303
249.6604 | 525.8401 | 201.2381 | 185.2594 | 56.4531
250.6604 | 525.9205 | 202.0214 | 185.9901 | 56.603
251.6604 | 526.0261 | 202.749 | 186.6988 | 56.7683
252.6604 | 525.9392 | 203.4413 | 187.3667 | 56.9362
253.6604 | 525.859 | 204.1743 | 188.0342 | 57.1192
254.6604 | 525.7221 | 204.8391 | 188.6871 | 57.3195
255.6604 | 525.5766 | 205.6007 | 189.4676 | 57.5359
256.6604 | 525.645 | 206.3368 | 190.2319 | 57.7482
257.6604 | 525.5093 | 207.0496 | 190.8897 | 57.976
258.6604 | 525.5665 | 207.6925 | 191.5332 | 58.2027
259.6604 | 525.6445 | 208.4322 | 192.1809 | 58.439
260.6604 | 525.5707 | 209.1213 | 192.8733 | 58.6877
261.6604 | 525.5516 | 209.8177 | 193.5482 | 58.9353
262.6604 | 525.6312 | 210.4274 | 194.2257 | 59.1924
263.6604 | 525.58 | 211.0537 | 194.8515 | 59.4455
264.6604 | 525.6743 | 211.7334 | 195.4526 | 59.7051
265.6604 | 525.6331 | 212.4675 | 196.1837 | 59.9721
266.6604 | 525.6197 | 213.192 | 196.9035 | 60.2405
267.6604 | 525.6388 | 213.888 | 197.5498 | 60.5026
268.6604 | 525.6847 | 214.5773 | 198.2076 | 60.7779
269.6604 | 525.6895 | 215.3111 | 198.9101 | 61.0584
270.6604 | 525.6367 | 216.0211 | 199.5932 | 61.3411
271.6604 | 525.546 | 216.7095 | 200.253 | 61.6258
272.6604 | 525.4611 | 217.3996 | 200.8596 | 61.9188
273.6604 | 525.4703 | 218.1204 | 201.5383 | 62.2113
274.6604 | 525.6048 | 218.761 | 202.1774 | 62.5157
275.6604 | 525.6253 | 219.4338 | 202.7863 | 62.8171
276.6604 | 525.6749 | 220.126 | 203.4858 | 63.1368
277.6604 | 525.7336 | 220.7582 | 204.1522 | 63.4545
278.6604 | 525.8692 | 221.4982 | 204.7997 | 63.7772
279.6604 | 526.0953 | 222.1549 | 205.4537 | 64.1011
280.6604 | 526.0395 | 222.7404 | 206.0778 | 64.4287
281.6604 | 525.7794 | 223.3976 | 206.7467 | 64.7713
282.6604 | 525.6172 | 224.1303 | 207.3429 | 65.1124
283.6604 | 525.5432 | 224.8089 | 207.9194 | 65.4622
284.6604 | 525.3978 | 225.478 | 208.5398 | 65.8033
285.6604 | 525.446 | 226.1393 | 209.1578 | 66.1524
286.6604 | 525.2844 | 226.8155 | 209.7899 | 66.5022
287.6604 | 525.1988 | 227.4933 | 210.3892 | 66.8528
288.6604 | 525.2415 | 228.1676 | 211.0024 | 67.202
289.6604 | 525.1743 | 228.7803 | 211.6659 | 67.559
290.6604 | 525.1417 | 229.3999 | 212.256 | 67.9141
291.6604 | 525.0377 | 230.0874 | 212.8493 | 68.2733
292.6604 | 524.728 | 230.7739 | 213.4546 | 68.6325
293.6604 | 524.5487 | 231.4772 | 214.0497 | 68.9986
294.6604 | 524.5027 | 232.0697 | 214.6382 | 69.3607
295.6604 | 524.4136 | 232.6744 | 215.2189 | 69.7343
296.6604 | 524.4 | 233.2842 | 215.8293 | 70.1024
297.6604 | 524.3378 | 233.9021 | 216.4239 | 70.4767
298.6604 | 524.335 | 234.4977 | 217.0196 | 70.8483
299.6604 | 524.3288 | 235.1689 | 217.5903 | 71.2347
300.6604 | 524.4373 | 235.8732 | 218.1606 | 71.6087
301.6604 | 524.5956 | 236.472 | 218.7571 | 71.9961
302.6604 | 524.7098 | 237.0931 | 219.3447 | 72.3737
303.6604 | 524.8039 | 237.7308 | 219.9542 | 72.7597
304.6604 | 524.8231 | 238.4095 | 220.5484 | 73.144
305.6604 | 524.8417 | 239.0771 | 221.1507 | 73.5281
306.6604 | 524.8245 | 239.702 | 221.7339 | 73.9059
307.6604 | 524.8244 | 240.312 | 222.286 | 74.2989
308.6604 | 524.9071 | 240.9312 | 222.8822 | 74.6914
309.6604 | 524.8272 | 241.5913 | 223.486 | 75.0794
310.6604 | 524.7747 | 242.2373 | 224.0771 | 75.4623
311.6604 | 524.7517 | 242.8401 | 224.6777 | 75.8537
312.6604 | 524.8003 | 243.45 | 225.2767 | 76.2399
313.6604 | 524.8623 | 244.0132 | 225.892 | 76.6283
314.6604 | 524.8279 | 244.6531 | 226.4674 | 77.0146
315.6604 | 524.7766 | 245.3087 | 227.0566 | 77.4041
316.6604 | 524.7958 | 245.9135 | 227.6641 | 77.7899
317.6604 | 524.7774 | 246.5375 | 228.2956 | 78.1776
318.6604 | 524.7 | 247.1529 | 228.8898 | 78.5774
319.6604 | 524.6463 | 247.7662 | 229.4563 | 78.9603
320.6604 | 524.5487 | 248.3688 | 230.078 | 79.3572
321.6604 | 524.403 | 249.0203 | 230.6686 | 79.742
322.6604 | 524.3728 | 249.6136 | 231.2703 | 80.1366
323.6604 | 524.4731 | 250.1891 | 231.9014 | 80.5234
324.6604 | 524.4201 | 250.7254 | 232.4662 | 80.9168
325.6604 | 524.3386 | 251.3757 | 233.0799 | 81.3162
326.6604 | 524.3445 | 252.022 | 233.6438 | 81.7101
327.6604 | 524.4222 | 252.633 | 234.265 | 82.1057
328.6604 | 524.4501 | 253.2118 | 234.8721 | 82.496
329.6604 | 524.3788 | 253.7809 | 235.4868 | 82.8873
330.6604 | 524.3542 | 254.3704 | 236.1071 | 83.2801
331.6604 | 524.3247 | 254.9675 | 236.7251 | 83.6747
332.6604 | 524.3107 | 255.5903 | 237.3192 | 84.0822
333.6604 | 524.262 | 256.1803 | 237.8904 | 84.4878
334.6604 | 524.2843 | 256.7836 | 238.5097 | 84.8917
335.6604 | 524.3972 | 257.3677 | 239.1255 | 85.2899
336.6604 | 524.4551 | 257.9484 | 239.7437 | 85.6913
337.6604 | 524.4476 | 258.5005 | 240.3584 | 86.0919
338.6604 | 524.5495 | 259.0884 | 240.9441 | 86.5027
339.6604 | 524.64 | 259.6413 | 241.5903 | 86.9128
340.6604 | 524.608 | 260.2097 | 242.1522 | 87.3129
341.6604 | 524.6123 | 260.7818 | 242.7462 | 87.7265
342.6604 | 524.5356 | 261.3473 | 243.3603 | 88.1399
343.6604 | 524.5436 | 261.8941 | 243.9813 | 88.5544
344.6604 | 524.5657 | 262.4898 | 244.5967 | 88.9734
345.6604 | 524.5988 | 263.0845 | 245.1622 | 89.3892
346.6604 | 524.7632 | 263.6307 | 245.7498 | 89.8101
347.6604 | 524.7227 | 264.1899 | 246.3383 | 90.2312
348.6604 | 524.6594 | 264.7822 | 246.934 | 90.6506
349.6604 | 524.6653 | 265.3818 | 247.5237 | 91.0835
350.6604 | 524.6849 | 265.9421 | 248.1189 | 91.4957
351.6604 | 524.6271 | 266.5231 | 248.7024 | 91.917
352.6604 | 524.5835 | 267.1177 | 249.2743 | 92.3477
353.6604 | 524.5428 | 267.6722 | 249.8475 | 92.7708
354.6604 | 524.4626 | 268.2665 | 250.4276 | 93.1946
355.6604 | 524.361 | 268.7789 | 250.978 | 93.6438
356.6604 | 524.3418 | 269.2798 | 251.5547 | 94.0785
357.6604 | 524.2157 | 269.8594 | 252.1175 | 94.5127
358.6604 | 524.2857 | 270.496 | 252.7076 | 94.9616
359.6604 | 524.3164 | 271.0696 | 253.2793 | 95.3986
360.6604 | 524.4252 | 271.6466 | 253.8319 | 95.8465
361.6604 | 524.5503 | 272.2077 | 254.4208 | 96.2865
362.6604 | 524.5688 | 272.8195 | 254.9396 | 96.7297
363.6604 | 524.4728 | 273.3984 | 255.5193 | 97.1789
364.6604 | 524.5022 | 273.9541 | 256.1141 | 97.6253
365.6604 | 524.5427 | 274.5165 | 256.7371 | 98.0877
366.6604 | 524.624 | 275.0785 | 257.3158 | 98.5391
367.6604 | 524.6732 | 275.643 | 257.8612 | 98.9962
368.6604 | 524.6694 | 276.2139 | 258.4589 | 99.4526
369.6604 | 524.6391 | 276.7654 | 259.0362 | 99.9101
370.6604 | 524.7416 | 277.3076 | 259.6035 | 100.3655
371.6604 | 524.8011 | 277.871 | 260.1636 | 100.8282
372.6604 | 524.927 | 278.3976 | 260.7236 | 101.2989
373.6604 | 524.7998 | 278.9926 | 261.2518 | 101.7657
374.6604 | 524.6983 | 279.556 | 261.7963 | 102.24
375.6604 | 524.6954 | 280.1061 | 262.3273 | 102.7219
376.6604 | 524.6086 | 280.6886 | 262.8822 | 103.2125
377.6604 | 524.5446 | 281.2456 | 263.4328 | 103.6926
378.6604 | 524.5261 | 281.8144 | 264.0102 | 104.1701
379.6604 | 524.4267 | 282.3716 | 264.5104 | 104.6514
380.6604 | 524.3863 | 282.935 | 265.1048 | 105.1361
381.6604 | 524.4219 | 283.5027 | 265.6586 | 105.6201
382.6604 | 524.3529 | 284.0531 | 266.1707 | 106.109
383.6604 | 524.3861 | 284.6104 | 266.7529 | 106.5866
384.6604 | 524.4955 | 285.1669 | 267.2969 | 107.0869
385.6604 | 524.5774 | 285.7307 | 267.8597 | 107.582
386.6604 | 524.7099 | 286.2573 | 268.4163 | 108.0694
387.6604 | 524.7647 | 286.8134 | 268.94 | 108.5739
388.6604 | 524.6699 | 287.3685 | 269.4873 | 109.0761
389.6604 | 524.5731 | 287.8904 | 269.9988 | 109.5841
390.6604 | 524.5844 | 288.4274 | 270.5549 | 110.1031
391.6604 | 524.5929 | 288.9805 | 271.1029 | 110.6117
392.6604 | 524.5011 | 289.518 | 271.6915 | 111.128
393.6604 | 524.5761 | 290.0724 | 272.237 | 111.6512
394.6604 | 524.7843 | 290.6219 | 272.7322 | 112.1761
395.6604 | 524.6933 | 291.1573 | 273.295 | 112.7113
396.6604 | 524.7035 | 291.6885 | 273.8379 | 113.2408
397.6604 | 524.8407 | 292.2189 | 274.354 | 113.7736
398.6604 | 524.8646 | 292.7325 | 274.8945 | 114.3071
399.6604 | 524.7901 | 293.2633 | 275.4426 | 114.8404
400.6604 | 524.7034 | 293.8129 | 275.9771 | 115.39
401.6604 | 524.6972 | 294.3605 | 276.5654 | 115.9281
402.6604 | 524.7103 | 294.8913 | 277.0376 | 116.4786
403.6604 | 524.6894 | 295.4015 | 277.5889 | 117.0314
404.6604 | 524.6641 | 295.953 | 278.1309 | 117.5826
405.6604 | 524.7213 | 296.505 | 278.6254 | 118.1335
406.6604 | 524.7508 | 297.0333 | 279.1501 | 118.6966
407.6604 | 524.5705 | 297.5264 | 279.6772 | 119.2539
408.6604 | 524.5757 | 298.0675 | 280.2604 | 119.825
409.6604 | 524.481 | 298.6111 | 280.8332 | 120.3972
410.6604 | 524.4864 | 299.1369 | 281.4054 | 120.9712
411.6604 | 524.4087 | 299.6743 | 281.9174 | 121.5456
412.6604 | 524.3195 | 300.1661 | 282.4812 | 122.1419
413.6604 | 524.362 | 300.6938 | 282.9439 | 122.7272
414.6604 | 524.4334 | 301.1822 | 283.4792 | 123.3144
415.6604 | 524.512 | 301.7171 | 283.9912 | 123.9062
416.6604 | 524.5863 | 302.2073 | 284.4598 | 124.4924
417.6604 | 524.5886 | 302.724 | 284.9686 | 125.0872
418.6604 | 524.6228 | 303.2548 | 285.484 | 125.6849
419.6604 | 524.5993 | 303.7751 | 285.9677 | 126.2883
420.6604 | 524.583 | 304.2735 | 286.5143 | 126.8864
421.6604 | 524.5244 | 304.8015 | 287.0737 | 127.4979
422.6604 | 524.5916 | 305.3323 | 287.6247 | 128.1075
423.6604 | 524.6133 | 305.8299 | 288.1393 | 128.726
424.6604 | 524.667 | 306.3457 | 288.6054 | 129.3406
425.6604 | 524.6368 | 306.8579 | 289.0979 | 129.9707
426.6604 | 524.6305 | 307.3415 | 289.6512 | 130.5981
427.6604 | 524.7149 | 307.8453 | 290.1891 | 131.231
428.6604 | 524.6826 | 308.2937 | 290.769 | 131.883
429.6604 | 524.5845 | 308.8276 | 291.2514 | 132.5239
430.6604 | 524.6552 | 309.3424 | 291.7136 | 133.174
431.6604 | 524.5303 | 309.8526 | 292.2674 | 133.8198
432.6604 | 524.4926 | 310.3433 | 292.7252 | 134.485
433.6604 | 524.3629 | 310.851 | 293.1959 | 135.1717
434.6604 | 524.3284 | 311.3513 | 293.6892 | 135.8748
435.6604 | 524.2477 | 311.858 | 294.137 | 136.5973
436.6604 | 524.1744 | 312.3397 | 294.7167 | 137.3665
437.6604 | 524.1744 | 312.8361 | 295.2958 | 138.1663
438.6604 | 524.1066 | 313.3201 | 295.7796 | 138.9999
439.6604 | 524.2059 | 313.7922 | 296.2817 | 139.863
440.6604 | 524.2246 | 314.2967 | 296.7551 | 140.7661
441.6604 | 524.1406 | 314.7931 | 297.2406 | 141.6891
442.6604 | 524.1431 | 315.2724 | 297.8208 | 142.6217
443.6604 | 524.1357 | 315.7683 | 298.445 | 143.5776
444.6604 | 524.1242 | 316.2544 | 298.8654 | 144.5437
445.6604 | 524.1121 | 316.7414 | 299.3475 | 145.5318
446.6604 | 524.0317 | 317.2305 | 299.8523 | 146.52
447.6604 | 524.0658 | 317.7224 | 300.3174 | 147.5319
448.6604 | 524.2579 | 318.1901 | 300.8433 | 148.5566
449.6604 | 524.248 | 318.6806 | 301.4339 | 149.5904
450.6604 | 524.2844 | 319.1609 | 301.8529 | 150.637
451.6604 | 524.3506 | 319.6373 | 302.3607 | 151.7034
452.6604 | 524.4192 | 320.0867 | 302.8137 | 152.7738
453.6604 | 524.3293 | 320.5625 | 303.264 | 153.8658
454.6604 | 524.4005 | 321.0512 | 303.8195 | 154.9778
455.6604 | 524.3473 | 321.5229 | 304.3238 | 156.1022
456.6604 | 524.3012 | 321.998 | 304.8376 | 157.2554
457.6604 | 524.3168 | 322.4636 | 305.3072 | 158.4247
458.6604 | 524.3528 | 322.9104 | 305.6824 | 159.6261
459.6604 | 524.3267 | 323.3465 | 306.2664 | 160.8656
460.6604 | 524.4299 | 323.8315 | 306.9436 | 162.1159
461.6604 | 524.4003 | 324.3177 | 307.5482 | 163.3994
462.6604 | 524.2091 | 324.7688 | 308.0303 | 164.728
463.6604 | 524.1703 | 325.205 | 308.3923 | 166.1033
464.6604 | 524.145 | 325.6078 | 308.7627 | 167.52
465.6604 | 524.2502 | 326.0782 | 309.3465 | 168.9779
466.6604 | 524.3286 | 326.5044 | 309.7238 | 170.4892
467.6604 | 524.2649 | 326.9847 | 310.1278 | 172.0347
468.6604 | 524.3701 | 327.4839 | 310.5782 | 173.625
469.6604 | 524.5587 | 327.9489 | 311.0625 | 175.2446
470.6604 | 524.5759 | 328.4294 | 311.5532 | 176.869
471.6604 | 524.6527 | 328.8751 | 312.0117 | 178.5058
472.6604 | 524.5489 | 329.34 | 312.3386 | 180.1482
473.6604 | 524.5149 | 329.7953 | 312.7557 | 181.7919
474.6604 | 524.5354 | 330.2358 | 313.2569 | 183.464
475.6604 | 524.4191 | 330.6974 | 313.6433 | 185.1433
476.6604 | 524.4176 | 331.144 | 314.2444 | 186.859
477.6604 | 524.4579 | 331.5957 | 314.8572 | 188.582
478.6604 | 524.4711 | 332.0555 | 315.3702 | 190.3424
479.6604 | 524.5754 | 332.5121 | 315.8131 | 192.0952
480.6604 | 524.5314 | 332.9447 | 316.1178 | 193.848
481.6604 | 524.5828 | 333.4016 | 316.5774 | 195.6006
482.6604 | 524.6696 | 333.8466 | 316.944 | 197.3438
483.6604 | 524.6794 | 334.2958 | 317.4534 | 199.0888
484.6604 | 524.722 | 334.7376 | 317.9529 | 200.8173
485.6604 | 524.8144 | 335.1857 | 318.4749 | 202.5324
486.6604 | 524.7429 | 335.6122 | 319.0484 | 204.2194
487.6604 | 524.7153 | 336.0457 | 319.5227 | 205.8811
488.6604 | 524.6549 | 336.4774 | 319.9526 | 207.4996
489.6604 | 524.6679 | 336.9262 | 320.3466 | 209.0943
490.6604 | 524.6818 | 337.3261 | 320.7246 | 210.672
491.6604 | 524.7079 | 337.7686 | 321.1265 | 212.2128
492.6604 | 524.7402 | 338.1967 | 321.62 | 213.7194
493.6604 | 524.8085 | 338.632 | 322.1409 | 215.1876
494.6604 | 524.7986 | 339.044 | 322.4572 | 216.6409
495.6604 | 524.8263 | 339.4723 | 322.821 | 218.0664
496.6604 | 524.7841 | 339.8736 | 323.2884 | 219.4769
497.6604 | 524.7344 | 340.2736 | 323.6682 | 220.8519
498.6604 | 524.7345 | 340.7137 | 324.0011 | 222.2234
499.6604 | 524.7601 | 341.1756 | 324.482 | 223.5451
500.6604 | 524.7276 | 341.597 | 324.8923 | 224.8412
501.6604 | 524.6565 | 342.0049 | 325.3626 | 226.1003
502.6604 | 524.6816 | 342.4482 | 325.7293 | 227.3293
503.6604 | 524.8127 | 342.8639 | 326.0769 | 228.5239
504.6604 | 524.8893 | 343.279 | 326.5726 | 229.7008
505.6604 | 524.9075 | 343.7051 | 327.049 | 230.844
506.6604 | 524.8916 | 344.116 | 327.4283 | 231.9639
507.6604 | 524.8903 | 344.5267 | 327.8752 | 233.0514
508.6604 | 524.8745 | 344.9468 | 328.2469 | 234.1405
509.6604 | 524.8073 | 345.3589 | 328.7671 | 235.201
510.6604 | 524.7864 | 345.7616 | 329.2541 | 236.2525
511.6604 | 524.8906 | 346.1697 | 329.5183 | 237.2837
512.6604 | 524.9367 | 346.5846 | 329.8895 | 238.3061
513.6604 | 524.774 | 346.9823 | 330.2987 | 239.3146
514.6604 | 524.808 | 347.3705 | 330.7025 | 240.2822
515.6604 | 524.8087 | 347.7682 | 331.2241 | 241.2481
516.6604 | 524.8448 | 348.1685 | 331.7376 | 242.1857
517.6604 | 524.7099 | 348.5633 | 332.0474 | 243.1094
518.6604 | 524.6068 | 348.9567 | 332.494 | 244.0138
519.6604 | 524.4635 | 349.3757 | 333.034 | 244.914
520.6604 | 524.2428 | 349.7654 | 333.4117 | 245.7933
521.6604 | 524.1463 | 350.1685 | 333.6929 | 246.6493
522.6604 | 524.185 | 350.5662 | 333.9666 | 247.5045
523.6604 | 524.2696 | 350.9368 | 334.3601 | 248.3569
524.6604 | 524.2187 | 351.3385 | 334.6559 | 249.1709
525.6604 | 524.2252 | 351.746 | 335.1016 | 249.9785
526.6604 | 523.9939 | 352.1343 | 335.6931 | 250.781
527.6604 | 523.9619 | 352.5079 | 336.0864 | 251.5654
528.6604 | 523.928 | 352.8998 | 336.5174 | 252.3534
529.6604 | 523.9239 | 353.2313 | 336.8361 | 253.1197
530.6604 | 524.0206 | 353.6287 | 337.1991 | 253.8778
531.6604 | 524.034 | 354.0025 | 337.6366 | 254.6246
532.6604 | 524.0077 | 354.4079 | 338.078 | 255.3645
533.6604 | 523.926 | 354.7985 | 338.4499 | 256.0913
534.6604 | 524.0384 | 355.1615 | 338.9859 | 256.8004
535.6604 | 524.3054 | 355.5647 | 339.4098 | 257.5081
536.6604 | 524.3852 | 355.9476 | 339.7233 | 258.2015
537.6604 | 524.5705 | 356.3218 | 340.1777 | 258.8674
538.6604 | 524.6106 | 356.6892 | 340.433 | 259.5218
539.6604 | 524.8114 | 357.0766 | 340.8239 | 260.1718
540.6604 | 524.8248 | 357.4468 | 341.1863 | 260.8148
541.6604 | 524.7921 | 357.7965 | 341.7067 | 261.4573
542.6604 | 524.8599 | 358.1547 | 342.2074 | 262.0846
543.6604 | 524.863 | 358.462 | 342.6291 | 262.7021
544.6604 | 524.7508 | 358.8625 | 342.8979 | 263.318
545.6604 | 524.7024 | 359.2425 | 343.344 | 263.9179
546.6604 | 524.6788 | 359.6127 | 343.6447 | 264.5145
547.6604 | 524.5992 | 359.9867 | 343.9722 | 265.1022
548.6604 | 524.6039 | 360.3609 | 344.245 | 265.6756
549.6604 | 524.6014 | 360.668 | 344.6161 | 266.2384
550.6604 | 524.6007 | 361.0614 | 345.0303 | 266.7783
551.6604 | 524.5995 | 361.43 | 345.6836 | 267.3145
552.6604 | 524.6389 | 361.8287 | 345.943 | 267.8367
553.6604 | 524.6777 | 362.1934 | 346.4842 | 268.335
554.6604 | 524.7509 | 362.5322 | 346.906 | 268.8144
555.6604 | 524.7676 | 362.8795 | 347.3438 | 269.2819
556.6604 | 524.7753 | 363.2727 | 347.7693 | 269.7452
557.6604 | 524.6751 | 363.6014 | 348.1277 | 270.2064
558.6604 | 524.5236 | 363.988 | 348.4998 | 270.6462
559.6604 | 524.6809 | 364.3459 | 348.995 | 271.0779
560.6604 | 524.8578 | 364.6936 | 349.3276 | 271.4868
561.6604 | 524.952 | 365.0719 | 349.6045 | 271.8826
562.6604 | 525.0359 | 365.4307 | 350.0223 | 272.2541
563.6604 | 525.0498 | 365.7863 | 350.5128 | 272.6162
564.6604 | 525.1001 | 366.139 | 350.9811 | 272.9703
565.6604 | 525.1103 | 366.4857 | 351.238 | 273.34
566.6604 | 525.2147 | 366.798 | 351.4508 | 273.7
567.6604 | 525.3219 | 367.1533 | 351.6858 | 274.0638
568.6604 | 525.3859 | 367.5012 | 351.9569 | 274.4258
569.6604 | 525.5848 | 367.8496 | 352.2869 | 274.7829
570.6604 | 525.5603 | 368.2234 | 352.7092 | 275.1351
571.6604 | 525.5523 | 368.5733 | 353.1033 | 275.4974
572.6604 | 525.4832 | 368.9328 | 353.5107 | 275.8843
573.6604 | 525.4758 | 369.2857 | 353.9363 | 276.2472
574.6604 | 525.4424 | 369.6189 | 354.4455 | 276.6418
575.6604 | 525.3696 | 369.9502 | 354.8423 | 277.0327
576.6604 | 525.3741 | 370.3173 | 355.1415 | 277.4145
577.6604 | 525.3031 | 370.6145 | 355.3045 | 277.7819
578.6604 | 525.2168 | 370.95 | 355.5727 | 278.1593
579.6604 | 525.0946 | 371.2998 | 356.0659 | 278.5226
580.6604 | 525.0789 | 371.6552 | 356.5169 | 278.8853
581.6604 | 524.9783 | 371.987 | 356.7206 | 279.2444
582.6604 | 524.905 | 372.2893 | 357.089 | 279.6176
583.6604 | 524.6717 | 372.5812 | 357.5867 | 279.9669
584.6604 | 524.4812 | 372.913 | 357.967 | 280.3085
585.6604 | 524.4069 | 373.2808 | 358.3035 | 280.6623
586.6604 | 524.2432 | 373.6275 | 358.7194 | 281.0113
587.6604 | 524.1637 | 373.9213 | 359.0255 | 281.3753
588.6604 | 524.0668 | 374.2446 | 359.2792 | 281.7249
589.6604 | 523.8834 | 374.5591 | 359.6144 | 282.0896
590.6604 | 523.9285 | 374.887 | 359.8834 | 282.4457
591.6604 | 523.7459 | 375.2232 | 360.1053 | 282.8053
592.6604 | 523.6486 | 375.5323 | 360.4528 | 283.157
593.6604 | 523.7566 | 375.8635 | 360.7309 | 283.5101
594.6604 | 523.7206 | 376.1632 | 361.3941 | 283.8554
595.6604 | 523.643 | 376.474 | 361.9091 | 284.2126
596.6604 | 523.5658 | 376.7784 | 362.2319 | 284.5559
597.6604 | 523.5151 | 377.121 | 362.4017 | 284.8902
598.6604 | 523.487 | 377.332 | 362.6461 | 285.2279
599.6604 | 523.5236 | 377.6985 | 363.171 | 285.5578
600.6604 | 523.5172 | 378.0441 | 363.424 | 285.8815
601.6604 | 523.5468 | 378.3807 | 363.5985 | 286.1926
602.6604 | 523.4445 | 378.6807 | 364.0313 | 286.5187
603.6604 | 523.4647 | 378.9616 | 364.4497 | 286.8339
604.6604 | 523.3884 | 379.1952 | 364.8633 | 287.1381
605.6604 | 523.4722 | 379.5398 | 365.2572 | 287.438
606.6604 | 523.5576 | 379.8538 | 365.546 | 287.731
607.6604 | 523.6551 | 380.1366 | 365.955 | 288.0286
608.6604 | 523.7395 | 380.4661 | 366.2307 | 288.3187
609.6604 | 523.8534 | 380.7797 | 366.6001 | 288.5952
610.6604 | 523.9509 | 381.1112 | 366.7177 | 288.8757
611.6604 | 524.0553 | 381.4056 | 366.9162 | 289.1507
612.6604 | 524.0448 | 381.715 | 367.3664 | 289.4241
613.6604 | 523.992 | 382.027 | 367.5535 | 289.6928
614.6604 | 523.8801 | 382.3297 | 367.8946 | 289.9619
615.6604 | 523.9029 | 382.6397 | 368.3206 | 290.2275
616.6604 | 524.0447 | 382.9502 | 368.6497 | 290.487
617.6604 | 524.069 | 383.2909 | 368.8501 | 290.7577
618.6604 | 524.0589 | 383.5737 | 369.0849 | 291.03
619.6604 | 523.9136 | 383.8725 | 369.4664 | 291.3011
620.6604 | 523.8446 | 384.1557 | 369.8195 | 291.5519
621.6604 | 523.8617 | 384.4211 | 369.9821 | 291.803
622.6604 | 523.7926 | 384.743 | 370.2071 | 292.0722
623.6604 | 523.7302 | 385.0435 | 370.5759 | 292.3405
624.6604 | 523.661 | 385.3437 | 370.921 | 292.61
625.6604 | 523.6462 | 385.5873 | 371.4532 | 292.8612
626.6604 | 523.6307 | 385.8884 | 371.854 | 293.1265
627.6604 | 523.6548 | 386.1674 | 372.2704 | 293.3969
628.6604 | 523.6401 | 386.4621 | 372.4316 | 293.6525
629.6604 | 523.638 | 386.7565 | 372.6166 | 293.9005
630.6604 | 523.535 | 387.0658 | 372.8442 | 294.1103
631.6604 | 523.5212 | 387.3386 | 373.3461 | 294.2942
632.6604 | 523.5248 | 387.6165 | 373.7521 | 294.4871
633.6604 | 523.4927 | 387.939 | 373.9094 | 294.6787
634.6604 | 523.6546 | 388.2343 | 374.2856 | 294.8727
635.6604 | 523.7189 | 388.5043 | 374.7559 | 295.0555
636.6604 | 523.7669 | 388.7903 | 374.8434 | 295.2211
637.6604 | 523.8 | 389.1047 | 375.2266 | 295.3779
638.6604 | 523.7683 | 389.3727 | 375.5798 | 295.5395
639.6604 | 523.7453 | 389.6383 | 375.6581 | 295.6819
640.6604 | 523.747 | 389.9275 | 375.6737 | 295.8228
641.6604 | 523.7986 | 390.2367 | 376.007 | 295.9486
642.6604 | 523.8416 | 390.5209 | 376.2355 | 296.0679
643.676 | 523.8126 | 390.8246 | 376.5089 | 296.1967
644.6604 | 523.6972 | 391.0943 | 376.6211 | 296.3159
645.6604 | 523.6069 | 391.369 | 376.9445 | 296.452
646.6604 | 523.5761 | 391.6582 | 377.2824 | 296.5858
647.6604 | 523.6313 | 391.9291 | 377.6102 | 296.7197
648.6604 | 523.6051 | 392.2064 | 378.0033 | 296.8436
649.6604 | 523.5778 | 392.4785 | 378.26 | 296.9257
650.6604 | 523.4805 | 392.7763 | 378.4552 | 296.9904
651.6604 | 523.4281 | 393.042 | 378.9456 | 297.0721
652.6604 | 523.4232 | 393.2841 | 379.2385 | 297.1972
653.6604 | 523.3017 | 393.554 | 379.471 | 297.3527
654.6604 | 523.1563 | 393.8236 | 379.5542 | 297.4984
655.6604 | 523.0429 | 394.0889 | 379.7586 | 297.6567
656.6604 | 522.9463 | 394.3674 | 380.312 | 297.8223
657.6604 | 522.8305 | 394.6421 | 380.6848 | 298.0271
658.6604 | 522.7011 | 394.8956 | 380.7948 | 298.2343
659.6604 | 522.6031 | 395.1395 | 380.9807 | 298.4487
660.6604 | 522.5367 | 395.3675 | 381.3883 | 298.6539
661.6604 | 522.5814 | 395.6334 | 381.6546 | 298.8511
662.6604 | 522.4935 | 395.9384 | 382.1064 | 299.0531
663.6604 | 522.4086 | 396.195 | 382.3162 | 299.2454
664.6604 | 522.3643 | 396.4808 | 382.6225 | 299.4344
665.6604 | 522.256 | 396.7464 | 382.9078 | 299.6195
666.6604 | 522.1772 | 397.005 | 383.1723 | 299.8049
667.6604 | 522.2023 | 397.273 | 383.5233 | 300.0024
668.6604 | 522.2689 | 397.5419 | 383.8379 | 300.2411
669.6604 | 522.3406 | 397.8128 | 383.8944 | 300.5078
670.6604 | 522.418 | 398.0836 | 384.1362 | 300.7756
671.6604 | 522.5764 | 398.3534 | 384.4961 | 301.0576
672.6604 | 522.6579 | 398.6293 | 384.7329 | 301.3432
673.6604 | 522.7417 | 398.8945 | 385.0643 | 301.6582
674.6604 | 522.7231 | 399.1217 | 385.3993 | 301.9716
675.6604 | 522.7425 | 399.3844 | 385.6289 | 302.2053
676.6604 | 522.7449 | 399.5994 | 385.6713 | 302.3495
677.6604 | 522.7613 | 399.8451 | 385.8343 | 302.5609
678.6604 | 522.72 | 400.0759 | 386.3285 | 302.9446
679.6604 | 522.6835 | 400.3412 | 386.6157 | 303.339
680.6604 | 522.7576 | 400.5926 | 386.9427 | 303.7099
681.6604 | 522.7415 | 400.8338 | 386.9967 | 304.1147
682.6604 | 522.7939 | 401.0879 | 387.1429 | 304.5645
683.6604 | 522.9548 | 401.3408 | 387.3386 | 305.065
684.6604 | 523.093 | 401.6455 | 387.5713 | 305.5597
685.6604 | 523.0638 | 401.886 | 387.8314 | 305.9925
686.6604 | 523.1603 | 402.1457 | 388.2709 | 306.4385
687.6604 | 523.1938 | 402.3823 | 388.6871 | 307.0025
688.6604 | 523.3002 | 402.6116 | 388.9961 | 307.61
689.6604 | 523.3072 | 402.8539 | 389.2893 | 308.2146
690.6604 | 523.1999 | 403.0519 | 389.5475 | 308.8142
691.6604 | 523.2343 | 403.3746 | 389.5646 | 309.4131
692.6604 | 523.0154 | 403.6546 | 389.6942 | 310.0281
693.6604 | 522.8844 | 403.8393 | 390.0394 | 310.6577
694.6604 | 522.949 | 404.0892 | 390.5785 | 311.3127
695.6604 | 522.9896 | 404.3332 | 390.7819 | 311.9979
696.6604 | 522.9192 | 404.5897 | 390.78 | 312.6996
697.6604 | 522.8616 | 404.8372 | 390.8632 | 313.3799
698.6604 | 522.9105 | 405.0805 | 391.0171 | 314.0534
699.6604 | 523.0603 | 405.3404 | 391.4576 | 314.7457
700.6604 | 523.1308 | 405.5661 | 391.7126 | 315.422
701.6604 | 523.1322 | 405.684 | 391.8355 | 316.088
702.6604 | 523.1217 | 405.9785 | 391.8996 | 316.7368
703.6604 | 523.1773 | 406.3177 | 392.145 | 317.3983
704.6604 | 523.1036 | 406.579 | 392.2896 | 318.0367
705.6604 | 523.0347 | 406.8648 | 392.457 | 318.727
706.6604 | 523.1524 | 407.1486 | 392.9677 | 319.4518
707.6604 | 523.2207 | 407.3925 | 393.2767 | 320.1928
708.6604 | 523.1739 | 407.5846 | 393.71 | 320.9549
709.6604 | 523.0928 | 407.8556 | 394.1603 | 321.6781
710.6604 | 523.0315 | 408.0689 | 394.1599 | 322.3901
711.6604 | 523.0514 | 408.3145 | 394.4233 | 323.0724
712.6604 | 523 | 408.5785 | 394.6904 | 323.7624
713.6604 | 522.7931 | 408.799 | 395.072 | 324.4194
714.6604 | 522.7925 | 409.0831 | 395.1986 | 325.0601
715.6604 | 522.8754 | 409.3488 | 395.2601 | 325.7008
716.6604 | 522.8803 | 409.5902 | 395.4369 | 326.3234
717.6604 | 522.9925 | 409.8109 | 395.7334 | 326.9282
718.6604 | 523.0699 | 410.0757 | 395.9724 | 327.5289
719.6604 | 523.1665 | 410.325 | 396.3728 | 328.1518
720.6604 | 523.231 | 410.5728 | 396.5308 | 328.746
721.6604 | 523.2402 | 410.8365 | 396.581 | 329.3151
722.6604 | 523.431 | 411.0646 | 396.908 | 329.8649
723.6604 | 523.5544 | 411.3447 | 397.3071 | 330.4074
724.6604 | 523.5581 | 411.6149 | 397.4983 | 330.9422
725.6604 | 523.6842 | 411.8703 | 397.5394 | 331.4655
726.6604 | 523.7654 | 412.1065 | 397.8181 | 332.0194
727.6604 | 523.7347 | 412.3171 | 398.0175 | 332.5651
728.6604 | 523.7211 | 412.5337 | 398.2104 | 333.1003
729.6604 | 523.7581 | 412.7877 | 398.4381 | 333.6368
730.6604 | 523.6572 | 412.9641 | 398.6439 | 334.1486
731.6604 | 523.6175 | 413.2474 | 398.8832 | 334.6444
732.6604 | 523.591 | 413.5158 | 398.8583 | 335.1298
733.6604 | 523.6586 | 413.746 | 399.2819 | 335.6229
734.6604 | 523.7474 | 414.0191 | 399.7288 | 336.1273
735.6604 | 523.7509 | 414.2745 | 399.7641 | 336.6372
736.6604 | 523.7358 | 414.5315 | 400.1712 | 337.1383
737.6604 | 523.7204 | 414.8092 | 400.4514 | 337.6187
738.6604 | 523.6804 | 415.0286 | 400.5985 | 338.0795
739.6604 | 523.7157 | 415.2271 | 400.5759 | 338.5387
740.6604 | 523.6416 | 415.4885 | 400.9159 | 338.9925
741.6604 | 523.7486 | 415.7029 | 401.4002 | 339.4384
742.6604 | 523.8138 | 415.9575 | 401.5675 | 339.8884
743.6604 | 523.7883 | 416.2008 | 401.5684 | 340.3354
744.6604 | 523.9489 | 416.4557 | 401.827 | 340.7668
745.6604 | 524.0384 | 416.7068 | 402.1006 | 341.1936
746.6604 | 524.0057 | 416.9607 | 402.1895 | 341.6182
747.6604 | 523.982 | 417.2253 | 402.3885 | 342.0552
748.6604 | 524.1005 | 417.4415 | 402.5226 | 342.4658
749.6604 | 524.1972 | 417.7064 | 402.7511 | 342.907
750.6604 | 524.0984 | 417.9439 | 402.8489 | 343.3333
751.6604 | 524.0944 | 418.2258 | 403.0417 | 343.7632
752.6604 | 524.0164 | 418.4627 | 403.2967 | 344.1976
753.6604 | 524.0427 | 418.7422 | 403.8281 | 344.6332
754.6604 | 524.0396 | 418.9735 | 404.1158 | 345.0742
755.6604 | 524.0906 | 419.2289 | 404.3994 | 345.5034
756.6604 | 524.1173 | 419.4683 | 404.6894 | 345.9215
757.6604 | 524.2439 | 419.6699 | 404.7824 | 346.3297
758.6604 | 524.4081 | 419.8588 | 404.8126 | 346.7226
759.6604 | 524.3916 | 420.0737 | 404.9208 | 347.0982
760.6604 | 524.4773 | 420.3273 | 405.3136 | 347.4732
761.6604 | 524.5312 | 420.537 | 405.3096 | 347.8477
762.6604 | 524.5875 | 420.7563 | 405.337 | 348.194
763.6604 | 524.5579 | 420.9016 | 405.3534 | 348.5477
764.6604 | 524.5856 | 421.2339 | 405.6522 | 348.891
765.6604 | 524.5991 | 421.4696 | 405.8819 | 349.2386
766.6604 | 524.4843 | 421.7194 | 406.0462 | 349.5843
767.6604 | 524.2515 | 422.0011 | 406.3768 | 349.9287
768.6604 | 524.1616 | 422.2436 | 406.6269 | 350.2622
769.6604 | 524.0181 | 422.4492 | 406.8173 | 350.6028
770.6604 | 523.8842 | 422.7301 | 407.0957 | 350.9068
771.6604 | 523.8974 | 422.9546 | 407.0382 | 351.2801
772.6604 | 523.8886 | 423.1316 | 407.1294 | 351.63
773.6604 | 523.905 | 423.3861 | 407.5383 | 351.9793
774.6604 | 523.9155 | 423.6447 | 407.7506 | 352.3376
775.6604 | 523.9804 | 423.8602 | 407.8484 | 352.67
776.6604 | 523.8056 | 424.0715 | 407.946 | 353.0015
777.6604 | 523.7592 | 424.3165 | 408.2128 | 353.3272
778.6604 | 523.8195 | 424.5609 | 408.104 | 353.6471
779.6604 | 523.8336 | 424.7641 | 408.3452 | 353.9531
780.6604 | 523.9103 | 425.0061 | 408.5752 | 354.2639
781.6604 | 523.8551 | 425.2735 | 408.8577 | 354.5542
782.6604 | 523.8943 | 425.5649 | 408.7721 | 354.8479
783.6604 | 523.935 | 425.7106 | 409.022 | 355.1266
784.6604 | 523.8978 | 425.9741 | 409.4705 | 355.4346
785.6604 | 524.023 | 426.2266 | 409.7016 | 355.731
786.6604 | 524.0124 | 426.4898 | 409.9142 | 356.0284
787.6604 | 524.0636 | 426.649 | 410.2115 | 356.3188
788.6604 | 524.0823 | 426.8523 | 410.4046 | 356.6011
789.6604 | 523.9665 | 427.0824 | 410.3443 | 356.8783
790.6604 | 524.0181 | 427.3272 | 410.6568 | 357.149
791.6604 | 524.1429 | 427.5283 | 410.9872 | 357.4413
792.6604 | 524.2402 | 427.8251 | 411.0263 | 357.7172
793.6604 | 524.3526 | 428.0403 | 411.0879 | 358.005
794.6604 | 524.3558 | 428.2611 | 411.4105 | 358.2945
795.6604 | 524.3462 | 428.5026 | 411.5523 | 358.5859
796.6604 | 524.4337 | 428.7267 | 411.8523 | 358.8752
797.6604 | 524.4953 | 428.9593 | 412.3361 | 359.1625
798.6604 | 524.475 | 429.2216 | 412.6061 | 359.4634
799.6604 | 524.4081 | 429.4472 | 412.9046 | 359.7836
800.6604 | 524.3493 | 429.5901 | 413.2357 | 360.0856
801.6604 | 524.1704 | 429.8692 | 413.4984 | 360.3861
802.6604 | 524.2858 | 430.064 | 413.6805 | 360.6825
803.6604 | 524.3403 | 430.3272 | 413.8199 | 360.9817
804.6604 | 524.2868 | 430.5363 | 413.9714 | 361.2742
805.6604 | 524.1557 | 430.7855 | 414.1872 | 361.5401
806.6604 | 524.074 | 431.0014 | 414.4243 | 361.8053
807.6604 | 524.0706 | 431.2178 | 414.5734 | 362.064
808.6604 | 524.0712 | 431.4416 | 414.6468 | 362.3194
809.6604 | 524.0243 | 431.6646 | 414.716 | 362.5794
810.6604 | 523.9047 | 431.8954 | 414.8114 | 362.8269
811.6604 | 523.7008 | 432.0317 | 414.917 | 363.0715
812.6604 | 523.535 | 432.244 | 415.2889 | 363.3005
813.6604 | 523.6263 | 432.4963 | 415.4818 | 363.5366
814.6604 | 523.7128 | 432.7045 | 415.3326 | 363.7725
815.6604 | 523.6178 | 432.9214 | 415.6251 | 364.0109
816.6604 | 523.5926 | 433.1873 | 416.1123 | 364.2428
817.6604 | 523.6185 | 433.4276 | 416.1609 | 364.4806
818.6604 | 523.6718 | 433.6772 | 416.1023 | 364.6953
819.6604 | 523.6379 | 433.8883 | 416.3468 | 364.9111
820.6604 | 523.5787 | 434.0682 | 416.4795 | 365.1348
821.6604 | 523.4504 | 434.3001 | 416.6781 | 365.3504
822.6604 | 523.5218 | 434.4924 | 417.0007 | 365.5822
823.6604 | 523.599 | 434.6677 | 417.0684 | 365.8229
824.6604 | 523.5584 | 434.8977 | 417.3646 | 366.0387
825.6604 | 523.5785 | 435.1097 | 417.3725 | 366.2532
826.6604 | 523.5484 | 435.3106 | 417.7242 | 366.4837
827.6604 | 523.4568 | 435.5254 | 417.7989 | 366.708
828.6604 | 523.4259 | 435.7098 | 417.9289 | 366.9285
829.6604 | 523.3431 | 435.9056 | 418.029 | 367.152
830.6604 | 523.4287 | 436.0772 | 418.1114 | 367.3643
831.6604 | 523.3932 | 436.3036 | 418.3014 | 367.5944
832.6604 | 523.2503 | 436.4415 | 418.739 | 367.8249
833.6604 | 523.0887 | 436.675 | 419.0424 | 368.0456
834.6604 | 523.2093 | 436.8702 | 418.9799 | 368.2674
835.6604 | 523.3073 | 437.0654 | 418.8985 | 368.4753
836.6604 | 523.343 | 437.2239 | 418.8563 | 368.698
837.6604 | 523.2768 | 437.5091 | 419.2028 | 368.9237
838.6604 | 523.195 | 437.7188 | 419.3586 | 369.172
839.6604 | 523.1337 | 437.9219 | 419.3843 | 369.4059
840.6604 | 523.1725 | 438.1418 | 419.6399 | 369.6444
841.6604 | 523.2327 | 438.3134 | 419.803 | 369.9023
842.6604 | 523.27 | 438.5238 | 420.1317 | 370.165
843.6604 | 523.3409 | 438.6693 | 420.3059 | 370.405
844.6604 | 523.3205 | 438.8603 | 420.4074 | 370.6318
845.6604 | 523.3558 | 439.0785 | 420.6922 | 370.8529
846.6604 | 523.3396 | 439.3601 | 420.774 | 371.1103
847.6604 | 523.3605 | 439.5703 | 421.0072 | 371.3433
848.6604 | 523.476 | 439.7693 | 421.2339 | 371.5739
849.6604 | 523.5031 | 440.0125 | 421.3476 | 371.8013
850.6604 | 523.5412 | 440.1934 | 421.5484 | 372.0179
851.6604 | 523.5361 | 440.3418 | 421.9667 | 372.2425
852.6604 | 523.5244 | 440.5628 | 421.9299 | 372.4643
853.6604 | 523.5372 | 440.7002 | 421.7868 | 372.6954
854.6604 | 523.5529 | 440.9494 | 422.1467 | 372.9274
855.6604 | 523.5362 | 441.1334 | 422.2455 | 373.1584
856.6604 | 523.6014 | 441.3242 | 422.3865 | 373.3991
857.6604 | 523.5761 | 441.5611 | 422.816 | 373.6191
858.6604 | 523.521 | 441.738 | 422.974 | 373.8502
859.6604 | 523.4822 | 441.9599 | 422.846 | 374.0807
860.6604 | 523.4676 | 442.1551 | 422.7674 | 374.3257
861.6604 | 523.4443 | 442.2811 | 422.9583 | 374.5555
862.6604 | 523.3695 | 442.4023 | 423.2124 | 374.7879
863.6604 | 523.2418 | 442.5 | 423.408 | 375.0007
864.6604 | 523.1257 | 442.7262 | 423.6915 | 375.1992
865.6604 | 523.1324 | 443.0019 | 423.7721 | 375.3843
866.6604 | 523.0795 | 443.2191 | 423.9511 | 375.5751
867.6604 | 523.1102 | 443.4623 | 424.247 | 375.7667
868.6604 | 523.1349 | 443.6659 | 424.4693 | 375.9571
869.6604 | 523.2359 | 443.8297 | 424.3752 | 376.1347
870.6604 | 523.2253 | 443.9522 | 424.6024 | 376.3434
871.6604 | 523.1865 | 444.1495 | 424.7233 | 376.5263
872.6604 | 523.2132 | 444.2798 | 424.6719 | 376.7434
873.6604 | 523.1593 | 444.5276 | 425.1732 | 376.9564
874.6604 | 523.1988 | 444.7548 | 425.2976 | 377.1744
875.6604 | 523.2296 | 444.9537 | 425.3195 | 377.388
876.6604 | 523.2903 | 445.1562 | 425.7264 | 377.5947
877.6604 | 523.3537 | 445.3645 | 425.8921 | 377.7987
878.6604 | 523.4244 | 445.4751 | 425.6032 | 377.9951
879.6604 | 523.5909 | 445.6098 | 425.825 | 378.2048
880.6604 | 523.6409 | 445.8048 | 425.9972 | 378.3998
881.6604 | 523.5926 | 445.9852 | 426.1884 | 378.6019
882.6604 | 523.6751 | 446.1974 | 426.5035 | 378.7967
883.6604 | 523.7674 | 446.367 | 426.4139 | 378.9928
884.6604 | 523.7878 | 446.5048 | 426.2236 | 379.1858
885.6604 | 523.6752 | 446.7455 | 426.2258 | 379.3892
886.6604 | 523.7144 | 446.9336 | 426.4007 | 379.5942
887.6604 | 523.7598 | 447.1361 | 426.7977 | 379.8218
888.6604 | 523.7766 | 447.3055 | 426.8741 | 380.0511
889.6604 | 523.8883 | 447.5063 | 426.9072 | 380.2617
890.6604 | 523.9043 | 447.7046 | 427.29 | 380.4766
891.6604 | 523.7989 | 447.7937 | 427.5421 | 380.6872
892.6604 | 523.7816 | 448.0036 | 427.5917 | 380.8975
893.6604 | 523.6964 | 448.2042 | 427.5372 | 381.1018
894.6604 | 523.6681 | 448.434 | 427.6585 | 381.3274
895.6604 | 523.6749 | 448.6006 | 427.9118 | 381.5542
896.6604 | 523.6303 | 448.7905 | 428.1431 | 381.7799
897.6604 | 523.4743 | 448.9323 | 428.0815 | 382.0139
898.6604 | 523.3936 | 449.1275 | 428.2456 | 382.2462
899.6604 | 523.4104 | 449.3231 | 428.7793 | 382.4776
900.6604 | 523.3696 | 449.4507 | 429.1551 | 382.7245
901.6604 | 523.4689 | 449.5518 | 429.3533 | 382.9828
902.6604 | 523.4411 | 449.7511 | 429.5591 | 383.2378
903.6604 | 523.3257 | 449.9105 | 429.6342 | 383.4964
904.6604 | 523.1679 | 450.0901 | 429.6361 | 383.7385
905.6604 | 523.0606 | 450.2473 | 430.0836 | 383.9796
906.6604 | 522.9807 | 450.4235 | 430.3405 | 384.2127
907.6604 | 523.0869 | 450.5436 | 430.5508 | 384.4489
908.6604 | 523.0123 | 450.7778 | 430.5689 | 384.6885
909.6604 | 522.9961 | 450.9332 | 430.5134 | 384.9364
910.6604 | 522.9221 | 451.0624 | 430.3438 | 385.1976
911.6604 | 522.8873 | 451.1698 | 430.6848 | 385.4633
912.6604 | 522.8433 | 451.4078 | 430.8689 | 385.7203
913.6604 | 522.8368 | 451.5706 | 431.0246 | 385.9783
914.6604 | 522.9538 | 451.7689 | 430.9567 | 386.2388
915.6604 | 523.0947 | 451.9575 | 431.0578 | 386.4933
916.6604 | 523.2484 | 452.0978 | 431.3532 | 386.7551
917.6604 | 523.3365 | 452.247 | 431.2955 | 387.0238
918.6604 | 523.4103 | 452.3787 | 431.3516 | 387.2807
919.6604 | 523.3941 | 452.5406 | 431.6076 | 387.5414
920.6604 | 523.4042 | 452.6604 | 431.4862 | 387.8068
921.6604 | 523.4875 | 452.7879 | 431.7194 | 388.1039
922.6604 | 523.4556 | 452.972 | 431.8766 | 388.4016
923.6604 | 523.3961 | 453.1409 | 431.8508 | 388.6976
924.6604 | 523.4315 | 453.2668 | 431.9734 | 388.9679
925.6604 | 523.4895 | 453.3831 | 432.4119 | 389.2483
926.6604 | 523.5248 | 453.5352 | 432.5559 | 389.5438
927.6604 | 523.5609 | 453.7345 | 432.6265 | 389.8496
928.6604 | 523.5675 | 453.9097 | 432.8438 | 390.1321
929.6604 | 523.6039 | 454.0527 | 433.0729 | 390.4259
930.6604 | 523.5489 | 454.2417 | 433.2302 | 390.7259
931.6604 | 523.6036 | 454.371 | 433.3438 | 391.0428
932.6604 | 523.7312 | 454.5144 | 433.7265 | 391.3632
933.6604 | 523.7929 | 454.7009 | 433.7671 | 391.6868
934.6604 | 523.7447 | 454.8394 | 433.7539 | 391.9976
935.6604 | 523.7009 | 454.8993 | 434.1187 | 392.2944
936.6604 | 523.723 | 455.1012 | 434.2505 | 392.6072
937.6604 | 523.7178 | 455.3277 | 434.1801 | 392.923
938.6604 | 523.8057 | 455.4621 | 434.2951 | 393.2386
939.6604 | 523.8433 | 455.6161 | 434.4724 | 393.5597
940.6604 | 523.6641 | 455.7668 | 434.6735 | 393.8801
941.6604 | 523.6615 | 455.8219 | 434.8953 | 394.2135
942.6604 | 523.7194 | 456.0377 | 435.0395 | 394.5309
943.6604 | 523.7255 | 456.1984 | 435.1294 | 394.854
944.6604 | 523.7004 | 456.3715 | 435.0624 | 395.1664
945.6604 | 523.6499 | 456.5577 | 435.234 | 395.4721
946.6604 | 523.6816 | 456.6926 | 435.7478 | 395.7736
947.6604 | 523.6965 | 456.7364 | 436.048 | 396.0756
948.6604 | 523.6247 | 456.9309 | 436.0872 | 396.3796
949.6604 | 523.6423 | 457.1003 | 436.161 | 396.6824
950.6604 | 523.7526 | 457.3171 | 436.1709 | 396.9861
951.6604 | 523.8699 | 457.3804 | 436.3143 | 397.2746
952.6604 | 523.828 | 457.5376 | 436.7446 | 397.5801
953.6604 | 523.6734 | 457.7147 | 436.9844 | 397.8635
954.6604 | 523.5961 | 457.8838 | 436.8355 | 398.1661
955.6604 | 523.5033 | 457.9689 | 436.8854 | 398.464
956.6604 | 523.5303 | 458.0579 | 436.8828 | 398.7706
957.6604 | 523.4454 | 458.2138 | 436.6942 | 399.0894
958.6604 | 523.4405 | 458.4056 | 436.6805 | 399.4004
959.6604 | 523.39 | 458.5882 | 437.1062 | 399.6984
960.6604 | 523.2814 | 458.7213 | 437.1313 | 400.0044
961.676 | 523.4008 | 458.8946 | 437.3763 | 400.316
962.6604 | 523.3608 | 459.0432 | 437.5051 | 400.6143
963.6604 | 523.4081 | 459.1661 | 437.9513 | 400.9284
964.6604 | 523.4345 | 459.2943 | 438.2233 | 401.2479
965.6604 | 523.449 | 459.3994 | 438.0523 | 401.5605
966.6604 | 523.4248 | 459.4972 | 438.301 | 401.865
967.6604 | 523.4385 | 459.6472 | 438.573 | 402.1697
968.6604 | 523.4413 | 459.7724 | 438.4718 | 402.4726
969.6604 | 523.5543 | 459.9467 | 438.8086 | 402.7765
970.6604 | 523.6459 | 460.0477 | 438.9413 | 403.0776
971.6604 | 523.6839 | 460.1557 | 439.1891 | 403.3896
972.6604 | 523.7216 | 460.368 | 439.0301 | 403.7034
973.6604 | 523.6789 | 460.5122 | 439.1086 | 403.9926
974.6604 | 523.7779 | 460.5634 | 439.2199 | 404.3325
975.6604 | 523.717 | 460.7426 | 439.2269 | 404.6397
976.6604 | 523.6892 | 460.8982 | 439.3658 | 404.9324
977.6604 | 523.7285 | 461.0533 | 439.1583 | 405.2462
978.6604 | 523.7572 | 461.1474 | 439.4233 | 405.5513
979.6604 | 523.7225 | 461.1953 | 439.8068 | 405.8534
980.6604 | 523.7002 | 461.345 | 439.9054 | 406.1639
981.6604 | 523.7083 | 461.5125 | 439.926 | 406.4675
982.6604 | 523.6739 | 461.6498 | 440.0112 | 406.7587
983.6604 | 523.6685 | 461.7526 | 439.6421 | 407.0318
984.6604 | 523.5569 | 461.8889 | 439.788 | 407.3178
985.6604 | 523.5776 | 462.0454 | 439.8272 | 407.5833
986.6604 | 523.4888 | 462.1394 | 440.1469 | 407.8785
987.6604 | 523.3777 | 462.2631 | 440.2844 | 408.1497
988.6604 | 523.3252 | 462.37 | 440.4534 | 408.4253
989.6604 | 523.2117 | 462.5366 | 440.5152 | 408.6624
990.6604 | 523.073 | 462.6563 | 440.5047 | 408.9225
991.6604 | 523.1276 | 462.8092 | 440.5054 | 409.1835
992.6604 | 523.2012 | 462.9253 | 440.7519 | 409.4486
993.6604 | 523.2647 | 463.0491 | 441.1264 | 409.7055
994.6604 | 523.2838 | 463.1892 | 440.9545 | 409.9781
995.6604 | 523.2501 | 463.2916 | 441.1489 | 410.2252
996.6604 | 523.2079 | 463.4348 | 441.2889 | 410.4744
997.6604 | 523.2615 | 463.5832 | 441.4945 | 410.7069
998.6604 | 523.2882 | 463.6386 | 441.6726 | 410.9511
999.6604 | 523.2874 | 463.6552 | 441.7787 | 411.1963
1000.6604 | 523.1793 | 463.7868 | 442.0603 | 411.4276
1001.6604 | 523.0897 | 463.8969 | 442.0064 | 411.6447
1002.6604 | 523.0709 | 464.0174 | 442.1232 | 411.8941
1003.6604 | 523.0535 | 464.1886 | 442.3796 | 412.1382
1004.6604 | 522.9977 | 464.3067 | 442.3603 | 412.3602
1005.6604 | 523.0483 | 464.4124 | 442.7472 | 412.5787
1006.6604 | 522.9917 | 464.5078 | 443.0121 | 412.7914
1007.6604 | 522.9905 | 464.6544 | 442.9957 | 413
1008.6604 | 522.9276 | 464.7421 | 442.8294 | 413.218
1009.6604 | 522.8002 | 464.7824 | 443.1896 | 413.419
1010.6604 | 522.9074 | 464.9765 | 443.3661 | 413.6101
1011.6604 | 523.0361 | 465.0464 | 443.1917 | 413.7839
1012.6604 | 523.1568 | 465.1689 | 443.4017 | 413.9642
1013.6604 | 523.2535 | 465.2615 | 443.4931 | 414.1519
1014.6604 | 523.3548 | 465.4093 | 443.5399 | 414.3375
1015.6604 | 523.4517 | 465.603 | 443.5575 | 414.4951
1016.6604 | 523.5723 | 465.7723 | 444.0589 | 414.666
1017.6604 | 523.6379 | 465.8833 | 443.8408 | 414.8428
1018.6604 | 523.614 | 465.9595 | 444.0155 | 415.0172
1019.6604 | 523.5632 | 466.1119 | 444.0608 | 415.1885
1020.6604 | 523.6436 | 466.2017 | 444.0119 | 415.3833
1021.6604 | 523.8054 | 466.2782 | 443.9815 | 415.5771
1022.6604 | 523.8948 | 466.4115 | 444.1765 | 415.7516
1023.6604 | 523.9548 | 466.4194 | 444.3848 | 415.9222
1024.6604 | 523.892 | 466.485 | 444.5176 | 416.0916
1025.6604 | 523.8936 | 466.682 | 444.5114 | 416.2943
1026.6604 | 523.7927 | 466.8179 | 444.5962 | 416.4779
1027.6604 | 523.7959 | 466.9259 | 444.5577 | 416.6681
1028.6604 | 523.7265 | 466.9933 | 444.6854 | 416.8304
1029.6604 | 523.7469 | 467.1167 | 444.5515 | 416.9848
1030.6604 | 523.6742 | 467.2055 | 444.6531 | 417.1832
1031.6604 | 523.5485 | 467.3591 | 444.763 | 417.3244
1032.6604 | 523.4734 | 467.4859 | 445.0633 | 417.5391
1033.6604 | 523.4361 | 467.5169 | 445.501 | 417.7176
1034.6604 | 523.3459 | 467.6133 | 445.2793 | 417.8882
1035.6604 | 523.3609 | 467.7272 | 445.3423 | 418.0513
1036.6604 | 523.3598 | 467.7921 | 445.8016 | 418.2216
1037.6604 | 523.2959 | 467.8352 | 445.9593 | 418.3987
1038.6604 | 523.3642 | 467.9838 | 446.0025 | 418.5673
1039.6604 | 523.296 | 468.0541 | 445.9052 | 418.7302
1040.6604 | 523.3482 | 468.1487 | 446.065 | 418.8903
1041.6604 | 523.4027 | 468.2734 | 446.4309 | 419.056
1042.6604 | 523.4899 | 468.4094 | 446.3474 | 419.2235
1043.6604 | 523.4423 | 468.5364 | 446.2908 | 419.3909
1044.6604 | 523.425 | 468.645 | 446.416 | 419.5537
1045.6604 | 523.4307 | 468.7146 | 446.4098 | 419.7103
1046.6604 | 523.3603 | 468.8044 | 446.1876 | 419.8671
1047.6604 | 523.4601 | 468.8986 | 446.438 | 420.0288
1048.6604 | 523.4669 | 468.9917 | 446.5854 | 420.1776
1049.6604 | 523.3104 | 469.118 | 446.8502 | 420.3373
1050.6604 | 523.2289 | 469.1644 | 446.869 | 420.4802
1051.6604 | 523.1553 | 469.2106 | 447.2308 | 420.6466
1052.6604 | 523.0781 | 469.3336 | 447.5147 | 420.7885
1053.6604 | 523.177 | 469.4237 | 447.7805 | 420.9348
1054.6604 | 523.2646 | 469.5325 | 447.3833 | 421.0629
1055.6604 | 523.3275 | 469.4851 | 447.4082 | 421.1939
1056.6604 | 523.4041 | 469.6604 | 447.4288 | 421.333
1057.6604 | 523.4737 | 469.8001 | 447.4066 | 421.4719
1058.6604 | 523.6334 | 469.8336 | 447.6219 | 421.6078
1059.6604 | 523.5449 | 469.988 | 447.7042 | 421.7493
1060.6604 | 523.5783 | 470.0615 | 447.6657 | 421.8807
1061.6604 | 523.6554 | 470.2108 | 447.896 | 422.0127
1062.6604 | 523.785 | 470.3137 | 448.0081 | 422.1317
1063.6604 | 523.7902 | 470.4241 | 448.232 | 422.2605
1064.6604 | 523.7038 | 470.5199 | 448.6564 | 422.395
1065.6604 | 523.7105 | 470.6452 | 448.7887 | 422.5183
1066.6604 | 523.5767 | 470.7122 | 448.8341 | 422.6352
1067.6604 | 523.5484 | 470.7896 | 448.4873 | 422.7518
1068.6604 | 523.6342 | 470.8609 | 448.536 | 422.8733
1069.6604 | 523.6397 | 470.9548 | 448.3364 | 423.0277
1070.6604 | 523.6539 | 471.1307 | 448.3891 | 423.1613
1071.6604 | 523.6887 | 471.2402 | 448.7834 | 423.2822
1072.6604 | 523.7236 | 471.3719 | 449.2799 | 423.4088
1073.6604 | 523.6311 | 471.4687 | 449.403 | 423.5265
1074.6604 | 523.6201 | 471.4904 | 449.2877 | 423.6462
1075.6604 | 523.7244 | 471.6066 | 449.5522 | 423.7616
1076.6604 | 523.6638 | 471.7197 | 449.6087 | 423.9333
1077.676 | 523.6252 | 471.7898 | 449.6414 | 424.0897
1078.6604 | 523.5494 | 471.8985 | 450.0039 | 424.2427
1079.6604 | 523.44 | 471.9598 | 450.266 | 424.3677
1080.6604 | 523.3822 | 472.0425 | 450.178 | 424.4993
1081.6604 | 523.4271 | 472.1562 | 450.1072 | 424.6043
1082.6604 | 523.3666 | 472.1726 | 450.298 | 424.7051
1083.6604 | 523.2583 | 472.2424 | 450.1867 | 424.8236
1084.6604 | 523.2745 | 472.3744 | 450.678 | 424.928
1085.6604 | 523.1403 | 472.4802 | 450.6824 | 425.0339
1086.6604 | 523.0628 | 472.6007 | 450.7928 | 425.1264
1087.6604 | 522.9376 | 472.6253 | 450.698 | 425.2082
1088.6604 | 522.9418 | 472.7018 | 450.9386 | 425.3382
1089.6604 | 522.978 | 472.7329 | 451.3075 | 425.4235
1090.6604 | 522.8713 | 472.8449 | 451.4283 | 425.5274
1091.6604 | 522.9112 | 472.9083 | 451.5391 | 425.6579
1092.6604 | 522.9004 | 472.9884 | 451.4697 | 425.7452
1093.6604 | 522.8521 | 473.0314 | 451.1874 | 425.9017
1094.6604 | 522.8619 | 473.1265 | 451.2213 | 426.0232
1095.6604 | 522.8097 | 473.247 | 451.3883 | 426.1183
1096.6604 | 522.7426 | 473.3272 | 451.2361 | 426.214
1097.6604 | 522.6854 | 473.396 | 451.3213 | 426.3112
1098.6604 | 522.6046 | 473.4577 | 451.7713 | 426.3984
1099.6604 | 522.6136 | 473.5451 | 451.8534 | 426.507
1100.6604 | 522.6879 | 473.6677 | 451.9277 | 426.6173
1101.6604 | 522.7385 | 473.7729 | 452.0539 | 426.7318
1102.6604 | 522.8637 | 473.9094 | 452.3667 | 426.8419
1103.6604 | 522.8408 | 474.0081 | 452.193 | 426.9528
1104.6604 | 522.9383 | 474.0484 | 452.1255 | 427.091
1105.6604 | 522.981 | 474.1422 | 452.4268 | 427.2057
1106.6604 | 522.8787 | 474.2061 | 452.3223 | 427.3157
1107.6604 | 522.9811 | 474.3461 | 452.5008 | 427.4161
1108.6604 | 523.0461 | 474.3781 | 452.5149 | 427.5413
1109.6604 | 523.0521 | 474.393 | 452.221 | 427.6314
1110.6604 | 523.0267 | 474.5364 | 452.4298 | 427.725
1111.6604 | 522.8618 | 474.4726 | 452.4919 | 427.7962
1112.6604 | 522.9805 | 474.5602 | 452.5584 | 427.8907
1113.6604 | 522.9871 | 474.6979 | 452.8261 | 427.9676
1114.6604 | 522.973 | 474.6709 | 453.1091 | 428.0551
1115.6604 | 523.0296 | 474.8629 | 452.9975 | 428.1503
1116.6604 | 523.0372 | 474.9679 | 452.986 | 428.2367
1117.6604 | 523.0609 | 475.0433 | 453.3017 | 428.3127
1118.6604 | 523.0376 | 475.1471 | 453.4367 | 428.3895
1119.6604 | 523.0237 | 475.1619 | 453.4116 | 428.518
1120.6604 | 522.9636 | 475.2275 | 453.5361 | 428.582
1121.6604 | 522.9736 | 475.3306 | 453.3274 | 428.6686
1122.6604 | 523.0113 | 475.3584 | 453.5475 | 428.7647
1123.6604 | 523.0474 | 475.473 | 453.6299 | 428.8622
1124.6604 | 522.9959 | 475.5629 | 453.9998 | 428.9732
1125.6604 | 523.0564 | 475.5599 | 454.2786 | 429.0564
1126.6604 | 523.1616 | 475.6652 | 454.2615 | 429.1365
1127.6604 | 523.1787 | 475.7827 | 454.0847 | 429.2648
1128.6604 | 523.1627 | 475.8777 | 454.0104 | 429.3495
1129.6604 | 523.2331 | 475.9832 | 454.1523 | 429.4437
1130.6604 | 523.2063 | 476.1283 | 454.252 | 429.5594
1131.6604 | 523.25 | 476.0892 | 454.1896 | 429.6301
1132.6604 | 523.2807 | 476.1556 | 454.0384 | 429.7531
1133.6604 | 523.4191 | 476.1959 | 453.9584 | 429.8608
1134.6604 | 523.3194 | 476.3065 | 454.0286 | 429.9747
1135.6604 | 523.2162 | 476.379 | 454.4146 | 430.0449
1136.6604 | 523.1919 | 476.5074 | 454.7483 | 430.1327
1137.6604 | 523.3431 | 476.6382 | 454.8317 | 430.2106
1138.6604 | 523.4023 | 476.6779 | 454.7156 | 430.2898
1139.6604 | 523.4687 | 476.699 | 454.7353 | 430.4067
1140.6604 | 523.4568 | 476.7935 | 454.6424 | 430.5012
1141.6604 | 523.4244 | 476.8116 | 454.6221 | 430.6091
1142.6604 | 523.5115 | 476.8688 | 454.722 | 430.7076
1143.6604 | 523.5762 | 476.9134 | 454.9997 | 430.8196
1144.6604 | 523.5946 | 477.0114 | 455.2055 | 430.9232
1145.6604 | 523.6769 | 477.1607 | 455.2955 | 431.01
1146.6604 | 523.7237 | 477.2596 | 455.328 | 431.1071
1147.6604 | 523.7756 | 477.3248 | 455.4049 | 431.1912
1148.6604 | 523.8406 | 477.3222 | 455.5162 | 431.3057
1149.6604 | 523.7838 | 477.4737 | 455.9073 | 431.4314
1150.6604 | 523.8549 | 477.5849 | 455.9204 | 431.5282
1151.6604 | 523.7827 | 477.5889 | 455.9969 | 431.6633
1152.6604 | 523.827 | 477.7365 | 456.2052 | 431.7627
1153.6604 | 523.7871 | 477.7691 | 456.0696 | 431.8531
1154.6604 | 523.6809 | 477.7489 | 455.9423 | 431.9888
1155.6604 | 523.6353 | 477.819 | 455.9699 | 432.0642
1156.6604 | 523.6297 | 477.8955 | 455.6776 | 432.2256
1157.6604 | 523.6202 | 478.0165 | 455.6758 | 432.3777
1158.6604 | 523.6078 | 478.102 | 456.0748 | 432.5201
1159.6604 | 523.6246 | 478.1188 | 455.9243 | 432.6714
1160.6604 | 523.6355 | 478.1168 | 455.909 | 432.793
1161.6604 | 523.7017 | 478.1992 | 455.6263 | 432.9266
1162.6604 | 523.6703 | 478.3163 | 455.9896 | 433.0671
1163.6604 | 523.7359 | 478.3954 | 456.014 | 433.1666
1164.6604 | 523.7985 | 478.4578 | 456.199 | 433.3146
1165.6604 | 523.7855 | 478.5227 | 456.0775 | 433.4389
1166.6604 | 523.895 | 478.6147 | 456.156 | 433.5651
1167.6604 | 523.8583 | 478.6318 | 456.1341 | 433.6823
1168.6604 | 523.897 | 478.6809 | 455.9389 | 433.8216
1169.6604 | 523.9871 | 478.7996 | 456.0633 | 433.9518
1170.6604 | 524.0373 | 478.8856 | 456.0503 | 434.0733
1171.6604 | 524.0954 | 478.915 | 456.0582 | 434.2404
1172.6604 | 524.1373 | 478.9989 | 456.2617 | 434.3595
1173.6604 | 524.085 | 479.068 | 456.3143 | 434.4726
1174.6604 | 524.1064 | 479.161 | 456.2492 | 434.6129
1175.6604 | 524.1758 | 479.2265 | 456.2166 | 434.7505
1176.6604 | 524.3103 | 479.2677 | 456.5025 | 434.888
1177.6604 | 524.2448 | 479.3166 | 456.4615 | 435.0533
1178.6604 | 524.2321 | 479.4259 | 456.9586 | 435.2008
1179.6604 | 524.2099 | 479.5056 | 457.1847 | 435.313
1180.6604 | 524.2351 | 479.5689 | 457.5118 | 435.4636
1181.6604 | 524.2171 | 479.5671 | 457.3783 | 435.6179
1182.6604 | 524.1 | 479.6585 | 457.55 | 435.7642
1183.6604 | 523.9788 | 479.7549 | 457.4596 | 435.8715
1184.6604 | 523.9491 | 479.8619 | 457.745 | 436.0456
1185.6604 | 523.7954 | 479.9184 | 457.8873 | 436.1635
1186.6604 | 523.7824 | 480.0006 | 457.9033 | 436.2809
1187.6604 | 523.8101 | 480.0656 | 457.7296 | 436.4076
1188.6604 | 523.8997 | 479.9965 | 457.8579 | 436.5664
1189.6604 | 523.988 | 480.1144 | 457.8063 | 436.6993
1190.6604 | 524.0397 | 480.1774 | 457.8621 | 436.8287
1191.6604 | 524.0871 | 480.2696 | 458.0998 | 436.9367
1192.6604 | 524.0988 | 480.3547 | 458.3476 | 437.1155
1193.6604 | 524.0153 | 480.377 | 458.4545 | 437.2417
1194.6604 | 523.9546 | 480.4836 | 458.2866 | 437.4218
1195.6604 | 523.8927 | 480.5372 | 458.7479 | 437.511
1196.6604 | 523.9136 | 480.5424 | 458.7623 | 437.6577
1197.6604 | 523.9104 | 480.679 | 458.78 | 437.7692
1198.6604 | 523.7641 | 480.7568 | 458.7826 | 437.8837
1199.6604 | 523.6979 | 480.807 | 458.5636 | 438.0311
1200.6604 | 523.7543 | 480.8936 | 458.6127 | 438.0969
1201.6604 | 523.7743 | 480.9778 | 458.8153 | 438.2213
1202.6604 | 523.8781 | 481.0678 | 459.0459 | 438.3771
1203.6604 | 523.9741 | 481.0313 | 459.0448 | 438.5012
1204.6604 | 524.021 | 481.1495 | 458.8914 | 438.6364
1205.6604 | 523.9624 | 481.2719 | 458.8442 | 438.7379
1206.6604 | 523.824 | 481.2718 | 459.0106 | 438.878
1207.6604 | 523.801 | 481.3484 | 458.9771 | 439.0752
1208.6604 | 523.956 | 481.4065 | 459.0958 | 439.246
1209.6604 | 524.0035 | 481.4092 | 459.1236 | 439.4532
1210.6604 | 524.0122 | 481.4381 | 459.1096 | 439.6118
1211.6604 | 524.1105 | 481.5616 | 459.2839 | 439.7476
1212.6604 | 524.0718 | 481.577 | 459.2439 | 439.8921
1213.6604 | 524.1418 | 481.5882 | 459.1754 | 440.0611
1214.6604 | 524.3391 | 481.6634 | 459.1235 | 440.2287
1215.6604 | 524.3919 | 481.7528 | 459.2273 | 440.3638
1216.6604 | 524.4278 | 481.8356 | 459.621 | 440.5293
1217.6604 | 524.5568 | 481.9099 | 459.4853 | 440.7
1218.6604 | 524.6651 | 482.0213 | 459.8294 | 440.8683
1219.6604 | 524.6887 | 482.0472 | 460.1895 | 441.0585
1220.6604 | 524.6823 | 482.1182 | 460.0288 | 441.153
1221.6604 | 524.7116 | 482.1913 | 460.0926 | 441.318
1222.6604 | 524.7141 | 482.2169 | 460.0745 | 441.5313
1223.6604 | 524.6056 | 482.2804 | 460.365 | 441.7292
1224.6604 | 524.5742 | 482.2947 | 460.5963 | 441.9269
1225.6604 | 524.4467 | 482.2799 | 460.7238 | 442.0759
1226.6604 | 524.4262 | 482.2896 | 460.703 | 442.2555
1227.6604 | 524.3683 | 482.4132 | 460.6145 | 442.3957
1228.6604 | 524.3069 | 482.4328 | 460.595 | 442.5416
1229.6604 | 524.3042 | 482.4972 | 460.4512 | 442.7327
1230.6604 | 524.2612 | 482.5841 | 460.7821 | 442.8481
1231.6604 | 524.1727 | 482.6703 | 460.7724 | 443.0321
1232.6604 | 523.9411 | 482.631 | 460.8952 | 443.1927
1233.6604 | 523.8127 | 482.63 | 460.8686 | 443.3667
1234.6604 | 523.6587 | 482.7166 | 460.8742 | 443.5218
1235.6604 | 523.5408 | 482.7905 | 460.7148 | 443.6649
1236.6604 | 523.4659 | 482.9106 | 460.7744 | 443.8203
1237.6604 | 523.3551 | 483.0196 | 460.8951 | 443.9999
1238.6604 | 523.4127 | 483.0419 | 460.7929 | 444.1528
1239.6604 | 523.4138 | 483.0779 | 461.2992 | 444.3076
1240.6604 | 523.4011 | 483.2291 | 461.5127 | 444.4361
1241.6604 | 523.288 | 483.3251 | 461.7296 | 444.5671
1242.6604 | 523.2076 | 483.3575 | 461.7901 | 444.6887
1243.6604 | 523.0576 | 483.406 | 461.9188 | 444.8217
1244.6604 | 523.0567 | 483.4987 | 461.9922 | 445.0255
1245.6604 | 522.9699 | 483.4834 | 462.1385 | 445.138
1246.6604 | 523.0413 | 483.581 | 462.1343 | 445.3056
1247.6604 | 522.9009 | 483.6357 | 462.0733 | 445.4198
1248.6604 | 522.9383 | 483.6433 | 462.2521 | 445.5773
1249.6604 | 522.9699 | 483.7603 | 462.3654 | 445.7242
1250.6604 | 523.0234 | 483.7091 | 462.2869 | 445.8317
1251.6604 | 523.032 | 483.7992 | 462.1025 | 445.9511
1252.6604 | 523.0839 | 483.8798 | 462.2271 | 446.1021
1253.6604 | 523.1057 | 483.9415 | 462.0854 | 446.2445
1254.6604 | 523.1323 | 483.9599 | 462.3482 | 446.4193
1255.6604 | 523.2309 | 484.0221 | 462.5117 | 446.5193
1256.6604 | 523.2958 | 484.0841 | 462.5443 | 446.6937
1257.6604 | 523.303 | 484.1609 | 462.6862 | 446.7672
1258.6604 | 523.2965 | 484.1974 | 462.6749 | 446.89
1259.6604 | 523.3048 | 484.2023 | 462.7604 | 446.9984
1260.6604 | 523.4894 | 484.2326 | 462.5645 | 447.1481
1261.6604 | 523.5928 | 484.3508 | 462.6688 | 447.2963
1262.6604 | 523.7165 | 484.3761 | 462.436 | 447.3522
1263.6604 | 523.6794 | 484.287 | 462.5462 | 447.5094
1264.6604 | 523.5681 | 484.4406 | 462.7827 | 447.6721
1265.6604 | 523.5216 | 484.5227 | 462.7421 | 447.7986
1266.6604 | 523.4751 | 484.6007 | 463.0572 | 447.8732
1267.6604 | 523.4327 | 484.6551 | 463.0155 | 448.0784
1268.6604 | 523.431 | 484.705 | 462.8491 | 448.2315
1269.6604 | 523.4989 | 484.7568 | 462.9123 | 448.4075
1270.6604 | 523.5939 | 484.7157 | 462.9055 | 448.5166
1271.6604 | 523.5398 | 484.7544 | 463.0118 | 448.6928
1272.6604 | 523.5854 | 484.8709 | 463.2236 | 448.8687
1273.6604 | 523.5601 | 484.988 | 463.4082 | 448.9719
1274.6604 | 523.5234 | 485.0222 | 463.662 | 449.135
1275.6604 | 523.403 | 485.0647 | 463.3946 | 449.2701
1276.6604 | 523.2867 | 485.0443 | 463.5447 | 449.3946
1277.6604 | 523.2158 | 485.0629 | 463.2694 | 449.5396
1278.6604 | 523.157 | 485.027 | 463.0469 | 449.6182
1279.6604 | 523.2339 | 485.1395 | 463.1505 | 449.7944
1280.6604 | 523.2295 | 485.2208 | 463.3596 | 449.8486
1281.6604 | 523.1006 | 485.251 | 463.2446 | 449.9391
1282.6604 | 523.1194 | 485.3938 | 463.3457 | 450.0651
1283.6604 | 523.1314 | 485.4187 | 463.5783 | 450.1736
1284.6604 | 523.1094 | 485.5257 | 463.8803 | 450.2796
1285.6604 | 523.1223 | 485.5076 | 463.6507 | 450.3931
1286.6604 | 523.1827 | 485.6156 | 463.9491 | 450.4743
1287.6604 | 523.0739 | 485.6249 | 464.1318 | 450.5932
1288.6604 | 522.954 | 485.6661 | 463.9988 | 450.7231
1289.6604 | 522.9505 | 485.622 | 463.7822 | 450.8847
1290.6604 | 523.04 | 485.6714 | 463.8831 | 451.0267
1291.6604 | 522.9489 | 485.8085 | 464.1514 | 451.1601
1292.6604 | 522.9312 | 485.8655 | 464.2857 | 451.3041
1293.6604 | 522.8796 | 485.9539 | 464.3308 | 451.4454
1294.6604 | 522.764 | 485.9367 | 464.2474 | 451.5699
1295.6604 | 522.8252 | 485.9722 | 464.5108 | 451.5924
1296.6604 | 522.8857 | 485.9667 | 464.358 | 451.7039
1297.6604 | 522.8364 | 486.0063 | 464.3045 | 451.8059
1298.6604 | 522.7968 | 486.0753 | 464.4124 | 451.8975
1299.6604 | 522.8561 | 486.1248 | 464.2753 | 452.0312
1300.6604 | 522.8246 | 486.1324 | 464.4754 | 452.0932
1301.6604 | 522.7593 | 486.2372 | 464.6557 | 452.1761
1302.6604 | 522.7992 | 486.2769 | 464.3355 | 452.2635
1303.6604 | 522.8721 | 486.299 | 464.5438 | 452.3883
1304.6604 | 522.8015 | 486.3187 | 464.46 | 452.5411
1305.6604 | 522.8544 | 486.3542 | 464.2847 | 452.5746
1306.6604 | 522.9242 | 486.4142 | 464.3273 | 452.6857
1307.6604 | 522.9793 | 486.5457 | 464.0974 | 452.748
1308.6604 | 523.0856 | 486.603 | 464.4597 | 452.7993
1309.6604 | 523.0357 | 486.563 | 464.8543 | 452.9827
1310.6604 | 523.0292 | 486.6219 | 464.9912 | 453.1074
1311.6604 | 522.9359 | 486.693 | 464.7047 | 453.2285
1312.6604 | 522.9708 | 486.7399 | 465.0109 | 453.3607
1313.6604 | 523.0547 | 486.8587 | 464.9383 | 453.4516
1314.6604 | 523.0942 | 486.884 | 464.9841 | 453.637
1315.6604 | 523.1444 | 486.8813 | 465.0562 | 453.7049
1316.6604 | 523.1135 | 486.9598 | 465.4363 | 453.8374
1317.6604 | 523.0682 | 487.0126 | 465.3387 | 453.9502
1318.6604 | 522.875 | 487.0639 | 465.4774 | 454.0666
1319.6604 | 522.8084 | 487.061 | 465.4709 | 454.2079
1320.6604 | 522.8116 | 487.103 | 465.3143 | 454.288
1321.6604 | 522.769 | 487.0679 | 465.0445 | 454.3967
1322.6604 | 522.8049 | 487.0956 | 464.982 | 454.5201
1323.6604 | 522.8948 | 487.1412 | 464.823 | 454.6125
1324.6604 | 522.906 | 487.118 | 465.1595 | 454.7222
1325.6604 | 522.9382 | 487.2341 | 465.4264 | 454.8074
1326.6604 | 522.8549 | 487.2739 | 465.5922 | 454.8432
1327.6604 | 522.9069 | 487.336 | 465.6924 | 454.9753
1328.6604 | 522.8506 | 487.4393 | 465.9967 | 455.0464
1329.6604 | 522.8241 | 487.5229 | 466.1493 | 455.1582
1330.6604 | 522.8997 | 487.5158 | 465.7522 | 455.171
1331.6604 | 522.9966 | 487.5761 | 465.9367 | 455.316
1332.6604 | 523.0085 | 487.6466 | 465.9546 | 455.4241
1333.6604 | 522.9389 | 487.6299 | 466.2326 | 455.5396
1334.6604 | 522.9303 | 487.6647 | 466.3834 | 455.7021
1335.6604 | 522.9168 | 487.6966 | 466.4705 | 455.7024
1336.6604 | 522.9015 | 487.7073 | 466.5668 | 455.8507
1337.6604 | 522.9206 | 487.829 | 466.4562 | 455.9443
1338.6604 | 522.9858 | 487.8781 | 466.3526 | 456.0774
1339.6604 | 522.9802 | 487.9094 | 466.4247 | 456.2177
1340.6604 | 522.9716 | 487.9457 | 466.686 | 456.2596
1341.6604 | 522.9986 | 487.9489 | 466.8744 | 456.3984
1342.6604 | 523.0015 | 488.0011 | 467.1083 | 456.4523
1343.6604 | 522.9759 | 488.0459 | 467.2292 | 456.5627
1344.6604 | 523.0097 | 488.0612 | 467.0113 | 456.7179
1345.6604 | 523.0731 | 488.033 | 467.1213 | 456.7851
1346.6604 | 523.0461 | 488.1518 | 467.2884 | 456.8814
1347.6604 | 523.0969 | 488.2438 | 467.4341 | 456.9342
1348.6604 | 523.2034 | 488.3347 | 467.4437 | 457.1607
1349.6604 | 523.1692 | 488.3631 | 467.4468 | 457.2134
1350.6604 | 523.1299 | 488.386 | 467.3693 | 457.1777
1351.6604 | 523.0418 | 488.4426 | 467.6444 | 457.2684
1352.6604 | 523.0623 | 488.4782 | 467.5507 | 457.3836
1353.6604 | 523.0683 | 488.4696 | 467.1023 | 457.4597
1354.6604 | 523.1095 | 488.5457 | 467.2721 | 457.5826
1355.6604 | 523.1108 | 488.6567 | 467.2878 | 457.6391
1356.6604 | 523.2608 | 488.6932 | 467.4764 | 457.8565
1357.6604 | 523.3502 | 488.6703 | 467.4077 | 457.9624
1358.6604 | 523.2946 | 488.6448 | 467.5601 | 457.9739
1359.6604 | 523.4105 | 488.6069 | 467.4313 | 458.1928
1360.6604 | 523.4561 | 488.6935 | 467.4982 | 458.2452
1361.6604 | 523.4093 | 488.7432 | 467.8361 | 458.3351
1362.6604 | 523.3548 | 488.8233 | 467.8562 | 458.518
1363.6604 | 523.361 | 488.9062 | 467.6158 | 458.5691
1364.6604 | 523.4689 | 488.9584 | 467.8834 | 458.7325
1365.6604 | 523.4883 | 489.0374 | 467.976 | 458.7762
1366.6604 | 523.5 | 489.0566 | 468.1454 | 458.9358
1367.6604 | 523.5117 | 489.0435 | 468.2881 | 459.0527
1368.6604 | 523.3705 | 489.0681 | 468.5092 | 459.1756
1369.6604 | 523.283 | 489.1091 | 468.4311 | 459.3234
1370.6604 | 523.3558 | 489.0859 | 468.3741 | 459.3809
1371.6604 | 523.311 | 489.1831 | 468.5885 | 459.4619
1372.6604 | 523.3148 | 489.1772 | 468.6277 | 459.5269
1373.6604 | 523.2411 | 489.2052 | 468.6328 | 459.614
1374.6604 | 523.2317 | 489.3585 | 468.7739 | 459.6653
1375.6604 | 523.2488 | 489.3356 | 468.5932 | 459.662
1376.6604 | 523.2846 | 489.2783 | 468.6476 | 459.7862
1377.6604 | 523.21 | 489.3494 | 468.6181 | 459.8534
1378.6604 | 523.1225 | 489.3351 | 468.8224 | 459.9206
1379.6604 | 523.1101 | 489.4741 | 469.0588 | 460.0156
1380.6604 | 523.0579 | 489.4963 | 469.0258 | 460.023
1381.6604 | 523.186 | 489.4955 | 468.6532 | 460.1091
1382.6604 | 523.2521 | 489.5739 | 468.7768 | 460.2264
1383.6604 | 523.1554 | 489.6376 | 468.8507 | 460.1656
1384.6604 | 523.1635 | 489.5924 | 468.9413 | 460.3213
1385.6604 | 523.2076 | 489.7163 | 469.214 | 460.3527
1386.6604 | 523.1116 | 489.7982 | 469.2316 | 460.4405
1387.6604 | 523.1843 | 489.8213 | 469.116 | 460.5273
1388.6604 | 523.196 | 489.7994 | 468.8893 | 460.5464
1389.6604 | 523.1312 | 489.8519 | 469.0407 | 460.685
1390.6604 | 523.1 | 489.9217 | 469.2666 | 460.7075
1391.6604 | 523.0694 | 489.9295 | 469.0939 | 460.8242
1392.6604 | 523.1964 | 489.9833 | 469.1267 | 460.8523
1393.6604 | 523.1453 | 490.0191 | 469.2476 | 460.9413
1394.6604 | 523.069 | 490.0255 | 469.217 | 461.1049
1395.6604 | 523.103 | 490.0763 | 469.2621 | 461.2548
1396.6604 | 523.1892 | 490.0197 | 469.2519 | 461.3286
1397.6604 | 523.205 | 490.0095 | 469.1474 | 461.406
1398.6604 | 523.1604 | 490.1038 | 469.0626 | 461.498
1399.6604 | 523.1614 | 490.1251 | 468.969 | 461.5296
1400.6604 | 523.1302 | 490.1053 | 469.1676 | 461.4644
1401.6604 | 523.1084 | 490.1444 | 469.1536 | 461.6163
1402.6604 | 523.1833 | 490.2222 | 469.0015 | 461.6235
1403.6604 | 523.3447 | 490.2823 | 468.9526 | 461.657
1404.6604 | 523.4499 | 490.3338 | 469.0754 | 461.7784
1405.6604 | 523.4834 | 490.263 | 469.2441 | 461.8552
1406.6604 | 523.5093 | 490.2355 | 469.3632 | 461.885
1407.6604 | 523.4659 | 490.3106 | 469.2929 | 461.8821
1408.6604 | 523.3878 | 490.3689 | 469.1268 | 461.9806
1409.6604 | 523.4478 | 490.4686 | 469.1038 | 462.0341
1410.6604 | 523.5275 | 490.5257 | 469.3328 | 462.0243
1411.6604 | 523.6463 | 490.6224 | 469.0228 | 461.9808
1412.6604 | 523.5937 | 490.6213 | 469.0408 | 462.0638
1413.6604 | 523.5111 | 490.63 | 469.3544 | 462.2123
1414.6604 | 523.5027 | 490.6691 | 469.687 | 462.2182
1415.6604 | 523.502 | 490.7228 | 469.3746 | 462.3452
1416.6604 | 523.5661 | 490.7659 | 469.5902 | 462.388
1417.6604 | 523.5576 | 490.7558 | 469.9986 | 462.5235
1418.6604 | 523.4403 | 490.7623 | 469.9575 | 462.7023
1419.6604 | 523.269 | 490.8389 | 470.0055 | 462.9175
1420.6604 | 523.2163 | 490.9608 | 470.2128 | 462.8689
1421.6604 | 523.1735 | 490.9565 | 470.2655 | 462.9279
1422.6604 | 523.1656 | 490.9093 | 470.4246 | 462.9731
1423.6604 | 523.2409 | 490.9676 | 470.5977 | 463.1918
1424.6604 | 523.2105 | 491.016 | 470.4395 | 463.3316
1425.6604 | 523.1823 | 491.0683 | 470.5519 | 463.3566
1426.6604 | 523.1056 | 491.1512 | 470.3586 | 463.4514
1427.6604 | 523.074 | 491.1587 | 470.4114 | 463.5449
1428.6604 | 523.018 | 491.2435 | 470.6525 | 463.5215
1429.6604 | 523.0022 | 491.2655 | 470.5418 | 463.6153
1430.6604 | 522.9595 | 491.205 | 470.6343 | 463.5141
1431.6604 | 522.9533 | 491.2673 | 470.8424 | 463.6088
1432.6604 | 522.9795 | 491.3423 | 470.7797 | 463.8611
1433.6604 | 522.9787 | 491.3993 | 470.6226 | 463.9519
1434.6604 | 523.0662 | 491.4339 | 470.7119 | 464.0291
1435.6604 | 523.0843 | 491.5069 | 471.067 | 464.013
1436.6604 | 523.1578 | 491.5102 | 470.9585 | 464.1367
1437.6604 | 523.0734 | 491.5027 | 470.8989 | 464.1972
1438.6604 | 523.0857 | 491.5111 | 470.5476 | 464.2581
1439.6604 | 523.0032 | 491.5135 | 470.8761 | 464.4214
1440.6604 | 522.9693 | 491.5545 | 471.0573 | 464.5918
1441.6604 | 523.0337 | 491.6341 | 470.8844 | 464.6875
1442.6604 | 523.0684 | 491.6967 | 471.0968 | 464.8678
1443.6604 | 523.0279 | 491.714 | 471.3053 | 465.0477
1444.6604 | 522.9751 | 491.7334 | 471.2924 | 465.2501
1445.6604 | 522.9757 | 491.8215 | 471.4867 | 465.2825
1446.6604 | 523.0995 | 491.8302 | 471.417 | 465.381
1447.6604 | 523.0166 | 491.8239 | 471.4159 | 465.3799
1448.6604 | 523.0226 | 491.9206 | 471.4056 | 465.4303
1449.6604 | 522.9863 | 491.9964 | 471.6118 | 465.4968
1450.6604 | 523.0276 | 491.9898 | 471.475 | 465.4957
1451.6604 | 522.9232 | 491.9438 | 471.6467 | 465.6546
1452.6604 | 522.8979 | 492.027 | 471.6409 | 465.7008
1453.6604 | 522.8502 | 492.0739 | 471.7611 | 465.6917
1454.6604 | 522.9096 | 492.1618 | 471.5391 | 465.7957
1455.6604 | 523.1417 | 492.1559 | 471.4912 | 465.8318
1456.6604 | 523.235 | 492.2124 | 471.5939 | 465.886
1457.6604 | 523.3234 | 492.2521 | 471.3808 | 465.9835
1458.6604 | 523.2771 | 492.2604 | 471.492 | 466.0499
1459.6604 | 523.2197 | 492.3158 | 471.3073 | 466.1836
1460.6604 | 523.2402 | 492.2567 | 470.9894 | 466.2149
1461.6604 | 523.2657 | 492.3286 | 471.0896 | 466.2757
1462.6604 | 523.1235 | 492.3341 | 471.1413 | 466.2565
1463.6604 | 522.9033 | 492.4154 | 470.8379 | 466.388
1464.6604 | 522.8023 | 492.4254 | 470.9308 | 466.4052
1465.6604 | 522.7922 | 492.4016 | 471.3831 | 466.4499
1466.6604 | 522.7903 | 492.4853 | 471.8617 | 466.551
1467.6604 | 522.7591 | 492.518 | 471.8236 | 466.6952
1468.6604 | 522.7594 | 492.4255 | 471.9428 | 466.7175
1469.6604 | 522.7327 | 492.5117 | 472.2158 | 466.7904
1470.6604 | 522.7326 | 492.5851 | 472.1975 | 466.8275
1471.6604 | 522.7716 | 492.6618 | 471.7953 | 466.7991
1472.6604 | 522.8052 | 492.7277 | 471.8762 | 466.7967
1473.6604 | 522.8059 | 492.6526 | 472.068 | 466.7899
1474.6604 | 522.7791 | 492.7317 | 472.1304 | 466.9495
1475.6604 | 522.7224 | 492.7357 | 471.9026 | 467.0268
1476.6604 | 522.7301 | 492.6727 | 471.6041 | 467.1578
1477.6604 | 522.7833 | 492.8008 | 471.8099 | 467.2975
1478.6604 | 522.8312 | 492.869 | 471.6834 | 467.3714
1479.6604 | 522.8652 | 492.8996 | 471.6535 | 467.487
1480.6604 | 522.8879 | 492.9329 | 471.7212 | 467.5689
1481.6604 | 522.9746 | 492.9145 | 471.716 | 467.6964
1482.6604 | 523.0421 | 492.9209 | 471.7433 | 467.9146
1483.6604 | 523.025 | 492.9922 | 471.721 | 468.0442
1484.6604 | 523.0994 | 492.9321 | 471.7502 | 468.155
1485.6604 | 523.087 | 493.044 | 472.0558 | 468.1915
1486.6604 | 523.1215 | 493.0571 | 471.9945 | 468.2035
1487.6604 | 523.1049 | 493.1434 | 472.0483 | 468.1879
1488.6604 | 523.1496 | 493.2302 | 472.0096 | 468.2886
1489.6604 | 523.0898 | 493.2587 | 472.2227 | 468.442
1490.6604 | 522.9367 | 493.2252 | 472.1588 | 468.4403
1491.6604 | 523.0426 | 493.2561 | 472.177 | 468.5011
1492.6604 | 523.1599 | 493.3115 | 472.3632 | 468.5944
1493.6604 | 523.0937 | 493.3922 | 472.5559 | 468.6034
1494.6604 | 522.9434 | 493.4888 | 472.4675 | 468.7359
1495.6604 | 522.9203 | 493.5033 | 472.6345 | 468.7328
1496.6604 | 523.0252 | 493.478 | 472.7279 | 468.7231
1497.6604 | 523.1313 | 493.45 | 472.9025 | 468.7267
1498.6604 | 523.2034 | 493.424 | 472.6718 | 468.8392
1499.6604 | 523.1981 | 493.4232 | 472.5452 | 468.8864
1500.6604 | 523.0891 | 493.4698 | 472.7909 | 468.9552
1501.6604 | 523.0302 | 493.5705 | 472.9242 | 469.0061
1502.6604 | 523.0965 | 493.6725 | 473.0107 | 469.1088
1503.6604 | 523.1966 | 493.5944 | 472.7229 | 469.2375
1504.6604 | 523.2342 | 493.6708 | 472.751 | 469.2808
1505.6604 | 523.2998 | 493.6725 | 472.8744 | 469.3881
1506.6604 | 523.2516 | 493.768 | 472.4266 | 469.4778
1507.6604 | 523.2255 | 493.7339 | 472.283 | 469.4447
1508.6604 | 523.3863 | 493.8325 | 472.5595 | 469.4515
1509.6604 | 523.3611 | 493.8711 | 472.6168 | 469.2443
1510.6604 | 523.4264 | 493.9137 | 472.6822 | 469.0879
1511.6604 | 523.4273 | 493.9855 | 472.8815 | 468.9869
1512.6604 | 523.3963 | 494.0234 | 472.6579 | 468.8986
1513.6604 | 523.4967 | 493.9573 | 472.7828 | 468.9042
1514.6604 | 523.5873 | 494.0225 | 472.7323 | 468.9424
1515.6604 | 523.6427 | 494.0913 | 473.0738 | 469.0454
1516.6604 | 523.7619 | 494.1134 | 472.8616 | 469.237
1517.6604 | 523.7744 | 494.1721 | 472.9633 | 469.2141
1518.6604 | 523.7469 | 494.2275 | 472.8284 | 469.2707
1519.6604 | 523.8004 | 494.176 | 472.7593 | 469.3493
1520.6604 | 523.7547 | 494.2179 | 472.5203 | 469.3916
1521.6604 | 523.5401 | 494.2908 | 472.5669 | 469.528
1522.6604 | 523.4581 | 494.2935 | 472.7246 | 469.5473
1523.6604 | 523.3692 | 494.3463 | 472.911 | 469.6056
1524.6604 | 523.223 | 494.3582 | 473.1288 | 469.7601
1525.6604 | 523.1469 | 494.2706 | 472.9056 | 469.863
1526.6604 | 523.0156 | 494.2739 | 473.023 | 470.0073
1527.6604 | 522.8823 | 494.3552 | 473.1401 | 470.1914
1528.6604 | 522.7311 | 494.4565 | 473.3556 | 470.3545
1529.6604 | 522.7336 | 494.4454 | 473.1754 | 470.5441
1530.6604 | 522.7683 | 494.494 | 473.4271 | 470.5237
1531.6604 | 522.7146 | 494.5633 | 473.1946 | 470.7611
1532.6604 | 522.8784 | 494.5665 | 473.0067 | 470.9134
1533.6604 | 522.8729 | 494.5813 | 473.2401 | 470.7776
1534.6604 | 522.9414 | 494.5903 | 473.2592 | 471.0195
1535.6604 | 522.9369 | 494.6493 | 473.1223 | 471.0658
1536.6604 | 522.9263 | 494.645 | 473.211 | 471.1455
1537.6604 | 522.9113 | 494.6934 | 472.9284 | 471.3265
1538.6604 | 522.8439 | 494.6995 | 473.2102 | 471.1786
1539.6604 | 522.8655 | 494.7282 | 473.3553 | 471.2483
1540.6604 | 522.9504 | 494.6907 | 473.1233 | 470.3005
1541.6604 | 523.0598 | 494.7107 | 473.1399 | 470.2953
1542.6604 | 523.0579 | 494.7866 | 473.6038 | 471.3046
1543.6604 | 522.9805 | 494.8047 | 473.8188 | 471.3272
1544.6604 | 522.9516 | 494.8935 | 473.6059 | 471.3063
1545.6604 | 522.9591 | 494.9577 | 473.9126 | 471.4284
1546.6604 | 523.0953 | 494.9892 | 473.7919 | 470.6112
1547.6604 | 523.2159 | 494.9841 | 473.9024 | 471.6385
1548.6604 | 523.2563 | 495.0309 | 473.8412 | 471.0689
1549.6604 | 523.3047 | 495.0601 | 473.8961 | 471.9519
1550.6604 | 523.3888 | 495.117 | 473.8128 | 471.9173
1551.6604 | 523.4408 | 495.1496 | 473.7658 | 471.2282
1552.6604 | 523.4052 | 495.1798 | 473.9714 | 472.1501
1553.6604 | 523.4249 | 495.1973 | 473.9984 | 471.3954
1554.6604 | 523.361 | 495.2145 | 473.9768 | 471.7134
1555.6604 | 523.3536 | 495.1637 | 474.0689 | 471.4992
1556.6604 | 523.3133 | 495.2217 | 474.2268 | 472.1207
1557.6604 | 523.3995 | 495.1969 | 474.232 | 472.3352
1558.6604 | 523.4694 | 495.2523 | 474.1681 | 472.3997
1559.6604 | 523.5402 | 495.2786 | 473.892 | 472.312
1560.6604 | 523.5794 | 495.2725 | 473.9824 | 472.6063
1561.6604 | 523.6478 | 495.3738 | 474.3351 | 471.8435
1562.6604 | 523.6604 | 495.3282 | 474.0156 | 472.646
1563.6604 | 523.6435 | 495.3578 | 473.6933 | 472.3003
1564.6604 | 523.564 | 495.4459 | 474.0024 | 470.6978
1565.6604 | 523.4201 | 495.4821 | 474.0387 | 472.4344
1566.6604 | 523.4229 | 495.5433 | 474.1935 | 472.7637
1567.6604 | 523.3356 | 495.4938 | 473.776 | 471.9019
1568.6604 | 523.3619 | 495.5651 | 473.937 | 472.7414
1569.6604 | 523.308 | 495.5525 | 473.835 | 472.0001
1570.6604 | 523.3239 | 495.6472 | 473.8339 | 472.1877
1571.6604 | 523.2583 | 495.5802 | 473.8814 | 472.8899
1572.6604 | 523.2473 | 495.6087 | 473.7624 | 472.7846
1573.6604 | 523.2906 | 495.5896 | 473.7759 | 472.38
1574.6604 | 523.2873 | 495.7168 | 473.6783 | 472.4149
1575.6604 | 523.3842 | 495.7336 | 473.6925 | 472.7488
1576.6604 | 523.5317 | 495.687 | 473.5635 | 472.7628
1577.6604 | 523.5536 | 495.7644 | 473.6663 | 472.6393
1578.6604 | 523.55 | 495.7903 | 473.5284 | 472.935
1579.6604 | 523.6378 | 495.8371 | 473.7543 | 473.0747
1580.6604 | 523.6041 | 495.8042 | 473.9691 | 472.996
1581.6604 | 523.5606 | 495.847 | 473.7619 | 473.0976
1582.6604 | 523.6406 | 495.8606 | 473.7683 | 472.5911
1583.6604 | 523.7197 | 495.8227 | 473.9583 | 473.0755
1584.6604 | 523.7291 | 495.8714 | 473.8558 | 473.1618
1585.6604 | 523.9127 | 495.9902 | 473.9538 | 473.4526
1586.6604 | 524.0399 | 496.0588 | 474.2965 | 473.6721
1587.6604 | 523.8864 | 496.1375 | 474.4817 | 472.8478
1588.6604 | 523.9106 | 496.1322 | 474.3869 | 473.8034
1589.6604 | 523.9064 | 496.163 | 474.4699 | 473.7689
1590.6604 | 523.9247 | 496.1409 | 474.1251 | 473.7629
1591.6604 | 523.9814 | 496.234 | 474.2161 | 472.7367
1592.6604 | 523.9254 | 496.2537 | 474.349 | 473.8007
1593.6604 | 523.9438 | 496.2544 | 474.242 | 474.0112
1594.6604 | 523.788 | 496.2772 | 474.3874 | 474.1442
1595.6604 | 523.7417 | 496.245 | 474.6245 | 474.1576
1596.6604 | 523.6349 | 496.3302 | 474.5235 | 474.3787
1597.6604 | 523.6202 | 496.2864 | 474.7882 | 474.3886
1598.6604 | 523.5974 | 496.3584 | 474.4741 | 474.2013
1599.6604 | 523.5194 | 496.4185 | 474.3255 | 474.3258
1600.6604 | 523.4771 | 496.502 | 474.2816 | 474.2475
1601.6604 | 523.5177 | 496.4682 | 474.2295 | 474.1794
1602.6604 | 523.5681 | 496.5324 | 474.6235 | 474.3305
1603.6604 | 523.6337 | 496.5887 | 475.0183 | 473.5515
1604.6604 | 523.6288 | 496.6443 | 474.8806 | 474.4794
1605.6604 | 523.5882 | 496.6265 | 475.0126 | 474.3127
1606.6604 | 523.7178 | 496.6434 | 475.2854 | 474.6101
1607.6604 | 523.7738 | 496.6617 | 475.3761 | 474.3337
1608.6604 | 523.8137 | 496.6532 | 475.3579 | 474.2921
1609.6604 | 523.9144 | 496.6923 | 475.182 | 474.6666
1610.6604 | 524.0276 | 496.7749 | 475.4172 | 474.6577
1611.6604 | 524.037 | 496.7956 | 475.7395 | 474.4245
1612.6604 | 524.1532 | 496.7409 | 475.357 | 474.5764
1613.6604 | 524.0589 | 496.7869 | 475.4274 | 474.612
1614.6604 | 524.007 | 496.8501 | 475.492 | 474.5983
1615.6604 | 523.9849 | 496.8303 | 475.5403 | 474.6046
1616.6604 | 524.04 | 496.7998 | 475.8378 | 474.6369
1617.6604 | 524.0622 | 496.7614 | 475.6483 | 474.9431
1618.6604 | 524.0153 | 496.9109 | 475.3438 | 474.9197
1619.6604 | 523.9557 | 497.0382 | 475.3607 | 474.5634
1620.6604 | 523.8391 | 497.0972 | 475.6219 | 474.5944
1621.6604 | 523.8496 | 497.1407 | 475.7118 | 475.05
1622.6604 | 523.8119 | 497.1202 | 475.7865 | 475.0133
1623.6604 | 523.815 | 497.1806 | 475.5646 | 474.9064
1624.6604 | 523.8707 | 497.2088 | 475.615 | 474.7989
1625.6604 | 523.9528 | 497.1935 | 475.2659 | 475.1643
1626.6604 | 524.0303 | 497.1832 | 475.371 | 475.0168
1627.6604 | 524.0798 | 497.2357 | 475.3265 | 474.8171
1628.6604 | 524.2043 | 497.2389 | 475.0573 | 475.0313
1629.6604 | 524.2328 | 497.2128 | 475.1174 | 475.0052
1630.6604 | 524.044 | 497.2946 | 475.6328 | 474.7341
1631.6604 | 524.051 | 497.307 | 475.465 | 474.8187
1632.6604 | 524.1113 | 497.4267 | 475.2315 | 475.2172
1633.6604 | 524.1151 | 497.4364 | 475.2615 | 475.2197
1634.676 | 524.1493 | 497.2922 | 475.3958 | 474.939
1635.6604 | 524.1328 | 497.2264 | 475.3417 | 475.3152
1636.6604 | 524.0499 | 497.3178 | 475.1429 | 475.6068
1637.6604 | 524.097 | 497.4197 | 475.2934 | 475.5777
1638.6604 | 524.0541 | 497.4611 | 475.3446 | 473.3916
1639.6604 | 523.8985 | 497.4284 | 475.3219 | 475.3478
1640.6604 | 523.873 | 497.4293 | 475.3332 | 475.8045
1641.6604 | 523.8863 | 497.4765 | 475.4172 | 475.7699
1642.6604 | 523.9217 | 497.5265 | 475.6151 | 475.5523
1643.6604 | 523.8732 | 497.5752 | 475.4096 | 475.4408
1644.6604 | 523.9231 | 497.6148 | 475.6438 | 475.6006
1645.6604 | 523.9222 | 497.6413 | 475.8599 | 475.3893
1646.6604 | 523.9336 | 497.7262 | 475.7721 | 474.5777
1647.6604 | 523.9805 | 497.7267 | 475.9299 | 475.8963
1648.6604 | 524.0684 | 497.6943 | 476.2281 | 475.73
1649.6604 | 524.0517 | 497.791 | 475.9404 | 475.7359
1650.6604 | 524.0337 | 497.7639 | 475.644 | 475.3014
1651.6604 | 523.9658 | 497.8528 | 475.8244 | 473.2941
1652.6604 | 523.8026 | 497.9305 | 475.9756 | 475.2114
1653.6604 | 523.6655 | 497.9577 | 475.9755 | 475.5847
1654.6604 | 523.6913 | 497.9867 | 476.1373 | 475.3388
1655.6604 | 523.5121 | 497.9714 | 476.2849 | 474.6943
1656.6604 | 523.4426 | 497.9678 | 476.2591 | 475.2636
1657.6604 | 523.424 | 498.0546 | 476.3216 | 475.4031
1658.6604 | 523.293 | 498.0019 | 475.9934 | 475.6468
1659.6604 | 523.3205 | 498.0193 | 475.9864 | 475.9851
1660.6604 | 523.4384 | 498.0493 | 475.8841 | 475.9396
1661.6604 | 523.3734 | 498.1467 | 475.917 | 475.8088
1662.6604 | 523.5079 | 498.1479 | 476.0091 | 476.0401
1663.6604 | 523.4537 | 498.142 | 476.2188 | 475.0996
1664.6604 | 523.4074 | 498.2139 | 476.2051 | 475.8231
1665.6604 | 523.5022 | 498.2844 | 476.2782 | 475.8659
1666.6604 | 523.6613 | 498.2913 | 476.4498 | 474.2848
1667.6604 | 523.7404 | 498.2894 | 476.3914 | 475.9106
1668.6604 | 523.7149 | 498.2705 | 476.1944 | 476.0203
1669.6604 | 523.757 | 498.1828 | 476.1338 | 474.5184
1670.6604 | 523.7798 | 498.3058 | 476.2712 | 476.2535
1671.6604 | 523.8344 | 498.4461 | 476.433 | 476.0889
1672.6604 | 523.9579 | 498.4859 | 476.2052 | 476.0398
1673.6604 | 524.0759 | 498.4535 | 476.1948 | 476.1455
1674.6604 | 524.1858 | 498.4994 | 476.4831 | 476.4138
1675.6604 | 524.1963 | 498.4289 | 476.1083 | 475.709
1676.6604 | 524.1559 | 498.5542 | 476.2942 | 476.3775
1677.6604 | 524.156 | 498.6508 | 476.6469 | 476.1658
1678.6604 | 524.1054 | 498.6871 | 476.6939 | 476.494
1679.6604 | 524.0319 | 498.6666 | 476.5912 | 476.7426
1680.6604 | 523.9781 | 498.6992 | 476.8473 | 476.8508
1681.6604 | 524.084 | 498.7187 | 476.7373 | 476.666
1682.6604 | 524.1916 | 498.7687 | 476.828 | 476.6238
1683.6604 | 524.251 | 498.8543 | 476.9573 | 476.4886
1684.6604 | 524.2302 | 498.7701 | 476.7288 | 476.9139
1685.6604 | 524.1753 | 498.7921 | 476.6404 | 477.0159
1686.6604 | 524.2511 | 498.7541 | 476.5769 | 476.7795
1687.6604 | 524.3886 | 498.7842 | 476.3256 | 477.2051
1688.6604 | 524.3671 | 498.7287 | 476.3659 | 476.586
1689.6604 | 524.3537 | 498.8237 | 476.5842 | 477.2508
1690.6604 | 524.3505 | 498.941 | 476.5314 | 477.1006
1691.6604 | 524.3117 | 498.9044 | 476.5272 | 477.2145
1692.6604 | 524.2863 | 499.0257 | 476.7746 | 477.5642
1693.6604 | 524.286 | 499.0265 | 477.193 | 477.2386
1694.6604 | 524.3015 | 498.905 | 477.3672 | 475.7753
1695.6604 | 524.2803 | 498.947 | 477.3294 | 477.2591
1696.6604 | 524.2849 | 499.0001 | 477.4619 | 477.664
1697.6604 | 524.3414 | 499.0671 | 477.378 | 477.6516
1698.6604 | 524.2096 | 499.1795 | 477.3578 | 477.7721
1699.6604 | 524.0771 | 499.2459 | 477.3328 | 477.2817
1700.6604 | 524.0462 | 499.1891 | 477.0611 | 477.9482
1701.6604 | 523.9829 | 499.1992 | 477.4641 | 478.0322
1702.6604 | 523.9401 | 499.2162 | 477.307 | 477.8818
1703.6604 | 524.0133 | 499.2831 | 477.4764 | 477.9095
1704.6604 | 524.0276 | 499.2 | 477.57 | 477.7896
1705.6604 | 524.0997 | 499.2306 | 477.6207 | 478.2499
1706.6604 | 524.1582 | 499.329 | 477.3231 | 478.1583
1707.6604 | 524.167 | 499.3321 | 477.4906 | 477.9792
1708.6604 | 524.1784 | 499.3412 | 477.6139 | 477.9928
1709.6604 | 524.2271 | 499.4314 | 477.3766 | 478.2653
1710.6604 | 524.3358 | 499.4255 | 477.2382 | 478.1469
1711.6604 | 524.3083 | 499.5492 | 477.5404 | 477.734
1712.6604 | 524.4603 | 499.6306 | 477.5224 | 477.8984
1713.6604 | 524.4224 | 499.5236 | 477.5218 | 477.4781
1714.6604 | 524.2006 | 499.5677 | 477.6772 | 476.8887
1715.6604 | 524.1671 | 499.6093 | 477.9698 | 478.3953
1716.6604 | 524.291 | 499.6502 | 477.9225 | 478.1211
1717.6604 | 524.46 | 499.6238 | 477.713 | 478.0537
1718.6604 | 524.3376 | 499.5723 | 477.5496 | 478.296
1719.6604 | 524.2959 | 499.5453 | 477.372 | 477.3973
1720.6604 | 524.2876 | 499.669 | 477.6926 | 478.4497
1721.6604 | 524.3589 | 499.6579 | 477.9007 | 478.555
1722.6604 | 524.3273 | 499.7298 | 477.6802 | 478.5106
1723.6604 | 524.3169 | 499.6831 | 477.9687 | 478.5613
1724.6604 | 524.3061 | 499.7669 | 478.1915 | 477.9784
1725.6604 | 524.2486 | 499.8273 | 477.7323 | 477.9681
1726.6604 | 524.1087 | 499.8599 | 477.8845 | 478.4624
1727.6604 | 524.1563 | 499.8596 | 477.3985 | 478.3528
1728.6604 | 524.1551 | 499.8896 | 477.2587 | 477.8594
1729.6604 | 524.0025 | 499.8853 | 477.4902 | 478.1398
1730.6604 | 523.8625 | 499.9409 | 477.5121 | 477.9235
1731.6604 | 523.8499 | 499.9907 | 477.8006 | 478.188
1732.6604 | 523.8195 | 500.018 | 477.7973 | 478.0969
1733.6604 | 523.7718 | 499.9226 | 477.5268 | 478.622
1734.6604 | 523.8236 | 499.9921 | 477.5358 | 478.5495
1735.6604 | 523.6574 | 500.0438 | 477.4594 | 478.3689
1736.6604 | 523.575 | 500.0682 | 477.4156 | 477.955
1737.6604 | 523.5392 | 499.993 | 477.5859 | 478.1448
1738.6604 | 523.5575 | 500.065 | 477.6543 | 478.2633
1739.6604 | 523.5637 | 500.1267 | 477.8116 | 476.8313
1740.6604 | 523.428 | 500.1439 | 477.8464 | 478.3011
1741.6604 | 523.2685 | 500.1203 | 478.0946 | 477.9501
1742.6604 | 523.1906 | 500.0938 | 477.8245 | 478.1089
1743.6604 | 523.3529 | 500.0851 | 477.6569 | 478.4935
1744.6604 | 523.3662 | 500.2063 | 477.9963 | 478.1111
1745.6604 | 523.3879 | 500.1941 | 478.312 | 478.5443
1746.6604 | 523.321 | 500.1599 | 478.3984 | 478.4037
1747.6604 | 523.2621 | 500.2173 | 478.4161 | 478.5617
1748.6604 | 523.122 | 500.2862 | 478.3765 | 478.2889
1749.6604 | 523.1758 | 500.3705 | 478.6532 | 476.999
1750.6604 | 523.1996 | 500.3959 | 478.7505 | 478.3474
1751.6604 | 523.1828 | 500.3822 | 478.7237 | 478.5878
1752.6604 | 523.2258 | 500.4293 | 478.3888 | 478.4542
1753.6604 | 523.2098 | 500.3641 | 478.6603 | 478.6656
1754.6604 | 523.184 | 500.3968 | 478.7404 | 478.303
1755.6604 | 523.2327 | 500.465 | 478.5881 | 478.4816
1756.6604 | 523.3298 | 500.5308 | 478.5111 | 478.5315
1757.6604 | 523.4135 | 500.5795 | 478.6884 | 478.8002
1758.6604 | 523.4649 | 500.5475 | 478.8037 | 478.8164
1759.6604 | 523.5767 | 500.5174 | 478.9062 | 478.7248
1760.6604 | 523.4902 | 500.6008 | 478.8543 | 478.5862
1761.6604 | 523.4286 | 500.6303 | 478.9386 | 478.6013
1762.6604 | 523.2752 | 500.5849 | 479.1978 | 478.8722
1763.6604 | 523.1873 | 500.6797 | 479.1824 | 478.9958
1764.6604 | 523.2403 | 500.6834 | 479.27 | 478.9332
1765.6604 | 523.2031 | 500.6159 | 479.1426 | 478.9412
1766.6604 | 523.0955 | 500.7221 | 478.8492 | 478.7972
1767.6604 | 523.1734 | 500.7098 | 478.8569 | 479.2086
1768.6604 | 523.2044 | 500.6317 | 479.1591 | 479.2977
1769.6604 | 523.1629 | 500.7374 | 479.3316 | 478.9955
1770.6604 | 523.1752 | 500.8074 | 479.2878 | 479.2676
1771.6604 | 523.1573 | 500.7651 | 478.9432 | 479.1433
1772.6604 | 523.0393 | 500.7834 | 478.8191 | 479.539
1773.6604 | 522.9754 | 500.8363 | 479.1854 | 479.5882
1774.6604 | 522.9777 | 500.9158 | 479.2833 | 479.6334
1775.6604 | 523.0486 | 500.8529 | 478.9174 | 479.5649
1776.6604 | 522.8783 | 500.9222 | 479.0924 | 479.722
1777.6604 | 522.7261 | 500.9336 | 479.1982 | 479.0898
1778.6604 | 522.6282 | 500.8797 | 478.9291 | 479.7735
1779.6604 | 522.4891 | 500.8805 | 478.6737 | 479.6643
1780.6604 | 522.5263 | 500.9626 | 478.5196 | 479.2153
1781.6604 | 522.5325 | 501.0102 | 478.9296 | 479.6654
1782.6604 | 522.4569 | 501.0691 | 479.1387 | 479.7481
1783.6604 | 522.5493 | 501.128 | 478.644 | 478.5822
1784.6604 | 522.4699 | 501.1227 | 478.5621 | 479.8679
1785.6604 | 522.4926 | 501.1313 | 478.5928 | 478.7611
1786.6604 | 522.5551 | 501.2194 | 479.1091 | 479.8871
1787.6604 | 522.5884 | 501.2685 | 479.4375 | 478.768
1788.6604 | 522.5324 | 501.3086 | 479.5454 | 480.2531
1789.6604 | 522.6265 | 501.3131 | 479.3097 | 480.2111
1790.6604 | 522.5634 | 501.3036 | 479.4838 | 479.6573
1791.6604 | 522.578 | 501.355 | 479.4973 | 479.673
1792.6604 | 522.6305 | 501.4002 | 479.6285 | 480.2812
1793.6604 | 522.5994 | 501.4049 | 479.6707 | 480.3537
1794.6604 | 522.6093 | 501.3823 | 479.6519 | 480.3448
1795.6604 | 522.7365 | 501.4664 | 479.7314 | 480.2643
1796.6604 | 522.9302 | 501.5591 | 479.7193 | 480.223
1797.6604 | 523.0353 | 501.5741 | 479.5441 | 480.0606
1798.6604 | 523.0701 | 501.6524 | 479.6232 | 480.2984
1799.6604 | 523.2134 | 501.6537 | 479.4617 | 480.6949
1800.6604 | 523.3481 | 501.6059 | 479.4897 | 480.5055
1801.6604 | 523.4168 | 501.6483 | 479.4736 | 480.5012
1802.6604 | 523.4953 | 501.6212 | 479.5141 | 480.8555
1803.6604 | 523.5513 | 501.6734 | 479.3063 | 480.3128
1804.6604 | 523.6401 | 501.707 | 479.3599 | 480.2719
1805.6604 | 523.659 | 501.7916 | 479.5443 | 481.0732
1806.6604 | 523.7024 | 501.8 | 479.6215 | 480.4848
1807.6604 | 523.583 | 501.8028 | 479.2442 | 480.5145
1808.6604 | 523.5402 | 501.7842 | 479.1338 | 481.1767
1809.6604 | 523.5238 | 501.9315 | 479.4558 | 480.6939
1810.6604 | 523.5891 | 501.9758 | 479.6561 | 481.1647
1811.6604 | 523.4607 | 502.0105 | 479.6775 | 481.1121
1812.6604 | 523.2165 | 502.0667 | 479.7713 | 481.0281
1813.6604 | 523.1565 | 502.0992 | 479.6813 | 481.2311
1814.6604 | 523.1907 | 502.0578 | 479.6211 | 480.1677
1815.6604 | 523.1509 | 502.0813 | 479.8271 | 481.6661
1816.6604 | 523.0667 | 502.1337 | 479.8495 | 481.2371
1817.6604 | 522.9398 | 502.1598 | 479.8235 | 481.2313
1818.6604 | 522.899 | 502.1866 | 479.8123 | 481.7663
1819.6604 | 522.7526 | 502.1547 | 479.7198 | 481.804
1820.6604 | 522.7098 | 502.2304 | 479.6303 | 481.2662
1821.6604 | 522.5832 | 502.1796 | 479.8615 | 481.907
1822.6604 | 522.5019 | 502.2437 | 480.0894 | 481.9338
1823.6604 | 522.4573 | 502.2818 | 480.0543 | 481.9079
1824.6604 | 522.3038 | 502.2865 | 479.9349 | 482.2451
1825.6604 | 522.1903 | 502.3428 | 480.1401 | 481.7266
1826.6604 | 522.332 | 502.3351 | 480.1961 | 482.4795
1827.6604 | 522.3915 | 502.3581 | 480.0184 | 482.4529
1828.6604 | 522.4902 | 502.4275 | 480.0739 | 482.4659
1829.6604 | 522.4491 | 502.4188 | 480.2971 | 482.8222
1830.6604 | 522.4751 | 502.4909 | 480.359 | 482.6552
1831.6604 | 522.4333 | 502.4109 | 480.2061 | 482.8769
1832.6604 | 522.3829 | 502.4591 | 480.18 | 482.743
1833.6604 | 522.2884 | 502.4946 | 480.3269 | 482.8255
1834.6604 | 522.3618 | 502.5265 | 480.0745 | 483.2415
1835.6604 | 522.4836 | 502.5118 | 479.9678 | 483.1663
1836.6604 | 522.5365 | 502.5115 | 479.9458 | 483.2838
1837.6604 | 522.5839 | 502.5956 | 479.7676 | 482.882
1838.6604 | 522.7525 | 502.6562 | 480.1627 | 482.9208
1839.6604 | 522.8794 | 502.6278 | 480.4421 | 483.3705
1840.6604 | 522.9093 | 502.5798 | 480.2776 | 483.2821
1841.6604 | 523.0361 | 502.6354 | 480.2881 | 483.4844
1842.6604 | 523.1548 | 502.6745 | 480.342 | 483.0042
1843.6604 | 523.1326 | 502.7486 | 480.4395 | 483.6571
1844.6604 | 523.1667 | 502.8544 | 480.5176 | 483.6875
1845.6604 | 523.2441 | 502.9035 | 480.7315 | 483.75
1846.6604 | 523.2763 | 502.9392 | 480.6828 | 483.819
1847.6604 | 523.4803 | 502.9551 | 480.5966 | 482.9349
1848.6604 | 523.5607 | 502.9749 | 480.6781 | 484.057
1849.6604 | 523.5297 | 502.996 | 480.8137 | 484.2716
1850.6604 | 523.5481 | 502.9579 | 480.6122 | 484.1312
1851.6604 | 523.5303 | 502.95 | 480.6743 | 484.1634
1852.6604 | 523.52 | 502.9737 | 480.7809 | 484.4024
1853.6604 | 523.5215 | 503.0267 | 480.8765 | 484.535
1854.6604 | 523.5419 | 503.0027 | 480.9005 | 484.5181
1855.6604 | 523.5873 | 503.1573 | 481.0764 | 484.6851
1856.6604 | 523.5931 | 503.212 | 481.1455 | 484.2115
1857.6604 | 523.593 | 503.1932 | 481.1532 | 484.9031
1858.6604 | 523.5567 | 503.2182 | 480.8913 | 485.0801
1859.6604 | 523.6591 | 503.2438 | 480.5531 | 485.0754
1860.6604 | 523.7118 | 503.245 | 480.2389 | 485.2617
1861.6604 | 523.6744 | 503.3047 | 480.4532 | 484.8681
1862.6604 | 523.67 | 503.3228 | 480.5679 | 484.9455
1863.6604 | 523.7144 | 503.3948 | 480.6666 | 485.4763
1864.6604 | 523.7473 | 503.5115 | 480.7012 | 485.4866
1865.6604 | 523.6103 | 503.5219 | 480.6438 | 485.5612
1866.6604 | 523.4662 | 503.5055 | 480.5394 | 485.192
1867.6604 | 523.4711 | 503.6079 | 480.326 | 485.8167
1868.6604 | 523.4807 | 503.5977 | 480.4274 | 485.9096
1869.6604 | 523.512 | 503.6497 | 480.3126 | 485.9319
1870.6604 | 523.5256 | 503.6546 | 480.2225 | 485.9819
1871.6604 | 523.499 | 503.7108 | 480.4679 | 486.0385
1872.6604 | 523.5679 | 503.771 | 480.1917 | 485.9897
1873.6604 | 523.5039 | 503.7765 | 480.1577 | 486.1534
1874.6604 | 523.5554 | 503.6518 | 480.1871 | 486.2743
1875.6604 | 523.5832 | 503.6611 | 480.1446 | 486.3099
1876.6604 | 523.5866 | 503.7905 | 479.9414 | 486.4228
1877.6604 | 523.5687 | 503.7998 | 480.0086 | 486.4861
1878.6604 | 523.5364 | 503.7513 | 480.0703 | 486.4644
1879.6604 | 523.4452 | 503.8009 | 480.1345 | 486.5872
1880.6604 | 523.4304 | 503.85 | 479.8867 | 486.9122
1881.6604 | 523.5671 | 503.8671 | 479.9419 | 486.6599
1882.6604 | 523.5389 | 503.9048 | 480.1623 | 486.6831
1883.6604 | 523.6175 | 503.9392 | 479.8672 | 486.7337
1884.6604 | 523.6448 | 503.8962 | 480.0758 | 487.2046
1885.6604 | 523.6466 | 503.9351 | 479.8997 | 486.7886
1886.6604 | 523.7367 | 503.9901 | 480.0065 | 487.2446
1887.6604 | 523.6945 | 504.0243 | 480.0213 | 486.9691
1888.6604 | 523.6213 | 504.1095 | 479.7973 | 487.3523
1889.6604 | 523.6232 | 504.0832 | 479.7872 | 486.5073
1890.6604 | 523.5819 | 504.0877 | 479.9964 | 487.5367
1891.6604 | 523.5363 | 504.1831 | 480.016 | 486.9753
1892.6604 | 523.5774 | 504.2413 | 480.3106 | 487.9585
1893.6604 | 523.636 | 504.3093 | 480.7223 | 487.9
1894.6604 | 523.6564 | 504.3501 | 480.5076 | 488.1563
1895.6604 | 523.6525 | 504.3738 | 480.4615 | 488.2183
1896.6604 | 523.6567 | 504.3641 | 480.0265 | 488.216
1897.6604 | 523.703 | 504.4387 | 480.093 | 488.2038
1898.6604 | 523.6728 | 504.3916 | 479.9905 | 488.383
1899.6604 | 523.7869 | 504.4028 | 479.7341 | 488.5431
1900.6604 | 523.7457 | 504.3688 | 479.5423 | 488.227
1901.6604 | 523.7708 | 504.4306 | 479.9011 | 488.2542
1902.6604 | 523.7675 | 504.4537 | 480.3044 | 488.7539
1903.6604 | 523.717 | 504.3621 | 480.2182 | 488.9011
1904.6604 | 523.6991 | 504.4163 | 480.0955 | 488.7732
1905.6604 | 523.7317 | 504.4611 | 480.0059 | 488.9151
1906.6604 | 523.6695 | 504.5923 | 480.241 | 489.1601
1907.6604 | 523.6848 | 504.5972 | 480.3285 | 489.0593
1908.6604 | 523.5668 | 504.6505 | 480.1808 | 489.3017
1909.6604 | 523.4722 | 504.7612 | 480.0113 | 489.4407
1910.6604 | 523.4341 | 504.7716 | 480.1288 | 489.4274
1911.6604 | 523.3811 | 504.7945 | 480.1669 | 489.6671
1912.6604 | 523.405 | 504.8289 | 480.3536 | 489.712
1913.6604 | 523.4416 | 504.826 | 480.2851 | 489.3575
1914.6604 | 523.4812 | 504.8607 | 480.1073 | 489.8777
1915.6604 | 523.3438 | 504.7711 | 480.3267 | 489.9742
1916.6604 | 523.252 | 504.8515 | 480.5823 | 490.0202
1917.6604 | 523.3107 | 504.9237 | 480.3038 | 490.0865
1918.6604 | 523.343 | 505.0079 | 480.4555 | 489.84
1919.6604 | 523.3315 | 505.0033 | 480.1931 | 489.9132
1920.6604 | 523.4291 | 505.0477 | 480.2292 | 490.1283
1921.6604 | 523.4557 | 505.0504 | 480.1551 | 490.3608
1922.6604 | 523.5429 | 505.1365 | 480.2579 | 490.5524
1923.6604 | 523.4826 | 505.1857 | 480.6512 | 490.6229
1924.6604 | 523.5689 | 505.2215 | 480.7466 | 490.7634
1925.6604 | 523.6199 | 505.2131 | 480.9808 | 490.8829
1926.6604 | 523.6852 | 505.2137 | 480.5721 | 490.9671
1927.6604 | 523.6752 | 505.2546 | 480.2758 | 490.9993
1928.6604 | 523.6433 | 505.3202 | 480.2235 | 490.8637
1929.6604 | 523.7239 | 505.3626 | 480.532 | 491.0227
1930.6604 | 523.7564 | 505.3479 | 480.3778 | 491.2256
1931.6604 | 523.803 | 505.3134 | 480.0591 | 491.4643
1932.6604 | 523.8353 | 505.4357 | 480.3417 | 491.1571
1933.6604 | 523.7032 | 505.4168 | 480.4732 | 491.2763
1934.6604 | 523.6581 | 505.48 | 480.2271 | 491.5707
1935.6604 | 523.6651 | 505.54 | 480.172 | 491.6095
1936.6604 | 523.6293 | 505.5717 | 480.5799 | 491.9005
1937.6604 | 523.5302 | 505.6231 | 480.5665 | 491.5955
1938.6604 | 523.5873 | 505.6357 | 480.3661 | 491.5577
1939.6604 | 523.6307 | 505.5573 | 480.2959 | 491.9769
1940.6604 | 523.62 | 505.5952 | 480.4317 | 492.0157
1941.6604 | 523.5992 | 505.6591 | 480.4972 | 491.9846
1942.6604 | 523.5343 | 505.6227 | 480.5564 | 492.2625
1943.6604 | 523.5126 | 505.6798 | 480.439 | 492.2158
1944.6604 | 523.4365 | 505.6954 | 480.5097 | 492.2972
1945.6604 | 523.24 | 505.769 | 480.519 | 492.3134
1946.6604 | 523.1759 | 505.8322 | 480.6859 | 492.2989
1947.6604 | 523.2581 | 505.7929 | 480.8216 | 492.3376
1948.6604 | 523.2022 | 505.7061 | 480.9159 | 491.526
1949.6604 | 523.1221 | 505.7924 | 480.7969 | 492.4882
1950.6604 | 523.1182 | 505.7996 | 480.5242 | 492.3029
1951.6604 | 523.063 | 505.826 | 480.676 | 492.1432
1952.6604 | 523.0914 | 505.8239 | 480.5391 | 492.1992
1953.6604 | 523.2496 | 505.7885 | 480.7822 | 492.3688
1954.6604 | 523.275 | 505.9157 | 480.9247 | 492.5257
1955.6604 | 523.266 | 505.9617 | 480.947 | 492.2685
1956.6604 | 523.2872 | 505.9843 | 480.8558 | 492.2418
1957.6604 | 523.3451 | 506.0216 | 480.6771 | 492.618
1958.6604 | 523.3035 | 506.0007 | 481.1094 | 492.8176
1959.6604 | 523.3785 | 506.0215 | 481.1347 | 492.4947
1960.6604 | 523.3188 | 506.0649 | 481.4488 | 492.5096
1961.6604 | 523.2536 | 506.1123 | 481.6274 | 492.8957
1962.6604 | 523.1965 | 506.1688 | 481.531 | 492.9131
1963.6604 | 523.239 | 506.1886 | 481.4765 | 493.016
1964.6604 | 523.3524 | 506.2372 | 481.2399 | 493.2025
1965.6604 | 523.3801 | 506.1552 | 480.9911 | 493.3019
1966.6604 | 523.3504 | 506.248 | 481.0375 | 493.2559
1967.6604 | 523.32 | 506.337 | 480.8978 | 493.3217
1968.6604 | 523.305 | 506.3088 | 480.7575 | 493.3846
1969.6604 | 523.2368 | 506.2989 | 480.681 | 493.515
1970.6604 | 523.1081 | 506.3945 | 481.0393 | 493.5581
1971.6604 | 523.0459 | 506.4769 | 481.3737 | 493.6047
1972.6604 | 523.0883 | 506.4911 | 481.4124 | 493.4693
1973.6604 | 523.037 | 506.511 | 481.3868 | 493.5633
1974.6604 | 522.9603 | 506.5094 | 481.4612 | 493.8367
1975.6604 | 522.836 | 506.5967 | 481.4868 | 493.5422
1976.6604 | 522.902 | 506.5616 | 481.4926 | 493.6588
1977.6604 | 522.7612 | 506.6298 | 481.6392 | 494.1304
1978.6604 | 522.7013 | 506.6664 | 481.7963 | 494.1376
1979.6604 | 522.636 | 506.6313 | 481.8204 | 493.944
1980.6604 | 522.7237 | 506.7096 | 481.8162 | 494.1418
1981.6604 | 522.683 | 506.722 | 481.4773 | 493.9683
1982.6604 | 522.5804 | 506.7338 | 481.6902 | 494.0715
1983.6604 | 522.6076 | 506.7524 | 481.6696 | 494.4201
1984.6604 | 522.6806 | 506.7697 | 481.9206 | 494.4372
1985.6604 | 522.8546 | 506.7791 | 481.9753 | 494.2804
1986.6604 | 522.9149 | 506.7842 | 481.9377 | 494.4952
1987.6604 | 522.8734 | 506.8027 | 481.8618 | 494.5456
1988.6604 | 522.751 | 506.8837 | 481.8698 | 493.9597
1989.6604 | 522.6986 | 506.9575 | 481.886 | 494.7555
1990.6604 | 522.729 | 506.9168 | 481.9618 | 494.9375
1991.6604 | 522.7856 | 506.9218 | 481.863 | 494.6429
1992.6604 | 522.7264 | 506.9117 | 481.9444 | 494.6566
1993.6604 | 522.743 | 506.9537 | 481.7727 | 495.0254
1994.6604 | 522.8082 | 506.9285 | 481.9456 | 495.049
1995.6604 | 522.8688 | 506.8865 | 481.9131 | 494.8605
1996.6604 | 522.8382 | 506.9311 | 481.9332 | 495.2491
1997.6604 | 522.8221 | 506.9877 | 481.6018 | 495.2377
1998.6604 | 522.9822 | 507.0367 | 481.6885 | 494.8022
1999.6604 | 523.0831 | 507.158 | 482.0987 | 495.3429
2000.6604 | 523.0281 | 507.1513 | 482.292 | 495.015
2001.6604 | 523.1022 | 507.1605 | 482.1342 | 495.4835
2002.6604 | 523.0831 | 507.1947 | 482.0149 | 495.4733
2003.6604 | 523.1215 | 507.2211 | 481.8885 | 495.0805
2004.6604 | 523.1227 | 507.1988 | 482.0527 | 495.6308
2005.6604 | 523.1156 | 507.2574 | 482.0807 | 495.7902
2006.6604 | 523.0135 | 507.2465 | 482.3379 | 495.7912
2007.6604 | 523.0594 | 507.2711 | 481.9787 | 496.0232
2008.6604 | 523.0751 | 507.3712 | 481.9084 | 495.7186
2009.6604 | 523.1158 | 507.3996 | 481.7953 | 495.7732
2010.6604 | 523.0084 | 507.361 | 481.7086 | 496.1717
2011.6604 | 522.8632 | 507.3691 | 481.3982 | 496.0892
2012.6604 | 522.6023 | 507.4001 | 481.5821 | 496.1233
2013.6604 | 522.5657 | 507.3196 | 481.5483 | 496.3375
2014.6604 | 522.6149 | 507.3234 | 481.3271 | 496.1315
2015.6604 | 522.5755 | 507.3662 | 481.5877 | 496.1599
2016.6604 | 522.5297 | 507.3975 | 482.0841 | 496.5454
2017.6604 | 522.4155 | 507.4071 | 481.928 | 496.5041
2018.6604 | 522.3676 | 507.4955 | 481.7107 | 496.4334
2019.6604 | 522.3159 | 507.4932 | 481.8034 | 496.7849
2020.6604 | 522.276 | 507.52 | 481.358 | 496.8143
2021.6604 | 522.3278 | 507.61 | 481.1466 | 496.8217
2022.6604 | 522.4839 | 507.5446 | 481.2605 | 497.0614
2023.6604 | 522.4688 | 507.5853 | 481.6263 | 496.6607
2024.6604 | 522.4378 | 507.6058 | 481.6142 | 497.0712
2025.6604 | 522.5266 | 507.5945 | 482.1153 | 496.9904
2026.6604 | 522.6529 | 507.589 | 482.2862 | 497.0389
2027.6604 | 522.6124 | 507.6629 | 482.1469 | 496.9416
2028.6604 | 522.6621 | 507.7416 | 482.2618 | 497.1507
2029.6604 | 522.7063 | 507.7364 | 482.243 | 496.5964
2030.6604 | 522.7543 | 507.7419 | 482.3865 | 497.2739
2031.6604 | 522.9113 | 507.7891 | 482.3057 | 496.9556
2032.6604 | 522.9728 | 507.7375 | 482.0003 | 497.3791
2033.6604 | 523.0659 | 507.767 | 482.063 | 497.4831
2034.6604 | 523.1435 | 507.821 | 482.3268 | 497.3735
2035.6604 | 523.0866 | 507.8212 | 482.2104 | 497.4467
2036.6604 | 522.9782 | 507.8702 | 482.215 | 497.5217
2037.6604 | 523.0589 | 507.8415 | 482.0493 | 497.6641
2038.6604 | 523.1602 | 507.8959 | 482.126 | 497.8646
2039.6604 | 523.3008 | 507.9946 | 482.2216 | 497.8919
2040.6604 | 523.3739 | 508.0074 | 481.7021 | 497.9013
2041.6604 | 523.4302 | 507.9571 | 481.8008 | 497.9409
2042.6604 | 523.4132 | 508.0093 | 481.9829 | 497.2542
2043.6604 | 523.2812 | 508.0128 | 481.7286 | 498.0062
2044.6604 | 523.1582 | 507.9494 | 481.6065 | 498.1697
2045.6604 | 523.2297 | 507.9668 | 481.7631 | 498.0851
2046.6604 | 523.1848 | 508.0488 | 481.5615 | 498.1161
2047.6604 | 523.2487 | 507.9621 | 481.5693 | 498.0455
2048.6604 | 523.2263 | 508.1041 | 482.0575 | 498.2324
2049.6604 | 523.1108 | 508.12 | 482.021 | 498.4686
2050.6604 | 523.0606 | 508.2377 | 482.0243 | 498.4946
2051.6604 | 523.0665 | 508.1948 | 482.2222 | 498.6694
2052.6604 | 523.0172 | 508.2107 | 482.2331 | 498.8345
2053.6604 | 523.0842 | 508.2911 | 482.4088 | 498.823
2054.6604 | 523.138 | 508.2703 | 482.1671 | 498.8608
2055.6604 | 523.2201 | 508.2519 | 482.1197 | 498.7819
2056.6604 | 523.2286 | 508.2853 | 481.7949 | 498.8954
2057.6604 | 523.1807 | 508.2729 | 481.9491 | 498.9499
2058.6604 | 523.1962 | 508.3382 | 481.943 | 499.0145
2059.6604 | 523.2598 | 508.2963 | 482.2499 | 499.1809
2060.6604 | 523.2947 | 508.3972 | 482.0184 | 499.3623
2061.6604 | 523.4427 | 508.4028 | 481.5049 | 499.3209
2062.6604 | 523.4521 | 508.4775 | 481.3516 | 499.4657
2063.6604 | 523.3784 | 508.5843 | 481.4583 | 499.5611
2064.6604 | 523.3777 | 508.5799 | 481.5089 | 499.5332
2065.6604 | 523.3499 | 508.4916 | 481.3213 | 499.5754
2066.6604 | 523.4249 | 508.4987 | 481.5912 | 499.8293
2067.6604 | 523.4308 | 508.5637 | 481.5846 | 499.9926
2068.6604 | 523.4227 | 508.5606 | 481.3618 | 499.977
2069.6604 | 523.5435 | 508.5929 | 481.3684 | 499.9147
2070.6604 | 523.5939 | 508.3803 | 481.5084 | 500.0069
2071.6604 | 523.6194 | 508.393 | 481.9238 | 499.975
2072.6604 | 523.5391 | 508.477 | 482.2512 | 500.2293
2073.6604 | 523.4228 | 508.6354 | 482.2539 | 500.255
2074.6604 | 523.3008 | 508.6894 | 482.2501 | 500.1377
2075.6604 | 523.191 | 508.7181 | 482.0025 | 500.2902
2076.6604 | 523.3134 | 508.7376 | 482.2471 | 500.4523
2077.6604 | 523.3386 | 508.7233 | 482.4157 | 500.5274
2078.6604 | 523.3534 | 508.8373 | 482.5857 | 500.6116
2079.6604 | 523.284 | 508.8712 | 482.407 | 500.73
2080.6604 | 523.2716 | 508.8109 | 482.5363 | 500.3887
2081.6604 | 523.3803 | 508.8536 | 482.6619 | 500.8493
2082.6604 | 523.3582 | 508.9779 | 482.7821 | 500.8721
2083.6604 | 523.3131 | 509.0159 | 482.6007 | 500.7677
2084.6604 | 523.2049 | 509.0671 | 482.4057 | 500.8852
2085.6604 | 523.1389 | 509.0998 | 482.454 | 500.4213
2086.6604 | 523.1833 | 509.0441 | 482.4304 | 501.2559
2087.6604 | 523.2721 | 509.0668 | 482.352 | 501.2758
2088.6604 | 523.1911 | 509.077 | 482.7189 | 501.3707
2089.6604 | 523.2589 | 509.1801 | 482.9853 | 501.4273
2090.6604 | 523.2397 | 509.1797 | 482.9606 | 501.4052
2091.6604 | 523.2706 | 509.1953 | 483.0905 | 501.5431
2092.6604 | 523.1727 | 509.1212 | 483.165 | 501.4524
2093.6604 | 523.1109 | 509.1516 | 482.6447 | 501.6362
2094.6604 | 523.1219 | 509.1224 | 482.4683 | 501.7893
2095.6604 | 523.0841 | 509.1583 | 482.5035 | 501.7179
2096.6604 | 523.1072 | 509.2773 | 482.7573 | 501.9294
2097.6604 | 523.1234 | 509.2908 | 482.6609 | 501.9903
2098.6604 | 523.1382 | 509.2995 | 482.2577 | 502.0127
2099.6604 | 523.1771 | 509.3614 | 482.521 | 502.0288
2100.6604 | 523.1813 | 509.3814 | 482.2835 | 501.9765
2101.6604 | 523.123 | 509.3856 | 482.4086 | 501.9246
2102.6604 | 523.1196 | 509.4945 | 482.8658 | 501.9838
2103.6604 | 522.9814 | 509.4459 | 482.746 | 501.4001
2104.6604 | 522.9421 | 509.4687 | 482.6634 | 502.1479
2105.6604 | 523.0677 | 509.4806 | 482.3678 | 502.2173
2106.6604 | 523.1327 | 509.5804 | 482.7815 | 502.1982
2107.6604 | 523.1935 | 509.5763 | 482.6321 | 501.5095
2108.6604 | 523.2054 | 509.5827 | 482.5234 | 502.3469
2109.6604 | 523.2477 | 509.6047 | 482.6386 | 502.586
2110.6604 | 523.2071 | 509.596 | 483.0296 | 502.5344
2111.6604 | 523.3136 | 509.5759 | 483.0722 | 502.6662
2112.6604 | 523.4151 | 509.6953 | 482.7595 | 502.6158
2113.6604 | 523.396 | 509.761 | 482.8818 | 502.31
2114.6604 | 523.3007 | 509.7151 | 483.0863 | 502.3671
2115.6604 | 523.2807 | 509.7632 | 483.2048 | 502.8719
2116.6604 | 523.257 | 509.842 | 482.7743 | 502.8847
2117.6604 | 523.2813 | 509.8341 | 482.8863 | 502.8289
2118.6604 | 523.3843 | 509.9275 | 482.6815 | 502.5402
2119.6604 | 523.4648 | 509.9214 | 482.79 | 502.7808
2120.6604 | 523.4854 | 509.8883 | 482.5767 | 502.842
2121.6604 | 523.5675 | 509.9272 | 482.6255 | 502.3934
2122.6604 | 523.556 | 509.9472 | 482.4909 | 503.2689
2123.6604 | 523.5185 | 509.9264 | 482.4584 | 503.2011
2124.6604 | 523.5107 | 510.0055 | 482.6487 | 503.2117
2125.6604 | 523.5725 | 509.9625 | 482.5408 | 502.6772
2126.6604 | 523.4992 | 509.9731 | 482.7727 | 503.277
2127.6604 | 523.3556 | 510.0319 | 483.0153 | 503.5419
2128.6604 | 523.3859 | 509.9428 | 482.7043 | 503.5635
2129.6604 | 523.4377 | 510.0424 | 482.5624 | 503.6284
2130.6604 | 523.5458 | 510.0834 | 482.6019 | 503.7394
2131.6604 | 523.6365 | 510.0862 | 482.8774 | 503.4518
2132.6604 | 523.6576 | 510.1318 | 483.2661 | 503.7066
2133.6604 | 523.6137 | 510.075 | 482.6828 | 503.3083
2134.6604 | 523.6503 | 510.0719 | 482.5529 | 503.9209
2135.6604 | 523.628 | 510.0888 | 482.5965 | 504.1545
2136.6604 | 523.6296 | 510.1057 | 482.6569 | 504.1408
2137.6604 | 523.636 | 510.0597 | 482.9345 | 504.2344
2138.6604 | 523.5569 | 510.1427 | 483.1619 | 504.3424
2139.6604 | 523.5036 | 510.1784 | 483.0794 | 504.513
2140.6604 | 523.378 | 510.2155 | 483.2754 | 504.4882
2141.6604 | 523.3873 | 510.3265 | 483.5281 | 504.6978
2142.6604 | 523.3968 | 510.3927 | 483.3969 | 504.6711
2143.6604 | 523.4351 | 510.3849 | 483.5659 | 504.0473
2144.6604 | 523.3943 | 510.3497 | 483.2178 | 504.2282
2145.6604 | 523.3605 | 510.3886 | 483.3719 | 504.2889
2146.6604 | 523.4506 | 510.4509 | 483.3428 | 505.1167
2147.6604 | 523.4882 | 510.4615 | 483.1371 | 504.8272
2148.6604 | 523.583 | 510.522 | 483.4264 | 505.4859
2149.6604 | 523.6264 | 510.5366 | 483.7264 | 505.1076
2150.6604 | 523.6357 | 510.5481 | 483.8279 | 505.3845
2151.6604 | 523.5887 | 510.4894 | 483.5538 | 505.5574
2152.6604 | 523.6003 | 510.6125 | 483.6076 | 505.7392
2153.6604 | 523.5839 | 510.6174 | 483.3728 | 505.828
2154.6604 | 523.587 | 510.6854 | 483.4144 | 505.9434
2155.6604 | 523.4972 | 510.6692 | 483.4455 | 506.053
2156.6604 | 523.4504 | 510.7261 | 483.3544 | 506.1346
2157.6604 | 523.4275 | 510.704 | 483.565 | 506.2239
2158.6604 | 523.3408 | 510.6699 | 483.7973 | 506.3257
2159.6604 | 523.1892 | 510.7265 | 483.6893 | 506.501
2160.6604 | 523.1353 | 510.7964 | 483.5311 | 506.1576
2161.6604 | 523.1036 | 510.8407 | 483.2697 | 506.2291
2162.6604 | 523.1776 | 510.823 | 483.5008 | 506.3088
2163.6604 | 523.1678 | 510.8405 | 483.4714 | 506.3858
2164.6604 | 523.2814 | 510.8314 | 483.3983 | 506.413
2165.6604 | 523.4074 | 510.8148 | 483.6958 | 506.9327
2166.6604 | 523.52 | 510.823 | 483.6359 | 506.5195
2167.6604 | 523.5653 | 510.8458 | 483.7157 | 506.5951
2168.6604 | 523.6646 | 510.8228 | 483.6832 | 507.0578
2169.6604 | 523.7234 | 510.8863 | 483.8527 | 506.6551
2170.6604 | 523.6125 | 510.9354 | 483.7699 | 506.7195
2171.6604 | 523.5173 | 510.951 | 483.7651 | 507.0927
2172.6604 | 523.5481 | 510.9971 | 483.6783 | 507.2248
2173.6604 | 523.5438 | 511.0823 | 483.7024 | 506.613
2174.6604 | 523.415 | 511.1224 | 483.4256 | 506.8198
2175.6604 | 523.5539 | 511.1075 | 483.8707 | 507.527
2176.6604 | 523.6593 | 511.1479 | 484.1396 | 507.5753
2177.6604 | 523.6682 | 510.9714 | 484.3028 | 507.3088
2178.6604 | 523.6474 | 511.0985 | 484.2529 | 507.8014
2179.6604 | 523.6181 | 510.9464 | 484.0091 | 507.4927
2180.6604 | 523.4961 | 511.0371 | 484.1643 | 507.4945
2181.6604 | 523.5926 | 511.074 | 484.183 | 507.4949
2182.6604 | 523.6058 | 511.1029 | 483.946 | 507.5659
2183.6604 | 523.5976 | 511.1275 | 483.6275 | 507.5632
2184.6604 | 523.5688 | 511.0221 | 483.9605 | 507.7328
2185.6604 | 523.6764 | 511.1053 | 484.224 | 508.2069
2186.6604 | 523.67 | 511.2132 | 484.0037 | 507.6052
2187.6604 | 523.5899 | 511.2824 | 484.2587 | 507.9694
2188.6604 | 523.5101 | 511.3113 | 484.3536 | 508.5036
2189.6604 | 523.5192 | 511.3776 | 484.1628 | 508.5869
2190.6604 | 523.4066 | 511.3888 | 484.1319 | 508.6394
2191.6604 | 523.1864 | 511.2703 | 484.3478 | 508.7306
2192.6604 | 523.2797 | 511.2991 | 484.2817 | 508.8067
2193.6604 | 523.2535 | 511.3897 | 484.1388 | 508.8209
2194.6604 | 523.331 | 511.4671 | 484.1794 | 508.8691
2195.6604 | 523.3904 | 511.4321 | 484.039 | 508.4595
2196.6604 | 523.4637 | 511.4479 | 483.9648 | 508.926
2197.6604 | 523.4983 | 511.4992 | 483.6919 | 508.4646
2198.6604 | 523.5443 | 511.4855 | 484.0332 | 509.0457
2199.6604 | 523.5693 | 511.471 | 484.1095 | 508.4603
2200.6604 | 523.6178 | 511.4994 | 483.7262 | 508.5661
2201.6604 | 523.546 | 511.5651 | 483.6831 | 509.416
2202.6604 | 523.5319 | 511.5044 | 484.0878 | 509.4637
2203.6604 | 523.5462 | 511.5655 | 484.3659 | 508.982
2204.6604 | 523.6221 | 511.6172 | 484.4877 | 509.3358
2205.6604 | 523.6454 | 511.6818 | 484.2886 | 509.3849
2206.6604 | 523.7501 | 511.6067 | 484.3327 | 509.4299
2207.6604 | 523.8554 | 511.6893 | 484.6603 | 509.9245
2208.6604 | 523.7768 | 511.7542 | 484.3923 | 509.7275
2209.6604 | 523.6539 | 511.7403 | 484.1521 | 509.8503
2210.6604 | 523.6434 | 511.7387 | 484.3059 | 509.8791
2211.6604 | 523.739 | 511.7337 | 484.4043 | 509.6755
2212.6604 | 523.6242 | 511.797 | 484.3241 | 509.2111
2213.6604 | 523.5348 | 511.878 | 484.3914 | 509.3964
2214.6604 | 523.5731 | 511.8547 | 484.5571 | 510.1175
2215.6604 | 523.6514 | 511.8132 | 484.5283 | 510.1036
2216.6604 | 523.7122 | 511.864 | 484.5796 | 510.2202
2217.6604 | 523.7401 | 511.9098 | 484.9342 | 509.8703
2218.6604 | 523.7688 | 511.9301 | 484.4761 | 509.9579
2219.6604 | 523.6995 | 511.9293 | 484.6974 | 510.5357
2220.6604 | 523.742 | 512.0206 | 484.8887 | 510.6076
2221.6604 | 523.7947 | 512.027 | 485.0753 | 510.6945
2222.6604 | 523.8008 | 512.0287 | 485.1173 | 510.7314
2223.6604 | 523.7038 | 512.022 | 485.2594 | 510.7722
2224.6604 | 523.6993 | 511.9238 | 484.7226 | 510.8868
2225.6604 | 523.7359 | 511.9798 | 484.5296 | 510.9033
2226.6604 | 523.5715 | 511.9756 | 484.7948 | 510.6631
2227.6604 | 523.5399 | 512.0752 | 484.7567 | 510.7104
2228.6604 | 523.4965 | 512.0768 | 484.5747 | 511.1141
2229.6604 | 523.3572 | 512.1378 | 484.7181 | 511.0567
2230.6604 | 523.2725 | 512.1064 | 484.4565 | 510.464
2231.6604 | 523.183 | 512.0253 | 484.7729 | 511.1236
2232.6604 | 523.0649 | 512.0576 | 484.8238 | 510.6304
2233.6604 | 522.954 | 512.1386 | 484.8497 | 511.2158
2234.6604 | 522.8008 | 512.1823 | 484.7754 | 511.3122
2235.6604 | 522.7453 | 512.2386 | 484.8566 | 511.3772
2236.6604 | 522.7283 | 512.206 | 485.1696 | 511.7724
2237.6604 | 522.6706 | 512.2812 | 485.0227 | 511.9529
2238.6604 | 522.6085 | 512.2415 | 484.8726 | 511.7823
2239.6604 | 522.5534 | 512.2165 | 484.9238 | 511.9158
2240.6604 | 522.5356 | 512.1731 | 484.6928 | 512.4141
2241.6604 | 522.6291 | 512.23 | 484.5332 | 512.1461
2242.6604 | 522.6099 | 512.2922 | 484.7862 | 512.2099
2243.6604 | 522.7237 | 512.3189 | 484.5486 | 512.5709
2244.6604 | 522.9796 | 512.1875 | 484.6859 | 512.0563
2245.6604 | 522.9236 | 512.1658 | 484.5586 | 511.977
2246.6604 | 522.9326 | 512.2619 | 484.6484 | 512.1654
2247.6604 | 522.8551 | 512.2346 | 484.5901 | 512.0523
2248.6604 | 522.7832 | 512.2545 | 484.4296 | 512.202
2249.6604 | 522.8432 | 512.2985 | 484.6033 | 512.1845
2250.6604 | 522.8585 | 512.3478 | 484.8401 | 512.1897
2251.6604 | 522.8548 | 512.2995 | 484.8869 | 511.6721
2252.6604 | 522.9952 | 512.3276 | 485.0691 | 511.8304
2253.6604 | 523.1589 | 512.4144 | 484.8132 | 512.2653
2254.6604 | 523.2628 | 512.3754 | 484.8114 | 511.9182
2255.6604 | 523.3377 | 512.3888 | 485.1375 | 511.9313
2256.6604 | 523.2924 | 512.4563 | 485.4705 | 512.3489
2257.6604 | 523.3387 | 512.4357 | 485.4816 | 512.2842
2258.6604 | 523.4405 | 512.506 | 485.5609 | 511.995
2259.6604 | 523.4024 | 512.4854 | 485.1189 | 512.3659
2260.6604 | 523.4206 | 512.5621 | 485.0794 | 511.6488
2261.6604 | 523.3471 | 512.557 | 485.0869 | 512.5911
2262.6604 | 523.3459 | 512.6086 | 485.3445 | 512.6954
2263.6604 | 523.3276 | 512.6606 | 485.637 | 512.8319
2264.6604 | 523.2111 | 512.6554 | 485.6662 | 512.8502
2265.6604 | 523.1847 | 512.6828 | 485.7787 | 512.7342
2266.6604 | 523.138 | 512.7125 | 485.8319 | 511.9142
2267.6604 | 523.0969 | 512.6577 | 485.8718 | 513.1768
2268.6604 | 523.0606 | 512.6652 | 485.9872 | 513.1706
2269.6604 | 523.0681 | 512.7129 | 486.0991 | 513.3111
2270.6604 | 523.156 | 512.6949 | 485.8262 | 513.2799
2271.6604 | 523.2106 | 512.71 | 485.9122 | 513.2538
2272.6604 | 523.2176 | 512.7846 | 485.9452 | 513.1387
2273.6604 | 523.2433 | 512.7318 | 485.9769 | 513.0619
2274.6604 | 523.3011 | 512.771 | 486.2234 | 513.1412
2275.6604 | 523.419 | 512.8165 | 486.0475 | 513.0464
2276.6604 | 523.6196 | 512.844 | 486.0813 | 512.8158
2277.6604 | 523.6712 | 512.8818 | 486.046 | 512.8794
2278.6604 | 523.6377 | 512.9133 | 486.047 | 512.9005
2279.6604 | 523.6611 | 512.8857 | 486.2332 | 513.0631
2280.6604 | 523.6356 | 512.8912 | 486.1829 | 513.0191
2281.6604 | 523.4937 | 512.8614 | 486.3639 | 513.1352
2282.6604 | 523.4421 | 512.9466 | 486.2897 | 513.138
2283.6604 | 523.5252 | 512.9615 | 486.5044 | 513.1613
2284.6604 | 523.5288 | 512.9794 | 486.349 | 512.7607
2285.6604 | 523.5776 | 513.0402 | 486.5383 | 512.8342
2286.6604 | 523.4963 | 513.0052 | 486.2494 | 513.1163
2287.6604 | 523.4288 | 513.0986 | 486.2293 | 512.9274
2288.6604 | 523.37 | 513.064 | 486.4946 | 512.9461
2289.6604 | 523.2519 | 513.0358 | 486.4551 | 513.2818
2290.6604 | 523.0455 | 513.01 | 486.1763 | 512.9847
2291.6604 | 523.0342 | 513.0565 | 486.1113 | 512.7236
2292.6604 | 523.0133 | 513.0655 | 486.3375 | 513.3755
2293.6604 | 523.0248 | 513.0711 | 486.3155 | 513.4023
2294.6604 | 523.011 | 513.0466 | 486.2863 | 513.0339
2295.6604 | 523.0435 | 513.0091 | 486.3996 | 513.4168
2296.6604 | 523.0653 | 513.0468 | 486.4584 | 513.4142
2297.6604 | 523.0166 | 513.0545 | 486.6112 | 513.4324
2298.6604 | 522.8449 | 513.1329 | 486.7919 | 513.302
2299.6604 | 522.7619 | 513.2129 | 486.7383 | 513.5341
2300.6604 | 522.6898 | 513.1664 | 486.6258 | 513.106
2301.6604 | 522.7725 | 513.1595 | 486.273 | 513.4997
2302.6604 | 522.814 | 513.1136 | 486.2728 | 513.2271
2303.6604 | 522.7324 | 513.1257 | 486.2714 | 512.6513
2304.6604 | 522.7027 | 513.2392 | 486.3226 | 512.9041
2305.6604 | 522.858 | 513.2508 | 486.4487 | 512.8195
2306.6604 | 522.9731 | 513.1334 | 486.4178 | 512.6658
2307.6604 | 523.0028 | 513.1876 | 486.7163 | 511.9215
2308.6604 | 523.0014 | 513.2855 | 486.8307 | 512.0686
2309.6604 | 523.104 | 513.3044 | 486.7017 | 512.7969
2310.6604 | 523.1527 | 513.3434 | 486.7403 | 512.6307
2311.6604 | 523.3135 | 513.3703 | 486.7569 | 512.8637
2312.6604 | 523.48 | 513.3875 | 486.6551 | 512.889
2313.6604 | 523.4505 | 513.4028 | 486.7284 | 512.9168
2314.6604 | 523.4527 | 513.2734 | 486.8417 | 512.5202
2315.6604 | 523.3695 | 513.304 | 487.0106 | 512.3574
2316.6604 | 523.3706 | 513.3487 | 487.1398 | 512.8894
2317.6604 | 523.3126 | 513.3565 | 487.1487 | 512.5672
2318.6604 | 523.3843 | 513.4334 | 487.1934 | 512.4038
2319.6604 | 523.3355 | 513.4721 | 486.7747 | 512.5617
2320.6604 | 523.3491 | 513.4827 | 486.7505 | 511.7641
2321.6604 | 523.3417 | 513.4444 | 487.0276 | 511.721
2322.6604 | 523.2307 | 513.5103 | 487.2038 | 512.3644
2323.676 | 523.27 | 513.5068 | 487.0099 | 511.9044
2324.6604 | 523.3079 | 513.4099 | 486.7367 | 511.8562
2325.6604 | 523.3313 | 513.4208 | 487.0019 | 512.2788
2326.6604 | 523.3803 | 513.457 | 487.2586 | 512.0602
2327.6604 | 523.395 | 513.5523 | 487.3363 | 511.7584
2328.6604 | 523.3957 | 513.5644 | 487.2031 | 511.6197
2329.6604 | 523.4182 | 513.5623 | 487.3212 | 512.1133
2330.6604 | 523.3322 | 513.594 | 487.3624 | 511.593
2331.6604 | 523.3503 | 513.6105 | 487.5486 | 512.0514
2332.6604 | 523.4268 | 513.5934 | 487.4799 | 512.0308
2333.6604 | 523.4083 | 513.6375 | 487.3092 | 511.9624
2334.6604 | 523.3838 | 513.6577 | 487.3644 | 512.029
2335.6604 | 523.2847 | 513.6792 | 487.5106 | 511.8219
2336.6604 | 523.2768 | 513.6792 | 487.3906 | 511.0579
2337.6604 | 523.2917 | 513.6636 | 487.2536 | 511.1096
2338.6604 | 523.33 | 513.6603 | 487.2636 | 511.1985
2339.6604 | 523.3842 | 513.7599 | 487.608 | 510.9703
2340.6604 | 523.2347 | 513.7648 | 487.7479 | 511.6224
2341.6604 | 523.1615 | 513.8144 | 487.8217 | 511.1051
2342.6604 | 523.1353 | 513.7438 | 487.8767 | 511.0272
2343.6604 | 523.1559 | 513.7724 | 487.8988 | 511.3951
2344.6604 | 523.2257 | 513.7856 | 487.7777 | 511.1619
2345.6604 | 523.1525 | 513.7884 | 487.7466 | 511.1427
2346.6604 | 523.0723 | 513.7926 | 487.8683 | 511.0155
2347.6604 | 523.0137 | 513.8581 | 487.8107 | 510.463
2348.6604 | 523.0682 | 513.8577 | 487.5968 | 510.3695
2349.6604 | 523.0835 | 513.7694 | 487.7327 | 511.2643
2350.6604 | 523.1046 | 513.8896 | 487.901 | 511.2366
2351.6604 | 523.165 | 513.8815 | 488.0617 | 510.6841
2352.6604 | 523.1996 | 513.9617 | 488.0113 | 510.6106
2353.6604 | 523.16 | 513.9411 | 487.9037 | 510.6082
2354.6604 | 523.0659 | 513.9248 | 488.0071 | 510.8336
2355.6604 | 522.9887 | 513.8831 | 487.7886 | 510.6485
2356.6604 | 522.8776 | 513.8952 | 487.595 | 511.0695
2357.6604 | 522.7691 | 513.8781 | 487.905 | 510.6176
2358.6604 | 522.859 | 513.9051 | 487.5743 | 510.3811
2359.6604 | 522.9017 | 513.978 | 487.7831 | 510.8463
2360.6604 | 522.9206 | 514.016 | 487.951 | 510.9047
2361.6604 | 522.9211 | 513.9731 | 487.6289 | 510.7516
2362.6604 | 522.8627 | 514.0335 | 487.704 | 510.688
2363.6604 | 522.9928 | 514.0672 | 487.319 | 510.4995
2364.6604 | 522.9885 | 514.1031 | 487.2683 | 510.3391
2365.6604 | 522.915 | 514.0986 | 487.5779 | 509.9509
2366.6604 | 522.7725 | 514.1007 | 487.7085 | 510.1877
2367.6604 | 522.7925 | 514.1037 | 487.7878 | 510.1974
2368.6604 | 522.8288 | 514.0518 | 487.8361 | 509.7936
2369.6604 | 522.874 | 514.0718 | 487.7644 | 509.9068
2370.6604 | 522.923 | 514.1307 | 487.7829 | 509.2826
2371.6604 | 522.8488 | 514.092 | 487.9741 | 509.2751
2372.6604 | 522.8428 | 514.0916 | 488.1062 | 509.5469
2373.6604 | 522.8453 | 514.0959 | 488.2175 | 508.7845
2374.6604 | 522.7865 | 514.1819 | 488.2859 | 509.6234
2375.6917 | 522.6768 | 514.2249 | 488.2387 | 509.5036
2376.6604 | 522.7714 | 514.2986 | 488.3317 | 509.5977
2377.6604 | 522.8188 | 514.2842 | 488.414 | 509.5889
2378.6604 | 522.7522 | 514.2487 | 488.4854 | 509.4765
2379.6604 | 522.7316 | 514.1904 | 488.4774 | 508.8986
2380.6604 | 522.7268 | 514.262 | 488.246 | 508.8695
2381.6604 | 522.6656 | 514.2312 | 488.4009 | 509.3702
2382.6604 | 522.6554 | 514.1954 | 488.3693 | 508.9416
2383.6604 | 522.7425 | 514.2089 | 488.3018 | 509.0521
2384.6604 | 522.7977 | 514.2674 | 488.4665 | 509.2041
2385.6604 | 522.8772 | 514.2889 | 488.2729 | 509.2141
2386.6604 | 522.8883 | 514.3262 | 488.5439 | 509.092
2387.6604 | 522.8623 | 514.3344 | 488.706 | 509.0295
2388.6604 | 522.9403 | 514.3306 | 488.6535 | 509.139
2389.6604 | 522.95 | 514.4054 | 488.7537 | 508.6495
2390.6604 | 522.9462 | 514.4438 | 488.7136 | 508.6435
2391.6604 | 523.0679 | 514.4103 | 488.3599 | 508.922
2392.6604 | 523.0618 | 514.4755 | 488.4537 | 508.5608
2393.6604 | 523.0177 | 514.5103 | 488.66 | 508.4855
2394.6604 | 522.9638 | 514.4666 | 488.3148 | 508.7823
2395.6604 | 523.0798 | 514.5354 | 488.2717 | 508.7852
2396.6604 | 523.0982 | 514.5611 | 488.3948 | 508.6043
2397.6604 | 522.9953 | 514.3915 | 488.2784 | 508.7838
2398.6604 | 522.9643 | 514.4248 | 488.4502 | 508.2387
2399.6604 | 522.9271 | 514.5142 | 488.4835 | 508.4961
2400.6604 | 522.8392 | 514.5729 | 488.6057 | 508.0099
2401.6604 | 522.7478 | 514.58 | 488.6978 | 507.8587
2402.6604 | 522.6688 | 514.5925 | 488.3802 | 508.7089
2403.6604 | 522.4901 | 514.6588 | 488.6266 | 508.696
2404.6604 | 522.4403 | 514.6121 | 488.648 | 508.2885
2405.6604 | 522.4296 | 514.6185 | 488.6455 | 508.6346
2406.6604 | 522.4354 | 514.5318 | 487.9586 | 508.387
2407.6604 | 522.42 | 514.4795 | 487.9844 | 508.2337
2408.6604 | 522.4415 | 514.5563 | 488.3987 | 507.6555
2409.6604 | 522.4513 | 514.5697 | 488.7609 | 507.8899
2410.6604 | 522.5423 | 514.5877 | 488.5319 | 507.1415
2411.6604 | 522.668 | 514.6587 | 488.3502 | 507.2796
2412.6604 | 522.7818 | 514.6666 | 488.4799 | 507.4704
2413.7073 | 522.8159 | 514.6689 | 488.6627 | 507.0263
2414.6604 | 522.6953 | 514.6656 | 488.3365 | 507.0649
2415.6604 | 522.6397 | 514.7119 | 488.6109 | 506.7944
2416.6604 | 522.7252 | 514.7521 | 488.5985 | 506.4044
2417.6604 | 522.8934 | 514.7707 | 488.7191 | 506.4544
2418.6604 | 522.8949 | 514.7635 | 488.5311 | 506.545
2419.6604 | 522.9845 | 514.7616 | 488.5613 | 507.045
2420.6604 | 522.9979 | 514.7489 | 488.6448 | 506.6406
2421.6604 | 523.0383 | 514.7349 | 488.8921 | 505.679
2422.6604 | 523.0885 | 514.7795 | 488.657 | 506.6326
2423.6604 | 522.9777 | 514.7527 | 488.65 | 505.6284
2424.6604 | 522.9209 | 514.7743 | 488.79 | 505.0544
2425.6604 | 522.9291 | 514.8098 | 488.8026 | 506.3656
2426.6604 | 522.9561 | 514.8027 | 488.9518 | 506.4602
2427.6604 | 522.9018 | 514.7812 | 489.1438 | 506.0247
2428.6604 | 522.8295 | 514.7989 | 489.0758 | 506.2951
2429.6604 | 522.696 | 514.8445 | 489.1246 | 505.2118
2430.6604 | 522.7226 | 514.8863 | 489.1476 | 505.709
2431.6604 | 522.6739 | 514.949 | 489.2511 | 506.1778
2432.6604 | 522.7069 | 514.973 | 489.4065 | 505.9312
2433.6604 | 522.7287 | 514.9474 | 489.4564 | 505.8693
2434.6604 | 522.7461 | 514.9878 | 489.4585 | 505.8424
2435.6604 | 522.7229 | 514.9699 | 489.537 | 505.6651
2436.6604 | 522.7275 | 514.9765 | 489.3344 | 505.332
2437.6604 | 522.8606 | 515.0617 | 489.2797 | 505.4113
2438.6604 | 522.8377 | 514.9684 | 489.4689 | 505.3206
2439.6604 | 522.856 | 514.9472 | 489.4547 | 505.1912
2440.6604 | 522.9411 | 514.9958 | 489.1573 | 505.1552
2441.6604 | 523.0461 | 514.9426 | 489.4702 | 504.652
2442.6604 | 523.0864 | 514.9507 | 489.6301 | 505.0271
2443.6604 | 523.1123 | 514.9809 | 489.461 | 504.2731
2444.6604 | 523.0979 | 515.0225 | 489.11 | 504.3541
2445.6604 | 523.0486 | 515.0747 | 489.2369 | 504.0463
2446.6604 | 522.9282 | 515.0752 | 489.3075 | 504.6429
2447.6604 | 522.863 | 515.0311 | 489.3599 | 504.5875
2448.6604 | 522.8593 | 515.0863 | 489.2169 | 504.0366
2449.6604 | 522.8728 | 515.1339 | 489.427 | 504.0524
2450.6604 | 522.8541 | 515.167 | 489.4669 | 503.8092
2451.6604 | 522.8031 | 515.1436 | 489.5762 | 503.665
2452.6604 | 522.7521 | 515.1756 | 489.4614 | 503.6491
2453.6604 | 522.7578 | 515.2286 | 489.5902 | 503.2234
2454.676 | 522.7573 | 515.2256 | 489.4351 | 503.9027
2455.6604 | 522.8866 | 515.2304 | 489.1238 | 503.7001
2456.6604 | 522.9013 | 515.244 | 489.3379 | 502.9717
2457.6604 | 522.9045 | 515.2745 | 489.5469 | 502.9966
2458.6604 | 522.9253 | 515.3019 | 489.1788 | 502.222
2459.6604 | 522.9193 | 515.2053 | 489.1012 | 502.7556
2460.6604 | 522.9097 | 515.2239 | 489.2304 | 502.3237
2461.6604 | 522.837 | 515.206 | 489.5205 | 502.0505
2462.6604 | 522.8812 | 515.2134 | 489.5629 | 502.3805
2463.6604 | 522.886 | 515.2567 | 489.7028 | 502.1796
2464.6604 | 522.8358 | 515.2235 | 489.5623 | 484.4252
2465.6604 | 522.8239 | 515.1945 | 489.3859 | 523.4824
2466.6604 | 522.8031 | 515.2207 | 489.255 | 522.805
2467.6604 | 522.8341 | 515.14 | 488.888 | 523.4588
2468.6604 | 522.917 | 515.0797 | 488.5595 | 523.5491
2469.6604 | 522.9655 | 515.1089 | 488.4331 | 523.3518
2470.6604 | 522.9974 | 515.1033 | 488.682 | 523.4017
2471.6604 | 522.8489 | 515.1779 | 489.0408 | 524.0294
2472.6604 | 522.9293 | 515.2355 | 488.9986 | 524.0896
2473.6604 | 522.9182 | 515.263 | 489.0225 | 524.1063
2474.6604 | 522.9342 | 515.3485 | 488.9401 | 523.8374
2475.6604 | 523.0197 | 515.4016 | 488.5284 | 524.4142
2476.6604 | 522.8914 | 515.3834 | 488.5516 | 523.8111
2477.6604 | 522.8673 | 515.4038 | 488.3765 | 524.0354
2478.6604 | 522.8272 | 515.3954 | 488.7238 | 524.0761
2479.6604 | 522.8964 | 515.3336 | 488.611 | 523.8953
2480.6604 | 522.9064 | 515.4373 | 488.7384 | 524.0765
2481.6604 | 522.9301 | 515.4378 | 488.6635 | 523.7939
2482.6604 | 522.9454 | 515.4334 | 488.9478 | 523.5922
2483.6604 | 522.9879 | 515.4511 | 488.9959 | 523.6042
2484.6604 | 523.0177 | 515.4405 | 488.7384 | 523.4254
2485.6604 | 523.0231 | 515.4583 | 488.9054 | 523.7125
2486.6604 | 523.0609 | 515.4655 | 488.7479 | 523.462
2487.6604 | 523.0551 | 515.4346 | 488.691 | 523.8187
2488.6604 | 523.1005 | 515.5211 | 488.8538 | 523.3437
2489.6604 | 523.0933 | 515.4915 | 488.8698 | 523.1872
2490.6604 | 523.0795 | 515.462 | 489.0364 | 522.838
2491.6604 | 523.0374 | 515.4776 | 489.3581 | 523.3171
2492.6604 | 522.9383 | 515.5 | 489.2595 | 522.4923
2493.6604 | 522.9403 | 515.5627 | 489.3758 | 523.3517
2494.6604 | 522.8039 | 515.5412 | 489.4966 | 523.0852
2495.6604 | 522.7091 | 515.5387 | 489.4323 | 523.0072
2496.6604 | 522.6751 | 515.5843 | 489.5059 | 523.2172
2497.6604 | 522.6592 | 515.6292 | 489.4297 | 522.8763
2498.6604 | 522.6074 | 515.6241 | 489.5766 | 522.7778
2499.6604 | 522.6422 | 515.5967 | 489.7245 | 523.4657
2500.6604 | 522.6424 | 515.6099 | 489.7447 | 522.5371
2501.6604 | 522.5898 | 515.6437 | 489.7741 | 522.247
2502.6604 | 522.7081 | 515.7061 | 489.7512 | 522.3537
2503.6604 | 522.7178 | 515.5924 | 489.3949 | 522.6007
2504.6604 | 522.5923 | 515.6732 | 489.202 | 523.1311
2505.6604 | 522.5479 | 515.7115 | 489.2296 | 523.0637
2506.6604 | 522.4772 | 515.6779 | 489.3735 | 522.787
2507.6604 | 522.4581 | 515.6867 | 489.4368 | 522.7443
2508.6604 | 522.5495 | 515.7231 | 489.7016 | 522.2555
2509.6604 | 522.5768 | 515.7746 | 489.8173 | 522.1299
2510.6604 | 522.5308 | 515.7745 | 489.867 | 523.3437
2511.6604 | 522.5276 | 515.8019 | 489.9482 | 523.5431
2512.6604 | 522.6133 | 515.8923 | 490.0247 | 523.5759
2513.6604 | 522.6437 | 515.8841 | 489.9923 | 524.461
2514.6604 | 522.6569 | 515.8422 | 490.149 | 523.9608
2515.6604 | 522.7843 | 515.8923 | 490.3439 | 524.8452
2516.6604 | 522.7991 | 515.8735 | 490.3378 | 525.0411
2517.6604 | 522.8404 | 515.9033 | 490.3471 | 524.5472
2518.6604 | 522.781 | 515.9576 | 490.2951 | 524.6686
2519.6604 | 522.8447 | 515.9221 | 490.2285 | 525.2681
2520.6604 | 522.8994 | 515.9039 | 490.1619 | 527.2139
2521.6604 | 522.9207 | 515.923 | 490.3384 | 527.6311
2522.6604 | 522.9684 | 515.9118 | 490.3689 | 528.0985
2523.6604 | 522.8629 | 515.9061 | 490.312 | 528.9338
2524.6604 | 522.7723 | 515.9832 | 490.2287 | 528.7106
2525.6604 | 522.7749 | 516.0361 | 489.9067 | 528.9452
2526.6604 | 522.8736 | 515.8513 | 490.0315 | 529.2421
2527.6604 | 522.9952 | 516.0107 | 490.4012 | 528.7886
2528.6604 | 523.1565 | 515.9946 | 490.3885 | 529.1636
2529.6604 | 523.227 | 515.9834 | 490.3291 | 529.8918
2530.6604 | 523.2362 | 516.028 | 490.3929 | 530.2148
2531.6604 | 523.187 | 515.9977 | 490.3888 | 530.595
2532.6604 | 523.1731 | 515.9735 | 490.2002 | 530.3508
2533.6604 | 523.1837 | 515.9985 | 490.2633 | 530.598
2534.6604 | 523.2438 | 516.1246 | 490.0605 | 530.7139
2535.6604 | 523.2883 | 516.0976 | 490.337 | 530.1848
2536.6604 | 523.321 | 516.0998 | 490.5513 | 530.6441
2537.6604 | 523.3525 | 516.1334 | 490.4491 | 530.5313
2538.6604 | 523.3694 | 516.1413 | 490.4639 | 530.1198
2539.6604 | 523.3141 | 516.1362 | 490.285 | 529.7602
2540.6604 | 523.2708 | 516.1763 | 490.4534 | 529.7918
2541.6604 | 523.2633 | 516.0674 | 490.2005 | 529.7674
2542.6604 | 523.1685 | 516.0701 | 490.1172 | 530.5948
2543.6604 | 523.1733 | 516.0926 | 490.2736 | 531.2189
2544.6604 | 523.1736 | 516.1642 | 490.3326 | 531.3739
2545.6604 | 523.0879 | 516.225 | 490.3558 | 530.911
2546.6604 | 523.0402 | 516.1851 | 490.4752 | 531.7535
2547.6604 | 522.943 | 516.1717 | 490.2581 | 531.2682
2548.6604 | 522.8778 | 516.2119 | 490.1931 | 530.1931
2549.6604 | 522.883 | 516.3159 | 490.2844 | 530.6312
2550.6604 | 522.8339 | 516.2369 | 490.0191 | 531.9064
2551.6604 | 522.8014 | 516.2323 | 490.0032 | 532.8
2552.6604 | 522.7754 | 516.2871 | 490.3 | 503.1884
2553.6604 | 522.7478 | 516.3161 | 490.5746 | 502.7744
2554.6604 | 522.7067 | 516.3435 | 490.3563 | 507.183
2555.6604 | 522.7508 | 516.3803 | 490.2398 | 511.3178
2556.6604 | 522.8006 | 516.3479 | 490.1835 | 515.3942
2557.6604 | 522.863 | 516.3125 | 490.3245 | 501.7155
2558.6604 | 522.8963 | 516.3711 | 490.2481 | 529.8921
2559.6604 | 522.8684 | 516.3107 | 490.1014 | 538.2416
2560.6604 | 522.7739 | 516.3386 | 490.0768 | 541.9094
2561.6604 | 522.7155 | 516.3856 | 490.4099 | 496.6162
2562.6604 | 522.7227 | 516.5163 | 490.4727 | 626.7164
2563.6604 | 522.6908 | 516.5514 | 490.1933 | 627.3771
2564.6604 | 522.7106 | 516.4926 | 489.9809 | 627.5253
2565.6604 | 522.7824 | 516.5256 | 489.9384 | 627.8872
2566.6604 | 522.881 | 516.553 | 489.9286 | 628.2578
2567.6604 | 522.9679 | 516.5056 | 489.8441 | 628.0378
2568.6604 | 522.9513 | 516.4768 | 489.7478 | 627.5913
2569.6604 | 522.9304 | 516.5337 | 489.8214 | 596.1966
2570.6604 | 522.9715 | 516.5528 | 490.0297 | 595.4345
2571.6604 | 522.9971 | 516.6023 | 490.1122 | 628.7912
2572.6604 | 522.9503 | 516.5414 | 490.0695 | 627.1837
2573.6604 | 523.0012 | 516.5769 | 490.0209 | 627.1037
2574.6604 | 523.0523 | 516.6255 | 490.0868 | 627.5926
2575.6604 | 523.1478 | 516.7038 | 490.2801 | 627.5726
2576.6604 | 523.2433 | 516.6994 | 490.2523 | 628.1465
2577.6604 | 523.4049 | 516.7015 | 490.2735 | 627.8878
2578.6604 | 523.4224 | 516.6853 | 489.8815 | 628.464
2579.6604 | 523.4772 | 516.6188 | 489.4996 | 628.2793
2580.6604 | 523.5671 | 516.6539 | 489.9432 | 628.4901
2581.6604 | 523.5525 | 516.6616 | 490.1596 | 628.4899
2582.6604 | 523.5931 | 516.597 | 490.251 | 628.9584
2583.6604 | 523.7387 | 516.6568 | 490.1586 | 629.4739
2584.6604 | 523.7113 | 516.6131 | 490.1811 | 630.0006
2585.6604 | 523.6672 | 516.7029 | 490.5623 | 630.9387
2586.6604 | 523.5464 | 516.6685 | 490.3469 | 631.3786
2587.6604 | 523.4835 | 516.6424 | 490.1727 | 631.2008
2588.6604 | 523.4444 | 516.7452 | 490.4782 | 632.0555
2589.6604 | 523.4217 | 516.8592 | 490.6032 | 632.2058
2590.6604 | 523.4968 | 516.7266 | 490.6257 | 632.4087
2591.6604 | 523.468 | 516.7863 | 490.4725 | 632.0146
2592.6604 | 523.4985 | 516.8617 | 490.4633 | 632.4051
2593.6604 | 523.5176 | 516.8047 | 490.2819 | 632.9589
2594.6604 | 523.6052 | 516.7727 | 490.2214 | 633.1663
2595.6604 | 523.6392 | 516.759 | 490.2938 | 634.2602
2596.6604 | 523.5575 | 516.8098 | 490.3684 | 634.8036
2597.6604 | 523.4974 | 516.8841 | 490.4737 | 635.7387
2598.6604 | 523.5275 | 516.9368 | 490.3434 | 636.3818
2599.6604 | 523.4288 | 517.0053 | 490.4124 | 635.9396
2600.6604 | 523.4687 | 516.9241 | 490.4027 | 636.716
2601.6604 | 523.4657 | 516.9593 | 490.3344 | 636.1224
2602.6604 | 523.4453 | 516.8045 | 490.2945 | 636.4264
2603.6604 | 523.4102 | 516.7977 | 490.2348 | 636.8906
2604.6604 | 523.3446 | 516.9354 | 490.3765 | 636.8663
2605.6604 | 523.3374 | 516.9491 | 490.6155 | 637.2998
2606.6604 | 523.3794 | 516.8487 | 490.5736 | 638.41
2607.6604 | 523.3662 | 516.6858 | 490.5501 | 638.8636
2608.6604 | 523.4148 | 516.8475 | 490.6765 | 639.3008
2609.6604 | 523.4279 | 516.9711 | 490.5074 | 639.0406
2610.6604 | 523.4421 | 516.8987 | 490.5588 | 639.6993
2611.6604 | 523.382 | 516.9417 | 490.3833 | 640.5947
2612.6604 | 523.337 | 516.9032 | 490.3233 | 641.1049
2613.6604 | 523.3094 | 516.9414 | 490.4478 | 641.7403
2614.6604 | 523.1865 | 517.0267 | 490.3327 | 642.0579
2615.6604 | 523.2102 | 517.0327 | 490.2688 | 642.5708
2616.6604 | 523.1691 | 517.0492 | 490.1837 | 642.7556
2617.6604 | 523.0794 | 517.036 | 490.3631 | 643.1222
2618.6604 | 523.1319 | 516.935 | 490.2229 | 642.3884
2619.6604 | 523.1338 | 516.928 | 489.9465 | 642.9838
2620.6604 | 523.1476 | 516.9523 | 490.0018 | 644.5018
2621.6604 | 523.2203 | 516.998 | 490.0583 | 645.1426
2622.6604 | 523.3203 | 517.105 | 490.2952 | 645.4829
2623.6604 | 523.3573 | 517.0979 | 490.6297 | 645.6916
2624.6604 | 523.2746 | 517.1477 | 490.7746 | 645.4799
2625.6604 | 523.3554 | 517.1945 | 490.2648 | 645.6955
2626.6604 | 523.4103 | 517.1142 | 490.4364 | 645.8077
2627.6604 | 523.3487 | 517.1785 | 490.6944 | 653.1352
2628.6604 | 523.2695 | 517.177 | 490.9401 | 663.1033
2629.6604 | 523.3707 | 517.1685 | 490.9404 | 664.4262
2630.6604 | 523.3485 | 517.1823 | 490.8401 | 666.5422
2631.6604 | 523.2814 | 517.208 | 490.8696 | 667.8771
2632.6604 | 523.2218 | 517.2955 | 491.2653 | 670.2202
2633.6604 | 523.2961 | 517.3201 | 491.1288 | 671.6819
2634.6604 | 523.3424 | 517.3009 | 491.2295 | 672.7444
2635.6604 | 523.4307 | 517.3676 | 491.1353 | 673.9422
2636.6604 | 523.442 | 517.4051 | 491.2194 | 673.5917
2637.6604 | 523.5729 | 517.459 | 490.9891 | 674.5653
2638.6604 | 523.5936 | 517.4799 | 490.9035 | 675.0089
2639.6604 | 523.5905 | 517.3824 | 491.1487 | 675.7282
2640.6604 | 523.5187 | 517.4763 | 491.3206 | 676.4723
2641.6604 | 523.56 | 517.5004 | 490.9987 | 677.6546
2642.6604 | 523.5997 | 517.598 | 490.5699 | 679.0878
2643.6604 | 523.6027 | 517.568 | 490.8656 | 679.1999
2644.6604 | 523.8013 | 517.5667 | 491.0015 | 679.7535
2645.6604 | 523.793 | 517.595 | 490.8517 | 680.6555
2646.6604 | 523.8567 | 517.5307 | 490.9985 | 680.555
2647.6604 | 523.8086 | 517.566 | 491.097 | 682.0087
2648.6604 | 523.7995 | 517.4627 | 490.8917 | 682.3092
2649.6604 | 523.8461 | 517.5188 | 490.6302 | 682.132
2650.6604 | 523.7691 | 517.6178 | 491.1784 | 681.7498
2651.6604 | 523.7503 | 517.601 | 491.2454 | 673.2717
2652.6604 | 523.6474 | 517.6346 | 491.2797 | 650.5865
2653.6604 | 523.5421 | 517.6669 | 491.3817 | 625.8499
2654.6604 | 523.5006 | 517.7158 | 491.4694 | 558.3051
2655.6604 | 523.5343 | 517.7143 | 490.9984 | 605.8298
2656.6604 | 523.5573 | 517.7614 | 490.723 | 604.3696
2657.6604 | 523.6267 | 517.7715 | 490.9229 | 599.8748
2658.6604 | 523.638 | 517.8561 | 491.1039 | 596.7041
2659.6604 | 523.6524 | 517.8421 | 491.1752 | 594.8178
2660.6604 | 523.6474 | 517.8944 | 491.4203 | 590.8686
2661.6604 | 523.6307 | 517.9025 | 491.3986 | 586.8206
2662.6604 | 523.5944 | 517.9024 | 491.5388 | 582.143
2663.6604 | 523.527 | 517.9074 | 491.7524 | 574.7746
2664.6604 | 523.5128 | 517.8741 | 491.5221 | 569.1446
2665.6604 | 523.441 | 517.8855 | 491.1497 | 552.745
2666.6604 | 523.3126 | 517.9579 | 491.4085 | 559.5922
2667.6604 | 523.3252 | 517.9973 | 491.3718 | 527.2554
2668.6604 | 523.306 | 517.9547 | 491.6153 | 559.9934
2669.6604 | 523.2334 | 517.9949 | 491.3597 | 560.2119
2670.6604 | 523.1869 | 517.9192 | 491.3723 | 559.1389
2671.6604 | 523.2325 | 517.895 | 491.3797 | 553.405
2672.6604 | 523.1689 | 517.9201 | 491.2855 | 548.193
2673.6604 | 523.1719 | 517.9362 | 491.6176 | 546.1993
2674.6604 | 523.1451 | 517.9704 | 491.6989 | 544.0917
2675.6604 | 523.0562 | 518.0581 | 491.7306 | 545.4033
2676.6604 | 523.1302 | 518.1183 | 491.8477 | 542.055
2677.6604 | 522.9176 | 518.1435 | 492.0049 | 542.3167
2678.6604 | 522.816 | 518.0782 | 492.1531 | 541.6036
2679.6604 | 522.6956 | 518.0156 | 491.996 | 539.7466
2680.6604 | 522.6252 | 518.0831 | 492.0975 | 538.2452
2681.6604 | 522.5948 | 518.0859 | 492.1095 | 538.4488
2682.6604 | 522.586 | 518.0799 | 491.9968 | 533.0619
2683.6604 | 522.5591 | 518.0724 | 492.051 | 531.3679
2684.6604 | 522.7253 | 518.0839 | 491.8976 | 529.4048
2685.6604 | 522.8718 | 518.1783 | 491.798 | 525.4885
2686.6604 | 522.9121 | 518.1919 | 491.8768 | 523.424
2687.6604 | 523.1274 | 518.2215 | 492.0729 | 520.4265
2688.6604 | 523.1404 | 518.2115 | 492.3021 | 518.298
2689.6604 | 523.1492 | 518.2781 | 492.3403 | 519.5713
2690.6604 | 523.2331 | 518.2256 | 491.9302 | 513.5149
2691.6604 | 523.2954 | 518.2483 | 492.1124 | 512.3145
2692.6604 | 523.4651 | 518.3221 | 492.2122 | 511.199
2693.6604 | 523.4759 | 518.2636 | 491.9141 | 503.776
2694.6604 | 523.4753 | 518.2267 | 492.102 | 563.2814
2695.6604 | 523.4363 | 518.3272 | 492.2515 | 454.5593
2696.6604 | 523.4746 | 518.3905 | 492.3698 | 453.6567
2697.6604 | 523.5691 | 518.404 | 492.3275 | 439.894
2698.6604 | 523.5155 | 518.4012 | 492.5304 | 436.3056
2699.6604 | 523.4464 | 518.3885 | 492.6828 | 422.0405
2700.6604 | 523.3957 | 518.4193 | 492.758 | 433.8174
2701.6604 | 523.2885 | 518.4034 | 492.8288 | 437.9292
2702.6604 | 523.3142 | 518.4724 | 492.8265 | 437.8782
2703.6604 | 523.2038 | 518.4714 | 492.7569 | 433.6504
2704.6604 | 523.2006 | 518.4318 | 492.3766 | 432.9939
2705.6604 | 523.1884 | 518.4206 | 492.5605 | 431.3796
2706.6604 | 523.0557 | 518.4914 | 492.6967 | 432.4284
2707.6604 | 523.0378 | 518.5647 | 492.6811 | 432.7643
2708.6604 | 522.9897 | 518.535 | 492.8925 | 432.6749
2709.6604 | 522.9025 | 518.5017 | 492.7702 | 455.8238
2710.6604 | 522.8605 | 518.566 | 492.8824 | 429.0133
2711.6604 | 522.8965 | 518.5725 | 492.8737 | 428.0113
2712.6604 | 522.9263 | 518.5401 | 492.6311 | 428.8393
2713.6604 | 522.8802 | 518.6158 | 492.679 | 428.3089
2714.6604 | 522.8587 | 518.5857 | 492.8085 | 428.4727
2715.6604 | 522.82 | 518.5362 | 492.7321 | 427.8054
2716.6604 | 522.7785 | 518.6423 | 492.8449 | 427.3165
2717.6604 | 522.6881 | 518.6381 | 492.7749 | 425.7414
2718.6604 | 522.6733 | 518.5856 | 492.7444 | 425.3024
2719.6604 | 522.7829 | 518.6225 | 492.7357 | 425.7387
2720.6604 | 522.8503 | 518.661 | 492.9087 | 425.5521
2721.6604 | 522.8227 | 518.6944 | 493.0189 | 422.0016
2722.6604 | 522.9089 | 518.6727 | 493.0458 | 466.0434
2723.6604 | 523.0104 | 518.6051 | 492.7246 | 425.6701
2724.6604 | 523.1292 | 518.6457 | 492.6218 | 422.7935
2725.6604 | 523.1547 | 518.6059 | 492.716 | 422.894
2726.6604 | 523.0659 | 518.5631 | 492.6613 | 421.8428
2727.6604 | 523.0058 | 518.5648 | 492.76 | 422.4172
2728.6604 | 523.018 | 518.6475 | 492.6907 | 421.518
2729.6604 | 523.0629 | 518.6342 | 492.4625 | 418.7738
2730.6604 | 523.0866 | 518.7444 | 492.5845 | 417.471
2731.6604 | 523.2269 | 518.7422 | 492.485 | 417.1902
2732.6604 | 523.2915 | 518.7502 | 492.0873 | 417.3923
2733.6604 | 523.2872 | 518.7062 | 492.0119 | 416.3792
2734.6604 | 523.268 | 518.7795 | 492.4041 | 415.5481
2735.6604 | 523.1973 | 518.7373 | 492.3408 | 414.7479
2736.6604 | 523.1585 | 518.7507 | 492.6799 | 415.4542
2737.6604 | 523.2158 | 518.7884 | 492.8648 | 414.2304
2738.6604 | 523.213 | 518.8106 | 493.1033 | 414.2912
2739.6604 | 523.2197 | 518.8236 | 493.0109 | 414.8451
2740.6604 | 523.2466 | 518.7884 | 493.0974 | 413.8352
2741.6604 | 523.3424 | 518.698 | 492.9026 | 475.5138
2742.6604 | 523.4806 | 518.6939 | 492.8761 | 435.2404
2743.6604 | 523.6646 | 518.7728 | 493.2507 | 449.0197
2744.6604 | 523.6848 | 518.8874 | 493.4504 | 425.0112
2745.6604 | 523.7361 | 518.8621 | 493.4714 | 422.0897
2746.6604 | 523.7896 | 518.8273 | 493.4987 | 419.8203
2747.6604 | 523.8704 | 518.8764 | 493.5906 | 423.51
2748.6604 | 523.8748 | 518.9391 | 493.4712 | 417.9876
2749.6604 | 523.8453 | 518.8975 | 493.4892 | 414.292
2750.6604 | 523.8575 | 518.893 | 493.5794 | 414.1353
2751.6604 | 523.8018 | 518.8886 | 493.6991 | 411.9354
2752.6604 | 523.91 | 518.9365 | 493.5745 | 411.4684
2753.6604 | 523.8635 | 518.9188 | 493.6162 | 434.3821
2754.6604 | 523.7634 | 518.9582 | 493.3796 | 466.5946
2755.6604 | 523.577 | 519.0303 | 493.2931 | 491.7049
2756.6604 | 523.5463 | 519.0254 | 493.1881 | 476.898
2757.6604 | 523.3984 | 519.0926 | 493.3695 | 512.3478
2758.6604 | 523.2364 | 519.0951 | 493.37 | 501.9835
2759.6604 | 523.2791 | 519.1073 | 493.4082 | 522.4256
2760.6604 | 523.4318 | 519.1246 | 493.6351 | 514.4198
2761.6604 | 523.4926 | 519.1605 | 493.6457 | 584.4769
2762.6604 | 523.4183 | 519.0835 | 493.9326 | 746.9794
2763.6604 | 523.391 | 519.1559 | 493.9305 | 748.3952
2764.6604 | 523.3513 | 519.1103 | 493.8853 | 756.157
2765.6604 | 523.4246 | 519.174 | 493.7851 | 748.8148
2766.6604 | 523.5409 | 519.1747 | 493.7911 | 735.7968
2767.6604 | 523.5019 | 519.1883 | 493.7553 | 735.3237
2768.6604 | 523.5533 | 519.1524 | 493.6759 | 737.8226
2769.6604 | 523.4826 | 519.2114 | 493.5741 | 740.3404
2770.6604 | 523.5407 | 519.1219 | 493.582 | 741.4634
2771.6604 | 523.6651 | 519.0902 | 493.7514 | 743.635
2772.6604 | 523.7357 | 519.2081 | 493.9333 | 741.4911
2773.6604 | 523.7711 | 519.0841 | 493.8815 | 742.6833
2774.6604 | 523.9416 | 519.104 | 493.6125 | 742.514
2775.6604 | 524.0903 | 519.175 | 493.4956 | 745.1981
2776.6604 | 524.2195 | 519.2554 | 493.4259 | 744.7172
2777.6604 | 524.1829 | 519.2464 | 493.2536 | 736.6155
2778.6604 | 524.0897 | 519.2897 | 493.2612 | 517.5136
2779.6604 | 523.9853 | 519.2415 | 493.7367 | 742.7811
2780.6604 | 523.9436 | 519.3595 | 494.0459 | 747.0506
2781.6604 | 523.8669 | 519.3384 | 494.0004 | 747.319
2782.6604 | 523.8668 | 519.3219 | 493.8568 | 747.7667
2783.6604 | 523.7705 | 519.3706 | 493.5056 | 749.0015
2784.6604 | 523.6712 | 519.379 | 493.6657 | 752.0722
2785.6604 | 523.6311 | 519.3812 | 493.8423 | 749.3375
2786.6604 | 523.5421 | 519.4252 | 493.857 | 751.9081
2787.6604 | 523.4035 | 519.3837 | 493.919 | 755.0801
2788.6604 | 523.1298 | 519.4279 | 494.2383 | 753.9147
2789.6604 | 523.1407 | 519.4207 | 494.3796 | 753.5381
2790.6604 | 523.0748 | 519.455 | 494.4291 | 755.6262
2791.6604 | 523.0673 | 519.527 | 494.466 | 759.5343
2792.6604 | 523.1018 | 519.5672 | 494.4759 | 400.05
2793.6604 | 523.059 | 519.5843 | 494.3337 | 604.2388
2794.6604 | 522.9949 | 519.6016 | 494.5644 | 401.852
2795.6604 | 523.0415 | 519.6457 | 494.5217 | 398.6675
2796.6604 | 523.1098 | 519.6074 | 494.639 | 395.9385
2797.6604 | 523.2161 | 519.624 | 494.7332 | 394.499
2798.6604 | 523.3171 | 519.6383 | 494.7757 | 393.3025
2799.6604 | 523.4079 | 519.6379 | 494.7951 | 391.0986
2800.6604 | 523.4813 | 519.6296 | 494.821 | 390.4291
2801.6604 | 523.5096 | 519.5667 | 494.9238 | 389.5474
2802.6604 | 523.506 | 519.6575 | 495.0266 | 388.8339
2803.6604 | 523.5405 | 519.661 | 495.0192 | 388.4481
2804.6604 | 523.6167 | 519.6524 | 494.7639 | 387.7477
2805.6604 | 523.6174 | 519.6755 | 494.5718 | 386.0106
2806.6604 | 523.6038 | 519.676 | 494.8338 | 384.9873
2807.6604 | 523.6628 | 519.7377 | 494.9611 | 384.0339
2808.6604 | 523.6368 | 519.7935 | 494.9221 | 383.1173
2809.6604 | 523.5675 | 519.7663 | 495.0239 | 382.8251
2810.6604 | 523.577 | 519.7559 | 495.0388 | 383.2687
2811.6604 | 523.581 | 519.7939 | 495.1598 | 382.0316
2812.6604 | 523.659 | 519.8459 | 494.9715 | 381.5146
2813.6604 | 523.6556 | 519.867 | 494.9172 | 382.3623
2814.6604 | 523.5845 | 519.7554 | 494.8003 | 382.8671
2815.6604 | 523.6082 | 519.7161 | 494.9541 | 382.4585
2816.6604 | 523.5403 | 519.7498 | 494.9788 | 381.781
2817.6604 | 523.5393 | 519.8047 | 495.0052 | 380.3461
2818.6604 | 523.5436 | 519.8132 | 494.8608 | 380.9312
2819.6604 | 523.5157 | 519.887 | 495.0409 | 379.6165
2820.6604 | 523.3871 | 519.936 | 495.065 | 378.2718
2821.6604 | 523.4101 | 519.9336 | 495.2454 | 378.9959
2822.6604 | 523.3864 | 519.9483 | 495.2414 | 378.9963
2823.6604 | 523.3577 | 519.9615 | 495.2755 | 378.6996
2824.6604 | 523.3262 | 519.9321 | 495.1303 | 378.0375
2825.6604 | 523.2788 | 519.8406 | 494.9911 | 378.2066
2826.6604 | 523.3172 | 519.9178 | 495.0609 | 377.183
2827.6604 | 523.3582 | 519.9516 | 494.9431 | 376.8618
2828.6604 | 523.2517 | 519.8615 | 495.096 | 375.058
2829.6604 | 523.3133 | 519.9385 | 495.2354 | 374.9007
2830.6604 | 523.2588 | 520.0227 | 495.4439 | 386.6259
2831.6604 | 523.2619 | 519.9966 | 495.652 | 375.5855
2832.6604 | 523.1307 | 519.9195 | 495.6092 | 374.4585
2833.6604 | 523.1446 | 519.9355 | 495.6588 | 373.8494
2834.6604 | 523.0421 | 519.9831 | 495.5765 | 372.1596
2835.6604 | 522.9375 | 520.0229 | 495.6614 | 372.4231
2836.6604 | 522.8041 | 520.0386 | 495.5605 | 393.0456
2837.6604 | 522.7272 | 520.0157 | 495.6129 | 550.86
2838.6604 | 522.6852 | 520.0277 | 495.5711 | 641.1677
2839.6604 | 522.6845 | 519.9707 | 495.2387 | 567.8816
2840.6604 | 522.6113 | 520.0099 | 495.3942 | 681.9515
2841.6604 | 522.5272 | 519.9956 | 495.4717 | 762.0902
2842.6604 | 522.5749 | 520.1089 | 495.0181 | 771.0461
2843.6604 | 522.6662 | 519.9715 | 494.9582 | 778.7061
2844.6604 | 522.7228 | 519.952 | 494.9479 | 782.6801
2845.6604 | 522.7819 | 519.9966 | 494.7481 | 786.7486
2846.6604 | 522.8855 | 520.0548 | 494.9526 | 788.4325
2847.6604 | 522.9558 | 520.064 | 494.6773 | 791.3292
2848.6604 | 522.9802 | 520.0932 | 494.702 | 794.4848
2849.6604 | 523.0442 | 520.1367 | 494.9203 | 797.0269
2850.6604 | 523.0561 | 520.111 | 494.9915 | 798.3059
2851.6604 | 523.0771 | 520.129 | 495.1665 | 799.8538
2852.6604 | 523.1263 | 520.1491 | 494.8494 | 801.9871
2853.6604 | 523.0641 | 520.1932 | 494.7303 | 802.3403
2854.6604 | 523.1375 | 520.2309 | 494.5624 | 802.1289
2855.6604 | 523.155 | 520.2107 | 494.6518 | 803.9265
2856.6604 | 523.237 | 520.1653 | 494.7118 | 803.8855
2857.6604 | 523.2898 | 520.198 | 495.1546 | 804.8324
2858.6604 | 523.2909 | 520.1654 | 494.9169 | 805.0605
2859.6604 | 523.2791 | 520.1182 | 494.7627 | 804.4858
2860.6604 | 523.3277 | 520.2305 | 494.9924 | 805.6049
2861.6604 | 523.3867 | 520.2667 | 495.0636 | 806.5694
2862.6604 | 523.3046 | 520.1501 | 495.038 | 807.1959
2863.6604 | 523.1911 | 520.2331 | 494.9136 | 808.0776
2864.6604 | 523.1935 | 520.195 | 494.8299 | 809.1543
2865.6604 | 523.1875 | 520.258 | 495.1241 | 809.5081
2866.6604 | 523.1601 | 520.2371 | 495.2474 | 809.9467
2867.6604 | 523.2299 | 520.2691 | 495.302 | 810.2084
2868.6604 | 523.2563 | 520.263 | 495.3134 | 810.9048
2869.6604 | 523.2639 | 520.3429 | 495.3696 | 811.0638
2870.6604 | 523.2883 | 520.4138 | 495.3706 | 810.3534
2871.6604 | 523.2514 | 520.3674 | 495.6908 | 806.8386
2872.6604 | 523.0314 | 520.2723 | 495.2512 | 805.6989
2873.6604 | 522.9404 | 520.2191 | 495.19 | 824.1943
2874.6604 | 522.8916 | 520.2929 | 495.2439 | 838.6721
2875.6604 | 522.7791 | 520.2862 | 495.3828 | 835.2468
2876.6604 | 522.7444 | 520.2658 | 495.4352 | 834.6402
2877.6604 | 522.6784 | 520.2348 | 495.1475 | 810.6801
2878.6604 | 522.6323 | 520.2672 | 494.9525 | 811.0996
2879.6604 | 522.5596 | 520.224 | 494.9887 | 812.6661
2880.6604 | 522.6095 | 520.3166 | 494.8414 | 813.5976
2881.6604 | 522.6172 | 520.3648 | 495.1133 | 812.3057
2882.6604 | 522.6634 | 520.4648 | 495.1992 | 812.5573
2883.6604 | 522.7145 | 520.4205 | 495.3288 | 814.8487
2884.6604 | 522.7416 | 520.4082 | 495.4618 | 813.8401
2885.6604 | 522.7987 | 520.359 | 495.2065 | 813.6112
2886.6604 | 522.7813 | 520.3789 | 495.2161 | 816.0354
2887.6604 | 522.7998 | 520.3992 | 494.8356 | 814.9345
2888.6604 | 522.8959 | 520.4228 | 494.754 | 816.4402
2889.6604 | 522.9663 | 520.4107 | 495.2602 | 816.7108
2890.6604 | 522.9923 | 520.5195 | 495.6055 | 817.7438
2891.6604 | 522.9704 | 520.5002 | 495.7132 | 819.1738
2892.6604 | 522.8617 | 520.5518 | 495.2784 | 818.5904
2893.6604 | 522.8806 | 520.5775 | 495.0346 | 819.5863
2894.6604 | 523.0098 | 520.4576 | 494.892 | 843.9239
2895.6604 | 523.1322 | 520.4778 | 494.8755 | 528.9891
2896.6604 | 523.1765 | 520.3982 | 494.9732 | 527.3709
2897.6604 | 523.1805 | 520.4382 | 494.8522 | 527.1573
2898.6604 | 523.2265 | 520.5134 | 494.6768 | 527.8414
2899.6604 | 523.3137 | 520.5884 | 494.5729 | 527.7384
2900.6604 | 523.3437 | 520.6665 | 494.6845 | 527.5752
2901.6604 | 523.3314 | 520.6274 | 494.9311 | 527.5319
2902.6604 | 523.2709 | 520.6054 | 495.1502 | 526.3093
2903.6604 | 523.1702 | 520.5955 | 495.2079 | 525.9648
2904.6604 | 523.0144 | 520.5771 | 494.9471 | 526.6084
2905.6604 | 522.9087 | 520.6077 | 495.2387 | 527.7312
2906.6604 | 522.8292 | 520.6411 | 495.4009 | 527.2126
2907.6604 | 522.9547 | 520.6734 | 495.2659 | 526.187
2908.6604 | 523.0604 | 520.5884 | 495.4865 | 525.9786
2909.6604 | 523.008 | 520.569 | 495.7205 | 527.8222
2910.6604 | 522.9485 | 520.3679 | 495.6836 | 526.6232
2911.6604 | 523.0154 | 520.4219 | 495.8568 | 526.6494
2912.6604 | 522.9748 | 520.5024 | 495.7224 | 526.6959
2913.6604 | 523.0017 | 520.4863 | 495.6027 | 526.8726
2914.6604 | 522.9763 | 520.6448 | 495.4036 | 526.5021
2915.6604 | 523.0654 | 520.5615 | 495.4658 | 526.3657
2916.6604 | 523.1783 | 520.5833 | 495.3785 | 526.6819
2917.6604 | 523.1695 | 520.6871 | 495.3635 | 527.6391
2918.6604 | 523.1437 | 520.6812 | 495.3261 | 525.9932
2919.6604 | 523.088 | 520.6571 | 495.2064 | 526.0746
2920.6604 | 523.0698 | 520.6848 | 495.1738 | 526.504
2921.6604 | 523.0758 | 520.7399 | 495.4458 | 526.3468
2922.6604 | 523.0479 | 520.7773 | 495.3383 | 529.3402
2923.6604 | 523.1453 | 520.7787 | 494.8674 | 529.4426
2924.6604 | 523.174 | 520.7866 | 495.1656 | 528.6474
2925.6604 | 523.2279 | 520.816 | 495.6096 | 528.4775
2926.6604 | 523.1983 | 520.7584 | 495.0524 | 527.9076
2927.6604 | 523.4412 | 520.7145 | 494.812 | 527.7587
2928.6604 | 523.5019 | 520.6709 | 494.7957 | 527.8443
2929.6604 | 523.5492 | 520.7913 | 494.777 | 527.8934
2930.6604 | 523.5422 | 520.7853 | 495.0201 | 528.634
2931.6604 | 523.6469 | 520.8416 | 495.3885 | 528.7166
2932.6604 | 523.791 | 520.788 | 495.5256 | 528.8403
2933.6604 | 523.8098 | 520.794 | 495.6093 | 529.8573
2934.6604 | 523.9598 | 520.7866 | 495.5654 | 529.8306
2935.6604 | 523.9772 | 520.8845 | 495.2599 | 529.7534
2936.6604 | 523.9297 | 520.8747 | 495.0695 | 529.0569
2937.6604 | 523.876 | 520.8738 | 495.3363 | 529.5305
2938.6604 | 524.0017 | 520.8329 | 495.517 | 529.3696
2939.6604 | 523.9065 | 520.7726 | 495.5823 | 528.0895
2940.6604 | 523.7934 | 520.8825 | 495.5135 | 528.1257
2941.6604 | 523.6432 | 520.8655 | 495.6206 | 529.6274
2942.6604 | 523.5952 | 520.9499 | 495.5947 | 529.6056
2943.6604 | 523.6088 | 521.0549 | 495.6289 | 529.3552
2944.6604 | 523.6045 | 521.0457 | 495.5844 | 529.2224
2945.6604 | 523.5717 | 521.0318 | 495.5159 | 527.6898
2946.6604 | 523.4279 | 521.0441 | 495.798 | 527.6385
2947.6604 | 523.3851 | 521.0421 | 495.9458 | 529.1048
2948.6604 | 523.3107 | 521.0479 | 495.9111 | 527.9581
2949.6604 | 523.2426 | 520.8734 | 495.8641 | 527.3647
2950.6604 | 523.3654 | 521.0043 | 495.6312 | 528.5289
2951.6604 | 523.3836 | 520.9288 | 495.7408 | 528.851
2952.6604 | 523.3965 | 520.9891 | 495.9694 | 528.8304
2953.6604 | 523.3132 | 521.0192 | 495.8159 | 528.4952
2954.6604 | 523.2825 | 520.9824 | 496.0506 | 527.496
2955.6604 | 523.3466 | 521.0514 | 495.9459 | 528.5283
2956.6604 | 523.3496 | 521.0638 | 495.9242 | 528.2323
2957.6604 | 523.3344 | 521.145 | 496.0678 | 528.3464
2958.6604 | 523.3212 | 521.2404 | 496.1559 | 528.369
2959.6604 | 523.3611 | 521.1189 | 496.1152 | 528.3784
2960.6604 | 523.4134 | 521.1513 | 496.3053 | 528.3902
2961.6604 | 523.3786 | 521.1867 | 496.076 | 528.3345
2962.6604 | 523.3325 | 521.1108 | 496.2429 | 527.3858
2963.6604 | 523.2898 | 521.2019 | 495.9846 | 527.4738
2964.6604 | 523.2729 | 521.1351 | 496.0557 | 528.3019
2965.6604 | 523.3134 | 521.1514 | 496.3514 | 527.1216
2966.6604 | 523.3595 | 521.1439 | 496.1339 | 526.8991
2967.6604 | 523.3402 | 521.1898 | 496.3811 | 528.3487
2968.6604 | 523.4767 | 521.2059 | 496.1857 | 529.076
2969.6604 | 523.4934 | 521.2906 | 496.1247 | 529.1817
2970.6604 | 523.5307 | 521.2826 | 496.2525 | 528.0303
2971.6604 | 523.549 | 521.2972 | 496.2816 | 529.1128
2972.6604 | 523.5083 | 521.2399 | 496.1387 | 528.8838
2973.6604 | 523.5408 | 521.256 | 496.1774 | 527.913
2974.6604 | 523.5678 | 521.3365 | 496.1887 | 528.9309
2975.6604 | 523.6245 | 521.2946 | 496.3102 | 527.8612
2976.6604 | 523.7231 | 521.3608 | 496.3765 | 528.2959
2977.6604 | 523.6534 | 521.3551 | 496.303 | 528.162
2978.6604 | 523.7118 | 521.3218 | 496.1236 | 528.8738
2979.6604 | 523.6966 | 521.3342 | 496.0993 | 528.862
2980.6604 | 523.6764 | 521.3804 | 496.298 | 528.8276
2981.6604 | 523.7846 | 521.4222 | 496.0793 | 527.6696
2982.6604 | 523.7822 | 521.3355 | 495.9379 | 527.7128
2983.6604 | 523.7583 | 521.32 | 496.2268 | 528.6851
2984.6604 | 523.7446 | 521.2935 | 496.2099 | 528.256
2985.6604 | 523.7514 | 521.2733 | 496.2027 | 528.2978
2986.6604 | 523.5922 | 521.2079 | 496.3446 | 528.4635
2987.6604 | 523.4977 | 521.2894 | 496.0414 | 527.8472
2988.6604 | 523.4228 | 521.3719 | 495.9242 | 527.8578
2989.6604 | 523.3625 | 521.444 | 496.3956 | 527.6576
2990.6604 | 523.255 | 521.4126 | 496.3513 | 527.9993
2991.6604 | 523.0804 | 521.3834 | 495.9735 | 528.2189
2992.6604 | 522.9883 | 521.408 | 495.7816 | 528.7444
2993.6604 | 522.9807 | 521.3757 | 495.8677 | 528.6774
2994.6604 | 523.0414 | 521.3698 | 496.0671 | 527.404
2995.6604 | 523.0343 | 521.4135 | 496.3861 | 527.1953
2996.6604 | 523.0049 | 521.4481 | 496.3174 | 528.1504
2997.6604 | 522.9069 | 521.392 | 496.1533 | 528.3131
2998.6604 | 522.8677 | 521.4573 | 496.0244 | 528.6801
2999.6604 | 522.9032 | 521.4443 | 495.8535 | 528.6304
3000.6604 | 522.898 | 521.4714 | 496.1949 | 528.5578
3001.6604 | 522.8951 | 521.4901 | 495.7647 | 527.1243
3002.6604 | 522.9557 | 521.574 | 496.1461 | 527.3083
3003.6604 | 522.9917 | 521.5974 | 496.3298 | 528.5437
3004.6604 | 523.0511 | 521.52 | 496.4758 | 528.5774
3005.6604 | 523.0262 | 521.4355 | 496.3329 | 528.2367
3006.6604 | 523.0178 | 521.4275 | 496.2267 | 528.0858
3007.6604 | 522.9644 | 521.5292 | 496.3885 | 528.4551
3008.6604 | 522.995 | 521.5791 | 496.377 | 528.3646
3009.6604 | 523.0136 | 521.6 | 496.5765 | 527.0725
3010.6604 | 523.0366 | 521.6263 | 496.7917 | 527.1552
3011.6604 | 522.98 | 521.6449 | 496.5681 | 528.2378
3012.6604 | 522.8755 | 521.5876 | 496.6578 | 527.9223
3013.6604 | 522.8521 | 521.5913 | 496.6908 | 527.7372
3014.6604 | 522.9501 | 521.6001 | 496.8114 | 526.9348
3015.6604 | 522.9122 | 521.586 | 496.9487 | 526.2955
3016.6604 | 522.9317 | 521.596 | 496.8649 | 528.3056
3017.6604 | 522.8661 | 521.474 | 496.7073 | 527.0901
3018.6604 | 522.8968 | 521.4616 | 496.9266 | 527.1596
3019.6604 | 522.9418 | 521.5246 | 496.816 | 527.252
3020.6604 | 523.0601 | 521.5764 | 496.9607 | 528.0214
3021.6604 | 522.994 | 521.6087 | 497.0381 | 527.7172
3022.6604 | 522.906 | 521.6631 | 497.0285 | 528.1581
3023.6604 | 522.8337 | 521.5657 | 497.0541 | 528.1552
3024.676 | 522.7674 | 521.3953 | 497.0582 | 527.4851
3025.6604 | 522.6392 | 521.4811 | 497.2467 | 526.8909
3026.6604 | 522.6673 | 521.4929 | 497.2033 | 527.882
3027.6604 | 522.8162 | 521.4699 | 496.7544 | 527.7717
3028.6604 | 522.8234 | 521.4892 | 496.6481 | 527.3079
3029.6604 | 522.7565 | 521.5516 | 496.6017 | 527.8661
3030.6604 | 522.7521 | 521.3712 | 496.1474 | 527.0957
3031.6604 | 522.8218 | 521.3153 | 496.2878 | 527.1379
3032.6604 | 522.8561 | 521.3811 | 496.4771 | 527.5916
3033.6604 | 523.0102 | 521.3695 | 496.4239 | 527.522
3034.6604 | 523.0071 | 521.3712 | 496.7455 | 527.3674
3035.6604 | 522.9678 | 521.4457 | 496.4466 | 525.2854
3036.6604 | 522.9708 | 521.5537 | 496.586 | 527.4224
3037.6604 | 522.9509 | 521.5106 | 496.8753 | 527.274
3038.6604 | 522.9094 | 521.5116 | 496.6063 | 525.8133
3039.6604 | 522.8719 | 521.5229 | 496.6993 | 525.3092
3040.6604 | 522.8273 | 521.551 | 496.9115 | 527.5776
3041.6604 | 522.7567 | 521.6215 | 496.8154 | 527.503
3042.6604 | 522.734 | 521.6886 | 497.1265 | 527.4688
3043.6604 | 522.7204 | 521.629 | 497.1808 | 526.1817
3044.6604 | 522.5859 | 521.5592 | 497.2806 | 525.8539
3045.6604 | 522.5943 | 521.5481 | 497.3907 | 526.2305
3046.6604 | 522.6346 | 521.6189 | 497.4052 | 525.8986
3047.6604 | 522.5821 | 521.627 | 497.3349 | 527.2939
3048.6604 | 522.6345 | 521.6286 | 497.2421 | 526.9537
3049.6604 | 522.728 | 521.6743 | 496.963 | 526.5303
3050.6604 | 522.7921 | 521.6907 | 497.1192 | 526.8557
3051.6604 | 522.7501 | 521.6792 | 497.3826 | 527.194
3052.6604 | 522.7529 | 521.7088 | 497.3045 | 527.132
3053.6604 | 522.7603 | 521.7064 | 497.4403 | 525.3144
3054.6604 | 522.5622 | 521.7544 | 497.6343 | 525.0035
3055.6604 | 522.4319 | 521.6974 | 497.4399 | 525.7876
3056.6604 | 522.4849 | 521.6802 | 497.0628 | 526.096
3057.6604 | 522.4622 | 521.6312 | 497.0054 | 526.2965
3058.6604 | 522.4233 | 521.6825 | 497.3595 | 526.3644
3059.6604 | 522.3955 | 521.7377 | 497.4707 | 526.0082
3060.6604 | 522.2969 | 521.7048 | 497.4158 | 526.4909