## Test Conditions
DESIREE-FIRE Test Number 42 - Circuit Simulator Data Only
Test Date: | 2009-09-25
DCSim DAQ Start Time | 11:42
DCSim Time for Synchronization | 11:57
Heat Source Synchronization | 10:03 | minutes:seconds
Heat Source DAQ Start Time | 11:47
Heat Source Start Time | 11:59
DCSim Offset | 0:17 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 1020 | seconds
Heat Source Offset | 0:12 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 723 | seconds
Heat Source Stop Time | 13:44
Test Duration | 1:46 | minutes:seconds
| 6330 | seconds
CT500 Turns | 2 |  | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 Turns | 5
Pre-Test Baseline: | Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SWGR Close | XLPE/CSPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
SWGR Trip | XLPE/CSPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SWGR_CT500 | SWGR-a_CT35_1_PC | SWGR-a_CT35_2_N1 | SWGR-b_CT35_1_PT | SWGR-b_CT35_2_G | SWGR-b_CT35_3_R | SWGR-b_CT35_4_N2 | SWGR-a_VT7_1_C1 | SWGR-a_VTU_1_PC | SWGR-a_VTU_2_N1 | SWGR-b_VT7_1_G | SWGR-b_VT7_2_R | SWGR-b_VT7_3_T | SWGR-b_VT7_4_SP | SWGR-b_VT7_5_SP | SWGR-b_VTU_1_PT | SWGR-b_VTU_2_N2 | {SWGR-C} V(N1) - V(Batt -) | {SWGR-C} V(PC) - V(Batt +) | {SWGR-C} V(C1) - V(Batt +) | {SWGR-T} V(G) - V(Batt -) | {SWGR-T} V(R) - V(Batt +) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-T} V(PT) - V(Batt +) | {SWGR-C} V(C1) - V(N1) | {SWGR-T} V(SP1) - V(Batt -) | {SWGR-T} V(SP2) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PC) - V(Batt -) | {SWGR-T} V(C1) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-C} V(PC) - V(Batt -) | {SWGR-C} V(C1) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-C} V(N1) - V(Batt +) | {SWGR-T} V(N2) - V(Batt +)
-0.28125 | 124.2828 | -61.4044 | 62.5168 | -0.11574 | 0.0034201 | 0.0046548 | -0.0051974 | 0.065589 | -0.0018285 | 0.068795 | -61.496 | 62.3566 | -61.5005 | -61.5463 | 62.3611 | 0.1236 | -0.045776 | 0.16937 | 62.3978 | -61.5738 | -0.09613 | -0.16022 | -0.091553 | -0.14191 | -0.15564 | -0.16937 | -0.11902 | 0.004577 | 61.3586 | 61.5738 | 123.7656 | 123.761 | -0.091553 | 123.8022 | 61.528 | -0.16937 | 123.761 | -0.091553 | 61.528 | 123.7656 | 123.8022 | -124.0173 | -124.0906
0.71875 | 124.2645 | -61.3953 | 62.5488 | 0.059738 | 0.0051291 | 0.011064 | -0.0034886 | 0.066016 | -0.00011953 | 0.070077 | -61.5189 | 62.3611 | -61.5143 | -61.6058 | 62.3016 | 0.054932 | -0.073242 | 0.068665 | 62.3932 | -61.6104 | -0.11902 | -0.18768 | -0.1236 | -0.21057 | -0.24719 | -0.21515 | -0.15564 | -0.004578 | 61.322 | 61.4639 | 123.6969 | 123.7564 | -0.1236 | 123.7885 | 61.4502 | -0.21515 | 123.7564 | -0.1236 | 61.4502 | 123.6969 | 123.7885 | -124.0631 | -124.1592
1.7188 | 124.2691 | -61.3998 | 62.5351 | 0.021591 | 0.0068381 | 0.010636 | -0.0022068 | 0.065589 | -0.0014013 | 0.069863 | -61.5189 | 62.3383 | -61.5005 | -61.5829 | 62.3154 | 0.054932 | -0.068665 | 0.086975 | 62.4344 | -61.5417 | -0.10071 | -0.19684 | -0.11902 | -0.18311 | -0.21973 | -0.14191 | -0.10071 | -0.018311 | 61.3312 | 61.4868 | 123.7152 | 123.7381 | -0.11902 | 123.8342 | 61.4548 | -0.14191 | 123.7381 | -0.11902 | 61.4548 | 123.7152 | 123.8342 | -124.0356 | -124.0768
2.7188 | 124.1455 | -61.4273 | 62.5809 | -0.24544 | 0.0081197 | 0.010209 | 0.0022794 | 0.065375 | -0.0020421 | 0.067727 | -61.5234 | 62.4481 | -61.5326 | -61.6241 | 62.2742 | 0.054932 | 0.15564 | 0.082397 | 62.4619 | -61.6013 | -0.10529 | -0.13275 | -0.09613 | -0.19684 | -0.3067 | -0.17395 | -0.11902 | 0.009156 | 61.5829 | 61.5097 | 123.7015 | 123.8754 | -0.09613 | 123.8892 | 61.4822 | -0.17395 | 123.8754 | -0.09613 | 61.4822 | 123.7015 | 123.8892 | -124.1135 | -124.1821
3.7188 | 124.2599 | -61.409 | 62.5397 | 0.021591 | 0.0055563 | 0.0099954 | -0.0045566 | 0.067725 | -0.00097413 | 0.069436 | -61.528 | 62.3611 | -61.5189 | -61.5738 | 62.3337 | 0.07782 | -0.059509 | 0.09613 | 62.3978 | -61.5692 | -0.10986 | -0.17853 | -0.11902 | -0.16479 | -0.20599 | -0.16022 | -0.14191 | -0.009155 | 61.3495 | 61.5051 | 123.7427 | 123.7701 | -0.11902 | 123.8068 | 61.4868 | -0.16022 | 123.7701 | -0.11902 | 61.4868 | 123.7427 | 123.8068 | -124.0585 | -124.1089
4.7188 | 124.2828 | -61.4044 | 62.5488 | -0.047073 | 0.0070517 | 0.0080728 | -0.0030612 | 0.063239 | -0.00076053 | 0.071786 | -61.5097 | 62.3611 | -61.4868 | -61.5601 | 62.3611 | 0.10986 | -0.059509 | 0.13275 | 62.3886 | -61.5646 | -0.082397 | -0.18768 | -0.10529 | -0.15564 | -0.18768 | -0.16022 | -0.16022 | -0.022889 | 61.3449 | 61.5372 | 123.7656 | 123.7656 | -0.10529 | 123.793 | 61.5143 | -0.16022 | 123.7656 | -0.10529 | 61.5143 | 123.7656 | 123.793 | -124.0356 | -124.1135
5.7188 | 124.1913 | -61.4319 | 62.59 | 0.029221 | 0.0059835 | 0.0065774 | -0.001566 | 0.064093 | 0.00052127 | 0.070504 | -61.5005 | 62.4069 | -61.4914 | -61.5875 | 62.3108 | 0.091553 | 0.10986 | 0.11444 | 62.4481 | -61.5829 | -0.059509 | -0.18311 | -0.068664 | -0.15564 | -0.27924 | -0.15106 | -0.14191 | -0.009155 | 61.5417 | 61.5463 | 123.7427 | 123.8388 | -0.068664 | 123.88 | 61.5234 | -0.15106 | 123.8388 | -0.068664 | 61.5234 | 123.7427 | 123.88 | -124.0814 | -124.173
6.7188 | 124.2645 | -61.3953 | 62.5031 | 0.14366 | 0.0057699 | 0.0095682 | 0.0020656 | 0.066443 | -0.0014013 | 0.070077 | -61.4639 | 62.3566 | -61.5143 | -61.5417 | 62.352 | 0.073242 | -0.16479 | 0.082397 | 62.384 | -61.6241 | -0.11902 | -0.14648 | -0.068664 | -0.14648 | -0.15106 | -0.22888 | -0.11902 | 0.050354 | 61.2305 | 61.4777 | 123.7473 | 123.7518 | -0.068664 | 123.7793 | 61.4685 | -0.22888 | 123.7518 | -0.068664 | 61.4685 | 123.7473 | 123.7793 | -124.0173 | -124.1272
7.7188 | 124.3011 | -61.3815 | 62.5122 | 0.18181 | 0.0044881 | 0.0076456 | 0.0029202 | 0.067084 | -0.00076053 | 0.069863 | -61.4639 | 62.3611 | -61.496 | -61.5372 | 62.3566 | 0.068665 | -0.18768 | 0.082397 | 62.3611 | -61.5967 | -0.11444 | -0.15106 | -0.082397 | -0.15564 | -0.15564 | -0.21515 | -0.15106 | 0.032044 | 61.1938 | 61.4639 | 123.7381 | 123.7427 | -0.082397 | 123.7427 | 61.4502 | -0.21515 | 123.7427 | -0.082397 | 61.4502 | 123.7381 | 123.7427 | -124.0082 | -124.1089
8.7344 | 124.1684 | -61.4456 | 62.5717 | -0.19203 | 0.0085471 | 0.010209 | 0.00035684 | 0.065161 | 9.4068e-05 | 0.069436 | -61.5372 | 62.4344 | -61.5005 | -61.6013 | 62.2696 | 0.082397 | 0.13733 | 0.07782 | 62.439 | -61.6104 | -0.054931 | -0.13733 | -0.091552 | -0.15564 | -0.30212 | -0.16479 | -0.13275 | -0.036621 | 61.5829 | 61.5234 | 123.7152 | 123.88 | -0.091552 | 123.8846 | 61.528 | -0.16479 | 123.88 | -0.091552 | 61.528 | 123.7152 | 123.8846 | -124.0723 | -124.1821
9.7188 | 124.2783 | -61.4044 | 62.5122 | 0.22758 | 0.0087607 | 0.011064 | 0.0012112 | 0.067084 | -0.00033333 | 0.068795 | -61.4731 | 62.3749 | -61.5189 | -61.5326 | 62.3337 | 0.059509 | -0.19684 | 0.07782 | 62.3566 | -61.5646 | -0.11444 | -0.13733 | -0.068664 | -0.12817 | -0.17853 | -0.16022 | -0.15564 | 0.045777 | 61.2076 | 61.4822 | 123.7381 | 123.7793 | -0.068664 | 123.761 | 61.4639 | -0.16022 | 123.7793 | -0.068664 | 61.4639 | 123.7381 | 123.761 | -124.0311 | -124.0768
10.7188 | 124.3103 | -61.3953 | 62.4939 | 0.18181 | 0.0057699 | 0.010423 | 0.0016384 | 0.067939 | -0.0028967 | 0.069436 | -61.4548 | 62.352 | -61.5097 | -61.5601 | 62.3383 | 0.07782 | -0.16022 | 0.059509 | 62.3978 | -61.5921 | -0.11444 | -0.14191 | -0.059509 | -0.1648 | -0.15564 | -0.19684 | -0.09613 | 0.054932 | 61.235 | 61.4548 | 123.7335 | 123.7473 | -0.059509 | 123.793 | 61.4731 | -0.19684 | 123.7473 | -0.059509 | 61.4731 | 123.7335 | 123.793 | -124.0036 | -124.086
11.7188 | 124.3103 | -61.3861 | 62.5168 | -0.13863 | 0.0051291 | 0.011064 | -0.0030612 | 0.065161 | -0.00054693 | 0.069009 | -61.4456 | 62.3566 | -61.5189 | -61.5143 | 62.3795 | 0.13275 | -0.073242 | 0.16937 | 62.3795 | -61.5601 | -0.13275 | -0.16022 | -0.05951 | -0.12817 | -0.13733 | -0.17395 | -0.13733 | 0.073242 | 61.3129 | 61.5555 | 123.7656 | 123.7427 | -0.05951 | 123.7656 | 61.5189 | -0.17395 | 123.7427 | -0.05951 | 61.5189 | 123.7656 | 123.7656 | -124.0356 | -124.0768
12.7188 | 124.2828 | -61.3998 | 62.5214 | 0.14366 | 0.0051291 | 0.012345 | -0.00028416 | 0.06687 | -0.0024695 | 0.070504 | -61.4731 | 62.3428 | -61.496 | -61.5372 | 62.3337 | 0.07782 | -0.16479 | 0.07782 | 62.3428 | -61.5692 | -0.096131 | -0.17853 | -0.073242 | -0.13733 | -0.18768 | -0.16937 | -0.17853 | 0.022889 | 61.235 | 61.4777 | 123.7335 | 123.7427 | -0.073242 | 123.7427 | 61.4777 | -0.16937 | 123.7427 | -0.073242 | 61.4777 | 123.7335 | 123.7427 | -124.0173 | -124.0906
13.7188 | 124.3011 | -61.3907 | 62.5122 | 0.18944 | 0.0091879 | 0.013841 | -0.00071136 | 0.065161 | -0.0018285 | 0.069863 | -61.4685 | 62.3383 | -61.4914 | -61.5509 | 62.3383 | 0.073242 | -0.1831 | 0.086975 | 62.3383 | -61.5829 | -0.10071 | -0.17395 | -0.07782 | -0.16022 | -0.17395 | -0.19226 | -0.17395 | 0.022888 | 61.2076 | 61.4777 | 123.7289 | 123.7289 | -0.07782 | 123.7289 | 61.4639 | -0.19226 | 123.7289 | -0.07782 | 61.4639 | 123.7289 | 123.7289 | -124.0036 | -124.0952
14.7188 | 124.2462 | -61.3953 | 62.5214 | 0.17418 | 0.0057699 | 0.011918 | -0.0013522 | 0.065161 | -0.0018285 | 0.070291 | -61.5234 | 62.3749 | -61.5005 | -61.5921 | 62.2971 | 0.050354 | -0.086975 | 0.059509 | 62.3611 | -61.5875 | -0.10529 | -0.14648 | -0.12817 | -0.19684 | -0.2243 | -0.19226 | -0.16022 | -0.022888 | 61.3083 | 61.4548 | 123.6923 | 123.7701 | -0.12817 | 123.7564 | 61.4456 | -0.19226 | 123.7701 | -0.12817 | 61.4456 | 123.6923 | 123.7564 | -124.0219 | -124.1089
15.7188 | 124.2233 | -61.4227 | 62.4985 | 0.24284 | 0.0087607 | 0.014909 | 0.00527 | 0.06687 | 0.0013757 | 0.070504 | -61.5189 | 62.4252 | -61.5234 | -61.5509 | 62.2009 | -0.091553 | -0.064087 | -0.027466 | 62.3886 | -61.6013 | -0.10071 | -0.073242 | -0.096131 | -0.12817 | -0.29755 | -0.17853 | -0.10986 | 0.004577 | 61.3586 | 61.3953 | 123.6237 | 123.848 | -0.096131 | 123.8113 | 61.3312 | -0.17853 | 123.848 | -0.096131 | 61.3312 | 123.6237 | 123.8113 | -124.0219 | -124.0997
16.7188 | 124.2966 | -61.4182 | 62.5122 | 0.2047 | 0.0085471 | 0.012773 | 0.00035684 | 0.068579 | -0.0014013 | 0.070291 | -61.4731 | 62.3978 | -61.5143 | -61.5601 | 62.3245 | 0.054932 | -0.16022 | 0.064087 | 62.3795 | -61.6196 | -0.09613 | -0.11444 | -0.054931 | -0.14191 | -0.18768 | -0.20142 | -0.13275 | 0.041199 | 61.2579 | 61.4822 | 123.7427 | 123.8159 | -0.054931 | 123.7976 | 61.4731 | -0.20142 | 123.8159 | -0.054931 | 61.4731 | 123.7427 | 123.7976 | -124.0265 | -124.1318
17.7344 | 124.3057 | -61.377 | 62.5214 | -0.12337 | 0.0059835 | 0.0099954 | -0.0024204 | 0.067084 | -0.00097413 | 0.069009 | -61.4456 | 62.352 | -61.5143 | -61.5051 | 62.4023 | 0.17853 | -0.091553 | 0.20142 | 62.4023 | -61.5326 | -0.13733 | -0.16937 | -0.068665 | -0.12817 | -0.11902 | -0.15564 | -0.11902 | 0.068664 | 61.2854 | 61.5784 | 123.7793 | 123.7289 | -0.068665 | 123.7793 | 61.5555 | -0.15564 | 123.7289 | -0.068665 | 61.5555 | 123.7793 | 123.7793 | -124.0356 | -124.054
18.7188 | 124.205 | -61.4502 | 62.5351 | 0.18944 | 0.0074789 | 0.010423 | 0.0046292 | 0.067084 | -0.0016149 | 0.067086 | -61.5372 | 62.439 | -61.5234 | -61.6287 | 62.2604 | 0 | -0.091553 | 0.12817 | 62.4161 | -61.6196 | -0.073242 | -0.09613 | -0.086975 | -0.17853 | -0.27466 | -0.16937 | -0.11902 | -0.013733 | 61.3586 | 61.5784 | 123.7106 | 123.8892 | -0.086975 | 123.8663 | 61.4502 | -0.16937 | 123.8892 | -0.086975 | 61.4502 | 123.7106 | 123.8663 | -124.0585 | -124.1547
19.7188 | 124.205 | -61.4365 | 62.5397 | 0.22758 | 0.010683 | 0.014695 | 0.0044156 | 0.068579 | -0.00097413 | 0.07264 | -61.5372 | 62.4344 | -61.5463 | -61.6425 | 62.2467 | -0.036621 | -0.036621 | -0.041199 | 62.3978 | -61.6196 | -0.10986 | -0.10529 | -0.10071 | -0.20599 | -0.29297 | -0.18311 | -0.14191 | 0.009156 | 61.3998 | 61.3953 | 123.6832 | 123.8708 | -0.10071 | 123.8342 | 61.3998 | -0.18311 | 123.8708 | -0.10071 | 61.3998 | 123.6832 | 123.8342 | -124.086 | -124.1592
20.7188 | 124.3057 | -61.3815 | 62.5214 | -0.19966 | 0.0053427 | 0.0095682 | -0.0034886 | 0.066443 | -0.00054693 | 0.070931 | -61.4365 | 62.4023 | -61.5005 | -61.5005 | 62.4069 | 0.17395 | -0.041199 | 0.23346 | 62.3932 | -61.5509 | -0.11902 | -0.11902 | -0.054931 | -0.11902 | -0.11444 | -0.16937 | -0.12817 | 0.064087 | 61.3403 | 61.615 | 123.7885 | 123.7839 | -0.054931 | 123.7747 | 61.5555 | -0.16937 | 123.7839 | -0.054931 | 61.5555 | 123.7885 | 123.7747 | -124.0219 | -124.0723
21.7188 | 124.1592 | -61.4548 | 62.5534 | 0.1284 | 0.0096151 | 0.013841 | 0.0037746 | 0.068152 | -0.00097413 | 0.06965 | -61.5372 | 62.4664 | -61.5097 | -61.647 | 62.2375 | -0.027466 | 0.041199 | -0.022888 | 62.4207 | -61.6425 | -0.054932 | -0.086975 | -0.082397 | -0.19226 | -0.31586 | -0.18768 | -0.13275 | -0.027465 | 61.496 | 61.4319 | 123.6923 | 123.9212 | -0.082397 | 123.8754 | 61.4273 | -0.18768 | 123.9212 | -0.082397 | 61.4273 | 123.6923 | 123.8754 | -124.0631 | -124.1959
22.7188 | 124.173 | -61.4365 | 62.5854 | 0.12077 | 0.0081197 | 0.0132 | 0.0029202 | 0.070716 | -0.0018285 | 0.069222 | -61.5234 | 62.4619 | -61.528 | -61.6287 | 62.2559 | 0 | 0.036621 | -0.013733 | 62.4527 | -61.6196 | -0.091553 | -0.1236 | -0.086975 | -0.19226 | -0.32959 | -0.18311 | -0.13275 | 0.004578 | 61.4731 | 61.4227 | 123.6923 | 123.8983 | -0.086975 | 123.8892 | 61.4365 | -0.18311 | 123.8983 | -0.086975 | 61.4365 | 123.6923 | 123.8892 | -124.1135 | -124.205
23.7188 | 124.2325 | -61.4044 | 62.5305 | 0.013962 | 0.0057699 | 0.011491 | -0.0051974 | 0.070075 | -0.0018285 | 0.067513 | -61.5234 | 62.3932 | -61.5234 | -61.6058 | 62.3337 | 0.068665 | -0.045776 | 0.082397 | 62.4069 | -61.5646 | -0.11902 | -0.13733 | -0.11902 | -0.20142 | -0.19684 | -0.16022 | -0.1236 | 0 | 61.3586 | 61.4868 | 123.7381 | 123.7976 | -0.11902 | 123.8113 | 61.4731 | -0.16022 | 123.7976 | -0.11902 | 61.4731 | 123.7381 | 123.8113 | -124.054 | -124.0952
24.7188 | 124.1913 | -61.4685 | 62.558 | 0.19707 | 0.0096151 | 0.013841 | 0.00099764 | 0.067725 | -0.0014013 | 0.068368 | -61.5463 | 62.4664 | -61.5555 | -61.6699 | 62.2421 | -0.027466 | -0.004578 | -0.059509 | 62.3795 | -61.6196 | -0.086975 | -0.091552 | -0.07782 | -0.20142 | -0.31586 | -0.15106 | -0.17853 | 0.009155 | 61.4639 | 61.409 | 123.7106 | 123.9349 | -0.07782 | 123.848 | 61.441 | -0.15106 | 123.9349 | -0.07782 | 61.441 | 123.7106 | 123.848 | -124.1135 | -124.1776
25.7188 | 124.173 | -61.4456 | 62.5488 | 0.013962 | 0.0081197 | 0.012559 | 0.0029202 | 0.067084 | -0.0024695 | 0.070077 | -61.5234 | 62.4847 | -61.528 | -61.6379 | 62.2284 | -0.022888 | 0.054932 | -0.036621 | 62.4435 | -61.6241 | -0.082397 | -0.064087 | -0.077819 | -0.19226 | -0.32043 | -0.17853 | -0.10529 | 0.004578 | 61.5006 | 61.409 | 123.674 | 123.9304 | -0.077819 | 123.8892 | 61.4227 | -0.17853 | 123.9304 | -0.077819 | 61.4227 | 123.674 | 123.8892 | -124.0768 | -124.173
26.7188 | 124.2599 | -61.3998 | 62.4893 | 0.15129 | 0.0072653 | 0.0089274 | -0.0028476 | 0.067511 | -0.0018285 | 0.06965 | -61.4822 | 62.3474 | -61.528 | -61.5509 | 62.3566 | 0.068665 | -0.15564 | 0.082397 | 62.3611 | -61.5646 | -0.12817 | -0.14191 | -0.082398 | -0.15106 | -0.13275 | -0.16479 | -0.12817 | 0.045776 | 61.2442 | 61.4822 | 123.7564 | 123.7473 | -0.082398 | 123.761 | 61.4685 | -0.16479 | 123.7473 | -0.082398 | 61.4685 | 123.7564 | 123.761 | -124.0173 | -124.054
27.7188 | 124.1409 | -61.4639 | 62.5442 | 0.067368 | 0.0079061 | 0.011064 | 0.0044156 | 0.069434 | -0.0033239 | 0.070291 | -61.5555 | 62.4756 | -61.5326 | -61.6745 | 62.2421 | -0.036621 | 0.050354 | -0.045776 | 62.4252 | -61.6425 | -0.068665 | -0.068664 | -0.091553 | -0.21057 | -0.30212 | -0.17853 | -0.11902 | -0.022888 | 61.5143 | 61.4182 | 123.7061 | 123.9395 | -0.091553 | 123.8892 | 61.4273 | -0.17853 | 123.9395 | -0.091553 | 61.4273 | 123.7061 | 123.8892 | -124.0768 | -124.1867
28.7188 | 124.1409 | -61.4502 | 62.5534 | 0.059738 | 0.0089743 | 0.011064 | 0.00078404 | 0.071784 | -0.0014013 | 0.069863 | -61.5509 | 62.4664 | -61.5234 | -61.6653 | 62.2238 | -0.036621 | 0.032043 | -0.018311 | 62.439 | -61.6333 | -0.073242 | -0.086975 | -0.10071 | -0.21515 | -0.32959 | -0.18311 | -0.11444 | -0.027466 | 61.4822 | 61.4319 | 123.674 | 123.9166 | -0.10071 | 123.8892 | 61.4136 | -0.18311 | 123.9166 | -0.10071 | 61.4136 | 123.674 | 123.8892 | -124.0768 | -124.1867
29.7188 | 124.2325 | -61.4044 | 62.4985 | 0.15129 | 0.0061971 | 0.011491 | -0.0028476 | 0.068366 | -0.0022559 | 0.06965 | -61.4868 | 62.352 | -61.5417 | -61.5738 | 62.3337 | 0.086975 | -0.15564 | 0.082397 | 62.3749 | -61.5417 | -0.13733 | -0.14648 | -0.082397 | -0.16937 | -0.1648 | -0.13733 | -0.1236 | 0.054932 | 61.2488 | 61.4868 | 123.7381 | 123.7564 | -0.082397 | 123.7793 | 61.4914 | -0.13733 | 123.7564 | -0.082397 | 61.4914 | 123.7381 | 123.7793 | -124.0402 | -124.0402
30.7188 | 124.2142 | -61.4044 | 62.5534 | -0.0089264 | 0.0068381 | 0.012345 | 0.0044156 | 0.068579 | 0.00030767 | 0.0673 | -61.4822 | 62.471 | -61.5051 | -61.5967 | 62.2971 | 0.059509 | 0.027466 | 0.068665 | 62.4207 | -61.6241 | -0.10071 | -0.082398 | -0.07782 | -0.19226 | -0.25635 | -0.21973 | -0.13275 | 0.022888 | 61.4319 | 61.4731 | 123.7015 | 123.8754 | -0.07782 | 123.8251 | 61.4639 | -0.21973 | 123.8754 | -0.07782 | 61.4639 | 123.7015 | 123.8251 | -124.0585 | -124.1776
31.7188 | 124.3011 | -61.4044 | 62.5076 | 0.19707 | 0.0066245 | 0.0095682 | -0.0037022 | 0.068579 | -0.0016149 | 0.068582 | -61.4777 | 62.3749 | -61.5234 | -61.5692 | 62.3474 | 0.068665 | -0.15106 | 0.091553 | 62.3749 | -61.5601 | -0.11902 | -0.13275 | -0.073242 | -0.1648 | -0.16022 | -0.15564 | -0.13275 | 0.045776 | 61.2534 | 61.496 | 123.7518 | 123.7793 | -0.073242 | 123.7793 | 61.4731 | -0.15564 | 123.7793 | -0.073242 | 61.4731 | 123.7518 | 123.7793 | -124.0311 | -124.0677
32.7188 | 124.1821 | -61.4319 | 62.5397 | 0.03685 | 0.0089743 | 0.013627 | 0.00078404 | 0.06922 | -0.0026831 | 0.070718 | -61.5326 | 62.4847 | -61.5234 | -61.6562 | 62.2421 | -0.018311 | 0.050354 | -0.032043 | 62.4252 | -61.647 | -0.091552 | -0.054932 | -0.10071 | -0.2243 | -0.29755 | -0.21515 | -0.11444 | -0.009156 | 61.4822 | 61.3998 | 123.674 | 123.9166 | -0.10071 | 123.8571 | 61.4136 | -0.21515 | 123.9166 | -0.10071 | 61.4136 | 123.674 | 123.8571 | -124.0631 | -124.1867
33.7188 | 124.2828 | -61.3998 | 62.5031 | -0.069961 | 0.0066245 | 0.010636 | -0.0054112 | 0.067298 | -0.0016149 | 0.067727 | -61.496 | 62.3566 | -61.528 | -61.5646 | 62.3611 | 0.10529 | -0.054932 | 0.14648 | 62.4115 | -61.5555 | -0.12817 | -0.14648 | -0.096131 | -0.16479 | -0.14191 | -0.15564 | -0.091553 | 0.032043 | 61.3449 | 61.5463 | 123.761 | 123.7564 | -0.096131 | 123.8113 | 61.5051 | -0.15564 | 123.7564 | -0.096131 | 61.5051 | 123.761 | 123.8113 | -124.0311 | -124.0585
34.7188 | 124.2691 | -61.409 | 62.5259 | 1.4178 | 0.0083333 | 0.013413 | -0.00028416 | 0.068579 | 0.00094847 | 0.071572 | -61.496 | 62.4115 | -61.5234 | -61.5967 | 62.3199 | 0.036621 | -0.16022 | 0.045776 | 62.3749 | -61.6058 | -0.11444 | -0.11444 | -0.086975 | -0.18768 | -0.20599 | -0.19684 | -0.15106 | 0.027465 | 61.2488 | 61.4548 | 123.7289 | 123.8205 | -0.086975 | 123.7839 | 61.4456 | -0.19684 | 123.8205 | -0.086975 | 61.4456 | 123.7289 | 123.7839 | -124.0494 | -124.1318
35.7188 | 124.2096 | -61.409 | 62.5397 | -0.077591 | 0.0087607 | 0.012986 | 0.00527 | 0.068366 | -0.00054693 | 0.068795 | -61.4731 | 62.4802 | -61.5234 | -61.5692 | 62.2833 | 0.068665 | 0.018311 | 0.082397 | 62.4344 | -61.5967 | -0.11444 | -0.059509 | -0.064086 | -0.16022 | -0.25635 | -0.18768 | -0.10529 | 0.050354 | 61.4273 | 61.4914 | 123.6923 | 123.8892 | -0.064086 | 123.8434 | 61.4777 | -0.18768 | 123.8892 | -0.064086 | 61.4777 | 123.6923 | 123.8434 | -124.0631 | -124.1364
36.7188 | 124.1821 | -61.4548 | 62.5534 | 0.14366 | 0.0085471 | 0.013413 | 0.0029202 | 0.06922 | -0.00011953 | 0.068368 | -61.5509 | 62.4664 | -61.5509 | -61.6653 | 62.2055 | -0.027466 | -0.004578 | -0.054932 | 62.4252 | -61.6287 | -0.09613 | -0.086975 | -0.09613 | -0.21057 | -0.3479 | -0.17395 | -0.12817 | 0 | 61.4502 | 61.3998 | 123.6603 | 123.9212 | -0.09613 | 123.88 | 61.4273 | -0.17395 | 123.9212 | -0.09613 | 61.4273 | 123.6603 | 123.88 | -124.1043 | -124.1821
37.7188 | 124.1959 | -61.4182 | 62.5397 | -0.13863 | 0.0094015 | 0.012132 | 0.0016384 | 0.070502 | -0.0018285 | 0.06965 | -61.4868 | 62.4756 | -61.4822 | -61.5829 | 62.3199 | 0.082397 | 0.041199 | 0.10071 | 62.4573 | -61.615 | -0.064087 | -0.064087 | -0.068664 | -0.16479 | -0.21973 | -0.19684 | -0.082398 | -0.004577 | 61.4594 | 61.5189 | 123.7381 | 123.8937 | -0.068664 | 123.8754 | 61.5005 | -0.19684 | 123.8937 | -0.068664 | 61.5005 | 123.7381 | 123.8754 | -124.0219 | -124.1547
38.7188 | 124.2188 | -61.4319 | 62.5397 | -0.077591 | 0.0085471 | 0.013413 | 0.003561 | 0.071997 | -0.0018285 | 0.069436 | -61.4777 | 62.4756 | -61.5234 | -61.5829 | 62.3062 | 0.073242 | 0.013733 | 0.086975 | 62.4527 | -61.6013 | -0.091552 | -0.064087 | -0.045776 | -0.15106 | -0.23346 | -0.16937 | -0.086975 | 0.045776 | 61.4456 | 61.5189 | 123.7381 | 123.9075 | -0.045776 | 123.8846 | 61.5051 | -0.16937 | 123.9075 | -0.045776 | 61.5051 | 123.7381 | 123.8846 | -124.0631 | -124.1409
39.7188 | 124.2188 | -61.4273 | 62.558 | -0.039444 | 0.0098287 | 0.014482 | 0.00099764 | 0.071784 | 9.4068e-05 | 0.06965 | -61.4731 | 62.4756 | -61.5417 | -61.5738 | 62.3108 | 0.068665 | 0.036621 | 0.09613 | 62.4847 | -61.5784 | -0.11444 | -0.082397 | -0.045776 | -0.14648 | -0.24719 | -0.15106 | -0.073242 | 0.068665 | 61.4639 | 61.5234 | 123.7381 | 123.9029 | -0.045776 | 123.912 | 61.496 | -0.15106 | 123.9029 | -0.045776 | 61.496 | 123.7381 | 123.912 | -124.0997 | -124.1364
40.7188 | 124.1959 | -61.4182 | 62.5351 | 0.013962 | 0.010256 | 0.012559 | 0.0014248 | 0.071784 | -0.0035375 | 0.069009 | -61.4731 | 62.4619 | -61.5326 | -61.5875 | 62.3016 | 0.059509 | 0.027466 | 0.082397 | 62.4481 | -61.615 | -0.11444 | -0.073242 | -0.054931 | -0.16937 | -0.23346 | -0.19684 | -0.086975 | 0.05951 | 61.4456 | 61.5005 | 123.7198 | 123.88 | -0.054931 | 123.8663 | 61.4777 | -0.19684 | 123.88 | -0.054931 | 61.4777 | 123.7198 | 123.8663 | -124.0677 | -124.1501
41.7188 | 124.2554 | -61.3724 | 62.5168 | 0.18944 | 0.0070517 | 0.0132 | -0.0032748 | 0.070502 | 0.00030767 | 0.069863 | -61.4685 | 62.4207 | -61.5189 | -61.5784 | 62.3474 | 0.07782 | -0.15106 | 0.082397 | 62.3657 | -61.5646 | -0.14648 | -0.096131 | -0.096131 | -0.20599 | -0.16937 | -0.19226 | -0.15106 | 0.050354 | 61.2213 | 61.4548 | 123.7198 | 123.793 | -0.096131 | 123.7381 | 61.4502 | -0.19226 | 123.793 | -0.096131 | 61.4502 | 123.7198 | 123.7381 | -124.0356 | -124.0814
42.7188 | 124.173 | -61.4456 | 62.5717 | -0.2607 | 0.0070517 | 0.012345 | -0.0011386 | 0.068579 | -0.00097413 | 0.069436 | -61.5326 | 62.4985 | -61.5097 | -61.6196 | 62.2696 | 0.059509 | 0.16479 | 0.073242 | 62.471 | -61.6196 | -0.064087 | -0.073242 | -0.086975 | -0.17395 | -0.30212 | -0.17395 | -0.10071 | -0.022888 | 61.6104 | 61.5189 | 123.7152 | 123.9441 | -0.086975 | 123.9166 | 61.5051 | -0.17395 | 123.9441 | -0.086975 | 61.5051 | 123.7152 | 123.9166 | -124.0814 | -124.1913
43.7188 | 124.2279 | -61.4365 | 62.5442 | -0.0012969 | 0.0096151 | 0.014695 | 0.00057044 | 0.070929 | -0.0016149 | 0.066873 | -61.4822 | 62.471 | -61.5051 | -61.5829 | 62.3108 | 0.086975 | 0.018311 | 0.10071 | 62.4527 | -61.6104 | -0.068665 | -0.073242 | -0.045777 | -0.14648 | -0.23346 | -0.17395 | -0.091552 | 0.022888 | 61.4548 | 61.5372 | 123.7473 | 123.9075 | -0.045777 | 123.8892 | 61.5234 | -0.17395 | 123.9075 | -0.045777 | 61.5234 | 123.7473 | 123.8892 | -124.0494 | -124.1547
44.7188 | 124.2004 | -61.4456 | 62.5305 | 0.15892 | 0.0070517 | 0.010423 | 0.0014248 | 0.071143 | 9.4068e-05 | 0.072213 | -61.5463 | 62.4619 | -61.5326 | -61.6699 | 62.2467 | -0.022888 | -0.036621 | -0.027466 | 62.4435 | -61.6196 | -0.086975 | -0.068665 | -0.10071 | -0.2243 | -0.28381 | -0.17395 | -0.086976 | -0.013733 | 61.409 | 61.4182 | 123.6923 | 123.9075 | -0.10071 | 123.8892 | 61.4227 | -0.17395 | 123.9075 | -0.10071 | 61.4227 | 123.6923 | 123.8892 | -124.0631 | -124.1501
45.7188 | 124.2188 | -61.441 | 62.558 | -0.062332 | 0.0079061 | 0.015763 | 0.00099764 | 0.069007 | 0.00094847 | 0.067941 | -61.4548 | 62.471 | -61.5372 | -61.5921 | 62.3016 | 0.09613 | 0.018311 | 0.082397 | 62.4619 | -61.6241 | -0.09613 | -0.086975 | -0.013733 | -0.15106 | -0.25635 | -0.18311 | -0.09613 | 0.082397 | 61.4594 | 61.5234 | 123.7427 | 123.912 | -0.013733 | 123.9029 | 61.5372 | -0.18311 | 123.912 | -0.013733 | 61.5372 | 123.7427 | 123.9029 | -124.0952 | -124.1821
46.7188 | 124.1959 | -61.4639 | 62.5076 | -0.0012969 | 0.0087607 | 0.0132 | 0.0014248 | 0.071357 | -0.00011953 | 0.067513 | -61.5051 | 62.4527 | -61.5234 | -61.6241 | 62.2467 | -0.013733 | 0.050354 | 0.013733 | 62.4756 | -61.6425 | -0.059509 | -0.054931 | -0.041199 | -0.16022 | -0.26093 | -0.17853 | -0.032043 | 0.01831 | 61.5143 | 61.4777 | 123.7106 | 123.9166 | -0.041199 | 123.9395 | 61.4502 | -0.17853 | 123.9166 | -0.041199 | 61.4502 | 123.7106 | 123.9395 | -124.0311 | -124.1501
47.7188 | 124.1409 | -61.4182 | 62.5442 | -0.17677 | 0.0064107 | 0.012345 | -0.0028476 | 0.069648 | 0.00052127 | 0.067727 | -61.5234 | 62.4893 | -61.5326 | -61.6333 | 62.2742 | 0.064087 | 0.15106 | 0.10071 | 62.4893 | -61.6058 | -0.11444 | -0.054931 | -0.10529 | -0.21515 | -0.27008 | -0.18768 | -0.054931 | 0.009156 | 61.5692 | 61.5189 | 123.6923 | 123.9075 | -0.10529 | 123.9075 | 61.4822 | -0.18768 | 123.9075 | -0.10529 | 61.4822 | 123.6923 | 123.9075 | -124.0768 | -124.1501
48.7188 | 124.1501 | -61.4227 | 62.5854 | -0.23781 | 0.0094015 | 0.011277 | -0.00092496 | 0.067725 | -0.0014013 | 0.068795 | -61.5326 | 62.4619 | -61.5234 | -61.6196 | 62.2787 | 0.064087 | 0.15106 | 0.082397 | 62.5168 | -61.5784 | -0.10071 | -0.1236 | -0.10986 | -0.19684 | -0.3067 | -0.15564 | -0.068664 | -0.009156 | 61.5738 | 61.5051 | 123.7015 | 123.8846 | -0.10986 | 123.9395 | 61.4868 | -0.15564 | 123.8846 | -0.10986 | 61.4868 | 123.7015 | 123.9395 | -124.1089 | -124.1638
49.7188 | 124.1547 | -61.4273 | 62.5397 | -0.0089264 | 0.010042 | 0.0099954 | 0.00057044 | 0.069861 | -0.0018285 | 0.068582 | -61.4914 | 62.4802 | -61.5326 | -61.615 | 62.2787 | 0.036621 | 0.022888 | 0.022888 | 62.4619 | -61.615 | -0.10529 | -0.059509 | -0.064087 | -0.18768 | -0.26093 | -0.18768 | -0.07782 | 0.041199 | 61.4502 | 61.4502 | 123.7061 | 123.9075 | -0.064087 | 123.8892 | 61.4639 | -0.18768 | 123.9075 | -0.064087 | 61.4639 | 123.7061 | 123.8892 | -124.0723 | -124.1547
50.7188 | 124.1867 | -61.4319 | 62.5809 | -0.30647 | 0.0079061 | 0.011064 | -0.0013522 | 0.068152 | 0.00073487 | 0.067727 | -61.5189 | 62.4207 | -61.5143 | -61.6104 | 62.3016 | 0.082397 | 0.1236 | 0.10071 | 62.4985 | -61.5463 | -0.082397 | -0.16022 | -0.086975 | -0.17853 | -0.27924 | -0.11444 | -0.082398 | -0.004578 | 61.5555 | 61.5326 | 123.7335 | 123.8525 | -0.086975 | 123.9304 | 61.5143 | -0.11444 | 123.8525 | -0.086975 | 61.5143 | 123.7335 | 123.9304 | -124.0952 | -124.1272
51.7188 | 124.2371 | -61.4319 | 62.558 | -0.1844 | 0.010683 | 0.013413 | 0.0029202 | 0.068793 | -0.0033239 | 0.06965 | -61.6653 | 62.4619 | -61.5189 | -61.5829 | 62.3062 | 0.09613 | 0.064087 | 0.11902 | 62.4481 | -61.5692 | -0.086975 | -0.09613 | -0.23346 | -0.15106 | -0.25177 | -0.13733 | -0.10986 | -0.14648 | 61.496 | 61.5509 | 123.7381 | 123.8937 | -0.23346 | 123.88 | 61.528 | -0.13733 | 123.8937 | -0.23346 | 61.528 | 123.7381 | 123.88 | -124.0768 | -124.1272
52.7188 | 124.1913 | -61.4044 | 62.5854 | 0.082626 | 0.0076925 | 0.010636 | -0.0022068 | 0.067939 | 0.0013757 | 0.071145 | -61.4914 | 62.4435 | -61.5097 | -61.6058 | 62.3245 | 0.10986 | 0.1236 | 0.1236 | 62.4756 | -61.5784 | -0.10529 | -0.14191 | -0.086975 | -0.20142 | -0.26093 | -0.17395 | -0.10986 | 0.018311 | 61.528 | 61.528 | 123.7289 | 123.848 | -0.086975 | 123.88 | 61.5143 | -0.17395 | 123.848 | -0.086975 | 61.5143 | 123.7289 | 123.88 | -124.0952 | -124.1638
53.7188 | 124.1867 | -61.4456 | 62.5992 | -0.21492 | 0.0053427 | 0.0089274 | -0.0011386 | 0.06623 | 0.00052127 | 0.070291 | -61.5326 | 62.4756 | -61.528 | -61.6379 | 62.2742 | 0.064087 | 0.15564 | 0.07782 | 62.4756 | -61.6013 | -0.082397 | -0.1236 | -0.086975 | -0.19226 | -0.32501 | -0.15564 | -0.1236 | -0.004578 | 61.6013 | 61.5234 | 123.7198 | 123.9212 | -0.086975 | 123.9212 | 61.5097 | -0.15564 | 123.9212 | -0.086975 | 61.5097 | 123.7198 | 123.9212 | -124.1272 | -124.2004
54.7188 | 124.1501 | -61.4548 | 62.5488 | 0.10551 | 0.0089743 | 0.009141 | 0.001852 | 0.068579 | 0.00030767 | 0.071359 | -61.5601 | 62.4664 | -61.5417 | -61.6745 | 62.2192 | -0.041199 | 0.018311 | -0.050354 | 62.4481 | -61.6562 | -0.086975 | -0.082397 | -0.10529 | -0.21973 | -0.32959 | -0.20142 | -0.10071 | -0.018311 | 61.4731 | 61.4044 | 123.674 | 123.9212 | -0.10529 | 123.9029 | 61.4136 | -0.20142 | 123.9212 | -0.10529 | 61.4136 | 123.674 | 123.9029 | -124.0906 | -124.205
55.7188 | 124.2371 | -61.409 | 62.5259 | -0.054703 | 0.0076925 | 0.0132 | -0.0075474 | 0.070716 | -0.0011877 | 0.070931 | -61.528 | 62.3657 | -61.5234 | -61.6104 | 62.3291 | 0.068665 | -0.054932 | 0.09613 | 62.4298 | -61.5784 | -0.11444 | -0.16022 | -0.11902 | -0.20142 | -0.19684 | -0.16937 | -0.09613 | -0.004578 | 61.3541 | 61.5051 | 123.7381 | 123.7747 | -0.11902 | 123.8388 | 61.4777 | -0.16937 | 123.7747 | -0.11902 | 61.4777 | 123.7381 | 123.8388 | -124.0494 | -124.1043
56.7188 | 124.3195 | -61.377 | 62.5214 | -0.077591 | 0.0059835 | 0.0093546 | -0.0037022 | 0.06687 | -0.00033333 | 0.068795 | -61.4914 | 62.3428 | -61.5097 | -61.5326 | 62.3703 | 0.15106 | -0.082397 | 0.19684 | 62.4069 | -61.5509 | -0.13275 | -0.17853 | -0.11444 | -0.15564 | -0.15106 | -0.17395 | -0.11444 | 0.018311 | 61.2946 | 61.5738 | 123.7473 | 123.7198 | -0.11444 | 123.7839 | 61.528 | -0.17395 | 123.7198 | -0.11444 | 61.528 | 123.7473 | 123.7839 | -124.0311 | -124.0723
57.7188 | 124.324 | -61.3861 | 62.5397 | -0.069961 | 0.0040609 | 0.012559 | -0.0022068 | 0.064521 | 0.00052127 | 0.069436 | -61.441 | 62.352 | -61.5097 | -61.5051 | 62.3978 | 0.16479 | -0.068665 | 0.21973 | 62.4023 | -61.5692 | -0.1236 | -0.18768 | -0.054932 | -0.11902 | -0.14191 | -0.18311 | -0.13733 | 0.068665 | 61.3174 | 61.6058 | 123.7839 | 123.7381 | -0.054932 | 123.7885 | 61.5509 | -0.18311 | 123.7381 | -0.054932 | 61.5509 | 123.7839 | 123.7885 | -124.0494 | -124.1089
58.7188 | 124.2599 | -61.4044 | 62.5442 | 0.090256 | 0.0059835 | 0.011064 | -0.00049776 | 0.065375 | -0.00076053 | 0.069009 | -61.5234 | 62.352 | -61.5372 | -61.6196 | 62.2879 | 0.059509 | -0.07782 | 0.068665 | 62.3749 | -61.5875 | -0.13275 | -0.19226 | -0.11902 | -0.21515 | -0.25635 | -0.18311 | -0.16937 | 0.013733 | 61.3266 | 61.4731 | 123.6923 | 123.7564 | -0.11902 | 123.7793 | 61.4639 | -0.18311 | 123.7564 | -0.11902 | 61.4639 | 123.6923 | 123.7793 | -124.0814 | -124.1318
59.7188 | 124.1684 | -61.4319 | 62.5717 | -0.21492 | 0.0091879 | 0.0093546 | 0.00078404 | 0.063666 | -0.00054693 | 0.068582 | -61.5051 | 62.439 | -61.5143 | -61.5829 | 62.2833 | 0.064087 | 0.13275 | 0.10529 | 62.4481 | -61.5921 | -0.082397 | -0.13275 | -0.073242 | -0.15106 | -0.28839 | -0.16022 | -0.1236 | 0.009155 | 61.5646 | 61.5372 | 123.7152 | 123.8709 | -0.073242 | 123.88 | 61.496 | -0.16022 | 123.8709 | -0.073242 | 61.496 | 123.7152 | 123.88 | -124.086 | -124.1638
60.7188 | 124.2462 | -61.3953 | 62.5259 | -0.024185 | 0.0066245 | 0.01085 | -0.0034886 | 0.064734 | -0.00033333 | 0.06965 | -61.5097 | 62.3749 | -61.5234 | -61.5921 | 62.3108 | 0.041199 | -0.059509 | 0.086975 | 62.4161 | -61.5829 | -0.12817 | -0.15106 | -0.11444 | -0.19684 | -0.21515 | -0.18768 | -0.10986 | 0.013732 | 61.3358 | 61.4822 | 123.7061 | 123.7701 | -0.11444 | 123.8113 | 61.4365 | -0.18768 | 123.7701 | -0.11444 | 61.4365 | 123.7061 | 123.8113 | -124.0494 | -124.1089
61.7188 | 124.1867 | -61.4227 | 62.5854 | -0.23781 | 0.0081197 | 0.0095682 | 0.0067654 | 0.065161 | -0.00054693 | 0.069009 | -61.409 | 62.4252 | -61.5234 | -61.5417 | 62.3245 | 0.082397 | 0.10071 | 0.11902 | 62.4573 | -61.5967 | -0.10071 | -0.16022 | 0.013732 | -0.11902 | -0.26093 | -0.17395 | -0.12817 | 0.11444 | 61.5234 | 61.5417 | 123.7473 | 123.848 | 0.013732 | 123.88 | 61.5051 | -0.17395 | 123.848 | 0.013732 | 61.5051 | 123.7473 | 123.88 | -124.1089 | -124.1821
62.7188 | 124.2874 | -61.3953 | 62.5168 | 0.25047 | 0.0081197 | 0.013841 | 0.00099764 | 0.067298 | -0.0011877 | 0.0673 | -61.4548 | 62.3657 | -61.5189 | -61.5509 | 62.3199 | 0.059509 | -0.17853 | 0.07782 | 62.4023 | -61.5967 | -0.1236 | -0.15106 | -0.059509 | -0.15564 | -0.19684 | -0.20142 | -0.11444 | 0.064087 | 61.2167 | 61.4731 | 123.7152 | 123.761 | -0.059509 | 123.7976 | 61.4548 | -0.20142 | 123.761 | -0.059509 | 61.4548 | 123.7152 | 123.7976 | -124.0356 | -124.1135
63.7188 | 124.2599 | -61.3907 | 62.5122 | -0.047073 | 0.0074789 | 0.011704 | 0.0022794 | 0.068793 | 0.00030767 | 0.068582 | -61.5097 | 62.4161 | -61.5417 | -61.5784 | 62.2971 | 0.027466 | -0.15106 | 0.045776 | 62.3795 | -61.5967 | -0.15106 | -0.09613 | -0.11902 | -0.18768 | -0.21515 | -0.20599 | -0.13275 | 0.032043 | 61.2396 | 61.4365 | 123.6877 | 123.8068 | -0.11902 | 123.7701 | 61.4182 | -0.20599 | 123.8068 | -0.11902 | 61.4182 | 123.6877 | 123.7701 | -124.054 | -124.1089
64.7188 | 124.2599 | -61.3998 | 62.5031 | -0.031814 | 0.0055563 | 0.01085 | -0.004343 | 0.067511 | -0.00076053 | 0.069436 | -61.5097 | 62.352 | -61.5326 | -61.5692 | 62.3016 | 0.07782 | -0.064087 | 0.10529 | 62.4161 | -61.5646 | -0.13275 | -0.15106 | -0.10986 | -0.16937 | -0.20142 | -0.16479 | -0.086975 | 0.022888 | 61.3358 | 61.5051 | 123.7015 | 123.7518 | -0.10986 | 123.8159 | 61.4777 | -0.16479 | 123.7518 | -0.10986 | 61.4777 | 123.7015 | 123.8159 | -124.0356 | -124.0677
65.7188 | 124.2874 | -61.3907 | 62.5031 | 0.25047 | 0.0085471 | 0.011918 | -0.00071136 | 0.066657 | -0.0014013 | 0.06965 | -61.4594 | 62.3566 | -61.5005 | -61.5372 | 62.3154 | 0.068665 | -0.1831 | 0.082397 | 62.3611 | -61.6013 | -0.10986 | -0.14648 | -0.068665 | -0.14648 | -0.18768 | -0.21057 | -0.14191 | 0.041198 | 61.2076 | 61.4731 | 123.7061 | 123.7473 | -0.068665 | 123.7518 | 61.4594 | -0.21057 | 123.7473 | -0.068665 | 61.4594 | 123.7061 | 123.7518 | -124.0036 | -124.1043
66.7344 | 124.2279 | -61.4319 | 62.5488 | -0.19203 | 0.0083333 | 0.014909 | 0.004202 | 0.067298 | -0.0020421 | 0.069009 | -61.4731 | 62.4802 | -61.5051 | -61.5463 | 62.3108 | 0.09613 | 0.073242 | 0.11444 | 62.4619 | -61.6196 | -0.073242 | -0.068664 | -0.041198 | -0.11444 | -0.23804 | -0.18768 | -0.086975 | 0.032044 | 61.5051 | 61.5463 | 123.7427 | 123.912 | -0.041198 | 123.8937 | 61.528 | -0.18768 | 123.912 | -0.041198 | 61.528 | 123.7427 | 123.8937 | -124.054 | -124.1684
67.7188 | 124.2142 | -61.4319 | 62.4985 | 0.21996 | 0.0089743 | 0.01555 | 0.0022794 | 0.069434 | -0.00097413 | 0.069009 | -61.5189 | 62.4527 | -61.5509 | -61.5417 | 62.2513 | -0.11444 | -0.073242 | -0.013733 | 62.4115 | -61.615 | -0.11902 | -0.045776 | -0.086975 | -0.10986 | -0.24719 | -0.1831 | -0.086975 | 0.032043 | 61.3586 | 61.4182 | 123.6832 | 123.8846 | -0.086975 | 123.8434 | 61.3174 | -0.1831 | 123.8846 | -0.086975 | 61.3174 | 123.6832 | 123.8434 | -124.0494 | -124.1135
68.7188 | 124.2416 | -61.4182 | 62.5031 | 0.16655 | 0.0079061 | 0.013841 | 0.003561 | 0.069861 | -0.00011953 | 0.068154 | -61.496 | 62.4252 | -61.5692 | -61.4685 | 62.4802 | 0.14191 | -0.29297 | 0.059509 | 62.4115 | -61.6104 | -0.15106 | -0.07782 | -0.07782 | -0.050354 | -0.022888 | -0.19226 | -0.091553 | 0.073242 | 61.1252 | 61.4777 | 123.8983 | 123.8434 | -0.07782 | 123.8297 | 61.5601 | -0.19226 | 123.8434 | -0.07782 | 61.5601 | 123.8983 | 123.8297 | -124.0723 | -124.1135
69.7188 | 124.2416 | -61.3998 | 62.5351 | -0.031814 | 0.0057699 | 0.0063638 | -0.0037022 | 0.065802 | -0.0016149 | 0.06965 | -61.5189 | 62.3795 | -61.5189 | -61.5784 | 62.3245 | 0.07782 | -0.064087 | 0.10529 | 62.4115 | -61.5509 | -0.11902 | -0.15564 | -0.11902 | -0.17853 | -0.21057 | -0.15106 | -0.1236 | 0 | 61.3358 | 61.5051 | 123.7244 | 123.7793 | -0.11902 | 123.8113 | 61.4777 | -0.15106 | 123.7793 | -0.11902 | 61.4777 | 123.7244 | 123.8113 | -124.054 | -124.086
70.7188 | 124.1821 | -61.4227 | 62.5442 | 0.029221 | 0.0070517 | 0.017686 | 0.005911 | 0.069007 | -0.0026831 | 0.069436 | -61.7477 | 62.4344 | -61.5555 | -61.5509 | 62.2467 | -0.009155 | 0.045776 | -0.004578 | 62.4069 | -61.6287 | -0.13275 | -0.10986 | -0.32501 | -0.12817 | -0.29755 | -0.20599 | -0.13733 | -0.19226 | 61.4685 | 61.4182 | 123.6694 | 123.8571 | -0.32501 | 123.8296 | 61.4136 | -0.20599 | 123.8571 | -0.32501 | 61.4136 | 123.6694 | 123.8296 | -124.0997 | -124.173
71.7344 | 124.324 | -61.3358 | 62.5122 | -0.10048 | 0.0042745 | 0.0132 | -0.0024204 | 0.066443 | -0.0016149 | 0.069863 | -61.4365 | 62.3886 | -61.5189 | -61.4822 | 62.4207 | 0.16479 | -0.041199 | 0.21973 | 62.4344 | -61.5692 | -0.18311 | -0.1236 | -0.10071 | -0.14648 | -0.091553 | -0.23346 | -0.07782 | 0.082398 | 61.2946 | 61.5555 | 123.7564 | 123.7244 | -0.10071 | 123.7701 | 61.5005 | -0.23346 | 123.7244 | -0.10071 | 61.5005 | 123.7564 | 123.7701 | -124.0311 | -124.0814
72.7188 | 124.1409 | -61.4365 | 62.5488 | 0.052109 | 0.0091879 | 0.015336 | 0.0031338 | 0.067511 | -0.00076053 | 0.070718 | -61.5326 | 62.4802 | -61.5189 | -61.6608 | 62.2284 | -0.050354 | 0.041199 | -0.054932 | 62.4207 | -61.647 | -0.082398 | -0.068664 | -0.096131 | -0.22431 | -0.32043 | -0.21057 | -0.12817 | -0.013733 | 61.4777 | 61.3815 | 123.6649 | 123.9166 | -0.096131 | 123.8571 | 61.3861 | -0.21057 | 123.9166 | -0.096131 | 61.3861 | 123.6649 | 123.8571 | -124.0677 | -124.1959
73.7188 | 124.1776 | -61.441 | 62.5397 | 0.1284 | 0.0096151 | 0.015122 | 0.0014248 | 0.070502 | 0.00030767 | 0.06965 | -61.5372 | 62.4573 | -61.5417 | -61.6516 | 62.2467 | -0.036621 | 0.009155 | -0.064087 | 62.4573 | -61.6425 | -0.10071 | -0.082398 | -0.09613 | -0.21057 | -0.29297 | -0.20142 | -0.082398 | 0.004578 | 61.4502 | 61.377 | 123.6877 | 123.8983 | -0.09613 | 123.8983 | 61.4044 | -0.20142 | 123.8983 | -0.09613 | 61.4044 | 123.6877 | 123.8983 | -124.0814 | -124.1821
74.7188 | 124.3057 | -61.4227 | 62.4802 | 0.16655 | 0.0087607 | 0.014909 | 0.00078404 | 0.068366 | -0.0011877 | 0.069222 | -61.4594 | 62.4115 | -61.528 | -61.5601 | 62.352 | 0.064087 | -0.16937 | 0.086975 | 62.3749 | -61.5875 | -0.10529 | -0.068665 | -0.036622 | -0.13733 | -0.12817 | -0.1648 | -0.10529 | 0.068664 | 61.2534 | 61.5097 | 123.7747 | 123.8342 | -0.036622 | 123.7976 | 61.4868 | -0.1648 | 123.8342 | -0.036622 | 61.4868 | 123.7747 | 123.7976 | -124.0082 | -124.0677
75.7188 | 124.205 | -61.4136 | 62.5488 | -0.024185 | 0.0061971 | 0.011277 | 0.0014248 | 0.069861 | -0.0018285 | 0.067513 | -61.4868 | 62.4802 | -61.528 | -61.5784 | 62.2971 | 0.068665 | 0.027466 | 0.068665 | 62.4573 | -61.6379 | -0.11444 | -0.068664 | -0.073242 | -0.1648 | -0.25177 | -0.2243 | -0.091553 | 0.041199 | 61.441 | 61.4822 | 123.7106 | 123.8937 | -0.073242 | 123.8708 | 61.4822 | -0.2243 | 123.8937 | -0.073242 | 61.4822 | 123.7106 | 123.8708 | -124.0768 | -124.1867
76.7344 | 124.2416 | -61.3953 | 62.5031 | -0.047073 | 0.0057699 | 0.011491 | -0.0064792 | 0.067084 | -0.0035375 | 0.0673 | -61.5372 | 62.3566 | -61.5555 | -61.5875 | 62.3291 | 0.073242 | -0.054932 | 0.10071 | 62.4115 | -61.5784 | -0.16022 | -0.14648 | -0.14191 | -0.19226 | -0.17395 | -0.18311 | -0.091553 | 0.018311 | 61.3403 | 61.496 | 123.7244 | 123.7518 | -0.14191 | 123.8068 | 61.4685 | -0.18311 | 123.7518 | -0.14191 | 61.4685 | 123.7244 | 123.8068 | -124.0585 | -124.0814
77.7188 | 124.2279 | -61.4044 | 62.5488 | -0.031814 | 0.0066245 | 0.012132 | 0.0039882 | 0.06687 | 0.00030767 | 0.069436 | -61.4594 | 62.4847 | -61.5097 | -61.5875 | 62.2833 | 0.073242 | 0.004578 | 0.082397 | 62.439 | -61.6425 | -0.10529 | -0.064087 | -0.054932 | -0.18311 | -0.2655 | -0.23804 | -0.10986 | 0.050354 | 61.409 | 61.4868 | 123.6877 | 123.8892 | -0.054932 | 123.8434 | 61.4777 | -0.23804 | 123.8892 | -0.054932 | 61.4777 | 123.6877 | 123.8434 | -124.0585 | -124.1913
78.7188 | 124.2508 | -61.4227 | 62.558 | -0.26833 | 0.0059835 | 0.013841 | -0.0037022 | 0.068793 | -0.00054693 | 0.068368 | -61.5097 | 62.4802 | -61.5372 | -61.5372 | 62.4573 | 0.13733 | 0.082397 | 0.16479 | 62.4756 | -61.5829 | -0.11444 | -0.077819 | -0.086976 | -0.11444 | -0.10071 | -0.16022 | -0.082397 | 0.027465 | 61.5051 | 61.5875 | 123.88 | 123.9029 | -0.086976 | 123.8983 | 61.5601 | -0.16022 | 123.9029 | -0.086976 | 61.5601 | 123.88 | 123.8983 | -124.0952 | -124.1409
79.7344 | 124.2691 | -61.4136 | 62.4985 | 0.18181 | 0.0061971 | 0.0099954 | -0.00071136 | 0.070075 | 9.4068e-05 | 0.06965 | -61.4639 | 62.3795 | -61.5417 | -61.5417 | 62.3428 | 0.086975 | -0.16937 | 0.086975 | 62.3932 | -61.5738 | -0.12817 | -0.11902 | -0.050354 | -0.12817 | -0.15564 | -0.16022 | -0.10529 | 0.07782 | 61.2442 | 61.5005 | 123.7564 | 123.793 | -0.050354 | 123.8068 | 61.5005 | -0.16022 | 123.793 | -0.050354 | 61.5005 | 123.7564 | 123.8068 | -124.0402 | -124.0723
80.7188 | 124.2096 | -61.4182 | 62.5809 | -0.13863 | 0.0085471 | 0.0072184 | 0.0014248 | 0.068366 | -0.00097413 | 0.071145 | -61.5143 | 62.4756 | -61.528 | -61.5829 | 62.3199 | 0.07782 | 0.10986 | 0.091553 | 62.4573 | -61.5967 | -0.10986 | -0.10529 | -0.09613 | -0.16479 | -0.26093 | -0.17853 | -0.1236 | 0.013733 | 61.528 | 61.5097 | 123.7381 | 123.8937 | -0.09613 | 123.8754 | 61.496 | -0.17853 | 123.8937 | -0.09613 | 61.496 | 123.7381 | 123.8754 | -124.1089 | -124.1776
81.7188 | 124.173 | -61.4044 | 62.5351 | -0.0089264 | 0.010256 | 0.017045 | 0.001852 | 0.067298 | -0.00054693 | 0.069436 | -61.4868 | 62.4893 | -61.5417 | -61.5967 | 62.265 | 0.045776 | 0.027466 | 0.041199 | 62.4344 | -61.615 | -0.13733 | -0.045776 | -0.082397 | -0.19226 | -0.27008 | -0.21057 | -0.10071 | 0.054932 | 61.4319 | 61.4456 | 123.6694 | 123.8937 | -0.082397 | 123.8388 | 61.4502 | -0.21057 | 123.8937 | -0.082397 | 61.4502 | 123.6694 | 123.8388 | -124.0768 | -124.1501
82.7188 | 124.1867 | -61.4136 | 62.558 | -0.12337 | 0.01047 | 0.0099954 | 0.001852 | 0.068793 | -0.00011953 | 0.067727 | -61.4319 | 62.4435 | -61.5417 | -61.5097 | 62.2879 | 0.091553 | 0.032043 | 0.10986 | 62.4573 | -61.6013 | -0.12817 | -0.11444 | -0.018311 | -0.096131 | -0.27008 | -0.18768 | -0.10071 | 0.10986 | 61.4456 | 61.5234 | 123.7015 | 123.8571 | -0.018311 | 123.8708 | 61.5051 | -0.18768 | 123.8571 | -0.018311 | 61.5051 | 123.7015 | 123.8708 | -124.0997 | -124.1592
83.7188 | 124.173 | -61.4136 | 62.5442 | -0.26833 | 0.0042745 | 0.0082864 | -0.0041294 | 0.067084 | -0.00054693 | 0.068154 | -61.496 | 62.4298 | -61.5234 | -61.5738 | 62.3245 | 0.14191 | 0.09613 | 0.15564 | 62.4573 | -61.5463 | -0.10986 | -0.11444 | -0.082398 | -0.16022 | -0.21973 | -0.13275 | -0.086975 | 0.027465 | 61.5097 | 61.5692 | 123.7381 | 123.8434 | -0.082398 | 123.8708 | 61.5555 | -0.13275 | 123.8434 | -0.082398 | 61.5555 | 123.7381 | 123.8708 | -124.0677 | -124.0906
84.7188 | 124.2691 | -61.4227 | 62.5854 | -0.11574 | 0.0091879 | 0.0095682 | 0.0037746 | 0.06922 | -0.0028967 | 0.070931 | -61.4685 | 62.471 | -61.528 | -61.5646 | 62.3062 | 0.07782 | 0.045776 | -0.1831 | 62.4161 | -61.6241 | -0.10529 | -0.11444 | -0.045777 | -0.14191 | -0.27924 | -0.20142 | -0.16937 | 0.059509 | 61.4685 | 61.2396 | 123.7289 | 123.8937 | -0.045777 | 123.8388 | 61.5005 | -0.20142 | 123.8937 | -0.045777 | 61.5005 | 123.7289 | 123.8388 | -124.1135 | -124.2096
85.7188 | 124.1821 | -61.441 | 62.5717 | -0.22255 | 0.0072653 | 0.012132 | -0.002634 | 0.068366 | -0.0026831 | 0.072 | -61.5372 | 62.4619 | -61.5555 | -61.647 | 62.0819 | -0.059509 | 0.17853 | 0.064087 | 62.4435 | -61.6013 | -0.11444 | -0.10986 | -0.09613 | -0.20599 | -0.48981 | -0.16022 | -0.12817 | 0.018311 | 61.6196 | 61.5051 | 123.5229 | 123.9029 | -0.09613 | 123.8846 | 61.3815 | -0.16022 | 123.9029 | -0.09613 | 61.3815 | 123.5229 | 123.8846 | -124.1272 | -124.173
86.7188 | 124.1913 | -61.4044 | 62.5259 | -0.0089264 | 0.0068381 | 0.011704 | 0.0027066 | 0.070075 | -0.00097413 | 0.071359 | -61.4685 | 62.4573 | -61.5463 | -61.5829 | 62.3062 | 0.073242 | 0.027466 | 0.068665 | 62.4252 | -61.6013 | -0.14191 | -0.068665 | -0.064087 | -0.17853 | -0.21973 | -0.19684 | -0.10071 | 0.07782 | 61.4319 | 61.4731 | 123.7106 | 123.8617 | -0.064087 | 123.8297 | 61.4777 | -0.19684 | 123.8617 | -0.064087 | 61.4777 | 123.7106 | 123.8297 | -124.0723 | -124.1272
87.7188 | 124.173 | -61.3953 | 62.5626 | -0.23781 | 0.0059835 | 0.011277 | -0.0024204 | 0.06687 | -0.0018285 | 0.06965 | -61.4777 | 62.4207 | -61.5143 | -61.5646 | 62.3291 | 0.12817 | 0.091553 | 0.16937 | 62.4298 | -61.5829 | -0.11902 | -0.14191 | -0.082397 | -0.16937 | -0.23346 | -0.18768 | -0.13275 | 0.036621 | 61.4868 | 61.5646 | 123.7244 | 123.8159 | -0.082397 | 123.8251 | 61.5234 | -0.18768 | 123.8159 | -0.082397 | 61.5234 | 123.7244 | 123.8251 | -124.0768 | -124.1455
88.7188 | 124.1547 | -61.3953 | 62.558 | -0.22255 | 0.0070517 | 0.0093546 | -0.0024204 | 0.065589 | -0.00011953 | 0.06965 | -61.528 | 62.4344 | -61.5097 | -61.6013 | 62.3016 | 0.068665 | 0.13733 | 0.10071 | 62.4664 | -61.5967 | -0.11444 | -0.1236 | -0.13275 | -0.20599 | -0.25635 | -0.20142 | -0.091552 | -0.01831 | 61.5326 | 61.496 | 123.6969 | 123.8297 | -0.13275 | 123.8617 | 61.4639 | -0.20142 | 123.8297 | -0.13275 | 61.4639 | 123.6969 | 123.8617 | -124.0677 | -124.1547
89.7188 | 124.1776 | -61.3861 | 62.5671 | -0.15388 | 0.0094015 | 0.011918 | 0.0033474 | 0.072425 | -0.0016149 | 0.070931 | -61.4502 | 62.4481 | -61.496 | -61.5234 | 62.2604 | 0.054932 | 0.032043 | 0.10071 | 62.4481 | -61.615 | -0.10986 | -0.11902 | -0.064087 | -0.13733 | -0.3067 | -0.22888 | -0.11902 | 0.045777 | 61.4182 | 61.4868 | 123.6465 | 123.8342 | -0.064087 | 123.8342 | 61.441 | -0.22888 | 123.8342 | -0.064087 | 61.441 | 123.6465 | 123.8342 | -124.0631 | -124.1821
90.7188 | 124.2462 | -61.3586 | 62.558 | -0.23781 | 0.0064107 | 0.012559 | -0.0034886 | 0.066657 | -0.0028967 | 0.069863 | -61.4548 | 62.4069 | -61.5189 | -61.5509 | 62.3611 | 0.15564 | 0.022888 | 0.19226 | 62.4344 | -61.5463 | -0.16022 | -0.15106 | -0.09613 | -0.19226 | -0.19684 | -0.18768 | -0.1236 | 0.064087 | 61.3815 | 61.5509 | 123.7198 | 123.7656 | -0.09613 | 123.793 | 61.5143 | -0.18768 | 123.7656 | -0.09613 | 61.5143 | 123.7198 | 123.793 | -124.0768 | -124.1043
91.7188 | 124.2828 | -61.3815 | 62.5442 | -0.28358 | 0.0072653 | 0.0099954 | -0.0024204 | 0.067084 | -0.00076053 | 0.06495 | -61.4273 | 62.3932 | -61.5051 | -61.5189 | 62.3657 | 0.16937 | -0.032043 | 0.20142 | 62.4069 | -61.5417 | -0.1236 | -0.15106 | -0.045776 | -0.13733 | -0.17853 | -0.16022 | -0.13733 | 0.07782 | 61.3495 | 61.5829 | 123.7473 | 123.7747 | -0.045776 | 123.7885 | 61.5509 | -0.16022 | 123.7747 | -0.045776 | 61.5509 | 123.7473 | 123.7885 | -124.0494 | -124.086
92.7188 | 124.292 | -61.3861 | 62.4893 | -0.10811 | 0.0079061 | 0.0076456 | -0.0034886 | 0.066443 | -0.00054693 | 0.069436 | -61.4777 | 62.3566 | -61.5189 | -61.5143 | 62.3749 | 0.15564 | -0.073242 | 0.20599 | 62.4207 | -61.5417 | -0.13275 | -0.13275 | -0.091553 | -0.12817 | -0.11444 | -0.15564 | -0.068665 | 0.041199 | 61.3129 | 61.5921 | 123.761 | 123.7427 | -0.091553 | 123.8068 | 61.5417 | -0.15564 | 123.7427 | -0.091553 | 61.5417 | 123.761 | 123.8068 | -124.0082 | -124.0311
93.7344 | 124.1501 | -61.4227 | 62.5442 | 2.6308 | 0.0066245 | 0.0052958 | 0.0014248 | 0.067298 | -0.00011953 | 0.068582 | -61.2717 | 62.4435 | -61.5326 | -61.6241 | 62.2513 | -0.036621 | -0.009155 | -0.022888 | 62.4435 | -61.6379 | -0.10986 | -0.10071 | 0.15106 | -0.20142 | -0.29297 | -0.21515 | -0.10071 | 0.26093 | 61.4136 | 61.3998 | 123.674 | 123.8663 | 0.15106 | 123.8663 | 61.3861 | -0.21515 | 123.8663 | 0.15106 | 61.3861 | 123.674 | 123.8663 | -124.0768 | -124.1821
94.7188 | 124.2096 | -61.4136 | 62.5717 | -0.20729 | 0.0081197 | 0.014054 | 0.0037746 | 0.068152 | -0.0024695 | 0.069009 | -61.4639 | 62.4847 | -61.5326 | -61.5601 | 62.3062 | 0.086975 | 0.045776 | 0.10071 | 62.439 | -61.6104 | -0.11902 | -0.086975 | -0.050354 | -0.14649 | -0.2655 | -0.19684 | -0.13275 | 0.068665 | 61.4593 | 61.5143 | 123.7198 | 123.8983 | -0.050354 | 123.8525 | 61.5005 | -0.19684 | 123.8983 | -0.050354 | 61.5005 | 123.7198 | 123.8525 | -124.1043 | -124.1821
95.7188 | 124.2783 | -61.3998 | 62.5305 | -0.10048 | 0.0064107 | 0.012345 | -0.0037022 | 0.067939 | -0.0022559 | 0.067941 | -61.4822 | 62.3703 | -61.496 | -61.5417 | 62.3566 | 0.12817 | -0.059509 | 0.16479 | 62.4069 | -61.5601 | -0.096131 | -0.16022 | -0.082398 | -0.14191 | -0.17395 | -0.16022 | -0.1236 | 0.013733 | 61.3403 | 61.5646 | 123.7564 | 123.7701 | -0.082398 | 123.8068 | 61.528 | -0.16022 | 123.7701 | -0.082398 | 61.528 | 123.7564 | 123.8068 | -124.0265 | -124.0906
96.7188 | 124.2737 | -61.3815 | 62.5122 | -0.12337 | 0.0076925 | 0.0093546 | -0.0028476 | 0.066443 | -0.00033333 | 0.068368 | -61.4319 | 62.352 | -61.5097 | -61.5097 | 62.3932 | 0.15106 | -0.09613 | 0.21515 | 62.3932 | -61.5463 | -0.12817 | -0.16022 | -0.050354 | -0.12817 | -0.11902 | -0.16479 | -0.11902 | 0.07782 | 61.2854 | 61.5967 | 123.7747 | 123.7335 | -0.050354 | 123.7747 | 61.5326 | -0.16479 | 123.7335 | -0.050354 | 61.5326 | 123.7747 | 123.7747 | -124.0219 | -124.0585
97.7188 | 124.2416 | -61.4044 | 62.5122 | -0.0089264 | 0.0085471 | 0.010636 | -0.0019932 | 0.066016 | -0.0026831 | 0.067086 | -61.5189 | 62.3474 | -61.528 | -61.5829 | 62.3245 | 0.07782 | -0.059509 | 0.09613 | 62.4252 | -61.5646 | -0.1236 | -0.16479 | -0.11444 | -0.17853 | -0.18768 | -0.16022 | -0.086975 | 0.009155 | 61.3449 | 61.5005 | 123.7289 | 123.7518 | -0.11444 | 123.8297 | 61.4822 | -0.16022 | 123.7518 | -0.11444 | 61.4822 | 123.7289 | 123.8297 | -124.0402 | -124.0768
98.7188 | 124.292 | -61.3861 | 62.5259 | 0.013962 | 0.0034201 | 0.011277 | -0.002634 | 0.064307 | -0.0028967 | 0.06965 | -61.4822 | 62.3611 | -61.5234 | -61.5601 | 62.3337 | 0.11444 | -0.07782 | 0.13733 | 62.3886 | -61.5646 | -0.13733 | -0.16479 | -0.096131 | -0.17395 | -0.19226 | -0.17853 | -0.13733 | 0.041198 | 61.3083 | 61.5234 | 123.7198 | 123.7473 | -0.096131 | 123.7747 | 61.5005 | -0.17853 | 123.7473 | -0.096131 | 61.5005 | 123.7198 | 123.7747 | -124.0494 | -124.0906
99.7188 | 124.1821 | -61.4136 | 62.5809 | -0.23781 | 0.0057699 | 0.013627 | -0.00092496 | 0.06623 | -0.00097413 | 0.069436 | -61.5051 | 62.4298 | -61.5097 | -61.5829 | 62.3062 | 0.091553 | 0.12817 | 0.11902 | 62.439 | -61.6013 | -0.096131 | -0.15106 | -0.091553 | -0.16937 | -0.27466 | -0.18768 | -0.14191 | 0.004578 | 61.5417 | 61.5326 | 123.7198 | 123.8434 | -0.091553 | 123.8525 | 61.5051 | -0.18768 | 123.8434 | -0.091553 | 61.5051 | 123.7198 | 123.8525 | -124.0906 | -124.1821
100.7188 | 124.2554 | -61.3815 | 62.5259 | 0.47935 | 0.0055563 | 0.010636 | -0.002634 | 0.065589 | -0.0024695 | 0.070077 | -61.4914 | 62.3566 | -61.5326 | -61.5967 | 62.3108 | 0.036621 | -0.073242 | 0.09613 | 62.4252 | -61.5738 | -0.15106 | -0.16937 | -0.10986 | -0.21515 | -0.21515 | -0.19226 | -0.10071 | 0.041199 | 61.3083 | 61.4777 | 123.6923 | 123.7381 | -0.10986 | 123.8068 | 61.4182 | -0.19226 | 123.7381 | -0.10986 | 61.4182 | 123.6923 | 123.8068 | -124.0585 | -124.0997
101.7188 | 124.3103 | -61.3953 | 62.5305 | -0.09285 | 0.0034201 | 0.012773 | -0.0022068 | 0.063452 | -0.0020421 | 0.069009 | -61.4639 | 62.3566 | -61.5097 | -61.5051 | 62.384 | 0.14648 | -0.07782 | 0.19226 | 62.3749 | -61.5509 | -0.11444 | -0.17395 | -0.068664 | -0.10986 | -0.14648 | -0.15564 | -0.15564 | 0.045777 | 61.3174 | 61.5875 | 123.7793 | 123.7518 | -0.068664 | 123.7701 | 61.5417 | -0.15564 | 123.7518 | -0.068664 | 61.5417 | 123.7793 | 123.7701 | -124.0402 | -124.0814
102.7188 | 124.2783 | -61.3861 | 62.5214 | -0.10811 | 0.0057699 | 0.0076456 | -0.00092496 | 0.064734 | -0.00097413 | 0.068368 | -61.4822 | 62.3611 | -61.5234 | -61.5326 | 62.3566 | 0.11902 | -0.07782 | 0.16937 | 62.384 | -61.5555 | -0.13733 | -0.16022 | -0.096131 | -0.14648 | -0.1648 | -0.16937 | -0.13733 | 0.041198 | 61.3083 | 61.5555 | 123.7427 | 123.7473 | -0.096131 | 123.7701 | 61.5051 | -0.16937 | 123.7473 | -0.096131 | 61.5051 | 123.7427 | 123.7701 | -124.0448 | -124.0768
103.7188 | 124.2279 | -61.3907 | 62.5076 | 0.12077 | 0.0074789 | 0.006791 | 0.00035684 | 0.065589 | -0.00033333 | 0.06965 | -61.5005 | 62.3611 | -61.5143 | -61.6104 | 62.2925 | 0.032043 | -0.10071 | 0.050354 | 62.384 | -61.5784 | -0.1236 | -0.14648 | -0.10986 | -0.21973 | -0.21515 | -0.18768 | -0.1236 | 0.013733 | 61.29 | 61.441 | 123.6832 | 123.7518 | -0.10986 | 123.7747 | 61.4227 | -0.18768 | 123.7518 | -0.10986 | 61.4227 | 123.6832 | 123.7747 | -124.0219 | -124.086
104.7188 | 124.2828 | -61.3586 | 62.5168 | -0.08522 | 0.0051291 | 0.010209 | 0.00035684 | 0.064734 | -0.0020421 | 0.071145 | -61.4548 | 62.3657 | -61.5005 | -61.5005 | 62.3749 | 0.14648 | -0.059509 | 0.20142 | 62.3932 | -61.5921 | -0.14191 | -0.15106 | -0.09613 | -0.14191 | -0.14191 | -0.23346 | -0.1236 | 0.045776 | 61.2991 | 61.5601 | 123.7335 | 123.7244 | -0.09613 | 123.7518 | 61.5051 | -0.23346 | 123.7244 | -0.09613 | 61.5051 | 123.7335 | 123.7518 | -124.0173 | -124.1089
105.7188 | 124.2325 | -61.3998 | 62.5214 | 0.10551 | 0.0068381 | 0.011491 | 0.00014304 | 0.06388 | -0.0026831 | 0.069436 | -61.4731 | 62.3657 | -61.5189 | -61.5601 | 62.3062 | 0.050354 | -0.16022 | 0.068665 | 62.3795 | -61.6058 | -0.11902 | -0.15564 | -0.073242 | -0.16022 | -0.21515 | -0.20599 | -0.14191 | 0.045777 | 61.2396 | 61.4685 | 123.7061 | 123.7656 | -0.073242 | 123.7793 | 61.4502 | -0.20599 | 123.7656 | -0.073242 | 61.4502 | 123.7061 | 123.7793 | -124.0402 | -124.1272
106.7188 | 124.2645 | -61.3586 | 62.5488 | -0.11574 | 0.0064107 | 0.011918 | 0.001852 | 0.06388 | 9.4068e-05 | 0.067941 | -61.4548 | 62.3703 | -61.5234 | -61.4731 | 62.3795 | 0.15106 | -0.041199 | 0.21057 | 62.3932 | -61.5509 | -0.16479 | -0.17853 | -0.09613 | -0.11444 | -0.16937 | -0.19226 | -0.15564 | 0.068664 | 61.3174 | 61.5692 | 123.7381 | 123.7289 | -0.09613 | 123.7518 | 61.5097 | -0.19226 | 123.7289 | -0.09613 | 61.5097 | 123.7381 | 123.7518 | -124.0723 | -124.0997
107.7188 | 124.2737 | -61.3953 | 62.5168 | -0.047073 | 0.0057699 | 0.006791 | 0.00057044 | 0.066443 | -0.0014013 | 0.070077 | -61.5005 | 62.3657 | -61.5509 | -61.5692 | 62.3291 | 0.07782 | -0.07782 | 0.11902 | 62.3886 | -61.5555 | -0.15564 | -0.15106 | -0.10529 | -0.17395 | -0.18768 | -0.16022 | -0.12817 | 0.050354 | 61.3174 | 61.5143 | 123.7244 | 123.761 | -0.10529 | 123.7839 | 61.4731 | -0.16022 | 123.761 | -0.10529 | 61.4731 | 123.7244 | 123.7839 | -124.0677 | -124.0723
108.7188 | 124.2508 | -61.3998 | 62.5214 | 0.090256 | 0.0059835 | 0.010636 | 0.0027066 | 0.064734 | -0.0014013 | 0.069009 | -61.4822 | 62.3886 | -61.5143 | -61.5509 | 62.2925 | 0.045776 | -0.15106 | 0.064087 | 62.3474 | -61.5784 | -0.11444 | -0.13275 | -0.082398 | -0.15106 | -0.22888 | -0.17853 | -0.17395 | 0.032043 | 61.2488 | 61.4639 | 123.6923 | 123.7885 | -0.082398 | 123.7473 | 61.4456 | -0.17853 | 123.7885 | -0.082398 | 61.4456 | 123.6923 | 123.7473 | -124.0356 | -124.0997
109.7188 | 124.2737 | -61.3678 | 62.5305 | -0.23018 | 0.0059835 | 0.01085 | -7.0562e-05 | 0.065375 | -0.0026831 | 0.069222 | -61.4182 | 62.384 | -61.4914 | -61.4731 | 62.3795 | 0.16937 | -0.032043 | 0.2243 | 62.4069 | -61.5601 | -0.1236 | -0.14648 | -0.050354 | -0.10529 | -0.15106 | -0.19226 | -0.1236 | 0.073242 | 61.3358 | 61.5921 | 123.7473 | 123.7518 | -0.050354 | 123.7747 | 61.5372 | -0.19226 | 123.7518 | -0.050354 | 61.5372 | 123.7473 | 123.7747 | -124.0219 | -124.0906
110.7188 | 124.2416 | -61.409 | 62.5259 | 0.0063326 | 0.0055563 | 0.012345 | 0.00057044 | 0.065375 | -0.0022559 | 0.068368 | -61.3358 | 62.4023 | -61.4868 | -61.5738 | 62.2787 | 0.036621 | -0.073242 | 0.068665 | 62.384 | -61.5829 | -0.077819 | -0.1236 | 0.073243 | -0.16479 | -0.24719 | -0.17395 | -0.14191 | 0.15106 | 61.3358 | 61.4777 | 123.6877 | 123.8113 | 0.073243 | 123.793 | 61.4456 | -0.17395 | 123.8113 | 0.073243 | 61.4456 | 123.6877 | 123.793 | -124.0128 | -124.1089
111.7188 | 124.2462 | -61.3907 | 62.5305 | 0.021591 | 0.0074789 | 0.009141 | -0.00071136 | 0.064948 | -0.0020421 | 0.068368 | -61.5234 | 62.3932 | -61.528 | -61.5646 | 62.3154 | 0.068665 | -0.059509 | 0.10071 | 62.3932 | -61.5509 | -0.13733 | -0.13733 | -0.13275 | -0.17395 | -0.21515 | -0.16022 | -0.13733 | 0.004578 | 61.3312 | 61.4914 | 123.7061 | 123.7839 | -0.13275 | 123.7839 | 61.4594 | -0.16022 | 123.7839 | -0.13275 | 61.4594 | 123.7061 | 123.7839 | -124.0585 | -124.0814
112.7188 | 124.3011 | -61.3907 | 62.5031 | -1.7255 | 0.0085471 | 0.010636 | 0.003561 | 0.065802 | -0.0033239 | 0.068582 | -61.4548 | 62.384 | -61.4914 | -61.5372 | 62.3062 | 0.059509 | -0.17853 | 0.07782 | 62.352 | -61.6013 | -0.10071 | -0.11902 | -0.064087 | -0.14648 | -0.19684 | -0.21057 | -0.15106 | 0.036621 | 61.2122 | 61.4685 | 123.6969 | 123.7747 | -0.064087 | 123.7427 | 61.4502 | -0.21057 | 123.7747 | -0.064087 | 61.4502 | 123.6969 | 123.7427 | -123.9944 | -124.1043
113.7188 | 124.2828 | -61.3861 | 62.5076 | 0.15129 | 0.0076925 | 0.011491 | 0.0033474 | 0.066443 | -0.00033333 | 0.072854 | -61.4502 | 62.352 | -61.5234 | -61.5417 | 62.3383 | 0.068665 | -0.19226 | 0.073242 | 62.352 | -61.5784 | -0.13733 | -0.15564 | -0.064087 | -0.15564 | -0.16937 | -0.19226 | -0.15564 | 0.073242 | 61.1938 | 61.4594 | 123.7244 | 123.7381 | -0.064087 | 123.7381 | 61.4548 | -0.19226 | 123.7381 | -0.064087 | 61.4548 | 123.7244 | 123.7381 | -124.0311 | -124.086
114.7188 | 124.292 | -61.3495 | 62.5214 | -0.19966 | 0.0057699 | 0.0087138 | -0.0011386 | 0.066016 | -0.0026831 | 0.070077 | -61.4227 | 62.3703 | -61.5005 | -61.7111 | 62.0911 | 0.068665 | -0.059509 | 0.073242 | 62.3657 | -61.5692 | -0.15106 | -0.15106 | -0.073242 | -0.36163 | -0.4303 | -0.21973 | -0.15564 | 0.07782 | 61.29 | 61.4227 | 123.4406 | 123.7198 | -0.073242 | 123.7152 | 61.4182 | -0.21973 | 123.7198 | -0.073242 | 61.4182 | 123.4406 | 123.7152 | -124.0219 | -124.0906
115.7188 | 124.2233 | -61.3998 | 62.5168 | 0.18944 | 0.0068381 | 0.009141 | -0.0022068 | 0.063239 | -0.0043921 | 0.067941 | -61.5051 | 62.352 | -61.5051 | -61.5738 | 62.2787 | 0.036621 | -0.10529 | 0.045776 | 62.3703 | -61.5829 | -0.10529 | -0.16479 | -0.10529 | -0.17395 | -0.23804 | -0.18311 | -0.14648 | 0 | 61.2946 | 61.4456 | 123.6786 | 123.7518 | -0.10529 | 123.7701 | 61.4365 | -0.18311 | 123.7518 | -0.10529 | 61.4365 | 123.6786 | 123.7701 | -124.0219 | -124.0997
116.7188 | 124.2874 | -61.3907 | 62.4985 | 0.16655 | 0.0066245 | 0.015122 | 0.001852 | 0.066016 | -0.00033333 | 0.068368 | -61.4548 | 62.3703 | -61.528 | -61.528 | 62.3291 | 0.064087 | -0.16479 | 0.086975 | 62.3566 | -61.5967 | -0.13733 | -0.12817 | -0.064087 | -0.13733 | -0.16937 | -0.20599 | -0.14191 | 0.073242 | 61.2259 | 61.4777 | 123.7198 | 123.761 | -0.064087 | 123.7473 | 61.4548 | -0.20599 | 123.761 | -0.064087 | 61.4548 | 123.7198 | 123.7473 | -124.0265 | -124.0952
117.7188 | 124.1776 | -61.4182 | 62.5168 | 0.15892 | 0.0096151 | 0.0095682 | 0.0037746 | 0.067298 | -0.0011877 | 0.068795 | -61.5326 | 62.4481 | -61.5417 | -61.6287 | 62.2284 | -0.036621 | -0.045776 | -0.041199 | 62.4115 | -61.6379 | -0.1236 | -0.068665 | -0.11444 | -0.21057 | -0.28839 | -0.21973 | -0.10529 | 0.009155 | 61.3724 | 61.377 | 123.6465 | 123.8663 | -0.11444 | 123.8297 | 61.3815 | -0.21973 | 123.8663 | -0.11444 | 61.3815 | 123.6465 | 123.8297 | -124.0585 | -124.1547
118.7188 | 124.2645 | -61.3724 | 62.4939 | 0.18944 | 0.0059835 | 0.0087138 | 0.00057044 | 0.069861 | -0.00054693 | 0.068795 | -61.4731 | 62.4023 | -61.5189 | -61.5234 | 62.3337 | 0.036621 | -0.41199 | 0.30212 | 62.3474 | -61.5784 | -0.14648 | -0.091552 | -0.10071 | -0.15106 | -0.16022 | -0.20599 | -0.14648 | 0.045777 | 60.9604 | 61.6745 | 123.7061 | 123.7747 | -0.10071 | 123.7198 | 61.409 | -0.20599 | 123.7747 | -0.10071 | 61.409 | 123.7061 | 123.7198 | -124.0128 | -124.0723
119.7188 | 124.2828 | -61.3861 | 62.4939 | 0.43358 | 0.0068381 | 0.014268 | 0.00035684 | 0.067298 | -0.0011877 | 0.070504 | -61.4227 | 62.3703 | -61.5143 | -61.5372 | 62.3566 | 0.07782 | -0.19684 | 0.091553 | 62.3657 | -61.5555 | -0.12817 | -0.1236 | -0.036621 | -0.15106 | -0.13733 | -0.16937 | -0.12817 | 0.091553 | 61.1893 | 61.4777 | 123.7427 | 123.7564 | -0.036621 | 123.7518 | 61.4639 | -0.16937 | 123.7564 | -0.036621 | 61.4639 | 123.7427 | 123.7518 | -124.0082 | -124.0494
120.7188 | 124.2371 | -61.4273 | 62.4939 | 0.15129 | 0.0081197 | 0.012559 | 0.0037746 | 0.067939 | -0.0041785 | 0.069222 | -61.5005 | 62.4023 | -61.5555 | -61.5875 | 62.2787 | 0.013733 | -0.1236 | 0.009155 | 62.3795 | -61.6013 | -0.12817 | -0.091552 | -0.073242 | -0.16022 | -0.21515 | -0.17395 | -0.11444 | 0.054932 | 61.3037 | 61.4365 | 123.7061 | 123.8297 | -0.073242 | 123.8068 | 61.441 | -0.17395 | 123.8297 | -0.073242 | 61.441 | 123.7061 | 123.8068 | -124.0494 | -124.0952
121.7188 | 124.2828 | -61.3953 | 62.4847 | 0.16655 | 0.0091879 | 0.012986 | 0.001852 | 0.069007 | -0.0026831 | 0.071359 | -61.4685 | 62.4115 | -61.5326 | -61.5326 | 62.3245 | 0.059509 | -0.16937 | 0.054932 | 62.384 | -61.5692 | -0.13733 | -0.073242 | -0.073242 | -0.13733 | -0.16022 | -0.17395 | -0.10071 | 0.064087 | 61.2259 | 61.4502 | 123.7198 | 123.8068 | -0.073242 | 123.7793 | 61.4548 | -0.17395 | 123.8068 | -0.073242 | 61.4548 | 123.7198 | 123.7793 | -124.0173 | -124.054
122.7188 | 124.2279 | -61.409 | 62.4802 | 0.18944 | 0.0096151 | 0.013413 | 0.0014248 | 0.067084 | -0.0020421 | 0.070291 | -61.5189 | 62.4481 | -61.5372 | -61.5875 | 62.2879 | 0.018311 | -0.13733 | 0.013733 | 62.3795 | -61.6196 | -0.12817 | -0.032044 | -0.10986 | -0.17853 | -0.19226 | -0.21057 | -0.10071 | 0.01831 | 61.2717 | 61.4227 | 123.6969 | 123.8571 | -0.10986 | 123.7885 | 61.4273 | -0.21057 | 123.8571 | -0.10986 | 61.4273 | 123.6969 | 123.7885 | -124.0173 | -124.0997
123.7188 | 124.2828 | -61.377 | 62.5031 | 0.11314 | 0.0085471 | 0.014482 | 0.0014248 | 0.06922 | 0.00030767 | 0.069222 | -61.4685 | 62.4023 | -61.5234 | -61.5417 | 62.3245 | 0.059509 | -0.15564 | 0.082397 | 62.384 | -61.5692 | -0.14648 | -0.10071 | -0.091553 | -0.16479 | -0.17853 | -0.19226 | -0.11902 | 0.054931 | 61.2213 | 61.4594 | 123.7015 | 123.7793 | -0.091553 | 123.761 | 61.4365 | -0.19226 | 123.7793 | -0.091553 | 61.4365 | 123.7015 | 123.761 | -124.0265 | -124.0723
124.7188 | 124.1547 | -61.4456 | 62.5214 | 0.03685 | 0.0083333 | 0.011704 | 0.0031338 | 0.068366 | -0.0016149 | 0.070718 | -61.496 | 62.4527 | -61.528 | -61.615 | 62.2696 | 0.004578 | 0.032043 | 0.009155 | 62.4161 | -61.6562 | -0.082397 | -0.068664 | -0.050354 | -0.16937 | -0.25177 | -0.21057 | -0.10529 | 0.032043 | 61.4777 | 61.4548 | 123.7152 | 123.8983 | -0.050354 | 123.8617 | 61.4502 | -0.21057 | 123.8983 | -0.050354 | 61.4502 | 123.7152 | 123.8617 | -124.0494 | -124.1776
125.7188 | 124.1592 | -61.4273 | 62.5397 | -0.069961 | 0.01047 | 0.0089274 | 0.0029202 | 0.069007 | -0.00033333 | 0.068582 | -61.4685 | 62.471 | -61.5189 | -61.5967 | 62.2787 | 0.032043 | 0.027466 | 0.045776 | 62.4527 | -61.6241 | -0.091553 | -0.068665 | -0.041199 | -0.16937 | -0.26093 | -0.19684 | -0.086975 | 0.050354 | 61.4548 | 61.4731 | 123.7061 | 123.8983 | -0.041199 | 123.88 | 61.4594 | -0.19684 | 123.8983 | -0.041199 | 61.4594 | 123.7061 | 123.88 | -124.0585 | -124.1638
126.7188 | 124.2966 | -61.3953 | 62.4893 | -1.8629 | 0.0064107 | 0.016404 | -0.0011386 | 0.069648 | -0.0037511 | 0.069009 | -61.4319 | 62.3886 | -61.5005 | -61.5509 | 62.3154 | 0.068665 | -0.16937 | 0.091553 | 62.3703 | -61.5692 | -0.10529 | -0.10071 | -0.036621 | -0.15564 | -0.17395 | -0.17395 | -0.11902 | 0.068664 | 61.2259 | 61.4868 | 123.7106 | 123.7839 | -0.036621 | 123.7656 | 61.4639 | -0.17395 | 123.7839 | -0.036621 | 61.4639 | 123.7106 | 123.7656 | -123.9899 | -124.0585
127.7188 | 124.1776 | -61.441 | 62.5351 | 0.029221 | 0.0091879 | 0.011704 | 0.0029202 | 0.067511 | -0.0016149 | 0.070291 | -61.5143 | 62.4847 | -61.5417 | -61.6104 | 62.2879 | 0.022888 | 0.032043 | 0.018311 | 62.4527 | -61.6241 | -0.10071 | -0.050354 | -0.073242 | -0.16937 | -0.24719 | -0.18311 | -0.082397 | 0.027466 | 61.4731 | 61.4594 | 123.7289 | 123.9258 | -0.073242 | 123.8937 | 61.4639 | -0.18311 | 123.9258 | -0.073242 | 61.4639 | 123.7289 | 123.8937 | -124.0768 | -124.1592
128.7188 | 124.1409 | -61.4273 | 62.5397 | 0.23521 | 0.010897 | 0.014054 | -7.0562e-05 | 0.067511 | -0.0020421 | 0.070504 | -61.7889 | 62.4161 | -61.5784 | -61.6837 | 62.2513 | 0 | 0 | -0.050354 | 62.439 | -61.6425 | -0.15106 | -0.1236 | -0.36163 | -0.25635 | -0.28839 | -0.21515 | -0.10071 | -0.21057 | 61.4273 | 61.377 | 123.6786 | 123.8434 | -0.36163 | 123.8663 | 61.4273 | -0.21515 | 123.8434 | -0.36163 | 61.4273 | 123.6786 | 123.8663 | -124.118 | -124.1821
129.7188 | 123.9624 | -61.4777 | 62.4802 | 0.097885 | 0.0064107 | 0.011918 | 0.0050564 | 0.069861 | -0.0022559 | 0.06965 | -61.528 | 62.5168 | -61.5601 | -61.6699 | 62.2147 | -0.050354 | 0.032043 | -0.045776 | 62.4573 | -61.6287 | -0.082398 | 0.036621 | -0.050354 | -0.19226 | -0.2655 | -0.15106 | -0.022889 | 0.032044 | 61.5097 | 61.4319 | 123.6923 | 123.9944 | -0.050354 | 123.9349 | 61.4273 | -0.15106 | 123.9944 | -0.050354 | 61.4273 | 123.6923 | 123.9349 | -124.0402 | -124.1089
130.7188 | 124.1364 | -61.4182 | 62.5305 | 0.082626 | 0.0085471 | 0.011491 | 0.00057044 | 0.070716 | -0.00054693 | 0.068154 | -61.5189 | 62.5168 | -61.528 | -61.6333 | 62.233 | -0.022888 | 0.050354 | 0 | 62.4435 | -61.6196 | -0.10986 | -0.013733 | -0.10071 | -0.21515 | -0.29755 | -0.20142 | -0.086976 | 0.009155 | 61.4685 | 61.4182 | 123.6511 | 123.9349 | -0.10071 | 123.8617 | 61.3953 | -0.20142 | 123.9349 | -0.10071 | 61.3953 | 123.6511 | 123.8617 | -124.0585 | -124.1501
131.7188 | 124.2233 | -61.4182 | 62.5168 | -0.016556 | 0.0055563 | 0.011064 | -0.004343 | 0.069861 | 0.0018031 | 0.070291 | -61.5189 | 62.4115 | -61.5189 | -61.5967 | 62.3199 | 0.086975 | -0.068665 | 0.11444 | 62.4344 | -61.5509 | -0.10071 | -0.10529 | -0.10071 | -0.17853 | -0.19684 | -0.13275 | -0.082398 | 0 | 61.3495 | 61.5326 | 123.7381 | 123.8297 | -0.10071 | 123.8525 | 61.5051 | -0.13275 | 123.8297 | -0.10071 | 61.5051 | 123.7381 | 123.8525 | -124.0356 | -124.0677
132.7188 | 124.1821 | -61.3953 | 62.5671 | 0.013962 | 0.0079061 | 0.012773 | 0.0027066 | 0.06687 | -0.00054693 | 0.067513 | -61.6928 | 62.4527 | -61.5417 | -61.5601 | 62.3245 | 0.11444 | 0.032043 | 0.11902 | 62.4298 | -61.6196 | -0.14648 | -0.11444 | -0.29755 | -0.1648 | -0.24262 | -0.2243 | -0.13733 | -0.15106 | 61.4273 | 61.5143 | 123.7198 | 123.848 | -0.29755 | 123.8251 | 61.5097 | -0.2243 | 123.848 | -0.29755 | 61.5097 | 123.7198 | 123.8251 | -124.1089 | -124.1867
133.7188 | 124.1547 | -61.4319 | 62.5442 | -0.024185 | 0.0053427 | 0.012345 | 0.00057044 | 0.070075 | -0.00011953 | 0.068368 | -61.4639 | 62.4939 | -61.5097 | -61.5829 | 62.2925 | 0.082397 | 0.032043 | 0.086975 | 62.4573 | -61.6104 | -0.07782 | -0.050354 | -0.032043 | -0.15106 | -0.25177 | -0.17853 | -0.086975 | 0.045777 | 61.4639 | 61.5189 | 123.7244 | 123.9258 | -0.032043 | 123.8892 | 61.5143 | -0.17853 | 123.9258 | -0.032043 | 61.5143 | 123.7244 | 123.8892 | -124.054 | -124.1547
134.7188 | 124.2737 | -61.3815 | 62.4893 | 0.27336 | 0.0068381 | 0.0076456 | -0.001566 | 0.069007 | -0.00076053 | 0.069863 | -61.4685 | 62.3978 | -61.528 | -61.5646 | 62.3199 | 0.073242 | -0.16022 | 0.082397 | 62.4069 | -61.5738 | -0.14648 | -0.091553 | -0.086975 | -0.1831 | -0.16937 | -0.19226 | -0.082398 | 0.059509 | 61.2213 | 61.4639 | 123.7015 | 123.7793 | -0.086975 | 123.7885 | 61.4548 | -0.19226 | 123.7793 | -0.086975 | 61.4548 | 123.7015 | 123.7885 | -124.0173 | -124.0631
135.7188 | 124.1592 | -61.4227 | 62.5351 | 0.052109 | 0.0089743 | 0.014054 | 0.003561 | 0.071143 | -0.00033333 | 0.06965 | -61.496 | 62.471 | -61.5509 | -61.6333 | 62.2421 | 0.009155 | 0.036621 | 0.013733 | 62.4115 | -61.6241 | -0.12817 | -0.064087 | -0.073243 | -0.21057 | -0.29297 | -0.20142 | -0.1236 | 0.054931 | 61.4593 | 61.4365 | 123.6649 | 123.8937 | -0.073243 | 123.8342 | 61.4319 | -0.20142 | 123.8937 | -0.073243 | 61.4319 | 123.6649 | 123.8342 | -124.086 | -124.1592
136.7188 | 124.1638 | -61.4731 | 62.5351 | 0.013962 | 0.0081197 | 0.013413 | 0.0016384 | 0.070716 | -0.0016149 | 0.070718 | -61.5509 | 62.4664 | -61.5555 | -61.6608 | 62.2238 | -0.036621 | 0 | -0.041199 | 62.4481 | -61.6241 | -0.082398 | -0.068664 | -0.07782 | -0.18768 | -0.31128 | -0.15106 | -0.086975 | 0.004578 | 61.4731 | 61.4319 | 123.6969 | 123.9395 | -0.07782 | 123.9212 | 61.4365 | -0.15106 | 123.9395 | -0.07782 | 61.4365 | 123.6969 | 123.9212 | -124.0906 | -124.1592
137.7188 | 124.1821 | -61.3998 | 62.5534 | -0.19203 | 0.0079061 | 0.007432 | 0.00057044 | 0.069007 | -0.0018285 | 0.070077 | -61.5097 | 62.5031 | -61.5326 | -61.5875 | 62.2696 | 0.073242 | 0.11902 | 0.1236 | 62.4664 | -61.6058 | -0.13275 | -0.050354 | -0.10986 | -0.18768 | -0.28381 | -0.20599 | -0.086975 | 0.022888 | 61.5189 | 61.5234 | 123.6694 | 123.9029 | -0.10986 | 123.8663 | 61.4731 | -0.20599 | 123.9029 | -0.10986 | 61.4731 | 123.6694 | 123.8663 | -124.086 | -124.1592
138.7188 | 124.1776 | -61.4136 | 62.5397 | 0.6472 | 0.010042 | 0.013413 | 0.0027066 | 0.068366 | -0.0014013 | 0.069222 | -61.4182 | 62.4802 | -61.5326 | -61.5555 | 62.3199 | 0.068665 | 0.032043 | 0.10986 | 62.439 | -61.5829 | -0.11902 | -0.059509 | -0.004578 | -0.14191 | -0.21973 | -0.16937 | -0.10071 | 0.11444 | 61.4456 | 61.5234 | 123.7335 | 123.8937 | -0.004578 | 123.8525 | 61.4822 | -0.16937 | 123.8937 | -0.004578 | 61.4822 | 123.7335 | 123.8525 | -124.0723 | -124.1226
139.7188 | 124.1959 | -61.4182 | 62.5626 | 0.013962 | 0.010256 | 0.014268 | -0.00028416 | 0.069434 | -0.0028967 | 0.067727 | -61.4548 | 62.4802 | -61.5372 | -61.5601 | 62.2833 | 0.16479 | -0.23346 | 0.073242 | 62.4252 | -61.6333 | -0.11902 | -0.082397 | -0.036621 | -0.14191 | -0.27924 | -0.21515 | -0.13733 | 0.082397 | 61.1847 | 61.4914 | 123.7015 | 123.8983 | -0.036621 | 123.8434 | 61.5829 | -0.21515 | 123.8983 | -0.036621 | 61.5829 | 123.7015 | 123.8434 | -124.0997 | -124.1959
140.7188 | 124.1089 | -61.4273 | 62.5626 | -0.14626 | 0.0064107 | 0.0082864 | -0.00092496 | 0.069861 | -0.0011877 | 0.070718 | -61.528 | 62.4481 | -61.5417 | -61.615 | 62.2742 | 0.064087 | 0.14191 | 0.086975 | 62.4985 | -61.5875 | -0.11444 | -0.11444 | -0.10071 | -0.18768 | -0.28839 | -0.16022 | -0.064087 | 0.013733 | 61.5692 | 61.5143 | 123.7015 | 123.8754 | -0.10071 | 123.9258 | 61.4914 | -0.16022 | 123.8754 | -0.10071 | 61.4914 | 123.7015 | 123.9258 | -124.1043 | -124.1501
141.7188 | 124.1501 | -61.4502 | 62.5442 | 0.15892 | 0.0087607 | 0.0097818 | 0.0020656 | 0.070929 | -0.0031103 | 0.069009 | -61.5646 | 62.4481 | -61.5738 | -61.5097 | 62.1368 | -0.09613 | 0.16479 | -0.036621 | 62.4802 | -61.6241 | -0.1236 | -0.09613 | -0.11444 | -0.05951 | -0.40741 | -0.17395 | -0.064086 | 0.009156 | 61.615 | 61.4136 | 123.587 | 123.8983 | -0.11444 | 123.9304 | 61.3541 | -0.17395 | 123.8983 | -0.11444 | 61.3541 | 123.587 | 123.9304 | -124.118 | -124.1684
142.7188 | 124.1455 | -61.4319 | 62.5626 | -0.21492 | 0.01047 | 0.013841 | -0.0013522 | 0.068793 | -0.00054693 | 0.069436 | -61.5143 | 62.471 | -61.5417 | -61.6241 | 62.2742 | 0.068665 | 0.12817 | 0.086975 | 62.4802 | -61.5875 | -0.10986 | -0.091553 | -0.082397 | -0.19226 | -0.28839 | -0.15564 | -0.082397 | 0.027466 | 61.5601 | 61.5189 | 123.7061 | 123.9029 | -0.082397 | 123.912 | 61.5006 | -0.15564 | 123.9029 | -0.082397 | 61.5006 | 123.7061 | 123.912 | -124.1043 | -124.1501
143.7188 | 124.1776 | -61.4182 | 62.5763 | -0.15388 | 0.0053427 | 0.0093546 | -7.0562e-05 | 0.068152 | -0.0022559 | 0.071145 | -61.5143 | 62.4756 | -61.5417 | -61.6058 | 62.2833 | 0.082397 | 0.11902 | 0.09613 | 62.4893 | -61.5875 | -0.1236 | -0.10071 | -0.09613 | -0.18768 | -0.29297 | -0.16937 | -0.086975 | 0.027466 | 61.5372 | 61.5143 | 123.7015 | 123.8937 | -0.09613 | 123.9075 | 61.5005 | -0.16937 | 123.8937 | -0.09613 | 61.5005 | 123.7015 | 123.9075 | -124.118 | -124.1638
144.7188 | 124.2508 | -61.3907 | 62.4939 | 0.15892 | 0.0061971 | 0.011064 | -0.0011386 | 0.067725 | -0.00054693 | 0.068368 | -61.4914 | 62.4252 | -61.5234 | -61.5967 | 62.3062 | 0.041199 | -0.12817 | 0.036621 | 62.4023 | -61.6013 | -0.13275 | -0.068664 | -0.10071 | -0.20599 | -0.18768 | -0.21057 | -0.091552 | 0.032043 | 61.2625 | 61.4273 | 123.6969 | 123.8159 | -0.10071 | 123.793 | 61.4319 | -0.21057 | 123.8159 | -0.10071 | 61.4319 | 123.6969 | 123.793 | -124.0173 | -124.0952
145.7188 | 124.2783 | -61.3815 | 62.5214 | -0.14626 | 0.0047019 | 0.011064 | -0.0030612 | 0.069861 | -0.0016149 | 0.068795 | -61.4044 | 62.384 | -61.4914 | -61.5555 | 62.2559 | 0.13733 | 0 | 0.18768 | 62.4161 | -61.5555 | -0.10986 | -0.13733 | -0.022888 | -0.17395 | -0.2655 | -0.17395 | -0.10529 | 0.086975 | 61.3815 | 61.5692 | 123.6374 | 123.7656 | -0.022888 | 123.7976 | 61.5189 | -0.17395 | 123.7656 | -0.022888 | 61.5189 | 123.6374 | 123.7976 | -124.0128 | -124.0768
146.7188 | 124.1821 | -61.4136 | 62.5671 | -0.26833 | 0.0057699 | 0.010636 | 0.00099764 | 0.065375 | -0.00076053 | 0.069436 | -61.5326 | 62.4207 | -61.5372 | -61.6287 | 62.2513 | 0.054932 | 0.14648 | 0.086975 | 62.4573 | -61.5738 | -0.1236 | -0.14648 | -0.11902 | -0.21515 | -0.31586 | -0.16022 | -0.10986 | 0.004577 | 61.5601 | 61.5005 | 123.6649 | 123.8342 | -0.11902 | 123.8708 | 61.4685 | -0.16022 | 123.8342 | -0.11902 | 61.4685 | 123.6649 | 123.8708 | -124.1043 | -124.1409
147.7188 | 124.1913 | -61.377 | 62.5809 | -0.27596 | 0.0061971 | 0.009141 | -0.0030612 | 0.066443 | -0.0011877 | 0.068368 | -61.4868 | 62.384 | -61.5189 | -61.5646 | 62.3062 | 0.10071 | 0.11444 | 0.14648 | 62.471 | -61.5601 | -0.14191 | -0.19684 | -0.10986 | -0.18768 | -0.27466 | -0.18311 | -0.10986 | 0.032044 | 61.4914 | 61.5234 | 123.6832 | 123.761 | -0.10986 | 123.848 | 61.4777 | -0.18311 | 123.761 | -0.10986 | 61.4777 | 123.6832 | 123.848 | -124.0997 | -124.1409
148.7188 | 124.2325 | -61.3586 | 62.5809 | -0.16914 | 0.0044881 | 0.012345 | -0.0037022 | 0.064734 | -0.00097413 | 0.069863 | -61.4685 | 62.3932 | -61.5005 | -61.5372 | 62.3383 | 0.16937 | 0.027466 | 0.20142 | 62.4435 | -61.5417 | -0.14191 | -0.18768 | -0.10986 | -0.17853 | -0.24262 | -0.1831 | -0.13733 | 0.032043 | 61.3861 | 61.5601 | 123.6969 | 123.7518 | -0.10986 | 123.8022 | 61.528 | -0.1831 | 123.7518 | -0.10986 | 61.528 | 123.6969 | 123.8022 | -124.0814 | -124.1226
149.7188 | 124.1684 | -61.441 | 62.5626 | -0.19966 | 0.0081197 | 0.0132 | -0.00071136 | 0.067298 | -0.00054693 | 0.068795 | -61.5189 | 62.4893 | -61.528 | -61.6196 | 62.265 | 0.059509 | 0.12817 | 0.086975 | 62.4985 | -61.6104 | -0.086975 | -0.073242 | -0.07782 | -0.17853 | -0.29755 | -0.16937 | -0.064087 | 0.009155 | 61.5692 | 61.528 | 123.7061 | 123.9304 | -0.07782 | 123.9395 | 61.5005 | -0.16937 | 123.9304 | -0.07782 | 61.5005 | 123.7061 | 123.9395 | -124.0906 | -124.173
150.7188 | 124.2737 | -61.377 | 62.5442 | -0.16914 | 0.0049155 | 0.0059366 | -0.0073338 | 0.065802 | 0.0026575 | 0.069009 | -61.4136 | 62.352 | -61.4868 | -61.528 | 62.4573 | 0.1831 | -0.10986 | 0.26093 | 62.3978 | -61.5417 | -0.10986 | -0.19226 | -0.036621 | -0.15106 | -0.086975 | -0.16479 | -0.14648 | 0.073242 | 61.2671 | 61.6379 | 123.8342 | 123.7289 | -0.036621 | 123.7747 | 61.5601 | -0.16479 | 123.7289 | -0.036621 | 61.5601 | 123.8342 | 123.7747 | -124.0311 | -124.086
151.7188 | 124.2096 | -61.409 | 62.5717 | -0.16151 | 0.0091879 | 0.011704 | 0.0048428 | 0.066657 | -0.0031103 | 0.068154 | -61.5051 | 62.4298 | -61.5372 | -61.5692 | 62.2971 | 0.07782 | 0.086975 | 0.11902 | 62.4527 | -61.5646 | -0.12817 | -0.14191 | -0.09613 | -0.16022 | -0.27466 | -0.15564 | -0.11902 | 0.032043 | 61.496 | 61.528 | 123.7061 | 123.8388 | -0.09613 | 123.8617 | 61.4868 | -0.15564 | 123.8388 | -0.09613 | 61.4868 | 123.7061 | 123.8617 | -124.1089 | -124.1364
152.7188 | 124.3698 | -61.3632 | 62.5305 | 0.052109 | 0.0059835 | 0.0089274 | -0.0034886 | 0.064521 | -0.0028967 | 0.06965 | -61.5051 | 62.3566 | -61.5463 | -61.5784 | 62.2925 | 0.050354 | -0.073242 | 0.086975 | 62.4252 | -61.5784 | -0.18311 | -0.17395 | -0.14191 | -0.21515 | -0.23804 | -0.21515 | -0.10529 | 0.041199 | 61.29 | 61.4502 | 123.6557 | 123.7198 | -0.14191 | 123.7885 | 61.4136 | -0.21515 | 123.7198 | -0.14191 | 61.4136 | 123.6557 | 123.7885 | -124.0768 | -124.1089
153.7188 | 124.2645 | -61.409 | 62.4985 | 0.15892 | 0.0059835 | 0.012345 | 0.0022794 | 0.06922 | -0.0022559 | 0.069863 | -61.4639 | 62.3611 | -61.5234 | -61.7203 | 62.1643 | 0.11902 | -0.064087 | 0.068665 | 62.4161 | -61.5738 | -0.11444 | -0.13733 | -0.054931 | -0.31128 | -0.33417 | -0.16479 | -0.082397 | 0.059509 | 61.3449 | 61.4777 | 123.5733 | 123.7701 | -0.054931 | 123.8251 | 61.528 | -0.16479 | 123.7701 | -0.054931 | 61.528 | 123.5733 | 123.8251 | -124.0219 | -124.0723
154.7188 | 124.2462 | -61.3724 | 62.5259 | -0.24544 | 0.0074789 | 0.0099954 | -0.0034886 | 0.064948 | -0.0018285 | 0.068368 | -61.4227 | 62.4115 | -61.4914 | -61.5005 | 62.3749 | 0.16022 | -0.022888 | 0.21973 | 62.4115 | -61.5829 | -0.11902 | -0.11444 | -0.050354 | -0.12817 | -0.15106 | -0.21057 | -0.11444 | 0.068665 | 61.3495 | 61.5921 | 123.7473 | 123.7839 | -0.050354 | 123.7839 | 61.5326 | -0.21057 | 123.7839 | -0.050354 | 61.5326 | 123.7473 | 123.7839 | -124.0173 | -124.1089
155.7188 | 124.2416 | -61.3861 | 62.5305 | 0.013962 | 0.0055563 | 0.0085 | -0.0041294 | 0.065375 | -0.0018285 | 0.067941 | -61.5005 | 62.3932 | -61.5326 | -61.5829 | 62.3108 | 0.082397 | -0.082397 | 0.11444 | 62.4161 | -61.5646 | -0.14648 | -0.13733 | -0.11444 | -0.19684 | -0.21973 | -0.17853 | -0.11444 | 0.032044 | 61.3037 | 61.5005 | 123.6969 | 123.7793 | -0.11444 | 123.8022 | 61.4685 | -0.17853 | 123.7793 | -0.11444 | 61.4685 | 123.6969 | 123.8022 | -124.0631 | -124.0952
156.7188 | 124.173 | -61.409 | 62.5626 | -0.0089264 | 0.0079061 | 0.012559 | 0.005911 | 0.06623 | -0.0016149 | 0.067941 | -61.4639 | 62.4069 | -61.5463 | -61.5646 | 62.2742 | 0.059509 | 0.022888 | 0.07782 | 62.4435 | -61.6104 | -0.13733 | -0.15564 | -0.054931 | -0.15564 | -0.28839 | -0.20142 | -0.11902 | 0.082398 | 61.4319 | 61.4868 | 123.6832 | 123.8159 | -0.054931 | 123.8525 | 61.4685 | -0.20142 | 123.8159 | -0.054931 | 61.4685 | 123.6832 | 123.8525 | -124.1089 | -124.173
157.7188 | 124.2416 | -61.3998 | 62.5259 | 0.17418 | 0.011111 | 0.010636 | -0.00071136 | 0.066657 | 9.4068e-05 | 0.069222 | -61.4731 | 62.3291 | -61.5372 | -61.5601 | 62.3108 | 0.050354 | -0.14648 | 0.073242 | 62.3886 | -61.5921 | -0.13733 | -0.19684 | -0.073242 | -0.16022 | -0.21515 | -0.19226 | -0.13733 | 0.064087 | 61.2534 | 61.4731 | 123.7106 | 123.7289 | -0.073242 | 123.7885 | 61.4502 | -0.19226 | 123.7289 | -0.073242 | 61.4502 | 123.7106 | 123.7885 | -124.0631 | -124.118
158.7188 | 124.2691 | -61.3815 | 62.5031 | 0.2047 | 0.0074789 | 0.0095682 | -7.0562e-05 | 0.066657 | -0.0026831 | 0.070931 | -61.4548 | 62.3611 | -61.5234 | -61.5463 | 62.3291 | 0.064087 | -0.17853 | 0.082397 | 62.3886 | -61.5738 | -0.14191 | -0.14191 | -0.073242 | -0.16479 | -0.17395 | -0.19226 | -0.11444 | 0.068664 | 61.203 | 61.4639 | 123.7106 | 123.7427 | -0.073242 | 123.7701 | 61.4456 | -0.19226 | 123.7427 | -0.073242 | 61.4456 | 123.7106 | 123.7701 | -124.0265 | -124.0768
159.7188 | 124.2462 | -61.377 | 62.5168 | 0.074997 | 0.0079061 | 0.0089274 | -0.004343 | 0.064521 | -0.0022559 | 0.069436 | -61.5189 | 62.3703 | -61.5326 | -61.5784 | 62.2925 | 0.068665 | -0.059509 | 0.10529 | 62.4023 | -61.5967 | -0.15564 | -0.14648 | -0.14191 | -0.20142 | -0.22431 | -0.21973 | -0.11444 | 0.013733 | 61.3174 | 61.4822 | 123.6694 | 123.7473 | -0.14191 | 123.7793 | 61.4456 | -0.21973 | 123.7473 | -0.14191 | 61.4456 | 123.6694 | 123.7793 | -124.0494 | -124.1135
160.7188 | 124.1821 | -61.4227 | 62.5351 | 0.15129 | 0.0094015 | 0.011704 | 0.0033474 | 0.06687 | 9.4068e-05 | 0.069436 | -61.5234 | 62.4161 | -61.5417 | -61.5875 | 62.2513 | 0 | -0.11444 | 0.009155 | 62.3795 | -61.6104 | -0.11902 | -0.11902 | -0.10071 | -0.1648 | -0.28381 | -0.18768 | -0.15564 | 0.018311 | 61.3083 | 61.4319 | 123.674 | 123.8388 | -0.10071 | 123.8022 | 61.4227 | -0.18768 | 123.8388 | -0.10071 | 61.4227 | 123.674 | 123.8022 | -124.0768 | -124.1455
161.7188 | 124.2691 | -61.3907 | 62.4985 | -0.22255 | 0.0083333 | 0.011277 | 0.0022794 | 0.067939 | -0.00097413 | 0.070291 | -61.4594 | 62.3749 | -61.5005 | -61.528 | 62.3291 | 0.073242 | -0.17853 | 0.091553 | 62.3978 | -61.6013 | -0.10986 | -0.1236 | -0.068665 | -0.13733 | -0.16937 | -0.21057 | -0.10071 | 0.041198 | 61.2122 | 61.4822 | 123.7198 | 123.7656 | -0.068665 | 123.7885 | 61.4639 | -0.21057 | 123.7656 | -0.068665 | 61.4639 | 123.7198 | 123.7885 | -123.999 | -124.0997
162.7344 | 124.1501 | -61.4044 | 62.5763 | -0.2607 | 0.0074789 | 0.010423 | 0.00078404 | 0.066657 | -0.0014013 | 0.069863 | -61.4914 | 62.439 | -61.5372 | -61.5829 | 62.2604 | 0.068665 | 0.13275 | 0.10529 | 62.4481 | -61.6104 | -0.13275 | -0.13733 | -0.086975 | -0.17853 | -0.31586 | -0.20599 | -0.12817 | 0.045776 | 61.5372 | 61.5097 | 123.6649 | 123.8434 | -0.086975 | 123.8525 | 61.4731 | -0.20599 | 123.8434 | -0.086975 | 61.4731 | 123.6649 | 123.8525 | -124.1135 | -124.1867
163.7188 | 124.2599 | -61.3861 | 62.4802 | -0.11574 | 0.0064107 | 0.0082864 | 0.0012112 | 0.069648 | -0.0014013 | 0.068368 | -61.4594 | 62.3978 | -61.5051 | -61.5097 | 62.3245 | 0.068665 | -0.1831 | 0.086975 | 62.3932 | -61.5692 | -0.11902 | -0.082398 | -0.073243 | -0.1236 | -0.15564 | -0.18311 | -0.086976 | 0.045776 | 61.203 | 61.4731 | 123.7106 | 123.7839 | -0.073243 | 123.7793 | 61.4548 | -0.18311 | 123.7839 | -0.073243 | 61.4548 | 123.7106 | 123.7793 | -123.9853 | -124.0494
164.7188 | 124.2737 | -61.3724 | 62.4893 | 0.17418 | 0.0055563 | 0.011704 | 0.00078404 | 0.067084 | -0.00033333 | 0.069436 | -61.4502 | 62.3749 | -61.5417 | -61.5463 | 62.3291 | 0.064087 | -0.16479 | 0.09613 | 62.384 | -61.5784 | -0.16937 | -0.11444 | -0.07782 | -0.17395 | -0.16022 | -0.20599 | -0.10529 | 0.091553 | 61.2076 | 61.4685 | 123.7015 | 123.7473 | -0.07782 | 123.7564 | 61.4365 | -0.20599 | 123.7473 | -0.07782 | 61.4365 | 123.7015 | 123.7564 | -124.0311 | -124.0677
165.7188 | 124.1776 | -61.4456 | 62.5259 | 0.15892 | 0.010042 | 0.0097818 | 0.003561 | 0.066657 | -0.00076053 | 0.070291 | -61.5189 | 62.4527 | -61.5555 | -61.6196 | 62.2375 | -0.009155 | -0.068665 | -0.013733 | 62.4115 | -61.6425 | -0.10986 | -0.073242 | -0.073242 | -0.17395 | -0.28839 | -0.19684 | -0.11444 | 0.036621 | 61.377 | 61.4319 | 123.6832 | 123.8983 | -0.073242 | 123.8571 | 61.4365 | -0.19684 | 123.8983 | -0.073242 | 61.4365 | 123.6832 | 123.8571 | -124.0814 | -124.1684
166.7188 | 124.3286 | -61.3998 | 62.4985 | 0.14366 | 0.0064107 | 0.01085 | 0.0012112 | 0.066443 | -0.0016149 | 0.067727 | -61.4319 | 62.4115 | -61.5189 | -61.496 | 62.1643 | -0.14648 | 0.045776 | 0.16479 | 62.3795 | -61.5875 | -0.11902 | -0.086975 | -0.032044 | -0.096131 | -0.33417 | -0.18768 | -0.11902 | 0.086975 | 61.4456 | 61.5646 | 123.5641 | 123.8113 | -0.032044 | 123.7793 | 61.2534 | -0.18768 | 123.8113 | -0.032044 | 61.2534 | 123.5641 | 123.7793 | -124.0173 | -124.086
167.7188 | 124.2554 | -61.3724 | 62.4985 | -0.054703 | 0.0053427 | 0.010209 | -0.0019932 | 0.067084 | -0.0020421 | 0.067086 | -61.5005 | 62.3886 | -61.5326 | -61.5646 | 62.3199 | 0.068665 | -0.073242 | 0.09613 | 62.3932 | -61.5829 | -0.16022 | -0.10986 | -0.12817 | -0.19226 | -0.17853 | -0.21057 | -0.10529 | 0.032044 | 61.2991 | 61.4685 | 123.6923 | 123.761 | -0.12817 | 123.7656 | 61.441 | -0.21057 | 123.761 | -0.12817 | 61.441 | 123.6923 | 123.7656 | -124.0311 | -124.0814
168.7188 | 124.1455 | -61.4227 | 62.558 | 0.1284 | 0.0098287 | 0.012773 | 0.0022794 | 0.064734 | -0.00097413 | 0.068795 | -61.528 | 62.4527 | -61.5509 | -61.6379 | 62.4847 | -0.25635 | -0.19684 | 0.3067 | 62.3749 | -61.6379 | -0.12817 | -0.10529 | -0.10529 | -0.21515 | -0.073242 | -0.21515 | -0.1831 | 0.022888 | 61.2259 | 61.7294 | 123.9075 | 123.8754 | -0.10529 | 123.7976 | 61.1664 | -0.21515 | 123.8754 | -0.10529 | 61.1664 | 123.9075 | 123.7976 | -124.1089 | -124.1959
169.7188 | 124.2233 | -61.377 | 62.5397 | -0.15388 | 0.0053427 | 0.011064 | -0.0037022 | 0.067511 | -0.0043921 | 0.069863 | -61.4456 | 62.3932 | -61.5189 | -61.496 | 62.3657 | 0.16479 | -0.027466 | 0.21515 | 62.4161 | -61.5463 | -0.14191 | -0.14648 | -0.068665 | -0.11902 | -0.17395 | -0.16937 | -0.1236 | 0.073242 | 61.3495 | 61.5921 | 123.7427 | 123.7701 | -0.068665 | 123.793 | 61.5417 | -0.16937 | 123.7701 | -0.068665 | 61.5417 | 123.7427 | 123.793 | -124.0585 | -124.086
170.7188 | 124.1364 | -61.4273 | 62.5305 | 0.16655 | 0.0098287 | 0.011704 | 0.0048428 | 0.066657 | -0.00033333 | 0.069222 | -61.8759 | 62.4023 | -61.5738 | -61.6837 | 62.2101 | -0.004578 | 0.004578 | -0.059509 | 62.4207 | -61.6425 | -0.14648 | -0.12817 | -0.44861 | -0.25635 | -0.32044 | -0.21515 | -0.10986 | -0.30212 | 61.4319 | 61.3678 | 123.6374 | 123.8297 | -0.44861 | 123.848 | 61.4227 | -0.21515 | 123.8297 | -0.44861 | 61.4227 | 123.6374 | 123.848 | -124.1043 | -124.173
171.7188 | 124.086 | -61.4136 | 62.5534 | 0.1284 | 0.0096151 | 0.015977 | 0.0033474 | 0.067725 | -0.00054693 | 0.067941 | -61.5555 | 62.4847 | -61.5463 | -61.6516 | 62.233 | -0.018311 | -0.41657 | 0.14191 | 62.3978 | -61.647 | -0.13275 | -0.068665 | -0.14191 | -0.23804 | -0.32044 | -0.23346 | -0.15564 | -0.009155 | 60.997 | 61.5555 | 123.6465 | 123.8983 | -0.14191 | 123.8113 | 61.3953 | -0.23346 | 123.8983 | -0.14191 | 61.3953 | 123.6465 | 123.8113 | -124.0997 | -124.2004
172.7188 | 124.2188 | -61.409 | 62.5305 | -0.054703 | 0.0061971 | 0.011277 | -0.0079746 | 0.06623 | -0.0022559 | 0.071359 | -61.5051 | 62.3795 | -61.528 | -61.6425 | 62.3428 | 0.059509 | -0.054932 | 0.07782 | 62.3932 | -61.5829 | -0.11902 | -0.15106 | -0.09613 | -0.23346 | -0.18768 | -0.17395 | -0.13733 | 0.022888 | 61.3541 | 61.4868 | 123.7518 | 123.7885 | -0.09613 | 123.8022 | 61.4685 | -0.17395 | 123.7885 | -0.09613 | 61.4685 | 123.7518 | 123.8022 | -124.0585 | -124.1135
173.7188 | 124.1547 | -61.409 | 62.5488 | -0.0089264 | 0.0081197 | 0.014695 | 0.0054836 | 0.067084 | 9.4068e-05 | 0.069009 | -61.4731 | 62.4893 | -61.5234 | -61.5967 | 62.265 | 0.022888 | 0.022888 | 0.032043 | 62.4344 | -61.6425 | -0.11444 | -0.059509 | -0.064086 | -0.18768 | -0.28381 | -0.23346 | -0.11444 | 0.050354 | 61.4319 | 61.441 | 123.674 | 123.8983 | -0.064086 | 123.8434 | 61.4319 | -0.23346 | 123.8983 | -0.064086 | 61.4319 | 123.674 | 123.8434 | -124.0723 | -124.1913
174.7188 | 124.1501 | -61.4227 | 62.5259 | 0.03685 | 0.0079061 | 0.012986 | 0.0022794 | 0.071997 | 0.00030767 | 0.069436 | -61.496 | 62.4847 | -61.528 | -61.6287 | 62.2147 | -0.027466 | 0.018311 | -0.009155 | 62.4619 | -61.6425 | -0.10529 | -0.041199 | -0.073243 | -0.20599 | -0.31128 | -0.21973 | -0.064087 | 0.032043 | 61.441 | 61.4136 | 123.6374 | 123.9075 | -0.073243 | 123.8846 | 61.3953 | -0.21973 | 123.9075 | -0.073243 | 61.3953 | 123.6374 | 123.8846 | -124.054 | -124.1684
175.7188 | 124.1638 | -61.4182 | 62.5259 | 0.029221 | 0.010042 | 0.010209 | 0.0039882 | 0.068366 | -0.0018285 | 0.070291 | -61.4914 | 62.4939 | -61.5417 | -61.6333 | 62.2604 | -0.004578 | 0.036621 | -0.004578 | 62.4619 | -61.6013 | -0.1236 | -0.032044 | -0.073242 | -0.21515 | -0.2655 | -0.1831 | -0.064087 | 0.050354 | 61.4548 | 61.4136 | 123.6786 | 123.912 | -0.073242 | 123.88 | 61.4136 | -0.1831 | 123.912 | -0.073242 | 61.4136 | 123.6786 | 123.88 | -124.0677 | -124.1272
176.7188 | 124.1547 | -61.4502 | 62.5259 | 0.22758 | 0.0096151 | 0.01085 | 0.0012112 | 0.070288 | 0.0013757 | 0.068582 | -61.5234 | 62.4939 | -61.5509 | -61.6608 | 62.2238 | -0.041199 | 0 | -0.032043 | 62.4573 | -61.6287 | -0.10071 | -0.032044 | -0.073242 | -0.21057 | -0.30212 | -0.17853 | -0.068665 | 0.027466 | 61.4502 | 61.4182 | 123.674 | 123.9441 | -0.073242 | 123.9075 | 61.409 | -0.17853 | 123.9441 | -0.073242 | 61.409 | 123.674 | 123.9075 | -124.0768 | -124.1547
177.7188 | 124.1867 | -61.4365 | 62.4985 | 0.79979 | 0.0083333 | 0.010636 | 0.0022794 | 0.06922 | 0.00052127 | 0.070291 | -61.441 | 62.4893 | -61.5372 | -61.6608 | 62.2238 | -0.036621 | -0.009155 | -0.059509 | 62.4435 | -61.6333 | -0.10071 | -0.009155 | -0.004578 | -0.22431 | -0.27466 | -0.19684 | -0.054932 | 0.09613 | 61.4273 | 61.377 | 123.6603 | 123.9258 | -0.004578 | 123.88 | 61.3998 | -0.19684 | 123.9258 | -0.004578 | 61.3998 | 123.6603 | 123.88 | -124.0356 | -124.1318
178.7188 | 124.1409 | -61.4502 | 62.5488 | 0.15892 | 0.0083333 | 0.011704 | -0.0017796 | 0.069861 | -0.00033333 | 0.066659 | -61.3998 | 62.4664 | -61.5784 | -61.5601 | 62.2467 | -0.050354 | 0.036621 | 0.004578 | 62.4573 | -61.6241 | -0.12817 | -0.082397 | 0.050354 | -0.10986 | -0.30212 | -0.17395 | -0.091553 | 0.17853 | 61.4868 | 61.4548 | 123.6969 | 123.9166 | 0.050354 | 123.9075 | 61.3998 | -0.17395 | 123.9166 | 0.050354 | 61.3998 | 123.6969 | 123.9075 | -124.1272 | -124.173
179.7188 | 124.2645 | -61.4044 | 62.4619 | 0.23521 | 0.0083333 | 0.012559 | -0.0011386 | 0.067939 | 0.0011621 | 0.069436 | -61.4594 | 62.3795 | -61.5189 | -61.5829 | 62.3611 | 0.12817 | -0.21057 | 0.082397 | 62.3886 | -61.5555 | -0.11444 | -0.082397 | -0.054932 | -0.17853 | -0.10071 | -0.15106 | -0.073242 | 0.059509 | 61.1938 | 61.4868 | 123.7656 | 123.7839 | -0.054932 | 123.793 | 61.5326 | -0.15106 | 123.7839 | -0.054932 | 61.5326 | 123.7656 | 123.793 | -123.9807 | -124.0173
180.7188 | 124.1547 | -61.4182 | 62.5397 | -0.031814 | 0.0087607 | 0.014482 | 0.0022794 | 0.068152 | -0.00097413 | 0.071572 | -61.4822 | 62.4939 | -61.5189 | -61.6013 | 62.2467 | 0.022888 | 0.027466 | 0.027466 | 62.4298 | -61.6287 | -0.10071 | -0.045777 | -0.064087 | -0.1831 | -0.29297 | -0.21057 | -0.10986 | 0.036621 | 61.4456 | 61.4456 | 123.6649 | 123.912 | -0.064087 | 123.848 | 61.441 | -0.21057 | 123.912 | -0.064087 | 61.441 | 123.6649 | 123.848 | -124.0585 | -124.1684
181.7188 | 124.1409 | -61.4227 | 62.5305 | 0.082626 | 0.0081197 | 0.013413 | 0.00035684 | 0.068152 | -0.0018285 | 0.070504 | -61.5097 | 62.4802 | -61.5326 | -61.647 | 62.2284 | -0.022888 | 0.041199 | -0.022888 | 62.4664 | -61.6333 | -0.10986 | -0.050354 | -0.086976 | -0.22431 | -0.30212 | -0.21057 | -0.064087 | 0.022888 | 61.4639 | 61.3998 | 123.6511 | 123.9029 | -0.086976 | 123.8892 | 61.3998 | -0.21057 | 123.9029 | -0.086976 | 61.3998 | 123.6511 | 123.8892 | -124.0631 | -124.1638
182.7188 | 124.1226 | -61.4227 | 62.5351 | 0.052109 | 0.0085471 | 0.014054 | 0.00078404 | 0.069648 | -0.0028967 | 0.070504 | -61.5097 | 62.4847 | -61.5463 | -61.6379 | 62.2467 | 0 | 0.027466 | 0.013733 | 62.4619 | -61.6287 | -0.1236 | -0.050354 | -0.086976 | -0.21515 | -0.28839 | -0.20599 | -0.073242 | 0.036621 | 61.4502 | 61.4365 | 123.6694 | 123.9075 | -0.086976 | 123.8846 | 61.4227 | -0.20599 | 123.9075 | -0.086976 | 61.4227 | 123.6694 | 123.8846 | -124.0814 | -124.1638
183.7188 | 124.1455 | -61.4456 | 62.5397 | 0.13603 | 0.0072653 | 0.012132 | 0.0016384 | 0.067939 | 9.4068e-05 | 0.069436 | -61.5326 | 62.471 | -61.5601 | -61.6699 | 62.2284 | -0.022888 | -0.004578 | -0.027466 | 62.4435 | -61.6562 | -0.11444 | -0.068665 | -0.086975 | -0.2243 | -0.31128 | -0.21057 | -0.096131 | 0.027466 | 61.441 | 61.4182 | 123.674 | 123.9166 | -0.086975 | 123.8892 | 61.4227 | -0.21057 | 123.9166 | -0.086975 | 61.4227 | 123.674 | 123.8892 | -124.0997 | -124.1959
184.7188 | 124.205 | -61.409 | 62.5031 | 0.17418 | 0.0089743 | 0.012345 | -0.0011386 | 0.070502 | -0.00097413 | 0.070931 | -61.5372 | 62.4802 | -61.5372 | -61.6562 | 62.2467 | -0.013733 | -0.059509 | -0.009155 | 62.4207 | -61.6379 | -0.12817 | -0.022888 | -0.12817 | -0.24719 | -0.25635 | -0.22888 | -0.082398 | 0 | 61.3495 | 61.3998 | 123.6557 | 123.8892 | -0.12817 | 123.8297 | 61.3953 | -0.22888 | 123.8892 | -0.12817 | 61.3953 | 123.6557 | 123.8297 | -124.0402 | -124.1409
185.7188 | 124.2004 | -61.409 | 62.5351 | -0.047073 | 0.0089743 | 0.012559 | 0.0020656 | 0.068793 | -0.00097413 | 0.069436 | -61.4685 | 62.4985 | -61.528 | -61.5738 | 62.2787 | 0.059509 | 0.032043 | 0.07782 | 62.4619 | -61.6196 | -0.11902 | -0.036621 | -0.059509 | -0.16479 | -0.25635 | -0.21057 | -0.073242 | 0.059509 | 61.441 | 61.4868 | 123.6877 | 123.9075 | -0.059509 | 123.8708 | 61.4685 | -0.21057 | 123.9075 | -0.059509 | 61.4685 | 123.6877 | 123.8708 | -124.0631 | -124.1547
186.7188 | 124.1776 | -61.409 | 62.5397 | 0.36491 | 0.0085471 | 0.012345 | 0.00057044 | 0.070075 | -0.00097413 | 0.068368 | -61.4136 | 62.4985 | -61.528 | -61.5555 | 62.3062 | 0.07782 | 0.018311 | 0.09613 | 62.4527 | -61.6196 | -0.11902 | -0.041199 | -0.004577 | -0.14648 | -0.23346 | -0.21057 | -0.086975 | 0.11444 | 61.4273 | 61.5051 | 123.7152 | 123.9075 | -0.004577 | 123.8617 | 61.4868 | -0.21057 | 123.9075 | -0.004577 | 61.4868 | 123.7152 | 123.8617 | -124.0677 | -124.1592
187.7188 | 124.1959 | -61.4182 | 62.5534 | -0.17677 | 0.0091879 | 0.012345 | -0.00092496 | 0.068579 | -0.0024695 | 0.069436 | -61.4868 | 62.5214 | -61.5601 | -61.5829 | 62.2925 | 0.086975 | 0.10986 | 0.1236 | 62.4619 | -61.6013 | -0.14191 | -0.032044 | -0.068664 | -0.16479 | -0.26093 | -0.1831 | -0.091553 | 0.073243 | 61.528 | 61.5417 | 123.7106 | 123.9395 | -0.068664 | 123.88 | 61.5051 | -0.1831 | 123.9395 | -0.068664 | 61.5051 | 123.7106 | 123.88 | -124.1135 | -124.1547
188.7188 | 124.1547 | -61.3953 | 62.5397 | -0.20729 | 0.0066245 | 0.0099954 | 0.00078404 | 0.067725 | 0.00094847 | 0.070931 | -61.5097 | 62.5214 | -61.5463 | -61.6104 | 62.265 | 0.068665 | 0.13275 | 0.09613 | 62.4664 | -61.5967 | -0.15106 | -0.018311 | -0.11444 | -0.21515 | -0.27466 | -0.20142 | -0.073242 | 0.036621 | 61.528 | 61.4914 | 123.6603 | 123.9166 | -0.11444 | 123.8617 | 61.4639 | -0.20142 | 123.9166 | -0.11444 | 61.4639 | 123.6603 | 123.8617 | -124.086 | -124.1364
189.7188 | 124.118 | -61.4365 | 62.5259 | 2.524 | 0.0079061 | 0.0095682 | 0.001852 | 0.069007 | -0.00033333 | 0.069222 | -61.6882 | 62.4481 | -61.5784 | -61.6745 | 62.2513 | 0.009155 | -0.009155 | -0.045776 | 62.4435 | -61.6425 | -0.14191 | -0.07782 | -0.25177 | -0.23804 | -0.27466 | -0.20599 | -0.082398 | -0.10986 | 61.4273 | 61.3907 | 123.6877 | 123.8846 | -0.25177 | 123.88 | 61.4456 | -0.20599 | 123.8846 | -0.25177 | 61.4456 | 123.6877 | 123.88 | -124.1043 | -124.1684
190.7188 | 124.1821 | -61.409 | 62.558 | -0.16151 | 0.0083333 | 0.0089274 | 0.00057044 | 0.069861 | -0.00076053 | 0.06965 | -61.4639 | 62.5122 | -61.5463 | -61.5646 | 62.3016 | 0.07782 | 0.054932 | 0.11444 | 62.4573 | -61.6104 | -0.13733 | -0.045776 | -0.054931 | -0.15564 | -0.25635 | -0.20142 | -0.10071 | 0.082398 | 61.4639 | 61.5234 | 123.7106 | 123.9212 | -0.054931 | 123.8663 | 61.4868 | -0.20142 | 123.9212 | -0.054931 | 61.4868 | 123.7106 | 123.8663 | -124.1043 | -124.1684
191.7188 | 124.1867 | -61.3953 | 62.558 | -0.11574 | 0.0051291 | 0.01085 | -0.00049776 | 0.068366 | -0.0014013 | 0.069009 | -61.4914 | 62.4939 | -61.5234 | -61.5784 | 62.3062 | 0.086975 | 0.09613 | 0.1236 | 62.471 | -61.6013 | -0.12817 | -0.064087 | -0.09613 | -0.18311 | -0.25177 | -0.20599 | -0.086975 | 0.032043 | 61.4914 | 61.5189 | 123.7015 | 123.8892 | -0.09613 | 123.8663 | 61.4822 | -0.20599 | 123.8892 | -0.09613 | 61.4822 | 123.7015 | 123.8663 | -124.0814 | -124.1592
192.7188 | 124.1638 | -61.4182 | 62.5763 | -0.21492 | 0.0049155 | 0.012773 | -0.00071136 | 0.068152 | -0.0011877 | 0.068154 | -61.5051 | 62.4847 | -61.5326 | -61.6058 | 62.265 | 0.059509 | 0.12817 | 0.10071 | 62.4939 | -61.6058 | -0.11444 | -0.091553 | -0.086975 | -0.18768 | -0.31128 | -0.18768 | -0.082398 | 0.027466 | 61.5463 | 61.5189 | 123.6832 | 123.9029 | -0.086975 | 123.912 | 61.4777 | -0.18768 | 123.9029 | -0.086975 | 61.4777 | 123.6832 | 123.912 | -124.1089 | -124.1821
193.7188 | 124.1638 | -61.4227 | 62.5763 | -0.19966 | 0.0074789 | 0.012773 | -0.0039158 | 0.067084 | -0.00076053 | 0.070718 | -61.5143 | 62.4619 | -61.5234 | -61.6287 | 62.2696 | 0.068665 | 0.15564 | 0.09613 | 62.471 | -61.6196 | -0.10071 | -0.11444 | -0.091553 | -0.20599 | -0.3067 | -0.19684 | -0.10529 | 0.009155 | 61.5784 | 61.5189 | 123.6923 | 123.8846 | -0.091553 | 123.8937 | 61.4914 | -0.19684 | 123.8846 | -0.091553 | 61.4914 | 123.6923 | 123.8937 | -124.0997 | -124.1959
194.7188 | 124.1638 | -61.3953 | 62.5626 | -0.21492 | 0.0051291 | 0.010209 | -0.0037022 | 0.067939 | 0.00094847 | 0.069222 | -61.4594 | 62.4252 | -61.528 | -61.5692 | 62.3062 | 0.10986 | 0.11902 | 0.15106 | 62.4619 | -61.5646 | -0.13275 | -0.13733 | -0.064087 | -0.17395 | -0.25635 | -0.16937 | -0.10071 | 0.068664 | 61.5143 | 61.5463 | 123.7015 | 123.8205 | -0.064087 | 123.8571 | 61.5051 | -0.16937 | 123.8205 | -0.064087 | 61.5051 | 123.7015 | 123.8571 | -124.0906 | -124.1272
195.7188 | 124.1592 | -61.409 | 62.5534 | -0.23018 | 0.0066245 | 0.0099954 | -0.0034886 | 0.06687 | 9.4068e-05 | 0.069863 | -61.4868 | 62.4481 | -61.5326 | -61.5967 | 62.2604 | 0.068665 | 0.15106 | 0.11444 | 62.4847 | -61.5921 | -0.1236 | -0.10529 | -0.077819 | -0.18768 | -0.29297 | -0.1831 | -0.068665 | 0.045777 | 61.5601 | 61.5234 | 123.6694 | 123.8571 | -0.077819 | 123.8937 | 61.4777 | -0.1831 | 123.8571 | -0.077819 | 61.4777 | 123.6694 | 123.8937 | -124.086 | -124.1455
196.7188 | 124.205 | -61.3861 | 62.5351 | -0.24544 | 0.0068381 | 0.013413 | -0.0022068 | 0.066657 | -0.00097413 | 0.068154 | -61.4685 | 62.3978 | -61.496 | -61.5509 | 62.3062 | 0.1236 | 0.082397 | 0.16479 | 62.439 | -61.5784 | -0.10986 | -0.13733 | -0.082398 | -0.16479 | -0.22888 | -0.19226 | -0.09613 | 0.027466 | 61.4685 | 61.5509 | 123.6923 | 123.7839 | -0.082398 | 123.8251 | 61.5097 | -0.19226 | 123.7839 | -0.082398 | 61.5097 | 123.6923 | 123.8251 | -124.0311 | -124.1135
197.7188 | 124.1409 | -61.3998 | 62.5763 | -0.23781 | 0.0042745 | 0.0082864 | -0.0028476 | 0.066657 | -0.0028967 | 0.069863 | -61.4731 | 62.4298 | -61.528 | -61.5646 | 62.2925 | 0.086975 | 0.09613 | 0.15564 | 62.4939 | -61.5555 | -0.12817 | -0.14648 | -0.073242 | -0.16479 | -0.28381 | -0.15564 | -0.082398 | 0.054932 | 61.496 | 61.5555 | 123.6923 | 123.8297 | -0.073242 | 123.8937 | 61.4868 | -0.15564 | 123.8297 | -0.073242 | 61.4868 | 123.6923 | 123.8937 | -124.1043 | -124.1318
198.7188 | 124.2004 | -61.3861 | 62.5397 | -0.19203 | 0.0032065 | 0.007432 | -0.0022068 | 0.065375 | -0.00097413 | 0.069222 | -61.4365 | 62.3703 | -61.496 | -61.5234 | 62.3337 | 0.15106 | 0.032043 | 0.20142 | 62.4344 | -61.5875 | -0.10986 | -0.16937 | -0.050354 | -0.13733 | -0.20599 | -0.20142 | -0.10529 | 0.05951 | 61.4182 | 61.5875 | 123.7198 | 123.7564 | -0.050354 | 123.8205 | 61.5372 | -0.20142 | 123.7564 | -0.050354 | 61.5372 | 123.7198 | 123.8205 | -124.0356 | -124.1272
199.7188 | 124.2096 | -61.4044 | 62.5534 | -0.10048 | 0.0074789 | 0.01085 | 0.0027066 | 0.067084 | -0.00076053 | 0.06965 | -61.4685 | 62.471 | -61.528 | -61.5509 | 62.3062 | 0.086975 | 0.045776 | 0.11902 | 62.471 | -61.5875 | -0.1236 | -0.082398 | -0.064087 | -0.14648 | -0.24719 | -0.18311 | -0.082398 | 0.059509 | 61.4502 | 61.5234 | 123.7106 | 123.8754 | -0.064087 | 123.8754 | 61.4914 | -0.18311 | 123.8754 | -0.064087 | 61.4914 | 123.7106 | 123.8754 | -124.0814 | -124.1409
200.7188 | 124.2691 | -61.3586 | 62.5305 | -0.19203 | 0.0049155 | 0.010636 | -0.0045566 | 0.06922 | 0.00052127 | 0.068582 | -61.4136 | 62.3795 | -61.4914 | -61.4456 | 62.439 | 0.15106 | -0.082397 | 0.27466 | 62.4344 | -61.5463 | -0.13275 | -0.15106 | -0.054931 | -0.086975 | -0.091553 | -0.18768 | -0.096131 | 0.07782 | 61.2762 | 61.6333 | 123.7976 | 123.7381 | -0.054931 | 123.793 | 61.5097 | -0.18768 | 123.7381 | -0.054931 | 61.5097 | 123.7976 | 123.793 | -124.0219 | -124.0768
201.7188 | 124.2691 | -61.3815 | 62.5305 | -0.047073 | 0.0053427 | 0.0089274 | -0.0049838 | 0.06388 | -0.0011877 | 0.073281 | -61.5005 | 62.3657 | -61.5143 | -61.5463 | 62.3199 | 0.09613 | -0.073242 | 0.14191 | 62.4207 | -61.5738 | -0.13275 | -0.16479 | -0.11902 | -0.16479 | -0.21057 | -0.19226 | -0.10986 | 0.013733 | 61.3083 | 61.5234 | 123.7015 | 123.7473 | -0.11902 | 123.8022 | 61.4777 | -0.19226 | 123.7473 | -0.11902 | 61.4777 | 123.7015 | 123.8022 | -124.0448 | -124.1043
202.7188 | 124.2828 | -61.3632 | 62.5534 | -0.062332 | 0.0066245 | 0.010209 | -0.0034886 | 0.064948 | -0.00097413 | 0.070718 | -61.4685 | 62.3474 | -61.5189 | -61.5417 | 62.3474 | 0.10529 | -0.073242 | 0.15106 | 62.4207 | -61.5555 | -0.15564 | -0.20599 | -0.10529 | -0.17853 | -0.20599 | -0.19226 | -0.13275 | 0.050354 | 61.29 | 61.5143 | 123.7106 | 123.7106 | -0.10529 | 123.7839 | 61.4685 | -0.19226 | 123.7106 | -0.10529 | 61.4685 | 123.7106 | 123.7839 | -124.0723 | -124.1089
203.7188 | 124.2279 | -61.3724 | 62.5442 | 0.029221 | 0.0042745 | 0.012345 | -0.0045566 | 0.064521 | -0.00033333 | 0.069436 | -61.5051 | 62.3474 | -61.5509 | -61.5646 | 62.3016 | 0.07782 | -0.068665 | 0.12817 | 62.3978 | -61.5692 | -0.17853 | -0.19684 | -0.13275 | -0.19226 | -0.24261 | -0.19684 | -0.14648 | 0.045776 | 61.3037 | 61.5005 | 123.674 | 123.7198 | -0.13275 | 123.7701 | 61.4502 | -0.19684 | 123.7198 | -0.13275 | 61.4502 | 123.674 | 123.7701 | -124.0952 | -124.1135
204.7188 | 124.118 | -61.4136 | 62.6175 | -0.24544 | 0.0061971 | 0.011064 | 0.0037746 | 0.065589 | 0.0018031 | 0.069222 | -61.5097 | 62.4481 | -61.5326 | -61.6058 | 62.2559 | 0.050354 | 0.14191 | 0.10986 | 62.4573 | -61.5829 | -0.11902 | -0.16937 | -0.096131 | -0.19226 | -0.36163 | -0.16937 | -0.16022 | 0.022888 | 61.5555 | 61.5234 | 123.6694 | 123.8617 | -0.096131 | 123.8708 | 61.4639 | -0.16937 | 123.8617 | -0.096131 | 61.4639 | 123.6694 | 123.8708 | -124.1501 | -124.2004
205.7188 | 124.2371 | -61.377 | 62.5259 | 0.04448 | 0.0061971 | 0.01085 | -0.00049776 | 0.064307 | -0.0024695 | 0.067727 | -61.5234 | 62.3749 | -61.5234 | -61.5738 | 62.2833 | 0.059509 | -0.068665 | 0.11444 | 62.4115 | -61.5967 | -0.14648 | -0.15106 | -0.14648 | -0.19684 | -0.24262 | -0.21973 | -0.11444 | 0 | 61.3083 | 61.4914 | 123.6603 | 123.7518 | -0.14648 | 123.7885 | 61.4365 | -0.21973 | 123.7518 | -0.14648 | 61.4365 | 123.6603 | 123.7885 | -124.0494 | -124.1226
206.7188 | 124.2279 | -61.4182 | 62.5168 | 0.10551 | 0.0055563 | 0.0097818 | -0.0024204 | 0.059607 | 0.00073487 | 0.069863 | -61.5005 | 62.3749 | -61.5189 | -61.6882 | 62.3199 | 0.086975 | -0.09613 | 0.082397 | 62.4069 | -61.5509 | -0.10071 | -0.14191 | -0.082397 | -0.27008 | -0.19684 | -0.13275 | -0.10986 | 0.018311 | 61.322 | 61.5005 | 123.7381 | 123.793 | -0.082397 | 123.8251 | 61.5051 | -0.13275 | 123.793 | -0.082397 | 61.5051 | 123.7381 | 123.8251 | -124.0356 | -124.0677
207.7188 | 124.1913 | -61.3998 | 62.5397 | 0.12077 | 0.0044881 | 0.0063638 | 0.00014304 | 0.064948 | -0.0016149 | 0.073068 | -61.5051 | 62.3428 | -61.5372 | -61.5829 | 62.2787 | 0.054932 | -0.086975 | 0.073242 | 62.4207 | -61.5829 | -0.13733 | -0.19684 | -0.10529 | -0.18311 | -0.26093 | -0.18311 | -0.11902 | 0.032043 | 61.3129 | 61.4731 | 123.6786 | 123.7427 | -0.10529 | 123.8205 | 61.4548 | -0.18311 | 123.7427 | -0.10529 | 61.4548 | 123.6786 | 123.8205 | -124.0768 | -124.1226
208.7188 | 124.2462 | -61.3678 | 62.5122 | 0.32677 | 0.0064107 | 0.0085 | 0.002493 | 0.066443 | -0.0016149 | 0.069863 | -61.441 | 62.352 | -61.5326 | -61.5143 | 62.3245 | 0.059509 | -0.1831 | 0.09613 | 62.3428 | -61.5921 | -0.16479 | -0.16022 | -0.073242 | -0.14648 | -0.18768 | -0.2243 | -0.16937 | 0.091553 | 61.1847 | 61.4639 | 123.6923 | 123.7198 | -0.073242 | 123.7106 | 61.4273 | -0.2243 | 123.7198 | -0.073242 | 61.4273 | 123.6923 | 123.7106 | -124.0448 | -124.1043
209.7188 | 124.2371 | -61.3907 | 62.4985 | 0.15129 | 0.0072653 | 0.0082864 | 0.00014304 | 0.064307 | -0.0011877 | 0.068582 | -61.4594 | 62.3474 | -61.5143 | -61.5372 | 62.3062 | 0.064087 | -0.16479 | 0.10071 | 62.3657 | -61.5738 | -0.1236 | -0.15106 | -0.068665 | -0.14648 | -0.19226 | -0.18311 | -0.13275 | 0.054931 | 61.2259 | 61.4914 | 123.6969 | 123.7381 | -0.068665 | 123.7564 | 61.4548 | -0.18311 | 123.7381 | -0.068665 | 61.4548 | 123.6969 | 123.7564 | -124.0128 | -124.0723
210.7188 | 124.2462 | -61.3632 | 62.4893 | 0.40306 | 0.0070517 | 0.011704 | 0.00099764 | 0.066443 | 0.0013757 | 0.068582 | -61.4044 | 62.3795 | -61.5097 | -61.5143 | 62.3337 | 0.064087 | -0.17853 | 0.10071 | 62.3566 | -61.5921 | -0.14648 | -0.10986 | -0.041199 | -0.15106 | -0.15564 | -0.22888 | -0.13275 | 0.10529 | 61.1847 | 61.4639 | 123.6969 | 123.7427 | -0.041199 | 123.7198 | 61.4273 | -0.22888 | 123.7427 | -0.041199 | 61.4273 | 123.6969 | 123.7198 | -123.999 | -124.0814
211.7188 | 124.2325 | -61.3907 | 62.5076 | 0.18181 | 0.0064107 | 0.011277 | 0.00057044 | 0.064093 | 0.0011621 | 0.068368 | -61.4594 | 62.3383 | -61.5463 | -61.5189 | 62.3108 | 0.045776 | -0.16479 | 0.09613 | 62.352 | -61.5829 | -0.15564 | -0.16937 | -0.068665 | -0.12817 | -0.19684 | -0.19226 | -0.15564 | 0.086975 | 61.2259 | 61.4868 | 123.7015 | 123.7289 | -0.068665 | 123.7427 | 61.4365 | -0.19226 | 123.7289 | -0.068665 | 61.4365 | 123.7015 | 123.7427 | -124.054 | -124.0906
212.7188 | 124.2462 | -61.3678 | 62.4893 | 0.7235 | 0.0064107 | 0.0093546 | -0.00049776 | 0.064521 | -0.0022559 | 0.071145 | -61.4227 | 62.3932 | -61.5005 | -61.5326 | 62.3199 | 0.073242 | -0.19226 | 0.091553 | 62.352 | -61.5921 | -0.13275 | -0.096131 | -0.054931 | -0.16479 | -0.16937 | -0.2243 | -0.13733 | 0.07782 | 61.1755 | 61.4594 | 123.6877 | 123.761 | -0.054931 | 123.7198 | 61.441 | -0.2243 | 123.761 | -0.054931 | 61.441 | 123.6877 | 123.7198 | -123.9899 | -124.0814
213.7188 | 124.2554 | -61.3998 | 62.4802 | 0.16655 | 0.0081197 | 0.011064 | 0.002493 | 0.065161 | -0.00076053 | 0.071145 | -61.4273 | 62.3795 | -61.5326 | -61.528 | 62.3337 | 0.068665 | -0.18768 | 0.068665 | 62.3566 | -61.5967 | -0.13275 | -0.10071 | -0.027466 | -0.12817 | -0.14649 | -0.19684 | -0.1236 | 0.10529 | 61.2122 | 61.4685 | 123.7335 | 123.7793 | -0.027466 | 123.7564 | 61.4685 | -0.19684 | 123.7793 | -0.027466 | 61.4685 | 123.7335 | 123.7564 | -124.0128 | -124.0768
214.7188 | 124.2783 | -61.377 | 62.4939 | 1.3873 | 0.0055563 | 0.0078592 | 0.0033474 | 0.065802 | -0.0018285 | 0.069222 | -61.322 | 62.3703 | -61.5234 | -61.4914 | 62.3474 | 0.050354 | -0.20142 | 0.09613 | 62.3749 | -61.6058 | -0.14648 | -0.1236 | 0.054932 | -0.11444 | -0.14648 | -0.22888 | -0.11902 | 0.20142 | 61.1755 | 61.4731 | 123.7244 | 123.7473 | 0.054932 | 123.7518 | 61.4273 | -0.22888 | 123.7473 | 0.054932 | 61.4273 | 123.7244 | 123.7518 | -124.0173 | -124.0997
215.7188 | 124.1455 | -61.4136 | 62.5442 | -0.08522 | 0.01047 | 0.013627 | 0.0031338 | 0.067084 | -0.00033333 | 0.069436 | -61.5097 | 62.4619 | -61.5509 | -61.6425 | 62.2147 | -0.045776 | -0.018311 | -0.032043 | 62.4481 | -61.6379 | -0.13733 | -0.082397 | -0.096131 | -0.22888 | -0.32959 | -0.2243 | -0.09613 | 0.041198 | 61.3953 | 61.3815 | 123.6282 | 123.8754 | -0.096131 | 123.8617 | 61.3678 | -0.2243 | 123.8754 | -0.096131 | 61.3678 | 123.6282 | 123.8617 | -124.0952 | -124.1821
216.7188 | 124.1776 | -61.4182 | 62.5031 | 0.11314 | 0.0089743 | 0.014268 | 0.0016384 | 0.066016 | -0.00076053 | 0.069436 | -61.5143 | 62.4619 | -61.5646 | -61.6333 | 62.233 | -0.032043 | -0.036621 | -0.036621 | 62.4344 | -61.6425 | -0.14648 | -0.041199 | -0.09613 | -0.21515 | -0.27008 | -0.2243 | -0.068665 | 0.050354 | 61.3815 | 61.3815 | 123.6511 | 123.88 | -0.09613 | 123.8525 | 61.3861 | -0.2243 | 123.88 | -0.09613 | 61.3861 | 123.6511 | 123.8525 | -124.0677 | -124.1455
217.7188 | 124.1455 | -61.4319 | 62.5351 | -0.069961 | 0.0089743 | 0.010209 | 0.0027066 | 0.069434 | -0.0020421 | 0.069222 | -61.5555 | 62.4939 | -61.5555 | -61.6562 | 62.2147 | -0.050354 | -0.018311 | -0.036621 | 62.4435 | -61.6425 | -0.1236 | -0.041199 | -0.1236 | -0.2243 | -0.32043 | -0.21057 | -0.091553 | 0 | 61.4136 | 61.3953 | 123.6465 | 123.9258 | -0.1236 | 123.8754 | 61.3815 | -0.21057 | 123.9258 | -0.1236 | 61.3815 | 123.6465 | 123.8754 | -124.0906 | -124.1776
218.7188 | 124.1409 | -61.4365 | 62.5259 | 0.18181 | 0.0085471 | 0.011491 | 0.0014248 | 0.06687 | 0.00052127 | 0.070077 | -61.5326 | 62.471 | -61.5555 | -61.6241 | 62.2421 | -0.032043 | -0.022888 | -0.041199 | 62.4207 | -61.615 | -0.11902 | -0.054932 | -0.096131 | -0.18768 | -0.28381 | -0.17853 | -0.10529 | 0.022888 | 61.4136 | 61.3953 | 123.6786 | 123.9075 | -0.096131 | 123.8571 | 61.4044 | -0.17853 | 123.9075 | -0.096131 | 61.4044 | 123.6786 | 123.8571 | -124.0814 | -124.1409
219.7188 | 124.2371 | -61.3907 | 62.4939 | 0.10551 | 0.0072653 | 0.012559 | -0.0049838 | 0.068793 | 0.00030767 | 0.068795 | -61.5189 | 62.3978 | -61.5326 | -61.5967 | 62.2925 | 0.054932 | 0.26093 | 0.19684 | 62.4481 | -61.5463 | -0.14191 | -0.09613 | -0.12817 | -0.20599 | -0.20142 | -0.15564 | -0.045776 | 0.013733 | 61.6516 | 61.5875 | 123.6832 | 123.7885 | -0.12817 | 123.8388 | 61.4456 | -0.15564 | 123.7885 | -0.12817 | 61.4456 | 123.6832 | 123.8388 | -124.0265 | -124.0402
220.7188 | 124.0814 | -61.4136 | 62.5626 | 0.082626 | 0.0081197 | 0.011064 | 0.0037746 | 0.067939 | -0.0035375 | 0.069222 | -61.5463 | 62.4893 | -61.5646 | -61.6745 | 62.2513 | -0.17853 | -0.29297 | 0.28839 | 62.384 | -61.6608 | -0.15106 | -0.073242 | -0.13275 | -0.26093 | -0.31128 | -0.24719 | -0.17853 | 0.01831 | 61.1206 | 61.702 | 123.6649 | 123.9029 | -0.13275 | 123.7976 | 61.235 | -0.24719 | 123.9029 | -0.13275 | 61.235 | 123.6649 | 123.7976 | -124.1272 | -124.2233
221.7188 | 124.1272 | -61.4136 | 62.5259 | 0.13603 | 0.0085471 | 0.013413 | 0.003561 | 0.068152 | 0.00030767 | 0.066445 | -61.5097 | 62.4985 | -61.5509 | -61.6562 | 62.2147 | -0.022888 | 0.045776 | -0.009155 | 62.4481 | -61.6196 | -0.13733 | -0.027466 | -0.096131 | -0.24262 | -0.31128 | -0.20599 | -0.07782 | 0.041198 | 61.4593 | 61.4044 | 123.6282 | 123.912 | -0.096131 | 123.8617 | 61.3907 | -0.20599 | 123.912 | -0.096131 | 61.3907 | 123.6282 | 123.8617 | -124.0768 | -124.1455
222.7188 | 124.1547 | -61.4044 | 62.5305 | 0.013962 | 0.0085471 | 0.012773 | 0.002493 | 0.069007 | -0.0022559 | 0.070504 | -61.4502 | 62.4802 | -61.528 | -61.5646 | 62.2925 | 0.082397 | 0.032043 | 0.082397 | 62.439 | -61.6287 | -0.1236 | -0.050354 | -0.045776 | -0.16022 | -0.23804 | -0.2243 | -0.091553 | 0.07782 | 61.4365 | 61.4868 | 123.6969 | 123.8846 | -0.045776 | 123.8434 | 61.4868 | -0.2243 | 123.8846 | -0.045776 | 61.4868 | 123.6969 | 123.8434 | -124.0585 | -124.1592
223.7188 | 124.1409 | -61.3907 | 62.5442 | -0.0089264 | 0.0087607 | 0.011277 | 0.0022794 | 0.070075 | -0.00054693 | 0.071359 | -61.4731 | 62.4847 | -61.5601 | -61.5829 | 62.2467 | 0.036621 | 0.032043 | 0.050354 | 62.439 | -61.6104 | -0.16937 | -0.059509 | -0.082397 | -0.19226 | -0.29755 | -0.21973 | -0.10528 | 0.086976 | 61.4227 | 61.441 | 123.6374 | 123.8754 | -0.082397 | 123.8297 | 61.4273 | -0.21973 | 123.8754 | -0.082397 | 61.4273 | 123.6374 | 123.8297 | -124.1043 | -124.1547
224.7188 | 124.2691 | -61.3861 | 62.4802 | 0.21996 | 0.0066245 | 0.0097818 | -0.00092496 | 0.06922 | -0.0035375 | 0.072 | -61.441 | 62.3932 | -61.5417 | -61.5417 | 62.3108 | 0.09613 | -0.20142 | 0.073242 | 62.3978 | -61.5601 | -0.15564 | -0.086976 | -0.054932 | -0.15564 | -0.16937 | -0.17395 | -0.082398 | 0.10071 | 61.1847 | 61.4594 | 123.6969 | 123.7793 | -0.054932 | 123.7839 | 61.4822 | -0.17395 | 123.7793 | -0.054932 | 61.4822 | 123.6969 | 123.7839 | -124.0219 | -124.0402
225.7188 | 124.1455 | -61.4044 | 62.5397 | -0.016556 | 0.0066245 | 0.014054 | 0.004202 | 0.071784 | -0.0020421 | 0.067941 | -61.4822 | 62.4985 | -61.5189 | -61.5829 | 62.2787 | 0.041199 | 0.022888 | 0.050354 | 62.439 | -61.5967 | -0.11444 | -0.041199 | -0.07782 | -0.17853 | -0.26093 | -0.19226 | -0.10071 | 0.036621 | 61.4273 | 61.4548 | 123.6832 | 123.9029 | -0.07782 | 123.8434 | 61.4456 | -0.19226 | 123.9029 | -0.07782 | 61.4456 | 123.6832 | 123.8434 | -124.0585 | -124.1364
226.7188 | 124.1913 | -61.3998 | 62.5351 | -0.054703 | 0.0083333 | 0.010423 | 0.002493 | 0.071997 | -0.00097413 | 0.069436 | -61.4548 | 62.471 | -61.5234 | -61.5738 | 62.3016 | 0.073242 | 0.022888 | 0.11444 | 62.4619 | -61.6058 | -0.1236 | -0.064087 | -0.054932 | -0.17395 | -0.23346 | -0.20599 | -0.073242 | 0.068664 | 61.4227 | 61.5143 | 123.7015 | 123.8708 | -0.054932 | 123.8617 | 61.4731 | -0.20599 | 123.8708 | -0.054932 | 61.4731 | 123.7015 | 123.8617 | -124.0585 | -124.1409
227.7188 | 124.1867 | -61.4044 | 62.5442 | -0.016556 | 0.0068381 | 0.0087138 | 0.004202 | 0.073065 | -0.0018285 | 0.069863 | -61.441 | 62.4847 | -61.5326 | -61.4914 | 62.265 | 0.073242 | 0.022888 | 0.11902 | 62.4573 | -61.6241 | -0.12817 | -0.059509 | -0.036621 | -0.086975 | -0.27923 | -0.21973 | -0.086975 | 0.091553 | 61.4273 | 61.5234 | 123.6694 | 123.8892 | -0.036621 | 123.8617 | 61.4777 | -0.21973 | 123.8892 | -0.036621 | 61.4777 | 123.6694 | 123.8617 | -124.0768 | -124.1684
228.7188 | 124.1547 | -61.3998 | 62.5534 | -0.23018 | 0.0085471 | 0.011064 | -0.0013522 | 0.070075 | -0.0028967 | 0.068368 | -61.5051 | 62.4893 | -61.5189 | -61.6058 | 62.2604 | 0.073242 | 0.14191 | 0.10071 | 62.4847 | -61.5921 | -0.11902 | -0.064087 | -0.10529 | -0.20599 | -0.29297 | -0.19226 | -0.068665 | 0.013733 | 61.5417 | 61.5005 | 123.6603 | 123.8892 | -0.10529 | 123.8846 | 61.4731 | -0.19226 | 123.8892 | -0.10529 | 61.4731 | 123.6603 | 123.8846 | -124.0723 | -124.1455
229.7188 | 124.1684 | -61.4273 | 62.5626 | 0.14366 | 0.0064107 | 0.014695 | 0.0031338 | 0.068793 | -0.00097413 | 0.068795 | -61.5738 | 62.4756 | -61.5555 | -61.5601 | 62.1094 | -0.082397 | 0.13733 | -0.054932 | 62.4802 | -61.6196 | -0.12817 | -0.086975 | -0.14648 | -0.13275 | -0.45319 | -0.19226 | -0.082397 | -0.018311 | 61.5646 | 61.3724 | 123.5367 | 123.9029 | -0.14648 | 123.9075 | 61.3449 | -0.19226 | 123.9029 | -0.14648 | 61.3449 | 123.5367 | 123.9075 | -124.118 | -124.1821
230.7188 | 124.1638 | -61.4136 | 62.5763 | -0.16914 | 0.0087607 | 0.01555 | -0.0028476 | 0.068152 | -0.00076053 | 0.068582 | -61.5189 | 62.4985 | -61.528 | -61.6058 | 62.265 | 0.068665 | 0.13733 | 0.09613 | 62.4802 | -61.6058 | -0.11444 | -0.07782 | -0.10529 | -0.19226 | -0.31128 | -0.19226 | -0.09613 | 0.009155 | 61.5509 | 61.5097 | 123.6786 | 123.912 | -0.10529 | 123.8937 | 61.4822 | -0.19226 | 123.912 | -0.10529 | 61.4822 | 123.6786 | 123.8937 | -124.1043 | -124.1821
231.7188 | 124.1318 | -61.3907 | 62.5488 | -0.11574 | 0.011324 | 0.010423 | -0.0013522 | 0.069434 | 0.00030767 | 0.068368 | -61.5326 | 62.4802 | -61.5646 | -61.6013 | 62.2513 | 0.054932 | 0.15564 | 0.10529 | 62.4664 | -61.6013 | -0.17395 | -0.068664 | -0.14191 | -0.21057 | -0.29755 | -0.21057 | -0.082397 | 0.032043 | 61.5463 | 61.496 | 123.642 | 123.8709 | -0.14191 | 123.8571 | 61.4456 | -0.21057 | 123.8709 | -0.14191 | 61.4456 | 123.642 | 123.8571 | -124.1135 | -124.1501
232.7188 | 124.1638 | -61.3907 | 62.5488 | -0.22255 | 0.0091879 | 0.011277 | 0.00057044 | 0.068366 | -0.00011953 | 0.070718 | -61.496 | 62.5031 | -61.5326 | -61.5967 | 62.2696 | 0.068665 | 0.15106 | 0.10071 | 62.5031 | -61.5829 | -0.14191 | -0.045776 | -0.10529 | -0.20599 | -0.27924 | -0.19226 | -0.045776 | 0.036621 | 61.5417 | 61.4914 | 123.6603 | 123.8937 | -0.10529 | 123.8937 | 61.4594 | -0.19226 | 123.8937 | -0.10529 | 61.4594 | 123.6603 | 123.8937 | -124.0814 | -124.1318
233.7188 | 124.1501 | -61.409 | 62.5488 | 0.82268 | 0.0072653 | 0.0132 | -0.001566 | 0.066657 | -0.0011877 | 0.070077 | -61.4685 | 62.4481 | -61.5646 | -61.5921 | 62.2742 | 0.068665 | 0.14191 | 0.10071 | 62.4619 | -61.6104 | -0.15564 | -0.10071 | -0.059509 | -0.1831 | -0.27466 | -0.20142 | -0.086975 | 0.09613 | 61.5509 | 61.5097 | 123.6832 | 123.8571 | -0.059509 | 123.8708 | 61.4777 | -0.20142 | 123.8571 | -0.059509 | 61.4777 | 123.6832 | 123.8708 | -124.1135 | -124.1592
234.7188 | 124.1226 | -61.3907 | 62.5763 | -0.20729 | 0.0057699 | 0.0095682 | -0.00092496 | 0.068579 | -0.0011877 | 0.069009 | -61.5234 | 62.4619 | -61.5051 | -61.6104 | 62.265 | 0.068665 | 0.14648 | 0.09613 | 62.4619 | -61.5967 | -0.11444 | -0.11444 | -0.13275 | -0.21973 | -0.31128 | -0.20599 | -0.11444 | -0.01831 | 61.5372 | 61.4868 | 123.6557 | 123.8525 | -0.13275 | 123.8525 | 61.4594 | -0.20599 | 123.8525 | -0.13275 | 61.4594 | 123.6557 | 123.8525 | -124.0814 | -124.173
235.7188 | 124.2233 | -61.3586 | 62.5351 | -0.15388 | 0.0053427 | 0.01085 | -0.0034886 | 0.065589 | -0.00097413 | 0.070931 | -61.4502 | 62.3978 | -61.5326 | -61.4914 | 62.3428 | 0.16022 | -0.013733 | 0.21973 | 62.439 | -61.5646 | -0.17395 | -0.13733 | -0.091552 | -0.13275 | -0.19226 | -0.20599 | -0.09613 | 0.082398 | 61.3449 | 61.5784 | 123.7015 | 123.7564 | -0.091552 | 123.7976 | 61.5189 | -0.20599 | 123.7564 | -0.091552 | 61.5189 | 123.7015 | 123.7976 | -124.0677 | -124.0997
236.7188 | 124.2691 | -61.3724 | 62.5351 | -2.6868 | 0.0029929 | 0.0132 | -0.0037022 | 0.066443 | -0.0011877 | 0.067727 | -61.4502 | 62.4252 | -61.4639 | -61.4822 | 62.3108 | 0.14191 | -0.027466 | 0.21973 | 62.4252 | -61.5509 | -0.091553 | -0.10986 | -0.07782 | -0.10986 | -0.2243 | -0.17853 | -0.10986 | 0.013733 | 61.3449 | 61.5921 | 123.6832 | 123.7976 | -0.07782 | 123.7976 | 61.5143 | -0.17853 | 123.7976 | -0.07782 | 61.5143 | 123.6832 | 123.7976 | -123.999 | -124.086
237.7188 | 124.2416 | -61.3678 | 62.5259 | -0.41328 | 0.0038473 | 0.011064 | -0.0047702 | 0.064948 | -0.0022559 | 0.067727 | -61.4365 | 62.3978 | -61.496 | -61.5005 | 62.352 | 0.16022 | -0.022888 | 0.21973 | 62.4252 | -61.5509 | -0.12817 | -0.12817 | -0.068664 | -0.13275 | -0.17395 | -0.1831 | -0.10071 | 0.05951 | 61.3449 | 61.5875 | 123.7198 | 123.7656 | -0.068664 | 123.793 | 61.528 | -0.1831 | 123.7656 | -0.068664 | 61.528 | 123.7198 | 123.793 | -124.0219 | -124.0768
238.7188 | 124.324 | -61.3861 | 62.5351 | -0.12337 | 0.0049155 | 0.010636 | -0.0017796 | 0.065161 | -0.00097413 | 0.067727 | -61.4182 | 62.3657 | -61.5143 | -61.4822 | 62.3566 | 0.059509 | 0.42572 | 0.21973 | 62.4664 | -61.5417 | -0.12817 | -0.16937 | -0.032044 | -0.096131 | -0.17853 | -0.15564 | -0.068664 | 0.09613 | 61.8118 | 61.6058 | 123.7427 | 123.7518 | -0.032044 | 123.8525 | 61.4456 | -0.15564 | 123.7518 | -0.032044 | 61.4456 | 123.7427 | 123.8525 | -124.0494 | -124.0768
239.7188 | 124.1089 | -61.3953 | 62.5717 | 0.1284 | 0.0053427 | 0.011491 | 0.003561 | 0.065589 | -0.0011877 | 0.067086 | -61.5005 | 62.439 | -61.5509 | -61.615 | 62.2467 | 0.064087 | 0.14648 | 0.09613 | 62.4802 | -61.5875 | -0.15564 | -0.13275 | -0.10529 | -0.21973 | -0.32501 | -0.19226 | -0.091552 | 0.050354 | 61.5417 | 61.4914 | 123.642 | 123.8342 | -0.10529 | 123.8754 | 61.4594 | -0.19226 | 123.8342 | -0.10529 | 61.4594 | 123.642 | 123.8754 | -124.1226 | -124.1592
240.7188 | 124.2874 | -61.3541 | 62.5214 | -0.11574 | 0.0055563 | 0.0078592 | -0.0037022 | 0.065589 | -0.0022559 | 0.067727 | -61.4136 | 62.3703 | -61.5005 | -61.4777 | 62.3749 | 0.16022 | -0.086975 | 0.2243 | 62.4207 | -61.5372 | -0.14648 | -0.15106 | -0.059509 | -0.1236 | -0.14648 | -0.18311 | -0.10071 | 0.086975 | 61.2671 | 61.5784 | 123.7289 | 123.7244 | -0.059509 | 123.7747 | 61.5143 | -0.18311 | 123.7244 | -0.059509 | 61.5143 | 123.7289 | 123.7747 | -124.0219 | -124.0585
241.7188 | 124.2783 | -61.3907 | 62.5442 | -0.08522 | 0.0021383 | 0.0093546 | -0.002634 | 0.065375 | -0.0014013 | 0.070718 | -61.4639 | 62.384 | -61.5143 | -61.5463 | 62.3016 | 0.12817 | -0.059509 | 0.17395 | 62.4069 | -61.5646 | -0.1236 | -0.16022 | -0.073242 | -0.15564 | -0.24261 | -0.17395 | -0.13733 | 0.050354 | 61.3312 | 61.5646 | 123.6923 | 123.7747 | -0.073242 | 123.7976 | 61.5189 | -0.17395 | 123.7747 | -0.073242 | 61.5189 | 123.6923 | 123.7976 | -124.0585 | -124.1089
242.7188 | 124.1913 | -61.3724 | 62.558 | -0.0012969 | 0.0070517 | 0.0089274 | -0.0013522 | 0.064307 | 9.4068e-05 | 0.069863 | -61.5005 | 62.3749 | -61.5051 | -61.5784 | 62.265 | 0.050354 | -0.064087 | 0.082397 | 62.3886 | -61.5692 | -0.13275 | -0.1831 | -0.12817 | -0.20599 | -0.29297 | -0.19684 | -0.16937 | 0.004578 | 61.3083 | 61.4548 | 123.6374 | 123.7473 | -0.12817 | 123.761 | 61.4227 | -0.19684 | 123.7473 | -0.12817 | 61.4227 | 123.6374 | 123.761 | -124.0631 | -124.1272
243.7188 | 124.2325 | -61.409 | 62.5122 | 0.11314 | 0.0055563 | 0.0095682 | -0.00028416 | 0.06388 | -0.00076053 | 0.06965 | -61.4868 | 62.352 | -61.5417 | -61.5646 | 62.2696 | 0.018311 | -0.10986 | 0.07782 | 62.3657 | -61.5784 | -0.13275 | -0.16022 | -0.077819 | -0.15564 | -0.24261 | -0.16937 | -0.14648 | 0.054932 | 61.2991 | 61.4868 | 123.6786 | 123.761 | -0.077819 | 123.7747 | 61.4273 | -0.16937 | 123.761 | -0.077819 | 61.4273 | 123.6786 | 123.7747 | -124.054 | -124.0906
244.7188 | 124.2599 | -61.3678 | 62.5214 | -0.024185 | 0.0057699 | 0.0072184 | -0.0024204 | 0.062598 | 0.00052127 | 0.068582 | -61.4777 | 62.3657 | -61.5051 | -61.528 | 62.3383 | 0.09613 | -0.064087 | 0.16479 | 62.3886 | -61.5646 | -0.13733 | -0.15564 | -0.10986 | -0.16022 | -0.18311 | -0.19684 | -0.13275 | 0.027466 | 61.3037 | 61.5326 | 123.7061 | 123.7335 | -0.10986 | 123.7564 | 61.4639 | -0.19684 | 123.7335 | -0.10986 | 61.4639 | 123.7061 | 123.7564 | -124.0265 | -124.086
245.7188 | 124.2233 | -61.3861 | 62.5122 | 0.13603 | 0.0047019 | 0.0042276 | 0.002493 | 0.063239 | -0.0024695 | 0.068154 | -61.4548 | 62.3703 | -61.5189 | -61.5417 | 62.3016 | 0.064087 | -0.15106 | 0.086975 | 62.3657 | -61.5738 | -0.13275 | -0.14191 | -0.068665 | -0.15564 | -0.21057 | -0.18768 | -0.14648 | 0.064087 | 61.235 | 61.4731 | 123.6877 | 123.7564 | -0.068665 | 123.7518 | 61.4502 | -0.18768 | 123.7564 | -0.068665 | 61.4502 | 123.6877 | 123.7518 | -124.0311 | -124.086
246.7188 | 124.2233 | -61.4044 | 62.4893 | 0.1284 | 0.0066245 | 0.0082864 | 0.0014248 | 0.063666 | -0.0024695 | 0.068368 | -61.4731 | 62.3749 | -61.528 | -61.5555 | 62.2879 | 0.041199 | -0.16022 | 0.082397 | 62.3657 | -61.5875 | -0.1236 | -0.11444 | -0.068664 | -0.15106 | -0.20142 | -0.18311 | -0.1236 | 0.054932 | 61.2442 | 61.4868 | 123.6923 | 123.7793 | -0.068664 | 123.7701 | 61.4456 | -0.18311 | 123.7793 | -0.068664 | 61.4456 | 123.6923 | 123.7701 | -124.0173 | -124.0768
247.7188 | 124.2416 | -61.3678 | 62.4939 | 0.21996 | 0.0061971 | 0.014909 | 0.0014248 | 0.066016 | -0.0024695 | 0.0673 | -61.4319 | 62.3611 | -61.5372 | -61.5097 | 62.3291 | 0.050354 | -0.17395 | 0.10529 | 62.3749 | -61.5829 | -0.16937 | -0.13275 | -0.064087 | -0.14191 | -0.16479 | -0.21515 | -0.11902 | 0.10529 | 61.1938 | 61.4731 | 123.6969 | 123.7289 | -0.064087 | 123.7427 | 61.4182 | -0.21515 | 123.7289 | -0.064087 | 61.4182 | 123.6969 | 123.7427 | -124.0311 | -124.0768
248.7188 | 124.2645 | -61.3403 | 62.5122 | -0.10811 | 0.0057699 | 0.0089274 | -0.0024204 | 0.063239 | -0.00097413 | 0.069009 | -61.4319 | 62.3703 | -61.5051 | -61.4777 | 62.352 | 0.14191 | -0.09613 | 0.21515 | 62.3886 | -61.5738 | -0.1648 | -0.14191 | -0.091553 | -0.13733 | -0.16022 | -0.23346 | -0.1236 | 0.073242 | 61.2442 | 61.5555 | 123.6923 | 123.7106 | -0.091553 | 123.7289 | 61.4822 | -0.23346 | 123.7106 | -0.091553 | 61.4822 | 123.6923 | 123.7289 | -124.0173 | -124.086
249.7188 | 124.2371 | -61.3953 | 62.4939 | 0.21996 | 0.0070517 | 0.010636 | 0.0044156 | 0.065589 | -0.0014013 | 0.067086 | -61.4868 | 62.4252 | -61.5372 | -61.5601 | 62.2787 | 0.013733 | -0.16937 | 0.041199 | 62.4023 | -61.6196 | -0.14191 | -0.068664 | -0.091552 | -0.1648 | -0.21515 | -0.2243 | -0.091552 | 0.050354 | 61.2259 | 61.4365 | 123.674 | 123.8205 | -0.091552 | 123.7976 | 61.409 | -0.2243 | 123.8205 | -0.091552 | 61.409 | 123.674 | 123.7976 | -124.0311 | -124.1135
250.7188 | 124.1272 | -61.409 | 62.5351 | 0.15129 | 0.0079061 | 0.011277 | 0.0076198 | 0.065375 | -0.0022559 | 0.068582 | -61.5326 | 62.471 | -61.5646 | -61.6562 | 62.1552 | -0.041199 | 0.032043 | -0.086975 | 62.439 | -61.6333 | -0.15564 | -0.064087 | -0.1236 | -0.24719 | -0.37994 | -0.2243 | -0.09613 | 0.032043 | 61.441 | 61.322 | 123.5641 | 123.88 | -0.1236 | 123.848 | 61.3678 | -0.2243 | 123.88 | -0.1236 | 61.3678 | 123.5641 | 123.848 | -124.0997 | -124.1684
251.7188 | 124.1272 | -61.4456 | 62.5305 | 0.38017 | 0.011324 | 0.012986 | 0.002493 | 0.06687 | -0.0039649 | 0.069009 | -61.5372 | 62.4939 | -61.5463 | -61.6562 | 62.2055 | -0.041199 | -0.009155 | -0.041199 | 62.4619 | -61.6287 | -0.10071 | -0.036622 | -0.091552 | -0.21057 | -0.32501 | -0.1831 | -0.068665 | 0.009156 | 61.4365 | 61.4044 | 123.6511 | 123.9395 | -0.091552 | 123.9075 | 61.4044 | -0.1831 | 123.9395 | -0.091552 | 61.4044 | 123.6511 | 123.9075 | -124.0768 | -124.1592
252.7188 | 124.1592 | -61.4227 | 62.5259 | 0.04448 | 0.011111 | 0.013841 | 0.0033474 | 0.069648 | -0.0020421 | 0.069222 | -61.5326 | 62.4802 | -61.5646 | -61.6333 | 62.2238 | -0.041199 | -0.013733 | -0.018311 | 62.4481 | -61.647 | -0.14191 | -0.045776 | -0.10986 | -0.21057 | -0.30212 | -0.22431 | -0.07782 | 0.032043 | 61.409 | 61.4044 | 123.6465 | 123.9029 | -0.10986 | 123.8708 | 61.3815 | -0.22431 | 123.9029 | -0.10986 | 61.3815 | 123.6465 | 123.8708 | -124.0906 | -124.173
253.7344 | 124.2966 | -61.3495 | 62.5168 | -0.047073 | 0.0059835 | 0.011277 | -0.0034886 | 0.064307 | -0.00054693 | 0.070291 | -61.4182 | 62.384 | -61.5097 | -61.4685 | 62.3886 | 0.16937 | -0.07782 | 0.21515 | 62.4207 | -61.5372 | -0.16022 | -0.13275 | -0.068665 | -0.11902 | -0.12817 | -0.18768 | -0.096131 | 0.091553 | 61.2717 | 61.5646 | 123.7381 | 123.7335 | -0.068665 | 123.7701 | 61.5189 | -0.18768 | 123.7335 | -0.068665 | 61.5189 | 123.7381 | 123.7701 | -124.0265 | -124.054
254.7188 | 124.1638 | -61.3998 | 62.5168 | 0.13603 | 0.0098287 | 0.014054 | 0.00099764 | 0.066657 | -0.00097413 | 0.070504 | -61.5051 | 62.4527 | -61.5555 | -61.6058 | 62.2467 | -0.032043 | -0.050354 | -0.013733 | 62.384 | -61.615 | -0.15564 | -0.064087 | -0.10529 | -0.20599 | -0.27008 | -0.21515 | -0.13275 | 0.050354 | 61.3495 | 61.3861 | 123.6465 | 123.8525 | -0.10529 | 123.7839 | 61.3678 | -0.21515 | 123.8525 | -0.10529 | 61.3678 | 123.6465 | 123.7839 | -124.0723 | -124.1318
255.7188 | 124.1501 | -61.4182 | 62.5351 | 0.029221 | 0.01047 | 0.013627 | 0.0022794 | 0.06687 | -0.0020421 | 0.070718 | -61.4731 | 62.4664 | -61.5143 | -61.5921 | 62.2467 | 0.009155 | 0.036621 | 0.032043 | 62.4161 | -61.6333 | -0.09613 | -0.068664 | -0.054931 | -0.17395 | -0.28839 | -0.21515 | -0.11902 | 0.041199 | 61.4548 | 61.4502 | 123.6649 | 123.8846 | -0.054931 | 123.8342 | 61.4273 | -0.21515 | 123.8846 | -0.054931 | 61.4273 | 123.6649 | 123.8342 | -124.0494 | -124.1684
256.7188 | 124.118 | -61.4227 | 62.5305 | -0.062332 | 0.010256 | 0.014909 | 0.003561 | 0.069648 | -0.00076053 | 0.067727 | -61.4548 | 62.5031 | -61.5326 | -61.5463 | 62.3062 | 0.082397 | 0.036621 | 0.10071 | 62.4573 | -61.6241 | -0.10986 | -0.027466 | -0.032044 | -0.1236 | -0.22431 | -0.20142 | -0.073243 | 0.07782 | 61.4593 | 61.5234 | 123.7289 | 123.9258 | -0.032044 | 123.88 | 61.5051 | -0.20142 | 123.9258 | -0.032044 | 61.5051 | 123.7289 | 123.88 | -124.0631 | -124.1547
257.7188 | 124.2004 | -61.3724 | 62.5351 | -0.069961 | 0.0083333 | 0.012132 | 0.0027066 | 0.067939 | -0.0014013 | 0.068368 | -61.4273 | 62.4893 | -61.5372 | -61.5692 | 62.2742 | 0.086975 | 0.022888 | 0.11444 | 62.4344 | -61.5875 | -0.1648 | -0.045776 | -0.054932 | -0.19684 | -0.26093 | -0.21515 | -0.10071 | 0.10986 | 61.3953 | 61.4868 | 123.6465 | 123.8617 | -0.054932 | 123.8068 | 61.4594 | -0.21515 | 123.8617 | -0.054932 | 61.4594 | 123.6465 | 123.8068 | -124.0723 | -124.1226
258.7188 | 124.205 | -61.3861 | 62.4893 | 0.2047 | 0.0085471 | 0.012559 | -0.00049776 | 0.068579 | -0.00054693 | 0.069222 | -61.5097 | 62.4161 | -61.5463 | -61.5875 | 62.2696 | 0.022888 | -0.1236 | 0.013733 | 62.4069 | -61.6013 | -0.16022 | -0.073242 | -0.1236 | -0.20142 | -0.21973 | -0.21515 | -0.082398 | 0.036621 | 61.2625 | 61.3998 | 123.6557 | 123.8022 | -0.1236 | 123.793 | 61.409 | -0.21515 | 123.8022 | -0.1236 | 61.409 | 123.6557 | 123.793 | -124.0356 | -124.0906
259.7188 | 124.1638 | -61.4319 | 62.4985 | 0.15129 | 0.0066245 | 0.011918 | 0.00099764 | 0.068793 | -0.0016149 | 0.070077 | -61.5234 | 62.471 | -61.5326 | -61.6562 | 62.2375 | -0.009155 | -0.054932 | -0.018311 | 62.4207 | -61.6058 | -0.10071 | -0.027466 | -0.091552 | -0.2243 | -0.26093 | -0.17395 | -0.07782 | 0.009156 | 61.377 | 61.4136 | 123.6694 | 123.9029 | -0.091552 | 123.8525 | 61.4227 | -0.17395 | 123.9029 | -0.091552 | 61.4227 | 123.6694 | 123.8525 | -124.0311 | -124.1043
260.7188 | 124.1959 | -61.4182 | 62.5442 | -0.10811 | 0.0055563 | 0.012986 | 0.0012112 | 0.068579 | 0.00030767 | 0.070077 | -61.4731 | 62.4985 | -61.5326 | -61.5372 | 62.3016 | 0.10529 | 0.059509 | 0.11902 | 62.4435 | -61.6013 | -0.11444 | -0.045776 | -0.054931 | -0.11902 | -0.24261 | -0.1831 | -0.10071 | 0.05951 | 61.4777 | 61.5372 | 123.7198 | 123.9166 | -0.054931 | 123.8617 | 61.5234 | -0.1831 | 123.9166 | -0.054931 | 61.5234 | 123.7198 | 123.8617 | -124.0768 | -124.1455
261.7188 | 124.1592 | -61.4044 | 62.5442 | -0.11574 | 0.0059835 | 0.013413 | 0.00014304 | 0.069007 | -0.0020421 | 0.069436 | -61.5005 | 62.4847 | -61.5326 | -61.5784 | 62.2925 | 0.09613 | 0.091553 | 0.11902 | 62.471 | -61.5692 | -0.12817 | -0.059509 | -0.09613 | -0.17395 | -0.25177 | -0.1648 | -0.073242 | 0.032044 | 61.496 | 61.5234 | 123.6969 | 123.8892 | -0.09613 | 123.8754 | 61.5005 | -0.1648 | 123.8892 | -0.09613 | 61.5005 | 123.6969 | 123.8754 | -124.0768 | -124.1135
262.7188 | 124.1547 | -61.4227 | 62.558 | -0.21492 | 0.0055563 | 0.0099954 | -0.0017796 | 0.067725 | -0.0022559 | 0.068368 | -61.5051 | 62.4939 | -61.5646 | -61.5967 | 62.2604 | 0.064087 | 0.11902 | 0.091553 | 62.4893 | -61.5967 | -0.14191 | -0.064087 | -0.082398 | -0.17395 | -0.29755 | -0.17395 | -0.068664 | 0.059509 | 61.5417 | 61.5143 | 123.6832 | 123.9166 | -0.082398 | 123.912 | 61.4868 | -0.17395 | 123.9166 | -0.082398 | 61.4868 | 123.6832 | 123.912 | -124.1226 | -124.1547
263.7188 | 124.1043 | -61.4227 | 62.5259 | 0.04448 | 0.0066245 | 0.012773 | 0.00014304 | 0.06922 | -0.0031103 | 0.067941 | -61.496 | 62.471 | -61.5326 | -61.6196 | 62.2375 | 0.004578 | 0.045776 | 0.009155 | 62.4481 | -61.6013 | -0.10986 | -0.054932 | -0.073243 | -0.19684 | -0.28839 | -0.17853 | -0.07782 | 0.036621 | 61.4685 | 61.4319 | 123.6603 | 123.8937 | -0.073243 | 123.8708 | 61.4273 | -0.17853 | 123.8937 | -0.073243 | 61.4273 | 123.6603 | 123.8708 | -124.0585 | -124.1272
264.7188 | 124.0585 | -61.3998 | 62.5626 | -0.22255 | 0.0068381 | 0.0059366 | -0.0028476 | 0.068152 | -0.0014013 | 0.070504 | -61.528 | 62.4619 | -61.5463 | -61.6013 | 62.2604 | 0.073242 | 0.15564 | 0.30212 | 62.5031 | -61.5829 | -0.14648 | -0.10071 | -0.12817 | -0.20142 | -0.30212 | -0.18311 | -0.059509 | 0.018311 | 61.5555 | 61.702 | 123.6603 | 123.8617 | -0.12817 | 123.9029 | 61.4731 | -0.18311 | 123.8617 | -0.12817 | 61.4731 | 123.6603 | 123.9029 | -124.1089 | -124.1455
265.7188 | 124.1455 | -61.3953 | 62.5671 | -0.1844 | 0.0057699 | 0.0093546 | -0.0034886 | 0.066657 | 0.00073487 | 0.069863 | -61.496 | 62.4252 | -61.5234 | -61.5829 | 62.2787 | 0.10529 | 0.13275 | 0.1236 | 62.471 | -61.5738 | -0.12817 | -0.14191 | -0.10071 | -0.18768 | -0.28839 | -0.17853 | -0.096131 | 0.027465 | 61.528 | 61.5189 | 123.674 | 123.8205 | -0.10071 | 123.8663 | 61.5005 | -0.17853 | 123.8205 | -0.10071 | 61.5005 | 123.674 | 123.8663 | -124.0906 | -124.1409
266.7188 | 124.118 | -61.3998 | 62.59 | -0.20729 | 0.0076925 | 0.012773 | -0.00092496 | 0.067084 | -0.0014013 | 0.071145 | -61.5143 | 62.4573 | -61.5463 | -61.6104 | 62.2742 | 0.068665 | 0.12817 | 0.091553 | 62.4664 | -61.5921 | -0.14648 | -0.13275 | -0.11444 | -0.21057 | -0.31586 | -0.19226 | -0.1236 | 0.032044 | 61.528 | 61.4914 | 123.674 | 123.8571 | -0.11444 | 123.8663 | 61.4685 | -0.19226 | 123.8571 | -0.11444 | 61.4685 | 123.674 | 123.8663 | -124.1364 | -124.1821
267.7188 | 124.1455 | -61.3724 | 62.5488 | -0.23781 | 0.0057699 | 0.007432 | -0.001566 | 0.068152 | -0.0020421 | 0.068582 | -61.4502 | 62.4115 | -61.5234 | -61.5601 | 62.3154 | 0.12817 | 0.11444 | 0.15106 | 62.471 | -61.5555 | -0.15106 | -0.13733 | -0.07782 | -0.18768 | -0.23346 | -0.18311 | -0.07782 | 0.073242 | 61.4868 | 61.5234 | 123.6877 | 123.7839 | -0.07782 | 123.8434 | 61.5005 | -0.18311 | 123.7839 | -0.07782 | 61.5005 | 123.6877 | 123.8434 | -124.0723 | -124.1043
268.7188 | 124.2096 | -61.3815 | 62.558 | -0.17677 | 0.0068381 | 0.0070048 | -0.0037022 | 0.064948 | -0.0016149 | 0.069436 | -61.4182 | 62.384 | -61.5097 | -61.5097 | 62.3383 | 0.16022 | 0.032043 | 0.20599 | 62.4207 | -61.5326 | -0.12817 | -0.17395 | -0.036621 | -0.12817 | -0.21973 | -0.15106 | -0.13733 | 0.091553 | 61.4136 | 61.5875 | 123.7198 | 123.7656 | -0.036621 | 123.8022 | 61.5417 | -0.15106 | 123.7656 | -0.036621 | 61.5417 | 123.7198 | 123.8022 | -124.0677 | -124.0906
269.7188 | 124.1821 | -61.377 | 62.5488 | -0.10048 | 0.01047 | 0.016191 | 0.0046292 | 0.067084 | -0.0026831 | 0.066445 | -61.496 | 62.4344 | -61.5463 | -61.5692 | 62.2833 | 0.091553 | 0.027466 | 0.11444 | 62.4481 | -61.5738 | -0.16937 | -0.11444 | -0.11902 | -0.19226 | -0.2655 | -0.19684 | -0.10071 | 0.050354 | 61.4044 | 61.4914 | 123.6603 | 123.8113 | -0.11902 | 123.8251 | 61.4685 | -0.19684 | 123.8113 | -0.11902 | 61.4685 | 123.6603 | 123.8251 | -124.0952 | -124.1226
270.7188 | 124.2783 | -61.3632 | 62.5076 | -0.10811 | 0.0066245 | 0.0055094 | -0.0045566 | 0.067511 | -0.0033239 | 0.071145 | -61.4502 | 62.3657 | -61.5234 | -61.5051 | 62.3611 | 0.14191 | -0.082397 | 0.20142 | 62.4207 | -61.5417 | -0.16022 | -0.14191 | -0.086975 | -0.14191 | -0.14648 | -0.17853 | -0.086975 | 0.073242 | 61.2808 | 61.5646 | 123.7244 | 123.7289 | -0.086975 | 123.7839 | 61.5051 | -0.17853 | 123.7289 | -0.086975 | 61.5051 | 123.7244 | 123.7839 | -124.0311 | -124.0494
271.7188 | 124.2599 | -61.3495 | 62.5442 | -0.16151 | 0.0023519 | 0.01085 | -7.0562e-05 | 0.064521 | -0.0016149 | 0.068582 | -61.4227 | 62.3749 | -61.4777 | -61.4868 | 62.3611 | 0.16937 | -0.07782 | 0.23804 | 62.3795 | -61.5463 | -0.12817 | -0.16937 | -0.073242 | -0.13733 | -0.1831 | -0.19684 | -0.16479 | 0.054932 | 61.2717 | 61.5875 | 123.7106 | 123.7244 | -0.073242 | 123.7289 | 61.5189 | -0.19684 | 123.7244 | -0.073242 | 61.5189 | 123.7106 | 123.7289 | -124.0219 | -124.0906
272.7188 | 124.2599 | -61.3541 | 62.5214 | -0.08522 | 0.0057699 | 0.0042276 | 0.0014248 | 0.064521 | -0.0018285 | 0.068795 | -61.4548 | 62.3795 | -61.4914 | -61.5143 | 62.3428 | 0.14648 | -0.059509 | 0.18768 | 62.4069 | -61.528 | -0.13733 | -0.14191 | -0.10071 | -0.16022 | -0.17853 | -0.17395 | -0.11444 | 0.036621 | 61.2946 | 61.5417 | 123.6969 | 123.7335 | -0.10071 | 123.761 | 61.5005 | -0.17395 | 123.7335 | -0.10071 | 61.5005 | 123.6969 | 123.761 | -124.0128 | -124.0494
273.7188 | 124.2691 | -61.3403 | 62.5351 | -0.09285 | 0.0049155 | 0.0087138 | -0.00092496 | 0.06623 | -0.0014013 | 0.066873 | -61.4365 | 62.3657 | -61.5097 | -61.4868 | 62.3611 | 0.16937 | -0.059509 | 0.24261 | 62.3978 | -61.5326 | -0.16937 | -0.16937 | -0.09613 | -0.14648 | -0.17395 | -0.19226 | -0.13733 | 0.073243 | 61.2808 | 61.5829 | 123.7015 | 123.7061 | -0.09613 | 123.7381 | 61.5097 | -0.19226 | 123.7061 | -0.09613 | 61.5097 | 123.7015 | 123.7381 | -124.0448 | -124.0677
274.7188 | 124.1409 | -61.3861 | 62.5854 | -0.131 | 0.0047019 | 0.010209 | 0.002493 | 0.063452 | -0.0026831 | 0.068368 | -61.4822 | 62.471 | -61.5189 | -61.5692 | 62.2604 | 0.073242 | 0.10529 | 0.10529 | 62.471 | -61.6058 | -0.13275 | -0.11444 | -0.096131 | -0.18311 | -0.32501 | -0.21973 | -0.11444 | 0.036621 | 61.4914 | 61.4914 | 123.6465 | 123.8571 | -0.096131 | 123.8571 | 61.4594 | -0.21973 | 123.8571 | -0.096131 | 61.4594 | 123.6465 | 123.8571 | -124.1043 | -124.1913
275.7188 | 124.2462 | -61.3541 | 62.5214 | -0.0089264 | 0.0053427 | 0.0082864 | -0.0045566 | 0.064307 | -0.0022559 | 0.068582 | -61.4777 | 62.3795 | -61.496 | -61.5372 | 62.3108 | 0.09613 | -0.064087 | 0.15106 | 62.439 | -61.5372 | -0.14191 | -0.14191 | -0.1236 | -0.18311 | -0.21057 | -0.18311 | -0.082397 | 0.018311 | 61.29 | 61.5051 | 123.6649 | 123.7335 | -0.1236 | 123.793 | 61.4502 | -0.18311 | 123.7335 | -0.1236 | 61.4502 | 123.6649 | 123.793 | -124.0173 | -124.0585
276.7188 | 124.2279 | -61.3724 | 62.5305 | 0.021591 | 0.0059835 | 0.013627 | -0.0011386 | 0.062384 | -0.0014013 | 0.069863 | -61.5097 | 62.3749 | -61.5417 | -61.5646 | 62.2879 | 0.068665 | -0.082397 | 0.1236 | 62.4161 | -61.5601 | -0.16937 | -0.15564 | -0.13733 | -0.19226 | -0.24262 | -0.18768 | -0.11444 | 0.032043 | 61.29 | 61.496 | 123.6603 | 123.7473 | -0.13733 | 123.7885 | 61.441 | -0.18768 | 123.7473 | -0.13733 | 61.441 | 123.6603 | 123.7885 | -124.0723 | -124.0906
277.7188 | 124.2142 | -61.3861 | 62.5305 | 0.10551 | 0.0025655 | 0.0072184 | -0.00071136 | 0.063452 | -0.0018285 | 0.067941 | -61.4914 | 62.3474 | -61.5326 | -61.5692 | 62.265 | 0.022888 | -0.09613 | 0.068665 | 62.4069 | -61.5601 | -0.14648 | -0.18311 | -0.10529 | -0.18311 | -0.2655 | -0.17395 | -0.1236 | 0.041199 | 61.29 | 61.4548 | 123.6511 | 123.7335 | -0.10529 | 123.793 | 61.409 | -0.17395 | 123.7335 | -0.10529 | 61.409 | 123.6511 | 123.793 | -124.0631 | -124.0906
278.7188 | 124.2279 | -61.3907 | 62.4939 | 0.17418 | 0.0051291 | 0.010636 | -0.0019932 | 0.062171 | -0.0011877 | 0.067941 | -61.4731 | 62.3383 | -61.5463 | -61.5463 | 62.2971 | 0.036621 | -0.14648 | 0.086975 | 62.3657 | -61.5829 | -0.15564 | -0.15564 | -0.082397 | -0.15564 | -0.19684 | -0.19226 | -0.12817 | 0.073243 | 61.2442 | 61.4777 | 123.6877 | 123.7289 | -0.082397 | 123.7564 | 61.4273 | -0.19226 | 123.7289 | -0.082397 | 61.4273 | 123.6877 | 123.7564 | -124.0402 | -124.0768
279.7188 | 124.2233 | -61.3953 | 62.5305 | 0.75401 | 0.0061971 | 0.011491 | -0.00049776 | 0.066443 | -0.0024695 | 0.070291 | -61.496 | 62.384 | -61.5234 | -61.5738 | 62.265 | 0.045776 | -0.054932 | 0.09613 | 62.4298 | -61.5463 | -0.12817 | -0.14648 | -0.10071 | -0.17853 | -0.2655 | -0.15106 | -0.10071 | 0.027465 | 61.3403 | 61.4914 | 123.6603 | 123.7793 | -0.10071 | 123.8251 | 61.441 | -0.15106 | 123.7793 | -0.10071 | 61.441 | 123.6603 | 123.8251 | -124.054 | -124.0768
280.7188 | 124.2325 | -61.377 | 62.5259 | 0.074997 | 0.0047019 | 0.010636 | -0.0022068 | 0.063025 | 0.0013757 | 0.068795 | -61.496 | 62.3611 | -61.5417 | -61.5646 | 62.2742 | 0.022888 | 0.064087 | 0.036621 | 62.4298 | -61.5555 | -0.16479 | -0.16479 | -0.11902 | -0.18768 | -0.25177 | -0.17853 | -0.09613 | 0.045776 | 61.441 | 61.4136 | 123.6511 | 123.7381 | -0.11902 | 123.8068 | 61.3998 | -0.17853 | 123.7381 | -0.11902 | 61.3998 | 123.6511 | 123.8068 | -124.0677 | -124.0814
281.7188 | 124.2096 | -61.3815 | 62.5122 | 0.15892 | 0.0047019 | 0.010636 | -0.0017796 | 0.065802 | 0.00030767 | 0.069863 | -61.5005 | 62.3703 | -61.5326 | -61.5555 | 62.2879 | 0.036621 | -0.082397 | 0.07782 | 62.3795 | -61.5829 | -0.15106 | -0.14191 | -0.11902 | -0.17395 | -0.2243 | -0.20142 | -0.13275 | 0.032044 | 61.2991 | 61.4594 | 123.6694 | 123.7518 | -0.11902 | 123.761 | 61.4182 | -0.20142 | 123.7518 | -0.11902 | 61.4182 | 123.6694 | 123.761 | -124.0448 | -124.0952
282.7188 | 124.2142 | -61.3678 | 62.5259 | 0.10551 | 0.0070517 | 0.010423 | 0.0014248 | 0.06388 | -0.0018285 | 0.069009 | -61.4914 | 62.3566 | -61.5234 | -61.5784 | 62.265 | 0.036621 | -0.11444 | 0.068665 | 62.3795 | -61.5921 | -0.15564 | -0.16937 | -0.1236 | -0.21057 | -0.26093 | -0.2243 | -0.14648 | 0.032043 | 61.2534 | 61.4365 | 123.6328 | 123.7244 | -0.1236 | 123.7473 | 61.4044 | -0.2243 | 123.7244 | -0.1236 | 61.4044 | 123.6328 | 123.7473 | -124.0494 | -124.118
283.7188 | 124.2279 | -61.3724 | 62.5031 | 0.097885 | 0.0059835 | 0.01085 | -0.001566 | 0.064948 | -0.0018285 | 0.06965 | -61.4594 | 62.3566 | -61.5326 | -61.5555 | 62.2742 | 0.032043 | -0.13275 | 0.07782 | 62.3703 | -61.5738 | -0.16022 | -0.14648 | -0.086976 | -0.18311 | -0.22888 | -0.20142 | -0.13275 | 0.073242 | 61.2396 | 61.4502 | 123.6465 | 123.7289 | -0.086976 | 123.7427 | 61.4044 | -0.20142 | 123.7289 | -0.086976 | 61.4044 | 123.6465 | 123.7427 | -124.0356 | -124.0768
284.7188 | 124.3103 | -61.3586 | 62.5031 | -0.12337 | 0.0068381 | 0.012345 | -0.0011386 | 0.062384 | -0.0022559 | 0.069863 | -61.409 | 62.3795 | -61.5326 | -61.4548 | 62.384 | 0.17853 | -0.082397 | 0.22888 | 62.3886 | -61.5646 | -0.17395 | -0.1236 | -0.050354 | -0.09613 | -0.11902 | -0.20599 | -0.11444 | 0.1236 | 61.2762 | 61.5875 | 123.7427 | 123.7381 | -0.050354 | 123.7473 | 61.5372 | -0.20599 | 123.7381 | -0.050354 | 61.5372 | 123.7427 | 123.7473 | -124.0356 | -124.0677
285.7188 | 124.2874 | -61.3632 | 62.5351 | 0.13603 | 0.0072653 | 0.009141 | 0.0056972 | 0.06623 | -0.0014013 | 0.069222 | -61.4273 | 62.3566 | -61.528 | -61.5143 | 62.3108 | 0.045776 | -0.37079 | -0.15106 | 62.3337 | -61.6013 | -0.1648 | -0.17853 | -0.064087 | -0.15106 | -0.2243 | -0.23804 | -0.20142 | 0.10071 | 60.9924 | 61.2122 | 123.674 | 123.7198 | -0.064087 | 123.6969 | 61.409 | -0.23804 | 123.7198 | -0.064087 | 61.409 | 123.674 | 123.6969 | -124.0631 | -124.1364
286.7188 | 124.2371 | -61.3861 | 62.4756 | 0.3878 | 0.010256 | 0.0087138 | 0.0014248 | 0.065802 | -0.00076053 | 0.068582 | -61.409 | 62.3611 | -61.496 | -61.5097 | 62.2925 | 0.073242 | -0.19226 | 0.10071 | 62.384 | -61.5829 | -0.10986 | -0.11444 | -0.022889 | -0.1236 | -0.18311 | -0.19684 | -0.091553 | 0.086975 | 61.1938 | 61.4868 | 123.6786 | 123.7473 | -0.022889 | 123.7701 | 61.4594 | -0.19684 | 123.7473 | -0.022889 | 61.4594 | 123.6786 | 123.7701 | -123.9716 | -124.0585
287.7188 | 124.2279 | -61.377 | 62.4939 | 0.090256 | 0.0076925 | 0.0093546 | 0.0029202 | 0.065161 | -0.0014013 | 0.068582 | -61.4639 | 62.3749 | -61.528 | -61.5051 | 62.3108 | 0.068665 | -0.15564 | 0.091553 | 62.352 | -61.5784 | -0.15106 | -0.11902 | -0.086975 | -0.12817 | -0.1831 | -0.20142 | -0.14191 | 0.064087 | 61.2213 | 61.4685 | 123.6877 | 123.7518 | -0.086975 | 123.7289 | 61.4456 | -0.20142 | 123.7518 | -0.086975 | 61.4456 | 123.6877 | 123.7289 | -124.0219 | -124.0723
288.7188 | 124.2233 | -61.3815 | 62.4893 | 0.23521 | 0.0066245 | 0.011064 | 0.00078404 | 0.062812 | -0.00097413 | 0.065164 | -61.4456 | 62.3795 | -61.5097 | -61.528 | 62.3108 | 0.054932 | -0.18768 | 0.10529 | 62.3703 | -61.5738 | -0.12817 | -0.10986 | -0.064087 | -0.14648 | -0.17853 | -0.19226 | -0.11902 | 0.064087 | 61.1938 | 61.4868 | 123.6923 | 123.761 | -0.064087 | 123.7518 | 61.4365 | -0.19226 | 123.761 | -0.064087 | 61.4365 | 123.6923 | 123.7518 | -123.999 | -124.0631
289.7188 | 124.2371 | -61.3861 | 62.5122 | -0.069961 | 0.0083333 | 0.0085 | -0.0017796 | 0.06388 | -0.00011953 | 0.069222 | -61.4685 | 62.3611 | -61.5372 | -61.5097 | 62.3383 | 0.13275 | -0.073242 | 0.17395 | 62.3886 | -61.5784 | -0.15106 | -0.15106 | -0.082398 | -0.1236 | -0.17395 | -0.19226 | -0.1236 | 0.068664 | 61.3129 | 61.5601 | 123.7244 | 123.7473 | -0.082398 | 123.7747 | 61.5189 | -0.19226 | 123.7473 | -0.082398 | 61.5189 | 123.7244 | 123.7747 | -124.0494 | -124.0906
290.7188 | 124.205 | -61.3632 | 62.5031 | 0.19707 | 0.0076925 | 0.0065774 | 0.0037746 | 0.064734 | -0.0022559 | 0.069009 | -61.409 | 62.3978 | -61.5005 | -61.528 | 62.3428 | 0.068665 | -0.50354 | 0.2655 | 62.3337 | -61.6013 | -0.13733 | -0.10529 | -0.045777 | -0.1648 | -0.16022 | -0.23804 | -0.16937 | 0.091552 | 60.8597 | 61.6287 | 123.7061 | 123.761 | -0.045777 | 123.6969 | 61.4319 | -0.23804 | 123.761 | -0.045777 | 61.4319 | 123.7061 | 123.6969 | -124.0036 | -124.1043
291.7188 | 124.1638 | -61.3907 | 62.4985 | 0.15892 | 0.0083333 | 0.011277 | 0.00527 | 0.06623 | 0.00073487 | 0.070291 | -61.5143 | 62.4435 | -61.5509 | -61.6287 | 62.233 | -0.027466 | -0.064087 | -0.004578 | 62.4161 | -61.6013 | -0.16022 | -0.054932 | -0.1236 | -0.23804 | -0.2655 | -0.21057 | -0.082397 | 0.036621 | 61.3266 | 61.3861 | 123.6237 | 123.8342 | -0.1236 | 123.8068 | 61.3632 | -0.21057 | 123.8342 | -0.1236 | 61.3632 | 123.6237 | 123.8068 | -124.0494 | -124.0997
292.7188 | 124.1226 | -61.3998 | 62.5168 | 0.12077 | 0.0091879 | 0.0085 | 0.0027066 | 0.066443 | -0.00097413 | 0.069009 | -61.5189 | 62.4619 | -61.5417 | -61.6058 | 62.233 | -0.032043 | -0.032043 | -0.032043 | 62.439 | -61.6287 | -0.14191 | -0.054932 | -0.11902 | -0.20599 | -0.28381 | -0.22888 | -0.07782 | 0.022888 | 61.3678 | 61.3678 | 123.6328 | 123.8617 | -0.11902 | 123.8388 | 61.3678 | -0.22888 | 123.8617 | -0.11902 | 61.3678 | 123.6328 | 123.8388 | -124.0585 | -124.1455
293.7188 | 124.2096 | -61.4227 | 62.4893 | 0.15129 | 0.0089743 | 0.012986 | 0.0022794 | 0.069007 | -0.00076053 | 0.071145 | -61.4914 | 62.4619 | -61.5555 | -61.5921 | 62.2559 | -0.004578 | -0.091553 | 0.009155 | 62.4115 | -61.615 | -0.13275 | -0.027466 | -0.068665 | -0.16937 | -0.23346 | -0.19226 | -0.07782 | 0.064087 | 61.3312 | 61.4319 | 123.6786 | 123.8846 | -0.068665 | 123.8342 | 61.4182 | -0.19226 | 123.8846 | -0.068665 | 61.4182 | 123.6786 | 123.8342 | -124.0448 | -124.1043
294.7188 | 124.1913 | -61.3953 | 62.5122 | -0.1844 | 0.0076925 | 0.007432 | -0.0039158 | 0.067939 | -0.0028967 | 0.070291 | -61.5097 | 62.3886 | -61.5326 | -61.5692 | 62.3016 | 0.059509 | -0.045776 | 0.09613 | 62.4115 | -61.5509 | -0.13733 | -0.1236 | -0.11444 | -0.17395 | -0.21057 | -0.15564 | -0.10071 | 0.022888 | 61.3495 | 61.4914 | 123.6969 | 123.7839 | -0.11444 | 123.8068 | 61.4548 | -0.15564 | 123.7839 | -0.11444 | 61.4548 | 123.6969 | 123.8068 | -124.0448 | -124.0631
295.7188 | 124.1913 | -61.3907 | 62.4893 | 0.21233 | 0.0081197 | 0.0080728 | 0.0029202 | 0.06687 | -0.0011877 | 0.070077 | -61.5051 | 62.4619 | -61.5189 | -61.5921 | 62.2787 | 0.009155 | -0.11444 | 0.050354 | 62.384 | -61.6104 | -0.12817 | -0.027466 | -0.11444 | -0.20142 | -0.21057 | -0.21973 | -0.10529 | 0.013733 | 61.2762 | 61.441 | 123.6694 | 123.8525 | -0.11444 | 123.7747 | 61.3998 | -0.21973 | 123.8525 | -0.11444 | 61.3998 | 123.6694 | 123.7747 | -124.0082 | -124.0997
296.7188 | 124.1821 | -61.4182 | 62.5168 | 0.19707 | 0.0081197 | 0.012986 | 0.002493 | 0.068366 | -0.0018285 | 0.06965 | -61.5189 | 62.439 | -61.5372 | -61.6058 | 62.233 | -0.013733 | -0.054932 | 0 | 62.4115 | -61.6241 | -0.11902 | -0.07782 | -0.10071 | -0.18768 | -0.28381 | -0.20599 | -0.10529 | 0.01831 | 61.3632 | 61.4182 | 123.6511 | 123.8571 | -0.10071 | 123.8297 | 61.4044 | -0.20599 | 123.8571 | -0.10071 | 61.4044 | 123.6511 | 123.8297 | -124.054 | -124.1409
297.7188 | 124.1089 | -61.409 | 62.5122 | 0.17418 | 0.0085471 | 0.011064 | 0.0033474 | 0.067725 | -0.0024695 | 0.071145 | -61.5143 | 62.4802 | -61.5738 | -61.6196 | 62.233 | -0.022888 | -0.013733 | -0.022888 | 62.4207 | -61.6379 | -0.16479 | -0.032043 | -0.10529 | -0.21057 | -0.27924 | -0.22888 | -0.091553 | 0.05951 | 61.3953 | 61.3861 | 123.642 | 123.8892 | -0.10529 | 123.8297 | 61.3861 | -0.22888 | 123.8892 | -0.10529 | 61.3861 | 123.642 | 123.8297 | -124.086 | -124.1501
298.7188 | 124.1135 | -61.4044 | 62.5305 | 0.067368 | 0.0089743 | 0.011064 | 0.0029202 | 0.068366 | -0.0018285 | 0.068582 | -61.5234 | 62.4619 | -61.5463 | -61.6287 | 62.1964 | -0.045776 | 0.036621 | 0.004578 | 62.4298 | -61.6333 | -0.14191 | -0.068665 | -0.11902 | -0.2243 | -0.33417 | -0.22888 | -0.10071 | 0.022889 | 61.441 | 61.409 | 123.6008 | 123.8663 | -0.11902 | 123.8342 | 61.3586 | -0.22888 | 123.8663 | -0.11902 | 61.3586 | 123.6008 | 123.8342 | -124.0768 | -124.1638
299.7188 | 124.2691 | -61.3724 | 62.4619 | 0.21996 | 0.0083333 | 0.018327 | -0.0017796 | 0.067939 | -0.0022559 | 0.06965 | -61.6379 | 62.3383 | -61.5738 | -61.5372 | 62.2925 | 0.091553 | -0.16937 | 0.082397 | 62.384 | -61.5829 | -0.20142 | -0.1236 | -0.2655 | -0.1648 | -0.16937 | -0.21057 | -0.07782 | -0.064086 | 61.203 | 61.4548 | 123.6649 | 123.7106 | -0.2655 | 123.7564 | 61.4639 | -0.21057 | 123.7106 | -0.2655 | 61.4639 | 123.6649 | 123.7564 | -124.0356 | -124.0448
300.7188 | 124.1089 | -61.409 | 62.5351 | 0.13603 | 0.0079061 | 0.012773 | 0.0046292 | 0.069007 | -0.0018285 | 0.069222 | -61.5097 | 62.4893 | -61.5509 | -61.647 | 62.2238 | -0.036621 | 0.036621 | -0.027466 | 62.4344 | -61.647 | -0.14191 | -0.045776 | -0.10071 | -0.23804 | -0.31128 | -0.23804 | -0.10071 | 0.041198 | 61.4456 | 61.3815 | 123.6328 | 123.8983 | -0.10071 | 123.8434 | 61.3724 | -0.23804 | 123.8983 | -0.10071 | 61.3724 | 123.6328 | 123.8434 | -124.086 | -124.1821
301.7188 | 124.0952 | -61.409 | 62.5168 | 0.13603 | 0.0074789 | 0.011277 | 0.00527 | 0.071357 | -0.00097413 | 0.067941 | -61.8027 | 62.4252 | -61.615 | -61.6287 | 62.1597 | -0.068665 | 0.073242 | -0.041199 | 62.4344 | -61.6196 | -0.20599 | -0.091553 | -0.39368 | -0.21973 | -0.35706 | -0.21057 | -0.082398 | -0.18768 | 61.4822 | 61.3678 | 123.5687 | 123.8342 | -0.39368 | 123.8434 | 61.3403 | -0.21057 | 123.8342 | -0.39368 | 61.3403 | 123.5687 | 123.8434 | -124.1318 | -124.1364
302.7188 | 124.0402 | -61.4639 | 62.5397 | 0.11314 | 0.0083333 | 0.013627 | 0.0016384 | 0.069007 | -0.0020421 | 0.068368 | -61.5372 | 62.5122 | -61.5646 | -61.6516 | 62.1918 | -0.032043 | 0.013733 | -0.027466 | 62.4252 | -61.6425 | -0.10071 | -0.027466 | -0.073242 | -0.18768 | -0.3479 | -0.17853 | -0.11444 | 0.027466 | 61.4777 | 61.4365 | 123.6557 | 123.9761 | -0.073242 | 123.8892 | 61.4319 | -0.17853 | 123.9761 | -0.073242 | 61.4319 | 123.6557 | 123.8892 | -124.1043 | -124.1821
303.7188 | 124.0906 | -61.4319 | 62.5351 | 0.03685 | 0.011111 | 0.010636 | 0.0012112 | 0.069007 | -0.0016149 | 0.069863 | -61.5234 | 62.4939 | -61.5417 | -61.6333 | 62.2101 | -0.050354 | 0.045776 | -0.022888 | 62.4527 | -61.615 | -0.10986 | -0.041199 | -0.091552 | -0.20142 | -0.32501 | -0.1831 | -0.082397 | 0.018311 | 61.4777 | 61.409 | 123.642 | 123.9258 | -0.091552 | 123.8846 | 61.3815 | -0.1831 | 123.9258 | -0.091552 | 61.3815 | 123.642 | 123.8846 | -124.0768 | -124.1501
304.7188 | 124.2279 | -61.377 | 62.4756 | 0.13603 | 0.0070517 | 0.0097818 | -0.0039158 | 0.068793 | -0.0026831 | 0.068795 | -61.4685 | 62.3703 | -61.5372 | -61.5601 | 62.3108 | 0.064087 | -0.15564 | 0.10071 | 62.3886 | -61.5509 | -0.16022 | -0.10529 | -0.091553 | -0.18311 | -0.16479 | -0.17395 | -0.086975 | 0.068664 | 61.2213 | 61.4777 | 123.6877 | 123.7473 | -0.091553 | 123.7656 | 61.441 | -0.17395 | 123.7473 | -0.091553 | 61.441 | 123.6877 | 123.7656 | -124.0128 | -124.0265
305.7188 | 124.1684 | -61.4044 | 62.5397 | 0.35728 | 0.0079061 | 0.011491 | 0.0027066 | 0.06623 | -0.00054693 | 0.068154 | -61.4182 | 62.4939 | -61.5372 | -61.5372 | 62.2833 | 0.082397 | 0.013733 | 0.10529 | 62.4252 | -61.6196 | -0.13275 | -0.045777 | -0.013733 | -0.13275 | -0.25635 | -0.21515 | -0.11444 | 0.11902 | 61.4182 | 61.5097 | 123.6877 | 123.8983 | -0.013733 | 123.8297 | 61.4868 | -0.21515 | 123.8983 | -0.013733 | 61.4868 | 123.6877 | 123.8297 | -124.0768 | -124.1592
306.7188 | 124.1638 | -61.4044 | 62.5397 | -0.0012969 | 0.0089743 | 0.01085 | 0.00078404 | 0.06922 | -0.0014013 | 0.070077 | -61.4548 | 62.4939 | -61.5463 | -61.5692 | 62.265 | 0.050354 | 0.022888 | 0.07782 | 62.4619 | -61.5829 | -0.14191 | -0.045777 | -0.050354 | -0.1648 | -0.27466 | -0.17853 | -0.07782 | 0.091553 | 61.4273 | 61.4822 | 123.6694 | 123.8983 | -0.050354 | 123.8663 | 61.4548 | -0.17853 | 123.8983 | -0.050354 | 61.4548 | 123.6694 | 123.8663 | -124.086 | -124.1226
307.7188 | 124.1776 | -61.4182 | 62.5076 | -0.031814 | 0.0085471 | 0.0078592 | 0.0029202 | 0.069007 | -0.0020421 | 0.068795 | -61.4365 | 62.5168 | -61.5326 | -61.5692 | 62.2833 | 0.068665 | 0.022888 | 0.086975 | 62.4664 | -61.615 | -0.11444 | 0.009156 | -0.01831 | -0.15106 | -0.2243 | -0.19684 | -0.041198 | 0.096131 | 61.441 | 61.5051 | 123.7015 | 123.9349 | -0.01831 | 123.8846 | 61.4868 | -0.19684 | 123.9349 | -0.01831 | 61.4868 | 123.7015 | 123.8846 | -124.0402 | -124.1226
308.7188 | 124.1409 | -61.4273 | 62.5397 | -0.016556 | 0.0076925 | 0.010636 | 0.002493 | 0.071784 | -0.0011877 | 0.070504 | -61.4594 | 62.5122 | -61.5417 | -61.5921 | 62.2421 | 0.027466 | 0.032043 | 0.045776 | 62.4481 | -61.6104 | -0.11444 | -0.027466 | -0.032044 | -0.16479 | -0.29755 | -0.18311 | -0.091553 | 0.082397 | 61.4594 | 61.4731 | 123.6694 | 123.9395 | -0.032044 | 123.8754 | 61.4548 | -0.18311 | 123.9395 | -0.032044 | 61.4548 | 123.6694 | 123.8754 | -124.0814 | -124.1501
309.7188 | 124.2508 | -61.3541 | 62.4939 | 1.7229 | 0.0089743 | 0.011277 | -0.002634 | 0.070929 | -0.0022559 | 0.06965 | -61.4365 | 62.3795 | -61.5417 | -61.5601 | 62.3566 | 0.086975 | -0.20599 | 0.091553 | 62.3978 | -61.5601 | -0.18768 | -0.11444 | -0.082397 | -0.20599 | -0.13733 | -0.20599 | -0.09613 | 0.10529 | 61.1481 | 61.4456 | 123.7106 | 123.7335 | -0.082397 | 123.7518 | 61.441 | -0.20599 | 123.7335 | -0.082397 | 61.441 | 123.7106 | 123.7518 | -124.0356 | -124.054
310.7188 | 124.1272 | -61.409 | 62.5763 | 0.029221 | 0.0068381 | 0.0076456 | 0.003561 | 0.069007 | -0.0033239 | 0.068154 | -61.4731 | 62.471 | -61.5509 | -61.615 | 62.2375 | 0.013733 | 0.032043 | 0.018311 | 62.4573 | -61.6333 | -0.14191 | -0.10529 | -0.064086 | -0.20599 | -0.33874 | -0.2243 | -0.11902 | 0.07782 | 61.441 | 61.4273 | 123.6465 | 123.88 | -0.064086 | 123.8663 | 61.4227 | -0.2243 | 123.88 | -0.064086 | 61.4227 | 123.6465 | 123.8663 | -124.1272 | -124.2096
311.7188 | 124.2004 | -61.3998 | 62.558 | -0.062332 | 0.0089743 | 0.010209 | -7.0562e-05 | 0.069434 | -0.0028967 | 0.068154 | -61.4685 | 62.5031 | -61.528 | -61.496 | 62.2513 | 0.086975 | 0.036621 | 0.10986 | 62.4527 | -61.615 | -0.12817 | -0.054931 | -0.068665 | -0.096131 | -0.3067 | -0.21515 | -0.10529 | 0.059509 | 61.4365 | 61.5097 | 123.6511 | 123.9029 | -0.068665 | 123.8525 | 61.4868 | -0.21515 | 123.9029 | -0.068665 | 61.4868 | 123.6511 | 123.8525 | -124.086 | -124.173
312.7188 | 124.1592 | -61.3998 | 62.5534 | -0.20729 | 0.0083333 | 0.015763 | 0.00057044 | 0.06922 | -0.0011877 | 0.069863 | -61.4685 | 62.4893 | -61.5417 | -61.5829 | 62.2833 | 0.082397 | 0.11444 | 0.11902 | 62.4802 | -61.6013 | -0.14191 | -0.064087 | -0.068665 | -0.18311 | -0.27008 | -0.20142 | -0.073242 | 0.073242 | 61.5143 | 61.5189 | 123.6832 | 123.8892 | -0.068665 | 123.88 | 61.4822 | -0.20142 | 123.8892 | -0.068665 | 61.4822 | 123.6832 | 123.88 | -124.0952 | -124.1547
313.7188 | 124.1684 | -61.3861 | 62.5351 | -0.16151 | 0.0089743 | 0.012559 | 0.001852 | 0.068793 | -0.00076053 | 0.068582 | -61.441 | 62.4985 | -61.5417 | -61.5417 | 62.2925 | 0.10529 | 0.059509 | 0.11902 | 62.4802 | -61.5784 | -0.15564 | -0.036621 | -0.054932 | -0.15564 | -0.24262 | -0.19226 | -0.054931 | 0.10071 | 61.4456 | 61.5051 | 123.6786 | 123.8846 | -0.054932 | 123.8663 | 61.4914 | -0.19226 | 123.8846 | -0.054932 | 61.4914 | 123.6786 | 123.8663 | -124.0768 | -124.1135
314.7188 | 124.2004 | -61.4273 | 62.5076 | 0.15892 | 0.0072653 | 0.012345 | -0.00028416 | 0.06922 | -0.0011877 | 0.070291 | -61.5097 | 62.4481 | -61.5509 | -61.6333 | 62.2284 | 0.004578 | -0.064087 | 0 | 62.4298 | -61.5784 | -0.1236 | -0.059509 | -0.082398 | -0.20599 | -0.27923 | -0.15106 | -0.077819 | 0.041198 | 61.3632 | 61.4273 | 123.6557 | 123.8754 | -0.082398 | 123.8571 | 61.4319 | -0.15106 | 123.8754 | -0.082398 | 61.4319 | 123.6557 | 123.8571 | -124.0585 | -124.086
315.7188 | 124.1226 | -61.4136 | 62.5351 | -0.13863 | 0.0072653 | 0.012773 | 0.0020656 | 0.069434 | -0.0037511 | 0.070718 | -61.4639 | 62.5076 | -61.5234 | -61.5738 | 62.2787 | 0.091553 | 0.032043 | 0.11902 | 62.4527 | -61.6287 | -0.10986 | -0.027466 | -0.050354 | -0.16022 | -0.25635 | -0.21515 | -0.082397 | 0.059509 | 61.4456 | 61.5326 | 123.6923 | 123.9212 | -0.050354 | 123.8663 | 61.5051 | -0.21515 | 123.9212 | -0.050354 | 61.5051 | 123.6923 | 123.8663 | -124.0585 | -124.1638
316.7188 | 124.1501 | -61.3861 | 62.5442 | -0.23018 | 0.0081197 | 0.013841 | 0.00057044 | 0.069648 | -0.00097413 | 0.071572 | -61.441 | 62.4847 | -61.528 | -61.5601 | 62.2787 | 0.09613 | 0.050354 | 0.11902 | 62.4527 | -61.5784 | -0.14191 | -0.059509 | -0.054932 | -0.17395 | -0.2655 | -0.19226 | -0.091552 | 0.086975 | 61.4365 | 61.5051 | 123.6649 | 123.8708 | -0.054932 | 123.8388 | 61.4822 | -0.19226 | 123.8708 | -0.054932 | 61.4822 | 123.6649 | 123.8388 | -124.0723 | -124.1226
317.7188 | 124.1821 | -61.3861 | 62.5442 | -0.23781 | 0.0094015 | 0.011704 | 0.00099764 | 0.069007 | -0.00097413 | 0.069222 | -61.4594 | 62.4939 | -61.5555 | -61.5646 | 62.3062 | 0.09613 | 0.068665 | 0.15106 | 62.4802 | -61.6058 | -0.16937 | -0.050354 | -0.073243 | -0.17853 | -0.23804 | -0.21973 | -0.064086 | 0.09613 | 61.4548 | 61.5372 | 123.6923 | 123.88 | -0.073243 | 123.8663 | 61.4822 | -0.21973 | 123.88 | -0.073243 | 61.4822 | 123.6923 | 123.8663 | -124.0997 | -124.1501
318.7188 | 124.1455 | -61.3953 | 62.5442 | -0.15388 | 0.0057699 | 0.012559 | 0.00014304 | 0.070929 | -0.0028967 | 0.069863 | -61.4914 | 62.4847 | -61.528 | -61.5829 | 62.2879 | 0.086975 | 0.10071 | 0.13275 | 62.5031 | -61.5921 | -0.13275 | -0.059509 | -0.09613 | -0.18768 | -0.25635 | -0.19684 | -0.041198 | 0.036621 | 61.496 | 61.528 | 123.6832 | 123.88 | -0.09613 | 123.8983 | 61.4822 | -0.19684 | 123.88 | -0.09613 | 61.4822 | 123.6832 | 123.8983 | -124.0723 | -124.1364
319.7188 | 124.1547 | -61.4136 | 62.5351 | -0.069961 | 0.0085471 | 0.012132 | -7.0562e-05 | 0.069648 | 9.4068e-05 | 0.069863 | -61.4365 | 62.471 | -61.528 | -61.5509 | 62.2787 | 0.10071 | 0.054932 | 0.14191 | 62.4756 | -61.5875 | -0.11444 | -0.064087 | -0.022888 | -0.13733 | -0.25635 | -0.17395 | -0.059509 | 0.091553 | 61.4685 | 61.5555 | 123.6923 | 123.8846 | -0.022888 | 123.8892 | 61.5143 | -0.17395 | 123.8846 | -0.022888 | 61.5143 | 123.6923 | 123.8892 | -124.0631 | -124.1226
320.7188 | 124.1135 | -61.4044 | 62.5442 | -0.21492 | 0.0070517 | 0.009141 | -0.0017796 | 0.069007 | -0.00054693 | 0.06965 | -61.5005 | 62.5031 | -61.5601 | -61.6104 | 62.2513 | 0.064087 | 0.13733 | 0.082397 | 62.4939 | -61.6013 | -0.15564 | -0.041198 | -0.09613 | -0.20599 | -0.29297 | -0.19684 | -0.050354 | 0.05951 | 61.5417 | 61.4868 | 123.6557 | 123.9075 | -0.09613 | 123.8983 | 61.4685 | -0.19684 | 123.9075 | -0.09613 | 61.4685 | 123.6557 | 123.8983 | -124.1043 | -124.1455
321.7188 | 124.1089 | -61.3953 | 62.5809 | -0.16914 | 0.0068381 | 0.007432 | -7.0562e-05 | 0.068793 | -0.00054693 | 0.069222 | -61.5097 | 62.4802 | -61.5509 | -61.6058 | 62.2421 | 0.064087 | 0.14191 | 0.10071 | 62.4847 | -61.5784 | -0.15564 | -0.10071 | -0.11444 | -0.21057 | -0.33875 | -0.18311 | -0.096131 | 0.041198 | 61.5372 | 61.496 | 123.6374 | 123.8754 | -0.11444 | 123.88 | 61.4594 | -0.18311 | 123.8754 | -0.11444 | 61.4594 | 123.6374 | 123.88 | -124.1318 | -124.1592
322.7188 | 124.1409 | -61.4182 | 62.5442 | -0.19203 | 0.0089743 | 0.0063638 | 0.0012112 | 0.067939 | 0.00052127 | 0.06965 | -61.5005 | 62.5122 | -61.5509 | -61.5921 | 62.2467 | 0.059509 | 0.12817 | 0.11444 | 62.4939 | -61.5921 | -0.13275 | -0.032043 | -0.082397 | -0.17395 | -0.29755 | -0.17395 | -0.050354 | 0.050354 | 61.5463 | 61.5326 | 123.6649 | 123.9304 | -0.082397 | 123.912 | 61.4777 | -0.17395 | 123.9304 | -0.082397 | 61.4777 | 123.6649 | 123.912 | -124.0952 | -124.1364
323.7188 | 124.1226 | -61.409 | 62.5397 | -0.19203 | 0.0079061 | 0.006791 | -0.001566 | 0.068152 | -0.0022559 | 0.071359 | -61.4914 | 62.4664 | -61.5463 | -61.5967 | 62.2513 | 0.068665 | 0.13733 | 0.086975 | 62.4893 | -61.6013 | -0.13733 | -0.073242 | -0.082397 | -0.18768 | -0.28839 | -0.19226 | -0.050354 | 0.054932 | 61.5463 | 61.496 | 123.6603 | 123.8754 | -0.082397 | 123.8983 | 61.4777 | -0.19226 | 123.8754 | -0.082397 | 61.4777 | 123.6603 | 123.8983 | -124.086 | -124.1409
324.7188 | 124.118 | -61.3861 | 62.5626 | -0.17677 | 0.0053427 | 0.010423 | -7.0562e-05 | 0.067939 | -0.0018285 | 0.06965 | -61.5097 | 62.4756 | -61.5738 | -61.615 | 62.2513 | 0.059509 | 0.15564 | 0.10986 | 62.4847 | -61.5921 | -0.18768 | -0.086975 | -0.1236 | -0.22888 | -0.31128 | -0.20599 | -0.07782 | 0.064087 | 61.5417 | 61.496 | 123.6374 | 123.8617 | -0.1236 | 123.8708 | 61.4456 | -0.20599 | 123.8617 | -0.1236 | 61.4456 | 123.6374 | 123.8708 | -124.1364 | -124.1547
325.7188 | 124.1089 | -61.3953 | 62.5854 | 1.1126 | 0.0059835 | 0.0072184 | -0.00071136 | 0.067939 | -0.0024695 | 0.06965 | -61.4548 | 62.4527 | -61.5509 | -61.6058 | 62.2604 | 0.059509 | 0.15106 | 0.091553 | 62.5076 | -61.5967 | -0.15564 | -0.13275 | -0.059509 | -0.21057 | -0.32501 | -0.20142 | -0.07782 | 0.09613 | 61.5463 | 61.4868 | 123.6557 | 123.848 | -0.059509 | 123.9029 | 61.4548 | -0.20142 | 123.848 | -0.059509 | 61.4548 | 123.6557 | 123.9029 | -124.1364 | -124.1821
326.7188 | 124.1547 | -61.3678 | 62.5351 | -0.23781 | 0.0066245 | 0.007432 | -0.0024204 | 0.066443 | -0.00054693 | 0.0673 | -61.441 | 62.4252 | -61.5097 | -61.5463 | 62.2925 | 0.11902 | 0.10986 | 0.16022 | 62.4985 | -61.5875 | -0.14191 | -0.10986 | -0.073242 | -0.17853 | -0.24262 | -0.21973 | -0.036621 | 0.068665 | 61.4777 | 61.528 | 123.6603 | 123.793 | -0.073242 | 123.8663 | 61.4868 | -0.21973 | 123.793 | -0.073242 | 61.4868 | 123.6603 | 123.8663 | -124.0448 | -124.1226
327.7188 | 124.1364 | -61.3724 | 62.5992 | -0.23018 | 0.0074789 | 0.0099954 | -0.00049776 | 0.067511 | 9.4068e-05 | 0.069436 | -61.5097 | 62.4435 | -61.5234 | -61.6104 | 62.2284 | 0.059509 | 0.14191 | 0.10529 | 62.471 | -61.5784 | -0.15106 | -0.15564 | -0.13733 | -0.23804 | -0.37079 | -0.20599 | -0.12817 | 0.013732 | 61.5143 | 61.4777 | 123.6008 | 123.8159 | -0.13733 | 123.8434 | 61.4319 | -0.20599 | 123.8159 | -0.13733 | 61.4319 | 123.6008 | 123.8434 | -124.1226 | -124.1776
328.7188 | 124.1409 | -61.3953 | 62.5717 | -0.22255 | 0.0066245 | 0.0093546 | -0.00049776 | 0.065375 | -0.0014013 | 0.068154 | -61.4777 | 62.4344 | -61.5326 | -61.5967 | 62.2513 | 0.068665 | 0.13275 | 0.13275 | 62.4802 | -61.6013 | -0.13733 | -0.13733 | -0.082397 | -0.20142 | -0.32043 | -0.20599 | -0.091552 | 0.054932 | 61.528 | 61.528 | 123.6465 | 123.8297 | -0.082397 | 123.8754 | 61.4639 | -0.20599 | 123.8297 | -0.082397 | 61.4639 | 123.6465 | 123.8754 | -124.1043 | -124.173
329.7188 | 124.1226 | -61.4273 | 62.5351 | 0.013962 | 0.0076925 | 0.011704 | 0.0044156 | 0.06922 | -0.00033333 | 0.071359 | -61.4548 | 62.4939 | -61.528 | -61.5921 | 62.2101 | 0.004578 | 0.013733 | 0.036621 | 62.4619 | -61.615 | -0.10071 | -0.041199 | -0.027466 | -0.16479 | -0.32501 | -0.18768 | -0.073242 | 0.073242 | 61.441 | 61.4639 | 123.6374 | 123.9212 | -0.027466 | 123.8892 | 61.4319 | -0.18768 | 123.9212 | -0.027466 | 61.4319 | 123.6374 | 123.8892 | -124.0631 | -124.1501
330.7188 | 124.118 | -61.4273 | 62.5351 | -0.1844 | 0.0061971 | 0.012986 | -0.001566 | 0.065161 | -0.0024695 | 0.067941 | -61.496 | 62.4573 | -61.5555 | -61.5967 | 62.2879 | 0.25635 | 0.10529 | -0.086975 | 62.5168 | -61.5921 | -0.12817 | -0.07782 | -0.068665 | -0.16937 | -0.24719 | -0.16479 | -0.01831 | 0.059509 | 61.5326 | 61.3403 | 123.7152 | 123.8846 | -0.068665 | 123.9441 | 61.6837 | -0.16479 | 123.8846 | -0.068665 | 61.6837 | 123.7152 | 123.9441 | -124.0906 | -124.1272
331.7188 | 124.1318 | -61.409 | 62.5763 | -0.23018 | 0.0079061 | 0.010209 | -0.0022068 | 0.068366 | 0.00052127 | 0.068368 | -61.496 | 62.4573 | -61.5417 | -61.6013 | 62.2467 | 0.068665 | 0.14191 | 0.11902 | 62.4847 | -61.6058 | -0.13275 | -0.11902 | -0.086975 | -0.19226 | -0.32959 | -0.19684 | -0.091553 | 0.045776 | 61.5509 | 61.528 | 123.6557 | 123.8663 | -0.086975 | 123.8937 | 61.4777 | -0.19684 | 123.8663 | -0.086975 | 61.4777 | 123.6557 | 123.8937 | -124.118 | -124.1821
332.7188 | 124.1318 | -61.3998 | 62.5717 | -0.21492 | 0.0049155 | 0.011064 | -0.0030612 | 0.068793 | -0.0014013 | 0.06965 | -61.4777 | 62.4527 | -61.5417 | -61.5875 | 62.2467 | 0.086975 | 0.1236 | 0.1236 | 62.4756 | -61.5829 | -0.14191 | -0.11902 | -0.07782 | -0.18768 | -0.32501 | -0.18311 | -0.09613 | 0.064087 | 61.5234 | 61.5234 | 123.6465 | 123.8525 | -0.07782 | 123.8754 | 61.4868 | -0.18311 | 123.8525 | -0.07782 | 61.4868 | 123.6465 | 123.8754 | -124.1135 | -124.1547
333.7188 | 124.2233 | -61.3815 | 62.5671 | -0.16914 | 0.0061971 | 0.0099954 | -0.0034886 | 0.064521 | -0.0014013 | 0.068582 | -61.3998 | 62.3978 | -61.5143 | -61.5005 | 62.3428 | 0.15106 | 0.004578 | 0.21057 | 62.471 | -61.5372 | -0.13275 | -0.16937 | -0.01831 | -0.11902 | -0.2243 | -0.15564 | -0.096131 | 0.11444 | 61.3861 | 61.5921 | 123.7244 | 123.7793 | -0.01831 | 123.8525 | 61.5326 | -0.15564 | 123.7793 | -0.01831 | 61.5326 | 123.7244 | 123.8525 | -124.0814 | -124.1043
334.7344 | 124.2508 | -61.377 | 62.5031 | 0.1284 | 0.0061971 | 0.012559 | -0.00028416 | 0.068793 | -0.0014013 | 0.069436 | -61.4365 | 62.3795 | -61.5509 | -61.5234 | 62.3016 | 0.054932 | -0.17853 | 0.09613 | 62.4069 | -61.5601 | -0.17395 | -0.1236 | -0.059509 | -0.14648 | -0.20142 | -0.18311 | -0.096131 | 0.11444 | 61.1984 | 61.4731 | 123.6786 | 123.7564 | -0.059509 | 123.7839 | 61.4319 | -0.18311 | 123.7564 | -0.059509 | 61.4319 | 123.6786 | 123.7839 | -124.054 | -124.0631
335.7188 | 124.1592 | -61.3678 | 62.5671 | -0.23781 | 0.0038473 | 0.0097818 | 0.001852 | 0.065375 | -0.00054693 | 0.068795 | -61.4365 | 62.4207 | -61.5189 | -61.5463 | 62.3016 | 0.11902 | 0.059509 | 0.18768 | 62.4619 | -61.5875 | -0.15106 | -0.14648 | -0.068664 | -0.17853 | -0.2655 | -0.21973 | -0.10529 | 0.082398 | 61.4273 | 61.5555 | 123.6694 | 123.7885 | -0.068664 | 123.8297 | 61.4868 | -0.21973 | 123.7885 | -0.068664 | 61.4868 | 123.6694 | 123.8297 | -124.086 | -124.1547
336.7188 | 124.0997 | -61.3998 | 62.5763 | -0.24544 | 0.0068381 | 0.010423 | 0.00099764 | 0.064093 | -0.00097413 | 0.068582 | -61.496 | 62.4527 | -61.5326 | -61.5875 | 62.2559 | 0.064087 | 0.14648 | 0.10071 | 62.4619 | -61.6058 | -0.13275 | -0.1236 | -0.096131 | -0.18768 | -0.32043 | -0.20599 | -0.11444 | 0.036621 | 61.5463 | 61.5005 | 123.6557 | 123.8525 | -0.096131 | 123.8617 | 61.4639 | -0.20599 | 123.8525 | -0.096131 | 61.4639 | 123.6557 | 123.8617 | -124.1089 | -124.1821
337.7188 | 124.0997 | -61.3815 | 62.5626 | -0.35225 | 0.0042745 | 0.0082864 | 0.0012112 | 0.06687 | -0.0014013 | 0.066659 | -61.4822 | 62.4619 | -61.5372 | -61.5784 | 62.2513 | 0.059509 | 0.12817 | 0.1236 | 62.4756 | -61.6058 | -0.15564 | -0.10071 | -0.10071 | -0.19684 | -0.31128 | -0.2243 | -0.086975 | 0.054931 | 61.5097 | 61.5051 | 123.6328 | 123.8434 | -0.10071 | 123.8571 | 61.441 | -0.2243 | 123.8434 | -0.10071 | 61.441 | 123.6328 | 123.8571 | -124.0997 | -124.1684
338.7188 | 124.1272 | -61.3815 | 62.5946 | -0.21492 | 0.0059835 | 0.0061502 | 0.0014248 | 0.065802 | -0.0022559 | 0.068368 | -61.4777 | 62.4481 | -61.5555 | -61.5738 | 62.2513 | 0.068665 | 0.11444 | 0.11444 | 62.4756 | -61.5738 | -0.17395 | -0.14648 | -0.09613 | -0.19226 | -0.34332 | -0.19226 | -0.11902 | 0.07782 | 61.496 | 61.496 | 123.6328 | 123.8297 | -0.09613 | 123.8571 | 61.4502 | -0.19226 | 123.8297 | -0.09613 | 61.4502 | 123.6328 | 123.8571 | -124.1501 | -124.1684
339.7344 | 124.2783 | -61.3861 | 62.5031 | 0.18181 | 0.0079061 | 0.0089274 | 0.00057044 | 0.066016 | -0.0018285 | 0.068154 | -61.4227 | 62.3795 | -61.5189 | -61.5189 | 62.2971 | 0.068665 | -0.40741 | -0.14191 | 62.352 | -61.5921 | -0.13275 | -0.1236 | -0.036621 | -0.13275 | -0.20599 | -0.20599 | -0.15106 | 0.096131 | 60.9787 | 61.2442 | 123.6832 | 123.7656 | -0.036621 | 123.7381 | 61.4548 | -0.20599 | 123.7656 | -0.036621 | 61.4548 | 123.6832 | 123.7381 | -124.0219 | -124.0952
340.7188 | 124.2325 | -61.3449 | 62.5122 | -0.24544 | 0.0049155 | 0.0089274 | -0.0032748 | 0.066657 | 0.00052127 | 0.06965 | -61.409 | 62.4161 | -61.5005 | -61.4868 | 62.3474 | 0.14648 | -0.027466 | 0.21973 | 62.4252 | -61.5509 | -0.15564 | -0.09613 | -0.064087 | -0.14191 | -0.16479 | -0.20599 | -0.086975 | 0.091552 | 61.3174 | 61.5646 | 123.6923 | 123.761 | -0.064087 | 123.7701 | 61.4914 | -0.20599 | 123.761 | -0.064087 | 61.4914 | 123.6923 | 123.7701 | -124.0128 | -124.0631
341.7188 | 124.1638 | -61.377 | 62.5442 | -0.22255 | 0.0032065 | 0.012773 | 0.002493 | 0.063666 | -0.0011877 | 0.069863 | -61.4365 | 62.4252 | -61.5005 | -61.5189 | 62.3062 | 0.13275 | 0.050354 | 0.17853 | 62.4435 | -61.5784 | -0.1236 | -0.11902 | -0.059509 | -0.14191 | -0.23804 | -0.20142 | -0.10071 | 0.064087 | 61.4273 | 61.5555 | 123.6832 | 123.8022 | -0.059509 | 123.8205 | 61.5097 | -0.20142 | 123.8022 | -0.059509 | 61.5097 | 123.6832 | 123.8205 | -124.0448 | -124.1226
342.7188 | 124.1867 | -61.3724 | 62.5305 | -0.23018 | 0.0047019 | 0.0097818 | 0.00035684 | 0.06388 | -0.00076053 | 0.070718 | -61.4273 | 62.4252 | -61.5234 | -61.5143 | 62.3199 | 0.13733 | 0.041199 | 0.19226 | 62.439 | -61.5417 | -0.15106 | -0.10529 | -0.054932 | -0.14191 | -0.21057 | -0.16937 | -0.091553 | 0.09613 | 61.4136 | 61.5646 | 123.6923 | 123.7976 | -0.054932 | 123.8113 | 61.5097 | -0.16937 | 123.7976 | -0.054932 | 61.5097 | 123.6923 | 123.8113 | -124.054 | -124.0723
343.7188 | 124.1135 | -61.3953 | 62.5671 | -0.25307 | 0.0038473 | 0.010209 | 0.0016384 | 0.064734 | -0.0016149 | 0.068795 | -61.4822 | 62.4344 | -61.5189 | -61.5738 | 62.2513 | 0.068665 | 0.1236 | 0.09613 | 62.4664 | -61.5967 | -0.1236 | -0.13275 | -0.086975 | -0.17853 | -0.31586 | -0.20142 | -0.10071 | 0.036621 | 61.5189 | 61.4914 | 123.6465 | 123.8297 | -0.086975 | 123.8617 | 61.4639 | -0.20142 | 123.8297 | -0.086975 | 61.4639 | 123.6465 | 123.8617 | -124.086 | -124.1638
344.7344 | 124.2325 | -61.4136 | 62.5031 | 0.10551 | 0.0079061 | 0.012773 | 0.0020656 | 0.067939 | -0.0020421 | 0.066018 | -61.4365 | 62.3795 | -61.5234 | -61.6241 | 62.0728 | 0.036621 | -0.032043 | 0.07782 | 62.3932 | -61.5646 | -0.10986 | -0.1236 | -0.022888 | -0.21057 | -0.4303 | -0.15106 | -0.10986 | 0.086975 | 61.3815 | 61.4914 | 123.4863 | 123.793 | -0.022888 | 123.8068 | 61.4502 | -0.15106 | 123.793 | -0.022888 | 61.4502 | 123.4863 | 123.8068 | -124.0265 | -124.0677
345.7188 | 124.1409 | -61.3815 | 62.5488 | -0.2607 | 0.0070517 | 0.0082864 | -0.001566 | 0.063025 | -0.0014013 | 0.067941 | -61.4594 | 62.4161 | -61.528 | -61.5509 | 62.2833 | 0.10529 | 0.10071 | 0.16937 | 62.4664 | -61.5646 | -0.14648 | -0.13275 | -0.07782 | -0.16937 | -0.2655 | -0.1831 | -0.082397 | 0.068664 | 61.4822 | 61.5509 | 123.6649 | 123.7976 | -0.07782 | 123.848 | 61.4868 | -0.1831 | 123.7976 | -0.07782 | 61.4868 | 123.6649 | 123.848 | -124.0768 | -124.1135
346.7188 | 124.2554 | -61.3632 | 62.5305 | -0.13863 | 0.0057699 | 0.011064 | -0.0032748 | 0.064734 | -0.0020421 | 0.068795 | -61.3998 | 62.3795 | -61.5097 | -61.4731 | 62.352 | 0.16937 | -0.041199 | 0.23346 | 62.4344 | -61.528 | -0.14648 | -0.15106 | -0.036621 | -0.10986 | -0.17853 | -0.1648 | -0.096131 | 0.10986 | 61.322 | 61.5967 | 123.7152 | 123.7427 | -0.036621 | 123.7976 | 61.5326 | -0.1648 | 123.7427 | -0.036621 | 61.5326 | 123.7152 | 123.7976 | -124.0402 | -124.0585
347.7188 | 124.2416 | -61.3495 | 62.5122 | 0.082626 | 0.0061971 | 0.011064 | -0.0028476 | 0.065161 | -0.0022559 | 0.065377 | -61.4594 | 62.3611 | -61.5234 | -61.4822 | 62.352 | 0.16479 | -0.036621 | 0.23346 | 62.4298 | -61.5143 | -0.17395 | -0.15106 | -0.10986 | -0.13275 | -0.16022 | -0.16479 | -0.082397 | 0.064086 | 61.3129 | 61.5829 | 123.7015 | 123.7106 | -0.10986 | 123.7793 | 61.5143 | -0.16479 | 123.7106 | -0.10986 | 61.5143 | 123.7015 | 123.7793 | -124.0356 | -124.0265
348.7188 | 124.1867 | -61.3632 | 62.5534 | -0.17677 | 0.0066245 | 0.009141 | 0.00078404 | 0.065375 | -0.0026831 | 0.068368 | -61.4182 | 62.4023 | -61.5097 | -61.4777 | 62.3383 | 0.15106 | 0 | 0.21515 | 62.4344 | -61.5417 | -0.14648 | -0.15106 | -0.054932 | -0.11444 | -0.21515 | -0.17853 | -0.11902 | 0.091553 | 61.3632 | 61.5784 | 123.7015 | 123.7656 | -0.054932 | 123.7976 | 61.5143 | -0.17853 | 123.7656 | -0.054932 | 61.5143 | 123.7015 | 123.7976 | -124.0631 | -124.0952
349.7344 | 124.173 | -61.4136 | 62.5122 | 0.15892 | 0.0087607 | 0.011704 | 0.0044156 | 0.065802 | 9.4068e-05 | 0.067941 | -61.496 | 62.4573 | -61.5463 | -61.5875 | 62.2375 | -0.018311 | -0.10071 | 0.009155 | 62.4207 | -61.6196 | -0.13275 | -0.054932 | -0.082398 | -0.17395 | -0.27466 | -0.20599 | -0.091553 | 0.050354 | 61.3129 | 61.4227 | 123.6511 | 123.8708 | -0.082398 | 123.8342 | 61.3953 | -0.20599 | 123.8708 | -0.082398 | 61.3953 | 123.6511 | 123.8342 | -124.0585 | -124.1318
350.7188 | 124.1776 | -61.3586 | 62.5214 | -0.25307 | 0.0051291 | 0.0055094 | -0.00071136 | 0.066016 | -0.0020421 | 0.069009 | -61.4273 | 62.3932 | -61.5463 | -61.5143 | 62.3154 | 0.14648 | 0.059509 | 0.17853 | 62.439 | -61.5738 | -0.18768 | -0.12817 | -0.068664 | -0.15564 | -0.20599 | -0.21515 | -0.082397 | 0.11902 | 61.4182 | 61.5372 | 123.674 | 123.7518 | -0.068664 | 123.7976 | 61.5051 | -0.21515 | 123.7518 | -0.068664 | 61.5051 | 123.674 | 123.7976 | -124.0677 | -124.0952
351.7188 | 124.205 | -61.3724 | 62.5351 | -0.22255 | 0.0074789 | 0.0093546 | -0.0017796 | 0.066657 | -0.0033239 | 0.066232 | -61.4319 | 62.4115 | -61.496 | -61.5097 | 62.3291 | 0.14648 | 0.032043 | 0.21057 | 62.4298 | -61.5692 | -0.1236 | -0.1236 | -0.05951 | -0.13733 | -0.20599 | -0.19684 | -0.10528 | 0.064087 | 61.4044 | 61.5829 | 123.7015 | 123.7839 | -0.05951 | 123.8022 | 61.5189 | -0.19684 | 123.7839 | -0.05951 | 61.5189 | 123.7015 | 123.8022 | -124.0311 | -124.1043
352.7188 | 124.1913 | -61.3541 | 62.5442 | -0.16914 | 0.0042745 | 0.0095682 | -0.0013522 | 0.065161 | -0.0031103 | 0.069436 | -61.4182 | 62.4161 | -61.5234 | -61.496 | 62.3474 | 0.16022 | -0.009155 | 0.2243 | 62.4207 | -61.5326 | -0.16937 | -0.12817 | -0.064087 | -0.14191 | -0.19684 | -0.17853 | -0.1236 | 0.10529 | 61.3449 | 61.5784 | 123.7015 | 123.7701 | -0.064087 | 123.7747 | 61.5143 | -0.17853 | 123.7701 | -0.064087 | 61.5143 | 123.7015 | 123.7747 | -124.0677 | -124.0768
353.7188 | 124.2645 | -61.3403 | 62.5946 | -0.14626 | 0.0042745 | 0.0082864 | -0.0034886 | 0.065375 | -0.0022559 | 0.069863 | -61.3953 | 62.3978 | -61.5143 | -61.4594 | 62.3749 | 0.16479 | -0.059509 | 0.23346 | 62.3932 | -61.5189 | -0.17395 | -0.19684 | -0.054932 | -0.11902 | -0.21973 | -0.17853 | -0.20142 | 0.11902 | 61.2808 | 61.5738 | 123.7152 | 123.7381 | -0.054932 | 123.7335 | 61.5051 | -0.17853 | 123.7381 | -0.054932 | 61.5051 | 123.7152 | 123.7335 | -124.1089 | -124.1135
354.7188 | 124.1776 | -61.3815 | 62.5854 | -0.24544 | 0.0061971 | 0.0078592 | 0.0016384 | 0.065589 | -0.0037511 | 0.067086 | -61.496 | 62.4802 | -61.528 | -61.5738 | 62.2513 | 0.050354 | 0.15106 | 0.10071 | 62.4939 | -61.6013 | -0.14648 | -0.10528 | -0.11444 | -0.19226 | -0.33417 | -0.21973 | -0.091553 | 0.032043 | 61.5326 | 61.4822 | 123.6328 | 123.8617 | -0.11444 | 123.8754 | 61.4319 | -0.21973 | 123.8617 | -0.11444 | 61.4319 | 123.6328 | 123.8754 | -124.1135 | -124.1867
355.7188 | 124.2416 | -61.3403 | 62.5122 | -0.55061 | 0.0049155 | 0.0132 | -0.00028416 | 0.066657 | -0.0031103 | 0.070077 | -61.6699 | 62.3978 | -61.5417 | -61.5234 | 62.3566 | 0.20142 | -0.064087 | 0.21973 | 62.4023 | -61.5326 | -0.20142 | -0.11444 | -0.32959 | -0.18311 | -0.15564 | -0.19226 | -0.10986 | -0.12817 | 61.2762 | 61.5601 | 123.6969 | 123.7381 | -0.32959 | 123.7427 | 61.5417 | -0.19226 | 123.7381 | -0.32959 | 61.5417 | 123.6969 | 123.7427 | -124.054 | -124.0448
356.7188 | 124.2142 | -61.3678 | 62.558 | -0.16914 | 0.0059835 | 0.0078592 | 0.00035684 | 0.064734 | -0.0018285 | 0.066018 | -61.4136 | 62.4069 | -61.5051 | -61.4868 | 62.3428 | 0.15564 | 0.009155 | 0.20142 | 62.4069 | -61.5601 | -0.13733 | -0.15106 | -0.045776 | -0.11902 | -0.21515 | -0.19226 | -0.15106 | 0.091553 | 61.377 | 61.5692 | 123.7106 | 123.7747 | -0.045776 | 123.7747 | 61.5234 | -0.19226 | 123.7747 | -0.045776 | 61.5234 | 123.7106 | 123.7747 | -124.0631 | -124.118
357.7188 | 124.1867 | -61.3541 | 62.5259 | -0.24544 | 0.0059835 | 0.010209 | -0.00028416 | 0.065802 | -0.0022559 | 0.068368 | -61.4182 | 62.3886 | -61.5051 | -61.4731 | 62.3428 | 0.16022 | -0.022888 | 0.21057 | 62.4252 | -61.5234 | -0.15106 | -0.13733 | -0.064087 | -0.11902 | -0.18311 | -0.16937 | -0.10071 | 0.086975 | 61.3312 | 61.5646 | 123.6969 | 123.7427 | -0.064087 | 123.7793 | 61.5143 | -0.16937 | 123.7427 | -0.064087 | 61.5143 | 123.6969 | 123.7793 | -124.0311 | -124.0494
358.7188 | 124.2462 | -61.3358 | 62.5168 | -0.42091 | 0.0053427 | 0.013627 | -0.0017796 | 0.063666 | -0.0035375 | 0.068368 | -61.4044 | 62.3932 | -61.5189 | -61.4822 | 62.3337 | 0.16937 | -0.059509 | 0.21515 | 62.4069 | -61.5051 | -0.18311 | -0.1236 | -0.068665 | -0.14648 | -0.18311 | -0.16937 | -0.10986 | 0.11444 | 61.2762 | 61.5509 | 123.6694 | 123.7289 | -0.068665 | 123.7427 | 61.5051 | -0.16937 | 123.7289 | -0.068665 | 61.5051 | 123.6694 | 123.7427 | -124.0356 | -124.0219
359.7188 | 124.0997 | -61.4044 | 62.5397 | -0.047073 | 0.0074789 | 0.010423 | 0.0061246 | 0.065161 | -0.0026831 | 0.066232 | -61.4136 | 62.4664 | -61.5372 | -61.5326 | 62.265 | 0.073242 | 0.018311 | 0.11444 | 62.4435 | -61.6104 | -0.13275 | -0.073242 | -0.009155 | -0.12817 | -0.27466 | -0.20599 | -0.096131 | 0.1236 | 61.4227 | 61.5189 | 123.6694 | 123.8708 | -0.009155 | 123.848 | 61.4777 | -0.20599 | 123.8708 | -0.009155 | 61.4777 | 123.6694 | 123.848 | -124.0768 | -124.1501
360.7188 | 124.2554 | -61.3586 | 62.5214 | -0.11574 | 0.0053427 | 0.0082864 | -0.0045566 | 0.062812 | -0.0026831 | 0.071145 | -61.4639 | 62.384 | -61.5189 | -61.4914 | 62.3474 | 0.15564 | -0.059509 | 0.2243 | 62.3749 | -61.5646 | -0.16022 | -0.13733 | -0.10529 | -0.13275 | -0.17395 | -0.20599 | -0.14648 | 0.054932 | 61.2991 | 61.5829 | 123.7061 | 123.7427 | -0.10529 | 123.7335 | 61.5143 | -0.20599 | 123.7427 | -0.10529 | 61.5143 | 123.7061 | 123.7335 | -124.0402 | -124.086
361.7188 | 124.2325 | -61.3449 | 62.5168 | -0.08522 | 0.0040609 | 0.0080728 | -0.0011386 | 0.063666 | -0.00054693 | 0.069222 | -61.4731 | 62.4023 | -61.5051 | -61.5051 | 62.3337 | 0.14648 | -0.068665 | 0.1831 | 62.3932 | -61.5555 | -0.16022 | -0.11444 | -0.12817 | -0.16022 | -0.18311 | -0.21057 | -0.1236 | 0.032044 | 61.2762 | 61.528 | 123.6786 | 123.7473 | -0.12817 | 123.7381 | 61.4914 | -0.21057 | 123.7473 | -0.12817 | 61.4914 | 123.6786 | 123.7381 | -124.0219 | -124.0723
362.7188 | 124.2783 | -61.3403 | 62.5076 | -0.047073 | 0.0055563 | 0.011491 | -0.001566 | 0.063666 | -0.0018285 | 0.070291 | -61.4182 | 62.3886 | -61.5143 | -61.4456 | 62.3703 | 0.1831 | -0.059509 | 0.21973 | 62.4161 | -61.5189 | -0.17395 | -0.11902 | -0.07782 | -0.10529 | -0.13733 | -0.17853 | -0.091552 | 0.09613 | 61.2808 | 61.5601 | 123.7106 | 123.7289 | -0.07782 | 123.7564 | 61.5234 | -0.17853 | 123.7289 | -0.07782 | 61.5234 | 123.7106 | 123.7564 | -124.0219 | -124.0265
363.7188 | 124.2416 | -61.3495 | 62.5168 | 0.58617 | 0.0072653 | 0.0076456 | 0.00099764 | 0.063025 | -0.00097413 | 0.069222 | -61.441 | 62.3749 | -61.496 | -61.4685 | 62.352 | 0.16022 | -0.041199 | 0.23346 | 62.3749 | -61.5417 | -0.14648 | -0.14191 | -0.091553 | -0.11902 | -0.16479 | -0.19226 | -0.14191 | 0.054932 | 61.3083 | 61.5829 | 123.7015 | 123.7244 | -0.091553 | 123.7244 | 61.5097 | -0.19226 | 123.7244 | -0.091553 | 61.5097 | 123.7015 | 123.7244 | -124.0128 | -124.0585
364.7188 | 124.2371 | -61.3358 | 62.5351 | -0.17677 | 0.0064107 | 0.011064 | 0.0056972 | 0.062598 | -0.0020421 | 0.067086 | -61.4044 | 62.3978 | -61.4914 | -61.4914 | 62.2421 | 0.15106 | -0.027466 | 0.18768 | 62.3932 | -61.5463 | -0.15564 | -0.13733 | -0.068665 | -0.15564 | -0.29297 | -0.21057 | -0.14191 | 0.086975 | 61.3083 | 61.5234 | 123.5779 | 123.7335 | -0.068665 | 123.7289 | 61.4868 | -0.21057 | 123.7335 | -0.068665 | 61.4868 | 123.5779 | 123.7289 | -124.0265 | -124.0814
365.7188 | 124.1409 | -61.3586 | 62.4985 | -0.16151 | 0.0055563 | 0.009141 | -7.0562e-05 | 0.064307 | -0.0011877 | 0.068795 | -61.3998 | 62.3749 | -61.496 | -61.4594 | 62.3795 | 0.16479 | -0.054932 | 0.65918 | 62.4619 | -61.4914 | -0.13733 | -0.1236 | -0.041198 | -0.10071 | -0.11902 | -0.13275 | -0.036621 | 0.096131 | 61.3037 | 62.0178 | 123.7381 | 123.7335 | -0.041198 | 123.8205 | 61.5234 | -0.13275 | 123.7335 | -0.041198 | 61.5234 | 123.7381 | 123.8205 | -123.9944 | -123.9899
366.7188 | 124.2325 | -61.3495 | 62.5214 | -0.09285 | 0.0051291 | 0.0035868 | -0.0011386 | 0.061957 | -0.0014013 | 0.068154 | -61.409 | 62.3474 | -61.5005 | -61.4365 | 62.3749 | 0.16937 | -0.082397 | 0.23346 | 62.4023 | -61.5234 | -0.15106 | -0.17395 | -0.05951 | -0.086975 | -0.14648 | -0.17395 | -0.11902 | 0.091552 | 61.2671 | 61.5829 | 123.7244 | 123.6969 | -0.05951 | 123.7518 | 61.5189 | -0.17395 | 123.6969 | -0.05951 | 61.5189 | 123.7244 | 123.7518 | -124.0219 | -124.0448
367.7188 | 124.2188 | -61.3815 | 62.5214 | -0.039444 | 0.0044881 | 0.006791 | -0.0024204 | 0.063239 | -0.00097413 | 0.067727 | -61.4685 | 62.3886 | -61.5326 | -61.5372 | 62.3016 | 0.10071 | -0.068665 | 0.13275 | 62.3795 | -61.5509 | -0.15106 | -0.13275 | -0.086975 | -0.15564 | -0.21973 | -0.16937 | -0.14191 | 0.064087 | 61.3129 | 61.5143 | 123.6832 | 123.7701 | -0.086975 | 123.761 | 61.4822 | -0.16937 | 123.7701 | -0.086975 | 61.4822 | 123.6832 | 123.761 | -124.054 | -124.0723
368.7188 | 124.1913 | -61.377 | 62.5259 | 0.013962 | 0.0066245 | 0.0085 | -7.0562e-05 | 0.064093 | -0.0011877 | 0.06965 | -61.496 | 62.3657 | -61.5143 | -61.5601 | 62.2833 | 0.068665 | -0.073242 | 0.11444 | 62.4115 | -61.5509 | -0.13733 | -0.16022 | -0.11902 | -0.18311 | -0.24262 | -0.17395 | -0.11444 | 0.01831 | 61.3037 | 61.4914 | 123.6603 | 123.7427 | -0.11902 | 123.7885 | 61.4456 | -0.17395 | 123.7427 | -0.11902 | 61.4456 | 123.6603 | 123.7885 | -124.0402 | -124.0768
369.7188 | 124.1272 | -61.4044 | 62.5671 | -0.21492 | 0.0070517 | 0.0087138 | 0.0020656 | 0.064307 | -0.0016149 | 0.066232 | -61.4868 | 62.4664 | -61.5234 | -61.5646 | 62.2513 | -0.018311 | 0.44861 | 0.15106 | 62.471 | -61.5646 | -0.11902 | -0.10071 | -0.082397 | -0.16022 | -0.31586 | -0.16022 | -0.096131 | 0.036621 | 61.853 | 61.5555 | 123.6557 | 123.8708 | -0.082397 | 123.8754 | 61.3861 | -0.16022 | 123.8708 | -0.082397 | 61.3861 | 123.6557 | 123.8754 | -124.0906 | -124.1318
370.7188 | 124.2325 | -61.3449 | 62.5214 | -0.11574 | 0.0044881 | 0.0085 | -0.0019932 | 0.064734 | -0.0016149 | 0.0673 | -61.4182 | 62.3703 | -61.5051 | -61.4822 | 62.3657 | 0.16479 | -0.091553 | 0.21057 | 62.4207 | -61.5372 | -0.16022 | -0.15106 | -0.073242 | -0.13733 | -0.15564 | -0.19226 | -0.10071 | 0.086975 | 61.2534 | 61.5555 | 123.7106 | 123.7152 | -0.073242 | 123.7656 | 61.5097 | -0.19226 | 123.7152 | -0.073242 | 61.5097 | 123.7106 | 123.7656 | -124.0265 | -124.0585
371.7188 | 124.2279 | -61.3586 | 62.5168 | -0.062332 | 0.0040609 | 0.011491 | -0.0032748 | 0.064521 | -0.00011953 | 0.068154 | -61.4365 | 62.3474 | -61.5372 | -61.4868 | 62.3337 | 0.14648 | -0.082397 | 0.18768 | 62.3795 | -61.5509 | -0.17853 | -0.16937 | -0.077819 | -0.12817 | -0.18311 | -0.19226 | -0.13733 | 0.10071 | 61.2762 | 61.5463 | 123.6923 | 123.7061 | -0.077819 | 123.7381 | 61.5051 | -0.19226 | 123.7061 | -0.077819 | 61.5051 | 123.6923 | 123.7381 | -124.054 | -124.0677
372.7188 | 124.2096 | -61.3541 | 62.5351 | -0.054703 | 0.0044881 | 0.013627 | -0.0013522 | 0.064093 | -0.0031103 | 0.069009 | -61.4548 | 62.3474 | -61.5143 | -61.5143 | 62.3245 | 0.1236 | -0.082397 | 0.16479 | 62.3932 | -61.528 | -0.16022 | -0.18768 | -0.10071 | -0.16022 | -0.21057 | -0.17395 | -0.14191 | 0.059509 | 61.2717 | 61.5189 | 123.6786 | 123.7015 | -0.10071 | 123.7473 | 61.4777 | -0.17395 | 123.7015 | -0.10071 | 61.4777 | 123.6786 | 123.7473 | -124.0494 | -124.0631
373.7188 | 124.2096 | -61.3632 | 62.5122 | -0.031814 | 0.0061971 | 0.0082864 | -0.0022068 | 0.063239 | -0.0020421 | 0.067513 | -61.4731 | 62.3657 | -61.528 | -61.5189 | 62.3016 | 0.073242 | -0.068665 | 0.13733 | 62.3932 | -61.5417 | -0.1648 | -0.14648 | -0.10986 | -0.15564 | -0.21057 | -0.17853 | -0.11902 | 0.054932 | 61.2946 | 61.5005 | 123.6649 | 123.7289 | -0.10986 | 123.7564 | 61.4365 | -0.17853 | 123.7289 | -0.10986 | 61.4365 | 123.6649 | 123.7564 | -124.0402 | -124.054
374.7188 | 124.0768 | -61.3861 | 62.5534 | -0.17677 | 0.0057699 | 0.009141 | -7.0562e-05 | 0.062812 | -0.0028967 | 0.070504 | -61.496 | 62.4252 | -61.5372 | -61.5417 | 62.4893 | 0.21515 | -0.086975 | 0.059509 | 62.4344 | -61.6058 | -0.15106 | -0.12817 | -0.10986 | -0.15564 | -0.064087 | -0.21973 | -0.11902 | 0.041198 | 61.2991 | 61.4456 | 123.8754 | 123.8113 | -0.10986 | 123.8205 | 61.6013 | -0.21973 | 123.8113 | -0.10986 | 61.6013 | 123.8754 | 123.8205 | -124.0906 | -124.1592
375.7188 | 124.1776 | -61.3678 | 62.5076 | 0.1284 | 0.0047019 | 0.0097818 | -0.0032748 | 0.067084 | -0.0018285 | 0.070504 | -61.4731 | 62.3428 | -61.5417 | -61.5555 | 62.2787 | 0.032043 | -0.11902 | 0.050354 | 62.3978 | -61.5326 | -0.17395 | -0.16479 | -0.10529 | -0.18768 | -0.22888 | -0.16479 | -0.10986 | 0.068665 | 61.2488 | 61.4182 | 123.6465 | 123.7106 | -0.10529 | 123.7656 | 61.3998 | -0.16479 | 123.7106 | -0.10529 | 61.3998 | 123.6465 | 123.7656 | -124.0494 | -124.0402
376.7188 | 124.1821 | -61.3815 | 62.5259 | 0.052109 | 0.0066245 | 0.0097818 | -0.001566 | 0.064734 | -0.0018285 | 0.067727 | -61.4914 | 62.3611 | -61.5463 | -61.5555 | 62.2742 | 0.050354 | -0.07782 | 0.082397 | 62.384 | -61.5509 | -0.16479 | -0.16479 | -0.10986 | -0.17395 | -0.25177 | -0.16937 | -0.14191 | 0.054932 | 61.3037 | 61.4639 | 123.6557 | 123.7427 | -0.10986 | 123.7656 | 61.4319 | -0.16937 | 123.7427 | -0.10986 | 61.4319 | 123.6557 | 123.7656 | -124.0723 | -124.0768
377.7188 | 124.1684 | -61.3815 | 62.5168 | 0.059738 | 0.0087607 | 0.010423 | -0.001566 | 0.066657 | 0.00052127 | 0.069009 | -61.4777 | 62.3795 | -61.528 | -61.5509 | 62.2192 | 0.054932 | -0.082397 | 0.07782 | 62.3978 | -61.5784 | -0.14648 | -0.13733 | -0.09613 | -0.16937 | -0.29755 | -0.19684 | -0.11902 | 0.050354 | 61.2991 | 61.4594 | 123.6008 | 123.761 | -0.09613 | 123.7793 | 61.4365 | -0.19684 | 123.761 | -0.09613 | 61.4365 | 123.6008 | 123.7793 | -124.0448 | -124.0952
378.7188 | 124.205 | -61.377 | 62.5214 | 0.052109 | 0.0070517 | 0.013841 | -0.0011386 | 0.063025 | -0.0026831 | 0.068368 | -61.5097 | 62.3703 | -61.5509 | -61.5555 | 62.2604 | 0.032043 | -0.09613 | 0.091553 | 62.3566 | -61.5372 | -0.17395 | -0.15106 | -0.13275 | -0.17853 | -0.26093 | -0.16022 | -0.1648 | 0.041198 | 61.2808 | 61.4685 | 123.6374 | 123.7473 | -0.13275 | 123.7335 | 61.409 | -0.16022 | 123.7473 | -0.13275 | 61.409 | 123.6374 | 123.7335 | -124.0723 | -124.0585
379.7188 | 124.205 | -61.3403 | 62.5259 | -0.1844 | 0.0072653 | 0.009141 | -7.0562e-05 | 0.064093 | 0.00030767 | 0.069222 | -61.4273 | 62.4207 | -61.5234 | -61.4777 | 62.3199 | 0.15106 | 0.018311 | 0.21057 | 62.4069 | -61.5417 | -0.18311 | -0.10529 | -0.086975 | -0.13733 | -0.20599 | -0.20142 | -0.11902 | 0.09613 | 61.3586 | 61.5509 | 123.6603 | 123.761 | -0.086975 | 123.7473 | 61.4914 | -0.20142 | 123.761 | -0.086975 | 61.4914 | 123.6603 | 123.7473 | -124.0494 | -124.0677
380.7188 | 124.2188 | -61.377 | 62.5076 | 0.19707 | 0.0051291 | 0.0082864 | -7.0562e-05 | 0.064521 | -0.0028967 | 0.070077 | -61.4548 | 62.3657 | -61.5234 | -61.5417 | 62.2833 | 0.050354 | -0.15106 | 0.091553 | 62.3474 | -61.5692 | -0.14648 | -0.14191 | -0.07782 | -0.16479 | -0.2243 | -0.19226 | -0.16022 | 0.068664 | 61.2259 | 61.4685 | 123.6603 | 123.7427 | -0.07782 | 123.7244 | 61.4273 | -0.19226 | 123.7427 | -0.07782 | 61.4273 | 123.6603 | 123.7244 | -124.0311 | -124.0768
381.7188 | 124.2004 | -61.3586 | 62.4939 | 0.21233 | 0.0070517 | 0.01085 | 0.0033474 | 0.064521 | -0.00097413 | 0.066659 | -61.4227 | 62.3749 | -61.5601 | -61.7111 | 62.2559 | 0.15564 | -0.13275 | 0.068665 | 62.3749 | -61.5692 | -0.20142 | -0.11902 | -0.064086 | -0.35248 | -0.23804 | -0.21057 | -0.11902 | 0.13733 | 61.2259 | 61.4273 | 123.6145 | 123.7335 | -0.064086 | 123.7335 | 61.5143 | -0.21057 | 123.7335 | -0.064086 | 61.5143 | 123.6145 | 123.7335 | -124.054 | -124.0631
382.7188 | 124.2508 | -61.3815 | 62.5122 | 0.13603 | 0.0066245 | 0.011491 | 0.002493 | 0.064948 | -0.0035375 | 0.069222 | -61.441 | 62.4023 | -61.5555 | -61.5234 | 62.3016 | 0.064087 | -0.1831 | 0.091553 | 62.3795 | -61.5555 | -0.17395 | -0.10986 | -0.059509 | -0.14191 | -0.21057 | -0.17395 | -0.13275 | 0.11444 | 61.1984 | 61.4731 | 123.6832 | 123.7839 | -0.059509 | 123.761 | 61.4456 | -0.17395 | 123.7839 | -0.059509 | 61.4456 | 123.6832 | 123.761 | -124.0677 | -124.0677
383.7188 | 124.2233 | -61.3632 | 62.471 | 0.18181 | 0.0042745 | 0.011704 | 0.00035684 | 0.064521 | -0.0011877 | 0.070931 | -61.4273 | 62.4115 | -61.496 | -61.5417 | 62.3474 | 0.1236 | -0.23346 | 0.10529 | 62.3886 | -61.5509 | -0.13275 | -0.059509 | -0.064087 | -0.17853 | -0.1236 | -0.18768 | -0.082397 | 0.068665 | 61.1298 | 61.4685 | 123.7106 | 123.7747 | -0.064087 | 123.7518 | 61.4868 | -0.18768 | 123.7747 | -0.064087 | 61.4868 | 123.7106 | 123.7518 | -123.967 | -124.0219
384.7188 | 124.2691 | -61.377 | 62.5076 | -0.10048 | 0.0064107 | 0.006791 | -0.002634 | 0.064307 | -0.0026831 | 0.069009 | -61.4365 | 62.384 | -61.528 | -61.4868 | 62.3474 | 0.15106 | -0.07782 | 0.19226 | 62.384 | -61.5417 | -0.15106 | -0.1236 | -0.059509 | -0.10986 | -0.16022 | -0.16479 | -0.1236 | 0.091553 | 61.2991 | 61.5692 | 123.7244 | 123.761 | -0.059509 | 123.761 | 61.528 | -0.16479 | 123.761 | -0.059509 | 61.528 | 123.7244 | 123.761 | -124.0356 | -124.0494
385.7188 | 124.2325 | -61.3861 | 62.4664 | 0.21233 | 0.0064107 | 0.0093546 | -7.0562e-05 | 0.067298 | -0.00097413 | 0.067727 | -61.5143 | 62.3749 | -61.5326 | -61.528 | 62.3383 | 0.086975 | -0.21515 | 0.086975 | 62.3291 | -61.5875 | -0.14648 | -0.091553 | -0.12817 | -0.14191 | -0.12817 | -0.20142 | -0.13733 | 0.018311 | 61.171 | 61.4731 | 123.7244 | 123.761 | -0.12817 | 123.7152 | 61.4731 | -0.20142 | 123.761 | -0.12817 | 61.4731 | 123.7244 | 123.7152 | -123.999 | -124.054
386.7188 | 124.3195 | -61.3861 | 62.4847 | 0.15129 | 0.0057699 | 0.0065774 | 0.003561 | 0.06623 | -0.0011877 | 0.067727 | -61.4044 | 62.3978 | -61.5189 | -61.5005 | 62.3108 | 0.068665 | -0.20599 | 0.004578 | 62.3749 | -61.6241 | -0.13275 | -0.086975 | -0.018311 | -0.11444 | -0.17395 | -0.23804 | -0.10986 | 0.11444 | 61.1801 | 61.3907 | 123.6969 | 123.7839 | -0.018311 | 123.761 | 61.4548 | -0.23804 | 123.7839 | -0.018311 | 61.4548 | 123.6969 | 123.761 | -124.0036 | -124.1089
387.7188 | 124.2416 | -61.3815 | 62.4847 | 0.2047 | 0.0079061 | 0.010636 | 0.003561 | 0.065802 | 9.4068e-05 | 0.068795 | -61.4456 | 62.4069 | -61.5372 | -61.5234 | 62.2833 | 0.059509 | -0.17853 | 0.086975 | 62.3795 | -61.6058 | -0.15564 | -0.07782 | -0.064087 | -0.14191 | -0.20142 | -0.2243 | -0.10529 | 0.091552 | 61.203 | 61.4685 | 123.6649 | 123.7885 | -0.064087 | 123.761 | 61.441 | -0.2243 | 123.7885 | -0.064087 | 61.441 | 123.6649 | 123.761 | -124.0219 | -124.0906
388.7188 | 124.1226 | -61.3907 | 62.5168 | 0.15892 | 0.0083333 | 0.0085 | 0.004202 | 0.06623 | -0.00054693 | 0.070931 | -61.5189 | 62.4573 | -61.5646 | -61.6196 | 62.1964 | -0.045776 | -0.013733 | -0.018311 | 62.4344 | -61.6241 | -0.17395 | -0.05951 | -0.12817 | -0.22888 | -0.32043 | -0.23346 | -0.082398 | 0.045776 | 61.377 | 61.3724 | 123.587 | 123.848 | -0.12817 | 123.8251 | 61.3449 | -0.23346 | 123.848 | -0.12817 | 61.3449 | 123.587 | 123.8251 | -124.0814 | -124.1409
389.7188 | 124.1592 | -61.3907 | 62.5076 | 0.15892 | 0.010042 | 0.013413 | 0.0027066 | 0.067939 | -0.0026831 | 0.068582 | -61.5005 | 62.4344 | -61.5463 | -61.5967 | 62.2284 | 0.004578 | -0.082397 | -0.009155 | 62.4115 | -61.6058 | -0.15564 | -0.073242 | -0.10986 | -0.20599 | -0.27923 | -0.21515 | -0.09613 | 0.045777 | 61.3083 | 61.3815 | 123.6191 | 123.8251 | -0.10986 | 123.8022 | 61.3953 | -0.21515 | 123.8251 | -0.10986 | 61.3953 | 123.6191 | 123.8022 | -124.054 | -124.1135
390.7188 | 124.1272 | -61.4044 | 62.5076 | 0.074997 | 0.0096151 | 0.0078592 | 0.0016384 | 0.067511 | -0.00097413 | 0.070291 | -61.4868 | 62.4619 | -61.5463 | -61.6058 | 62.2147 | -0.022888 | -0.022888 | -0.004578 | 62.4161 | -61.6013 | -0.14191 | -0.045776 | -0.082397 | -0.20142 | -0.29297 | -0.19684 | -0.091552 | 0.05951 | 61.3815 | 61.3998 | 123.6191 | 123.8663 | -0.082397 | 123.8205 | 61.3815 | -0.19684 | 123.8663 | -0.082397 | 61.3815 | 123.6191 | 123.8205 | -124.054 | -124.1089
391.7188 | 124.1867 | -61.3953 | 62.4802 | 0.18181 | 0.010042 | 0.011491 | -7.0562e-05 | 0.068366 | 9.4068e-05 | 0.070504 | -61.4868 | 62.4481 | -61.5463 | -61.5738 | 62.2467 | 0.009155 | -0.1236 | 0.036621 | 62.4023 | -61.6058 | -0.15106 | -0.032044 | -0.091552 | -0.17853 | -0.23346 | -0.21057 | -0.07782 | 0.05951 | 61.2717 | 61.4319 | 123.642 | 123.8434 | -0.091552 | 123.7976 | 61.4044 | -0.21057 | 123.8434 | -0.091552 | 61.4044 | 123.642 | 123.7976 | -124.0265 | -124.086
392.7188 | 124.1364 | -61.3861 | 62.5031 | 0.15129 | 0.0064107 | 0.011277 | 0.0020656 | 0.069648 | -0.0020421 | 0.07264 | -61.4914 | 62.4619 | -61.5601 | -61.5921 | 62.2467 | -0.022888 | -0.086975 | 0.004578 | 62.4252 | -61.6104 | -0.17395 | -0.041199 | -0.10529 | -0.20599 | -0.25635 | -0.22431 | -0.07782 | 0.068665 | 61.2991 | 61.3907 | 123.6328 | 123.848 | -0.10529 | 123.8113 | 61.3632 | -0.22431 | 123.848 | -0.10529 | 61.3632 | 123.6328 | 123.8113 | -124.0631 | -124.1135
393.7188 | 124.1409 | -61.3907 | 62.5076 | 0.12077 | 0.011324 | 0.011491 | 0.0014248 | 0.068579 | 0.00030767 | 0.069436 | -61.5051 | 62.4756 | -61.5601 | -61.6241 | 62.2055 | -0.027466 | -0.045776 | -0.013733 | 62.4252 | -61.6013 | -0.16937 | -0.032043 | -0.11444 | -0.23346 | -0.30212 | -0.21057 | -0.082397 | 0.054932 | 61.3449 | 61.377 | 123.5962 | 123.8663 | -0.11444 | 123.8159 | 61.3632 | -0.21057 | 123.8663 | -0.11444 | 61.3632 | 123.5962 | 123.8159 | -124.0677 | -124.1089
394.7188 | 124.173 | -61.3907 | 62.5031 | 0.059738 | 0.0044881 | 0.0095682 | -0.0041294 | 0.065161 | 0.00073487 | 0.070077 | -61.5143 | 62.3886 | -61.5417 | -61.5738 | 62.3062 | 0.064087 | -0.059509 | 0.086975 | 62.4161 | -61.5646 | -0.15106 | -0.11444 | -0.1236 | -0.18311 | -0.19684 | -0.17395 | -0.086975 | 0.027466 | 61.3312 | 61.4777 | 123.6969 | 123.7793 | -0.1236 | 123.8068 | 61.4548 | -0.17395 | 123.7793 | -0.1236 | 61.4548 | 123.6969 | 123.8068 | -124.0448 | -124.0677
395.7188 | 124.0906 | -61.4044 | 62.5259 | 0.03685 | 0.011111 | 0.0072184 | 0.0044156 | 0.068579 | -0.0026831 | 0.070718 | -61.4914 | 62.4664 | -61.5463 | -61.6287 | 62.2101 | -0.027466 | 0.032043 | -0.013733 | 62.4207 | -61.6241 | -0.14191 | -0.059509 | -0.086975 | -0.2243 | -0.31586 | -0.21973 | -0.10529 | 0.054932 | 61.4365 | 61.3907 | 123.6145 | 123.8708 | -0.086975 | 123.8251 | 61.377 | -0.21973 | 123.8708 | -0.086975 | 61.377 | 123.6145 | 123.8251 | -124.0723 | -124.1501
396.7188 | 124.1272 | -61.4044 | 62.5305 | 0.090256 | 0.0096151 | 0.011277 | 0.0056972 | 0.067084 | -0.0028967 | 0.067727 | -61.4868 | 62.4847 | -61.5601 | -61.6058 | 62.2284 | 0 | 0.036621 | 0.004578 | 62.4435 | -61.6241 | -0.15564 | -0.045777 | -0.082397 | -0.20142 | -0.30212 | -0.21973 | -0.086976 | 0.073243 | 61.441 | 61.409 | 123.6328 | 123.8892 | -0.082397 | 123.848 | 61.4044 | -0.21973 | 123.8892 | -0.082397 | 61.4044 | 123.6328 | 123.848 | -124.0906 | -124.1547
397.7188 | 123.8892 | -61.409 | 62.4527 | 0.082626 | 0.0098287 | 0.013841 | 0.001852 | 0.068579 | -0.00054693 | 0.070291 | -61.496 | 62.5031 | -61.5372 | -61.6699 | 62.1735 | -0.059509 | 0.009155 | -0.022888 | 62.4619 | -61.6287 | -0.12817 | 0.050354 | -0.086975 | -0.26093 | -0.27924 | -0.21973 | 0.009155 | 0.041198 | 61.4182 | 61.3861 | 123.5825 | 123.912 | -0.086975 | 123.8708 | 61.3495 | -0.21973 | 123.912 | -0.086975 | 61.3495 | 123.5825 | 123.8708 | -123.9899 | -124.0814
398.7188 | 124.0997 | -61.3953 | 62.5031 | 0.17418 | 0.011751 | 0.010209 | 0.001852 | 0.069007 | -0.0014013 | 0.070077 | -61.5372 | 62.5214 | -61.5509 | -61.6562 | 62.1964 | -0.036621 | -0.004578 | -0.022888 | 62.4344 | -61.6196 | -0.15564 | 0.01831 | -0.14191 | -0.26093 | -0.3067 | -0.2243 | -0.068665 | 0.013733 | 61.3907 | 61.3724 | 123.5916 | 123.9166 | -0.14191 | 123.8297 | 61.3586 | -0.2243 | 123.9166 | -0.14191 | 61.3586 | 123.5916 | 123.8297 | -124.054 | -124.1226
399.7188 | 124.0814 | -61.441 | 62.5122 | 0.16655 | 0.010256 | 0.0097818 | 0.0022794 | 0.069648 | -0.0039649 | 0.069222 | -61.6837 | 62.4344 | -61.5875 | -61.5967 | 62.1552 | -0.086975 | 0.050354 | -0.018311 | 62.4802 | -61.6379 | -0.14648 | -0.07782 | -0.24262 | -0.15564 | -0.35706 | -0.19684 | -0.032043 | -0.096131 | 61.4914 | 61.4227 | 123.5962 | 123.8754 | -0.24262 | 123.9212 | 61.3541 | -0.19684 | 123.8754 | -0.24262 | 61.3541 | 123.5962 | 123.9212 | -124.0997 | -124.1501
400.7188 | 124.1409 | -61.409 | 62.5534 | 0.097885 | 0.0068381 | 0.012559 | 0.001852 | 0.068793 | -0.00076053 | 0.068795 | -61.528 | 62.5076 | -61.5738 | -61.6562 | 62.1735 | -0.032043 | -0.41657 | -0.36163 | 62.384 | -61.6562 | -0.16479 | -0.045777 | -0.11902 | -0.24719 | -0.37994 | -0.24719 | -0.16937 | 0.045777 | 60.9924 | 61.0474 | 123.5825 | 123.9166 | -0.11902 | 123.793 | 61.377 | -0.24719 | 123.9166 | -0.11902 | 61.377 | 123.5825 | 123.793 | -124.1272 | -124.2096
401.7188 | 124.0677 | -61.409 | 62.5031 | 0.059738 | 0.0072653 | 0.01085 | 0.0020656 | 0.071143 | -0.0024695 | 0.069222 | -61.5234 | 62.4893 | -61.5601 | -61.6516 | 62.1918 | -0.022888 | 0.027466 | -0.032043 | 62.4527 | -61.615 | -0.15106 | -0.013733 | -0.11444 | -0.24261 | -0.31128 | -0.20599 | -0.050354 | 0.036622 | 61.4365 | 61.377 | 123.6008 | 123.8983 | -0.11444 | 123.8617 | 61.3861 | -0.20599 | 123.8983 | -0.11444 | 61.3861 | 123.6008 | 123.8617 | -124.0631 | -124.118
402.7188 | 124.1547 | -61.3861 | 62.5076 | -0.039444 | 0.0083333 | 0.0097818 | 0.0029202 | 0.069861 | -0.0020421 | 0.070931 | -61.4548 | 62.5122 | -61.5417 | -61.5738 | 62.2421 | 0.054932 | 0.022888 | 0.082397 | 62.4619 | -61.6196 | -0.15564 | 0.004578 | -0.068665 | -0.18768 | -0.2655 | -0.23346 | -0.045776 | 0.086975 | 61.409 | 61.4685 | 123.6282 | 123.8983 | -0.068665 | 123.848 | 61.441 | -0.23346 | 123.8983 | -0.068665 | 61.441 | 123.6282 | 123.848 | -124.0494 | -124.1272
403.7188 | 124.1547 | -61.4182 | 62.5305 | -0.0089264 | 0.0072653 | 0.0099954 | 0.00078404 | 0.069861 | 9.4068e-05 | 0.069436 | -61.441 | 62.4939 | -61.5463 | -61.5601 | 62.2742 | 0.07782 | 0.032043 | 0.07782 | 62.471 | -61.6196 | -0.12817 | -0.036622 | -0.022888 | -0.14191 | -0.25635 | -0.20142 | -0.05951 | 0.10529 | 61.4502 | 61.496 | 123.6923 | 123.912 | -0.022888 | 123.8892 | 61.496 | -0.20142 | 123.912 | -0.022888 | 61.496 | 123.6923 | 123.8892 | -124.0768 | -124.1501
404.7188 | 124.173 | -61.3678 | 62.4985 | 0.18944 | 0.0055563 | 0.011064 | 0.00014304 | 0.069434 | -0.00076053 | 0.071786 | -61.4822 | 62.4756 | -61.5509 | -61.615 | 62.2467 | 0 | -0.10071 | 0.032043 | 62.4161 | -61.5921 | -0.1831 | -0.022888 | -0.11444 | -0.24719 | -0.25177 | -0.2243 | -0.082397 | 0.068664 | 61.2671 | 61.3998 | 123.6145 | 123.8434 | -0.11444 | 123.7839 | 61.3678 | -0.2243 | 123.8434 | -0.11444 | 61.3678 | 123.6145 | 123.7839 | -124.0494 | -124.0906
405.7188 | 124.0677 | -61.4182 | 62.5351 | 0.059738 | 0.0079061 | 0.012986 | 0.0022794 | 0.069007 | -0.0020421 | 0.071359 | -61.4868 | 62.5168 | -61.5326 | -61.647 | 62.2055 | -0.022888 | 0.045776 | -0.004578 | 62.4527 | -61.6333 | -0.11444 | -0.01831 | -0.068664 | -0.22888 | -0.32959 | -0.21515 | -0.082397 | 0.045777 | 61.4639 | 61.4136 | 123.6237 | 123.9349 | -0.068664 | 123.8708 | 61.3953 | -0.21515 | 123.9349 | -0.068664 | 61.3953 | 123.6237 | 123.8708 | -124.0677 | -124.1684
406.7188 | 124.0906 | -61.4136 | 62.5488 | 0.04448 | 0.010042 | 0.018113 | 0.0022794 | 0.068366 | 9.4068e-05 | 0.067727 | -61.4914 | 62.4985 | -61.5509 | -61.615 | 62.2009 | -0.004578 | 0.032043 | 0.022888 | 62.4573 | -61.6104 | -0.13733 | -0.050354 | -0.07782 | -0.20142 | -0.3479 | -0.19684 | -0.091553 | 0.059509 | 61.4456 | 61.4365 | 123.6145 | 123.912 | -0.07782 | 123.8708 | 61.409 | -0.19684 | 123.912 | -0.07782 | 61.409 | 123.6145 | 123.8708 | -124.0997 | -124.1592
407.7188 | 124.1089 | -61.3998 | 62.5122 | -0.024185 | 0.010683 | 0.012773 | -7.0562e-05 | 0.069007 | -0.0011877 | 0.069863 | -61.4594 | 62.5076 | -61.528 | -61.5967 | 62.2238 | 0.018311 | 0.027466 | 0.032043 | 62.4939 | -61.6058 | -0.12817 | -0.004578 | -0.05951 | -0.19684 | -0.28839 | -0.20599 | -0.018311 | 0.068664 | 61.4273 | 61.4319 | 123.6237 | 123.9075 | -0.05951 | 123.8937 | 61.4182 | -0.20599 | 123.9075 | -0.05951 | 61.4182 | 123.6237 | 123.8937 | -124.0402 | -124.118
408.7188 | 124.1318 | -61.409 | 62.5305 | -0.039444 | 0.0068381 | 0.010636 | 0.002493 | 0.071357 | -0.00054693 | 0.068368 | -61.4685 | 62.5122 | -61.528 | -61.5875 | 62.2604 | 0.027466 | 0.045776 | 0.050354 | 62.4847 | -61.6058 | -0.11902 | -0.018311 | -0.059509 | -0.17853 | -0.27008 | -0.19684 | -0.045777 | 0.059509 | 61.4548 | 61.4594 | 123.6694 | 123.9212 | -0.059509 | 123.8937 | 61.4365 | -0.19684 | 123.9212 | -0.059509 | 61.4365 | 123.6694 | 123.8937 | -124.0585 | -124.1364
409.7188 | 124.1318 | -61.3953 | 62.5351 | -0.024185 | 0.0059835 | 0.014268 | -0.00028416 | 0.071357 | -0.0037511 | 0.068582 | -61.4456 | 62.4893 | -61.528 | -61.5738 | 62.265 | 0.068665 | 0.027466 | 0.082397 | 62.471 | -61.6013 | -0.13275 | -0.045776 | -0.050354 | -0.17853 | -0.27008 | -0.20599 | -0.064087 | 0.082397 | 61.4227 | 61.4777 | 123.6603 | 123.8846 | -0.050354 | 123.8663 | 61.4639 | -0.20599 | 123.8846 | -0.050354 | 61.4639 | 123.6603 | 123.8663 | -124.0631 | -124.1364
410.7188 | 124.1547 | -61.3861 | 62.5168 | 0.0063326 | 0.0079061 | 0.012345 | -0.00049776 | 0.070502 | -0.0016149 | 0.066873 | -61.4273 | 62.4893 | -61.5326 | -61.5738 | 62.2604 | 0.059509 | 0.022888 | 0.10071 | 62.4802 | -61.6058 | -0.14648 | -0.027466 | -0.041199 | -0.18768 | -0.25635 | -0.21973 | -0.036621 | 0.10529 | 61.409 | 61.4868 | 123.6465 | 123.8754 | -0.041199 | 123.8663 | 61.4456 | -0.21973 | 123.8754 | -0.041199 | 61.4456 | 123.6465 | 123.8663 | -124.0494 | -124.1226
411.7188 | 124.1364 | -61.3632 | 62.5122 | 1.8221 | 0.0066245 | 0.010423 | 0.00078404 | 0.069861 | 9.4068e-05 | 0.070718 | -61.3266 | 62.4802 | -61.5463 | -61.5372 | 62.265 | 0.073242 | 0.027466 | 0.11902 | 62.471 | -61.5829 | -0.18311 | -0.032043 | 0.036621 | -0.17395 | -0.24719 | -0.21973 | -0.041199 | 0.21973 | 61.3907 | 61.4822 | 123.6282 | 123.8434 | 0.036621 | 123.8342 | 61.4365 | -0.21973 | 123.8434 | 0.036621 | 61.4365 | 123.6282 | 123.8342 | -124.0585 | -124.0952
412.7188 | 124.1455 | -61.4182 | 62.5397 | -0.039444 | 0.0085471 | 0.01085 | 0.0014248 | 0.068579 | -0.00097413 | 0.071572 | -61.4502 | 62.4939 | -61.5646 | -61.5875 | 62.2513 | 0.041199 | 0.022888 | 0.064087 | 62.4756 | -61.615 | -0.14648 | -0.045777 | -0.032043 | -0.16937 | -0.28839 | -0.19684 | -0.064087 | 0.11444 | 61.441 | 61.4822 | 123.6694 | 123.912 | -0.032043 | 123.8937 | 61.4594 | -0.19684 | 123.912 | -0.032043 | 61.4594 | 123.6694 | 123.8937 | -124.1043 | -124.1547
413.7188 | 124.1226 | -61.3907 | 62.5122 | -0.054703 | 0.0089743 | 0.0078592 | 0.0016384 | 0.070075 | 0.0030847 | 0.070504 | -61.4365 | 62.4847 | -61.5372 | -61.5601 | 62.2604 | 0.054932 | 0.032043 | 0.082397 | 62.4847 | -61.6013 | -0.14648 | -0.027466 | -0.045776 | -0.16937 | -0.25177 | -0.21057 | -0.027466 | 0.10071 | 61.4227 | 61.4731 | 123.6511 | 123.8754 | -0.045776 | 123.8754 | 61.4456 | -0.21057 | 123.8754 | -0.045776 | 61.4456 | 123.6511 | 123.8754 | -124.0494 | -124.1135
414.7188 | 124.205 | -61.3907 | 62.4756 | 0.18944 | 0.0061971 | 0.011277 | -0.0028476 | 0.068366 | -0.0026831 | 0.071145 | -61.4273 | 62.3978 | -61.5509 | -61.5417 | 62.2925 | 0.059509 | -0.19226 | 0.091553 | 62.4207 | -61.5784 | -0.16022 | -0.07782 | -0.036621 | -0.15106 | -0.18311 | -0.18768 | -0.054932 | 0.1236 | 61.1984 | 61.4822 | 123.6832 | 123.7885 | -0.036621 | 123.8113 | 61.4502 | -0.18768 | 123.7885 | -0.036621 | 61.4502 | 123.6832 | 123.8113 | -124.0265 | -124.054
415.7188 | 124.118 | -61.3907 | 62.5259 | -0.047073 | 0.0068381 | 0.011491 | 0.0033474 | 0.069007 | -0.0020421 | 0.068795 | -61.4273 | 62.4939 | -61.5234 | -61.5875 | 62.2421 | 0.11902 | -0.004578 | 0.13275 | 62.4756 | -61.6058 | -0.13275 | -0.032044 | -0.036621 | -0.19684 | -0.28381 | -0.21515 | -0.050354 | 0.09613 | 61.3861 | 61.5234 | 123.6328 | 123.8846 | -0.036621 | 123.8663 | 61.5097 | -0.21515 | 123.8846 | -0.036621 | 61.5097 | 123.6328 | 123.8663 | -124.0494 | -124.1318
416.7188 | 124.1409 | -61.3678 | 62.5488 | -0.11574 | 0.0089743 | 0.0097818 | -0.0013522 | 0.070502 | -0.0022559 | 0.069436 | -61.4639 | 62.4847 | -61.528 | -61.5646 | 62.2787 | 0.082397 | 0.086975 | 0.1236 | 62.4939 | -61.615 | -0.16022 | -0.064087 | -0.09613 | -0.19684 | -0.27008 | -0.24719 | -0.054932 | 0.064087 | 61.4548 | 61.4914 | 123.6465 | 123.8525 | -0.09613 | 123.8617 | 61.4502 | -0.24719 | 123.8525 | -0.09613 | 61.4502 | 123.6465 | 123.8617 | -124.0768 | -124.1638
417.7188 | 124.118 | -61.3953 | 62.5671 | -0.13863 | 0.0081197 | 0.011918 | 0.00057044 | 0.068152 | -0.0026831 | 0.068154 | -61.4227 | 62.5168 | -61.5189 | -61.5509 | 62.2696 | 0.09613 | 0.054932 | 0.1236 | 62.4985 | -61.615 | -0.1236 | -0.050354 | -0.027465 | -0.15564 | -0.29755 | -0.21973 | -0.068665 | 0.096131 | 61.4502 | 61.5189 | 123.6649 | 123.912 | -0.027465 | 123.8937 | 61.4914 | -0.21973 | 123.912 | -0.027465 | 61.4914 | 123.6649 | 123.8937 | -124.086 | -124.1821
418.7188 | 124.1638 | -61.3724 | 62.5534 | -0.069961 | 0.0083333 | 0.01085 | 0.00057044 | 0.06922 | -0.0028967 | 0.067086 | -61.441 | 62.5031 | -61.5463 | -61.5417 | 62.233 | 0.07782 | 0.013733 | 0.11902 | 62.4847 | -61.6241 | -0.17395 | -0.050354 | -0.068665 | -0.16937 | -0.32044 | -0.25177 | -0.068665 | 0.10529 | 61.3861 | 61.4914 | 123.6053 | 123.8754 | -0.068665 | 123.8571 | 61.4502 | -0.25177 | 123.8754 | -0.068665 | 61.4502 | 123.6053 | 123.8571 | -124.0997 | -124.1776
419.7188 | 124.1226 | -61.3953 | 62.5168 | 0.11314 | 0.0072653 | 0.012559 | -0.001566 | 0.069861 | 0.00030767 | 0.069863 | -61.496 | 62.4985 | -61.5738 | -61.6379 | 62.2009 | -0.022888 | -0.045776 | -0.018311 | 62.4664 | -61.6104 | -0.17853 | -0.018311 | -0.10071 | -0.24261 | -0.31586 | -0.21515 | -0.050354 | 0.07782 | 61.3495 | 61.377 | 123.5962 | 123.8937 | -0.10071 | 123.8617 | 61.3724 | -0.21515 | 123.8937 | -0.10071 | 61.3724 | 123.5962 | 123.8617 | -124.0906 | -124.1272
420.7188 | 124.1821 | -61.4044 | 62.5397 | -0.08522 | 0.0079061 | 0.011491 | 0.0022794 | 0.06922 | -0.00054693 | 0.069863 | -61.4319 | 62.5076 | -61.5372 | -61.5509 | 62.2604 | 0.091553 | 0.036621 | 0.1236 | 62.4756 | -61.6104 | -0.13275 | -0.032044 | -0.027466 | -0.14648 | -0.27924 | -0.20599 | -0.064087 | 0.10529 | 61.441 | 61.528 | 123.6649 | 123.912 | -0.027466 | 123.88 | 61.496 | -0.20599 | 123.912 | -0.027466 | 61.496 | 123.6649 | 123.88 | -124.0768 | -124.1501
421.7188 | 124.1547 | -61.3907 | 62.5305 | -0.1844 | 0.0094015 | 0.0085 | 0.0022794 | 0.06922 | -0.0022559 | 0.070504 | -61.4273 | 62.4847 | -61.5417 | -61.5326 | 62.2696 | 0.091553 | 0.059509 | 0.1236 | 62.4802 | -61.6104 | -0.15106 | -0.045777 | -0.036621 | -0.14191 | -0.26093 | -0.21973 | -0.050354 | 0.11444 | 61.4502 | 61.5143 | 123.6603 | 123.8754 | -0.036621 | 123.8709 | 61.4822 | -0.21973 | 123.8754 | -0.036621 | 61.4822 | 123.6603 | 123.8709 | -124.0723 | -124.1409
422.7188 | 124.173 | -61.3998 | 62.5488 | -0.13863 | 0.0085471 | 0.009141 | -0.00028416 | 0.069434 | -0.0022559 | 0.070504 | -61.4594 | 62.4985 | -61.5463 | -61.5417 | 62.2833 | 0.09613 | 0.07782 | 0.13733 | 62.4847 | -61.6013 | -0.14648 | -0.050354 | -0.05951 | -0.14191 | -0.2655 | -0.20142 | -0.064087 | 0.086975 | 61.4777 | 61.5372 | 123.6832 | 123.8983 | -0.05951 | 123.8846 | 61.496 | -0.20142 | 123.8983 | -0.05951 | 61.496 | 123.6832 | 123.8846 | -124.0952 | -124.1501
423.7188 | 124.0906 | -61.3953 | 62.5488 | -0.23018 | 0.0070517 | 0.0089274 | -0.00049776 | 0.067298 | -0.0026831 | 0.067513 | -61.5051 | 62.5076 | -61.528 | -61.6104 | 62.2375 | 0.064087 | 0.13733 | 0.09613 | 62.5031 | -61.6013 | -0.13275 | -0.041199 | -0.10986 | -0.21515 | -0.31128 | -0.20599 | -0.045776 | 0.022888 | 61.5326 | 61.4914 | 123.6328 | 123.9029 | -0.10986 | 123.8983 | 61.4594 | -0.20599 | 123.9029 | -0.10986 | 61.4594 | 123.6328 | 123.8983 | -124.0768 | -124.1501
424.7188 | 124.1043 | -61.409 | 62.5397 | 0.04448 | 0.011538 | 0.012559 | 0.0014248 | 0.069007 | -0.00076053 | 0.070718 | -61.4639 | 62.4893 | -61.5372 | -61.5967 | 62.2147 | 0.013733 | 0.004578 | 0.022888 | 62.4802 | -61.6196 | -0.12817 | -0.050354 | -0.054931 | -0.18768 | -0.32501 | -0.21057 | -0.059509 | 0.073242 | 61.4136 | 61.4319 | 123.6237 | 123.8983 | -0.054931 | 123.8892 | 61.4227 | -0.21057 | 123.8983 | -0.054931 | 61.4227 | 123.6237 | 123.8892 | -124.0768 | -124.1592
425.7188 | 124.1043 | -61.3998 | 62.5305 | -0.73372 | 0.0091879 | 0.010636 | 0.00035684 | 0.071357 | -0.00076053 | 0.070931 | -61.5189 | 62.4802 | -61.5509 | -61.6287 | 62.1689 | -0.054932 | -0.018311 | -0.045776 | 62.4756 | -61.6241 | -0.15106 | -0.050354 | -0.11902 | -0.22888 | -0.36163 | -0.22431 | -0.054932 | 0.032043 | 61.3815 | 61.3541 | 123.5687 | 123.88 | -0.11902 | 123.8754 | 61.3449 | -0.22431 | 123.88 | -0.11902 | 61.3449 | 123.5687 | 123.8754 | -124.0814 | -124.1547
426.7188 | 124.1547 | -61.3907 | 62.5259 | -0.16914 | 0.0081197 | 0.0095682 | 0.00078404 | 0.070075 | -0.0011877 | 0.068582 | -61.4456 | 62.5259 | -61.5601 | -61.5646 | 62.265 | 0.086975 | 0.068665 | 0.11902 | 62.5031 | -61.5875 | -0.16937 | 0 | -0.054932 | -0.17395 | -0.26093 | -0.19684 | -0.022888 | 0.11444 | 61.4594 | 61.5097 | 123.6557 | 123.9166 | -0.054932 | 123.8937 | 61.4777 | -0.19684 | 123.9166 | -0.054932 | 61.4777 | 123.6557 | 123.8937 | -124.086 | -124.1135
427.7188 | 124.1272 | -61.377 | 62.5488 | -0.22255 | 0.0076925 | 0.012132 | 0.00057044 | 0.068366 | -0.0024695 | 0.069009 | -61.4639 | 62.4893 | -61.5555 | -61.5875 | 62.2375 | 0.068665 | 0.10986 | 0.10529 | 62.5122 | -61.5921 | -0.17853 | -0.059509 | -0.086975 | -0.21057 | -0.31128 | -0.21515 | -0.036621 | 0.091553 | 61.4868 | 61.4822 | 123.6145 | 123.8663 | -0.086975 | 123.8892 | 61.4456 | -0.21515 | 123.8663 | -0.086975 | 61.4456 | 123.6145 | 123.8892 | -124.1043 | -124.1409
428.7188 | 124.1272 | -61.3907 | 62.5671 | -0.19966 | 0.0064107 | 0.0080728 | -0.002634 | 0.066657 | -0.00076053 | 0.070077 | -61.4914 | 62.4985 | -61.5463 | -61.5921 | 62.233 | 0.054932 | 0.1236 | 0.091553 | 62.5076 | -61.5967 | -0.15564 | -0.068665 | -0.10071 | -0.20142 | -0.33417 | -0.20599 | -0.05951 | 0.054932 | 61.5143 | 61.4822 | 123.6237 | 123.8892 | -0.10071 | 123.8983 | 61.4456 | -0.20599 | 123.8892 | -0.10071 | 61.4456 | 123.6237 | 123.8983 | -124.1135 | -124.1638
429.7188 | 124.1409 | -61.377 | 62.5534 | -0.024185 | 0.0074789 | 0.011704 | 0.0037746 | 0.069007 | -0.00054693 | 0.067941 | -61.4365 | 62.4893 | -61.5417 | -61.5829 | 62.2284 | 0.022888 | 0.018311 | 0.050354 | 62.471 | -61.615 | -0.16479 | -0.064087 | -0.059509 | -0.20599 | -0.32501 | -0.23804 | -0.082398 | 0.10529 | 61.3953 | 61.4273 | 123.6053 | 123.8663 | -0.059509 | 123.848 | 61.3998 | -0.23804 | 123.8663 | -0.059509 | 61.3998 | 123.6053 | 123.848 | -124.0952 | -124.1684
430.7344 | 124.2004 | -61.3678 | 62.4756 | 2.1502 | 0.0057699 | 0.0065774 | -0.0037022 | 0.069434 | -0.0022559 | 0.069436 | -61.2991 | 62.3932 | -61.5372 | -61.5143 | 62.3474 | 0.059509 | -0.21973 | 0.086975 | 62.4115 | -61.5921 | -0.16937 | -0.082398 | 0.068665 | -0.14648 | -0.12817 | -0.2243 | -0.064087 | 0.23804 | 61.1481 | 61.4548 | 123.7152 | 123.761 | 0.068665 | 123.7793 | 61.4273 | -0.2243 | 123.761 | 0.068665 | 61.4273 | 123.7152 | 123.7793 | -124.0128 | -124.0677
431.7188 | 124.118 | -61.3998 | 62.5534 | 0.75401 | 0.0074789 | 0.0059366 | -0.00092496 | 0.065802 | -0.0016149 | 0.070077 | -61.4548 | 62.4893 | -61.5555 | -61.5784 | 62.2467 | 0.059509 | 0.15106 | 0.091553 | 62.4985 | -61.5967 | -0.15564 | -0.064087 | -0.054932 | -0.17853 | -0.3067 | -0.19684 | -0.054932 | 0.10071 | 61.5509 | 61.4914 | 123.6465 | 123.8892 | -0.054932 | 123.8983 | 61.4594 | -0.19684 | 123.8892 | -0.054932 | 61.4594 | 123.6465 | 123.8983 | -124.1089 | -124.1501
432.7188 | 124.118 | -61.409 | 62.5671 | -0.21492 | 0.0068381 | 0.0072184 | -0.0030612 | 0.06388 | -0.0014013 | 0.069436 | -61.5097 | 62.4619 | -61.5417 | -61.6882 | 62.2421 | 0.10529 | 0.054932 | 0.10986 | 62.4985 | -61.615 | -0.13275 | -0.10529 | -0.10071 | -0.27923 | -0.32501 | -0.20599 | -0.068665 | 0.032043 | 61.4639 | 61.5189 | 123.6511 | 123.8708 | -0.10071 | 123.9075 | 61.5143 | -0.20599 | 123.8708 | -0.10071 | 61.5143 | 123.6511 | 123.9075 | -124.1089 | -124.1821
433.7188 | 124.1226 | -61.3907 | 62.5717 | -0.23018 | 0.0089743 | 0.0085 | -0.00049776 | 0.06623 | 0.00052127 | 0.068582 | -61.4822 | 62.4847 | -61.5601 | -61.5967 | 62.2284 | 0.064087 | 0.10986 | 0.082397 | 62.5031 | -61.5921 | -0.16937 | -0.086975 | -0.091553 | -0.20599 | -0.34332 | -0.20142 | -0.068664 | 0.07782 | 61.5005 | 61.4731 | 123.6191 | 123.8754 | -0.091553 | 123.8937 | 61.4548 | -0.20142 | 123.8754 | -0.091553 | 61.4548 | 123.6191 | 123.8937 | -124.1318 | -124.1638
434.7188 | 124.0768 | -61.3953 | 62.5442 | -0.10811 | 0.0072653 | 0.0095682 | 0.0039882 | 0.067725 | -0.0016149 | 0.067941 | -61.4319 | 62.4893 | -61.5097 | -61.5509 | 62.265 | 0.073242 | 0.032043 | 0.10986 | 62.4847 | -61.6058 | -0.11444 | -0.054931 | -0.036621 | -0.15564 | -0.27923 | -0.21057 | -0.059509 | 0.07782 | 61.4273 | 61.5051 | 123.6603 | 123.8846 | -0.036621 | 123.88 | 61.4685 | -0.21057 | 123.8846 | -0.036621 | 61.4685 | 123.6603 | 123.88 | -124.054 | -124.1501
435.7188 | 124.0173 | -61.4456 | 62.5351 | 0.1284 | 0.010042 | 0.01085 | 0.001852 | 0.068579 | -0.0026831 | 0.069436 | -61.5189 | 62.4985 | -61.5738 | -61.6608 | 62.1506 | -0.050354 | -0.009155 | -0.045776 | 62.4893 | -61.615 | -0.12817 | -0.036621 | -0.073242 | -0.21515 | -0.38452 | -0.16937 | -0.045776 | 0.054932 | 61.4365 | 61.3998 | 123.5962 | 123.9441 | -0.073242 | 123.9349 | 61.3953 | -0.16937 | 123.9441 | -0.073242 | 61.3953 | 123.5962 | 123.9349 | -124.1089 | -124.1501
436.7188 | 124.1592 | -61.377 | 62.558 | -0.19966 | 0.0066245 | 0.0093546 | -0.0047702 | 0.067511 | -0.0016149 | 0.070077 | -61.4502 | 62.4344 | -61.5463 | -61.5372 | 62.2787 | 0.11444 | 0.09613 | 0.14191 | 62.5031 | -61.5738 | -0.16937 | -0.1236 | -0.073242 | -0.16022 | -0.27923 | -0.19684 | -0.054931 | 0.096131 | 61.4731 | 61.5189 | 123.6557 | 123.8113 | -0.073242 | 123.88 | 61.4914 | -0.19684 | 123.8113 | -0.073242 | 61.4914 | 123.6557 | 123.88 | -124.1043 | -124.1318
437.7188 | 124.1592 | -61.3678 | 62.5397 | -0.26833 | 0.0064107 | 0.0082864 | -0.0028476 | 0.066016 | -0.0022559 | 0.068154 | -61.4319 | 62.4115 | -61.5189 | -61.5234 | 62.2971 | 0.12817 | 0.050354 | 0.16479 | 62.4939 | -61.5646 | -0.15106 | -0.12817 | -0.064087 | -0.15564 | -0.24262 | -0.19684 | -0.045777 | 0.086975 | 61.4182 | 61.5326 | 123.6649 | 123.7793 | -0.064087 | 123.8617 | 61.496 | -0.19684 | 123.7793 | -0.064087 | 61.496 | 123.6649 | 123.8617 | -124.0585 | -124.1043
438.7188 | 124.1043 | -61.3907 | 62.5809 | -0.19966 | 0.0059835 | 0.0097818 | -0.00071136 | 0.06623 | -0.0018285 | 0.068154 | -61.496 | 62.4527 | -61.5326 | -61.5921 | 62.2421 | 0.064087 | 0.1236 | 0.11444 | 62.4802 | -61.6013 | -0.14191 | -0.12817 | -0.10529 | -0.20142 | -0.33875 | -0.21057 | -0.10071 | 0.036621 | 61.5143 | 61.5051 | 123.6328 | 123.8434 | -0.10529 | 123.8709 | 61.4548 | -0.21057 | 123.8434 | -0.10529 | 61.4548 | 123.6328 | 123.8709 | -124.1135 | -124.1821
439.7188 | 124.0997 | -61.3998 | 62.5717 | -0.62691 | 0.0091879 | 0.0072184 | -0.00028416 | 0.064734 | -0.0020421 | 0.068154 | -61.528 | 62.471 | -61.5555 | -61.5875 | 62.233 | 0.059509 | 0.13733 | 0.086975 | 62.4893 | -61.615 | -0.15564 | -0.10071 | -0.12817 | -0.18768 | -0.33875 | -0.21515 | -0.082397 | 0.027466 | 61.5372 | 61.4868 | 123.6328 | 123.8708 | -0.12817 | 123.8892 | 61.4594 | -0.21515 | 123.8708 | -0.12817 | 61.4594 | 123.6328 | 123.8892 | -124.1272 | -124.1867
440.7344 | 124.1318 | -61.3861 | 62.4893 | 0.19707 | 0.0074789 | 0.011704 | 0.001852 | 0.069861 | -0.0011877 | 0.069222 | -61.4822 | 62.4573 | -61.5601 | -61.6013 | 62.233 | -0.004578 | -0.12817 | 0.009155 | 62.4573 | -61.5829 | -0.17395 | -0.032044 | -0.096131 | -0.21515 | -0.25635 | -0.19684 | -0.032044 | 0.07782 | 61.2579 | 61.3953 | 123.6191 | 123.8434 | -0.096131 | 123.8434 | 61.3815 | -0.19684 | 123.8434 | -0.096131 | 61.3815 | 123.6191 | 123.8434 | -124.0494 | -124.0723
441.7188 | 124.0356 | -61.3724 | 62.5442 | -0.19203 | 0.0064107 | 0.0078592 | -0.001566 | 0.064948 | -0.0014013 | 0.070077 | -61.5097 | 62.4619 | -61.5326 | -61.5738 | 62.233 | 0.068665 | 0.13275 | 0.28839 | 62.5351 | -61.5875 | -0.16022 | -0.082397 | -0.13733 | -0.20142 | -0.31128 | -0.21515 | -0.009155 | 0.022888 | 61.5051 | 61.6608 | 123.6053 | 123.8342 | -0.13733 | 123.9075 | 61.441 | -0.21515 | 123.8342 | -0.13733 | 61.441 | 123.6053 | 123.9075 | -124.0768 | -124.1318
442.7188 | 124.086 | -61.3678 | 62.5809 | -0.19203 | 0.0068381 | 0.0082864 | 0.0012112 | 0.065589 | -0.0018285 | 0.069222 | -61.4914 | 62.471 | -61.5417 | -61.5738 | 62.2467 | 0.068665 | 0.1236 | 0.10071 | 62.4939 | -61.5875 | -0.17395 | -0.10986 | -0.1236 | -0.20599 | -0.33417 | -0.21973 | -0.086976 | 0.050354 | 61.4914 | 61.4685 | 123.6145 | 123.8388 | -0.1236 | 123.8617 | 61.4365 | -0.21973 | 123.8388 | -0.1236 | 61.4365 | 123.6145 | 123.8617 | -124.1226 | -124.1684
443.7188 | 124.173 | -61.3449 | 62.5534 | -0.19203 | 0.0049155 | 0.0059366 | -0.0017796 | 0.066443 | -0.0018285 | 0.068795 | -61.4136 | 62.4161 | -61.5234 | -61.4914 | 62.3199 | 0.16479 | 0.004578 | 0.19226 | 62.439 | -61.5509 | -0.17853 | -0.13733 | -0.068664 | -0.14648 | -0.23346 | -0.20599 | -0.11444 | 0.10986 | 61.3495 | 61.5372 | 123.6649 | 123.761 | -0.068664 | 123.7839 | 61.5097 | -0.20599 | 123.761 | -0.068664 | 61.5097 | 123.6649 | 123.7839 | -124.0768 | -124.1043
444.7188 | 124.1364 | -61.3815 | 62.558 | -0.13863 | 0.0064107 | 0.010209 | 0.004202 | 0.066657 | -0.0033239 | 0.068154 | -61.4182 | 62.4802 | -61.5463 | -61.5189 | 62.2742 | 0.09613 | 0.032043 | 0.1236 | 62.4527 | -61.5967 | -0.16479 | -0.077819 | -0.036621 | -0.13733 | -0.28381 | -0.21515 | -0.10529 | 0.12817 | 61.4136 | 61.5051 | 123.6557 | 123.8617 | -0.036621 | 123.8342 | 61.4777 | -0.21515 | 123.8617 | -0.036621 | 61.4777 | 123.6557 | 123.8342 | -124.1043 | -124.1547
445.7188 | 124.1318 | -61.3586 | 62.5397 | -0.27596 | 0.0055563 | 0.0078592 | -0.0032748 | 0.067511 | -0.0014013 | 0.068582 | -61.4182 | 62.4344 | -61.5234 | -61.5372 | 62.3016 | 0.11444 | 0.073242 | 0.17395 | 62.4573 | -61.5692 | -0.16479 | -0.10529 | -0.059509 | -0.17853 | -0.23804 | -0.21057 | -0.082398 | 0.10529 | 61.4319 | 61.5326 | 123.6603 | 123.793 | -0.059509 | 123.8159 | 61.4731 | -0.21057 | 123.793 | -0.059509 | 61.4731 | 123.6603 | 123.8159 | -124.0631 | -124.1089
446.7188 | 124.0631 | -61.3998 | 62.5671 | -0.29884 | 0.0064107 | 0.012345 | 0.0012112 | 0.066443 | 0.0015893 | 0.066659 | -61.4777 | 62.4481 | -61.5326 | -61.5921 | 62.2513 | 0.064087 | 0.13275 | 0.09613 | 62.4847 | -61.5875 | -0.13275 | -0.11902 | -0.07782 | -0.19226 | -0.31586 | -0.18768 | -0.082398 | 0.054932 | 61.5326 | 61.496 | 123.6511 | 123.848 | -0.07782 | 123.8846 | 61.4639 | -0.18768 | 123.848 | -0.07782 | 61.4639 | 123.6511 | 123.8846 | -124.0997 | -124.1547
447.7188 | 124.0952 | -61.3998 | 62.6038 | -0.22255 | 0.0072653 | 0.01085 | 0.0014248 | 0.066443 | -0.0020421 | 0.067086 | -61.4868 | 62.4481 | -61.5234 | -61.5829 | 62.2421 | 0.068665 | 0.10986 | 0.10529 | 62.4939 | -61.5601 | -0.1236 | -0.15564 | -0.086975 | -0.18311 | -0.36163 | -0.16022 | -0.10986 | 0.036621 | 61.5097 | 61.5051 | 123.642 | 123.848 | -0.086975 | 123.8937 | 61.4685 | -0.16022 | 123.848 | -0.086975 | 61.4685 | 123.642 | 123.8937 | -124.1272 | -124.1638
448.7188 | 124.1089 | -61.377 | 62.5763 | -0.23018 | 0.0068381 | 0.01085 | -0.00092496 | 0.064521 | -0.0031103 | 0.067941 | -61.4456 | 62.4298 | -61.5234 | -61.5509 | 62.2604 | 0.07782 | 0.10529 | 0.15564 | 62.4664 | -61.5692 | -0.14648 | -0.14648 | -0.068665 | -0.17395 | -0.31586 | -0.19226 | -0.10986 | 0.077819 | 61.4822 | 61.5326 | 123.6374 | 123.8068 | -0.068665 | 123.8434 | 61.4548 | -0.19226 | 123.8068 | -0.068665 | 61.4548 | 123.6374 | 123.8434 | -124.0997 | -124.1455
449.7188 | 124.1226 | -61.377 | 62.5534 | -0.25307 | 0.0061971 | 0.0089274 | 0.00099764 | 0.065589 | -0.0024695 | 0.068795 | -61.441 | 62.4344 | -61.528 | -61.5326 | 62.2971 | 0.12817 | 0.059509 | 0.16479 | 62.4573 | -61.5646 | -0.15106 | -0.11902 | -0.064087 | -0.15564 | -0.25635 | -0.18768 | -0.096131 | 0.086975 | 61.4365 | 61.5417 | 123.674 | 123.8113 | -0.064087 | 123.8342 | 61.5051 | -0.18768 | 123.8113 | -0.064087 | 61.5051 | 123.674 | 123.8342 | -124.0814 | -124.118
450.7188 | 124.2142 | -61.322 | 62.5214 | -1.4509 | 0.0036337 | 0.010209 | -0.002634 | 0.06623 | -0.0031103 | 0.068154 | -61.5051 | 62.3703 | -61.5372 | -61.4685 | 62.3474 | 0.16479 | -0.059509 | 0.23346 | 62.4298 | -61.5326 | -0.21515 | -0.15106 | -0.18311 | -0.14648 | -0.17395 | -0.21057 | -0.091552 | 0.032043 | 61.2625 | 61.5555 | 123.6694 | 123.6923 | -0.18311 | 123.7518 | 61.4868 | -0.21057 | 123.6923 | -0.18311 | 61.4868 | 123.6694 | 123.7518 | -124.0585 | -124.054
451.7188 | 124.2142 | -61.3541 | 62.5351 | -0.1844 | 0.0051291 | 0.010636 | -0.0017796 | 0.064093 | -0.00076053 | 0.068795 | -61.5417 | 62.4207 | -61.4822 | -61.5509 | 62.3703 | 0.20599 | -0.09613 | 0.19684 | 62.4344 | -61.5555 | -0.12817 | -0.11444 | -0.18768 | -0.19684 | -0.16479 | -0.20142 | -0.10071 | -0.059509 | 61.2579 | 61.5509 | 123.7244 | 123.7747 | -0.18768 | 123.7885 | 61.5601 | -0.20142 | 123.7747 | -0.18768 | 61.5601 | 123.7244 | 123.7885 | -124.0173 | -124.0906
452.7188 | 124.2233 | -61.3586 | 62.5305 | -0.19203 | 0.0032065 | 0.01085 | -0.00092496 | 0.064734 | -0.0024695 | 0.067513 | -61.4182 | 62.4023 | -61.5189 | -61.4777 | 62.3337 | 0.16479 | -0.036621 | 0.21515 | 62.4069 | -61.5509 | -0.16022 | -0.12817 | -0.059509 | -0.11902 | -0.19684 | -0.19226 | -0.1236 | 0.10071 | 61.322 | 61.5738 | 123.6923 | 123.761 | -0.059509 | 123.7656 | 61.5234 | -0.19226 | 123.761 | -0.059509 | 61.5234 | 123.6923 | 123.7656 | -124.0494 | -124.0814
453.7188 | 124.173 | -61.3541 | 62.5626 | -0.25307 | 0.0057699 | 0.0072184 | -0.00028416 | 0.064948 | -0.0046057 | 0.067513 | -61.4365 | 62.4252 | -61.5143 | -61.5143 | 62.2787 | 0.1236 | 0.064087 | 0.16937 | 62.4527 | -61.5601 | -0.16022 | -0.13733 | -0.082397 | -0.16022 | -0.28381 | -0.20599 | -0.10986 | 0.07782 | 61.4182 | 61.5234 | 123.6328 | 123.7793 | -0.082397 | 123.8068 | 61.4777 | -0.20599 | 123.7793 | -0.082397 | 61.4777 | 123.6328 | 123.8068 | -124.0768 | -124.1226
454.7188 | 124.0997 | -61.3815 | 62.5671 | -0.13863 | 0.0064107 | 0.012132 | 0.0039882 | 0.063025 | -0.00054693 | 0.069436 | -61.4822 | 62.4802 | -61.5555 | -61.5784 | 62.2284 | 0.073242 | 0.12817 | 0.10071 | 62.4619 | -61.5921 | -0.17395 | -0.086975 | -0.10071 | -0.19684 | -0.33874 | -0.21057 | -0.10529 | 0.073242 | 61.5097 | 61.4822 | 123.6099 | 123.8617 | -0.10071 | 123.8434 | 61.4548 | -0.21057 | 123.8617 | -0.10071 | 61.4548 | 123.6099 | 123.8434 | -124.1226 | -124.1592
455.7188 | 124.205 | -61.322 | 62.5397 | -0.21492 | 0.0040609 | 0.0065774 | -0.00049776 | 0.064307 | -0.0011877 | 0.066659 | -61.4136 | 62.4207 | -61.5143 | -61.4914 | 62.3199 | 0.15564 | 0.013733 | 0.20599 | 62.4527 | -61.5417 | -0.19226 | -0.11902 | -0.091553 | -0.16937 | -0.21973 | -0.21973 | -0.086975 | 0.10071 | 61.3358 | 61.528 | 123.642 | 123.7427 | -0.091553 | 123.7747 | 61.4777 | -0.21973 | 123.7427 | -0.091553 | 61.4777 | 123.642 | 123.7747 | -124.054 | -124.0814
456.7188 | 124.1913 | -61.3403 | 62.5259 | -0.14626 | 0.0059835 | 0.0061502 | -0.0037022 | 0.065161 | -0.00097413 | 0.069009 | -61.4182 | 62.4023 | -61.5097 | -61.4822 | 62.3199 | 0.16022 | -0.018311 | 0.21973 | 62.4298 | -61.5326 | -0.16937 | -0.1236 | -0.07782 | -0.14191 | -0.20599 | -0.19226 | -0.09613 | 0.091553 | 61.322 | 61.5601 | 123.6603 | 123.7427 | -0.07782 | 123.7701 | 61.5005 | -0.19226 | 123.7427 | -0.07782 | 61.5005 | 123.6603 | 123.7701 | -124.0356 | -124.0585
457.7188 | 124.2508 | -61.3174 | 62.5534 | -0.10811 | 0.0064107 | 0.0042276 | -0.0030612 | 0.063025 | 9.4068e-05 | 0.069436 | -61.3998 | 62.3657 | -61.5005 | -61.4594 | 62.3795 | 0.16479 | -0.068665 | 0.21057 | 62.4252 | -61.5417 | -0.1831 | -0.18768 | -0.082397 | -0.14191 | -0.17395 | -0.2243 | -0.12817 | 0.10071 | 61.2488 | 61.528 | 123.6969 | 123.6832 | -0.082397 | 123.7427 | 61.4822 | -0.2243 | 123.6832 | -0.082397 | 61.4822 | 123.6969 | 123.7427 | -124.054 | -124.0952
458.7188 | 124.205 | -61.3312 | 62.5305 | 0.57854 | 0.0053427 | 0.0097818 | 0.00014304 | 0.064307 | -0.0033239 | 0.067513 | -61.3678 | 62.3978 | -61.496 | -61.4685 | 62.352 | 0.16937 | -0.064087 | 0.2243 | 62.4161 | -61.5509 | -0.1648 | -0.13275 | -0.036621 | -0.13733 | -0.17853 | -0.21973 | -0.11444 | 0.12817 | 61.2671 | 61.5555 | 123.6832 | 123.7289 | -0.036621 | 123.7473 | 61.5005 | -0.21973 | 123.7289 | -0.036621 | 61.5005 | 123.6832 | 123.7473 | -124.0265 | -124.0814
459.7188 | 124.1959 | -61.3541 | 62.5168 | -0.23781 | 0.0072653 | 0.007432 | 0.00014304 | 0.063239 | -0.0035375 | 0.065804 | -61.4044 | 62.3795 | -61.5143 | -61.4868 | 62.3108 | 0.14648 | 0.009155 | 0.20599 | 62.4252 | -61.5372 | -0.16022 | -0.13733 | -0.050354 | -0.13275 | -0.20599 | -0.18311 | -0.091553 | 0.10986 | 61.3632 | 61.5601 | 123.6649 | 123.7335 | -0.050354 | 123.7793 | 61.5005 | -0.18311 | 123.7335 | -0.050354 | 61.5005 | 123.6649 | 123.7793 | -124.0311 | -124.054
460.7188 | 124.1959 | -61.3541 | 62.5259 | -0.14626 | 0.0064107 | 0.010423 | 0.0012112 | 0.063239 | -0.0024695 | 0.0673 | -61.4136 | 62.3932 | -61.5097 | -61.4594 | 62.3383 | 0.16937 | -0.022888 | 0.21515 | 62.3978 | -61.5234 | -0.15564 | -0.13275 | -0.059509 | -0.10529 | -0.18768 | -0.16937 | -0.12817 | 0.096131 | 61.3312 | 61.5692 | 123.6923 | 123.7473 | -0.059509 | 123.7518 | 61.5234 | -0.16937 | 123.7473 | -0.059509 | 61.5234 | 123.6923 | 123.7518 | -124.0356 | -124.0494
461.7188 | 124.2416 | -61.3449 | 62.5351 | -0.16914 | 0.0012839 | 0.0059366 | -0.00092496 | 0.063666 | -0.0020421 | 0.067941 | -61.3953 | 62.3932 | -61.5051 | -61.4594 | 62.3566 | 0.16479 | -0.059509 | 0.2243 | 62.4207 | -61.5463 | -0.16022 | -0.14191 | -0.050354 | -0.11444 | -0.17853 | -0.20142 | -0.11444 | 0.10986 | 61.2854 | 61.5692 | 123.7015 | 123.7381 | -0.050354 | 123.7656 | 61.5097 | -0.20142 | 123.7381 | -0.050354 | 61.5097 | 123.7015 | 123.7656 | -124.0402 | -124.0814
462.7188 | 124.2096 | -61.3312 | 62.5351 | 0.63194 | 0.0070517 | 0.0095682 | -0.00049776 | 0.063452 | -0.0026831 | 0.069009 | -61.3861 | 62.3749 | -61.5326 | -61.4548 | 62.3383 | 0.1831 | -0.064087 | 0.21973 | 62.4344 | -61.528 | -0.20142 | -0.16022 | -0.054931 | -0.1236 | -0.19684 | -0.19684 | -0.10071 | 0.14648 | 61.2671 | 61.5509 | 123.6694 | 123.7061 | -0.054931 | 123.7656 | 61.5143 | -0.19684 | 123.7061 | -0.054931 | 61.5143 | 123.6694 | 123.7656 | -124.0677 | -124.0631
463.7188 | 124.2462 | -61.3449 | 62.5076 | -0.20729 | 0.0053427 | 0.009141 | 0.00078404 | 0.064948 | -0.0016149 | 0.069222 | -61.2488 | 62.4252 | -61.4914 | -61.5189 | 62.3611 | 0.20599 | -0.11444 | 0.2243 | 62.4115 | -61.5234 | -0.14648 | -0.082397 | 0.096131 | -0.17395 | -0.14648 | -0.17853 | -0.09613 | 0.24262 | 61.2305 | 61.5692 | 123.7061 | 123.7701 | 0.096131 | 123.7564 | 61.5509 | -0.17853 | 123.7701 | 0.096131 | 61.5509 | 123.7061 | 123.7564 | -123.999 | -124.0311
464.7188 | 124.1043 | -61.3678 | 62.5763 | -0.16914 | 0.0083333 | 0.0076456 | 0.003561 | 0.063025 | -0.0026831 | 0.066873 | -61.4777 | 62.4664 | -61.5097 | -61.5601 | 62.2513 | 0.068665 | 0.10529 | 0.091553 | 62.4619 | -61.5967 | -0.14191 | -0.10986 | -0.10986 | -0.19226 | -0.32501 | -0.22888 | -0.11444 | 0.032044 | 61.4731 | 61.4594 | 123.6191 | 123.8342 | -0.10986 | 123.8297 | 61.4365 | -0.22888 | 123.8342 | -0.10986 | 61.4365 | 123.6191 | 123.8297 | -124.086 | -124.173
465.7188 | 124.2279 | -61.3541 | 62.5214 | -0.069961 | 0.0036337 | 0.0095682 | -0.0011386 | 0.065589 | -0.0016149 | 0.068582 | -61.4548 | 62.3703 | -61.5326 | -61.496 | 62.3108 | 0.11902 | -0.10071 | 0.16937 | 62.4207 | -61.528 | -0.17853 | -0.15106 | -0.10071 | -0.14191 | -0.21057 | -0.17395 | -0.10071 | 0.07782 | 61.2534 | 61.5234 | 123.6649 | 123.7244 | -0.10071 | 123.7747 | 61.4731 | -0.17395 | 123.7244 | -0.10071 | 61.4731 | 123.6649 | 123.7747 | -124.054 | -124.0494
466.7188 | 124.2737 | -61.3586 | 62.5076 | -0.10048 | 0.0064107 | 0.0042276 | 0.00057044 | 0.062598 | -0.00033333 | 0.069222 | -61.4227 | 62.3566 | -61.5326 | -61.4639 | 62.3703 | 0.17853 | -0.10071 | 0.21515 | 62.3703 | -61.5234 | -0.17395 | -0.15106 | -0.064086 | -0.10529 | -0.13733 | -0.16479 | -0.13733 | 0.10986 | 61.2579 | 61.5738 | 123.7289 | 123.7152 | -0.064086 | 123.7289 | 61.5372 | -0.16479 | 123.7152 | -0.064086 | 61.5372 | 123.7289 | 123.7289 | -124.0402 | -124.0311
467.7188 | 124.2325 | -61.3312 | 62.558 | -0.47432 | 0.0072653 | 0.0059366 | 0.00099764 | 0.06153 | -0.0022559 | 0.072 | -61.6608 | 62.3795 | -61.5189 | -61.5051 | 62.3474 | 0.17395 | -0.073242 | 0.21057 | 62.384 | -61.5189 | -0.18768 | -0.17853 | -0.32959 | -0.17395 | -0.21057 | -0.18768 | -0.17395 | -0.14191 | 61.2579 | 61.5417 | 123.6786 | 123.7106 | -0.32959 | 123.7152 | 61.5051 | -0.18768 | 123.7106 | -0.32959 | 61.5051 | 123.6786 | 123.7152 | -124.0768 | -124.0768
468.7188 | 124.2233 | -61.3586 | 62.5168 | -0.1844 | 0.0064107 | 0.0070048 | -0.0051974 | 0.062598 | -0.00033333 | 0.068582 | -61.3815 | 62.3611 | -61.5372 | -61.5509 | 62.4435 | 0.22888 | -0.20142 | 0.24719 | 62.3795 | -61.5417 | -0.17853 | -0.15564 | -0.022888 | -0.19226 | -0.073243 | -0.1831 | -0.13733 | 0.15564 | 61.1572 | 61.6058 | 123.8022 | 123.7198 | -0.022888 | 123.7381 | 61.5875 | -0.1831 | 123.7198 | -0.022888 | 61.5875 | 123.8022 | 123.7381 | -124.054 | -124.0585
469.7188 | 124.0814 | -61.3129 | 62.5076 | -0.11574 | 0.0055563 | 0.0093546 | -7.0562e-05 | 0.062812 | -0.0041785 | 0.069863 | -61.3861 | 62.384 | -61.5005 | -61.4182 | 62.384 | 0.18768 | -0.073242 | 0.65002 | 62.4527 | -61.5051 | -0.18768 | -0.1236 | -0.073242 | -0.10529 | -0.1236 | -0.19226 | -0.054931 | 0.11444 | 61.2396 | 61.9629 | 123.6969 | 123.6969 | -0.073242 | 123.7656 | 61.5005 | -0.19226 | 123.6969 | -0.073242 | 61.5005 | 123.6969 | 123.7656 | -124.0082 | -124.0128
470.7188 | 124.2325 | -61.3449 | 62.5351 | -0.14626 | 0.0042745 | 0.0055094 | -0.0017796 | 0.064093 | -0.0014013 | 0.069009 | -61.409 | 62.3795 | -61.5143 | -61.4594 | 62.3566 | 0.19226 | -0.10529 | 0.21973 | 62.4115 | -61.5417 | -0.16937 | -0.15564 | -0.064087 | -0.11444 | -0.17853 | -0.19684 | -0.1236 | 0.10529 | 61.2396 | 61.5646 | 123.7015 | 123.7244 | -0.064087 | 123.7564 | 61.5372 | -0.19684 | 123.7244 | -0.064087 | 61.5372 | 123.7015 | 123.7564 | -124.0494 | -124.0768
471.7188 | 124.2188 | -61.3541 | 62.5214 | -0.047073 | 0.0044881 | 0.0059366 | -0.0028476 | 0.062384 | -0.0014013 | 0.068795 | -61.4639 | 62.3932 | -61.5326 | -61.5005 | 62.2925 | 0.10986 | -0.091553 | 0.14191 | 62.3978 | -61.5234 | -0.17853 | -0.12817 | -0.10986 | -0.14648 | -0.22888 | -0.16937 | -0.1236 | 0.068665 | 61.2625 | 61.496 | 123.6465 | 123.7473 | -0.10986 | 123.7518 | 61.4639 | -0.16937 | 123.7473 | -0.10986 | 61.4639 | 123.6465 | 123.7518 | -124.054 | -124.0448
472.7188 | 124.1913 | -61.3403 | 62.4985 | -0.016556 | 0.0066245 | 0.010209 | 0.00057044 | 0.062171 | -0.00097413 | 0.068154 | -61.4731 | 62.3703 | -61.5189 | -61.528 | 62.2787 | 0.091553 | -0.091553 | 0.1236 | 62.4161 | -61.5372 | -0.17853 | -0.12817 | -0.13275 | -0.18768 | -0.21973 | -0.19684 | -0.082397 | 0.045777 | 61.2488 | 61.4639 | 123.6191 | 123.7106 | -0.13275 | 123.7564 | 61.4319 | -0.19684 | 123.7106 | -0.13275 | 61.4319 | 123.6191 | 123.7564 | -124.0173 | -124.0356
473.7188 | 124.1959 | -61.3541 | 62.5442 | -0.08522 | 0.0036337 | 0.0095682 | -0.002634 | 0.061957 | -0.00076053 | 0.0673 | -61.4319 | 62.3611 | -61.5143 | -61.5005 | 62.3108 | 0.14191 | -0.082397 | 0.16022 | 62.3978 | -61.528 | -0.16022 | -0.1831 | -0.07782 | -0.14648 | -0.23346 | -0.17395 | -0.14648 | 0.082397 | 61.2717 | 61.5143 | 123.6649 | 123.7152 | -0.07782 | 123.7518 | 61.496 | -0.17395 | 123.7152 | -0.07782 | 61.496 | 123.6649 | 123.7518 | -124.0585 | -124.0723
474.7188 | 124.0997 | -61.3861 | 62.5626 | -0.33699 | 0.0070517 | 0.011491 | 0.0046292 | 0.063025 | -0.00097413 | 0.068154 | -61.4777 | 62.4893 | -61.528 | -61.5738 | 62.2284 | 0.068665 | 0.10529 | 0.086975 | 62.4664 | -61.5784 | -0.14191 | -0.073242 | -0.091553 | -0.18768 | -0.33417 | -0.19226 | -0.09613 | 0.050354 | 61.4914 | 61.4731 | 123.6145 | 123.8754 | -0.091553 | 123.8525 | 61.4548 | -0.19226 | 123.8754 | -0.091553 | 61.4548 | 123.6145 | 123.8525 | -124.0906 | -124.1409
475.7188 | 124.2188 | -61.3541 | 62.4847 | -0.062332 | 0.0053427 | 0.010423 | -0.0030612 | 0.063452 | -0.00054693 | 0.068795 | -61.4456 | 62.3749 | -61.5372 | -61.4777 | 62.3199 | 0.13733 | -0.10071 | 0.1831 | 62.4115 | -61.5143 | -0.18311 | -0.10986 | -0.091553 | -0.1236 | -0.16479 | -0.16022 | -0.073242 | 0.091552 | 61.2534 | 61.5372 | 123.674 | 123.7289 | -0.091553 | 123.7656 | 61.4914 | -0.16022 | 123.7289 | -0.091553 | 61.4914 | 123.674 | 123.7656 | -124.0219 | -123.999
476.7188 | 124.205 | -61.3266 | 62.5259 | -0.131 | 0.0064107 | 0.006791 | -0.001566 | 0.065375 | -0.0014013 | 0.068368 | -61.4594 | 62.3886 | -61.5143 | -61.5005 | 62.3291 | 0.11902 | -0.09613 | 0.15106 | 62.4023 | -61.5234 | -0.18768 | -0.13733 | -0.13275 | -0.17395 | -0.19684 | -0.19684 | -0.1236 | 0.054931 | 61.2305 | 61.4777 | 123.6557 | 123.7152 | -0.13275 | 123.7289 | 61.4456 | -0.19684 | 123.7152 | -0.13275 | 61.4456 | 123.6557 | 123.7289 | -124.0402 | -124.0494
477.7188 | 124.1867 | -61.3495 | 62.5122 | -0.031814 | 0.0061971 | 0.0078592 | -0.002634 | 0.061957 | -0.0016149 | 0.069009 | -61.4685 | 62.352 | -61.5005 | -61.528 | 62.2925 | 0.11444 | -0.091553 | 0.12817 | 62.4023 | -61.5417 | -0.15106 | -0.16022 | -0.11902 | -0.17853 | -0.21973 | -0.19226 | -0.10986 | 0.032043 | 61.2579 | 61.4777 | 123.642 | 123.7015 | -0.11902 | 123.7518 | 61.4639 | -0.19226 | 123.7015 | -0.11902 | 61.4639 | 123.642 | 123.7518 | -124.0128 | -124.054
478.7188 | 124.1821 | -61.3541 | 62.5214 | 0.052109 | 0.0029929 | 0.0063638 | 0.00035684 | 0.062171 | -0.0022559 | 0.069222 | -61.4914 | 62.3703 | -61.5372 | -61.5555 | 62.2787 | 0.059509 | -0.091553 | 0.086975 | 62.3886 | -61.5555 | -0.18311 | -0.15106 | -0.13733 | -0.20142 | -0.24261 | -0.20142 | -0.13275 | 0.045776 | 61.2625 | 61.441 | 123.6328 | 123.7244 | -0.13733 | 123.7427 | 61.4136 | -0.20142 | 123.7244 | -0.13733 | 61.4136 | 123.6328 | 123.7427 | -124.0585 | -124.0768
479.7188 | 124.2599 | -61.3174 | 62.5351 | -0.077591 | 0.0059835 | 0.004014 | 0.00035684 | 0.06388 | -0.0014013 | 0.067941 | -61.4044 | 62.384 | -61.5326 | -61.4456 | 62.3703 | 0.19226 | -0.10986 | 0.23804 | 62.384 | -61.5097 | -0.21515 | -0.15106 | -0.086975 | -0.12817 | -0.16479 | -0.19226 | -0.15106 | 0.12817 | 61.2076 | 61.5555 | 123.6877 | 123.7015 | -0.086975 | 123.7015 | 61.5097 | -0.19226 | 123.7015 | -0.086975 | 61.5097 | 123.6877 | 123.7015 | -124.0677 | -124.0448
480.7188 | 124.1638 | -61.3541 | 62.5031 | 0.090256 | 0.0070517 | 0.0059366 | -0.0022068 | 0.063666 | -0.00033333 | 0.068582 | -61.4594 | 62.3886 | -61.5463 | -61.5326 | 62.2009 | 0.17395 | -0.068665 | -0.036621 | 62.3978 | -61.5234 | -0.19226 | -0.11444 | -0.10529 | -0.17853 | -0.30212 | -0.16937 | -0.10529 | 0.086975 | 61.2854 | 61.3174 | 123.555 | 123.7427 | -0.10529 | 123.7518 | 61.528 | -0.16937 | 123.7427 | -0.10529 | 61.528 | 123.555 | 123.7518 | -124.0494 | -124.0265
481.7188 | 124.2279 | -61.3403 | 62.5122 | -0.077591 | 0.0036337 | 0.0089274 | -0.0037022 | 0.063025 | -0.00033333 | 0.069436 | -61.4365 | 62.3703 | -61.5417 | -61.4822 | 62.3199 | 0.11902 | -0.10529 | 0.16479 | 62.4161 | -61.5463 | -0.20142 | -0.14191 | -0.09613 | -0.14191 | -0.19226 | -0.20599 | -0.09613 | 0.10529 | 61.235 | 61.5051 | 123.6603 | 123.7106 | -0.09613 | 123.7564 | 61.4594 | -0.20599 | 123.7106 | -0.09613 | 61.4594 | 123.6603 | 123.7564 | -124.054 | -124.0585
482.7188 | 124.1455 | -61.3907 | 62.5122 | 0.013962 | 0.0023519 | 0.006791 | 0.00035684 | 0.063025 | -0.0020421 | 0.069863 | -61.4731 | 62.3749 | -61.5189 | -61.5555 | 62.2925 | 0.073242 | -0.091553 | 0.07782 | 62.384 | -61.5417 | -0.12817 | -0.13733 | -0.082397 | -0.16479 | -0.21973 | -0.15106 | -0.12817 | 0.045777 | 61.2991 | 61.4685 | 123.6832 | 123.7656 | -0.082397 | 123.7747 | 61.4639 | -0.15106 | 123.7656 | -0.082397 | 61.4639 | 123.6832 | 123.7747 | -124.0311 | -124.054
483.7188 | 124.2233 | -61.3632 | 62.5351 | 0.029221 | 0.0059835 | 0.010636 | -0.0017796 | 0.062598 | -0.00011953 | 0.069436 | -61.4731 | 62.3474 | -61.5509 | -61.5372 | 62.2696 | 0.059509 | -0.10071 | 0.073242 | 62.4023 | -61.5417 | -0.18768 | -0.18768 | -0.10986 | -0.17395 | -0.2655 | -0.17853 | -0.13275 | 0.07782 | 61.2625 | 61.4365 | 123.6328 | 123.7106 | -0.10986 | 123.7656 | 61.4227 | -0.17853 | 123.7106 | -0.10986 | 61.4227 | 123.6328 | 123.7656 | -124.086 | -124.0768
484.7188 | 124.2554 | -61.3403 | 62.5122 | -0.11574 | 0.0057699 | 0.010423 | -0.0013522 | 0.064307 | -0.0024695 | 0.06965 | -61.409 | 62.3703 | -61.5051 | -61.441 | 62.3703 | 0.20599 | -0.10529 | 0.2243 | 62.3978 | -61.5463 | -0.1648 | -0.14191 | -0.068665 | -0.10071 | -0.14191 | -0.20599 | -0.11444 | 0.09613 | 61.235 | 61.5646 | 123.7106 | 123.7106 | -0.068665 | 123.7381 | 61.5463 | -0.20599 | 123.7106 | -0.068665 | 61.5463 | 123.7106 | 123.7381 | -124.0173 | -124.0585
485.7188 | 124.2188 | -61.3586 | 62.5031 | 0.18944 | 0.0059835 | 0.009141 | 0.00057044 | 0.064948 | -0.0011877 | 0.067941 | -61.4227 | 62.384 | -61.5097 | -61.4914 | 62.2925 | 0.082397 | -0.19226 | 0.082397 | 62.3703 | -61.5372 | -0.15106 | -0.11902 | -0.064086 | -0.13275 | -0.21057 | -0.17853 | -0.13275 | 0.086976 | 61.1664 | 61.441 | 123.6511 | 123.7427 | -0.064086 | 123.7289 | 61.441 | -0.17853 | 123.7427 | -0.064086 | 61.441 | 123.6511 | 123.7289 | -124.0128 | -124.0402
486.7188 | 124.2233 | -61.3541 | 62.4939 | 0.12077 | 0.0089743 | 0.0132 | 0.0033474 | 0.062598 | -0.00033333 | 0.068368 | -61.409 | 62.3703 | -61.5189 | -61.5005 | 62.3154 | 0.091553 | -0.21057 | 0.082397 | 62.3474 | -61.5692 | -0.16479 | -0.1236 | -0.054932 | -0.14648 | -0.17853 | -0.21515 | -0.14648 | 0.10986 | 61.1435 | 61.4365 | 123.6694 | 123.7244 | -0.054932 | 123.7015 | 61.4456 | -0.21515 | 123.7244 | -0.054932 | 61.4456 | 123.6694 | 123.7015 | -124.0128 | -124.0631
487.7188 | 124.2188 | -61.3403 | 62.471 | 0.14366 | 0.0055563 | 0.01085 | 0.00035684 | 0.06388 | -0.00054693 | 0.070077 | -61.4319 | 62.384 | -61.5372 | -61.5143 | 62.3108 | 0.07782 | -0.17853 | 0.086975 | 62.3703 | -61.528 | -0.19684 | -0.086975 | -0.091553 | -0.17395 | -0.16022 | -0.18768 | -0.10071 | 0.10529 | 61.1618 | 61.4273 | 123.6511 | 123.7244 | -0.091553 | 123.7106 | 61.4182 | -0.18768 | 123.7244 | -0.091553 | 61.4182 | 123.6511 | 123.7106 | -124.0082 | -123.999
488.7188 | 124.173 | -61.3586 | 62.5076 | 0.14366 | 0.0076925 | 0.011491 | 0.0016384 | 0.064948 | -0.0028967 | 0.069222 | -61.4594 | 62.3566 | -61.5189 | -61.5372 | 62.2787 | 0.054932 | -0.15106 | 0.064087 | 62.3703 | -61.5601 | -0.16022 | -0.15106 | -0.10071 | -0.17853 | -0.22888 | -0.20142 | -0.13733 | 0.059509 | 61.2076 | 61.4227 | 123.6374 | 123.7152 | -0.10071 | 123.7289 | 61.4136 | -0.20142 | 123.7152 | -0.10071 | 61.4136 | 123.6374 | 123.7289 | -124.0265 | -124.0677
489.7188 | 124.2096 | -61.3495 | 62.5168 | -0.031814 | 0.0051291 | 0.0072184 | -0.00092496 | 0.062598 | 0.00030767 | 0.068368 | -61.441 | 62.3886 | -61.5005 | -61.4914 | 62.3474 | 0.13275 | -0.09613 | 0.15564 | 62.3795 | -61.5326 | -0.15106 | -0.12817 | -0.091553 | -0.14191 | -0.16937 | -0.18311 | -0.13733 | 0.059509 | 61.2534 | 61.5051 | 123.6969 | 123.7381 | -0.091553 | 123.7289 | 61.4822 | -0.18311 | 123.7381 | -0.091553 | 61.4822 | 123.6969 | 123.7289 | -124.0173 | -124.0494
490.7188 | 124.2371 | -61.3449 | 62.4756 | 0.16655 | 0.0051291 | 0.012559 | 0.0016384 | 0.064521 | -0.00033333 | 0.069436 | -61.4227 | 62.4161 | -61.5189 | -61.5097 | 62.3016 | 0.07782 | -0.19226 | 0.091553 | 62.3566 | -61.5646 | -0.17395 | -0.059509 | -0.077819 | -0.16479 | -0.17395 | -0.21973 | -0.11902 | 0.096131 | 61.1526 | 61.4365 | 123.6465 | 123.761 | -0.077819 | 123.7015 | 61.4227 | -0.21973 | 123.761 | -0.077819 | 61.4227 | 123.6465 | 123.7015 | -123.9944 | -124.0402
491.7188 | 124.205 | -61.3403 | 62.4939 | 0.31151 | 0.0061971 | 0.011277 | 0.0022794 | 0.064093 | -0.0011877 | 0.067513 | -61.4044 | 62.3886 | -61.5143 | -61.4777 | 62.2925 | 0.073242 | -0.21057 | 0.091553 | 62.3428 | -61.5509 | -0.17395 | -0.10529 | -0.064087 | -0.13733 | -0.20142 | -0.21057 | -0.15106 | 0.10986 | 61.1298 | 61.4319 | 123.6328 | 123.7289 | -0.064087 | 123.6832 | 61.4136 | -0.21057 | 123.7289 | -0.064087 | 61.4136 | 123.6328 | 123.6832 | -124.0082 | -124.0448
492.7188 | 124.2233 | -61.3678 | 62.4939 | 0.18181 | 0.0076925 | 0.012559 | 0.0033474 | 0.066016 | 0.00030767 | 0.06965 | -61.4365 | 62.4023 | -61.5601 | -61.496 | 62.2604 | 0.054932 | -0.1831 | 0.068665 | 62.3611 | -61.5967 | -0.19226 | -0.091552 | -0.068664 | -0.12817 | -0.23346 | -0.22888 | -0.13275 | 0.1236 | 61.1847 | 61.4365 | 123.6282 | 123.7701 | -0.068664 | 123.7289 | 61.4227 | -0.22888 | 123.7701 | -0.068664 | 61.4227 | 123.6282 | 123.7289 | -124.054 | -124.0906
493.7188 | 124.1821 | -61.3724 | 62.4893 | 0.18181 | 0.010042 | 0.011064 | 0.00527 | 0.066016 | -0.0024695 | 0.070291 | -61.4822 | 62.4435 | -61.5509 | -61.5555 | 62.2421 | 0.027466 | -0.13733 | 0.032043 | 62.4023 | -61.5875 | -0.17853 | -0.045777 | -0.10986 | -0.18311 | -0.24719 | -0.21515 | -0.086975 | 0.068664 | 61.235 | 61.4044 | 123.6145 | 123.8159 | -0.10986 | 123.7747 | 61.3998 | -0.21515 | 123.8159 | -0.10986 | 61.3998 | 123.6145 | 123.7747 | -124.0402 | -124.0768
494.7188 | 124.0997 | -61.3586 | 62.4939 | 0.059738 | 0.0053427 | 0.0095682 | -0.0028476 | 0.065589 | -0.0026831 | 0.070291 | -61.4822 | 62.3886 | -61.5143 | -61.5372 | 62.2787 | 0.068665 | -0.082397 | 0.20142 | 62.4069 | -61.528 | -0.15564 | -0.10529 | -0.1236 | -0.17853 | -0.21515 | -0.16937 | -0.086975 | 0.032043 | 61.2762 | 61.5601 | 123.6374 | 123.7473 | -0.1236 | 123.7656 | 61.4273 | -0.16937 | 123.7473 | -0.1236 | 61.4273 | 123.6374 | 123.7656 | -124.0082 | -124.0219
495.7188 | 124.2188 | -61.3632 | 62.4802 | 0.13603 | 0.0057699 | 0.0089274 | 0.0031338 | 0.067511 | -0.0048193 | 0.071145 | -61.2762 | 62.4115 | -61.5372 | -61.4914 | 62.3062 | 0.059509 | -0.21515 | 0.10071 | 62.3657 | -61.5555 | -0.17395 | -0.068665 | 0.086975 | -0.12817 | -0.17395 | -0.19226 | -0.11444 | 0.26093 | 61.1481 | 61.4639 | 123.6694 | 123.7747 | 0.086975 | 123.7289 | 61.4227 | -0.19226 | 123.7747 | 0.086975 | 61.4227 | 123.6694 | 123.7289 | -124.0173 | -124.0356
496.7188 | 124.2142 | -61.3449 | 62.4939 | 0.2047 | 0.0057699 | 0.0093546 | 0.0012112 | 0.066443 | -0.0031103 | 0.068368 | -61.4182 | 62.4023 | -61.5234 | -61.4639 | 62.233 | -0.1236 | -0.027466 | 0.22888 | 62.3703 | -61.5463 | -0.17853 | -0.091552 | -0.073242 | -0.11902 | -0.26093 | -0.20142 | -0.1236 | 0.10529 | 61.3174 | 61.5738 | 123.5779 | 123.7473 | -0.073242 | 123.7152 | 61.2213 | -0.20142 | 123.7473 | -0.073242 | 61.2213 | 123.5779 | 123.7152 | -124.0173 | -124.0402
497.7188 | 124.2004 | -61.3678 | 62.4985 | 0.34966 | 0.0064107 | 0.012986 | 0.003561 | 0.067298 | -0.0020421 | 0.071786 | -61.4273 | 62.4069 | -61.5097 | -61.5051 | 62.3062 | 0.09613 | -0.19226 | 0.086975 | 62.3749 | -61.5555 | -0.14191 | -0.091553 | -0.059509 | -0.13733 | -0.19226 | -0.18768 | -0.1236 | 0.082398 | 61.1755 | 61.4548 | 123.674 | 123.7747 | -0.059509 | 123.7427 | 61.4639 | -0.18768 | 123.7747 | -0.059509 | 61.4639 | 123.674 | 123.7427 | -124.0082 | -124.054
498.7188 | 124.1867 | -61.3541 | 62.5122 | 0.21996 | 0.0068381 | 0.0061502 | 0.0037746 | 0.067298 | -0.0020421 | 0.069436 | -61.4548 | 62.4481 | -61.5509 | -61.5097 | 62.2559 | 0.050354 | -0.17395 | 0.064087 | 62.384 | -61.5875 | -0.19684 | -0.064087 | -0.10071 | -0.15564 | -0.25635 | -0.23346 | -0.12817 | 0.09613 | 61.1801 | 61.4182 | 123.6099 | 123.8022 | -0.10071 | 123.7381 | 61.4044 | -0.23346 | 123.8022 | -0.10071 | 61.4044 | 123.6099 | 123.7381 | -124.0631 | -124.0997
499.7188 | 124.2004 | -61.3449 | 62.4939 | 0.15892 | 0.0059835 | 0.0099954 | -0.0019932 | 0.064948 | -0.0014013 | 0.069009 | -61.4365 | 62.3795 | -61.5372 | -61.5005 | 62.3108 | 0.086975 | -0.19226 | 0.09613 | 62.3795 | -61.5784 | -0.19226 | -0.11444 | -0.091552 | -0.15564 | -0.1831 | -0.23346 | -0.11444 | 0.10071 | 61.1526 | 61.441 | 123.6557 | 123.7244 | -0.091552 | 123.7244 | 61.4319 | -0.23346 | 123.7244 | -0.091552 | 61.4319 | 123.6557 | 123.7244 | -124.0311 | -124.0723
500.7188 | 124.0997 | -61.3907 | 62.5351 | 0.15892 | 0.0081197 | 0.0078592 | 0.0033474 | 0.066016 | -0.0016149 | 0.068154 | -61.528 | 62.4893 | -61.5463 | -61.6333 | 62.1872 | -0.022888 | -0.018311 | -0.045776 | 62.4252 | -61.6104 | -0.15564 | -0.045776 | -0.13733 | -0.24262 | -0.3479 | -0.21973 | -0.10986 | 0.018311 | 61.3724 | 61.3449 | 123.5779 | 123.88 | -0.13733 | 123.8159 | 61.3678 | -0.21973 | 123.88 | -0.13733 | 61.3678 | 123.5779 | 123.8159 | -124.0814 | -124.1455
501.7188 | 124.1226 | -61.4044 | 62.5031 | 0.1284 | 0.0072653 | 0.01085 | 0.0022794 | 0.068579 | -0.0018285 | 0.070077 | -61.496 | 62.4756 | -61.5417 | -61.5921 | 62.2055 | -0.013733 | -0.059509 | -0.036621 | 62.4298 | -61.6241 | -0.13733 | -0.027466 | -0.091553 | -0.18768 | -0.29755 | -0.21973 | -0.073242 | 0.045776 | 61.3449 | 61.3678 | 123.6099 | 123.88 | -0.091553 | 123.8342 | 61.3907 | -0.21973 | 123.88 | -0.091553 | 61.3907 | 123.6099 | 123.8342 | -124.0448 | -124.1272
502.7188 | 124.1776 | -61.3815 | 62.4802 | 0.17418 | 0.0076925 | 0.012559 | 0.003561 | 0.067939 | -0.0016149 | 0.068795 | -61.4822 | 62.4619 | -61.528 | -61.5555 | 62.2467 | 0.050354 | -0.13733 | 0.036621 | 62.3886 | -61.5921 | -0.14648 | -0.018311 | -0.10071 | -0.17395 | -0.23346 | -0.21057 | -0.091553 | 0.045776 | 61.2442 | 61.4182 | 123.6282 | 123.8434 | -0.10071 | 123.7701 | 61.4319 | -0.21057 | 123.8434 | -0.10071 | 61.4319 | 123.6282 | 123.7701 | -124.0082 | -124.0723
503.7188 | 124.1501 | -61.3815 | 62.4893 | 0.15129 | 0.0076925 | 0.0082864 | 0.0022794 | 0.067511 | -0.0033239 | 0.068154 | -61.4777 | 62.471 | -61.5738 | -61.5967 | 62.2147 | 0.009155 | -0.091553 | -0.009155 | 62.4115 | -61.5967 | -0.19226 | -0.018311 | -0.09613 | -0.21515 | -0.27466 | -0.21515 | -0.07782 | 0.096131 | 61.29 | 61.3724 | 123.5962 | 123.8525 | -0.09613 | 123.793 | 61.3907 | -0.21515 | 123.8525 | -0.09613 | 61.3907 | 123.5962 | 123.793 | -124.0631 | -124.086
504.7188 | 124.1867 | -61.3815 | 62.4985 | 0.21996 | 0.0049155 | 0.0085 | -0.0051974 | 0.065375 | -0.0026831 | 0.07264 | -61.4502 | 62.3978 | -61.528 | -61.5509 | 62.2742 | 0.082397 | -0.050354 | 0.10529 | 62.4207 | -61.5326 | -0.14648 | -0.10071 | -0.068664 | -0.16937 | -0.2243 | -0.15106 | -0.07782 | 0.07782 | 61.3312 | 61.4868 | 123.6557 | 123.7793 | -0.068664 | 123.8022 | 61.4639 | -0.15106 | 123.7793 | -0.068664 | 61.4639 | 123.6557 | 123.8022 | -124.0265 | -124.0311
505.7188 | 124.1226 | -61.4044 | 62.5076 | 0.40306 | 0.0076925 | 0.012345 | 0.0033474 | 0.068366 | -0.0026831 | 0.069222 | -61.4868 | 62.4802 | -61.5509 | -61.6058 | 62.1918 | 0.009155 | -0.022888 | -0.027466 | 62.439 | -61.6241 | -0.14648 | -0.027465 | -0.082397 | -0.20142 | -0.31586 | -0.21973 | -0.068664 | 0.064087 | 61.3815 | 61.377 | 123.5962 | 123.8846 | -0.082397 | 123.8434 | 61.4136 | -0.21973 | 123.8846 | -0.082397 | 61.4136 | 123.5962 | 123.8434 | -124.0585 | -124.1318
506.7188 | 124.0723 | -61.4044 | 62.5214 | 0.059738 | 0.0091879 | 0.012132 | 0.004202 | 0.06623 | -0.00097413 | 0.06965 | -61.4731 | 62.4802 | -61.5463 | -61.6058 | 62.1872 | 0 | 0.022888 | -0.027466 | 62.4573 | -61.6196 | -0.14191 | -0.041198 | -0.068664 | -0.20142 | -0.33417 | -0.21515 | -0.064087 | 0.073243 | 61.4273 | 61.377 | 123.5916 | 123.8846 | -0.068664 | 123.8617 | 61.4044 | -0.21515 | 123.8846 | -0.068664 | 61.4044 | 123.5916 | 123.8617 | -124.0677 | -124.1409
507.7188 | 124.0906 | -61.4136 | 62.5442 | 0.029221 | 0.0091879 | 0.011277 | 0.0029202 | 0.067939 | -0.00097413 | 0.067941 | -61.4456 | 62.4939 | -61.5326 | -61.5967 | 62.2055 | 0.022888 | 0.018311 | 0.009155 | 62.4664 | -61.6058 | -0.11902 | -0.050354 | -0.032044 | -0.18311 | -0.33874 | -0.19226 | -0.077819 | 0.086975 | 61.4319 | 61.4227 | 123.6191 | 123.9075 | -0.032044 | 123.88 | 61.4365 | -0.19226 | 123.9075 | -0.032044 | 61.4365 | 123.6191 | 123.88 | -124.0768 | -124.1501
508.7188 | 124.0723 | -61.3998 | 62.5168 | 0.10551 | 0.0087607 | 0.0093546 | 0.0020656 | 0.069007 | -0.0014013 | 0.06965 | -61.5143 | 62.5031 | -61.5692 | -61.6562 | 62.1689 | -0.018311 | 0.018311 | -0.050354 | 62.4252 | -61.6287 | -0.16937 | -0.013733 | -0.11444 | -0.25635 | -0.3479 | -0.22888 | -0.091553 | 0.054932 | 61.4182 | 61.3495 | 123.5687 | 123.9029 | -0.11444 | 123.8251 | 61.3815 | -0.22888 | 123.9029 | -0.11444 | 61.3815 | 123.5687 | 123.8251 | -124.086 | -124.1455
509.7188 | 124.2279 | -61.3724 | 62.471 | 0.24284 | 0.0068381 | 0.011064 | -0.0024204 | 0.069648 | 0.0013757 | 0.069222 | -61.441 | 62.4344 | -61.5601 | -61.5372 | 62.2971 | 0.09613 | -0.19226 | 0.07782 | 62.4115 | -61.5555 | -0.18768 | -0.036621 | -0.068665 | -0.1648 | -0.17395 | -0.18311 | -0.059509 | 0.11902 | 61.1801 | 61.4502 | 123.6694 | 123.8068 | -0.068665 | 123.7839 | 61.4685 | -0.18311 | 123.8068 | -0.068665 | 61.4685 | 123.6694 | 123.7839 | -124.0311 | -124.0265
510.7188 | 124.0356 | -61.3815 | 62.5488 | 0.11314 | 0.0085471 | 0.0059366 | 0.0029202 | 0.069861 | 9.4068e-05 | 0.070931 | -61.528 | 62.4985 | -61.5601 | -61.6241 | 62.3108 | -0.054932 | -0.37537 | 0.21973 | 62.4023 | -61.6196 | -0.17853 | -0.050354 | -0.14648 | -0.24262 | -0.23804 | -0.23804 | -0.14648 | 0.032044 | 61.0062 | 61.6013 | 123.6923 | 123.88 | -0.14648 | 123.7839 | 61.3266 | -0.23804 | 123.88 | -0.14648 | 61.3266 | 123.6923 | 123.7839 | -124.1089 | -124.1684
511.7188 | 124.0814 | -61.4227 | 62.5259 | 0.067368 | 0.0074789 | 0.0080728 | 0.00078404 | 0.068793 | -0.0018285 | 0.067727 | -61.496 | 62.5031 | -61.5738 | -61.6425 | 62.1735 | -0.027466 | 0.018311 | -0.041199 | 62.4481 | -61.6379 | -0.15106 | -0.022888 | -0.073243 | -0.21973 | -0.35248 | -0.21515 | -0.07782 | 0.07782 | 61.441 | 61.3815 | 123.5962 | 123.9258 | -0.073243 | 123.8708 | 61.3953 | -0.21515 | 123.9258 | -0.073243 | 61.3953 | 123.5962 | 123.8708 | -124.0997 | -124.1638
512.7188 | 124.0814 | -61.4044 | 62.5031 | 0.03685 | 0.0083333 | 0.012773 | 0.002493 | 0.071357 | -0.0026831 | 0.070504 | -61.4639 | 62.5351 | -61.5555 | -61.615 | 62.1964 | -0.013733 | 0.036621 | -0.009155 | 62.4619 | -61.6241 | -0.15106 | 0.032043 | -0.059509 | -0.21057 | -0.3067 | -0.21973 | -0.041199 | 0.091553 | 61.441 | 61.3953 | 123.6008 | 123.9395 | -0.059509 | 123.8663 | 61.3907 | -0.21973 | 123.9395 | -0.059509 | 61.3907 | 123.6008 | 123.8663 | -124.0585 | -124.1272
513.7188 | 124.1089 | -61.3678 | 62.5076 | -0.08522 | 0.0064107 | 0.01085 | 0.00099764 | 0.068366 | -0.0011877 | 0.06965 | -61.4319 | 62.4802 | -61.528 | -61.5555 | 62.265 | 0.091553 | 0.004578 | 0.082397 | 62.4619 | -61.5829 | -0.16022 | -0.027465 | -0.064087 | -0.18768 | -0.24261 | -0.21515 | -0.045776 | 0.09613 | 61.3724 | 61.4502 | 123.6328 | 123.848 | -0.064087 | 123.8297 | 61.4594 | -0.21515 | 123.848 | -0.064087 | 61.4594 | 123.6328 | 123.8297 | -124.0356 | -124.0906
514.7188 | 124.086 | -61.3953 | 62.5351 | 0.03685 | 0.0079061 | 0.0095682 | 0.001852 | 0.070502 | -0.0022559 | 0.070504 | -61.496 | 62.4939 | -61.5738 | -61.647 | 62.178 | -0.022888 | 0.036621 | -0.041199 | 62.4756 | -61.615 | -0.17853 | -0.041199 | -0.10071 | -0.25177 | -0.35705 | -0.21973 | -0.059509 | 0.07782 | 61.4319 | 61.3541 | 123.5733 | 123.8892 | -0.10071 | 123.8708 | 61.3724 | -0.21973 | 123.8892 | -0.10071 | 61.3724 | 123.5733 | 123.8708 | -124.1089 | -124.1501
515.7188 | 124.0494 | -61.4136 | 62.5442 | 0.082626 | 0.0079061 | 0.014909 | 0.0027066 | 0.068366 | -0.0016149 | 0.069009 | -61.4822 | 62.4985 | -61.5509 | -61.6058 | 62.1918 | -0.009155 | 0.036621 | -0.018311 | 62.471 | -61.615 | -0.13733 | -0.045776 | -0.068665 | -0.19226 | -0.35248 | -0.20142 | -0.073242 | 0.068664 | 61.4502 | 61.3953 | 123.6053 | 123.912 | -0.068665 | 123.8846 | 61.4044 | -0.20142 | 123.912 | -0.068665 | 61.4044 | 123.6053 | 123.8846 | -124.0952 | -124.1592
516.7188 | 124.0997 | -61.3953 | 62.5305 | 0.013962 | 0.0094015 | 0.011704 | 0.00035684 | 0.07157 | -0.0016149 | 0.067941 | -61.4777 | 62.4985 | -61.5601 | -61.6058 | 62.2238 | 0.009155 | 0.027466 | 0.018311 | 62.4802 | -61.6196 | -0.1648 | -0.032044 | -0.082397 | -0.21057 | -0.3067 | -0.2243 | -0.050354 | 0.082398 | 61.4227 | 61.4136 | 123.6191 | 123.8937 | -0.082397 | 123.8754 | 61.4044 | -0.2243 | 123.8937 | -0.082397 | 61.4044 | 123.6191 | 123.8754 | -124.0906 | -124.1501
517.7188 | 124.0997 | -61.377 | 62.5442 | 0.0063326 | 0.0085471 | 0.014054 | 0.0016384 | 0.068579 | -0.0037511 | 0.070504 | -61.441 | 62.5122 | -61.5417 | -61.5875 | 62.2467 | 0.050354 | 0.004578 | 0.045776 | 62.4802 | -61.5784 | -0.16479 | -0.032043 | -0.064087 | -0.21057 | -0.29755 | -0.20142 | -0.064086 | 0.10071 | 61.3815 | 61.4227 | 123.6237 | 123.8892 | -0.064087 | 123.8571 | 61.4273 | -0.20142 | 123.8892 | -0.064087 | 61.4273 | 123.6237 | 123.8571 | -124.086 | -124.1226
518.7188 | 124.1318 | -61.3861 | 62.5351 | -0.10048 | 0.010042 | 0.01085 | 0.0016384 | 0.069861 | -0.0020421 | 0.069222 | -61.4365 | 62.5031 | -61.5509 | -61.5601 | 62.2421 | 0.073242 | 0.013733 | 0.068665 | 62.4664 | -61.6013 | -0.16479 | -0.032043 | -0.050354 | -0.17395 | -0.29297 | -0.21515 | -0.068664 | 0.11444 | 61.3998 | 61.4548 | 123.6282 | 123.8892 | -0.050354 | 123.8525 | 61.4594 | -0.21515 | 123.8892 | -0.050354 | 61.4594 | 123.6282 | 123.8525 | -124.086 | -124.1364
519.7188 | 124.1867 | -61.3586 | 62.5076 | 0.19707 | 0.0089743 | 0.01085 | -0.0013522 | 0.071143 | -0.0026831 | 0.070077 | -61.4639 | 62.439 | -61.5646 | -61.5784 | 62.2513 | 0.036621 | -0.16022 | 0.041199 | 62.4481 | -61.5875 | -0.20599 | -0.068664 | -0.10529 | -0.21973 | -0.25635 | -0.22888 | -0.059509 | 0.10071 | 61.1984 | 61.3998 | 123.6099 | 123.7976 | -0.10529 | 123.8068 | 61.3953 | -0.22888 | 123.7976 | -0.10529 | 61.3953 | 123.6099 | 123.8068 | -124.0723 | -124.0952
520.7188 | 124.1272 | -61.377 | 62.5351 | -0.14626 | 0.0094015 | 0.013841 | 0.00099764 | 0.06687 | -0.0022559 | 0.070291 | -61.4273 | 62.5168 | -61.5234 | -61.5143 | 62.2742 | 0.13275 | 0.064087 | 0.1236 | 62.5031 | -61.6058 | -0.14648 | -0.01831 | -0.050354 | -0.13733 | -0.26093 | -0.22888 | -0.032043 | 0.09613 | 61.441 | 61.5005 | 123.6511 | 123.8937 | -0.050354 | 123.88 | 61.5097 | -0.22888 | 123.8937 | -0.050354 | 61.5097 | 123.6511 | 123.88 | -124.0585 | -124.1409
521.7188 | 124.205 | -61.3541 | 62.4802 | 0.47173 | 0.0079061 | 0.0078592 | -0.0034886 | 0.067511 | -0.00033333 | 0.070718 | -61.3907 | 62.3978 | -61.528 | -61.5189 | 62.3062 | 0.086975 | -0.20142 | 0.091553 | 62.4435 | -61.5555 | -0.17395 | -0.082398 | -0.036621 | -0.16479 | -0.17395 | -0.20142 | -0.036622 | 0.13733 | 61.1526 | 61.4456 | 123.6603 | 123.7518 | -0.036621 | 123.7976 | 61.441 | -0.20142 | 123.7518 | -0.036621 | 61.441 | 123.6603 | 123.7976 | -124.0082 | -124.0356
522.7188 | 124.1318 | -61.3632 | 62.5488 | -0.069961 | 0.0066245 | 0.0099954 | -7.0562e-05 | 0.065802 | -0.0022559 | 0.069009 | -61.409 | 62.5031 | -61.5326 | -61.5463 | 62.2742 | 0.11444 | 0.018311 | 0.12817 | 62.4756 | -61.5875 | -0.16937 | -0.045776 | -0.045777 | -0.18311 | -0.27466 | -0.2243 | -0.073242 | 0.1236 | 61.3815 | 61.4914 | 123.6374 | 123.8663 | -0.045777 | 123.8388 | 61.4777 | -0.2243 | 123.8663 | -0.045777 | 61.4777 | 123.6374 | 123.8388 | -124.0814 | -124.1364
523.7188 | 124.1364 | -61.3724 | 62.5351 | 0.34966 | 0.0094015 | 0.0085 | 0.0022794 | 0.067084 | -0.0035375 | 0.070077 | -61.3678 | 62.5076 | -61.5051 | -61.5417 | 62.2833 | 0.11444 | -0.004578 | 0.11444 | 62.4756 | -61.5646 | -0.13275 | -0.027466 | 0.004577 | -0.16937 | -0.25177 | -0.19226 | -0.059509 | 0.13733 | 61.3678 | 61.4868 | 123.6557 | 123.88 | 0.004577 | 123.848 | 61.4868 | -0.19226 | 123.88 | 0.004577 | 61.4868 | 123.6557 | 123.848 | -124.0402 | -124.0997
524.7188 | 124.086 | -61.3998 | 62.5305 | 1.6009 | 0.0055563 | 0.0050822 | -7.0562e-05 | 0.069861 | -0.00076053 | 0.069009 | -61.2076 | 62.4802 | -61.5738 | -61.5921 | 62.2147 | -0.027466 | -0.018311 | -0.018311 | 62.4802 | -61.6196 | -0.17395 | -0.050354 | 0.19226 | -0.19226 | -0.31586 | -0.21973 | -0.050354 | 0.36621 | 61.3815 | 61.3815 | 123.6145 | 123.88 | 0.19226 | 123.88 | 61.3724 | -0.21973 | 123.88 | 0.19226 | 61.3724 | 123.6145 | 123.88 | -124.1043 | -124.1501
525.7188 | 124.0311 | -61.3724 | 62.5076 | -0.131 | 0.0094015 | 0.010423 | 0.00078404 | 0.067725 | -0.0022559 | 0.068154 | -61.4227 | 62.4939 | -61.528 | -61.528 | 62.2559 | 0.10529 | 0.022888 | 0.11902 | 62.471 | -61.6241 | -0.15564 | -0.013733 | -0.050354 | -0.15564 | -0.25177 | -0.25177 | -0.036621 | 0.10529 | 61.3953 | 61.4914 | 123.6282 | 123.8663 | -0.050354 | 123.8434 | 61.4777 | -0.25177 | 123.8663 | -0.050354 | 61.4777 | 123.6282 | 123.8434 | -124.0356 | -124.1318
526.7188 | 124.173 | -61.3861 | 62.4939 | 0.18181 | 0.0074789 | 0.014482 | 0.00057044 | 0.069434 | 9.4068e-05 | 0.068368 | -61.4914 | 62.4619 | -61.5555 | -61.5646 | 62.233 | 0.036621 | -0.14648 | 0.036621 | 62.4527 | -61.6196 | -0.16937 | -0.032043 | -0.10529 | -0.17853 | -0.26093 | -0.23346 | -0.041198 | 0.064087 | 61.2396 | 61.4227 | 123.6191 | 123.848 | -0.10529 | 123.8388 | 61.4227 | -0.23346 | 123.848 | -0.10529 | 61.4227 | 123.6191 | 123.8388 | -124.0494 | -124.1135
527.7188 | 124.1043 | -61.3632 | 62.5397 | -0.19966 | 0.0083333 | 0.007432 | -0.00028416 | 0.067939 | -0.0022559 | 0.069436 | -61.4685 | 62.5122 | -61.5143 | -61.5829 | 62.2238 | 0.068665 | 0.10986 | 0.09613 | 62.5031 | -61.5921 | -0.15106 | -0.027466 | -0.10529 | -0.21973 | -0.31586 | -0.22888 | -0.036621 | 0.045776 | 61.4731 | 61.4594 | 123.587 | 123.8754 | -0.10529 | 123.8663 | 61.4319 | -0.22888 | 123.8754 | -0.10529 | 61.4319 | 123.587 | 123.8663 | -124.054 | -124.1318
528.7188 | 124.1364 | -61.3678 | 62.5397 | -0.19966 | 0.0083333 | 0.012559 | 0.0027066 | 0.06922 | -0.0022559 | 0.067727 | -61.4365 | 62.4985 | -61.5051 | -61.5372 | 62.2513 | 0.11444 | 0.064087 | 0.12817 | 62.5031 | -61.5738 | -0.13733 | -0.041199 | -0.068664 | -0.16937 | -0.28839 | -0.20599 | -0.036621 | 0.068665 | 61.4319 | 61.496 | 123.6191 | 123.8663 | -0.068664 | 123.8708 | 61.4822 | -0.20599 | 123.8663 | -0.068664 | 61.4822 | 123.6191 | 123.8708 | -124.0448 | -124.1135
529.7188 | 124.0631 | -61.3861 | 62.5214 | 0.03685 | 0.0076925 | 0.014909 | 0.002493 | 0.070716 | -0.0014013 | 0.068154 | -61.4731 | 62.5076 | -61.5417 | -61.5967 | 62.2009 | 0.009155 | 0.018311 | 0.027466 | 62.4802 | -61.6241 | -0.15564 | -0.013733 | -0.086975 | -0.21057 | -0.32043 | -0.23804 | -0.041198 | 0.068665 | 61.4044 | 61.4136 | 123.587 | 123.8937 | -0.086975 | 123.8663 | 61.3953 | -0.23804 | 123.8937 | -0.086975 | 61.3953 | 123.587 | 123.8663 | -124.0631 | -124.1455
530.7188 | 124.1364 | -61.377 | 62.5397 | -0.21492 | 0.0079061 | 0.006791 | -7.0562e-05 | 0.068152 | -0.0014013 | 0.069222 | -61.4182 | 62.5031 | -61.5143 | -61.5417 | 62.2696 | 0.11444 | 0.036621 | 0.12817 | 62.4893 | -61.5875 | -0.13733 | -0.036621 | -0.041199 | -0.16479 | -0.27008 | -0.21057 | -0.050354 | 0.09613 | 61.4136 | 61.5051 | 123.6465 | 123.88 | -0.041199 | 123.8663 | 61.4914 | -0.21057 | 123.88 | -0.041199 | 61.4914 | 123.6465 | 123.8663 | -124.054 | -124.1272
531.7344 | 124.2142 | -61.3358 | 62.4802 | 0.12077 | 0.0057699 | 0.01085 | -0.0017796 | 0.069434 | -0.00033333 | 0.070718 | -61.4227 | 62.384 | -61.5372 | -61.5326 | 62.2879 | 0.091553 | -0.17395 | 0.10529 | 62.4115 | -61.5784 | -0.20142 | -0.096131 | -0.086975 | -0.19684 | -0.19226 | -0.24262 | -0.068665 | 0.11444 | 61.1618 | 61.441 | 123.6237 | 123.7198 | -0.086975 | 123.7473 | 61.4273 | -0.24262 | 123.7198 | -0.086975 | 61.4273 | 123.6237 | 123.7473 | -124.0173 | -124.0585
532.7188 | 124.1043 | -61.3678 | 62.5534 | -0.19966 | 0.0061971 | 0.009141 | -0.00028416 | 0.06922 | -0.0014013 | 0.068795 | -61.4182 | 62.4985 | -61.5372 | -61.528 | 62.2604 | 0.10986 | 0.064087 | 0.15106 | 62.4527 | -61.6379 | -0.16937 | -0.054932 | -0.050354 | -0.16022 | -0.29297 | -0.27008 | -0.10071 | 0.11902 | 61.4319 | 61.5189 | 123.6282 | 123.8663 | -0.050354 | 123.8205 | 61.4777 | -0.27008 | 123.8663 | -0.050354 | 61.4777 | 123.6282 | 123.8205 | -124.0906 | -124.1913
533.7188 | 124.1592 | -61.3678 | 62.5488 | -0.25307 | 0.0059835 | 0.0038004 | 0.00014304 | 0.067298 | -0.00097413 | 0.067727 | -61.441 | 62.5168 | -61.496 | -61.528 | 62.2513 | 0.10529 | 0.07782 | 0.13733 | 62.5122 | -61.5921 | -0.12817 | -0.032043 | -0.073242 | -0.16022 | -0.29755 | -0.2243 | -0.036621 | 0.054932 | 61.4456 | 61.5051 | 123.6191 | 123.8846 | -0.073242 | 123.88 | 61.4731 | -0.2243 | 123.8846 | -0.073242 | 61.4731 | 123.6191 | 123.88 | -124.0448 | -124.1409
534.7188 | 124.1226 | -61.377 | 62.5351 | -0.0012969 | 0.0068381 | 0.011491 | 0.0014248 | 0.066443 | -0.0022559 | 0.069863 | -61.4273 | 62.4985 | -61.5326 | -61.5555 | 62.2467 | 0.059509 | 0.018311 | 0.07782 | 62.4847 | -61.6241 | -0.15564 | -0.036621 | -0.050354 | -0.17853 | -0.28839 | -0.24719 | -0.050354 | 0.10529 | 61.3953 | 61.4548 | 123.6237 | 123.8754 | -0.050354 | 123.8617 | 61.4365 | -0.24719 | 123.8754 | -0.050354 | 61.4365 | 123.6237 | 123.8617 | -124.0677 | -124.1592
535.7188 | 124.1272 | -61.377 | 62.5259 | -0.19203 | 0.0074789 | 0.0097818 | 0.0012112 | 0.069434 | -0.0031103 | 0.0673 | -61.4365 | 62.4985 | -61.5417 | -61.5601 | 62.2696 | 0.09613 | 0.082397 | 0.11444 | 62.4939 | -61.5967 | -0.16479 | -0.027466 | -0.059509 | -0.18311 | -0.25635 | -0.21973 | -0.032044 | 0.10529 | 61.4594 | 61.4914 | 123.6465 | 123.8754 | -0.059509 | 123.8708 | 61.4731 | -0.21973 | 123.8754 | -0.059509 | 61.4731 | 123.6465 | 123.8708 | -124.0677 | -124.1226
536.7188 | 124.1272 | -61.3724 | 62.5397 | -0.09285 | 0.0076925 | 0.010636 | 0.00078404 | 0.06922 | -0.0018285 | 0.069222 | -61.4182 | 62.5031 | -61.5189 | -61.5326 | 62.265 | 0.10529 | 0.027466 | 0.11444 | 62.4756 | -61.6013 | -0.14648 | -0.036621 | -0.045777 | -0.16022 | -0.27466 | -0.22888 | -0.064087 | 0.10071 | 61.3998 | 61.4868 | 123.6374 | 123.8754 | -0.045777 | 123.848 | 61.4777 | -0.22888 | 123.8754 | -0.045777 | 61.4777 | 123.6374 | 123.848 | -124.0585 | -124.1409
537.7188 | 124.1272 | -61.377 | 62.5534 | -0.14626 | 0.0076925 | 0.012773 | 0.00014304 | 0.068793 | -0.00097413 | 0.069436 | -61.4182 | 62.5259 | -61.5509 | -61.528 | 62.2559 | 0.11902 | 0.013733 | 0.11444 | 62.4939 | -61.6058 | -0.17395 | -0.027466 | -0.041199 | -0.15106 | -0.29755 | -0.22888 | -0.05951 | 0.13275 | 61.3907 | 61.4914 | 123.6328 | 123.9029 | -0.041199 | 123.8708 | 61.496 | -0.22888 | 123.9029 | -0.041199 | 61.496 | 123.6328 | 123.8708 | -124.1043 | -124.1592
538.7188 | 124.1318 | -61.3632 | 62.5488 | -0.11574 | 0.0072653 | 0.011704 | 0.0012112 | 0.067725 | -0.00076053 | 0.069222 | -61.4319 | 62.5214 | -61.5463 | -61.5372 | 62.2513 | 0.10071 | 0.045776 | 0.12817 | 62.4893 | -61.5784 | -0.18311 | -0.027466 | -0.068665 | -0.17395 | -0.29755 | -0.21515 | -0.059509 | 0.11444 | 61.409 | 61.4914 | 123.6145 | 123.8846 | -0.068665 | 123.8525 | 61.4639 | -0.21515 | 123.8846 | -0.068665 | 61.4639 | 123.6145 | 123.8525 | -124.0952 | -124.1272
539.7188 | 124.1089 | -61.377 | 62.5351 | -0.016556 | 0.01047 | 0.0097818 | 0.0014248 | 0.069861 | -0.0018285 | 0.067513 | -61.4502 | 62.5031 | -61.5326 | -61.5829 | 62.2238 | 0.036621 | 0.022888 | 0.050354 | 62.4619 | -61.6287 | -0.15564 | -0.032043 | -0.073242 | -0.20599 | -0.31128 | -0.25177 | -0.073242 | 0.082398 | 61.3998 | 61.4273 | 123.6008 | 123.88 | -0.073242 | 123.8388 | 61.4136 | -0.25177 | 123.88 | -0.073242 | 61.4136 | 123.6008 | 123.8388 | -124.0677 | -124.1638
540.7188 | 124.1364 | -61.3724 | 62.5351 | -0.10811 | 0.0047019 | 0.0095682 | 0.0012112 | 0.068152 | -0.0014013 | 0.068368 | -61.4182 | 62.5168 | -61.5417 | -61.528 | 62.2787 | 0.13275 | 0.050354 | 0.13275 | 62.4847 | -61.5967 | -0.16937 | -0.01831 | -0.045777 | -0.15564 | -0.25635 | -0.22431 | -0.050354 | 0.1236 | 61.4227 | 61.5051 | 123.6511 | 123.8892 | -0.045777 | 123.8571 | 61.5051 | -0.22431 | 123.8892 | -0.045777 | 61.5051 | 123.6511 | 123.8571 | -124.0768 | -124.1318
541.7188 | 124.1089 | -61.3632 | 62.5397 | -0.24544 | 0.0068381 | 0.012345 | -0.00049776 | 0.068793 | -0.0022559 | 0.067727 | -61.4685 | 62.5442 | -61.5234 | -61.5784 | 62.233 | 0.086975 | 0.11902 | 0.10071 | 62.5351 | -61.6058 | -0.16022 | 0.004577 | -0.10529 | -0.21515 | -0.3067 | -0.24262 | -0.004578 | 0.054931 | 61.4822 | 61.4639 | 123.5962 | 123.9075 | -0.10529 | 123.8983 | 61.4502 | -0.24262 | 123.9075 | -0.10529 | 61.4502 | 123.5962 | 123.8983 | -124.0631 | -124.1455
542.7188 | 124.1318 | -61.3724 | 62.5305 | -0.19203 | 0.0068381 | 0.0082864 | -0.0022068 | 0.06623 | -0.00076053 | 0.06965 | -61.4502 | 62.4985 | -61.5143 | -61.5463 | 62.2513 | 0.11444 | 0.07782 | 0.11902 | 62.4847 | -61.5967 | -0.14191 | -0.032044 | -0.07782 | -0.17395 | -0.27924 | -0.22431 | -0.045777 | 0.064087 | 61.4502 | 61.4914 | 123.6237 | 123.8708 | -0.07782 | 123.8571 | 61.4868 | -0.22431 | 123.8708 | -0.07782 | 61.4868 | 123.6237 | 123.8571 | -124.0448 | -124.1272
543.7188 | 124.118 | -61.3953 | 62.5259 | -0.08522 | 0.010683 | 0.012773 | 0.00099764 | 0.068152 | -0.00054693 | 0.068795 | -61.4182 | 62.5076 | -61.5555 | -61.5326 | 62.2604 | 0.11444 | 0.013733 | 0.10986 | 62.4939 | -61.6241 | -0.16022 | -0.018311 | -0.022888 | -0.13733 | -0.2655 | -0.22888 | -0.032044 | 0.13733 | 61.409 | 61.5051 | 123.6557 | 123.9029 | -0.022888 | 123.8892 | 61.5097 | -0.22888 | 123.9029 | -0.022888 | 61.5097 | 123.6557 | 123.8892 | -124.0814 | -124.1501
544.7188 | 124.1547 | -61.3815 | 62.5351 | -0.16151 | 0.0094015 | 0.011064 | 0.0012112 | 0.070075 | -0.0018285 | 0.067941 | -61.4319 | 62.4847 | -61.5326 | -61.5326 | 62.265 | 0.10071 | 0.041199 | 0.11444 | 62.4664 | -61.5875 | -0.15106 | -0.050354 | -0.050354 | -0.15106 | -0.27008 | -0.20599 | -0.068664 | 0.10071 | 61.4227 | 61.496 | 123.6465 | 123.8663 | -0.050354 | 123.848 | 61.4822 | -0.20599 | 123.8663 | -0.050354 | 61.4822 | 123.6465 | 123.848 | -124.0677 | -124.1226
545.7188 | 124.1364 | -61.3861 | 62.5397 | -0.14626 | 0.0064107 | 0.012132 | 0.0016384 | 0.069861 | -0.00076053 | 0.070718 | -61.3998 | 62.4847 | -61.528 | -61.5189 | 62.2742 | 0.11902 | 0.027466 | 0.12817 | 62.4802 | -61.5921 | -0.14191 | -0.054932 | -0.013733 | -0.13275 | -0.2655 | -0.20599 | -0.059509 | 0.12817 | 61.4136 | 61.5143 | 123.6603 | 123.8708 | -0.013733 | 123.8663 | 61.5051 | -0.20599 | 123.8708 | -0.013733 | 61.5051 | 123.6603 | 123.8663 | -124.0677 | -124.1318
546.7188 | 124.1592 | -61.3678 | 62.5534 | -0.10048 | 0.0083333 | 0.013627 | 0.0020656 | 0.067939 | -0.00011953 | 0.068154 | -61.409 | 62.4939 | -61.528 | -61.5326 | 62.2787 | 0.10986 | 0.036621 | 0.14191 | 62.5122 | -61.5875 | -0.16022 | -0.05951 | -0.041199 | -0.16479 | -0.27466 | -0.21973 | -0.041199 | 0.11902 | 61.4044 | 61.5097 | 123.6465 | 123.8617 | -0.041199 | 123.88 | 61.4777 | -0.21973 | 123.8617 | -0.041199 | 61.4777 | 123.6465 | 123.88 | -124.0814 | -124.1409
547.7188 | 124.1272 | -61.3861 | 62.5626 | -0.22255 | 0.0070517 | 0.0093546 | -0.0013522 | 0.068366 | -0.00054693 | 0.069436 | -61.4777 | 62.4985 | -61.5417 | -61.5692 | 62.2467 | 0.082397 | 0.10986 | 0.10071 | 62.4985 | -61.6058 | -0.15564 | -0.064087 | -0.091553 | -0.18311 | -0.31586 | -0.21973 | -0.064087 | 0.064087 | 61.496 | 61.4868 | 123.6328 | 123.8846 | -0.091553 | 123.8846 | 61.4685 | -0.21973 | 123.8846 | -0.091553 | 61.4685 | 123.6328 | 123.8846 | -124.1043 | -124.1684
548.7188 | 124.0952 | -61.377 | 62.5809 | -0.21492 | 0.0074789 | 0.010423 | 0.00035684 | 0.067511 | -0.0016149 | 0.069009 | -61.4731 | 62.4847 | -61.5372 | -61.5829 | 62.2375 | 0.091553 | 0.11902 | 0.091553 | 62.5168 | -61.5967 | -0.16022 | -0.096131 | -0.09613 | -0.20599 | -0.34332 | -0.21973 | -0.064087 | 0.064087 | 61.496 | 61.4685 | 123.6145 | 123.8617 | -0.09613 | 123.8937 | 61.4685 | -0.21973 | 123.8617 | -0.09613 | 61.4685 | 123.6145 | 123.8937 | -124.118 | -124.1776
549.7188 | 124.1272 | -61.3586 | 62.5626 | -0.15388 | 0.0057699 | 0.014054 | 0.0020656 | 0.070075 | 0.00094847 | 0.067941 | -61.4227 | 62.4664 | -61.5509 | -61.6104 | 62.4252 | 0.09613 | 0.064087 | 0.13733 | 62.4756 | -61.6196 | -0.19226 | -0.09613 | -0.064086 | -0.25177 | -0.13733 | -0.26093 | -0.086975 | 0.12817 | 61.4227 | 61.496 | 123.7839 | 123.8251 | -0.064086 | 123.8342 | 61.4548 | -0.26093 | 123.8251 | -0.064086 | 61.4548 | 123.7839 | 123.8342 | -124.1135 | -124.1821
550.7188 | 124.1089 | -61.3861 | 62.558 | -0.039444 | 0.0083333 | 0.012132 | 0.0022794 | 0.068793 | -0.0014013 | 0.070718 | -61.4182 | 62.4985 | -61.5234 | -61.528 | 62.2604 | 0.16479 | -0.17853 | 0.13733 | 62.4573 | -61.6241 | -0.13733 | -0.059509 | -0.032044 | -0.14191 | -0.29755 | -0.23804 | -0.10071 | 0.10529 | 61.2076 | 61.5234 | 123.6465 | 123.8846 | -0.032044 | 123.8434 | 61.5509 | -0.23804 | 123.8846 | -0.032044 | 61.5509 | 123.6465 | 123.8434 | -124.0814 | -124.1821
551.7188 | 124.118 | -61.3724 | 62.5259 | -0.09285 | 0.0083333 | 0.01085 | 0.00057044 | 0.069861 | 0.00094847 | 0.069222 | -61.4182 | 62.5031 | -61.5509 | -61.5326 | 62.2787 | 0.10986 | 0.022888 | 0.11902 | 62.5031 | -61.6104 | -0.17853 | -0.022888 | -0.045777 | -0.16022 | -0.24719 | -0.23804 | -0.022888 | 0.13275 | 61.3953 | 61.4914 | 123.6511 | 123.8754 | -0.045777 | 123.8754 | 61.4822 | -0.23804 | 123.8754 | -0.045777 | 61.4822 | 123.6511 | 123.8754 | -124.0768 | -124.1364
552.7188 | 124.1364 | -61.3724 | 62.5076 | -0.21492 | 0.0079061 | 0.0095682 | 0.00078404 | 0.067084 | -0.0028967 | 0.070718 | -61.4273 | 62.4893 | -61.5234 | -61.5234 | 62.2742 | 0.10986 | 0.027466 | 0.13275 | 62.4756 | -61.6104 | -0.15106 | -0.01831 | -0.054932 | -0.15106 | -0.23346 | -0.23804 | -0.032043 | 0.09613 | 61.3998 | 61.5051 | 123.6465 | 123.8617 | -0.054932 | 123.848 | 61.4822 | -0.23804 | 123.8617 | -0.054932 | 61.4822 | 123.6465 | 123.848 | -124.0311 | -124.118
553.7188 | 124.1089 | -61.3678 | 62.5122 | -0.10811 | 0.0079061 | 0.0087138 | 0.00099764 | 0.069648 | -0.0016149 | 0.071359 | -61.4319 | 62.5168 | -61.5509 | -61.5326 | 62.2696 | 0.12817 | 0.045776 | 0.11444 | 62.4985 | -61.5921 | -0.1831 | 0.004578 | -0.064087 | -0.16479 | -0.24261 | -0.2243 | -0.013733 | 0.11902 | 61.4136 | 61.4822 | 123.6374 | 123.8846 | -0.064087 | 123.8663 | 61.496 | -0.2243 | 123.8846 | -0.064087 | 61.496 | 123.6374 | 123.8663 | -124.0631 | -124.1043
554.7188 | 124.173 | -61.3861 | 62.4985 | 0.23521 | 0.0059835 | 0.010209 | -0.0013522 | 0.066657 | 0.00052127 | 0.06965 | -61.4914 | 62.4619 | -61.5417 | -61.6013 | 62.2147 | 0.013733 | -0.086975 | 0.013733 | 62.4664 | -61.6013 | -0.15564 | -0.036621 | -0.10529 | -0.21515 | -0.28381 | -0.21515 | -0.032043 | 0.050354 | 61.2991 | 61.3998 | 123.6008 | 123.848 | -0.10529 | 123.8525 | 61.3998 | -0.21515 | 123.848 | -0.10529 | 61.3998 | 123.6008 | 123.8525 | -124.0402 | -124.0997
555.7188 | 124.0768 | -61.3815 | 62.5442 | -0.2607 | 0.0070517 | 0.0076456 | -0.0024204 | 0.067298 | 0.0011621 | 0.067727 | -61.4822 | 62.5076 | -61.5509 | -61.5784 | 62.2421 | 0.07782 | 0.11444 | 0.09613 | 62.4847 | -61.6196 | -0.16937 | -0.036621 | -0.10071 | -0.19684 | -0.30212 | -0.23804 | -0.059509 | 0.068664 | 61.496 | 61.4777 | 123.6237 | 123.8892 | -0.10071 | 123.8663 | 61.4594 | -0.23804 | 123.8892 | -0.10071 | 61.4594 | 123.6237 | 123.8663 | -124.0952 | -124.1638
556.7188 | 124.1135 | -61.3815 | 62.5351 | -0.24544 | 0.0081197 | 0.0078592 | 0.00035684 | 0.06922 | -0.0039649 | 0.068582 | -61.4548 | 62.4985 | -61.5509 | -61.5417 | 62.2421 | 0.086975 | 0.09613 | 0.1236 | 62.5031 | -61.615 | -0.16937 | -0.036621 | -0.073242 | -0.16022 | -0.29297 | -0.23346 | -0.032043 | 0.09613 | 61.4777 | 61.5051 | 123.6237 | 123.88 | -0.073242 | 123.8846 | 61.4685 | -0.23346 | 123.88 | -0.073242 | 61.4685 | 123.6237 | 123.8846 | -124.086 | -124.1501
557.7188 | 124.1501 | -61.3541 | 62.5351 | -0.21492 | 0.0083333 | 0.0089274 | 0.001852 | 0.067725 | -0.00076053 | 0.067086 | -61.409 | 62.4847 | -61.5143 | -61.5326 | 62.265 | 0.10986 | 0.032043 | 0.11902 | 62.4664 | -61.615 | -0.16022 | -0.050354 | -0.054932 | -0.17853 | -0.27008 | -0.26093 | -0.068664 | 0.10529 | 61.3861 | 61.4731 | 123.6191 | 123.8388 | -0.054932 | 123.8205 | 61.4639 | -0.26093 | 123.8388 | -0.054932 | 61.4639 | 123.6191 | 123.8205 | -124.0494 | -124.1501
558.7188 | 124.1089 | -61.377 | 62.5442 | -0.10811 | 0.0096151 | 0.010209 | 0.0031338 | 0.068366 | -0.0011877 | 0.069436 | -61.4182 | 62.5122 | -61.5326 | -61.5189 | 62.2604 | 0.10986 | 0.050354 | 0.13275 | 62.471 | -61.5921 | -0.15564 | -0.032043 | -0.041199 | -0.14191 | -0.28381 | -0.21515 | -0.073242 | 0.11444 | 61.4273 | 61.5097 | 123.6374 | 123.8892 | -0.041199 | 123.848 | 61.4868 | -0.21515 | 123.8892 | -0.041199 | 61.4868 | 123.6374 | 123.848 | -124.0768 | -124.1364
559.7188 | 124.0631 | -61.377 | 62.5442 | 0.067368 | 0.0091879 | 0.012986 | 0.0014248 | 0.068579 | -0.0014013 | 0.068582 | -61.4685 | 62.4893 | -61.5601 | -61.6058 | 62.1918 | 0 | 0.050354 | -0.013733 | 62.4893 | -61.6104 | -0.18311 | -0.054931 | -0.091553 | -0.22888 | -0.35248 | -0.23346 | -0.054931 | 0.091553 | 61.4273 | 61.3632 | 123.5687 | 123.8663 | -0.091553 | 123.8663 | 61.377 | -0.23346 | 123.8663 | -0.091553 | 61.377 | 123.5687 | 123.8663 | -124.1043 | -124.1547
560.7188 | 124.1272 | -61.3678 | 62.5534 | -0.27596 | 0.0091879 | 0.009141 | -0.00049776 | 0.06687 | 9.4068e-05 | 0.069222 | -61.441 | 62.5076 | -61.5234 | -61.5143 | 62.2467 | 0.11444 | 0.091553 | 0.13275 | 62.5259 | -61.6058 | -0.15564 | -0.045777 | -0.073242 | -0.14648 | -0.3067 | -0.23804 | -0.027466 | 0.082397 | 61.4594 | 61.5005 | 123.6145 | 123.8754 | -0.073242 | 123.8937 | 61.4822 | -0.23804 | 123.8754 | -0.073242 | 61.4822 | 123.6145 | 123.8937 | -124.0768 | -124.1592
561.7188 | 124.1043 | -61.377 | 62.5854 | -0.30647 | 0.0087607 | 0.014695 | -0.00092496 | 0.067298 | -0.0026831 | 0.069009 | -61.4868 | 62.5122 | -61.5463 | -61.5784 | 62.2192 | 0.064087 | 0.14648 | 0.10529 | 62.4985 | -61.5738 | -0.16937 | -0.073242 | -0.10986 | -0.20142 | -0.36621 | -0.19684 | -0.086975 | 0.05951 | 61.5234 | 61.4822 | 123.5962 | 123.8892 | -0.10986 | 123.8754 | 61.441 | -0.19684 | 123.8892 | -0.10986 | 61.441 | 123.5962 | 123.8754 | -124.1318 | -124.1592
562.7188 | 124.0723 | -61.3815 | 62.5717 | -1.9926 | 0.0053427 | 0.005723 | -0.001566 | 0.067084 | -0.0016149 | 0.068795 | -61.4731 | 62.5214 | -61.5463 | -61.5784 | 62.1964 | 0.050354 | 0.16022 | 0.11902 | 62.5305 | -61.6104 | -0.16479 | -0.050354 | -0.091552 | -0.19684 | -0.37537 | -0.22888 | -0.041198 | 0.073243 | 61.5417 | 61.5006 | 123.5779 | 123.9029 | -0.091552 | 123.912 | 61.4319 | -0.22888 | 123.9029 | -0.091552 | 61.4319 | 123.5779 | 123.912 | -124.118 | -124.1821
563.7188 | 124.1043 | -61.3815 | 62.5626 | -0.17677 | 0.0070517 | 0.0097818 | -0.00092496 | 0.067084 | -0.0031103 | 0.068368 | -61.4685 | 62.5031 | -61.5097 | -61.5692 | 62.2375 | 0.086975 | 0.1236 | 0.10529 | 62.5259 | -61.5646 | -0.12817 | -0.059509 | -0.086975 | -0.18768 | -0.32501 | -0.1831 | -0.036621 | 0.041199 | 61.5051 | 61.4868 | 123.6191 | 123.8846 | -0.086975 | 123.9075 | 61.4685 | -0.1831 | 123.8846 | -0.086975 | 61.4685 | 123.6191 | 123.9075 | -124.0723 | -124.1272
564.7188 | 124.086 | -61.4227 | 62.5397 | 3.4777 | 0.0096151 | 0.0078592 | -0.00049776 | 0.069007 | -0.0024695 | 0.069009 | -61.3083 | 62.4481 | -61.5509 | -61.6241 | 62.2284 | 0.004578 | -0.022888 | -0.022888 | 62.4893 | -61.6104 | -0.12817 | -0.091553 | 0.11444 | -0.20142 | -0.31128 | -0.18768 | -0.050354 | 0.24261 | 61.3998 | 61.3998 | 123.6511 | 123.8708 | 0.11444 | 123.912 | 61.4273 | -0.18768 | 123.8708 | 0.11444 | 61.4273 | 123.6511 | 123.912 | -124.0906 | -124.1501
565.7188 | 124.1318 | -61.3541 | 62.5214 | -0.11574 | 0.0094015 | 0.0099954 | 0.002493 | 0.069861 | -0.00097413 | 0.06965 | -61.4365 | 62.5351 | -61.5326 | -61.5326 | 62.2513 | 0.10529 | 0.10529 | 0.1236 | 62.5122 | -61.6058 | -0.17853 | 0.013733 | -0.082397 | -0.17853 | -0.27008 | -0.25177 | -0.009155 | 0.096131 | 61.4594 | 61.4777 | 123.6053 | 123.8892 | -0.082397 | 123.8663 | 61.4594 | -0.25177 | 123.8892 | -0.082397 | 61.4594 | 123.6053 | 123.8663 | -124.054 | -124.1272
566.7188 | 124.0997 | -61.377 | 62.5351 | -0.14626 | 0.0076925 | 0.0093546 | 0.00099764 | 0.067939 | -0.0020421 | 0.069222 | -61.4548 | 62.5168 | -61.5463 | -61.5417 | 62.2604 | 0.09613 | 0.086975 | 0.1236 | 62.4939 | -61.5738 | -0.16937 | -0.01831 | -0.07782 | -0.16479 | -0.27466 | -0.19684 | -0.041199 | 0.091553 | 61.4639 | 61.5005 | 123.6374 | 123.8937 | -0.07782 | 123.8708 | 61.4731 | -0.19684 | 123.8937 | -0.07782 | 61.4731 | 123.6374 | 123.8708 | -124.0814 | -124.1089
567.7188 | 124.1226 | -61.3815 | 62.558 | -0.19966 | 0.0059835 | 0.0095682 | -0.0017796 | 0.06922 | -0.0016149 | 0.068154 | -61.4594 | 62.4985 | -61.5463 | -61.5646 | 62.2421 | 0.086975 | 0.11444 | 0.10071 | 62.5122 | -61.5829 | -0.16479 | -0.059509 | -0.07782 | -0.1831 | -0.31586 | -0.20142 | -0.045776 | 0.086975 | 61.496 | 61.4822 | 123.6237 | 123.88 | -0.07782 | 123.8937 | 61.4685 | -0.20142 | 123.88 | -0.07782 | 61.4685 | 123.6237 | 123.8937 | -124.1043 | -124.1409
568.7188 | 124.0768 | -61.3724 | 62.5305 | -0.23781 | 0.0079061 | 0.0044412 | -0.00092496 | 0.06388 | -0.0039649 | 0.067727 | -61.4822 | 62.4619 | -61.528 | -61.6882 | 62.059 | -0.045776 | 0.16937 | 0.054932 | 62.471 | -61.615 | -0.15564 | -0.068665 | -0.10986 | -0.31586 | -0.4715 | -0.24262 | -0.05951 | 0.045776 | 61.5417 | 61.4273 | 123.4314 | 123.8342 | -0.10986 | 123.8434 | 61.3266 | -0.24262 | 123.8342 | -0.10986 | 61.3266 | 123.4314 | 123.8434 | -124.0585 | -124.1455
569.7188 | 124.1226 | -61.3815 | 62.5305 | -0.039444 | 0.0083333 | 0.011704 | 0.0020656 | 0.067939 | -0.0031103 | 0.069436 | -61.4273 | 62.4847 | -61.5372 | -61.5738 | 62.2055 | 0.045776 | 0.022888 | 0.068665 | 62.4756 | -61.5875 | -0.15564 | -0.045777 | -0.045776 | -0.19226 | -0.32501 | -0.20599 | -0.054932 | 0.10986 | 61.4044 | 61.4502 | 123.587 | 123.8663 | -0.045776 | 123.8571 | 61.4273 | -0.20599 | 123.8663 | -0.045776 | 61.4273 | 123.587 | 123.8571 | -124.0677 | -124.118
570.7188 | 124.0997 | -61.3632 | 62.558 | -0.25307 | 0.0072653 | 0.0095682 | -0.00092496 | 0.066657 | -0.0026831 | 0.068154 | -61.4822 | 62.5031 | -61.5326 | -61.5738 | 62.2238 | 0.086975 | 0.12817 | 0.09613 | 62.4893 | -61.5829 | -0.16937 | -0.054931 | -0.11902 | -0.21057 | -0.33417 | -0.21973 | -0.068664 | 0.050354 | 61.4914 | 61.4594 | 123.587 | 123.8663 | -0.11902 | 123.8525 | 61.4502 | -0.21973 | 123.8663 | -0.11902 | 61.4502 | 123.587 | 123.8525 | -124.0906 | -124.1409
571.7188 | 124.1272 | -61.3449 | 62.5442 | -0.14626 | 0.0085471 | 0.0085 | 0.0027066 | 0.068152 | -0.00076053 | 0.068154 | -61.4319 | 62.5168 | -61.528 | -61.5372 | 62.2559 | 0.11444 | 0.086975 | 0.14648 | 62.5031 | -61.5967 | -0.18311 | -0.027465 | -0.086975 | -0.19226 | -0.28839 | -0.25177 | -0.041198 | 0.09613 | 61.4319 | 61.4914 | 123.6008 | 123.8617 | -0.086975 | 123.848 | 61.4594 | -0.25177 | 123.8617 | -0.086975 | 61.4594 | 123.6008 | 123.848 | -124.0723 | -124.1409
572.7188 | 124.1272 | -61.3815 | 62.5671 | -0.13863 | 0.0081197 | 0.011491 | -0.00049776 | 0.067298 | 0.00052127 | 0.069009 | -61.4594 | 62.4939 | -61.5326 | -61.5372 | 62.2604 | 0.10071 | 0.10529 | 0.1236 | 62.471 | -61.5784 | -0.15106 | -0.073243 | -0.07782 | -0.15564 | -0.3067 | -0.19684 | -0.096131 | 0.073242 | 61.4868 | 61.5051 | 123.642 | 123.8754 | -0.07782 | 123.8525 | 61.4822 | -0.19684 | 123.8754 | -0.07782 | 61.4822 | 123.642 | 123.8525 | -124.0997 | -124.1455
573.7188 | 124.1135 | -61.3632 | 62.5671 | -0.1844 | 0.0074789 | 0.0087138 | -0.0011386 | 0.06687 | -0.0018285 | 0.067086 | -61.4548 | 62.5168 | -61.5189 | -61.5509 | 62.2604 | 0.09613 | 0.10529 | 0.1236 | 62.5031 | -61.615 | -0.15564 | -0.050354 | -0.091553 | -0.18768 | -0.3067 | -0.25177 | -0.064087 | 0.064087 | 61.4685 | 61.4868 | 123.6237 | 123.88 | -0.091553 | 123.8663 | 61.4594 | -0.25177 | 123.88 | -0.091553 | 61.4594 | 123.6237 | 123.8663 | -124.086 | -124.1821
574.7188 | 124.1684 | -61.3815 | 62.4802 | 0.21233 | 0.0091879 | 0.012345 | -0.0013522 | 0.068793 | -0.00097413 | 0.068795 | -61.4777 | 62.4573 | -61.5463 | -61.5784 | 62.233 | 0.022888 | -0.1236 | 0.045776 | 62.439 | -61.5875 | -0.16479 | -0.022889 | -0.09613 | -0.19684 | -0.24719 | -0.20599 | -0.041199 | 0.068665 | 61.2579 | 61.4273 | 123.6145 | 123.8388 | -0.09613 | 123.8205 | 61.4044 | -0.20599 | 123.8388 | -0.09613 | 61.4044 | 123.6145 | 123.8205 | -124.0265 | -124.0677
575.7188 | 124.0723 | -61.3586 | 62.558 | -0.23781 | 0.0072653 | 0.01085 | 0.00099764 | 0.067725 | -0.00076053 | 0.067727 | -61.4777 | 62.4893 | -61.5372 | -61.5601 | 62.2421 | 0.045776 | 0.14648 | 0.12817 | 62.5076 | -61.5967 | -0.17853 | -0.068664 | -0.11902 | -0.20142 | -0.31586 | -0.23804 | -0.050354 | 0.059509 | 61.5051 | 61.4868 | 123.6008 | 123.848 | -0.11902 | 123.8663 | 61.4044 | -0.23804 | 123.848 | -0.11902 | 61.4044 | 123.6008 | 123.8663 | -124.0952 | -124.1547
576.7188 | 124.054 | -61.3815 | 62.5626 | -0.20729 | 0.0074789 | 0.014268 | -0.0013522 | 0.064307 | -0.00076053 | 0.067727 | -61.4914 | 62.4847 | -61.5463 | -61.5417 | 62.4985 | 0.21973 | -0.064087 | 0.086975 | 62.4847 | -61.5829 | -0.16479 | -0.07782 | -0.10986 | -0.16022 | -0.064087 | -0.20142 | -0.07782 | 0.054932 | 61.3174 | 61.4685 | 123.88 | 123.8663 | -0.10986 | 123.8663 | 61.6013 | -0.20142 | 123.8663 | -0.10986 | 61.6013 | 123.88 | 123.8663 | -124.1089 | -124.1455
577.7188 | 124.0723 | -61.3724 | 62.5717 | -0.24544 | 0.0057699 | 0.011491 | -0.00049776 | 0.065589 | -0.0011877 | 0.069009 | -61.4822 | 62.4847 | -61.5555 | -61.5738 | 62.2055 | 0.082397 | 0.12817 | 0.091553 | 62.5122 | -61.5967 | -0.18311 | -0.086975 | -0.10986 | -0.20142 | -0.36621 | -0.22431 | -0.059509 | 0.073242 | 61.5005 | 61.4639 | 123.5779 | 123.8571 | -0.10986 | 123.8846 | 61.4548 | -0.22431 | 123.8571 | -0.10986 | 61.4548 | 123.5779 | 123.8846 | -124.1272 | -124.1684
578.7188 | 124.1501 | -61.3495 | 62.5534 | -0.12337 | 0.0079061 | 0.012986 | 0.00099764 | 0.069861 | -0.0024695 | 0.068154 | -61.441 | 62.5031 | -61.5372 | -61.5372 | 62.265 | 0.10529 | 0.091553 | 0.14191 | 62.5031 | -61.5921 | -0.18768 | -0.050354 | -0.091553 | -0.18768 | -0.28839 | -0.24261 | -0.050354 | 0.09613 | 61.441 | 61.4914 | 123.6145 | 123.8525 | -0.091553 | 123.8525 | 61.4548 | -0.24261 | 123.8525 | -0.091553 | 61.4548 | 123.6145 | 123.8525 | -124.0906 | -124.1455
579.7188 | 124.1135 | -61.3953 | 62.5442 | 0.10551 | 0.0072653 | 0.013413 | 0.0012112 | 0.070716 | -0.0031103 | 0.072 | -61.5051 | 62.5031 | -61.5601 | -61.9446 | 61.9263 | 0.12817 | 0.11902 | -0.09613 | 62.5076 | -61.6058 | -0.1648 | -0.041198 | -0.10986 | -0.54932 | -0.61798 | -0.21057 | -0.036621 | 0.054932 | 61.5143 | 61.2991 | 123.3215 | 123.8983 | -0.10986 | 123.9029 | 61.5234 | -0.21057 | 123.8983 | -0.10986 | 61.5234 | 123.3215 | 123.9029 | -124.1043 | -124.1501
580.7188 | 124.1364 | -61.3724 | 62.5534 | -0.22255 | 0.0066245 | 0.0087138 | 0.0012112 | 0.068152 | 0.00094847 | 0.068582 | -61.4594 | 62.4893 | -61.5417 | -61.5646 | 62.2284 | 0.091553 | 0.10529 | 0.11444 | 62.4985 | -61.5509 | -0.16937 | -0.064087 | -0.086976 | -0.19226 | -0.32501 | -0.17853 | -0.054932 | 0.082397 | 61.4777 | 61.4868 | 123.6008 | 123.8617 | -0.086976 | 123.8708 | 61.4639 | -0.17853 | 123.8617 | -0.086976 | 61.4639 | 123.6008 | 123.8708 | -124.0952 | -124.1043
581.7188 | 124.0814 | -61.377 | 62.558 | -0.14626 | 0.0085471 | 0.0095682 | 0.00057044 | 0.067725 | -0.0035375 | 0.069863 | -61.4502 | 62.4985 | -61.5189 | -61.5692 | 62.2375 | 0.09613 | 0.11902 | 0.11902 | 62.4893 | -61.5738 | -0.14191 | -0.059509 | -0.073242 | -0.19226 | -0.32043 | -0.19684 | -0.068664 | 0.068665 | 61.496 | 61.496 | 123.6145 | 123.8754 | -0.073242 | 123.8663 | 61.4731 | -0.19684 | 123.8754 | -0.073242 | 61.4731 | 123.6145 | 123.8663 | -124.0768 | -124.1318
582.7188 | 124.0814 | -61.3953 | 62.5671 | -0.17677 | 0.0034201 | 0.0078592 | -7.0562e-05 | 0.067084 | -0.0033239 | 0.0673 | -61.4822 | 62.4802 | -61.5417 | -61.3861 | 62.1231 | -0.050354 | 0.13733 | 0.1236 | 62.5122 | -61.6058 | -0.14648 | -0.086975 | -0.086975 | 0.009156 | -0.44403 | -0.21057 | -0.054932 | 0.059509 | 61.5326 | 61.5189 | 123.5184 | 123.8754 | -0.086975 | 123.9075 | 61.3449 | -0.21057 | 123.8754 | -0.086975 | 61.3449 | 123.5184 | 123.9075 | -124.1089 | -124.173
583.7188 | 124.1318 | -61.3541 | 62.5992 | -0.23781 | 0.0055563 | 0.010209 | -0.00092496 | 0.064734 | -0.0020421 | 0.067727 | -61.4639 | 62.4802 | -61.5189 | -61.5692 | 62.2192 | 0.086975 | 0.13733 | 0.1236 | 62.4939 | -61.5829 | -0.16479 | -0.11902 | -0.10986 | -0.21515 | -0.37994 | -0.22888 | -0.10529 | 0.054932 | 61.4914 | 61.4777 | 123.5733 | 123.8342 | -0.10986 | 123.848 | 61.441 | -0.22888 | 123.8342 | -0.10986 | 61.441 | 123.5733 | 123.848 | -124.118 | -124.1821
584.7188 | 124.086 | -61.3953 | 62.5488 | 0.082626 | 0.0076925 | 0.010423 | 0.003561 | 0.06687 | -0.0020421 | 0.067086 | -61.4548 | 62.5031 | -61.5463 | -61.5692 | 62.1918 | 0 | 0.022888 | 0.027466 | 62.4893 | -61.6241 | -0.15106 | -0.045776 | -0.059509 | -0.17395 | -0.35706 | -0.22888 | -0.059509 | 0.091553 | 61.4182 | 61.4227 | 123.587 | 123.8983 | -0.059509 | 123.8846 | 61.3953 | -0.22888 | 123.8983 | -0.059509 | 61.3953 | 123.587 | 123.8846 | -124.0952 | -124.173
585.7188 | 124.0997 | -61.377 | 62.5259 | -0.19203 | 0.0089743 | 0.0082864 | -0.00028416 | 0.066657 | -0.0011877 | 0.070718 | -61.441 | 62.4985 | -61.5463 | -61.5463 | 62.2284 | 0.091553 | 0.11444 | 0.12817 | 62.5076 | -61.6013 | -0.16937 | -0.027466 | -0.064087 | -0.16937 | -0.29755 | -0.2243 | -0.018311 | 0.10529 | 61.4914 | 61.5051 | 123.6053 | 123.8754 | -0.064087 | 123.8846 | 61.4685 | -0.2243 | 123.8754 | -0.064087 | 61.4685 | 123.6053 | 123.8846 | -124.0723 | -124.1272
586.7188 | 124.1272 | -61.3678 | 62.5534 | -0.23781 | 0.0070517 | 0.0095682 | 0.00078404 | 0.067939 | -0.0014013 | 0.0673 | -61.4594 | 62.5031 | -61.5372 | -61.5555 | 62.233 | 0.091553 | 0.11902 | 0.1236 | 62.4847 | -61.5738 | -0.16937 | -0.050354 | -0.091553 | -0.18768 | -0.32044 | -0.20599 | -0.068665 | 0.077819 | 61.4868 | 61.4914 | 123.6008 | 123.8708 | -0.091553 | 123.8525 | 61.4594 | -0.20599 | 123.8708 | -0.091553 | 61.4594 | 123.6008 | 123.8525 | -124.0906 | -124.1272
587.7188 | 124.0906 | -61.3907 | 62.5626 | -0.20729 | 0.0070517 | 0.007432 | 0.0016384 | 0.067939 | -0.00076053 | 0.065804 | -61.4502 | 62.4939 | -61.5417 | -61.5738 | 62.2375 | 0.073242 | 0.1236 | 0.11902 | 62.4985 | -61.5738 | -0.15106 | -0.068665 | -0.059509 | -0.18311 | -0.32501 | -0.18311 | -0.064087 | 0.091553 | 61.5143 | 61.5097 | 123.6282 | 123.8846 | -0.059509 | 123.8892 | 61.4639 | -0.18311 | 123.8846 | -0.059509 | 61.4639 | 123.6282 | 123.8892 | -124.1043 | -124.1364
588.7188 | 124.0906 | -61.3815 | 62.5671 | -0.24544 | 0.0072653 | 0.0089274 | -0.00049776 | 0.066657 | -0.0016149 | 0.068368 | -61.4822 | 62.4985 | -61.5555 | -61.5784 | 62.2238 | 0.086975 | 0.12817 | 0.091553 | 62.5076 | -61.5875 | -0.17395 | -0.068665 | -0.10071 | -0.19684 | -0.34332 | -0.20599 | -0.05951 | 0.073242 | 61.5097 | 61.4731 | 123.6053 | 123.88 | -0.10071 | 123.8892 | 61.4685 | -0.20599 | 123.88 | -0.10071 | 61.4685 | 123.6053 | 123.8892 | -124.1226 | -124.1547
589.7188 | 124.1089 | -61.3586 | 62.5305 | 0.11314 | 0.0085471 | 0.010423 | -7.0562e-05 | 0.067511 | -0.0018285 | 0.070077 | -61.4822 | 62.4664 | -61.5646 | -61.6013 | 62.1964 | -0.013733 | -0.027466 | -0.013733 | 62.4619 | -61.615 | -0.20599 | -0.064087 | -0.1236 | -0.24261 | -0.33417 | -0.25635 | -0.068665 | 0.082397 | 61.3312 | 61.3449 | 123.555 | 123.8251 | -0.1236 | 123.8205 | 61.3449 | -0.25635 | 123.8251 | -0.1236 | 61.3449 | 123.555 | 123.8205 | -124.0952 | -124.1455
590.7188 | 124.0814 | -61.3724 | 62.558 | -0.21492 | 0.0040609 | 0.0063638 | -0.0034886 | 0.067725 | -0.0024695 | 0.070077 | -61.4456 | 62.4756 | -61.5143 | -61.5372 | 62.2513 | 0.10529 | 0.10986 | 0.13275 | 62.4985 | -61.5509 | -0.14191 | -0.082397 | -0.073243 | -0.1648 | -0.3067 | -0.17853 | -0.059509 | 0.068664 | 61.4822 | 61.5051 | 123.6237 | 123.848 | -0.073243 | 123.8708 | 61.4777 | -0.17853 | 123.848 | -0.073243 | 61.4777 | 123.6237 | 123.8708 | -124.0723 | -124.1089
591.7188 | 124.0585 | -61.3586 | 62.558 | -0.20729 | 0.0061971 | 0.007432 | -0.0019932 | 0.067084 | -0.00011953 | 0.070718 | -61.4914 | 62.4893 | -61.528 | -61.615 | 62.2833 | 0.068665 | 0.12817 | 0.13733 | 62.5168 | -61.5921 | -0.16937 | -0.068664 | -0.13275 | -0.25635 | -0.27466 | -0.23346 | -0.041198 | 0.036621 | 61.4868 | 61.496 | 123.642 | 123.848 | -0.13275 | 123.8754 | 61.4273 | -0.23346 | 123.848 | -0.13275 | 61.4273 | 123.642 | 123.8754 | -124.086 | -124.1501
592.7188 | 124.1226 | -61.3815 | 62.558 | -0.23018 | 0.0083333 | 0.005723 | 0.0016384 | 0.066016 | -0.0018285 | 0.068368 | -61.4731 | 62.4893 | -61.5417 | -61.5829 | 62.2284 | 0.086975 | 0.11444 | 0.10529 | 62.4893 | -61.5738 | -0.16022 | -0.068664 | -0.091552 | -0.20142 | -0.32959 | -0.19226 | -0.068664 | 0.068665 | 61.496 | 61.4868 | 123.6099 | 123.8709 | -0.091552 | 123.8709 | 61.4685 | -0.19226 | 123.8709 | -0.091552 | 61.4685 | 123.6099 | 123.8709 | -124.0997 | -124.1318
593.7188 | 124.0768 | -61.3907 | 62.5671 | -0.36751 | 0.0059835 | 0.012559 | 0.00078404 | 0.064307 | -0.0011877 | 0.0673 | -61.4639 | 62.4939 | -61.5143 | -61.5784 | 62.2192 | 0.091553 | 0.14648 | 0.10529 | 62.5122 | -61.6013 | -0.1236 | -0.073243 | -0.073242 | -0.18768 | -0.3479 | -0.21057 | -0.054932 | 0.050354 | 61.5372 | 61.496 | 123.6099 | 123.8846 | -0.073242 | 123.9029 | 61.4822 | -0.21057 | 123.8846 | -0.073242 | 61.4822 | 123.6099 | 123.9029 | -124.0814 | -124.1684
594.7188 | 124.0906 | -61.3953 | 62.5214 | 0.021591 | 0.0094015 | 0.011064 | 0.0037746 | 0.068152 | -0.00097413 | 0.067513 | -61.4456 | 62.4939 | -61.5234 | -61.5692 | 62.2101 | 0.018311 | 0.027466 | 0.045776 | 62.4664 | -61.6013 | -0.12817 | -0.027466 | -0.050354 | -0.17395 | -0.31128 | -0.20599 | -0.054931 | 0.077819 | 61.4227 | 61.441 | 123.6053 | 123.8892 | -0.050354 | 123.8617 | 61.4136 | -0.20599 | 123.8892 | -0.050354 | 61.4136 | 123.6053 | 123.8617 | -124.0448 | -124.1226
595.7188 | 124.0631 | -61.3724 | 62.5442 | -0.27596 | 0.0057699 | 0.007432 | -0.001566 | 0.065802 | -0.00054693 | 0.068795 | -61.4914 | 62.4756 | -61.5417 | -61.7065 | 62.1414 | 0.10529 | 0.10529 | 0.07782 | 62.4985 | -61.5738 | -0.16937 | -0.068664 | -0.11902 | -0.33417 | -0.40283 | -0.20142 | -0.045776 | 0.050354 | 61.4777 | 61.4502 | 123.5138 | 123.848 | -0.11902 | 123.8708 | 61.4777 | -0.20142 | 123.848 | -0.11902 | 61.4777 | 123.5138 | 123.8708 | -124.086 | -124.118
596.7188 | 123.9899 | -61.3495 | 62.5442 | -0.1844 | 0.0055563 | 0.010209 | -0.0019932 | 0.064948 | -0.0014013 | 0.068795 | -61.4639 | 62.4939 | -61.5509 | -61.5555 | 62.2375 | 0.10071 | 0.13275 | 0.21057 | 62.4847 | -61.5326 | -0.20142 | -0.050354 | -0.11444 | -0.20599 | -0.3067 | -0.18311 | -0.059509 | 0.086975 | 61.4822 | 61.5601 | 123.587 | 123.8434 | -0.11444 | 123.8342 | 61.4502 | -0.18311 | 123.8434 | -0.11444 | 61.4502 | 123.587 | 123.8342 | -124.0952 | -124.0768
597.7188 | 124.1455 | -61.3586 | 62.5442 | -0.17677 | 0.0059835 | 0.0078592 | -0.0045566 | 0.066016 | -0.0016149 | 0.069009 | -61.4136 | 62.4298 | -61.5005 | -61.496 | 62.3016 | 0.16479 | 0.041199 | 0.21973 | 62.4573 | -61.5417 | -0.14191 | -0.11444 | -0.054931 | -0.13733 | -0.24261 | -0.1831 | -0.086975 | 0.086975 | 61.3998 | 61.5784 | 123.6603 | 123.7885 | -0.054931 | 123.8159 | 61.5234 | -0.1831 | 123.7885 | -0.054931 | 61.5234 | 123.6603 | 123.8159 | -124.0448 | -124.086
598.7188 | 124.118 | -61.3586 | 62.5442 | -0.29884 | 0.0034201 | 0.0044412 | -0.0017796 | 0.063025 | -0.00076053 | 0.068368 | -61.4548 | 62.4664 | -61.5143 | -61.5555 | 62.2375 | 0.09613 | 0.12817 | 0.14191 | 62.4893 | -61.5463 | -0.15564 | -0.077819 | -0.09613 | -0.19684 | -0.3067 | -0.18768 | -0.054931 | 0.059509 | 61.4868 | 61.5006 | 123.5962 | 123.8251 | -0.09613 | 123.848 | 61.4548 | -0.18768 | 123.8251 | -0.09613 | 61.4548 | 123.5962 | 123.848 | -124.0585 | -124.0906
599.7188 | 124.118 | -61.3815 | 62.5397 | 0.30388 | 0.0066245 | 0.011277 | 0.005911 | 0.066016 | -0.0035375 | 0.0673 | -61.3678 | 62.4985 | -61.5601 | -61.5051 | 62.2696 | 0.10071 | 0.009155 | 0.13733 | 62.4939 | -61.6013 | -0.17853 | -0.041199 | 0.013733 | -0.1236 | -0.27008 | -0.21973 | -0.045777 | 0.19226 | 61.3907 | 61.5189 | 123.6511 | 123.88 | 0.013733 | 123.8754 | 61.4822 | -0.21973 | 123.88 | 0.013733 | 61.4822 | 123.6511 | 123.8754 | -124.0997 | -124.1409
600.7188 | 123.9944 | -61.3312 | 62.5534 | -0.2607 | 0.0066245 | 0.0085 | -0.0017796 | 0.064948 | -0.0018285 | 0.069009 | -61.4731 | 62.4619 | -61.5417 | -61.5692 | 62.2192 | 0.09613 | 0.15106 | 0.25177 | 62.5305 | -61.5509 | -0.21057 | -0.091553 | -0.14191 | -0.23804 | -0.33417 | -0.21973 | -0.022888 | 0.068665 | 61.4822 | 61.5829 | 123.5504 | 123.793 | -0.14191 | 123.8617 | 61.4273 | -0.21973 | 123.793 | -0.14191 | 61.4273 | 123.5504 | 123.8617 | -124.0952 | -124.1043
601.7188 | 124.0768 | -61.3541 | 62.5809 | -0.23018 | 0.0072653 | 0.0085 | -0.00071136 | 0.065802 | -0.00033333 | 0.068795 | -61.4731 | 62.471 | -61.5601 | -61.5738 | 62.2192 | 0.09613 | 0.14191 | 0.1236 | 62.5031 | -61.5555 | -0.20599 | -0.10986 | -0.11902 | -0.21973 | -0.36163 | -0.20142 | -0.07782 | 0.086976 | 61.496 | 61.4777 | 123.5733 | 123.8251 | -0.11902 | 123.8571 | 61.4502 | -0.20142 | 123.8251 | -0.11902 | 61.4502 | 123.5733 | 123.8571 | -124.1409 | -124.1364
602.7188 | 124.0952 | -61.3678 | 62.5626 | -0.19203 | 0.0057699 | 0.0063638 | -0.00028416 | 0.065375 | -0.0031103 | 0.0673 | -61.4868 | 62.4664 | -61.5326 | -61.5555 | 62.2421 | 0.086975 | 0.10986 | 0.13275 | 62.471 | -61.5509 | -0.16479 | -0.09613 | -0.11902 | -0.18768 | -0.32044 | -0.1831 | -0.091553 | 0.045777 | 61.4777 | 61.5005 | 123.6099 | 123.8342 | -0.11902 | 123.8388 | 61.4548 | -0.1831 | 123.8342 | -0.11902 | 61.4548 | 123.6099 | 123.8388 | -124.0952 | -124.1135
603.7188 | 124.1867 | -61.3541 | 62.5214 | -0.11574 | 0.0034201 | 0.0097818 | -0.0034886 | 0.065375 | -0.00076053 | 0.0673 | -61.4044 | 62.4023 | -61.5097 | -61.4731 | 62.3245 | 0.1831 | -0.004578 | 0.23346 | 62.4527 | -61.5463 | -0.15564 | -0.11902 | -0.050354 | -0.11902 | -0.19684 | -0.19226 | -0.068664 | 0.10529 | 61.3495 | 61.5875 | 123.6786 | 123.7564 | -0.050354 | 123.8068 | 61.5372 | -0.19226 | 123.7564 | -0.050354 | 61.5372 | 123.6786 | 123.8068 | -124.0311 | -124.0677
604.7188 | 124.086 | -61.3449 | 62.5671 | -0.16914 | 0.0059835 | 0.011064 | 0.0031338 | 0.065802 | 0.00030767 | 0.067513 | -61.4685 | 62.4985 | -61.5417 | -61.5509 | 62.2192 | 0.091553 | 0.11902 | 0.11902 | 62.471 | -61.6013 | -0.19684 | -0.068665 | -0.1236 | -0.20599 | -0.3479 | -0.25635 | -0.096131 | 0.073242 | 61.4639 | 61.4639 | 123.5641 | 123.8434 | -0.1236 | 123.8159 | 61.4365 | -0.25635 | 123.8434 | -0.1236 | 61.4365 | 123.5641 | 123.8159 | -124.1089 | -124.1684
605.7188 | 124.118 | -61.377 | 62.5488 | -0.2607 | 0.0055563 | 0.0078592 | -0.0032748 | 0.06623 | -0.0011877 | 0.068368 | -61.4182 | 62.4115 | -61.5417 | -61.5189 | 62.2833 | 0.13733 | 0.07782 | 0.17395 | 62.4756 | -61.528 | -0.16479 | -0.13733 | -0.041199 | -0.14191 | -0.2655 | -0.15106 | -0.073242 | 0.1236 | 61.4548 | 61.5509 | 123.6603 | 123.7885 | -0.041199 | 123.8525 | 61.5143 | -0.15106 | 123.7885 | -0.041199 | 61.5143 | 123.6603 | 123.8525 | -124.0906 | -124.0768
606.7188 | 124.0768 | -61.3358 | 62.59 | -0.21492 | 0.0057699 | 0.0078592 | -0.0011386 | 0.064948 | -0.0018285 | 0.067086 | -61.4731 | 62.471 | -61.5189 | -61.5509 | 62.233 | 0.07782 | 0.14648 | 0.11902 | 62.4985 | -61.5738 | -0.18311 | -0.11902 | -0.13733 | -0.21515 | -0.35706 | -0.23804 | -0.091553 | 0.045777 | 61.4822 | 61.4548 | 123.5687 | 123.8068 | -0.13733 | 123.8342 | 61.4136 | -0.23804 | 123.8068 | -0.13733 | 61.4136 | 123.5687 | 123.8342 | -124.1089 | -124.1638
607.7188 | 124.0723 | -61.3953 | 62.5397 | 0.0063326 | 0.0081197 | 0.0093546 | 0.0037746 | 0.069007 | -0.0043921 | 0.069009 | -61.4594 | 62.4939 | -61.5372 | -61.5601 | 62.2009 | 0.018311 | 0.041199 | 0.032043 | 62.4802 | -61.6058 | -0.14191 | -0.045777 | -0.064087 | -0.1648 | -0.33875 | -0.21057 | -0.059509 | 0.077819 | 61.4365 | 61.4273 | 123.5962 | 123.8892 | -0.064087 | 123.8754 | 61.4136 | -0.21057 | 123.8892 | -0.064087 | 61.4136 | 123.5962 | 123.8754 | -124.0768 | -124.1455
608.7188 | 124.0723 | -61.3541 | 62.5626 | -0.22255 | 0.0066245 | 0.0095682 | -0.0028476 | 0.067939 | -0.0024695 | 0.069436 | -61.4594 | 62.471 | -61.5097 | -61.5646 | 62.2604 | 0.09613 | 0.14191 | 0.12817 | 62.4985 | -61.5601 | -0.15564 | -0.091553 | -0.10529 | -0.21057 | -0.30212 | -0.20599 | -0.064087 | 0.050354 | 61.496 | 61.4822 | 123.6145 | 123.8251 | -0.10529 | 123.8525 | 61.4502 | -0.20599 | 123.8251 | -0.10529 | 61.4502 | 123.6145 | 123.8525 | -124.0723 | -124.1226
609.7188 | 124.0997 | -61.3678 | 62.5351 | -0.13863 | 0.0070517 | 0.0082864 | 0.004202 | 0.066016 | -0.00033333 | 0.067941 | -61.4044 | 62.4664 | -61.5143 | -61.5143 | 62.2467 | 0.091553 | 0.022888 | 0.10986 | 62.471 | -61.615 | -0.14648 | -0.068664 | -0.036621 | -0.14648 | -0.28839 | -0.24719 | -0.064087 | 0.10986 | 61.3907 | 61.4777 | 123.6145 | 123.8342 | -0.036621 | 123.8388 | 61.4594 | -0.24719 | 123.8342 | -0.036621 | 61.4594 | 123.6145 | 123.8388 | -124.0494 | -124.1501
610.7188 | 124.1821 | -61.3632 | 62.5259 | -0.13863 | 0.0038473 | 0.0048684 | -0.0051974 | 0.066443 | -0.0011877 | 0.068795 | -61.3953 | 62.4207 | -61.5189 | -61.4685 | 62.3337 | 0.19226 | -0.013733 | 0.22888 | 62.4527 | -61.5326 | -0.15564 | -0.10529 | -0.032044 | -0.10529 | -0.19226 | -0.16937 | -0.073242 | 0.1236 | 61.3495 | 61.5921 | 123.6969 | 123.7839 | -0.032044 | 123.8159 | 61.5555 | -0.16937 | 123.7839 | -0.032044 | 61.5555 | 123.6969 | 123.8159 | -124.0448 | -124.0585
611.7188 | 124.0723 | -61.3678 | 62.558 | -0.21492 | 0.0055563 | 0.0065774 | 0.00014304 | 0.065802 | -0.00076053 | 0.069863 | -61.4319 | 62.4527 | -61.5005 | -61.5234 | 62.2696 | 0.12817 | 0.09613 | 0.16937 | 62.4893 | -61.5692 | -0.13275 | -0.10529 | -0.064087 | -0.15564 | -0.28839 | -0.20142 | -0.068664 | 0.068664 | 61.4639 | 61.5372 | 123.6374 | 123.8205 | -0.064087 | 123.8571 | 61.496 | -0.20142 | 123.8205 | -0.064087 | 61.496 | 123.6374 | 123.8571 | -124.0585 | -124.1272
612.7188 | 124.0997 | -61.3861 | 62.5305 | -0.016556 | 0.0085471 | 0.01085 | 0.0044156 | 0.067725 | -0.0026831 | 0.068795 | -61.4273 | 62.4573 | -61.5097 | -61.5326 | 62.2284 | 0.050354 | 0.032043 | 0.064087 | 62.471 | -61.5967 | -0.1236 | -0.073243 | -0.041199 | -0.14648 | -0.30212 | -0.21057 | -0.05951 | 0.082398 | 61.4182 | 61.4502 | 123.6145 | 123.8434 | -0.041199 | 123.8571 | 61.4365 | -0.21057 | 123.8434 | -0.041199 | 61.4365 | 123.6145 | 123.8571 | -124.0402 | -124.1272
613.7188 | 124.0906 | -61.3541 | 62.5763 | -0.2607 | 0.0070517 | 0.0080728 | -7.0562e-05 | 0.064734 | -0.0014013 | 0.067941 | -61.4685 | 62.4893 | -61.5326 | -61.5692 | 62.2421 | 0.073242 | 0.16479 | 0.1236 | 62.5122 | -61.5692 | -0.17853 | -0.086975 | -0.11444 | -0.21515 | -0.33417 | -0.21515 | -0.064087 | 0.064087 | 61.5189 | 61.4777 | 123.5962 | 123.8434 | -0.11444 | 123.8663 | 61.4273 | -0.21515 | 123.8434 | -0.11444 | 61.4273 | 123.5962 | 123.8663 | -124.1089 | -124.1455
614.7188 | 124.1135 | -61.3724 | 62.5488 | -0.131 | 0.0055563 | 0.0082864 | 0.001852 | 0.067511 | -0.0011877 | 0.068582 | -61.3953 | 62.4802 | -61.5143 | -61.5189 | 62.265 | 0.086975 | 0.027466 | 0.13275 | 62.471 | -61.5829 | -0.14191 | -0.068664 | -0.022889 | -0.14648 | -0.28381 | -0.21057 | -0.07782 | 0.11902 | 61.3998 | 61.5051 | 123.6374 | 123.8525 | -0.022889 | 123.8434 | 61.4594 | -0.21057 | 123.8525 | -0.022889 | 61.4594 | 123.6374 | 123.8434 | -124.0631 | -124.1318
615.7188 | 124.0906 | -61.3632 | 62.5214 | -0.20729 | 0.0066245 | 0.0078592 | -0.0030612 | 0.067298 | -0.0011877 | 0.067727 | -61.4685 | 62.4664 | -61.5326 | -61.5646 | 62.2513 | 0.091553 | 0.13275 | 0.12817 | 62.4939 | -61.5601 | -0.16937 | -0.054931 | -0.10529 | -0.20142 | -0.27008 | -0.19684 | -0.027466 | 0.064087 | 61.496 | 61.4914 | 123.6145 | 123.8297 | -0.10529 | 123.8571 | 61.4548 | -0.19684 | 123.8297 | -0.10529 | 61.4548 | 123.6145 | 123.8571 | -124.054 | -124.0814
616.7188 | 124.0814 | -61.3861 | 62.5763 | -0.30647 | 0.0064107 | 0.016404 | -0.0019932 | 0.065802 | -0.0018285 | 0.069436 | -61.4365 | 62.471 | -61.5005 | -61.5372 | 62.265 | 0.10986 | 0.12817 | 0.14648 | 62.4802 | -61.5555 | -0.11444 | -0.10529 | -0.050354 | -0.15106 | -0.31128 | -0.16937 | -0.09613 | 0.064087 | 61.5143 | 61.5326 | 123.6511 | 123.8571 | -0.050354 | 123.8663 | 61.496 | -0.16937 | 123.8571 | -0.050354 | 61.496 | 123.6511 | 123.8663 | -124.0768 | -124.1318
617.7188 | 124.1913 | -61.3495 | 62.4893 | 0.19707 | 0.0049155 | 0.010423 | -7.0562e-05 | 0.067084 | -0.0026831 | 0.069222 | -61.409 | 62.4344 | -61.5417 | -61.5005 | 62.2696 | 0.082397 | -0.15564 | 0.10071 | 62.4023 | -61.5829 | -0.19226 | -0.054932 | -0.05951 | -0.15106 | -0.21973 | -0.23346 | -0.086975 | 0.13275 | 61.1938 | 61.4502 | 123.6191 | 123.7839 | -0.05951 | 123.7518 | 61.4319 | -0.23346 | 123.7839 | -0.05951 | 61.4319 | 123.6191 | 123.7518 | -124.0311 | -124.0723
618.7188 | 124.1226 | -61.3495 | 62.5488 | -0.2607 | 0.0068381 | 0.005723 | -0.0017796 | 0.065375 | -0.0016149 | 0.068154 | -61.4136 | 62.4161 | -61.5326 | -61.5326 | 62.2787 | 0.14191 | 0.10529 | 0.19226 | 62.4527 | -61.5463 | -0.18311 | -0.13275 | -0.064087 | -0.18311 | -0.27008 | -0.19684 | -0.09613 | 0.11902 | 61.4548 | 61.5417 | 123.6282 | 123.7656 | -0.064087 | 123.8022 | 61.4914 | -0.19684 | 123.7656 | -0.064087 | 61.4914 | 123.6282 | 123.8022 | -124.0814 | -124.0952
619.7188 | 124.1318 | -61.3541 | 62.5397 | -0.27596 | 0.0038473 | 0.0055094 | -0.0017796 | 0.065589 | -0.0018285 | 0.066873 | -61.4182 | 62.4207 | -61.5189 | -61.4914 | 62.2879 | 0.15564 | 0.068665 | 0.21515 | 62.471 | -61.5509 | -0.16479 | -0.11902 | -0.064087 | -0.13733 | -0.25177 | -0.19684 | -0.068665 | 0.10071 | 61.4227 | 61.5692 | 123.642 | 123.7747 | -0.064087 | 123.8251 | 61.5097 | -0.19684 | 123.7747 | -0.064087 | 61.5097 | 123.642 | 123.8251 | -124.0585 | -124.0906
620.7188 | 124.1043 | -61.3724 | 62.5763 | -0.4438 | 0.0070517 | 0.0055094 | -7.0562e-05 | 0.063452 | -0.00076053 | 0.068154 | -61.4731 | 62.4802 | -61.5372 | -61.5463 | 62.2192 | 0.086975 | 0.14191 | 0.12817 | 62.4756 | -61.5463 | -0.1648 | -0.09613 | -0.10071 | -0.17395 | -0.35706 | -0.17395 | -0.10071 | 0.064087 | 61.5143 | 61.5005 | 123.5916 | 123.8525 | -0.10071 | 123.848 | 61.4594 | -0.17395 | 123.8525 | -0.10071 | 61.4594 | 123.5916 | 123.848 | -124.1135 | -124.1226
621.7188 | 124.0768 | -61.3815 | 62.5488 | 0.2047 | 0.0061971 | 0.0080728 | 0.0022794 | 0.065161 | -0.00097413 | 0.068154 | -61.5875 | 62.4756 | -61.5601 | -61.5829 | 62.2742 | 0.10986 | 0.14648 | 0.10986 | 62.5031 | -61.6013 | -0.17853 | -0.073242 | -0.20599 | -0.20142 | -0.27466 | -0.21973 | -0.045776 | -0.027465 | 61.528 | 61.4914 | 123.6557 | 123.8571 | -0.20599 | 123.8846 | 61.4914 | -0.21973 | 123.8571 | -0.20599 | 61.4914 | 123.6557 | 123.8846 | -124.1089 | -124.1501
622.7188 | 124.205 | -61.3083 | 62.4847 | 0.19707 | 0.0047019 | 0.0089274 | 0.00057044 | 0.069007 | -0.0020421 | 0.068368 | -61.4273 | 62.3932 | -61.5509 | -61.5097 | 62.2696 | 0.07782 | -0.17395 | 0.10986 | 62.3932 | -61.5601 | -0.24261 | -0.091553 | -0.11902 | -0.20142 | -0.21515 | -0.25177 | -0.091553 | 0.1236 | 61.1343 | 61.4182 | 123.5779 | 123.7015 | -0.11902 | 123.7015 | 61.3861 | -0.25177 | 123.7015 | -0.11902 | 61.3861 | 123.5779 | 123.7015 | -124.0356 | -124.0448
623.7188 | 124.1135 | -61.3403 | 62.558 | -0.21492 | 0.0076925 | 0.0085 | -0.0019932 | 0.064948 | -0.0033239 | 0.068582 | -61.4227 | 62.4435 | -61.528 | -61.5005 | 62.2787 | 0.14191 | 0.091553 | 0.1831 | 62.4527 | -61.5372 | -0.18768 | -0.11444 | -0.082397 | -0.16022 | -0.27923 | -0.19684 | -0.10529 | 0.10529 | 61.4319 | 61.5234 | 123.6191 | 123.7839 | -0.082397 | 123.793 | 61.4822 | -0.19684 | 123.7839 | -0.082397 | 61.4822 | 123.6191 | 123.793 | -124.086 | -124.0952
624.7188 | 124.1135 | -61.3541 | 62.5717 | -0.16914 | 0.0066245 | 0.012345 | 0.0050564 | 0.066657 | 9.4068e-05 | 0.069222 | -61.4227 | 62.5214 | -61.5097 | -61.5005 | 62.2742 | 0.10529 | 0.082397 | 0.14648 | 62.4756 | -61.5784 | -0.15564 | -0.050354 | -0.068664 | -0.14648 | -0.29755 | -0.2243 | -0.09613 | 0.086976 | 61.4365 | 61.5005 | 123.6282 | 123.8754 | -0.068664 | 123.8297 | 61.4594 | -0.2243 | 123.8754 | -0.068664 | 61.4594 | 123.6282 | 123.8297 | -124.0814 | -124.1501
625.7188 | 124.1547 | -61.322 | 62.5442 | -0.22255 | 0.0061971 | 0.0087138 | -0.00028416 | 0.065161 | -0.0024695 | 0.069222 | -61.3998 | 62.4435 | -61.5097 | -61.4868 | 62.3154 | 0.15106 | 0.018311 | 0.2243 | 62.4664 | -61.5326 | -0.18768 | -0.10071 | -0.07782 | -0.16479 | -0.22888 | -0.21057 | -0.077819 | 0.10986 | 61.3403 | 61.5463 | 123.6374 | 123.7656 | -0.07782 | 123.7885 | 61.4731 | -0.21057 | 123.7656 | -0.07782 | 61.4731 | 123.6374 | 123.7885 | -124.054 | -124.0768
626.7188 | 124.0997 | -61.3586 | 62.5717 | -0.22255 | 0.0064107 | 0.0082864 | -0.00092496 | 0.065589 | -0.00097413 | 0.070077 | -61.441 | 62.4802 | -61.5097 | -61.5417 | 62.2375 | 0.10071 | 0.13275 | 0.15564 | 62.4802 | -61.5555 | -0.15106 | -0.091552 | -0.082397 | -0.1831 | -0.33417 | -0.19684 | -0.091552 | 0.068665 | 61.4914 | 61.5143 | 123.5962 | 123.8388 | -0.082397 | 123.8388 | 61.4594 | -0.19684 | 123.8388 | -0.082397 | 61.4594 | 123.5962 | 123.8388 | -124.0814 | -124.1272
627.7188 | 124.0585 | -61.3449 | 62.5763 | -0.21492 | 0.0066245 | 0.007432 | -0.0034886 | 0.064307 | -0.0020421 | 0.067941 | -61.4227 | 62.4527 | -61.5372 | -61.5189 | 62.265 | 0.12817 | 0.10071 | 0.17853 | 62.4847 | -61.5509 | -0.19226 | -0.1236 | -0.077819 | -0.17395 | -0.31128 | -0.20599 | -0.091553 | 0.11444 | 61.4456 | 61.5234 | 123.6099 | 123.7976 | -0.077819 | 123.8297 | 61.4731 | -0.20599 | 123.7976 | -0.077819 | 61.4731 | 123.6099 | 123.8297 | -124.1135 | -124.1272
628.7188 | 124.1364 | -61.3403 | 62.5534 | -0.24544 | 0.0021383 | 0.0061502 | -0.00092496 | 0.066657 | -0.0041785 | 0.068154 | -61.4136 | 62.4619 | -61.496 | -61.5005 | 62.2879 | 0.1236 | 0.09613 | 0.17395 | 62.4756 | -61.5372 | -0.15564 | -0.091553 | -0.073242 | -0.16022 | -0.2655 | -0.19684 | -0.07782 | 0.082398 | 61.4365 | 61.5143 | 123.6282 | 123.8022 | -0.073242 | 123.8159 | 61.4639 | -0.19684 | 123.8022 | -0.073242 | 61.4639 | 123.6282 | 123.8159 | -124.0494 | -124.0906
629.7188 | 124.0768 | -61.3861 | 62.558 | 0.03685 | 0.0089743 | 0.011064 | 0.0054836 | 0.066443 | -0.0026831 | 0.066659 | -61.4594 | 62.4985 | -61.5509 | -61.5692 | 62.1689 | -0.018311 | 0.054932 | 0.022888 | 62.4619 | -61.6104 | -0.16479 | -0.059509 | -0.073243 | -0.18311 | -0.3891 | -0.22431 | -0.09613 | 0.091552 | 61.441 | 61.409 | 123.555 | 123.8846 | -0.073243 | 123.848 | 61.3678 | -0.22431 | 123.8846 | -0.073243 | 61.3678 | 123.555 | 123.848 | -124.1089 | -124.1684
630.7188 | 124.118 | -61.3358 | 62.5626 | -0.27596 | 0.0057699 | 0.0063638 | -0.0019932 | 0.064734 | -0.0043921 | 0.069222 | -61.3998 | 62.439 | -61.5051 | -61.4777 | 62.3016 | 0.16479 | 0.068665 | 0.21515 | 62.4756 | -61.5189 | -0.16937 | -0.1236 | -0.064087 | -0.14191 | -0.26093 | -0.18311 | -0.086975 | 0.10529 | 61.4044 | 61.5509 | 123.6374 | 123.7747 | -0.064087 | 123.8113 | 61.5005 | -0.18311 | 123.7747 | -0.064087 | 61.5005 | 123.6374 | 123.8113 | -124.0677 | -124.0814
631.7188 | 124.2142 | -61.3083 | 62.5305 | -3.4498 | 0.0038473 | 0.0087138 | -0.00092496 | 0.067725 | -0.0024695 | 0.070077 | -61.4502 | 62.4573 | -61.4914 | -61.4594 | 62.3108 | 0.14191 | -0.022888 | 0.25177 | 62.4619 | -61.5417 | -0.1831 | -0.073243 | -0.14191 | -0.15106 | -0.21973 | -0.23346 | -0.068665 | 0.041199 | 61.2854 | 61.5601 | 123.6191 | 123.7656 | -0.14191 | 123.7701 | 61.4502 | -0.23346 | 123.7656 | -0.14191 | 61.4502 | 123.6191 | 123.7701 | -124.0219 | -124.0723
632.7188 | 124.1501 | -61.3358 | 62.5534 | -0.22255 | 0.0049155 | 0.0082864 | -0.00071136 | 0.063239 | -0.0018285 | 0.066873 | -61.3907 | 62.4023 | -61.5143 | -61.4777 | 62.3154 | 0.1831 | 0.004578 | 0.24719 | 62.4527 | -61.5372 | -0.17853 | -0.15106 | -0.054932 | -0.14191 | -0.23804 | -0.20142 | -0.10071 | 0.1236 | 61.3403 | 61.5829 | 123.6511 | 123.7381 | -0.054932 | 123.7885 | 61.5189 | -0.20142 | 123.7381 | -0.054932 | 61.5189 | 123.6511 | 123.7885 | -124.0677 | -124.0906
633.7188 | 124.1135 | -61.3586 | 62.5534 | -0.23781 | 0.0049155 | 0.0076456 | 0.00057044 | 0.066443 | -0.0014013 | 0.068154 | -61.4182 | 62.4298 | -61.5051 | -61.5234 | 62.2421 | 0.10529 | 0.13733 | 0.17853 | 62.4664 | -61.5509 | -0.14648 | -0.1236 | -0.059509 | -0.16479 | -0.31128 | -0.19226 | -0.086975 | 0.086975 | 61.496 | 61.5372 | 123.6008 | 123.7885 | -0.059509 | 123.8251 | 61.4639 | -0.19226 | 123.7885 | -0.059509 | 61.4639 | 123.6008 | 123.8251 | -124.0585 | -124.1043
634.7188 | 124.1409 | -61.3541 | 62.5351 | -0.14626 | 0.0066245 | 0.0085 | 0.0027066 | 0.067511 | -0.0026831 | 0.069009 | -61.528 | 62.4619 | -61.5555 | -61.4914 | 62.2421 | 0.10071 | 0.027466 | 0.14191 | 62.4527 | -61.5555 | -0.20142 | -0.073242 | -0.17395 | -0.13733 | -0.29297 | -0.20142 | -0.082397 | 0.027466 | 61.3815 | 61.496 | 123.5962 | 123.8159 | -0.17395 | 123.8068 | 61.4548 | -0.20142 | 123.8159 | -0.17395 | 61.4548 | 123.5962 | 123.8068 | -124.0906 | -124.0906
635.7188 | 124.1364 | -61.3358 | 62.5626 | -0.2607 | 0.0064107 | 0.0080728 | -0.0011386 | 0.065589 | -0.0024695 | 0.069436 | -61.4227 | 62.4252 | -61.5051 | -61.496 | 62.2971 | 0.15106 | 0.07782 | 0.19226 | 62.4619 | -61.528 | -0.16937 | -0.13733 | -0.086975 | -0.16022 | -0.2655 | -0.19226 | -0.10071 | 0.082398 | 61.4136 | 61.528 | 123.6328 | 123.761 | -0.086975 | 123.7976 | 61.4868 | -0.19226 | 123.761 | -0.086975 | 61.4868 | 123.6328 | 123.7976 | -124.0677 | -124.0906
636.7188 | 124.1364 | -61.3449 | 62.5763 | -0.28358 | 0.0053427 | 0.010423 | -0.0017796 | 0.065589 | -0.0024695 | 0.071145 | -61.3998 | 62.4207 | -61.5005 | -61.4914 | 62.3154 | 0.15106 | 0.059509 | 0.21057 | 62.4344 | -61.5326 | -0.15564 | -0.15564 | -0.054931 | -0.14648 | -0.26093 | -0.18768 | -0.14191 | 0.10071 | 61.4044 | 61.5555 | 123.6603 | 123.7656 | -0.054931 | 123.7793 | 61.496 | -0.18768 | 123.7656 | -0.054931 | 61.496 | 123.6603 | 123.7793 | -124.0768 | -124.1089
637.7188 | 124.1364 | -61.322 | 62.5397 | -0.23018 | 0.0049155 | 0.0085 | -0.0030612 | 0.062812 | -0.0033239 | 0.065591 | -61.3953 | 62.4023 | -61.496 | -61.4639 | 62.3108 | 0.16022 | 0.027466 | 0.21973 | 62.4481 | -61.5326 | -0.17395 | -0.13733 | -0.073243 | -0.14191 | -0.22888 | -0.21057 | -0.091553 | 0.10071 | 61.3495 | 61.5417 | 123.6328 | 123.7244 | -0.073243 | 123.7701 | 61.4822 | -0.21057 | 123.7244 | -0.073243 | 61.4822 | 123.6328 | 123.7701 | -124.0356 | -124.0723
638.7188 | 124.2096 | -61.3266 | 62.5259 | -0.1844 | 0.0032065 | 0.007432 | 0.0037746 | 0.063239 | -0.0031103 | 0.067941 | -61.5417 | 62.4207 | -61.4822 | -61.5005 | 62.2421 | 0.17853 | -0.045776 | 0.21057 | 62.4527 | -61.496 | -0.15564 | -0.10529 | -0.21515 | -0.17395 | -0.28381 | -0.16937 | -0.073242 | -0.059509 | 61.2808 | 61.5372 | 123.5687 | 123.7473 | -0.21515 | 123.7793 | 61.5051 | -0.16937 | 123.7473 | -0.21515 | 61.5051 | 123.5687 | 123.7793 | -124.0082 | -124.0219
639.7188 | 124.1272 | -61.3632 | 62.5717 | -0.13863 | 0.0089743 | 0.0085 | 0.0037746 | 0.065589 | -0.0022559 | 0.069863 | -61.4548 | 62.5076 | -61.5143 | -61.528 | 62.2375 | 0.07782 | 0.13733 | 0.11902 | 62.4619 | -61.5784 | -0.15106 | -0.064087 | -0.091553 | -0.1648 | -0.33417 | -0.21515 | -0.10986 | 0.059509 | 61.5005 | 61.4822 | 123.6008 | 123.8708 | -0.091553 | 123.8251 | 61.441 | -0.21515 | 123.8708 | -0.091553 | 61.441 | 123.6008 | 123.8251 | -124.086 | -124.1501
640.7188 | 124.0311 | -61.3586 | 62.5259 | -0.19966 | 0.0038473 | 0.0087138 | 0.00035684 | 0.065589 | -0.0011877 | 0.067941 | -61.4685 | 62.4619 | -61.5463 | -61.5234 | 62.4802 | 0.25635 | -0.091553 | 0.086975 | 62.4893 | -61.5692 | -0.18768 | -0.064087 | -0.10986 | -0.16479 | -0.045776 | -0.21057 | -0.036621 | 0.07782 | 61.2671 | 61.4456 | 123.8388 | 123.8205 | -0.10986 | 123.848 | 61.615 | -0.21057 | 123.8205 | -0.10986 | 61.615 | 123.8388 | 123.848 | -124.0723 | -124.0952
641.7188 | 124.1409 | -61.3312 | 62.5626 | -0.23781 | 0.0049155 | 0.011064 | 0.0014248 | 0.065589 | -0.0052465 | 0.069222 | -61.3861 | 62.4344 | -61.496 | -61.4777 | 62.3062 | 0.16479 | 0.045776 | 0.21057 | 62.4573 | -61.5234 | -0.1648 | -0.12817 | -0.054931 | -0.14648 | -0.25635 | -0.19226 | -0.10529 | 0.10986 | 61.377 | 61.5417 | 123.6374 | 123.7656 | -0.054931 | 123.7885 | 61.496 | -0.19226 | 123.7656 | -0.054931 | 61.496 | 123.6374 | 123.7885 | -124.0585 | -124.086
642.7188 | 124.1776 | -61.322 | 62.5351 | -0.1844 | 0.0049155 | 0.0089274 | -0.0032748 | 0.06388 | -0.0037511 | 0.070077 | -61.3907 | 62.4023 | -61.5234 | -61.4685 | 62.3291 | 0.17853 | 0.013733 | 0.21973 | 62.4344 | -61.5189 | -0.20142 | -0.13275 | -0.068665 | -0.14648 | -0.20599 | -0.19684 | -0.10071 | 0.13275 | 61.3358 | 61.5417 | 123.6511 | 123.7244 | -0.068665 | 123.7564 | 61.5005 | -0.19684 | 123.7244 | -0.068665 | 61.5005 | 123.6511 | 123.7564 | -124.0585 | -124.054
643.7188 | 124.1638 | -61.322 | 62.5488 | -0.21492 | 0.0070517 | 0.0093546 | -0.00049776 | 0.062598 | -0.0014013 | 0.06965 | -61.3815 | 62.4023 | -61.4868 | -61.4548 | 62.3383 | 0.17853 | 0.009155 | 0.23346 | 62.4664 | -61.5097 | -0.16479 | -0.14648 | -0.05951 | -0.13275 | -0.21057 | -0.18768 | -0.082397 | 0.10528 | 61.3312 | 61.5555 | 123.6603 | 123.7244 | -0.05951 | 123.7885 | 61.5005 | -0.18768 | 123.7244 | -0.05951 | 61.5005 | 123.6603 | 123.7885 | -124.0356 | -124.0585
644.7188 | 124.1226 | -61.3358 | 62.5626 | -0.069961 | 0.0061971 | 0.011277 | 0.0039882 | 0.064948 | -0.0014013 | 0.067513 | -61.4044 | 62.5076 | -61.528 | -61.4914 | 62.2833 | 0.1236 | 0.054932 | 0.13275 | 62.4847 | -61.5692 | -0.19226 | -0.054932 | -0.068665 | -0.15564 | -0.27924 | -0.23346 | -0.07782 | 0.1236 | 61.3907 | 61.4685 | 123.6191 | 123.8434 | -0.068665 | 123.8205 | 61.4594 | -0.23346 | 123.8434 | -0.068665 | 61.4594 | 123.6191 | 123.8205 | -124.0906 | -124.1318
645.7188 | 124.2279 | -61.3037 | 62.5259 | -0.069961 | 0.0010703 | 0.0059366 | -0.0024204 | 0.065161 | -0.00076053 | 0.068795 | -61.3724 | 62.3795 | -61.5097 | -61.4319 | 62.3749 | 0.19226 | -0.07782 | 0.25635 | 62.439 | -61.5326 | -0.20599 | -0.14648 | -0.068664 | -0.12817 | -0.15106 | -0.22888 | -0.086975 | 0.13733 | 61.2259 | 61.5601 | 123.6786 | 123.6832 | -0.068664 | 123.7427 | 61.496 | -0.22888 | 123.6832 | -0.068664 | 61.496 | 123.6786 | 123.7427 | -124.0356 | -124.0585
646.7188 | 124.2142 | -61.2991 | 62.5488 | 0.65483 | 0.0051291 | 0.0076456 | 0.00014304 | 0.063025 | -0.0026831 | 0.067941 | -61.3815 | 62.3795 | -61.5372 | -61.4319 | 62.3474 | 0.17853 | -0.032043 | 0.23804 | 62.4344 | -61.528 | -0.23804 | -0.16937 | -0.082398 | -0.13275 | -0.20142 | -0.22888 | -0.11444 | 0.15564 | 61.2671 | 61.5372 | 123.6465 | 123.6786 | -0.082398 | 123.7335 | 61.4777 | -0.22888 | 123.6786 | -0.082398 | 61.4777 | 123.6465 | 123.7335 | -124.086 | -124.0768
647.7188 | 124.1638 | -61.322 | 62.5488 | -0.22255 | 0.0040609 | 0.0076456 | -0.00071136 | 0.063666 | -0.00097413 | 0.068795 | -61.3861 | 62.3978 | -61.4914 | -61.4548 | 62.3245 | 0.16937 | 0.018311 | 0.22888 | 62.4435 | -61.528 | -0.16937 | -0.15106 | -0.064087 | -0.13275 | -0.2243 | -0.20599 | -0.10529 | 0.10529 | 61.3403 | 61.5509 | 123.6465 | 123.7198 | -0.064087 | 123.7656 | 61.4914 | -0.20599 | 123.7198 | -0.064087 | 61.4914 | 123.6465 | 123.7656 | -124.0402 | -124.0768
648.7188 | 124.2004 | -61.3129 | 62.5442 | -0.1844 | 0.0053427 | 0.005723 | -0.00071136 | 0.064093 | -0.0041785 | 0.06965 | -61.377 | 62.4023 | -61.4822 | -61.4502 | 62.3337 | 0.16937 | -0.022888 | 0.24719 | 62.4298 | -61.5463 | -0.16937 | -0.14191 | -0.064087 | -0.13733 | -0.21057 | -0.23346 | -0.11444 | 0.10529 | 61.29 | 61.5601 | 123.6465 | 123.7152 | -0.064087 | 123.7427 | 61.4822 | -0.23346 | 123.7152 | -0.064087 | 61.4822 | 123.6465 | 123.7427 | -124.0265 | -124.0906
649.7188 | 124.1684 | -61.3174 | 62.5259 | -0.22255 | 0.0040609 | 0.0076456 | -7.0562e-05 | 0.06388 | -0.0011877 | 0.068582 | -61.3815 | 62.384 | -61.4868 | -61.4548 | 62.3245 | 0.18768 | -0.027466 | 0.23804 | 62.4344 | -61.5234 | -0.16937 | -0.14191 | -0.064087 | -0.13733 | -0.20142 | -0.20599 | -0.091553 | 0.10528 | 61.29 | 61.5555 | 123.642 | 123.7015 | -0.064087 | 123.7518 | 61.5051 | -0.20599 | 123.7015 | -0.064087 | 61.5051 | 123.642 | 123.7518 | -124.0128 | -124.0494
650.7188 | 124.2279 | -61.3174 | 62.5259 | -0.47432 | 0.0053427 | 0.0089274 | 0.0020656 | 0.064093 | -0.0022559 | 0.069009 | -61.3953 | 62.4023 | -61.5097 | -61.4273 | 62.352 | 0.20142 | -0.032043 | 0.24719 | 62.439 | -61.5372 | -0.19226 | -0.1236 | -0.07782 | -0.10986 | -0.17395 | -0.21973 | -0.086975 | 0.11444 | 61.2854 | 61.5646 | 123.6694 | 123.7198 | -0.07782 | 123.7564 | 61.5189 | -0.21973 | 123.7198 | -0.07782 | 61.5189 | 123.6694 | 123.7564 | -124.0356 | -124.0631
651.7188 | 124.173 | -61.3083 | 62.5442 | 0.10551 | 0.0074789 | 0.011704 | -0.0024204 | 0.063452 | -0.0018285 | 0.06965 | -61.5555 | 62.4023 | -61.5143 | -61.4639 | 62.352 | 0.19226 | -0.041199 | 0.24261 | 62.4252 | -61.5189 | -0.20599 | -0.14191 | -0.24719 | -0.15564 | -0.19226 | -0.21057 | -0.11902 | -0.041199 | 61.2671 | 61.5509 | 123.6603 | 123.7106 | -0.24719 | 123.7335 | 61.5006 | -0.21057 | 123.7106 | -0.24719 | 61.5006 | 123.6603 | 123.7335 | -124.0585 | -124.0631
652.7188 | 124.2096 | -61.2946 | 62.5488 | -0.039444 | 0.0051291 | 0.010209 | -0.00092496 | 0.062812 | -0.0011877 | 0.070504 | -61.3953 | 62.384 | -61.5097 | -61.4594 | 62.3199 | 0.17853 | -0.07782 | 0.23804 | 62.3978 | -61.5097 | -0.21515 | -0.16479 | -0.10071 | -0.16479 | -0.22888 | -0.21515 | -0.15106 | 0.11444 | 61.2167 | 61.5326 | 123.6145 | 123.6786 | -0.10071 | 123.6923 | 61.4731 | -0.21515 | 123.6786 | -0.10071 | 61.4731 | 123.6145 | 123.6923 | -124.0585 | -124.0585
653.7188 | 124.1638 | -61.3129 | 62.5168 | -0.21492 | 0.0029929 | 0.0052958 | -0.00028416 | 0.06153 | -0.0031103 | 0.068795 | -61.3495 | 62.3886 | -61.4868 | -61.496 | 62.6724 | 0.50812 | -0.3891 | 0.045776 | 62.4252 | -61.5189 | -0.17395 | -0.12817 | -0.036621 | -0.18311 | 0.15564 | -0.20599 | -0.091553 | 0.13733 | 60.9238 | 61.3586 | 123.9853 | 123.7015 | -0.036621 | 123.7381 | 61.821 | -0.20599 | 123.7015 | -0.036621 | 61.821 | 123.9853 | 123.7381 | -124.0036 | -124.0356
654.7188 | 124.118 | -61.322 | 62.5488 | -0.09285 | 0.0087607 | 0.011491 | 0.004202 | 0.064948 | -0.0020421 | 0.068795 | -61.5509 | 62.4802 | -61.5234 | -61.4914 | 62.2559 | 0.12817 | 0.004578 | 0.14648 | 62.4527 | -61.5692 | -0.20142 | -0.068664 | -0.22888 | -0.16937 | -0.29297 | -0.24719 | -0.09613 | -0.027466 | 61.3266 | 61.4685 | 123.5779 | 123.8022 | -0.22888 | 123.7747 | 61.4502 | -0.24719 | 123.8022 | -0.22888 | 61.4502 | 123.5779 | 123.7747 | -124.0723 | -124.118
655.7188 | 124.1776 | -61.2946 | 62.5351 | -0.14626 | 0.0034201 | 0.0070048 | -0.0011386 | 0.066443 | -0.00076053 | 0.067727 | -61.3815 | 62.4069 | -61.5051 | -61.4365 | 62.3428 | 0.20599 | -0.032043 | 0.24261 | 62.4344 | -61.496 | -0.21057 | -0.12817 | -0.086975 | -0.14191 | -0.19226 | -0.20142 | -0.10071 | 0.1236 | 61.2625 | 61.5372 | 123.6374 | 123.7015 | -0.086975 | 123.7289 | 61.5005 | -0.20142 | 123.7015 | -0.086975 | 61.5005 | 123.6374 | 123.7289 | -124.0402 | -124.0311
656.7188 | 124.1913 | -61.3129 | 62.5488 | -0.24544 | 0.0019247 | 0.0089274 | -0.00049776 | 0.063666 | -0.0022559 | 0.067941 | -61.4044 | 62.3886 | -61.4822 | -61.4182 | 62.3383 | 0.21515 | -0.036621 | 0.24719 | 62.4435 | -61.5051 | -0.16937 | -0.16022 | -0.091553 | -0.10529 | -0.21057 | -0.19226 | -0.10529 | 0.07782 | 61.2762 | 61.5601 | 123.6511 | 123.7015 | -0.091553 | 123.7564 | 61.528 | -0.19226 | 123.7015 | -0.091553 | 61.528 | 123.6511 | 123.7564 | -124.0311 | -124.054
657.7188 | 124.1821 | -61.3174 | 62.5626 | -1.5195 | 0.0040609 | 0.0087138 | -0.00071136 | 0.06388 | -0.0041785 | 0.066445 | -61.4731 | 62.3703 | -61.4777 | -61.4044 | 62.3566 | 0.21057 | -0.032043 | 0.25177 | 62.4298 | -61.5189 | -0.16022 | -0.19226 | -0.15564 | -0.086975 | -0.20599 | -0.20142 | -0.13275 | 0.004578 | 61.2854 | 61.5692 | 123.674 | 123.6877 | -0.15564 | 123.7473 | 61.528 | -0.20142 | 123.6877 | -0.15564 | 61.528 | 123.674 | 123.7473 | -124.0402 | -124.0814
658.7188 | 124.205 | -61.3129 | 62.5488 | -3.465 | 0.0038473 | 0.0097818 | 0.00035684 | 0.063239 | -0.0018285 | 0.067513 | -61.6287 | 62.4161 | -61.4914 | -61.4594 | 62.2879 | 0.21515 | -0.013733 | 0.25635 | 62.4207 | -61.5143 | -0.17853 | -0.13275 | -0.31586 | -0.14648 | -0.26093 | -0.20142 | -0.12817 | -0.13733 | 61.2991 | 61.5692 | 123.6008 | 123.7289 | -0.31586 | 123.7335 | 61.528 | -0.20142 | 123.7289 | -0.31586 | 61.528 | 123.6008 | 123.7335 | -124.0402 | -124.0631
659.7188 | 124.1043 | -61.3541 | 62.5626 | -0.23018 | 0.0051291 | 0.0065774 | 0.0039882 | 0.065375 | -0.00097413 | 0.066018 | -61.4136 | 62.5259 | -61.5189 | -61.4868 | 62.2559 | 0.10986 | 0.11902 | 0.14191 | 62.471 | -61.5601 | -0.16479 | -0.036621 | -0.059509 | -0.13275 | -0.3067 | -0.20599 | -0.091553 | 0.10529 | 61.4731 | 61.496 | 123.6099 | 123.88 | -0.059509 | 123.8251 | 61.4639 | -0.20599 | 123.88 | -0.059509 | 61.4639 | 123.6099 | 123.8251 | -124.0814 | -124.1226
660.7188 | 124.1821 | -61.3083 | 62.5259 | -0.20729 | 0.0042745 | 0.0061502 | 0.0027066 | 0.060889 | 9.4068e-05 | 0.068582 | -61.3541 | 62.4069 | -61.5005 | -61.6425 | 62.352 | 0.31586 | -0.19226 | 0.23804 | 62.4161 | -61.5005 | -0.19226 | -0.11902 | -0.045776 | -0.33417 | -0.17395 | -0.19226 | -0.10986 | 0.14648 | 61.116 | 61.5463 | 123.6603 | 123.7152 | -0.045776 | 123.7244 | 61.6241 | -0.19226 | 123.7152 | -0.045776 | 61.6241 | 123.6603 | 123.7244 | -124.0265 | -124.0265
661.7188 | 124.1547 | -61.3037 | 62.5488 | -0.16914 | 0.0042745 | 0.0055094 | 0.00014304 | 0.063452 | -0.0014013 | 0.06965 | -61.3815 | 62.4207 | -61.5097 | -61.4365 | 62.3428 | 0.20599 | 0.009155 | 0.24719 | 62.4573 | -61.5005 | -0.20599 | -0.12817 | -0.07782 | -0.13275 | -0.20599 | -0.19684 | -0.091553 | 0.12817 | 61.3129 | 61.5509 | 123.6465 | 123.7244 | -0.07782 | 123.761 | 61.5097 | -0.19684 | 123.7244 | -0.07782 | 61.5097 | 123.6465 | 123.761 | -124.0585 | -124.0494
662.7188 | 124.1684 | -61.2946 | 62.5534 | -0.131 | 0.0049155 | 0.007432 | 0.0031338 | 0.06388 | -0.0022559 | 0.069009 | -61.3724 | 62.4344 | -61.4914 | -61.4227 | 62.3428 | 0.21973 | -0.009155 | 0.23804 | 62.4298 | -61.5097 | -0.19684 | -0.11902 | -0.077819 | -0.12817 | -0.21057 | -0.21515 | -0.1236 | 0.11902 | 61.2854 | 61.5326 | 123.6374 | 123.7289 | -0.077819 | 123.7244 | 61.5143 | -0.21515 | 123.7289 | -0.077819 | 61.5143 | 123.6374 | 123.7244 | -124.0448 | -124.0631
663.7188 | 124.1684 | -61.3083 | 62.558 | -0.20729 | 0.0049155 | 0.0087138 | 0.0012112 | 0.06388 | -0.0026831 | 0.0673 | -61.3907 | 62.4161 | -61.5097 | -61.4456 | 62.3383 | 0.2243 | -0.004578 | 0.24719 | 62.4344 | -61.496 | -0.20142 | -0.14191 | -0.082397 | -0.13733 | -0.21973 | -0.18768 | -0.1236 | 0.11902 | 61.3037 | 61.5555 | 123.6465 | 123.7244 | -0.082397 | 123.7427 | 61.5326 | -0.18768 | 123.7244 | -0.082397 | 61.5326 | 123.6465 | 123.7427 | -124.0677 | -124.054
664.7188 | 124.0906 | -61.3312 | 62.6083 | -0.23018 | 0.0066245 | 0.012132 | 0.001852 | 0.065375 | -0.0024695 | 0.068795 | -61.3998 | 62.4664 | -61.5143 | -61.5051 | 62.265 | 0.16479 | 0.13733 | 0.18768 | 62.4847 | -61.5097 | -0.18311 | -0.14191 | -0.068664 | -0.17395 | -0.34332 | -0.17853 | -0.1236 | 0.11444 | 61.4685 | 61.5189 | 123.5962 | 123.7976 | -0.068664 | 123.8159 | 61.496 | -0.17853 | 123.7976 | -0.068664 | 61.496 | 123.5962 | 123.8159 | -124.1226 | -124.118
665.7188 | 124.1913 | -61.3129 | 62.5259 | -0.17677 | 0.0053427 | 0.0080728 | -0.00092496 | 0.062171 | -0.00097413 | 0.067941 | -61.3449 | 62.3932 | -61.5051 | -61.3953 | 62.3611 | 0.25635 | 0.41199 | 0.55847 | 62.4802 | -61.4639 | -0.19226 | -0.13275 | -0.032044 | -0.082398 | -0.16479 | -0.15106 | -0.045776 | 0.16022 | 61.7249 | 61.8713 | 123.674 | 123.7061 | -0.032044 | 123.793 | 61.5692 | -0.15106 | 123.7061 | -0.032044 | 61.5692 | 123.674 | 123.793 | -124.0311 | -123.9899
666.7188 | 124.0723 | -61.2671 | 62.5259 | -0.2607 | 0.00021574 | 0.0087138 | -0.002634 | 0.061743 | -0.0039649 | 0.068154 | -61.3449 | 62.4115 | -61.496 | -61.4044 | 62.3657 | 0.24719 | -0.041199 | 0.49896 | 62.4527 | -61.4777 | -0.22888 | -0.11444 | -0.07782 | -0.13733 | -0.16022 | -0.21057 | -0.073242 | 0.15106 | 61.2259 | 61.7661 | 123.6328 | 123.6786 | -0.07782 | 123.7198 | 61.5143 | -0.21057 | 123.6786 | -0.07782 | 61.5143 | 123.6328 | 123.7198 | -124.0219 | -124.0036
667.7188 | 124.1821 | -61.3129 | 62.5351 | -0.19966 | 0.0029929 | 0.0080728 | 0.001852 | 0.062384 | -0.0033239 | 0.067086 | -61.3495 | 62.4023 | -61.4914 | -61.4319 | 62.3428 | 0.24261 | -0.018311 | 0.25635 | 62.439 | -61.496 | -0.17853 | -0.13275 | -0.036621 | -0.11902 | -0.19226 | -0.18311 | -0.09613 | 0.14191 | 61.2946 | 61.5692 | 123.6557 | 123.7152 | -0.036621 | 123.7518 | 61.5555 | -0.18311 | 123.7152 | -0.036621 | 61.5555 | 123.6557 | 123.7518 | -124.0265 | -124.0311
668.7188 | 124.0906 | -61.3037 | 62.6175 | -0.27596 | 0.0053427 | 0.012986 | 0.001852 | 0.063239 | -0.0026831 | 0.067727 | -61.377 | 62.4481 | -61.4868 | -61.4731 | 62.2925 | 0.19226 | 0.10071 | 0.18768 | 62.4619 | -61.5234 | -0.1831 | -0.16937 | -0.073242 | -0.16937 | -0.32501 | -0.21973 | -0.15564 | 0.10986 | 61.4044 | 61.4914 | 123.5962 | 123.7518 | -0.073242 | 123.7656 | 61.496 | -0.21973 | 123.7518 | -0.073242 | 61.496 | 123.5962 | 123.7656 | -124.1043 | -124.1409
669.7188 | 124.1089 | -61.3358 | 62.5626 | -0.0089264 | 0.0085471 | 0.011064 | 0.0061246 | 0.064734 | 9.4068e-05 | 0.06965 | -61.3907 | 62.5122 | -61.4868 | -61.4914 | 62.2284 | 0.11902 | 0.027466 | 0.09613 | 62.4619 | -61.5601 | -0.15106 | -0.050354 | -0.054932 | -0.15564 | -0.33417 | -0.22431 | -0.10071 | 0.09613 | 61.3632 | 61.4319 | 123.5641 | 123.848 | -0.054932 | 123.7976 | 61.4548 | -0.22431 | 123.848 | -0.054932 | 61.4548 | 123.5641 | 123.7976 | -124.0494 | -124.1226
670.7188 | 124.118 | -61.2991 | 62.5717 | -0.28358 | 0.0044881 | 0.01085 | -7.0562e-05 | 0.064734 | -0.0037511 | 0.068368 | -61.3861 | 62.4481 | -61.5051 | -61.4685 | 62.3199 | 0.21515 | 0.086975 | 0.21515 | 62.4802 | -61.5097 | -0.20599 | -0.1236 | -0.086975 | -0.16937 | -0.25177 | -0.21057 | -0.091552 | 0.11902 | 61.3861 | 61.5143 | 123.6191 | 123.7473 | -0.086975 | 123.7793 | 61.5143 | -0.21057 | 123.7473 | -0.086975 | 61.5143 | 123.6191 | 123.7793 | -124.0768 | -124.0814
671.7188 | 124.118 | -61.3129 | 62.5671 | -0.26833 | 0.0049155 | 0.0082864 | -0.00092496 | 0.067084 | -0.0035375 | 0.067513 | -61.3815 | 62.4344 | -61.4777 | -61.4731 | 62.3154 | 0.23346 | 0.068665 | 0.21515 | 62.4985 | -61.528 | -0.16479 | -0.13275 | -0.068665 | -0.16022 | -0.25177 | -0.21515 | -0.068665 | 0.09613 | 61.3815 | 61.528 | 123.6282 | 123.7473 | -0.068665 | 123.8113 | 61.5463 | -0.21515 | 123.7473 | -0.068665 | 61.5463 | 123.6282 | 123.8113 | -124.0448 | -124.0952
672.7188 | 124.1821 | -61.29 | 62.5488 | -0.35988 | 0.0040609 | 0.0095682 | -0.0013522 | 0.063239 | -0.0039649 | 0.067727 | -61.3541 | 62.4161 | -61.4822 | -61.409 | 62.3428 | 0.27466 | -0.041199 | 0.25177 | 62.4573 | -61.496 | -0.19226 | -0.13275 | -0.064087 | -0.11902 | -0.20599 | -0.20599 | -0.091553 | 0.12817 | 61.2488 | 61.5417 | 123.6328 | 123.7061 | -0.064087 | 123.7473 | 61.5646 | -0.20599 | 123.7061 | -0.064087 | 61.5646 | 123.6328 | 123.7473 | -124.0311 | -124.0448
673.7188 | 124.1776 | -61.2946 | 62.5626 | -0.10811 | 0.0027791 | 0.005723 | 0.00014304 | 0.063452 | -0.0028967 | 0.06965 | -61.3403 | 62.4298 | -61.4822 | -61.3998 | 62.3428 | 0.28381 | -0.022888 | 0.26093 | 62.4298 | -61.5005 | -0.18768 | -0.13275 | -0.045776 | -0.10529 | -0.21973 | -0.20599 | -0.13275 | 0.14191 | 61.2717 | 61.5555 | 123.6374 | 123.7244 | -0.045776 | 123.7244 | 61.5784 | -0.20599 | 123.7244 | -0.045776 | 61.5784 | 123.6374 | 123.7244 | -124.0448 | -124.0631
674.7188 | 124.0906 | -61.3449 | 62.5717 | -0.062332 | 0.0083333 | 0.011704 | 0.0065518 | 0.064521 | -0.0033239 | 0.064736 | -61.3724 | 62.5305 | -61.5051 | -61.702 | 62.1185 | 0.1831 | 0.050354 | 0.14191 | 62.4573 | -61.5555 | -0.16022 | -0.041198 | -0.027465 | -0.35706 | -0.45319 | -0.21057 | -0.11444 | 0.13275 | 61.3953 | 61.4868 | 123.4634 | 123.8754 | -0.027465 | 123.8022 | 61.528 | -0.21057 | 123.8754 | -0.027465 | 61.528 | 123.4634 | 123.8022 | -124.0768 | -124.1272
675.7188 | 124.0723 | -61.3037 | 62.59 | -0.16151 | 0.0072653 | 0.0078592 | 0.0020656 | 0.065802 | -0.0024695 | 0.070077 | -61.4456 | 62.5168 | -61.5143 | -61.5097 | 62.2513 | 0.18768 | 0.14648 | 0.16022 | 62.5031 | -61.5463 | -0.21057 | -0.073242 | -0.14191 | -0.20599 | -0.33874 | -0.24262 | -0.086975 | 0.068664 | 61.4502 | 61.4639 | 123.555 | 123.8205 | -0.14191 | 123.8068 | 61.4914 | -0.24262 | 123.8205 | -0.14191 | 61.4914 | 123.555 | 123.8068 | -124.1043 | -124.1364
676.7188 | 124.086 | -61.3129 | 62.6038 | -0.35225 | 0.0051291 | 0.010209 | -0.00092496 | 0.064093 | -0.0039649 | 0.069436 | -61.4548 | 62.4847 | -61.496 | -61.5234 | 62.2467 | 0.18768 | 0.1236 | 0.16022 | 62.5259 | -61.5234 | -0.18311 | -0.11902 | -0.14191 | -0.21057 | -0.35706 | -0.21057 | -0.07782 | 0.041199 | 61.4365 | 61.4731 | 123.5596 | 123.7976 | -0.14191 | 123.8388 | 61.5005 | -0.21057 | 123.7976 | -0.14191 | 61.5005 | 123.5596 | 123.8388 | -124.0997 | -124.1272
677.7188 | 124.0677 | -61.3403 | 62.6038 | -0.016556 | 0.0089743 | 0.0087138 | 0.0029202 | 0.063025 | -0.00097413 | 0.068154 | -61.4227 | 62.4985 | -61.5509 | -61.528 | 62.2513 | 0.19684 | 0.14648 | 0.14191 | 62.4985 | -61.5463 | -0.21057 | -0.10529 | -0.082397 | -0.18768 | -0.35248 | -0.20599 | -0.10529 | 0.12817 | 61.4868 | 61.4822 | 123.5916 | 123.8388 | -0.082397 | 123.8388 | 61.5372 | -0.20599 | 123.8388 | -0.082397 | 61.5372 | 123.5916 | 123.8388 | -124.1547 | -124.1501
678.7188 | 124.0677 | -61.3266 | 62.5763 | -0.22255 | 0.0074789 | 0.0085 | 0.00057044 | 0.06388 | -0.0018285 | 0.067727 | -61.4365 | 62.4756 | -61.5143 | -61.5234 | 62.2742 | 0.20142 | 0.1236 | 0.17395 | 62.5122 | -61.5234 | -0.18768 | -0.10071 | -0.10986 | -0.19684 | -0.30212 | -0.19684 | -0.064087 | 0.07782 | 61.4502 | 61.5005 | 123.6008 | 123.8022 | -0.10986 | 123.8388 | 61.528 | -0.19684 | 123.8022 | -0.10986 | 61.528 | 123.6008 | 123.8388 | -124.0906 | -124.0997
679.7188 | 124.205 | -61.3815 | 62.5763 | 0.15892 | 0.0072653 | 0.010423 | 0.002493 | 0.066443 | -0.0020421 | 0.06965 | -61.4502 | 62.5214 | -61.5417 | -61.5875 | 62.1597 | 0.10529 | 0.027466 | -0.39825 | 62.4435 | -61.5829 | -0.16022 | -0.054932 | -0.068664 | -0.20599 | -0.41656 | -0.20142 | -0.13275 | 0.091553 | 61.409 | 60.9833 | 123.5413 | 123.9029 | -0.068664 | 123.8251 | 61.4868 | -0.20142 | 123.9029 | -0.068664 | 61.4868 | 123.5413 | 123.8251 | -124.118 | -124.1592
680.7188 | 124.0631 | -61.3495 | 62.59 | -0.20729 | 0.0059835 | 0.0063638 | -0.0013522 | 0.064948 | -0.0020421 | 0.069009 | -61.4044 | 62.5168 | -61.5143 | -61.496 | 62.2742 | 0.21973 | 0.13275 | 0.15564 | 62.4847 | -61.5189 | -0.16479 | -0.073242 | -0.054932 | -0.14648 | -0.31586 | -0.16937 | -0.10529 | 0.10986 | 61.4822 | 61.5051 | 123.6237 | 123.8663 | -0.054932 | 123.8342 | 61.5692 | -0.16937 | 123.8663 | -0.054932 | 61.5692 | 123.6237 | 123.8342 | -124.1043 | -124.1089
681.7188 | 124.0997 | -61.3083 | 62.6038 | -0.26833 | 0.0068381 | 0.010423 | -0.0011386 | 0.064734 | -0.0033239 | 0.067513 | -61.3998 | 62.4985 | -61.5005 | -61.496 | 62.2742 | 0.2243 | 0.13275 | 0.15106 | 62.5305 | -61.5189 | -0.19226 | -0.10529 | -0.091552 | -0.18768 | -0.32959 | -0.21057 | -0.073242 | 0.10071 | 61.441 | 61.4594 | 123.5825 | 123.8068 | -0.091552 | 123.8388 | 61.5326 | -0.21057 | 123.8068 | -0.091552 | 61.5326 | 123.5825 | 123.8388 | -124.1043 | -124.1226
682.7188 | 124.0768 | -61.3358 | 62.59 | -0.26833 | 0.0057699 | 0.0087138 | 0.0039882 | 0.064948 | -0.0014013 | 0.068368 | -61.5189 | 62.5168 | -61.4822 | -61.5692 | 62.2559 | 0.21973 | 0.11444 | 0.11902 | 62.5168 | -61.5417 | -0.14648 | -0.073242 | -0.18311 | -0.23346 | -0.33417 | -0.20599 | -0.073242 | -0.036621 | 61.4502 | 61.4548 | 123.5916 | 123.8525 | -0.18311 | 123.8525 | 61.5555 | -0.20599 | 123.8525 | -0.18311 | 61.5555 | 123.5916 | 123.8525 | -124.0723 | -124.1318
683.7188 | 124.0494 | -61.3083 | 62.6083 | -0.28358 | 0.0049155 | 0.010209 | -0.0011386 | 0.067084 | -0.00076053 | 0.069009 | -61.4227 | 62.5305 | -61.4777 | -61.5829 | 62.3016 | 0.2243 | 0.11902 | 0.15106 | 62.5031 | -61.5326 | -0.16937 | -0.077819 | -0.11444 | -0.27466 | -0.3067 | -0.2243 | -0.10529 | 0.054932 | 61.4273 | 61.4594 | 123.6099 | 123.8388 | -0.11444 | 123.8113 | 61.5326 | -0.2243 | 123.8388 | -0.11444 | 61.5326 | 123.6099 | 123.8113 | -124.086 | -124.1409
684.7188 | 124.0723 | -61.3266 | 62.6038 | -0.1844 | 0.0087607 | 0.0095682 | 0.0022794 | 0.065161 | -0.0018285 | 0.069863 | -61.4044 | 62.5305 | -61.5005 | -61.5097 | 62.2467 | 0.20599 | 0.1236 | 0.1236 | 62.5259 | -61.5143 | -0.17395 | -0.073242 | -0.07782 | -0.18311 | -0.35706 | -0.18768 | -0.07782 | 0.09613 | 61.4502 | 61.4502 | 123.5733 | 123.8571 | -0.07782 | 123.8525 | 61.5326 | -0.18768 | 123.8571 | -0.07782 | 61.5326 | 123.5733 | 123.8525 | -124.1043 | -124.118
685.7188 | 124.1135 | -61.3358 | 62.5946 | -0.19966 | 0.0076925 | 0.0082864 | 0.00035684 | 0.064093 | -0.0011877 | 0.068582 | -61.4273 | 62.5305 | -61.4914 | -61.5189 | 62.2284 | 0.19684 | 0.44403 | -0.064087 | 62.5442 | -61.528 | -0.15564 | -0.064086 | -0.091553 | -0.18311 | -0.36621 | -0.19226 | -0.050354 | 0.064087 | 61.7798 | 61.2717 | 123.5641 | 123.8663 | -0.091553 | 123.88 | 61.5326 | -0.19226 | 123.8663 | -0.091553 | 61.5326 | 123.5641 | 123.88 | -124.086 | -124.1226
686.7188 | 124.1272 | -61.3037 | 62.6083 | -0.19966 | 0.0051291 | 0.0082864 | -0.00092496 | 0.065802 | -0.0016149 | 0.067513 | -61.3632 | 62.4847 | -61.4868 | -61.4502 | 62.3154 | 0.27008 | 0.064087 | 0.17395 | 62.5122 | -61.496 | -0.1831 | -0.1236 | -0.059509 | -0.14648 | -0.29297 | -0.19226 | -0.09613 | 0.1236 | 61.3678 | 61.4777 | 123.6191 | 123.7885 | -0.059509 | 123.8159 | 61.5738 | -0.19226 | 123.7885 | -0.059509 | 61.5738 | 123.6191 | 123.8159 | -124.0952 | -124.1043
687.7188 | 124.1318 | -61.2854 | 62.6038 | -0.23018 | 0.0047019 | 0.0085 | -0.0011386 | 0.065161 | -0.0016149 | 0.06965 | -61.3632 | 62.5031 | -61.4822 | -61.4594 | 62.3062 | 0.27466 | 0.059509 | 0.16479 | 62.5168 | -61.5143 | -0.19684 | -0.10071 | -0.07782 | -0.17395 | -0.29755 | -0.22888 | -0.086975 | 0.11902 | 61.3449 | 61.4502 | 123.5916 | 123.7885 | -0.07782 | 123.8022 | 61.5601 | -0.22888 | 123.7885 | -0.07782 | 61.5601 | 123.5916 | 123.8022 | -124.086 | -124.118
688.7188 | 124.054 | -61.3083 | 62.6175 | -0.23781 | 0.0059835 | 0.012559 | -0.00028416 | 0.064948 | -0.0024695 | 0.066873 | -61.4227 | 62.5031 | -61.4914 | -61.5189 | 62.2696 | 0.21057 | 0.1236 | 0.10529 | 62.5351 | -61.5372 | -0.1831 | -0.11444 | -0.11444 | -0.21057 | -0.3479 | -0.22888 | -0.082398 | 0.068665 | 61.4319 | 61.4136 | 123.5779 | 123.8113 | -0.11444 | 123.8434 | 61.5189 | -0.22888 | 123.8113 | -0.11444 | 61.5189 | 123.5779 | 123.8434 | -124.1089 | -124.1547
689.7188 | 124.0677 | -61.3174 | 62.5717 | 0.052109 | 0.0087607 | 0.0095682 | 0.0054836 | 0.06687 | -0.0022559 | 0.069009 | -61.3815 | 62.5442 | -61.4822 | -61.5234 | 62.233 | 0.11902 | 0.013733 | -0.009155 | 62.4893 | -61.5646 | -0.16479 | -0.027466 | -0.064087 | -0.20599 | -0.33875 | -0.24719 | -0.082397 | 0.10071 | 61.3312 | 61.3083 | 123.5504 | 123.8617 | -0.064087 | 123.8068 | 61.4365 | -0.24719 | 123.8617 | -0.064087 | 61.4365 | 123.5504 | 123.8068 | -124.054 | -124.1364
690.7188 | 124.0585 | -61.3083 | 62.6083 | -0.077591 | 0.0061971 | 0.007432 | 0.0014248 | 0.067298 | -0.0016149 | 0.069009 | -61.3998 | 62.558 | -61.496 | -61.5097 | 62.2467 | 0.20142 | 0.11902 | 0.059509 | 62.5259 | -61.5234 | -0.18768 | -0.050354 | -0.091552 | -0.20142 | -0.36163 | -0.21515 | -0.082397 | 0.096131 | 61.4273 | 61.3678 | 123.555 | 123.8663 | -0.091552 | 123.8342 | 61.5097 | -0.21515 | 123.8663 | -0.091552 | 61.5097 | 123.555 | 123.8342 | -124.1043 | -124.1318
691.7188 | 124.0677 | -61.3083 | 62.59 | -0.91682 | 0.0061971 | 0.0048684 | 0.0014248 | 0.06623 | -0.0011877 | 0.068154 | -61.4594 | 62.5122 | -61.5189 | -61.5143 | 62.2467 | 0.20599 | 0.12817 | 0.050354 | 62.5534 | -61.5051 | -0.21057 | -0.07782 | -0.15106 | -0.20599 | -0.34332 | -0.19684 | -0.036621 | 0.059509 | 61.4365 | 61.3586 | 123.555 | 123.8205 | -0.15106 | 123.8617 | 61.5143 | -0.19684 | 123.8205 | -0.15106 | 61.5143 | 123.555 | 123.8617 | -124.1089 | -124.0952
692.7188 | 124.054 | -61.3266 | 62.5809 | -0.76424 | 0.0070517 | 0.015122 | -0.0022068 | 0.064948 | -0.0026831 | 0.067086 | -61.5555 | 62.5305 | -61.5005 | -61.5372 | 62.265 | 0.20599 | 0.10986 | 0.036621 | 62.5534 | -61.528 | -0.17395 | -0.050354 | -0.22888 | -0.21057 | -0.31586 | -0.20142 | -0.027466 | -0.054932 | 61.4365 | 61.3632 | 123.5916 | 123.8571 | -0.22888 | 123.88 | 61.5326 | -0.20142 | 123.8571 | -0.22888 | 61.5326 | 123.5916 | 123.88 | -124.0814 | -124.1089
693.7344 | 124.1455 | -61.3266 | 62.5076 | 0.21996 | 0.0068381 | 0.007432 | 0.00078404 | 0.068579 | -0.0014013 | 0.068368 | -61.3358 | 62.4619 | -61.4456 | -61.4502 | 62.3154 | 0.20142 | -0.23346 | 0.036621 | 62.4619 | -61.5051 | -0.11902 | -0.045776 | -0.009155 | -0.1236 | -0.19226 | -0.17853 | -0.045776 | 0.10986 | 61.0931 | 61.3632 | 123.642 | 123.7885 | -0.009155 | 123.7885 | 61.528 | -0.17853 | 123.7885 | -0.009155 | 61.528 | 123.642 | 123.7885 | -123.9532 | -124.0128
694.7188 | 124.0952 | -61.2991 | 62.6175 | -0.25307 | 0.0064107 | 0.011704 | -0.0011386 | 0.064093 | -0.0018285 | 0.068582 | -61.3632 | 62.4939 | -61.4868 | -61.4502 | 62.2833 | 0.23346 | 0.054932 | 0.07782 | 62.5214 | -61.5097 | -0.18768 | -0.1236 | -0.064087 | -0.15106 | -0.33417 | -0.21057 | -0.096131 | 0.1236 | 61.3541 | 61.377 | 123.5825 | 123.793 | -0.064087 | 123.8205 | 61.5326 | -0.21057 | 123.793 | -0.064087 | 61.5326 | 123.5825 | 123.8205 | -124.1043 | -124.1272
695.7188 | 123.9716 | -61.2762 | 62.6129 | -0.19966 | 0.0055563 | 0.0087138 | 0.00057044 | 0.067298 | -0.0026831 | 0.069222 | -61.3998 | 62.5351 | -61.4548 | -61.5005 | 62.2559 | 0.19226 | 0.082397 | 0.1831 | 62.5305 | -61.4777 | -0.17853 | -0.07782 | -0.1236 | -0.2243 | -0.35706 | -0.20142 | -0.082397 | 0.054932 | 61.3586 | 61.4594 | 123.5321 | 123.8113 | -0.1236 | 123.8068 | 61.4685 | -0.20142 | 123.8113 | -0.1236 | 61.4685 | 123.5321 | 123.8068 | -124.0677 | -124.0906
696.7188 | 124.0768 | -61.3174 | 62.6175 | -0.27596 | 0.0076925 | 0.014268 | -7.0562e-05 | 0.065161 | -0.00076053 | 0.068368 | -61.4136 | 62.5305 | -61.4731 | -61.496 | 62.2421 | 0.16937 | 0.082397 | -0.022888 | 62.5122 | -61.5143 | -0.15564 | -0.086975 | -0.09613 | -0.17853 | -0.37537 | -0.19684 | -0.10529 | 0.059509 | 61.3998 | 61.2946 | 123.5596 | 123.848 | -0.09613 | 123.8297 | 61.4868 | -0.19684 | 123.848 | -0.09613 | 61.4868 | 123.5596 | 123.8297 | -124.0906 | -124.1318
697.7188 | 124.0906 | -61.3403 | 62.6129 | -0.12337 | 0.0091879 | 0.0087138 | 0.00078404 | 0.066443 | -0.0011877 | 0.068154 | -61.3815 | 62.5534 | -61.4777 | -61.5097 | 62.2513 | 0.16022 | 0.07782 | -0.041199 | 62.5305 | -61.4914 | -0.13733 | -0.059509 | -0.041199 | -0.16937 | -0.36163 | -0.15106 | -0.082397 | 0.09613 | 61.4182 | 61.2991 | 123.5916 | 123.8937 | -0.041199 | 123.8708 | 61.5005 | -0.15106 | 123.8937 | -0.041199 | 61.5005 | 123.5916 | 123.8708 | -124.0906 | -124.1043
698.7344 | 124.1638 | -61.2808 | 62.5442 | 0.28862 | 0.0061971 | 0.0087138 | 0.003561 | 0.067939 | -0.0024695 | 0.070077 | -61.3861 | 62.5168 | -61.4685 | -61.4639 | 62.2833 | 0.13733 | -0.21973 | -0.07782 | 62.4985 | -61.5234 | -0.18768 | -0.027465 | -0.10529 | -0.18311 | -0.26093 | -0.24261 | -0.045776 | 0.082398 | 61.0611 | 61.203 | 123.5641 | 123.7976 | -0.10529 | 123.7793 | 61.4182 | -0.24261 | 123.7976 | -0.10529 | 61.4182 | 123.5641 | 123.7793 | -124.0128 | -124.0677
699.7188 | 124.0677 | -61.3083 | 62.6038 | -0.0012969 | 0.0089743 | 0.0082864 | 0.0029202 | 0.066443 | -0.0037511 | 0.0673 | -61.377 | 62.5397 | -61.4777 | -61.5097 | 62.2192 | 0.10071 | -0.082397 | -0.12817 | 62.5214 | -61.5555 | -0.16937 | -0.064087 | -0.068664 | -0.20142 | -0.38452 | -0.24719 | -0.082398 | 0.10071 | 61.2259 | 61.1801 | 123.5275 | 123.848 | -0.068664 | 123.8297 | 61.409 | -0.24719 | 123.848 | -0.068664 | 61.409 | 123.5275 | 123.8297 | -124.0814 | -124.1592
700.7188 | 124.0997 | -61.3083 | 62.6129 | -0.26833 | 0.0051291 | 0.0082864 | -0.00092496 | 0.064307 | -0.0020421 | 0.069436 | -61.3724 | 62.5305 | -61.4548 | -61.4731 | 62.2742 | 0.16479 | 0.022888 | -0.036621 | 62.5717 | -61.4822 | -0.14648 | -0.082397 | -0.064086 | -0.16479 | -0.33875 | -0.17395 | -0.041199 | 0.082398 | 61.3312 | 61.2717 | 123.5825 | 123.8388 | -0.064086 | 123.88 | 61.4731 | -0.17395 | 123.8388 | -0.064086 | 61.4731 | 123.5825 | 123.88 | -124.0677 | -124.0952
701.7188 | 124.0723 | -61.2671 | 62.6038 | -0.23018 | 0.0070517 | 0.0072184 | -0.0022068 | 0.065375 | -0.0011877 | 0.068795 | -61.3678 | 62.5168 | -61.4594 | -61.4594 | 62.2971 | 0.19684 | -0.013733 | -0.045776 | 62.5214 | -61.4914 | -0.19226 | -0.086975 | -0.10071 | -0.19226 | -0.3067 | -0.2243 | -0.082398 | 0.091553 | 61.2534 | 61.2213 | 123.5641 | 123.7839 | -0.10071 | 123.7885 | 61.4639 | -0.2243 | 123.7839 | -0.10071 | 61.4639 | 123.5641 | 123.7885 | -124.0631 | -124.0952
702.7188 | 124.0906 | -61.3037 | 62.6312 | -0.16914 | 0.0066245 | 0.0089274 | -0.00028416 | 0.065802 | -0.0028967 | 0.069009 | -61.409 | 62.5397 | -61.4777 | -61.4914 | 62.2559 | 0.027466 | 0.34332 | -0.13733 | 62.5809 | -61.4868 | -0.17395 | -0.091553 | -0.10529 | -0.18768 | -0.37537 | -0.1831 | -0.050354 | 0.068664 | 61.647 | 61.1664 | 123.5596 | 123.8434 | -0.10529 | 123.8846 | 61.3312 | -0.1831 | 123.8434 | -0.10529 | 61.3312 | 123.5596 | 123.8846 | -124.1089 | -124.118
703.7344 | 124.1501 | -61.2808 | 62.5717 | 0.12077 | 0.0053427 | 0.011064 | 0.00014304 | 0.066657 | 0.00030767 | 0.069436 | -61.3724 | 62.4435 | -61.4868 | -61.4639 | 62.2879 | 0.13275 | -0.30212 | -0.15106 | 62.4939 | -61.5005 | -0.20599 | -0.12817 | -0.091552 | -0.18311 | -0.28381 | -0.21973 | -0.07782 | 0.11444 | 60.9787 | 61.1298 | 123.5687 | 123.7244 | -0.091552 | 123.7747 | 61.4136 | -0.21973 | 123.7244 | -0.091552 | 61.4136 | 123.5687 | 123.7747 | -124.0585 | -124.0723
704.7188 | 124.0768 | -61.2808 | 62.6266 | -0.33699 | 0.0057699 | 0.010636 | 0.0029202 | 0.064307 | -0.0018285 | 0.067727 | -61.377 | 62.5717 | -61.4731 | -61.5051 | 62.2421 | 0.086975 | -0.013733 | -0.16937 | 62.5442 | -61.5509 | -0.19226 | -0.054932 | -0.09613 | -0.2243 | -0.38452 | -0.27008 | -0.082398 | 0.09613 | 61.2671 | 61.1114 | 123.5229 | 123.8525 | -0.09613 | 123.8251 | 61.3678 | -0.27008 | 123.8525 | -0.09613 | 61.3678 | 123.5229 | 123.8251 | -124.0997 | -124.1776
705.7188 | 124.0814 | -61.2717 | 62.6221 | -0.7795 | 0.0051291 | 0.0050822 | 0.0029202 | 0.066657 | -0.0022559 | 0.068368 | -61.4365 | 62.5488 | -61.4914 | -61.4868 | 62.2559 | 0.086975 | -0.022888 | -0.17853 | 62.5671 | -61.5189 | -0.21973 | -0.073242 | -0.16479 | -0.21515 | -0.36621 | -0.24719 | -0.054931 | 0.054932 | 61.2488 | 61.0931 | 123.5275 | 123.8205 | -0.16479 | 123.8388 | 61.3586 | -0.24719 | 123.8205 | -0.16479 | 61.3586 | 123.5275 | 123.8388 | -124.1135 | -124.1409
706.7188 | 124.0768 | -61.2946 | 62.6266 | -0.23018 | 0.0042745 | 0.0093546 | -0.0019932 | 0.066443 | -0.0020421 | 0.065591 | -61.1755 | 62.5992 | -61.4502 | -61.4822 | 62.265 | 0.068665 | -0.054932 | -0.17395 | 62.5626 | -61.496 | -0.15564 | -0.027466 | 0.11902 | -0.18768 | -0.36163 | -0.20142 | -0.064087 | 0.27466 | 61.2396 | 61.1206 | 123.5596 | 123.8937 | 0.11902 | 123.8571 | 61.3632 | -0.20142 | 123.8937 | 0.11902 | 61.3632 | 123.5596 | 123.8571 | -124.0768 | -124.1226
707.7188 | 124.0768 | -61.2762 | 62.6175 | -0.22255 | 0.0047019 | 0.007432 | -0.0032748 | 0.064734 | -0.0020421 | 0.068154 | -61.3358 | 62.5351 | -61.4365 | -61.4456 | 62.3016 | 0.13733 | -0.09613 | -0.17395 | 62.5534 | -61.4777 | -0.16022 | -0.082398 | -0.059509 | -0.16937 | -0.31586 | -0.20142 | -0.064087 | 0.10071 | 61.1801 | 61.1023 | 123.5779 | 123.8113 | -0.059509 | 123.8297 | 61.4136 | -0.20142 | 123.8113 | -0.059509 | 61.4136 | 123.5779 | 123.8297 | -124.054 | -124.0952
708.7188 | 124.0952 | -61.2579 | 62.6221 | -0.077591 | 0.0064107 | 0.0078592 | 0.0033474 | 0.06623 | -0.0028967 | 0.067086 | -61.3449 | 62.5671 | -61.4594 | -61.4273 | 62.2879 | 0.10529 | -0.14191 | -0.21973 | 62.5351 | -61.4868 | -0.20142 | -0.054931 | -0.086975 | -0.16937 | -0.33417 | -0.22888 | -0.086975 | 0.11444 | 61.116 | 61.0382 | 123.5458 | 123.8251 | -0.086975 | 123.793 | 61.3632 | -0.22888 | 123.8251 | -0.086975 | 61.3632 | 123.5458 | 123.793 | -124.0814 | -124.1089
709.7188 | 124.0814 | -61.2671 | 62.6175 | -0.21492 | 0.0044881 | 0.0065774 | -0.0017796 | 0.066016 | -0.00033333 | 0.070931 | -61.377 | 62.558 | -61.4685 | -61.496 | 62.265 | 0.064087 | -0.086975 | -0.24261 | 62.5763 | -61.4868 | -0.20142 | -0.05951 | -0.10986 | -0.22888 | -0.35248 | -0.21973 | -0.041199 | 0.091553 | 61.1801 | 61.0245 | 123.5321 | 123.8251 | -0.10986 | 123.8434 | 61.3312 | -0.21973 | 123.8251 | -0.10986 | 61.3312 | 123.5321 | 123.8434 | -124.086 | -124.1043
710.7188 | 124.0585 | -61.2808 | 62.6266 | -0.062332 | 0.0064107 | 0.0082864 | 0.0016384 | 0.066657 | -0.00076053 | 0.06965 | -61.3632 | 62.5946 | -61.4594 | -61.4685 | 62.265 | 0.059509 | -0.10071 | -0.28839 | 62.5763 | -61.5097 | -0.17853 | -0.032044 | -0.082397 | -0.18768 | -0.36163 | -0.22888 | -0.050354 | 0.096131 | 61.1801 | 60.9924 | 123.5458 | 123.8754 | -0.082397 | 123.8571 | 61.3403 | -0.22888 | 123.8754 | -0.082397 | 61.3403 | 123.5458 | 123.8571 | -124.086 | -124.1364
711.7188 | 124.0448 | -61.2946 | 62.645 | -0.35225 | 0.0061971 | 0.0089274 | 0.0020656 | 0.06687 | -0.0016149 | 0.068582 | -61.3953 | 62.5671 | -61.4685 | -61.4868 | 62.265 | 0.045776 | -0.09613 | -0.28381 | 62.5854 | -61.4914 | -0.17395 | -0.077819 | -0.10071 | -0.19226 | -0.37994 | -0.19684 | -0.059509 | 0.073242 | 61.1984 | 61.0107 | 123.5596 | 123.8617 | -0.10071 | 123.88 | 61.3403 | -0.19684 | 123.8617 | -0.10071 | 61.3403 | 123.5596 | 123.88 | -124.1135 | -124.1364
712.7188 | 124.0631 | -61.2671 | 62.6587 | -0.22255 | 0.0042745 | 0.0070048 | -0.00071136 | 0.06687 | 0.00052127 | 0.067941 | -61.235 | 62.5946 | -61.441 | -61.4639 | 62.2284 | 0.022888 | -0.10529 | -0.29755 | 62.5809 | -61.4822 | -0.17395 | -0.064087 | 0.032044 | -0.19684 | -0.4303 | -0.21515 | -0.077819 | 0.20599 | 61.1618 | 60.9695 | 123.4955 | 123.8617 | 0.032044 | 123.848 | 61.29 | -0.21515 | 123.8617 | 0.032044 | 61.29 | 123.4955 | 123.848 | -124.0997 | -124.1409
713.7188 | 124.0768 | -61.2854 | 62.6587 | -0.28358 | 0.0049155 | 0.0072184 | -0.0034886 | 0.069861 | -0.00076053 | 0.067086 | -61.377 | 62.5534 | -61.4685 | -61.4731 | 62.2787 | 0.013733 | -0.1236 | -0.31586 | 62.59 | -61.496 | -0.18311 | -0.10528 | -0.091553 | -0.18768 | -0.37994 | -0.21057 | -0.068664 | 0.091553 | 61.1618 | 60.9695 | 123.5641 | 123.8388 | -0.091553 | 123.8754 | 61.2991 | -0.21057 | 123.8388 | -0.091553 | 61.2991 | 123.5641 | 123.8754 | -124.1272 | -124.1547
714.7188 | 124.0952 | -61.2762 | 62.6083 | -0.024185 | 0.0098287 | 0.010209 | 0.0037746 | 0.065589 | -0.0018285 | 0.068582 | -61.3129 | 62.5809 | -61.4639 | -61.4548 | 62.2742 | 0.004578 | -0.27924 | -0.40283 | 62.5351 | -61.5326 | -0.18768 | -0.027465 | -0.036621 | -0.17853 | -0.33417 | -0.25635 | -0.073242 | 0.15106 | 60.997 | 60.8734 | 123.5504 | 123.8571 | -0.036621 | 123.8113 | 61.2808 | -0.25635 | 123.8571 | -0.036621 | 61.2808 | 123.5504 | 123.8113 | -124.0723 | -124.1409
715.7188 | 124.0906 | -61.2488 | 62.6266 | -0.19966 | 0.0057699 | 0.0097818 | -0.0017796 | 0.065161 | 9.4068e-05 | 0.071572 | -61.3037 | 62.5168 | -61.441 | -61.3998 | 62.3245 | 0.11444 | -0.24261 | -0.27924 | 62.5534 | -61.4731 | -0.19226 | -0.10986 | -0.054932 | -0.15106 | -0.30212 | -0.2243 | -0.073242 | 0.13733 | 61.0062 | 60.9695 | 123.5733 | 123.7656 | -0.054932 | 123.8022 | 61.3632 | -0.2243 | 123.7656 | -0.054932 | 61.3632 | 123.5733 | 123.8022 | -124.0677 | -124.0997
716.7188 | 124.0494 | -61.2717 | 62.6312 | -0.24544 | 0.0068381 | 0.0080728 | 0.00014304 | 0.063666 | -0.0024695 | 0.068368 | -61.377 | 62.5763 | -61.4502 | -61.4822 | 62.2742 | 0.054932 | -0.18768 | -0.36163 | 62.5763 | -61.4731 | -0.17853 | -0.054932 | -0.10529 | -0.21057 | -0.35706 | -0.20142 | -0.054932 | 0.073242 | 61.084 | 60.91 | 123.5458 | 123.848 | -0.10529 | 123.848 | 61.3266 | -0.20142 | 123.848 | -0.10529 | 61.3266 | 123.5458 | 123.848 | -124.0814 | -124.1043
717.7188 | 124.0677 | -61.2671 | 62.6541 | -0.34462 | 0.0076925 | 0.0076456 | -0.0011386 | 0.064734 | -0.0022559 | 0.071572 | -61.3632 | 62.59 | -61.4868 | -61.4639 | 62.2559 | 0.050354 | -0.18768 | -0.37537 | 62.5763 | -61.4822 | -0.21973 | -0.064087 | -0.09613 | -0.19684 | -0.39825 | -0.21515 | -0.07782 | 0.1236 | 61.0794 | 60.8917 | 123.5229 | 123.8571 | -0.09613 | 123.8434 | 61.3174 | -0.21515 | 123.8571 | -0.09613 | 61.3174 | 123.5229 | 123.8434 | -124.1409 | -124.1364
718.7188 | 124.0585 | -61.2625 | 62.645 | 0.10551 | 0.0064107 | 0.0080728 | -0.00049776 | 0.065802 | -0.0043921 | 0.069863 | -61.3449 | 62.5809 | -61.4685 | -61.4914 | 62.2742 | 0.045776 | -0.20142 | -0.40741 | 62.5992 | -61.5005 | -0.20599 | -0.064086 | -0.082398 | -0.22888 | -0.37079 | -0.23804 | -0.045776 | 0.1236 | 61.0611 | 60.8551 | 123.5367 | 123.8434 | -0.082398 | 123.8617 | 61.3083 | -0.23804 | 123.8434 | -0.082398 | 61.3083 | 123.5367 | 123.8617 | -124.1135 | -124.1455
719.7188 | 124.1135 | -61.2946 | 62.6129 | -0.054703 | 0.0085471 | 0.0085 | 0.00099764 | 0.069007 | -0.0011877 | 0.068368 | -61.2946 | 62.5854 | -61.4639 | -61.4182 | 62.2787 | 0.073242 | -0.32959 | -0.42114 | 62.558 | -61.4822 | -0.16937 | -0.027466 | 0 | -0.1236 | -0.33417 | -0.18768 | -0.054932 | 0.16937 | 60.965 | 60.8734 | 123.5733 | 123.88 | 0 | 123.8525 | 61.3678 | -0.18768 | 123.88 | 0 | 61.3678 | 123.5733 | 123.8525 | -124.0768 | -124.0952
720.7188 | 124.0677 | -61.2671 | 62.6541 | -1.634 | 0.0051291 | 0.011064 | 0.00078404 | 0.067511 | -0.0022559 | 0.067727 | -61.4777 | 62.5992 | -61.4594 | -61.4777 | 62.2284 | 0.064087 | -0.18768 | -0.4303 | 62.5763 | -61.4731 | -0.19226 | -0.054932 | -0.21057 | -0.21057 | -0.42572 | -0.20599 | -0.07782 | -0.01831 | 61.0794 | 60.8368 | 123.4955 | 123.8663 | -0.21057 | 123.8434 | 61.3312 | -0.20599 | 123.8663 | -0.21057 | 61.3312 | 123.4955 | 123.8434 | -124.1135 | -124.1272
721.7188 | 124.0631 | -61.2442 | 62.6541 | -0.28358 | 0.0076925 | 0.0087138 | -0.002634 | 0.065375 | -0.0031103 | 0.067941 | -61.3129 | 62.5351 | -61.4182 | -61.4365 | 62.2925 | 0.091553 | -0.26093 | -0.3891 | 62.59 | -61.4822 | -0.17395 | -0.11902 | -0.068664 | -0.19226 | -0.36163 | -0.23804 | -0.064087 | 0.10529 | 60.9833 | 60.8551 | 123.5367 | 123.7793 | -0.068664 | 123.8342 | 61.3358 | -0.23804 | 123.7793 | -0.068664 | 61.3358 | 123.5367 | 123.8342 | -124.0723 | -124.1364
722.7188 | 124.0814 | -61.2579 | 62.6404 | -0.23781 | 0.0072653 | 0.0076456 | -0.0022068 | 0.064948 | -0.0020421 | 0.068795 | -61.3037 | 62.5671 | -61.4227 | -61.4227 | 62.3199 | 0.10529 | -0.27466 | -0.3891 | 62.5946 | -61.4777 | -0.16479 | -0.073242 | -0.045776 | -0.16479 | -0.32043 | -0.21973 | -0.045777 | 0.11902 | 60.9833 | 60.8688 | 123.5779 | 123.8251 | -0.045776 | 123.8525 | 61.3632 | -0.21973 | 123.8251 | -0.045776 | 61.3632 | 123.5779 | 123.8525 | -124.0631 | -124.118
723.7188 | 124.086 | -61.2671 | 62.6587 | -0.22255 | 0.0064107 | 0.0097818 | 0.004202 | 0.065161 | -0.0022559 | 0.06965 | -61.3495 | 62.59 | -61.4548 | -61.4639 | 62.265 | 0.059509 | -0.27466 | -0.46692 | 62.5809 | -61.4914 | -0.18768 | -0.068664 | -0.082397 | -0.19684 | -0.39368 | -0.2243 | -0.077819 | 0.10529 | 60.9924 | 60.8002 | 123.5321 | 123.8571 | -0.082397 | 123.848 | 61.3266 | -0.2243 | 123.8571 | -0.082397 | 61.3266 | 123.5321 | 123.848 | -124.1135 | -124.1501
724.7188 | 124.0402 | -61.2579 | 62.6312 | -0.031814 | 0.0083333 | 0.0095682 | 0.0031338 | 0.067084 | -0.0026831 | 0.067727 | -61.3083 | 62.5854 | -61.4777 | -61.4548 | 62.2513 | 0.050354 | -0.36163 | -0.51727 | 62.5534 | -61.5189 | -0.21973 | -0.045777 | -0.050354 | -0.19684 | -0.37994 | -0.26092 | -0.07782 | 0.16937 | 60.8963 | 60.7407 | 123.5092 | 123.8434 | -0.050354 | 123.8113 | 61.3083 | -0.26092 | 123.8434 | -0.050354 | 61.3083 | 123.5092 | 123.8113 | -124.1089 | -124.1501
725.7188 | 124.0585 | -61.2625 | 62.645 | -0.19966 | 0.0076925 | 0.0087138 | 0.0012112 | 0.066443 | -0.0041785 | 0.069436 | -61.3586 | 62.59 | -61.4502 | -61.4639 | 62.265 | 0.073242 | -0.27924 | -0.48981 | 62.5946 | -61.4914 | -0.18768 | -0.054931 | -0.096131 | -0.20142 | -0.37994 | -0.22888 | -0.050354 | 0.091552 | 60.9833 | 60.7727 | 123.5275 | 123.8525 | -0.096131 | 123.8571 | 61.3358 | -0.22888 | 123.8525 | -0.096131 | 61.3358 | 123.5275 | 123.8571 | -124.0952 | -124.1364
726.7188 | 124.0814 | -61.2488 | 62.6816 | -0.26833 | 0.0061971 | 0.0095682 | 0.0014248 | 0.066443 | 0.00030767 | 0.069222 | -61.377 | 62.5763 | -61.4548 | -61.4639 | 62.2513 | 0.091553 | -0.28839 | -0.49896 | 62.59 | -61.4731 | -0.20599 | -0.10529 | -0.12817 | -0.21515 | -0.4303 | -0.2243 | -0.091553 | 0.07782 | 60.9604 | 60.7498 | 123.5001 | 123.8251 | -0.12817 | 123.8388 | 61.3403 | -0.2243 | 123.8251 | -0.12817 | 61.3403 | 123.5001 | 123.8388 | -124.1364 | -124.1547
727.7188 | 124.054 | -61.2625 | 62.6587 | -0.15388 | 0.0085471 | 0.009141 | -0.0017796 | 0.065375 | -0.0016149 | 0.068582 | -61.3495 | 62.5992 | -61.4594 | -61.4639 | 62.2742 | 0.10071 | -0.28381 | -0.49896 | 62.6083 | -61.4731 | -0.19684 | -0.059509 | -0.086975 | -0.20142 | -0.38452 | -0.21057 | -0.050354 | 0.10986 | 60.9787 | 60.7636 | 123.5367 | 123.8617 | -0.086975 | 123.8708 | 61.3632 | -0.21057 | 123.8617 | -0.086975 | 61.3632 | 123.5367 | 123.8708 | -124.118 | -124.1318
728.7188 | 124.0631 | -61.2534 | 62.6587 | -0.17677 | 0.0072653 | 0.0095682 | -0.00071136 | 0.064093 | -0.00097413 | 0.069009 | -61.3541 | 62.59 | -61.409 | -61.4594 | 62.2787 | 0.11902 | -0.29755 | -0.49439 | 62.5854 | -61.496 | -0.15564 | -0.068664 | -0.10071 | -0.20599 | -0.37994 | -0.24262 | -0.073242 | 0.054932 | 60.9558 | 60.759 | 123.5321 | 123.8434 | -0.10071 | 123.8388 | 61.3724 | -0.24262 | 123.8434 | -0.10071 | 61.3724 | 123.5321 | 123.8388 | -124.0677 | -124.1547
729.7188 | 123.9853 | -61.2762 | 62.6221 | -0.12337 | 0.0064107 | 0.007432 | 0.0044156 | 0.068366 | -0.0011877 | 0.070077 | -61.29 | 62.5992 | -61.4319 | -61.4136 | 62.3108 | 0.14648 | -0.40741 | -0.48523 | 62.5717 | -61.5005 | -0.15564 | -0.022888 | -0.013733 | -0.13733 | -0.31128 | -0.2243 | -0.050354 | 0.14191 | 60.8688 | 60.791 | 123.587 | 123.8754 | -0.013733 | 123.848 | 61.4227 | -0.2243 | 123.8754 | -0.013733 | 61.4227 | 123.587 | 123.848 | -124.054 | -124.1226
730.7188 | 124.118 | -61.2717 | 62.6633 | -0.19966 | 0.0064107 | 0.0065774 | 0.0022794 | 0.066443 | -0.0026831 | 0.068368 | -61.3312 | 62.59 | -61.4136 | -61.4227 | 62.2787 | 0.15564 | -0.33417 | -0.50354 | 62.5992 | -61.4639 | -0.14191 | -0.073242 | -0.05951 | -0.15106 | -0.38452 | -0.19226 | -0.064087 | 0.082397 | 60.9375 | 60.7681 | 123.5504 | 123.8617 | -0.05951 | 123.8708 | 61.4273 | -0.19226 | 123.8617 | -0.05951 | 61.4273 | 123.5504 | 123.8708 | -124.0768 | -124.1272
731.7188 | 124.0952 | -61.2442 | 62.6678 | -0.27596 | 0.0083333 | 0.0089274 | 0.0016384 | 0.06687 | -0.00076053 | 0.069222 | -61.3358 | 62.5992 | -61.441 | -61.4365 | 62.2696 | 0.14648 | -0.33875 | -0.5127 | 62.5992 | -61.4731 | -0.19684 | -0.068665 | -0.091552 | -0.19226 | -0.39825 | -0.22888 | -0.068665 | 0.10529 | 60.9055 | 60.7315 | 123.5138 | 123.8434 | -0.091552 | 123.8434 | 61.3907 | -0.22888 | 123.8434 | -0.091552 | 61.3907 | 123.5138 | 123.8434 | -124.1089 | -124.1409
732.7188 | 124.1272 | -61.2488 | 62.6541 | -0.19203 | 0.0055563 | 0.010636 | 0.00078404 | 0.065589 | -0.0035375 | 0.069863 | -61.3312 | 62.6129 | -61.4044 | -61.4456 | 62.2696 | 0.16022 | -0.35248 | -0.50812 | 62.6221 | -61.4822 | -0.15564 | -0.041199 | -0.082398 | -0.19684 | -0.38452 | -0.23346 | -0.032044 | 0.073242 | 60.8963 | 60.7407 | 123.5184 | 123.8617 | -0.082398 | 123.8708 | 61.409 | -0.23346 | 123.8617 | -0.082398 | 61.409 | 123.5184 | 123.8708 | -124.0585 | -124.1364
733.7188 | 124.0997 | -61.2579 | 62.6404 | -0.19966 | 0.0061971 | 0.0078592 | 0.00078404 | 0.067511 | -0.0020421 | 0.067513 | -61.3358 | 62.6083 | -61.4227 | -61.4319 | 62.2879 | 0.16479 | -0.3479 | -0.52185 | 62.6038 | -61.441 | -0.16479 | -0.032044 | -0.077819 | -0.17395 | -0.35248 | -0.1831 | -0.036621 | 0.086975 | 60.91 | 60.7361 | 123.5458 | 123.8663 | -0.077819 | 123.8617 | 61.4227 | -0.1831 | 123.8663 | -0.077819 | 61.4227 | 123.5458 | 123.8617 | -124.0631 | -124.0814
734.7188 | 124.0814 | -61.2808 | 62.6358 | 0.097885 | 0.0057699 | 0.010209 | 0.002493 | 0.068579 | -0.0014013 | 0.070718 | -61.3586 | 62.5809 | -61.441 | -61.4914 | 62.233 | 0.10071 | -0.46692 | -0.6546 | 62.5763 | -61.496 | -0.16022 | -0.054931 | -0.07782 | -0.21057 | -0.40283 | -0.21515 | -0.059509 | 0.082397 | 60.8139 | 60.6262 | 123.5138 | 123.8617 | -0.07782 | 123.8571 | 61.3815 | -0.21515 | 123.8617 | -0.07782 | 61.3815 | 123.5138 | 123.8571 | -124.0768 | -124.1318
735.7188 | 124.0585 | -61.2305 | 62.6404 | -0.19203 | 0.0070517 | 0.0089274 | 0.00014304 | 0.06687 | -0.0011877 | 0.068582 | -61.4365 | 62.59 | -61.4044 | -61.5051 | 62.2604 | 0.21515 | -0.37079 | -0.55389 | 62.5946 | -61.4914 | -0.17395 | -0.050354 | -0.20599 | -0.27466 | -0.37994 | -0.26093 | -0.045777 | -0.032043 | 60.8597 | 60.6766 | 123.4909 | 123.8205 | -0.20599 | 123.8251 | 61.4456 | -0.26093 | 123.8205 | -0.20599 | 61.4456 | 123.4909 | 123.8251 | -124.0448 | -124.1318
736.7188 | 124.0952 | -61.2534 | 62.6724 | -0.16914 | 0.0047019 | 0.0099954 | 0.0012112 | 0.066016 | -0.0028967 | 0.069436 | -61.3495 | 62.6038 | -61.4182 | -61.4365 | 62.265 | 0.21973 | -0.37994 | -0.52643 | 62.5992 | -61.4548 | -0.16479 | -0.068664 | -0.09613 | -0.1831 | -0.40741 | -0.20142 | -0.073242 | 0.068665 | 60.8734 | 60.7269 | 123.5184 | 123.8571 | -0.09613 | 123.8525 | 61.4731 | -0.20142 | 123.8571 | -0.09613 | 61.4731 | 123.5184 | 123.8525 | -124.0906 | -124.1272
737.7188 | 124.0952 | -61.2671 | 62.6404 | -0.22255 | 0.0061971 | 0.011491 | 0.001852 | 0.068152 | -0.0018285 | 0.069222 | -61.2991 | 62.6175 | -61.4365 | -61.3953 | 62.3108 | 0.27008 | -0.43945 | -0.51727 | 62.5992 | -61.4594 | -0.16937 | -0.022888 | -0.032043 | -0.12817 | -0.32959 | -0.19226 | -0.041199 | 0.13733 | 60.8276 | 60.7498 | 123.5779 | 123.8846 | -0.032043 | 123.8663 | 61.5372 | -0.19226 | 123.8846 | -0.032043 | 61.5372 | 123.5779 | 123.8663 | -124.0768 | -124.0997
738.7188 | 124.1135 | -61.2213 | 62.645 | -0.17677 | 0.0066245 | 0.009141 | 0.0012112 | 0.06687 | -0.0020421 | 0.069436 | -61.2991 | 62.6038 | -61.4456 | -61.409 | 62.3199 | 0.26093 | -0.4303 | -0.50354 | 62.59 | -61.4456 | -0.22431 | -0.041198 | -0.07782 | -0.18768 | -0.32501 | -0.22431 | -0.054931 | 0.14649 | 60.791 | 60.7178 | 123.5413 | 123.8251 | -0.07782 | 123.8113 | 61.4822 | -0.22431 | 123.8251 | -0.07782 | 61.4822 | 123.5413 | 123.8113 | -124.0906 | -124.0906
739.7188 | 124.1043 | -61.235 | 62.6221 | -0.047073 | 0.0076925 | 0.0095682 | 0.00014304 | 0.067939 | -0.0020421 | 0.069009 | -61.2946 | 62.5854 | -61.4456 | -61.4319 | 62.2696 | 0.2243 | -0.46234 | -0.58136 | 62.6038 | -61.4822 | -0.21057 | -0.036621 | -0.05951 | -0.19684 | -0.35248 | -0.24719 | -0.01831 | 0.15106 | 60.7727 | 60.6537 | 123.5046 | 123.8205 | -0.05951 | 123.8388 | 61.4593 | -0.24719 | 123.8205 | -0.05951 | 61.4593 | 123.5046 | 123.8388 | -124.0677 | -124.1043
740.7188 | 124.0997 | -61.2534 | 62.645 | -0.14626 | 0.0074789 | 0.0080728 | 0.00014304 | 0.068793 | -0.00076053 | 0.068368 | -61.3129 | 62.6266 | -61.4365 | -61.4227 | 62.3108 | 0.2655 | -0.40741 | -0.52185 | 62.5946 | -61.4639 | -0.1831 | -0.01831 | -0.059509 | -0.16937 | -0.33417 | -0.21057 | -0.050354 | 0.1236 | 60.8459 | 60.7315 | 123.5641 | 123.88 | -0.059509 | 123.848 | 61.5189 | -0.21057 | 123.88 | -0.059509 | 61.5189 | 123.5641 | 123.848 | -124.0814 | -124.1089
741.7188 | 124.0768 | -61.2488 | 62.6724 | -0.16914 | 0.0072653 | 0.0089274 | -0.0013522 | 0.069007 | -0.0033239 | 0.069009 | -61.322 | 62.6266 | -61.4456 | -61.4273 | 62.2696 | 0.28839 | -0.40283 | -0.53101 | 62.6129 | -61.4548 | -0.19684 | -0.045776 | -0.073242 | -0.17853 | -0.40283 | -0.20599 | -0.059509 | 0.1236 | 60.8459 | 60.7178 | 123.5184 | 123.8754 | -0.073242 | 123.8617 | 61.5372 | -0.20599 | 123.8754 | -0.073242 | 61.5372 | 123.5184 | 123.8617 | -124.118 | -124.1272
742.7188 | 124.0631 | -61.2625 | 62.6816 | -1.6569 | 0.0068381 | 0.015763 | -0.00049776 | 0.065589 | -0.00097413 | 0.067513 | -61.4456 | 62.6358 | -61.4365 | -61.4777 | 62.233 | 0.28839 | -0.34332 | -0.54474 | 62.6221 | -61.4731 | -0.17395 | -0.045777 | -0.18311 | -0.21515 | -0.44861 | -0.21057 | -0.05951 | -0.009156 | 60.9192 | 60.7178 | 123.4955 | 123.8983 | -0.18311 | 123.8846 | 61.5509 | -0.21057 | 123.8983 | -0.18311 | 61.5509 | 123.4955 | 123.8846 | -124.118 | -124.1547
743.7188 | 124.0768 | -61.2534 | 62.6724 | -0.13863 | 0.0094015 | 0.0082864 | 0.00014304 | 0.06687 | -0.0011877 | 0.069222 | -61.3174 | 62.5992 | -61.4227 | -61.4502 | 62.2604 | 0.31128 | -0.39368 | -0.54016 | 62.6221 | -61.4685 | -0.16937 | -0.073242 | -0.064087 | -0.19684 | -0.41199 | -0.21515 | -0.050354 | 0.10528 | 60.8597 | 60.7132 | 123.5138 | 123.8525 | -0.064087 | 123.8754 | 61.5646 | -0.21515 | 123.8525 | -0.064087 | 61.5646 | 123.5138 | 123.8754 | -124.0952 | -124.1409
744.7188 | 124.0448 | -61.2534 | 62.6312 | 0.029221 | 0.0076925 | 0.012132 | -0.00028416 | 0.067725 | -0.0018285 | 0.069009 | -61.3403 | 62.6175 | -61.4273 | -61.4822 | 62.2284 | 0.2243 | -0.48981 | -0.66834 | 62.6038 | -61.4914 | -0.17395 | -0.013733 | -0.086975 | -0.22888 | -0.40283 | -0.23804 | -0.027466 | 0.086975 | 60.7636 | 60.585 | 123.4818 | 123.8709 | -0.086975 | 123.8571 | 61.4777 | -0.23804 | 123.8709 | -0.086975 | 61.4777 | 123.4818 | 123.8571 | -124.0585 | -124.1226
745.7188 | 124.1043 | -61.2671 | 62.645 | -0.15388 | 0.0076925 | 0.0085 | 0.00099764 | 0.067511 | -0.0014013 | 0.06965 | -61.29 | 62.6221 | -61.4319 | -61.4044 | 62.3062 | 0.33417 | -0.46692 | -0.50354 | 62.6083 | -61.4685 | -0.16479 | -0.022888 | -0.022888 | -0.13733 | -0.33875 | -0.20142 | -0.036621 | 0.14191 | 60.8002 | 60.7636 | 123.5733 | 123.8892 | -0.022888 | 123.8754 | 61.6013 | -0.20142 | 123.8892 | -0.022888 | 61.6013 | 123.5733 | 123.8754 | -124.0768 | -124.1135
746.7188 | 124.1089 | -61.2579 | 62.645 | -0.16151 | 0.0072653 | 0.009141 | -0.0013522 | 0.068152 | -0.00033333 | 0.069222 | -61.3129 | 62.6175 | -61.4227 | -61.4182 | 62.265 | 0.36163 | -0.44403 | -0.52185 | 62.6175 | -61.4731 | -0.16479 | -0.027465 | -0.054931 | -0.16022 | -0.37994 | -0.21515 | -0.027465 | 0.10986 | 60.8139 | 60.7361 | 123.523 | 123.8754 | -0.054931 | 123.8754 | 61.6196 | -0.21515 | 123.8754 | -0.054931 | 61.6196 | 123.523 | 123.8754 | -124.0677 | -124.118
747.7188 | 124.0952 | -61.2305 | 62.6587 | -0.20729 | 0.0049155 | 0.0087138 | -0.0011386 | 0.067511 | -0.0041785 | 0.069009 | -61.3129 | 62.6175 | -61.4182 | -61.4319 | 62.265 | 0.36163 | -0.40741 | -0.54016 | 62.6266 | -61.4639 | -0.18768 | -0.041198 | -0.082397 | -0.20142 | -0.39368 | -0.23346 | -0.032043 | 0.10529 | 60.8231 | 60.6903 | 123.4955 | 123.848 | -0.082397 | 123.8571 | 61.5921 | -0.23346 | 123.848 | -0.082397 | 61.5921 | 123.4955 | 123.8571 | -124.0768 | -124.1226
748.7188 | 124.086 | -61.2259 | 62.6724 | -0.15388 | 0.0061971 | 0.0082864 | -0.0028476 | 0.066443 | -0.0024695 | 0.070077 | -61.3312 | 62.6129 | -61.4044 | -61.4365 | 62.2604 | 0.37537 | -0.41657 | -0.53101 | 62.6404 | -61.4594 | -0.17853 | -0.059509 | -0.10529 | -0.21057 | -0.41199 | -0.23346 | -0.032043 | 0.073242 | 60.8093 | 60.6949 | 123.4863 | 123.8388 | -0.10529 | 123.8663 | 61.6013 | -0.23346 | 123.8388 | -0.10529 | 61.6013 | 123.4863 | 123.8663 | -124.0768 | -124.1318
749.7188 | 124.0631 | -61.2442 | 62.6633 | 0.067368 | 0.0064107 | 0.0085 | 0.00078404 | 0.06922 | -0.0028967 | 0.070718 | -61.3312 | 62.6083 | -61.441 | -61.4868 | 62.1918 | 0.29755 | -0.48981 | -0.64087 | 62.59 | -61.4777 | -0.19684 | -0.054932 | -0.086975 | -0.24261 | -0.4715 | -0.23346 | -0.073242 | 0.10986 | 60.7544 | 60.6033 | 123.436 | 123.8525 | -0.086975 | 123.8342 | 61.5417 | -0.23346 | 123.8525 | -0.086975 | 61.5417 | 123.436 | 123.8342 | -124.1043 | -124.1409
750.7188 | 124.0448 | -61.2396 | 62.6587 | -0.34462 | 0.0053427 | 0.007432 | -0.0047702 | 0.068366 | -0.00033333 | 0.068368 | -61.322 | 62.6129 | -61.441 | -61.4456 | 62.2375 | 0.39825 | -0.41199 | -0.53101 | 62.6312 | -61.441 | -0.20142 | -0.045776 | -0.082397 | -0.20599 | -0.42114 | -0.20142 | -0.027465 | 0.11902 | 60.8276 | 60.7086 | 123.4772 | 123.8525 | -0.082397 | 123.8708 | 61.6379 | -0.20142 | 123.8525 | -0.082397 | 61.6379 | 123.4772 | 123.8708 | -124.0997 | -124.0997
751.7188 | 124.1043 | -61.2305 | 62.6678 | -0.19203 | 0.0064107 | 0.0097818 | 0.0012112 | 0.067725 | -0.0026831 | 0.069436 | -61.3037 | 62.6266 | -61.4136 | -61.4227 | 62.2604 | 0.42114 | -0.4303 | -0.51727 | 62.6358 | -61.4822 | -0.1831 | -0.041199 | -0.073242 | -0.19226 | -0.40741 | -0.25177 | -0.032044 | 0.10986 | 60.8002 | 60.7132 | 123.4909 | 123.8571 | -0.073242 | 123.8663 | 61.6516 | -0.25177 | 123.8571 | -0.073242 | 61.6516 | 123.4909 | 123.8663 | -124.0814 | -124.1501
752.7188 | 124.086 | -61.2259 | 62.6953 | -0.21492 | 0.0055563 | 0.0089274 | 0.0016384 | 0.068793 | -0.0022559 | 0.068154 | -61.322 | 62.6266 | -61.4273 | -61.4227 | 62.2467 | 0.4303 | -0.44403 | -0.54016 | 62.645 | -61.4685 | -0.20142 | -0.068664 | -0.09613 | -0.19684 | -0.44861 | -0.24262 | -0.050354 | 0.10529 | 60.7819 | 60.6857 | 123.4726 | 123.8525 | -0.09613 | 123.8708 | 61.6562 | -0.24262 | 123.8525 | -0.09613 | 61.6562 | 123.4726 | 123.8708 | -124.1226 | -124.1638
753.7188 | 124.0906 | -61.2442 | 62.6633 | -0.1844 | 0.0074789 | 0.0099954 | 0.00057044 | 0.067725 | -0.0016149 | 0.067941 | -61.3358 | 62.6129 | -61.4136 | -61.4319 | 62.2467 | 0.44403 | -0.41199 | -0.54016 | 62.6221 | -61.4639 | -0.16937 | -0.050354 | -0.091552 | -0.18768 | -0.41656 | -0.21973 | -0.041199 | 0.07782 | 60.8322 | 60.704 | 123.4909 | 123.8571 | -0.091552 | 123.8663 | 61.6882 | -0.21973 | 123.8571 | -0.091552 | 61.6882 | 123.4909 | 123.8663 | -124.0768 | -124.1272
754.7188 | 124.0402 | -61.2442 | 62.6587 | -0.34462 | 0.0076925 | 0.0089274 | -0.0017796 | 0.070075 | -0.0018285 | 0.069222 | -61.322 | 62.6175 | -61.4273 | -61.4456 | 62.2513 | 0.46692 | -0.39825 | -0.53558 | 62.6266 | -61.4777 | -0.1831 | -0.041198 | -0.077819 | -0.20142 | -0.40741 | -0.23346 | -0.032043 | 0.10529 | 60.8459 | 60.7086 | 123.4955 | 123.8617 | -0.077819 | 123.8709 | 61.7111 | -0.23346 | 123.8617 | -0.077819 | 61.7111 | 123.4955 | 123.8709 | -124.086 | -124.1364
755.7188 | 124.086 | -61.2534 | 62.6862 | -0.23018 | 0.0068381 | 0.0095682 | -0.0028476 | 0.065589 | -0.00033333 | 0.068368 | -61.3174 | 62.5717 | -61.4273 | -61.441 | 62.2375 | 0.48981 | -0.41657 | -0.5127 | 62.6175 | -61.4319 | -0.17395 | -0.11444 | -0.064087 | -0.18768 | -0.44861 | -0.17853 | -0.068664 | 0.10986 | 60.8368 | 60.7407 | 123.4909 | 123.8251 | -0.064087 | 123.8709 | 61.7432 | -0.17853 | 123.8251 | -0.064087 | 61.7432 | 123.4909 | 123.8709 | -124.1135 | -124.118
756.7188 | 124.0723 | -61.2442 | 62.6953 | -0.21492 | 0.0064107 | 0.0048684 | -0.0019932 | 0.066016 | -0.00097413 | 0.068154 | -61.2991 | 62.59 | -61.4182 | -61.409 | 62.2696 | 0.49896 | -0.42572 | -0.48523 | 62.6129 | -61.4365 | -0.17395 | -0.10529 | -0.054931 | -0.16479 | -0.42572 | -0.19226 | -0.082397 | 0.11902 | 60.8185 | 60.759 | 123.5138 | 123.8342 | -0.054931 | 123.8571 | 61.7432 | -0.19226 | 123.8342 | -0.054931 | 61.7432 | 123.5138 | 123.8571 | -124.1135 | -124.1318
757.7188 | 124.0768 | -61.2671 | 62.7182 | -0.2607 | 0.0074789 | 0.0093546 | 0.00014304 | 0.064521 | -0.0024695 | 0.070291 | -61.3312 | 62.5854 | -61.4182 | -61.235 | 62.3199 | 0.39825 | -0.46692 | -0.50354 | 62.6175 | -61.4822 | -0.15106 | -0.13275 | -0.064087 | 0.032044 | -0.39825 | -0.21515 | -0.10071 | 0.086975 | 60.8002 | 60.7636 | 123.587 | 123.8525 | -0.064087 | 123.8846 | 61.6653 | -0.21515 | 123.8525 | -0.064087 | 61.6653 | 123.587 | 123.8846 | -124.1364 | -124.2004
758.7188 | 124.0677 | -61.2213 | 62.645 | -0.16914 | 0.0085471 | 0.010209 | 0.00014304 | 0.06687 | -0.0014013 | 0.069436 | -61.3129 | 62.6266 | -61.409 | -61.4365 | 62.2513 | 0.51727 | -0.4303 | -0.51727 | 62.6175 | -61.4685 | -0.18768 | -0.01831 | -0.091553 | -0.21515 | -0.39368 | -0.24719 | -0.027465 | 0.096131 | 60.791 | 60.704 | 123.4726 | 123.848 | -0.091553 | 123.8388 | 61.7386 | -0.24719 | 123.848 | -0.091553 | 61.7386 | 123.4726 | 123.8388 | -124.054 | -124.1135
759.7344 | 124.1089 | -61.235 | 62.6175 | 0.074997 | 0.0042745 | 0.010636 | -0.0041294 | 0.065375 | -0.0020421 | 0.068582 | -61.3312 | 62.4985 | -61.4136 | -61.4273 | 62.2833 | 0.54474 | -0.61798 | -0.51727 | 62.5854 | -61.4319 | -0.17853 | -0.11902 | -0.096131 | -0.19226 | -0.33417 | -0.19684 | -0.032044 | 0.082397 | 60.6171 | 60.7178 | 123.5184 | 123.7335 | -0.096131 | 123.8205 | 61.7798 | -0.19684 | 123.7335 | -0.096131 | 61.7798 | 123.5184 | 123.8205 | -124.0311 | -124.0494
760.7188 | 124.0952 | -61.2167 | 62.6541 | -0.24544 | 0.0061971 | 0.0095682 | 0.0029202 | 0.066443 | -0.0026831 | 0.069009 | -61.2854 | 62.6221 | -61.3907 | -61.3815 | 62.2879 | 0.57678 | -0.45776 | -0.48065 | 62.6129 | -61.4822 | -0.17395 | -0.032044 | -0.068664 | -0.1648 | -0.36621 | -0.2655 | -0.041199 | 0.10529 | 60.759 | 60.7361 | 123.5046 | 123.8388 | -0.068664 | 123.8297 | 61.7935 | -0.2655 | 123.8388 | -0.068664 | 61.7935 | 123.5046 | 123.8297 | -124.0448 | -124.1364
761.7188 | 124.0814 | -61.2579 | 62.6678 | -0.97786 | 0.0066245 | 0.0085 | 0.00014304 | 0.066016 | -0.0031103 | 0.069009 | -61.3724 | 62.5992 | -61.4456 | -61.4136 | 62.2467 | 0.56763 | -0.42114 | -0.54016 | 62.6312 | -61.4777 | -0.18768 | -0.068665 | -0.11444 | -0.15564 | -0.42114 | -0.21973 | -0.036621 | 0.073243 | 60.8368 | 60.7178 | 123.5046 | 123.8571 | -0.11444 | 123.8892 | 61.8256 | -0.21973 | 123.8571 | -0.11444 | 61.8256 | 123.5046 | 123.8892 | -124.1135 | -124.1455
762.7188 | 124.0768 | -61.235 | 62.6999 | -0.14626 | 0.0044881 | 0.0059366 | -0.00071136 | 0.065161 | -0.0022559 | 0.068582 | -61.2991 | 62.5946 | -61.4136 | -61.4365 | 62.2513 | 0.59052 | -0.43488 | -0.49439 | 62.6221 | -61.4594 | -0.17853 | -0.10529 | -0.064087 | -0.20142 | -0.44861 | -0.22431 | -0.07782 | 0.11444 | 60.8002 | 60.7407 | 123.4863 | 123.8296 | -0.064087 | 123.8571 | 61.8256 | -0.22431 | 123.8296 | -0.064087 | 61.8256 | 123.4863 | 123.8571 | -124.1135 | -124.1592
763.7188 | 124.0677 | -61.2442 | 62.6816 | -0.24544 | 0.0066245 | 0.0063638 | -0.0011386 | 0.063239 | 0.00073487 | 0.069009 | -61.3037 | 62.6083 | -61.3998 | -61.409 | 62.2604 | 0.61798 | -0.43488 | -0.48065 | 62.6312 | -61.4456 | -0.15564 | -0.073243 | -0.059509 | -0.16479 | -0.42114 | -0.20142 | -0.050354 | 0.09613 | 60.8093 | 60.7636 | 123.5046 | 123.8525 | -0.059509 | 123.8754 | 61.8622 | -0.20142 | 123.8525 | -0.059509 | 61.8622 | 123.5046 | 123.8754 | -124.0814 | -124.1272
764.7188 | 124.0631 | -61.2534 | 62.677 | -0.27596 | 0.0049155 | 0.010423 | 0.00035684 | 0.064307 | -0.0022559 | 0.068795 | -61.3129 | 62.6266 | -61.4273 | -61.2442 | 62.3611 | 0.53101 | -0.46692 | -0.4715 | 62.59 | -61.4777 | -0.17395 | -0.050354 | -0.059509 | 0.009155 | -0.31586 | -0.2243 | -0.086975 | 0.11444 | 60.7864 | 60.7819 | 123.6145 | 123.88 | -0.059509 | 123.8434 | 61.7844 | -0.2243 | 123.88 | -0.059509 | 61.7844 | 123.6145 | 123.8434 | -124.1043 | -124.1547
765.7188 | 124.0677 | -61.2396 | 62.6862 | -0.14626 | 0.0079061 | 0.0089274 | 0.0031338 | 0.066657 | -0.0022559 | 0.069863 | -61.3083 | 62.6495 | -61.4182 | -61.4273 | 62.2604 | 0.6546 | -0.42572 | -0.48981 | 62.6266 | -61.4685 | -0.17853 | -0.036621 | -0.068665 | -0.18768 | -0.42572 | -0.22888 | -0.059509 | 0.10986 | 60.8139 | 60.7498 | 123.5001 | 123.8892 | -0.068665 | 123.8663 | 61.8942 | -0.22888 | 123.8892 | -0.068665 | 61.8942 | 123.5001 | 123.8663 | -124.1043 | -124.1547
766.7188 | 124.086 | -61.2305 | 62.6862 | -0.19203 | 0.0057699 | 0.006791 | 0.00078404 | 0.065589 | -0.0050329 | 0.069863 | -61.3174 | 62.6129 | -61.4136 | -61.4136 | 62.2559 | 0.65002 | -0.44403 | -0.48065 | 62.6358 | -61.4365 | -0.1831 | -0.073242 | -0.086975 | -0.1831 | -0.4303 | -0.20599 | -0.050354 | 0.09613 | 60.7864 | 60.7498 | 123.4863 | 123.8434 | -0.086975 | 123.8663 | 61.8805 | -0.20599 | 123.8434 | -0.086975 | 61.8805 | 123.4863 | 123.8663 | -124.0997 | -124.1226
767.7188 | 124.0494 | -61.2259 | 62.6678 | -0.22255 | 0.0068381 | 0.0095682 | -0.00071136 | 0.06623 | -0.0018285 | 0.069436 | -61.3129 | 62.6083 | -61.4227 | -61.409 | 62.2604 | 0.67291 | -0.41199 | -0.48981 | 62.6587 | -61.4456 | -0.19684 | -0.05951 | -0.086975 | -0.18311 | -0.40741 | -0.21973 | -0.009156 | 0.10986 | 60.8139 | 60.7361 | 123.4863 | 123.8342 | -0.086975 | 123.8846 | 61.8988 | -0.21973 | 123.8342 | -0.086975 | 61.8988 | 123.4863 | 123.8846 | -124.0906 | -124.1135
768.7188 | 124.0952 | -61.235 | 62.6862 | -0.17677 | 0.0081197 | 0.0132 | -0.00071136 | 0.067939 | -0.0016149 | 0.067941 | -61.2946 | 62.6221 | -61.4182 | -61.4182 | 62.2604 | 0.70038 | -0.41199 | -0.48981 | 62.6266 | -61.441 | -0.18311 | -0.064087 | -0.05951 | -0.18311 | -0.42572 | -0.20599 | -0.059509 | 0.1236 | 60.8231 | 60.7452 | 123.4955 | 123.8571 | -0.05951 | 123.8617 | 61.9354 | -0.20599 | 123.8571 | -0.05951 | 61.9354 | 123.4955 | 123.8617 | -124.1043 | -124.1272
769.7188 | 124.0631 | -61.235 | 62.6862 | -0.19966 | 0.0044881 | 0.01085 | -0.0011386 | 0.066443 | -0.0026831 | 0.066445 | -61.3037 | 62.6175 | -61.4182 | -61.4319 | 62.2513 | 0.70953 | -0.3891 | -0.4715 | 62.6312 | -61.4456 | -0.18311 | -0.068664 | -0.068665 | -0.19684 | -0.43487 | -0.21057 | -0.054931 | 0.11444 | 60.8459 | 60.7635 | 123.4863 | 123.8525 | -0.068665 | 123.8663 | 61.9446 | -0.21057 | 123.8525 | -0.068665 | 61.9446 | 123.4863 | 123.8663 | -124.1043 | -124.1318
770.7188 | 124.0677 | -61.2442 | 62.6953 | -0.25307 | 0.0074789 | 0.005723 | -0.0022068 | 0.065802 | -0.0011877 | 0.069436 | -61.3174 | 62.6175 | -61.3907 | -61.409 | 62.2559 | 0.74616 | -0.3891 | -0.44861 | 62.6038 | -61.4227 | -0.14648 | -0.077819 | -0.073242 | -0.16479 | -0.43945 | -0.17853 | -0.091552 | 0.073242 | 60.8551 | 60.7956 | 123.5001 | 123.8617 | -0.073242 | 123.848 | 61.9904 | -0.17853 | 123.8617 | -0.073242 | 61.9904 | 123.5001 | 123.848 | -124.086 | -124.118
771.7188 | 124.0768 | -61.235 | 62.6816 | 0.059738 | 0.0070517 | 0.0063638 | -0.00049776 | 0.06388 | -0.0016149 | 0.070718 | -61.2946 | 62.6495 | -61.409 | -61.4319 | 62.2604 | 0.74616 | -0.37537 | -0.46234 | 62.6312 | -61.4456 | -0.17395 | -0.032044 | -0.05951 | -0.19684 | -0.42114 | -0.21057 | -0.050354 | 0.11444 | 60.8597 | 60.7727 | 123.4955 | 123.8846 | -0.05951 | 123.8663 | 61.9812 | -0.21057 | 123.8846 | -0.05951 | 61.9812 | 123.4955 | 123.8663 | -124.0906 | -124.1272
772.7188 | 124.1043 | -61.2167 | 62.6816 | -0.16914 | 0.0055563 | 0.0085 | 0.002493 | 0.065375 | -0.0035375 | 0.06965 | -61.2625 | 62.6266 | -61.3953 | -61.3724 | 62.2787 | 0.81482 | -0.44403 | -0.4303 | 62.6358 | -61.4456 | -0.17853 | -0.054932 | -0.045776 | -0.15564 | -0.40283 | -0.22888 | -0.045777 | 0.13275 | 60.7727 | 60.7864 | 123.4955 | 123.8434 | -0.045776 | 123.8525 | 62.0316 | -0.22888 | 123.8434 | -0.045776 | 62.0316 | 123.4955 | 123.8525 | -124.0768 | -124.1272
773.7188 | 124.1272 | -61.2259 | 62.6633 | -0.25307 | 0.0057699 | 0.011064 | 0.00099764 | 0.067298 | -0.0031103 | 0.068582 | -61.2854 | 62.6404 | -61.3861 | -61.3815 | 62.2742 | 0.81482 | -0.43488 | -0.44403 | 62.6404 | -61.4594 | -0.16022 | -0.022888 | -0.059509 | -0.15564 | -0.3891 | -0.23346 | -0.022888 | 0.10071 | 60.791 | 60.7819 | 123.5001 | 123.8663 | -0.059509 | 123.8663 | 62.0407 | -0.23346 | 123.8663 | -0.059509 | 62.0407 | 123.5001 | 123.8663 | -124.0494 | -124.1226
774.7188 | 124.0768 | -61.2122 | 62.6678 | -0.131 | 0.0066245 | 0.009141 | 0.0016384 | 0.068579 | -0.0024695 | 0.067941 | -61.2534 | 62.6266 | -61.4182 | -61.3861 | 62.2787 | 0.83313 | -0.42572 | -0.43488 | 62.6541 | -61.441 | -0.20599 | -0.041199 | -0.041199 | -0.17395 | -0.3891 | -0.22888 | -0.013733 | 0.16479 | 60.7864 | 60.7773 | 123.4909 | 123.8388 | -0.041199 | 123.8663 | 62.0453 | -0.22888 | 123.8388 | -0.041199 | 62.0453 | 123.4909 | 123.8663 | -124.086 | -124.1089
775.7188 | 124.1135 | -61.2305 | 62.6724 | -0.19203 | 0.0081197 | 0.011918 | 0.0014248 | 0.066443 | -0.0016149 | 0.068368 | -61.2808 | 62.6175 | -61.3998 | -61.3907 | 62.2696 | 0.83313 | -0.41657 | -0.43488 | 62.6404 | -61.4365 | -0.16937 | -0.054931 | -0.050354 | -0.16022 | -0.40283 | -0.20599 | -0.032043 | 0.11902 | 60.8139 | 60.7956 | 123.5001 | 123.848 | -0.050354 | 123.8708 | 62.0636 | -0.20599 | 123.848 | -0.050354 | 62.0636 | 123.5001 | 123.8708 | -124.0723 | -124.1089
776.7188 | 124.0402 | -61.2213 | 62.6862 | 0.16655 | 0.0070517 | 0.010636 | 0.00057044 | 0.06687 | -0.0020421 | 0.067727 | -61.3083 | 62.6541 | -61.4044 | -61.4182 | 62.233 | 0.83771 | -0.37079 | -0.48523 | 62.6495 | -61.4639 | -0.18311 | -0.032043 | -0.086976 | -0.19684 | -0.45319 | -0.24262 | -0.036621 | 0.09613 | 60.8505 | 60.7361 | 123.4543 | 123.8754 | -0.086976 | 123.8708 | 62.059 | -0.24262 | 123.8754 | -0.086976 | 62.059 | 123.4543 | 123.8708 | -124.0906 | -124.1501
777.7188 | 124.0677 | -61.2259 | 62.7045 | -0.99312 | 0.0059835 | 0.0085 | 0.00099764 | 0.067939 | -0.00097413 | 0.068795 | -61.3541 | 62.6221 | -61.409 | -61.3907 | 62.2467 | 0.85602 | -0.36621 | -0.47607 | 62.6266 | -61.4365 | -0.18311 | -0.082398 | -0.12817 | -0.1648 | -0.45776 | -0.21057 | -0.07782 | 0.054932 | 60.8597 | 60.7498 | 123.4726 | 123.848 | -0.12817 | 123.8525 | 62.0819 | -0.21057 | 123.848 | -0.12817 | 62.0819 | 123.4726 | 123.8525 | -124.1135 | -124.1409
778.7188 | 124.0723 | -61.2213 | 62.6862 | -0.1844 | 0.0068381 | 0.0078592 | 0.00035684 | 0.067939 | -0.0014013 | 0.069436 | -61.29 | 62.6404 | -61.3678 | -61.3953 | 62.2787 | 0.89264 | -0.38452 | -0.4303 | 62.6312 | -61.4456 | -0.14648 | -0.045776 | -0.068665 | -0.17395 | -0.40741 | -0.22431 | -0.054931 | 0.07782 | 60.8368 | 60.791 | 123.5001 | 123.8617 | -0.068665 | 123.8525 | 62.114 | -0.22431 | 123.8617 | -0.068665 | 62.114 | 123.5001 | 123.8525 | -124.054 | -124.1318
779.7188 | 124.173 | -61.171 | 62.6221 | 0.17418 | 0.0076925 | 0.0082864 | -0.0019932 | 0.066657 | -0.0028967 | 0.067941 | -61.235 | 62.5259 | -61.3998 | -61.5417 | 62.4252 | 1.0529 | -0.70953 | -0.46692 | 62.558 | -61.377 | -0.22888 | -0.09613 | -0.064087 | -0.37079 | -0.19684 | -0.20599 | -0.064087 | 0.1648 | 60.4614 | 60.704 | 123.5962 | 123.6969 | -0.064087 | 123.7289 | 62.2238 | -0.20599 | 123.6969 | -0.064087 | 62.2238 | 123.5962 | 123.7289 | -124.0219 | -123.999
780.7188 | 124.0952 | -61.203 | 62.6541 | -0.09285 | 0.0074789 | 0.0097818 | 0.004202 | 0.065161 | -0.0014013 | 0.068368 | -61.2442 | 62.645 | -61.377 | -61.3586 | 62.2696 | 0.93842 | -0.4715 | -0.4303 | 62.6266 | -61.4456 | -0.17395 | -0.009156 | -0.041199 | -0.15564 | -0.38452 | -0.24262 | -0.027466 | 0.13275 | 60.7315 | 60.7727 | 123.4726 | 123.848 | -0.041199 | 123.8297 | 62.1414 | -0.24262 | 123.848 | -0.041199 | 62.1414 | 123.4726 | 123.8297 | -124.0311 | -124.0997
781.7188 | 124.1135 | -61.2213 | 62.6724 | -0.19966 | 0.0083333 | 0.007432 | 0.0048428 | 0.06922 | -0.0035375 | 0.070504 | -61.2396 | 62.6266 | -61.4182 | -61.3586 | 62.2604 | 0.9613 | -0.47607 | -0.43945 | 62.6495 | -61.4319 | -0.19684 | -0.045776 | -0.018311 | -0.13733 | -0.41199 | -0.21057 | -0.022888 | 0.17853 | 60.7452 | 60.7819 | 123.4818 | 123.848 | -0.018311 | 123.8708 | 62.1826 | -0.21057 | 123.848 | -0.018311 | 62.1826 | 123.4818 | 123.8708 | -124.0906 | -124.1043
782.7188 | 124.086 | -61.2076 | 62.6678 | -0.16914 | 0.0061971 | 0.014054 | 0.00099764 | 0.06922 | -0.0028967 | 0.068582 | -61.2213 | 62.6678 | -61.3907 | -61.3495 | 62.2833 | 0.97046 | -0.4715 | -0.43488 | 62.6129 | -61.4548 | -0.18311 | 0 | -0.013732 | -0.14191 | -0.38452 | -0.24719 | -0.054932 | 0.16937 | 60.7361 | 60.7727 | 123.4909 | 123.8754 | -0.013732 | 123.8205 | 62.178 | -0.24719 | 123.8754 | -0.013732 | 62.178 | 123.4909 | 123.8205 | -124.0585 | -124.1226
783.7188 | 124.0768 | -61.2259 | 62.6907 | -0.1844 | 0.0079061 | 0.011491 | 0.001852 | 0.067084 | -0.0024695 | 0.067727 | -61.2854 | 62.6495 | -61.3815 | -61.409 | 62.2742 | 0.95673 | -0.38452 | -0.44403 | 62.6541 | -61.4273 | -0.15564 | -0.041199 | -0.059509 | -0.18311 | -0.41656 | -0.20142 | -0.036621 | 0.096131 | 60.8414 | 60.7819 | 123.5001 | 123.8754 | -0.059509 | 123.88 | 62.1826 | -0.20142 | 123.8754 | -0.059509 | 62.1826 | 123.5001 | 123.88 | -124.0723 | -124.118
784.7188 | 124.0952 | -61.203 | 62.709 | -0.16151 | 0.0076925 | 0.0072184 | 0.00035684 | 0.067511 | -0.0016149 | 0.067727 | -61.2808 | 62.6633 | -61.3861 | -61.3907 | 62.265 | 0.96588 | -0.36621 | -0.45319 | 62.6266 | -61.4273 | -0.1831 | -0.045776 | -0.07782 | -0.18768 | -0.44403 | -0.2243 | -0.082397 | 0.10529 | 60.8368 | 60.7498 | 123.468 | 123.8663 | -0.07782 | 123.8297 | 62.1689 | -0.2243 | 123.8663 | -0.07782 | 62.1689 | 123.468 | 123.8297 | -124.0952 | -124.1364
785.7188 | 124.0952 | -61.2167 | 62.6816 | -0.14626 | 0.0051291 | 0.01085 | 0.002493 | 0.069434 | -0.0031103 | 0.06965 | -61.2213 | 62.6633 | -61.3953 | -61.3632 | 62.2971 | 1.0208 | -0.44861 | -0.41199 | 62.6358 | -61.409 | -0.17853 | -0.018311 | -0.004577 | -0.14648 | -0.38452 | -0.19226 | -0.045777 | 0.17395 | 60.7681 | 60.8047 | 123.5138 | 123.88 | -0.004577 | 123.8525 | 62.2375 | -0.19226 | 123.88 | -0.004577 | 62.2375 | 123.5138 | 123.8525 | -124.0768 | -124.0906
786.7188 | 124.086 | -61.203 | 62.6724 | -1.2373 | 0.0070517 | 0.0087138 | 0.00057044 | 0.067939 | -0.0022559 | 0.067727 | -61.2259 | 62.645 | -61.377 | -61.3632 | 62.2787 | 1.0483 | -0.4715 | -0.42114 | 62.6175 | -61.441 | -0.17395 | -0.027466 | -0.022888 | -0.16022 | -0.39368 | -0.23804 | -0.054931 | 0.15106 | 60.7315 | 60.7819 | 123.4818 | 123.848 | -0.022888 | 123.8205 | 62.2513 | -0.23804 | 123.848 | -0.022888 | 62.2513 | 123.4818 | 123.8205 | -124.0494 | -124.1135
787.7188 | 124.0585 | -61.2442 | 62.6953 | -0.047073 | 0.0076925 | 0.007432 | 0.0016384 | 0.070288 | -0.0016149 | 0.067727 | -61.3998 | 62.6358 | -61.409 | -61.3632 | 62.2787 | 1.062 | -0.48065 | -0.43488 | 62.6404 | -61.4365 | -0.16479 | -0.059509 | -0.15564 | -0.11902 | -0.41656 | -0.19226 | -0.054931 | 0.009156 | 60.7636 | 60.8093 | 123.523 | 123.88 | -0.15564 | 123.8846 | 62.3062 | -0.19226 | 123.88 | -0.15564 | 62.3062 | 123.523 | 123.8846 | -124.1043 | -124.1318
788.7188 | 124.1089 | -61.1938 | 62.6633 | -0.054703 | 0.0087607 | 0.010636 | 0.00057044 | 0.068152 | -0.0016149 | 0.06965 | -61.235 | 62.6266 | -61.3861 | -61.4044 | 62.2742 | 1.1078 | -0.46234 | -0.41657 | 62.645 | -61.4502 | -0.19226 | -0.036621 | -0.041198 | -0.21057 | -0.3891 | -0.25635 | -0.018311 | 0.15106 | 60.7315 | 60.7773 | 123.468 | 123.8205 | -0.041198 | 123.8388 | 62.3016 | -0.25635 | 123.8205 | -0.041198 | 62.3016 | 123.468 | 123.8388 | -124.0494 | -124.1135
789.7188 | 124.1547 | -61.1984 | 62.6724 | -0.67268 | 0.0055563 | 0.005723 | -0.0081882 | 0.067298 | -0.0018285 | 0.070077 | -61.3953 | 62.5626 | -61.3907 | -61.4182 | 62.2696 | 1.062 | -0.54016 | -0.46234 | 62.5946 | -61.377 | -0.19226 | -0.10986 | -0.19684 | -0.21973 | -0.40283 | -0.17853 | -0.07782 | -0.004578 | 60.6583 | 60.7361 | 123.468 | 123.761 | -0.19684 | 123.793 | 62.2604 | -0.17853 | 123.761 | -0.19684 | 62.2604 | 123.468 | 123.793 | -124.0631 | -124.0494
790.7188 | 124.1089 | -61.2167 | 62.6862 | -0.16914 | 0.0081197 | 0.010636 | 0.0037746 | 0.067298 | -0.0024695 | 0.067513 | -61.2488 | 62.6633 | -61.3586 | -61.377 | 62.2742 | 1.1032 | -0.39368 | -0.41199 | 62.6175 | -61.4639 | -0.14191 | -0.022888 | -0.032043 | -0.16022 | -0.41199 | -0.24719 | -0.068664 | 0.10986 | 60.8231 | 60.8047 | 123.4909 | 123.88 | -0.032043 | 123.8342 | 62.3199 | -0.24719 | 123.88 | -0.032043 | 62.3199 | 123.4909 | 123.8342 | -124.0448 | -124.1501
791.7188 | 124.086 | -61.1938 | 62.6953 | -0.19966 | 0.0087607 | 0.007432 | 0.0020656 | 0.066657 | -0.0018285 | 0.0673 | -61.2671 | 62.6724 | -61.4044 | -61.377 | 62.265 | 1.1032 | -0.38452 | -0.43945 | 62.6404 | -61.4182 | -0.21057 | -0.022888 | -0.073242 | -0.1831 | -0.4303 | -0.2243 | -0.054931 | 0.13733 | 60.8093 | 60.7544 | 123.4589 | 123.8663 | -0.073242 | 123.8342 | 62.2971 | -0.2243 | 123.8663 | -0.073242 | 62.2971 | 123.4589 | 123.8342 | -124.0997 | -124.1135
792.7188 | 124.1043 | -61.2076 | 62.6862 | -0.12337 | 0.0057699 | 0.014054 | 0.0039882 | 0.065802 | -0.0035375 | 0.067727 | -61.235 | 62.6587 | -61.3907 | -61.3495 | 62.2787 | 1.1307 | -0.43945 | -0.43488 | 62.6358 | -61.4227 | -0.18311 | -0.027466 | -0.027465 | -0.14191 | -0.40741 | -0.21515 | -0.050354 | 0.15564 | 60.7681 | 60.7727 | 123.4863 | 123.8663 | -0.027465 | 123.8434 | 62.3383 | -0.21515 | 123.8663 | -0.027465 | 62.3383 | 123.4863 | 123.8434 | -124.0768 | -124.1089
793.7188 | 124.0814 | -61.1938 | 62.6816 | -0.08522 | 0.0098287 | 0.013841 | 0.0033474 | 0.067084 | -0.0035375 | 0.069436 | -61.4044 | 62.6358 | -61.409 | -61.3495 | 62.2879 | 1.1536 | -0.47607 | -0.44403 | 62.6312 | -61.4365 | -0.21515 | -0.045777 | -0.21057 | -0.15564 | -0.39368 | -0.24261 | -0.050354 | 0.004578 | 60.7178 | 60.7498 | 123.4818 | 123.8297 | -0.21057 | 123.8251 | 62.3474 | -0.24261 | 123.8297 | -0.21057 | 62.3474 | 123.4818 | 123.8251 | -124.0906 | -124.118
794.7188 | 124.1364 | -61.203 | 62.6907 | -0.131 | 0.0068381 | 0.0063638 | 0.0031338 | 0.067511 | -0.0022559 | 0.070931 | -61.203 | 62.6312 | -61.4044 | -61.4594 | 62.3657 | 1.2222 | -0.48523 | -0.40741 | 62.645 | -61.4456 | -0.20142 | -0.059509 | 0 | -0.25635 | -0.32501 | -0.24262 | -0.045777 | 0.20142 | 60.7178 | 60.7956 | 123.5687 | 123.8342 | 0 | 123.848 | 62.4252 | -0.24262 | 123.8342 | 0 | 62.4252 | 123.5687 | 123.848 | -124.0952 | -124.1364
795.7188 | 124.1089 | -61.203 | 62.6587 | -0.08522 | 0.0079061 | 0.011704 | 0.0016384 | 0.067725 | -0.0016149 | 0.068154 | -61.2259 | 62.6541 | -61.3678 | -61.3724 | 62.2925 | 1.1719 | -0.48065 | -0.44403 | 62.6404 | -61.4365 | -0.16479 | -0.004577 | -0.022888 | -0.16937 | -0.36621 | -0.23346 | -0.01831 | 0.14191 | 60.7224 | 60.759 | 123.4955 | 123.8571 | -0.022888 | 123.8434 | 62.3749 | -0.23346 | 123.8571 | -0.022888 | 62.3749 | 123.4955 | 123.8434 | -124.0265 | -124.0952
796.7188 | 124.118 | -61.1984 | 62.6816 | -0.16151 | 0.0083333 | 0.011491 | 0.0020656 | 0.070075 | -0.0022559 | 0.067086 | -61.2259 | 62.6404 | -61.3815 | -61.3586 | 62.2742 | 1.1948 | -0.48065 | -0.44861 | 62.6404 | -61.3953 | -0.18311 | -0.041199 | -0.027466 | -0.16022 | -0.40741 | -0.19684 | -0.041199 | 0.15564 | 60.7178 | 60.7498 | 123.4726 | 123.8388 | -0.027466 | 123.8388 | 62.3932 | -0.19684 | 123.8388 | -0.027466 | 62.3932 | 123.4726 | 123.8388 | -124.0631 | -124.0768
797.7188 | 124.086 | -61.1847 | 62.7274 | -0.13863 | 0.0072653 | 0.0080728 | -0.00071136 | 0.069861 | -0.00097413 | 0.067727 | -61.2671 | 62.6633 | -61.4044 | -61.3998 | 62.2467 | 1.1765 | -0.39825 | -0.46234 | 62.6678 | -61.4319 | -0.21973 | -0.064087 | -0.082398 | -0.21515 | -0.48065 | -0.24719 | -0.059509 | 0.13733 | 60.7864 | 60.7224 | 123.4314 | 123.848 | -0.082398 | 123.8525 | 62.3611 | -0.24719 | 123.848 | -0.082398 | 62.3611 | 123.4314 | 123.8525 | -124.1318 | -124.1592
798.7188 | 124.0677 | -61.2122 | 62.6862 | -0.19966 | 0.0072653 | 0.010209 | -0.0022068 | 0.067725 | -0.0011877 | 0.070077 | -61.2625 | 62.6678 | -61.3953 | -61.3953 | 62.2284 | 1.1993 | -0.40283 | -0.48065 | 62.6816 | -61.4182 | -0.18311 | -0.01831 | -0.050354 | -0.18311 | -0.45776 | -0.20599 | -0.004577 | 0.13275 | 60.8093 | 60.7315 | 123.4406 | 123.88 | -0.050354 | 123.8937 | 62.4115 | -0.20599 | 123.88 | -0.050354 | 62.4115 | 123.4406 | 123.8937 | -124.0814 | -124.1043
799.7188 | 124.0128 | -61.1847 | 62.677 | -0.10811 | 0.0087607 | 0.012345 | 0.0027066 | 0.070288 | -0.0048193 | 0.070504 | -61.2122 | 62.6678 | -61.3907 | -61.3586 | 62.2604 | 1.2268 | -0.48065 | -0.44861 | 62.6633 | -61.4136 | -0.20599 | -0.009155 | -0.027466 | -0.17395 | -0.41656 | -0.22888 | -0.013733 | 0.17853 | 60.704 | 60.7361 | 123.4451 | 123.8525 | -0.027466 | 123.848 | 62.4115 | -0.22888 | 123.8525 | -0.027466 | 62.4115 | 123.4451 | 123.848 | -124.0677 | -124.0906
800.7188 | 124.0997 | -61.1938 | 62.6678 | -0.13863 | 0.0083333 | 0.0061502 | 0.0029202 | 0.068366 | -0.0011877 | 0.067086 | -61.2076 | 62.6633 | -61.3632 | -61.3632 | 62.2604 | 1.2497 | -0.4715 | -0.45319 | 62.6633 | -61.4227 | -0.16937 | -0.004578 | -0.013733 | -0.16937 | -0.40741 | -0.22888 | -0.004578 | 0.15564 | 60.7224 | 60.7407 | 123.4543 | 123.8571 | -0.013733 | 123.8571 | 62.4435 | -0.22888 | 123.8571 | -0.013733 | 62.4435 | 123.4543 | 123.8571 | -124.0311 | -124.0906
801.7188 | 124.0631 | -61.203 | 62.6678 | -0.17677 | 0.0083333 | 0.011064 | 0.00035684 | 0.069861 | -0.0024695 | 0.069222 | -61.2305 | 62.6587 | -61.3815 | -61.3586 | 62.3016 | 1.2634 | -0.45776 | -0.45319 | 62.6404 | -61.4136 | -0.17853 | -0.009156 | -0.027466 | -0.15564 | -0.36621 | -0.21057 | -0.027466 | 0.15106 | 60.7452 | 60.7498 | 123.5046 | 123.8617 | -0.027466 | 123.8434 | 62.4664 | -0.21057 | 123.8617 | -0.027466 | 62.4664 | 123.5046 | 123.8434 | -124.0494 | -124.0814
802.7188 | 124.0997 | -61.1801 | 62.6953 | -0.19966 | 0.0068381 | 0.010636 | 0.0020656 | 0.06687 | -0.0022559 | 0.069436 | -61.2396 | 62.6678 | -61.3953 | -61.3678 | 62.2696 | 1.2817 | -0.42114 | -0.43488 | 62.6678 | -61.3998 | -0.21515 | -0.027465 | -0.059509 | -0.18768 | -0.42572 | -0.21973 | -0.027465 | 0.15564 | 60.759 | 60.7452 | 123.4497 | 123.848 | -0.059509 | 123.848 | 62.4619 | -0.21973 | 123.848 | -0.059509 | 62.4619 | 123.4497 | 123.848 | -124.0906 | -124.0952
803.7188 | 124.0906 | -61.1984 | 62.7274 | -0.23018 | 0.0059835 | 0.0065774 | 0.00057044 | 0.068579 | -0.0046057 | 0.068582 | -61.2671 | 62.6816 | -61.377 | -61.3678 | 62.2421 | 1.268 | -0.40283 | -0.48065 | 62.6816 | -61.4273 | -0.17853 | -0.045776 | -0.068665 | -0.16937 | -0.48523 | -0.22888 | -0.045776 | 0.10986 | 60.7956 | 60.7178 | 123.4406 | 123.88 | -0.068665 | 123.88 | 62.4664 | -0.22888 | 123.88 | -0.068665 | 62.4664 | 123.4406 | 123.88 | -124.1043 | -124.1547
804.7188 | 124.0173 | -61.1847 | 62.7136 | -0.22255 | 0.0055563 | 0.0072184 | -0.0039158 | 0.064948 | 0.00094847 | 0.071145 | -61.2808 | 62.6678 | -61.3724 | -61.409 | 62.2421 | 1.2726 | -0.15564 | -0.25635 | 62.7182 | -61.3861 | -0.18768 | -0.045776 | -0.096131 | -0.22431 | -0.4715 | -0.20142 | 0.004578 | 0.091552 | 61.0291 | 60.9283 | 123.4268 | 123.8525 | -0.096131 | 123.9029 | 62.4573 | -0.20142 | 123.8525 | -0.096131 | 62.4573 | 123.4268 | 123.9029 | -124.086 | -124.0997
805.7188 | 124.0723 | -61.1664 | 62.7182 | -0.24544 | 0.0064107 | 0.0065774 | -0.0011386 | 0.066443 | -0.00054693 | 0.066873 | -61.2762 | 62.645 | -61.3815 | -61.3861 | 62.233 | 1.2863 | -0.37994 | -0.49439 | 62.6541 | -61.4319 | -0.21515 | -0.073243 | -0.10986 | -0.21973 | -0.48523 | -0.2655 | -0.064087 | 0.10529 | 60.7864 | 60.672 | 123.3994 | 123.8113 | -0.10986 | 123.8205 | 62.4527 | -0.2655 | 123.8113 | -0.10986 | 62.4527 | 123.3994 | 123.8205 | -124.0997 | -124.1501
806.7188 | 124.0952 | -61.1938 | 62.7411 | -0.1844 | 0.0083333 | 0.005723 | 0.00099764 | 0.06623 | -0.0016149 | 0.068582 | -61.2717 | 62.6633 | -61.3678 | -61.3815 | 62.2421 | 1.3138 | -0.40283 | -0.50354 | 62.6816 | -61.4273 | -0.17395 | -0.07782 | -0.077819 | -0.18768 | -0.49896 | -0.23346 | -0.059509 | 0.096131 | 60.791 | 60.6903 | 123.436 | 123.8571 | -0.077819 | 123.8754 | 62.5076 | -0.23346 | 123.8571 | -0.077819 | 62.5076 | 123.436 | 123.8754 | -124.1089 | -124.1684
807.7188 | 124.0265 | -61.1984 | 62.709 | -0.13863 | 0.0061971 | 0.0089274 | -0.00071136 | 0.066016 | -0.0037511 | 0.06965 | -61.2717 | 62.6587 | -61.377 | -61.3907 | 62.2375 | 1.3184 | -0.40283 | -0.52185 | 62.6862 | -61.4044 | -0.17853 | -0.050354 | -0.073242 | -0.19226 | -0.4715 | -0.20599 | -0.022888 | 0.10529 | 60.7956 | 60.6766 | 123.436 | 123.8571 | -0.073242 | 123.8846 | 62.5168 | -0.20599 | 123.8571 | -0.073242 | 62.5168 | 123.436 | 123.8846 | -124.086 | -124.1135
808.7188 | 124.054 | -61.1847 | 62.7182 | 1.5932 | 0.0049155 | 0.0076456 | -0.0024204 | 0.065589 | -0.0014013 | 0.070291 | -61.2534 | 62.6541 | -61.3953 | -61.3907 | 62.2513 | 1.3458 | -0.3891 | -0.53101 | 62.6907 | -61.3998 | -0.21057 | -0.064087 | -0.068665 | -0.20599 | -0.46692 | -0.21515 | -0.027466 | 0.14191 | 60.7956 | 60.6537 | 123.436 | 123.8388 | -0.068665 | 123.8754 | 62.5305 | -0.21515 | 123.8388 | -0.068665 | 62.5305 | 123.436 | 123.8754 | -124.1135 | -124.118
809.7188 | 123.999 | -61.1893 | 62.7182 | -0.1844 | 0.0066245 | 0.007432 | -0.001566 | 0.063452 | -0.00054693 | 0.070291 | -61.2946 | 62.6724 | -61.3861 | -61.4273 | 62.4893 | 1.5701 | -0.62256 | -0.57678 | 62.6724 | -61.4319 | -0.19684 | -0.045777 | -0.10529 | -0.23804 | -0.22888 | -0.24262 | -0.045777 | 0.091552 | 60.5667 | 60.6125 | 123.6786 | 123.8617 | -0.10529 | 123.8617 | 62.7594 | -0.24262 | 123.8617 | -0.10529 | 62.7594 | 123.6786 | 123.8617 | -124.1043 | -124.1501
810.7188 | 124.0585 | -61.1801 | 62.7502 | -0.27596 | 0.0076925 | 0.010209 | -0.0019932 | 0.064307 | -0.0024695 | 0.068368 | -61.2762 | 62.6587 | -61.3678 | -61.3861 | 62.2192 | 1.3504 | -0.37537 | -0.52643 | 62.677 | -61.4182 | -0.18768 | -0.091553 | -0.09613 | -0.20599 | -0.53101 | -0.23804 | -0.073242 | 0.091553 | 60.8047 | 60.6537 | 123.3994 | 123.8388 | -0.09613 | 123.8571 | 62.5305 | -0.23804 | 123.8388 | -0.09613 | 62.5305 | 123.3994 | 123.8571 | -124.118 | -124.1684
811.7188 | 124.1547 | -61.1389 | 62.7136 | -0.19966 | 0.0055563 | 0.0076456 | -0.0030612 | 0.064521 | -0.0014013 | 0.066445 | -61.1984 | 62.59 | -61.3449 | -61.2991 | 62.3154 | 1.4648 | -0.5127 | -0.43488 | 62.6404 | -61.3724 | -0.20599 | -0.1236 | -0.059509 | -0.16022 | -0.39825 | -0.23346 | -0.073242 | 0.14648 | 60.6262 | 60.704 | 123.4543 | 123.7289 | -0.059509 | 123.7793 | 62.6038 | -0.23346 | 123.7289 | -0.059509 | 62.6038 | 123.4543 | 123.7793 | -124.0585 | -124.086
812.7188 | 124.1409 | -61.1572 | 62.6862 | -0.37514 | 0.0055563 | 0.0076456 | -0.0037022 | 0.065802 | -0.0033239 | 0.066659 | -61.1847 | 62.59 | -61.3449 | -61.29 | 62.3199 | 1.4786 | -0.59052 | -0.41657 | 62.6266 | -61.3724 | -0.18768 | -0.09613 | -0.027465 | -0.13275 | -0.36621 | -0.21515 | -0.059509 | 0.16022 | 60.5667 | 60.7407 | 123.4772 | 123.7473 | -0.027465 | 123.7839 | 62.6358 | -0.21515 | 123.7473 | -0.027465 | 62.6358 | 123.4772 | 123.7839 | -124.0311 | -124.0585
813.7188 | 124.0631 | -61.171 | 62.7182 | -0.23018 | 0.0051291 | 0.0070048 | 0.0016384 | 0.063452 | -0.00097413 | 0.068154 | -61.2442 | 62.6266 | -61.3586 | -61.3815 | 62.2147 | 1.4145 | -0.41199 | -0.52643 | 62.6587 | -61.4136 | -0.18768 | -0.091553 | -0.073243 | -0.21057 | -0.50354 | -0.24261 | -0.05951 | 0.11444 | 60.759 | 60.6445 | 123.3856 | 123.7976 | -0.073243 | 123.8297 | 62.5854 | -0.24261 | 123.7976 | -0.073243 | 62.5854 | 123.3856 | 123.8297 | -124.0768 | -124.1318
814.7188 | 124.0814 | -61.1893 | 62.7365 | -0.21492 | 0.0072653 | 0.0059366 | -0.0019932 | 0.063666 | -0.0018285 | 0.067086 | -61.203 | 62.6038 | -61.3632 | -61.3449 | 62.2421 | 1.4557 | -0.43488 | -0.49439 | 62.6541 | -61.3815 | -0.17395 | -0.13275 | -0.013733 | -0.15564 | -0.49439 | -0.19226 | -0.082397 | 0.16022 | 60.7544 | 60.6949 | 123.4314 | 123.793 | -0.013733 | 123.8434 | 62.645 | -0.19226 | 123.793 | -0.013733 | 62.645 | 123.4314 | 123.8434 | -124.0997 | -124.118
815.7188 | 124.1226 | -61.1435 | 62.7182 | -0.26833 | 0.0072653 | 0.0080728 | -0.001566 | 0.064093 | -0.0018285 | 0.068795 | -61.1893 | 62.5992 | -61.3449 | -61.3083 | 62.2833 | 1.5106 | -0.48065 | -0.46692 | 62.6358 | -61.377 | -0.20142 | -0.11902 | -0.045776 | -0.1648 | -0.43488 | -0.23346 | -0.082398 | 0.15564 | 60.6628 | 60.6766 | 123.4268 | 123.7427 | -0.045776 | 123.7793 | 62.6541 | -0.23346 | 123.7427 | -0.045776 | 62.6541 | 123.4268 | 123.7793 | -124.0631 | -124.0952
816.7188 | 124.1501 | -61.1343 | 62.7136 | -0.16914 | 0.0036337 | 0.010423 | -0.0013522 | 0.062598 | -0.0014013 | 0.067513 | -61.1893 | 62.5626 | -61.3495 | -61.2808 | 62.3108 | 1.5335 | -0.52643 | -0.45776 | 62.6404 | -61.3724 | -0.21515 | -0.15106 | -0.054932 | -0.14648 | -0.40283 | -0.23804 | -0.073242 | 0.16022 | 60.6079 | 60.6766 | 123.4451 | 123.6969 | -0.054932 | 123.7747 | 62.6678 | -0.23804 | 123.6969 | -0.054932 | 62.6678 | 123.4451 | 123.7747 | -124.0631 | -124.086
817.7188 | 124.1821 | -61.1435 | 62.6816 | -0.48195 | 0.0014975 | 0.0065774 | 0.00014304 | 0.062598 | -0.0020421 | 0.0673 | -61.2122 | 62.5809 | -61.3541 | -61.2717 | 62.3337 | 1.5564 | -0.58594 | -0.4715 | 62.6129 | -61.3495 | -0.21057 | -0.10071 | -0.068664 | -0.12817 | -0.3479 | -0.20599 | -0.068665 | 0.14191 | 60.5576 | 60.672 | 123.4772 | 123.7244 | -0.068664 | 123.7564 | 62.6999 | -0.20599 | 123.7244 | -0.068664 | 62.6999 | 123.4772 | 123.7564 | -124.0356 | -124.0311
818.7188 | 124.1638 | -61.1435 | 62.6816 | -0.08522 | 0.0038473 | 0.0082864 | -0.0011386 | 0.063025 | -0.0026831 | 0.069436 | -61.1847 | 62.5442 | -61.3403 | -61.2808 | 62.3245 | 1.5839 | -0.64545 | -0.49439 | 62.6266 | -61.3495 | -0.19684 | -0.13733 | -0.041198 | -0.13733 | -0.35706 | -0.20599 | -0.054932 | 0.15564 | 60.498 | 60.6491 | 123.468 | 123.6877 | -0.041198 | 123.7701 | 62.7274 | -0.20599 | 123.6877 | -0.041198 | 62.7274 | 123.468 | 123.7701 | -124.0219 | -124.0311
819.7188 | 124.1776 | -61.1298 | 62.6862 | -0.016556 | 0.0042745 | 0.0070048 | -0.0030612 | 0.062384 | -0.0033239 | 0.069863 | -61.2122 | 62.5809 | -61.3541 | -61.29 | 62.3108 | 1.5564 | -0.63171 | -0.52643 | 62.6175 | -61.3495 | -0.2243 | -0.10529 | -0.082397 | -0.16022 | -0.37537 | -0.21973 | -0.068664 | 0.14191 | 60.498 | 60.6033 | 123.4406 | 123.7106 | -0.082397 | 123.7473 | 62.6862 | -0.21973 | 123.7106 | -0.082397 | 62.6862 | 123.4406 | 123.7473 | -124.0402 | -124.0356
820.7188 | 124.1821 | -61.1252 | 62.6907 | 0.50224 | 0.0066245 | 0.005723 | -0.00049776 | 0.061103 | -0.00033333 | 0.067513 | -61.3083 | 62.5717 | -61.3403 | -61.2808 | 62.3245 | 1.6434 | -0.60883 | -0.48065 | 62.5992 | -61.377 | -0.21515 | -0.11902 | -0.18311 | -0.15564 | -0.36621 | -0.25177 | -0.091553 | 0.032043 | 60.5164 | 60.6445 | 123.4497 | 123.6969 | -0.18311 | 123.7244 | 62.7686 | -0.25177 | 123.6969 | -0.18311 | 62.7686 | 123.4497 | 123.7244 | -124.0311 | -124.0677
821.7188 | 124.1776 | -61.1114 | 62.6816 | -0.14626 | 0.0021383 | 0.0055094 | -0.002634 | 0.061103 | -0.0033239 | 0.069009 | -61.1481 | 62.5488 | -61.3037 | -61.2305 | 62.3383 | 1.6251 | -0.11444 | -0.24261 | 62.677 | -61.3174 | -0.19226 | -0.13275 | -0.036621 | -0.11902 | -0.34332 | -0.20599 | -0.004578 | 0.15564 | 60.997 | 60.8688 | 123.4497 | 123.6603 | -0.036621 | 123.7885 | 62.7365 | -0.20599 | 123.6603 | -0.036621 | 62.7365 | 123.4497 | 123.7885 | -123.9853 | -123.999
822.7188 | 124.2142 | -61.1206 | 62.6724 | -0.10048 | 0.0059835 | 0.0042276 | 0.00035684 | 0.062171 | -0.0024695 | 0.068795 | -61.1755 | 62.5442 | -61.3403 | -61.2396 | 62.3337 | 1.6525 | -0.66376 | -0.5127 | 62.5854 | -61.3312 | -0.21973 | -0.12817 | -0.054932 | -0.11902 | -0.33875 | -0.21057 | -0.086975 | 0.16479 | 60.4568 | 60.6079 | 123.4543 | 123.6649 | -0.054932 | 123.7061 | 62.7731 | -0.21057 | 123.6649 | -0.054932 | 62.7731 | 123.4543 | 123.7061 | -124.0128 | -124.0036
823.7188 | 124.1684 | -61.1389 | 62.6999 | -0.08522 | 0.0057699 | 0.0046548 | -0.00028416 | 0.063452 | -0.0033239 | 0.068582 | -61.1847 | 62.5946 | -61.3449 | -61.2671 | 62.3062 | 1.6479 | -0.67291 | -0.54016 | 62.5992 | -61.3586 | -0.20599 | -0.10529 | -0.045776 | -0.12817 | -0.39368 | -0.21973 | -0.10071 | 0.16022 | 60.466 | 60.5988 | 123.4451 | 123.7335 | -0.045776 | 123.7381 | 62.7869 | -0.21973 | 123.7335 | -0.045776 | 62.7869 | 123.4451 | 123.7381 | -124.0448 | -124.0585
824.7188 | 124.173 | -61.1435 | 62.7136 | -0.08522 | 0.0051291 | 0.0052958 | -0.0013522 | 0.061957 | -0.0024695 | 0.067941 | -61.1938 | 62.5534 | -61.3358 | -61.2808 | 62.2925 | 1.6434 | -0.66834 | -0.60883 | 62.6129 | -61.3495 | -0.19226 | -0.16022 | -0.050354 | -0.13733 | -0.42114 | -0.20599 | -0.10071 | 0.14191 | 60.4752 | 60.5347 | 123.436 | 123.6969 | -0.050354 | 123.7564 | 62.7869 | -0.20599 | 123.6969 | -0.050354 | 62.7869 | 123.436 | 123.7564 | -124.0494 | -124.0631
825.7188 | 124.1409 | -61.1435 | 62.6907 | 0.03685 | 0.0049155 | 0.0048684 | -0.0022068 | 0.062171 | -0.0014013 | 0.066659 | -61.2442 | 62.5671 | -61.377 | -61.3586 | 62.4939 | 1.7761 | -0.82855 | -0.6546 | 62.6129 | -61.3403 | -0.23346 | -0.1236 | -0.10071 | -0.21515 | -0.19684 | -0.19684 | -0.07782 | 0.13275 | 60.3149 | 60.4889 | 123.6374 | 123.7106 | -0.10071 | 123.7564 | 62.9196 | -0.19684 | 123.7106 | -0.10071 | 62.9196 | 123.6374 | 123.7564 | -124.0677 | -124.0311
826.7188 | 124.1089 | -61.1298 | 62.6862 | 0.074997 | 0.0070517 | 0.0042276 | 0.00078404 | 0.062384 | -0.0018285 | 0.069009 | -61.2488 | 62.5305 | -61.3403 | -61.322 | 62.2421 | 1.6296 | -0.66834 | -0.68665 | 62.5854 | -61.3541 | -0.21057 | -0.15564 | -0.11902 | -0.19226 | -0.44403 | -0.2243 | -0.10071 | 0.091553 | 60.4614 | 60.4431 | 123.3719 | 123.6603 | -0.11902 | 123.7152 | 62.7594 | -0.2243 | 123.6603 | -0.11902 | 62.7594 | 123.3719 | 123.7152 | -124.0265 | -124.0402
827.7188 | 124.1364 | -61.1389 | 62.6907 | -0.0089264 | 0.0066245 | 0.007432 | -0.0028476 | 0.060462 | -0.0018285 | 0.067513 | -61.2396 | 62.5488 | -61.3449 | -61.29 | 62.2787 | 1.68 | -0.68665 | -0.64087 | 62.5946 | -61.3495 | -0.20599 | -0.14191 | -0.10071 | -0.15106 | -0.41199 | -0.21057 | -0.096131 | 0.10529 | 60.4523 | 60.498 | 123.4177 | 123.6877 | -0.10071 | 123.7335 | 62.8189 | -0.21057 | 123.6877 | -0.10071 | 62.8189 | 123.4177 | 123.7335 | -124.0356 | -124.0402
828.7188 | 124.1867 | -61.1389 | 62.7136 | -0.016556 | 0.0032065 | 0.005723 | -0.00028416 | 0.06153 | -0.0020421 | 0.066445 | -61.2259 | 62.5626 | -61.3358 | -61.3037 | 62.2787 | 1.6617 | -0.69122 | -0.68665 | 62.59 | -61.3312 | -0.19684 | -0.15106 | -0.086975 | -0.16479 | -0.43487 | -0.19226 | -0.1236 | 0.10986 | 60.4477 | 60.4523 | 123.4177 | 123.7015 | -0.086975 | 123.7289 | 62.8006 | -0.19226 | 123.7015 | -0.086975 | 62.8006 | 123.4177 | 123.7289 | -124.0494 | -124.0448
829.7188 | 124.118 | -61.1252 | 62.6907 | -0.19203 | 0.0040609 | 0.004014 | -0.0034886 | 0.062598 | 0.0020167 | 0.068582 | -61.2396 | 62.5626 | -61.3358 | -61.2946 | 62.2559 | 1.6617 | -0.68207 | -0.71869 | 62.59 | -61.3632 | -0.21057 | -0.12817 | -0.11444 | -0.16937 | -0.43488 | -0.23804 | -0.10071 | 0.09613 | 60.4431 | 60.4065 | 123.381 | 123.6877 | -0.11444 | 123.7152 | 62.7869 | -0.23804 | 123.6877 | -0.11444 | 62.7869 | 123.381 | 123.7152 | -124.0265 | -124.054
830.7188 | 124.1684 | -61.1389 | 62.677 | -1.9773 | 0.0064107 | 0.005723 | -0.00028416 | 0.062812 | -0.0033239 | 0.067086 | -61.3266 | 62.5809 | -61.322 | -61.322 | 62.2467 | 1.6663 | -0.72784 | -0.77362 | 62.5717 | -61.3632 | -0.1831 | -0.09613 | -0.18768 | -0.1831 | -0.4303 | -0.2243 | -0.10529 | -0.004578 | 60.4111 | 60.3653 | 123.3856 | 123.7198 | -0.18768 | 123.7106 | 62.8052 | -0.2243 | 123.7198 | -0.18768 | 62.8052 | 123.3856 | 123.7106 | -123.999 | -124.0402
831.7188 | 124.1089 | -61.1389 | 62.7136 | 0.021591 | 0.0027791 | 0.005723 | -0.0011386 | 0.063025 | -0.0020421 | 0.068368 | -61.2122 | 62.5809 | -61.3495 | -61.1938 | 62.2559 | 1.6113 | -0.70496 | -0.81024 | 62.5946 | -61.3495 | -0.21057 | -0.13275 | -0.073242 | -0.054932 | -0.45776 | -0.21057 | -0.11902 | 0.13733 | 60.434 | 60.3287 | 123.3948 | 123.7198 | -0.073242 | 123.7335 | 62.7502 | -0.21057 | 123.7198 | -0.073242 | 62.7502 | 123.3948 | 123.7335 | -124.0631 | -124.0631
832.7188 | 124.1364 | -61.1343 | 62.6953 | 0.22758 | 0.0051291 | 0.0080728 | -7.0562e-05 | 0.062598 | -0.00033333 | 0.067513 | -61.203 | 62.5488 | -61.3586 | -61.3129 | 62.2559 | 1.7487 | -0.81024 | -0.78735 | 62.59 | -61.3495 | -0.22431 | -0.14648 | -0.068665 | -0.17853 | -0.43945 | -0.21515 | -0.10529 | 0.15564 | 60.3241 | 60.347 | 123.3902 | 123.6832 | -0.068665 | 123.7244 | 62.883 | -0.21515 | 123.6832 | -0.068665 | 62.883 | 123.3902 | 123.7244 | -124.054 | -124.0448
833.7188 | 124.1364 | -61.1343 | 62.6816 | 0.14366 | 0.0072653 | 0.0095682 | -0.0024204 | 0.062171 | -0.0026831 | 0.071145 | -61.1847 | 62.5626 | -61.3541 | -61.29 | 62.2604 | 1.767 | -0.82855 | -0.82398 | 62.5763 | -61.3495 | -0.21973 | -0.11902 | -0.050354 | -0.15564 | -0.42114 | -0.21515 | -0.10529 | 0.16937 | 60.3058 | 60.3104 | 123.3948 | 123.6969 | -0.050354 | 123.7106 | 62.9013 | -0.21515 | 123.6969 | -0.050354 | 62.9013 | 123.3948 | 123.7106 | -124.0356 | -124.0311
834.7188 | 124.1455 | -61.1069 | 62.6999 | 0.31151 | 0.0036337 | 0.0097818 | -0.0017796 | 0.062812 | -0.00097413 | 0.069436 | -61.1984 | 62.6038 | -61.3403 | -61.3083 | 62.2559 | 1.7578 | -0.74158 | -0.83771 | 62.5854 | -61.3495 | -0.23346 | -0.09613 | -0.091552 | -0.20142 | -0.44403 | -0.24261 | -0.11444 | 0.14191 | 60.3653 | 60.2692 | 123.3627 | 123.7106 | -0.091552 | 123.6923 | 62.8647 | -0.24261 | 123.7106 | -0.091552 | 62.8647 | 123.3627 | 123.6923 | -124.0402 | -124.0494
835.7188 | 124.118 | -61.1298 | 62.6724 | 0.029221 | 0.0051291 | 0.0038004 | -0.0017796 | 0.062171 | -0.0028967 | 0.06965 | -61.1298 | 62.6175 | -61.3174 | -61.3129 | 62.2696 | 1.7624 | -0.77362 | -0.83313 | 62.5809 | -61.3449 | -0.18768 | -0.054931 | 0 | -0.1831 | -0.40283 | -0.21515 | -0.091552 | 0.18768 | 60.3561 | 60.2966 | 123.3994 | 123.7473 | 0 | 123.7106 | 62.8922 | -0.21515 | 123.7473 | 0 | 62.8922 | 123.3994 | 123.7106 | -123.9899 | -124.0173
836.7188 | 124.1455 | -61.1298 | 62.6862 | -0.0012969 | 0.0051291 | 0.0076456 | -0.0024204 | 0.064307 | -0.0016149 | 0.067086 | -61.2076 | 62.5809 | -61.3174 | -61.1526 | 62.3749 | 1.9043 | -0.79193 | -0.84228 | 62.5626 | -61.3266 | -0.18768 | -0.10529 | -0.07782 | -0.022888 | -0.31128 | -0.19684 | -0.1236 | 0.10986 | 60.3378 | 60.2875 | 123.5046 | 123.7106 | -0.07782 | 123.6923 | 63.0341 | -0.19684 | 123.7106 | -0.07782 | 63.0341 | 123.5046 | 123.6923 | -124.0036 | -124.0128
837.7188 | 124.2004 | -61.1298 | 62.6953 | -0.0089264 | 0.0049155 | 0.0025186 | -0.0013522 | 0.062171 | -0.0026831 | 0.068795 | -61.2213 | 62.5717 | -61.3358 | -61.3129 | 62.2421 | 1.8036 | -0.79193 | -0.87891 | 62.5946 | -61.3129 | -0.20599 | -0.1236 | -0.091552 | -0.1831 | -0.45319 | -0.1831 | -0.10071 | 0.11444 | 60.3378 | 60.2509 | 123.3719 | 123.7015 | -0.091552 | 123.7244 | 62.9334 | -0.1831 | 123.7015 | -0.091552 | 62.9334 | 123.3719 | 123.7244 | -124.0311 | -124.0082
838.7188 | 124.1501 | -61.116 | 62.7274 | 0.1284 | 0.0036337 | 0.010209 | -0.001566 | 0.063239 | -0.0022559 | 0.066018 | -61.2396 | 62.5809 | -61.3312 | -61.3174 | 62.2375 | 1.8219 | -0.80566 | -0.93842 | 62.5992 | -61.3266 | -0.21515 | -0.14648 | -0.1236 | -0.20142 | -0.48981 | -0.21057 | -0.12817 | 0.091553 | 60.3104 | 60.1776 | 123.3536 | 123.6969 | -0.1236 | 123.7152 | 62.9379 | -0.21057 | 123.6969 | -0.1236 | 62.9379 | 123.3536 | 123.7152 | -124.0585 | -124.054
839.7188 | 124.1364 | -61.1481 | 62.677 | 0.1284 | 0.0070517 | 0.005723 | -0.00092496 | 0.063239 | -0.0031103 | 0.069222 | -61.1893 | 62.558 | -61.3495 | -61.2854 | 62.265 | 1.8402 | -0.89722 | -0.93842 | 62.5809 | -61.3312 | -0.20142 | -0.11902 | -0.041199 | -0.13733 | -0.41199 | -0.18311 | -0.09613 | 0.16022 | 60.2509 | 60.2097 | 123.4131 | 123.7061 | -0.041199 | 123.7289 | 62.9883 | -0.18311 | 123.7061 | -0.041199 | 62.9883 | 123.4131 | 123.7289 | -124.0265 | -124.0082
840.7188 | 124.1638 | -61.1069 | 62.6724 | 0.18181 | 0.0053427 | 0.0089274 | -0.001566 | 0.063452 | 0.00030767 | 0.070718 | -61.1618 | 62.5626 | -61.322 | -61.2625 | 62.2742 | 1.8814 | -0.92926 | -0.94299 | 62.5671 | -61.3632 | -0.21515 | -0.10986 | -0.054931 | -0.15564 | -0.39825 | -0.25635 | -0.10529 | 0.16022 | 60.1776 | 60.1639 | 123.381 | 123.6694 | -0.054931 | 123.674 | 62.9883 | -0.25635 | 123.6694 | -0.054931 | 62.9883 | 123.381 | 123.674 | -123.9944 | -124.0356
841.7188 | 124.1409 | -61.116 | 62.6862 | 0.082626 | 0.0049155 | 0.0061502 | -0.0024204 | 0.063666 | 9.4068e-05 | 0.069436 | -61.2076 | 62.59 | -61.322 | -61.1252 | 62.3749 | 1.8997 | -0.84228 | -0.97046 | 62.5992 | -61.3449 | -0.20599 | -0.09613 | -0.091553 | -0.009155 | -0.31128 | -0.22888 | -0.086975 | 0.11444 | 60.2737 | 60.1456 | 123.4909 | 123.7061 | -0.091553 | 123.7152 | 63.0157 | -0.22888 | 123.7061 | -0.091553 | 63.0157 | 123.4909 | 123.7152 | -124.0082 | -124.0311
842.7188 | 124.2142 | -61.1343 | 62.7136 | -0.0089264 | 0.0049155 | 0.0085 | -0.004343 | 0.064093 | -0.0033239 | 0.069222 | -61.2167 | 62.5671 | -61.3037 | -61.3083 | 62.2467 | 1.8768 | -0.85602 | -0.97961 | 62.5717 | -61.3495 | -0.16937 | -0.14648 | -0.082398 | -0.17395 | -0.46692 | -0.21515 | -0.14191 | 0.086975 | 60.2783 | 60.1547 | 123.381 | 123.7015 | -0.082398 | 123.7061 | 63.0112 | -0.21515 | 123.7015 | -0.082398 | 63.0112 | 123.381 | 123.7061 | -124.0173 | -124.0631
843.7188 | 124.1272 | -61.1023 | 62.7274 | 0.10551 | 0.0053427 | 0.0072184 | -0.002634 | 0.06153 | -0.0035375 | 0.068795 | -61.2167 | 62.5763 | -61.3403 | -61.3083 | 62.2284 | 1.8951 | -0.89264 | -1.03 | 62.5854 | -61.3312 | -0.23804 | -0.15106 | -0.11444 | -0.20599 | -0.49896 | -0.22888 | -0.14191 | 0.1236 | 60.2097 | 60.0723 | 123.3307 | 123.6786 | -0.11444 | 123.6877 | 62.9974 | -0.22888 | 123.6786 | -0.11444 | 62.9974 | 123.3307 | 123.6877 | -124.0677 | -124.0585
844.7188 | 124.1501 | -61.1252 | 62.7045 | 0.090256 | 0.0064107 | 0.0048684 | -0.0013522 | 0.062384 | -0.0014013 | 0.066445 | -61.2259 | 62.5946 | -61.3403 | -61.322 | 62.2238 | 1.9089 | -0.89264 | -1.0574 | 62.5763 | -61.322 | -0.21515 | -0.10986 | -0.10071 | -0.19684 | -0.48065 | -0.19684 | -0.12817 | 0.11444 | 60.2325 | 60.0677 | 123.349 | 123.7198 | -0.10071 | 123.7015 | 63.0341 | -0.19684 | 123.7198 | -0.10071 | 63.0341 | 123.349 | 123.7015 | -124.0448 | -124.0265
845.7188 | 124.1226 | -61.116 | 62.6907 | 0.10551 | 0.0038473 | 0.0089274 | -0.0028476 | 0.065802 | -0.0020421 | 0.070077 | -61.2213 | 62.558 | -61.3266 | -61.3037 | 62.2192 | 1.9089 | -0.93842 | -1.0757 | 62.59 | -61.3312 | -0.21057 | -0.13275 | -0.10529 | -0.18768 | -0.4715 | -0.21515 | -0.10071 | 0.10529 | 60.1776 | 60.0403 | 123.3353 | 123.674 | -0.10529 | 123.7061 | 63.0249 | -0.21515 | 123.674 | -0.10529 | 63.0249 | 123.3353 | 123.7061 | -124.0173 | -124.0219
846.7188 | 124.1684 | -61.1023 | 62.6495 | 0.24284 | 0.0066245 | 0.009141 | 0.00014304 | 0.061316 | -0.0024695 | 0.069009 | -61.1572 | 62.5717 | -61.3129 | -61.2579 | 62.265 | 1.9592 | -1.0162 | -1.0437 | 62.5626 | -61.3083 | -0.21057 | -0.07782 | -0.054932 | -0.15564 | -0.38452 | -0.20599 | -0.086975 | 0.15564 | 60.0861 | 60.0586 | 123.3673 | 123.674 | -0.054932 | 123.6649 | 63.0615 | -0.20599 | 123.674 | -0.054932 | 63.0615 | 123.3673 | 123.6649 | -123.9624 | -123.9578
847.7188 | 124.1043 | -61.1069 | 62.6907 | 0.14366 | 0.0042745 | 0.0082864 | -0.0011386 | 0.063239 | -0.0014013 | 0.067513 | -61.1847 | 62.5763 | -61.3266 | -61.2854 | 62.2238 | 1.9363 | -0.99792 | -1.0986 | 62.5992 | -61.3358 | -0.21973 | -0.11444 | -0.077819 | -0.17853 | -0.46692 | -0.22888 | -0.091553 | 0.14191 | 60.1089 | 60.0082 | 123.3307 | 123.6832 | -0.077819 | 123.7061 | 63.0432 | -0.22888 | 123.6832 | -0.077819 | 63.0432 | 123.3307 | 123.7061 | -124.0173 | -124.0265
848.7188 | 124.1409 | -61.1298 | 62.7182 | 0.13603 | 0.0072653 | 0.0059366 | 0.00099764 | 0.063239 | -0.0024695 | 0.068368 | -61.2122 | 62.5992 | -61.3312 | -61.2991 | 62.2375 | 1.9455 | -0.93842 | -1.1261 | 62.59 | -61.3129 | -0.20142 | -0.11902 | -0.082397 | -0.16937 | -0.48065 | -0.1831 | -0.12817 | 0.11902 | 60.1913 | 60.0037 | 123.3673 | 123.7289 | -0.082397 | 123.7198 | 63.0753 | -0.1831 | 123.7289 | -0.082397 | 63.0753 | 123.3673 | 123.7198 | -124.0494 | -124.0311
849.7188 | 124.1226 | -61.1206 | 62.7182 | 0.082626 | 0.0051291 | 0.011064 | -0.0024204 | 0.063025 | -0.0022559 | 0.069222 | -61.2076 | 62.5809 | -61.3174 | -61.3129 | 62.2147 | 1.9592 | -0.94757 | -1.1536 | 62.5992 | -61.322 | -0.19684 | -0.13733 | -0.086976 | -0.19226 | -0.50354 | -0.20142 | -0.11902 | 0.10986 | 60.173 | 59.967 | 123.3353 | 123.7015 | -0.086976 | 123.7198 | 63.0798 | -0.20142 | 123.7015 | -0.086976 | 63.0798 | 123.3353 | 123.7198 | -124.0356 | -124.0402
850.7188 | 124.1318 | -61.116 | 62.709 | 0.15129 | 0.0049155 | 0.0063638 | -0.00071136 | 0.061103 | -0.0018285 | 0.069863 | -61.1893 | 62.5854 | -61.3083 | -61.3037 | 62.2192 | 1.973 | -0.96588 | -1.1581 | 62.5854 | -61.3174 | -0.19226 | -0.1236 | -0.073242 | -0.18768 | -0.48981 | -0.20142 | -0.1236 | 0.11902 | 60.1501 | 59.9579 | 123.3353 | 123.7015 | -0.073242 | 123.7015 | 63.089 | -0.20142 | 123.7015 | -0.073242 | 63.089 | 123.3353 | 123.7015 | -124.0173 | -124.0265
851.7188 | 124.1043 | -61.1206 | 62.7045 | 0.21233 | 0.0066245 | 0.0087138 | -0.00071136 | 0.062598 | -0.0022559 | 0.069222 | -61.1893 | 62.59 | -61.3083 | -61.29 | 62.2467 | 2.0004 | -1.0071 | -1.2039 | 62.5946 | -61.3266 | -0.18768 | -0.11444 | -0.068665 | -0.16937 | -0.45776 | -0.20599 | -0.10986 | 0.11902 | 60.1135 | 59.9167 | 123.3673 | 123.7106 | -0.068665 | 123.7152 | 63.121 | -0.20599 | 123.7106 | -0.068665 | 63.121 | 123.3673 | 123.7152 | -124.0128 | -124.0311
852.7188 | 124.1226 | -61.1114 | 62.6953 | 0.10551 | 0.0064107 | 0.010423 | -0.00028416 | 0.064307 | -0.0050329 | 0.072 | -61.1755 | 62.5854 | -61.322 | -61.2808 | 62.2238 | 2.0233 | -1.0574 | -1.2085 | 62.59 | -61.3449 | -0.21057 | -0.10986 | -0.064087 | -0.16937 | -0.4715 | -0.23346 | -0.10529 | 0.14648 | 60.054 | 59.903 | 123.3353 | 123.6969 | -0.064087 | 123.7015 | 63.1348 | -0.23346 | 123.6969 | -0.064087 | 63.1348 | 123.3353 | 123.7015 | -124.0173 | -124.0402
853.7188 | 124.1592 | -61.1069 | 62.6999 | 0.12077 | 0.0064107 | 0.007432 | 0.00099764 | 0.064093 | -0.0024695 | 0.068368 | -61.1069 | 62.6266 | -61.3083 | -61.2534 | 62.2604 | 2.0554 | -1.1124 | -1.2085 | 62.5671 | -61.3129 | -0.20142 | -0.073242 | 0 | -0.14648 | -0.43945 | -0.20599 | -0.13275 | 0.20142 | 59.9945 | 59.8984 | 123.3673 | 123.7335 | 0 | 123.674 | 63.1622 | -0.20599 | 123.7335 | 0 | 63.1622 | 123.3673 | 123.674 | -124.0082 | -124.0128
854.7188 | 124.1272 | -61.1206 | 62.6633 | 0.12077 | 0.0049155 | 0.0061502 | -0.00071136 | 0.064307 | -0.00054693 | 0.068368 | -61.1435 | 62.5992 | -61.3266 | -61.2991 | 62.2467 | 2.0554 | -1.0941 | -1.236 | 62.5946 | -61.3312 | -0.20599 | -0.064087 | -0.022889 | -0.17853 | -0.41656 | -0.21057 | -0.068665 | 0.18311 | 60.0266 | 59.8846 | 123.3673 | 123.7198 | -0.022889 | 123.7152 | 63.176 | -0.21057 | 123.7198 | -0.022889 | 63.176 | 123.3673 | 123.7152 | -123.9899 | -123.9944
855.7188 | 124.1409 | -61.1114 | 62.6999 | 0.090256 | 0.0042745 | 0.0059366 | -0.0024204 | 0.063239 | -0.00033333 | 0.067941 | -61.2076 | 62.5946 | -61.3266 | -61.2946 | 62.2192 | 2.037 | -1.0254 | -1.2817 | 62.6175 | -61.2946 | -0.21515 | -0.10529 | -0.096131 | -0.18311 | -0.48065 | -0.18311 | -0.082397 | 0.11902 | 60.0861 | 59.8297 | 123.3307 | 123.7061 | -0.096131 | 123.7289 | 63.1485 | -0.18311 | 123.7061 | -0.096131 | 63.1485 | 123.3307 | 123.7289 | -124.0265 | -123.9944
856.7188 | 124.1043 | -61.1206 | 62.7365 | 0.15129 | 0.0053427 | 0.0097818 | -7.0562e-05 | 0.062384 | -0.0016149 | 0.070504 | -61.1984 | 62.5763 | -61.2762 | -61.2991 | 62.2101 | 2.0462 | -1.0757 | -1.3 | 62.6083 | -61.3312 | -0.15564 | -0.16022 | -0.07782 | -0.17853 | -0.52643 | -0.21057 | -0.12817 | 0.07782 | 60.0449 | 59.8206 | 123.3307 | 123.6969 | -0.07782 | 123.7289 | 63.1668 | -0.21057 | 123.6969 | -0.07782 | 63.1668 | 123.3307 | 123.7289 | -124.0128 | -124.0677
857.7188 | 124.1226 | -61.0977 | 62.7182 | 0.14366 | 0.0061971 | 0.006791 | -0.00092496 | 0.063666 | -0.0031103 | 0.070504 | -61.1847 | 62.6175 | -61.3174 | -61.3037 | 62.2192 | 2.0462 | -1.0895 | -1.3275 | 62.6083 | -61.322 | -0.21973 | -0.10071 | -0.086975 | -0.20599 | -0.49896 | -0.2243 | -0.10986 | 0.13275 | 60.0082 | 59.7702 | 123.317 | 123.7152 | -0.086975 | 123.7061 | 63.1439 | -0.2243 | 123.7152 | -0.086975 | 63.1439 | 123.317 | 123.7061 | -124.0356 | -124.0402
858.7188 | 124.118 | -61.1114 | 62.7136 | 0.1284 | 0.0076925 | 0.009141 | 0.00035684 | 0.065161 | -0.00097413 | 0.067513 | -61.1755 | 62.59 | -61.3358 | -61.29 | 62.2421 | 2.0737 | -1.1169 | -1.3412 | 62.5763 | -61.3129 | -0.2243 | -0.1236 | -0.064087 | -0.17853 | -0.4715 | -0.20142 | -0.13733 | 0.16022 | 59.9945 | 59.7702 | 123.3536 | 123.7015 | -0.064087 | 123.6877 | 63.1851 | -0.20142 | 123.7015 | -0.064087 | 63.1851 | 123.3536 | 123.6877 | -124.0494 | -124.0265
859.7188 | 124.2142 | -61.084 | 62.7228 | 0.097885 | 0.0057699 | 0.0099954 | -0.00028416 | 0.063666 | -0.0016149 | 0.070077 | -61.1984 | 62.5946 | -61.3312 | -61.2808 | 62.2192 | 2.0966 | -1.0986 | -1.3733 | 62.5809 | -61.322 | -0.24719 | -0.12817 | -0.11444 | -0.19684 | -0.50354 | -0.23804 | -0.14191 | 0.13275 | 59.9854 | 59.7107 | 123.3032 | 123.6786 | -0.11444 | 123.6649 | 63.1805 | -0.23804 | 123.6786 | -0.11444 | 63.1805 | 123.3032 | 123.6649 | -124.054 | -124.0448
860.7188 | 124.1638 | -61.1069 | 62.7136 | -0.08522 | 0.0036337 | 0.011064 | 0.001852 | 0.06388 | -0.0018285 | 0.0673 | -61.1298 | 62.6038 | -61.2946 | -61.2259 | 62.2559 | 2.1057 | -1.2085 | -1.3641 | 62.5809 | -61.3358 | -0.18768 | -0.10986 | -0.022888 | -0.11902 | -0.45776 | -0.22888 | -0.13275 | 0.16479 | 59.8984 | 59.7427 | 123.3627 | 123.7106 | -0.022888 | 123.6877 | 63.2126 | -0.22888 | 123.7106 | -0.022888 | 63.2126 | 123.3627 | 123.6877 | -124.0082 | -124.0494
861.7188 | 124.1547 | -61.1023 | 62.7228 | 0.15129 | 0.0040609 | 0.011491 | 0.0012112 | 0.065375 | -0.00076053 | 0.070504 | -61.1526 | 62.5854 | -61.3083 | -61.2671 | 62.2421 | 2.124 | -1.1856 | -1.4053 | 62.5946 | -61.322 | -0.20599 | -0.13733 | -0.050354 | -0.1648 | -0.48065 | -0.21973 | -0.12817 | 0.15564 | 59.9167 | 59.697 | 123.3444 | 123.6877 | -0.050354 | 123.6969 | 63.2263 | -0.21973 | 123.6877 | -0.050354 | 63.2263 | 123.3444 | 123.6969 | -124.0311 | -124.0448
862.7188 | 124.1226 | -61.0977 | 62.7411 | 0.1284 | 0.0044881 | 0.0059366 | 0.00078404 | 0.062171 | -0.0026831 | 0.068368 | -61.1938 | 62.5946 | -61.3037 | -61.2854 | 62.2055 | 2.1103 | -1.149 | -1.4511 | 62.6266 | -61.2991 | -0.20599 | -0.14649 | -0.096131 | -0.18768 | -0.53558 | -0.20142 | -0.11444 | 0.10986 | 59.9487 | 59.6466 | 123.3032 | 123.6923 | -0.096131 | 123.7244 | 63.208 | -0.20142 | 123.6923 | -0.096131 | 63.208 | 123.3032 | 123.7244 | -124.0448 | -124.0402
863.7188 | 124.1226 | -61.1206 | 62.7228 | 0.11314 | 0.0051291 | 0.0052958 | -0.00028416 | 0.061957 | 0.00030767 | 0.068154 | -61.1893 | 62.6221 | -61.2808 | -61.2991 | 62.2009 | 2.1149 | -1.1719 | -1.4786 | 62.5854 | -61.3083 | -0.16022 | -0.10071 | -0.068665 | -0.17853 | -0.52185 | -0.18768 | -0.13733 | 0.091553 | 59.9487 | 59.642 | 123.3215 | 123.7427 | -0.068665 | 123.7061 | 63.2355 | -0.18768 | 123.7427 | -0.068665 | 63.2355 | 123.3215 | 123.7061 | -124.0036 | -124.0311
864.7188 | 124.1501 | -61.1023 | 62.7228 | 0.1284 | 0.0061971 | 0.0027322 | -0.00049776 | 0.061743 | -0.0020421 | 0.070504 | -61.1801 | 62.5854 | -61.3174 | -61.3037 | 62.2147 | 2.1103 | -1.1948 | -1.5152 | 62.6175 | -61.3266 | -0.21515 | -0.13733 | -0.07782 | -0.20142 | -0.50812 | -0.2243 | -0.10528 | 0.13733 | 59.9075 | 59.5871 | 123.317 | 123.6877 | -0.07782 | 123.7198 | 63.2126 | -0.2243 | 123.6877 | -0.07782 | 63.2126 | 123.317 | 123.7198 | -124.0402 | -124.0494
865.7188 | 124.1043 | -61.1252 | 62.7182 | 0.097885 | 0.0047019 | 0.0072184 | -0.001566 | 0.063025 | 9.4068e-05 | 0.069436 | -61.1755 | 62.6175 | -61.3083 | -61.3129 | 62.1872 | 2.124 | -1.2131 | -1.5289 | 62.5992 | -61.3129 | -0.18311 | -0.10071 | -0.050354 | -0.18768 | -0.53101 | -0.18768 | -0.11902 | 0.13275 | 59.9121 | 59.5963 | 123.3124 | 123.7427 | -0.050354 | 123.7244 | 63.2492 | -0.18768 | 123.7427 | -0.050354 | 63.2492 | 123.3124 | 123.7244 | -124.0265 | -124.0311
866.7188 | 124.1638 | -61.1023 | 62.7045 | 0.17418 | 0.0064107 | 0.0070048 | -7.0562e-05 | 0.065161 | -0.00076053 | 0.068154 | -61.1298 | 62.5992 | -61.2946 | -61.2305 | 62.2467 | 2.2018 | -1.3275 | -1.5289 | 62.6175 | -61.3129 | -0.19226 | -0.10529 | -0.027466 | -0.12817 | -0.45776 | -0.21057 | -0.086975 | 0.16479 | 59.7748 | 59.5734 | 123.349 | 123.7015 | -0.027466 | 123.7198 | 63.3041 | -0.21057 | 123.7015 | -0.027466 | 63.3041 | 123.349 | 123.7198 | -123.999 | -124.0173
867.7188 | 124.1638 | -61.0977 | 62.6953 | 0.14366 | 0.0061971 | 0.010636 | 0.0031338 | 0.062598 | -0.0026831 | 0.068154 | -61.1343 | 62.6129 | -61.3037 | -61.2442 | 62.233 | 2.2293 | -1.3184 | -1.5564 | 62.6038 | -61.3312 | -0.20599 | -0.082397 | -0.036621 | -0.14648 | -0.46234 | -0.23346 | -0.091552 | 0.16937 | 59.7794 | 59.5413 | 123.3307 | 123.7106 | -0.036621 | 123.7015 | 63.327 | -0.23346 | 123.7106 | -0.036621 | 63.327 | 123.3307 | 123.7015 | -123.999 | -124.0265
868.7188 | 124.1409 | -61.1023 | 62.7182 | 0.04448 | 0.0049155 | 0.0044412 | -0.00071136 | 0.062384 | -0.0016149 | 0.069863 | -61.1984 | 62.6175 | -61.3037 | -61.2854 | 62.3978 | 2.3621 | -1.4145 | -1.5884 | 62.6358 | -61.3174 | -0.20142 | -0.10071 | -0.09613 | -0.18311 | -0.32044 | -0.21515 | -0.082398 | 0.10529 | 59.6878 | 59.5139 | 123.5001 | 123.7198 | -0.09613 | 123.7381 | 63.4644 | -0.21515 | 123.7198 | -0.09613 | 63.4644 | 123.5001 | 123.7381 | -124.0219 | -124.0356
869.7188 | 124.1547 | -61.084 | 62.7365 | 0.04448 | 0.0049155 | 0.005723 | -0.00049776 | 0.063666 | -0.0026831 | 0.069222 | -61.1664 | 62.6312 | -61.3174 | -61.2946 | 62.2192 | 2.2202 | -1.1169 | -1.4832 | 62.6633 | -61.3037 | -0.23346 | -0.10529 | -0.082398 | -0.21057 | -0.51727 | -0.21973 | -0.073242 | 0.15106 | 59.967 | 59.6008 | 123.3032 | 123.7152 | -0.082398 | 123.7473 | 63.3041 | -0.21973 | 123.7152 | -0.082398 | 63.3041 | 123.3032 | 123.7473 | -124.054 | -124.0402
870.7188 | 124.1455 | -61.0748 | 62.7686 | 0.067368 | 0.0057699 | 0.0027322 | -0.00092496 | 0.062384 | -0.0039649 | 0.068154 | -61.171 | 62.6266 | -61.29 | -61.29 | 62.1872 | 2.2339 | -1.3092 | -1.7075 | 62.6129 | -61.3083 | -0.21515 | -0.14191 | -0.09613 | -0.21515 | -0.58136 | -0.23346 | -0.15564 | 0.11902 | 59.7656 | 59.3674 | 123.262 | 123.7015 | -0.09613 | 123.6877 | 63.3087 | -0.23346 | 123.7015 | -0.09613 | 63.3087 | 123.262 | 123.6877 | -124.0585 | -124.0768
871.7188 | 124.1272 | -61.1023 | 62.7365 | 0.074997 | 0.0034201 | 0.0061502 | -0.0024204 | 0.06153 | -0.0022559 | 0.069009 | -61.1755 | 62.6083 | -61.3174 | -61.2854 | 62.2147 | 2.243 | -1.3504 | -1.7166 | 62.6175 | -61.322 | -0.21515 | -0.12817 | -0.073242 | -0.18311 | -0.52185 | -0.21973 | -0.11902 | 0.14191 | 59.7519 | 59.3857 | 123.317 | 123.7106 | -0.073242 | 123.7198 | 63.3453 | -0.21973 | 123.7106 | -0.073242 | 63.3453 | 123.317 | 123.7198 | -124.054 | -124.0585
872.7188 | 124.1318 | -61.1252 | 62.7502 | 0.12077 | 0.0051291 | 0.0099954 | -0.00071136 | 0.06153 | -0.00033333 | 0.068368 | -61.1755 | 62.5992 | -61.2991 | -61.2854 | 62.1872 | 2.2659 | -1.3596 | -1.7395 | 62.6266 | -61.2991 | -0.17395 | -0.15106 | -0.050354 | -0.16022 | -0.56305 | -0.17395 | -0.1236 | 0.1236 | 59.7656 | 59.3857 | 123.3124 | 123.7244 | -0.050354 | 123.7518 | 63.3911 | -0.17395 | 123.7244 | -0.050354 | 63.3911 | 123.3124 | 123.7518 | -124.0494 | -124.0494
873.7188 | 124.1364 | -61.084 | 62.7274 | 0.13603 | 0.0047019 | 0.0082864 | -0.0011386 | 0.064734 | -0.0016149 | 0.067727 | -61.1298 | 62.5992 | -61.3129 | -61.2442 | 62.2009 | 2.2659 | -1.4603 | -1.7624 | 62.6083 | -61.3129 | -0.22888 | -0.12817 | -0.045777 | -0.16022 | -0.52643 | -0.22888 | -0.11902 | 0.1831 | 59.6237 | 59.3216 | 123.2849 | 123.6832 | -0.045777 | 123.6923 | 63.3499 | -0.22888 | 123.6832 | -0.045777 | 63.3499 | 123.2849 | 123.6923 | -124.0402 | -124.0402
874.7188 | 124.118 | -61.0977 | 62.7182 | 0.12077 | 0.0059835 | 0.0095682 | 0.0012112 | 0.064734 | -0.0014013 | 0.069436 | -61.1252 | 62.6129 | -61.2991 | -61.2396 | 62.2284 | 2.3071 | -1.506 | -1.8173 | 62.6083 | -61.3083 | -0.20142 | -0.10529 | -0.027466 | -0.14191 | -0.48981 | -0.21057 | -0.10986 | 0.17395 | 59.5917 | 59.2804 | 123.3261 | 123.7106 | -0.027466 | 123.7061 | 63.4048 | -0.21057 | 123.7106 | -0.027466 | 63.4048 | 123.3261 | 123.7061 | -124.0173 | -124.0265
875.7188 | 124.1409 | -61.1023 | 62.7411 | 0.14366 | 0.0072653 | 0.0061502 | -0.0011386 | 0.062812 | 0.00052127 | 0.067513 | -61.1801 | 62.5992 | -61.2946 | -61.2854 | 62.1964 | 2.2888 | -1.4465 | -1.8539 | 62.6175 | -61.3083 | -0.19226 | -0.14191 | -0.07782 | -0.18311 | -0.54474 | -0.20599 | -0.1236 | 0.11444 | 59.6558 | 59.2484 | 123.2986 | 123.7015 | -0.07782 | 123.7198 | 63.3911 | -0.20599 | 123.7015 | -0.07782 | 63.3911 | 123.2986 | 123.7198 | -124.0356 | -124.0494
876.7188 | 124.1684 | -61.0931 | 62.7228 | 0.04448 | 0.0053427 | 0.0065774 | -0.0011386 | 0.063452 | -0.0024695 | 0.067086 | -61.1618 | 62.6312 | -61.2854 | -61.2534 | 62.2192 | 2.2751 | -1.4328 | -1.8997 | 62.645 | -61.29 | -0.19226 | -0.091552 | -0.068664 | -0.16022 | -0.50354 | -0.19684 | -0.07782 | 0.1236 | 59.6603 | 59.1934 | 123.3124 | 123.7244 | -0.068664 | 123.7381 | 63.3682 | -0.19684 | 123.7244 | -0.068664 | 63.3682 | 123.3124 | 123.7381 | -124.0082 | -124.0128
877.7188 | 124.118 | -61.0931 | 62.7228 | 0.021591 | 0.0053427 | 0.0080728 | -0.00071136 | 0.063239 | -0.0024695 | 0.069222 | -61.1618 | 62.6266 | -61.2854 | -61.2717 | 62.114 | 2.3849 | -1.4465 | -2.0142 | 62.6495 | -61.2854 | -0.19226 | -0.09613 | -0.068664 | -0.17853 | -0.60882 | -0.19226 | -0.073242 | 0.1236 | 59.6466 | 59.079 | 123.2071 | 123.7198 | -0.068664 | 123.7427 | 63.4781 | -0.19226 | 123.7198 | -0.068664 | 63.4781 | 123.2071 | 123.7427 | -124.0082 | -124.0082
878.7188 | 124.118 | -61.0703 | 62.7228 | -0.0012969 | 0.0036337 | 0.0061502 | -0.001566 | 0.061316 | -0.0011877 | 0.072213 | -61.1618 | 62.6221 | -61.3037 | -61.2762 | 62.2009 | 2.3575 | -1.5198 | -1.9775 | 62.6221 | -61.2808 | -0.23346 | -0.10071 | -0.091553 | -0.20599 | -0.52185 | -0.21057 | -0.10071 | 0.14191 | 59.5505 | 59.0927 | 123.2712 | 123.6923 | -0.091553 | 123.6923 | 63.4277 | -0.21057 | 123.6923 | -0.091553 | 63.4277 | 123.2712 | 123.6923 | -124.0265 | -124.0036
879.7188 | 124.1364 | -61.0794 | 62.7228 | -0.039444 | 0.0061971 | 0.007432 | -0.0017796 | 0.064307 | -0.0035375 | 0.069222 | -61.1664 | 62.6312 | -61.2946 | -61.235 | 62.2055 | 2.3575 | -1.5244 | -1.9684 | 62.6266 | -61.3083 | -0.21515 | -0.091552 | -0.086975 | -0.15564 | -0.51727 | -0.22888 | -0.09613 | 0.12817 | 59.5551 | 59.111 | 123.2849 | 123.7106 | -0.086975 | 123.7061 | 63.4369 | -0.22888 | 123.7106 | -0.086975 | 63.4369 | 123.2849 | 123.7061 | -124.0173 | -124.0311
880.7188 | 124.1455 | -61.0519 | 62.7365 | 0.12077 | 0.0040609 | 0.006791 | 0.0022794 | 0.063666 | -0.0014013 | 0.066873 | -61.1252 | 62.6129 | -61.2946 | -61.2442 | 62.1964 | 2.3987 | -1.6434 | -2.0096 | 62.6221 | -61.2991 | -0.24262 | -0.1236 | -0.073242 | -0.19226 | -0.54016 | -0.24719 | -0.11444 | 0.16937 | 59.4086 | 59.0424 | 123.2483 | 123.6649 | -0.073242 | 123.674 | 63.4506 | -0.24719 | 123.6649 | -0.073242 | 63.4506 | 123.2483 | 123.674 | -124.0311 | -124.0356
881.7188 | 124.1226 | -61.0657 | 62.709 | 0.14366 | 0.0049155 | 0.0076456 | -0.00092496 | 0.060248 | -0.00097413 | 0.068368 | -61.1114 | 62.6038 | -61.3037 | -61.2167 | 62.2192 | 2.3987 | -1.6479 | -2.0142 | 62.6038 | -61.2946 | -0.23804 | -0.10529 | -0.045776 | -0.15106 | -0.48981 | -0.22888 | -0.10529 | 0.19226 | 59.4177 | 59.0515 | 123.2849 | 123.6694 | -0.045776 | 123.6694 | 63.4644 | -0.22888 | 123.6694 | -0.045776 | 63.4644 | 123.2849 | 123.6694 | -124.0128 | -124.0036
882.7188 | 124.1135 | -61.0977 | 62.7365 | 0.18181 | 0.0068381 | 0.0082864 | -0.001566 | 0.063452 | -0.00011953 | 0.068795 | -61.1526 | 62.6221 | -61.2854 | -61.2671 | 62.1964 | 2.3758 | -1.6251 | -2.1332 | 62.6495 | -61.3037 | -0.18768 | -0.11444 | -0.054932 | -0.16937 | -0.54016 | -0.20599 | -0.086975 | 0.13275 | 59.4727 | 58.9645 | 123.2941 | 123.7198 | -0.054932 | 123.7473 | 63.4735 | -0.20599 | 123.7198 | -0.054932 | 63.4735 | 123.2941 | 123.7473 | -124.0219 | -124.0402
883.7188 | 124.2371 | -61.0886 | 62.7457 | 0.10551 | 0.0051291 | 0.0055094 | -0.001566 | 0.063452 | -0.0014013 | 0.068154 | -61.1664 | 62.6175 | -61.2625 | -61.2534 | 62.178 | 2.4078 | -1.6205 | -2.1515 | 62.6129 | -61.2625 | -0.17395 | -0.12817 | -0.07782 | -0.16479 | -0.56763 | -0.17395 | -0.13275 | 0.09613 | 59.4681 | 58.9371 | 123.2666 | 123.7061 | -0.07782 | 123.7015 | 63.4964 | -0.17395 | 123.7061 | -0.07782 | 63.4964 | 123.2666 | 123.7015 | -124.0082 | -124.0082
884.7188 | 124.1226 | -61.0748 | 62.7457 | 0.082626 | 0.0051291 | 0.007432 | -0.0017796 | 0.063452 | -0.0016149 | 0.067086 | -61.171 | 62.6312 | -61.29 | -61.2579 | 62.1872 | 2.4078 | -1.6525 | -2.1835 | 62.6266 | -61.2808 | -0.21515 | -0.11444 | -0.09613 | -0.18311 | -0.55847 | -0.20599 | -0.11902 | 0.11902 | 59.4223 | 58.8913 | 123.262 | 123.7061 | -0.09613 | 123.7015 | 63.4827 | -0.20599 | 123.7061 | -0.09613 | 63.4827 | 123.262 | 123.7015 | -124.0356 | -124.0265
885.7188 | 124.1226 | -61.084 | 62.7365 | 0.082626 | 0.0061971 | 0.011704 | -0.00071136 | 0.06153 | -0.0026831 | 0.068582 | -61.1801 | 62.6312 | -61.2762 | -61.2625 | 62.1872 | 2.4078 | -1.6983 | -2.2339 | 62.6358 | -61.2854 | -0.19226 | -0.10529 | -0.096131 | -0.17853 | -0.54932 | -0.20142 | -0.10071 | 0.09613 | 59.3857 | 58.8501 | 123.2712 | 123.7152 | -0.096131 | 123.7198 | 63.4918 | -0.20142 | 123.7152 | -0.096131 | 63.4918 | 123.2712 | 123.7198 | -124.0128 | -124.0219
886.7188 | 124.1043 | -61.084 | 62.7365 | 0.0063326 | 0.0051291 | 0.010423 | -0.0019932 | 0.06153 | -0.0014013 | 0.069009 | -61.2442 | 62.6495 | -61.2671 | -61.2259 | 62.178 | 2.4353 | -1.7029 | -2.298 | 62.6266 | -61.2946 | -0.18311 | -0.086975 | -0.16022 | -0.14191 | -0.55847 | -0.21057 | -0.10986 | 0.022888 | 59.3811 | 58.786 | 123.262 | 123.7335 | -0.16022 | 123.7106 | 63.5193 | -0.21057 | 123.7335 | -0.16022 | 63.5193 | 123.262 | 123.7106 | -124.0036 | -124.0311
887.7188 | 124.1501 | -61.0748 | 62.7182 | 0.15892 | 0.0057699 | 0.0085 | 0.0031338 | 0.064093 | -0.00097413 | 0.068368 | -61.0748 | 62.6358 | -61.2671 | -61.2122 | 62.2055 | 2.4673 | -1.8311 | -2.3209 | 62.6175 | -61.2991 | -0.19226 | -0.082398 | 0 | -0.13733 | -0.5127 | -0.2243 | -0.10071 | 0.19226 | 59.2438 | 58.754 | 123.2803 | 123.7106 | 0 | 123.6923 | 63.5422 | -0.2243 | 123.7106 | 0 | 63.5422 | 123.2803 | 123.6923 | -123.9853 | -124.0173
888.7188 | 124.1455 | -61.0611 | 62.7686 | -0.039444 | 0.0049155 | 0.0099954 | -0.0028476 | 0.064307 | -0.0014013 | 0.068582 | -61.1618 | 62.6175 | -61.2808 | -61.2579 | 62.1552 | 2.4673 | -1.7761 | -2.3621 | 62.6587 | -61.2762 | -0.21973 | -0.15106 | -0.10071 | -0.19684 | -0.6134 | -0.21515 | -0.10986 | 0.11902 | 59.285 | 58.699 | 123.2162 | 123.6786 | -0.10071 | 123.7198 | 63.5284 | -0.21515 | 123.6786 | -0.10071 | 63.5284 | 123.2162 | 123.7198 | -124.0494 | -124.0448
889.7188 | 124.1318 | -61.0931 | 62.7365 | 0.1284 | 0.0068381 | 0.0052958 | -0.001566 | 0.062384 | -0.0018285 | 0.068154 | -61.1664 | 62.6404 | -61.29 | -61.2625 | 62.1735 | 2.4673 | -1.8219 | -2.4078 | 62.6175 | -61.2808 | -0.19684 | -0.09613 | -0.073242 | -0.16937 | -0.56305 | -0.18768 | -0.11902 | 0.1236 | 59.2712 | 58.6853 | 123.2666 | 123.7335 | -0.073242 | 123.7106 | 63.5605 | -0.18768 | 123.7335 | -0.073242 | 63.5605 | 123.2666 | 123.7106 | -124.0265 | -124.0173
890.7188 | 124.1043 | -61.0931 | 62.7777 | 0.14366 | 0.0057699 | 0.010636 | 0.00014304 | 0.061743 | -0.0026831 | 0.070291 | -61.1572 | 62.6266 | -61.29 | -61.2717 | 62.1597 | 2.4902 | -1.886 | -2.4673 | 62.6266 | -61.3037 | -0.19684 | -0.15106 | -0.064087 | -0.17853 | -0.61798 | -0.21057 | -0.15106 | 0.13275 | 59.2072 | 58.6258 | 123.2529 | 123.7198 | -0.064087 | 123.7198 | 63.5834 | -0.21057 | 123.7198 | -0.064087 | 63.5834 | 123.2529 | 123.7198 | -124.0677 | -124.0814
891.7188 | 124.1501 | -61.0794 | 62.7457 | 0.18944 | 0.0059835 | 0.009141 | 0.00078404 | 0.063452 | -0.0020421 | 0.068368 | -61.1481 | 62.645 | -61.2625 | -61.2534 | 62.1597 | 2.4673 | -1.9089 | -2.5223 | 62.6129 | -61.2991 | -0.1831 | -0.10071 | -0.068664 | -0.17395 | -0.58594 | -0.21973 | -0.13275 | 0.11444 | 59.1705 | 58.5571 | 123.2391 | 123.7244 | -0.068664 | 123.6923 | 63.5468 | -0.21973 | 123.7244 | -0.068664 | 63.5468 | 123.2391 | 123.6923 | -124.0082 | -124.0448
892.7188 | 124.0952 | -61.0565 | 62.7182 | 0.18944 | 0.0061971 | 0.0080728 | -0.00028416 | 0.063239 | 0.00030767 | 0.070291 | -61.1206 | 62.6083 | -61.2854 | -61.2442 | 62.1826 | 2.5085 | -1.973 | -2.5269 | 62.6129 | -61.3129 | -0.22888 | -0.10986 | -0.064086 | -0.18768 | -0.53558 | -0.25635 | -0.10529 | 0.1648 | 59.0836 | 58.5297 | 123.2391 | 123.6649 | -0.064086 | 123.6694 | 63.5651 | -0.25635 | 123.6649 | -0.064086 | 63.5651 | 123.2391 | 123.6694 | -124.0036 | -124.0311
893.7188 | 124.1272 | -61.0794 | 62.7365 | 0.1284 | 0.0066245 | 0.0078592 | 0.00057044 | 0.063666 | -0.0037511 | 0.069436 | -61.0931 | 62.6358 | -61.2854 | -61.2213 | 62.178 | 2.5269 | -2.0462 | -2.5406 | 62.6175 | -61.2946 | -0.20599 | -0.10071 | -0.013733 | -0.14191 | -0.55847 | -0.21515 | -0.11902 | 0.19226 | 59.0332 | 58.5388 | 123.2574 | 123.7152 | -0.013733 | 123.6969 | 63.6063 | -0.21515 | 123.7152 | -0.013733 | 63.6063 | 123.2574 | 123.6969 | -124.0219 | -124.0311
894.7188 | 124.173 | -61.084 | 62.7228 | 0.15129 | 0.0064107 | 0.0070048 | 0.0033474 | 0.063666 | -0.0024695 | 0.070931 | -61.0794 | 62.6404 | -61.29 | -61.1206 | 62.3703 | 2.6917 | -2.1057 | -2.504 | 62.6312 | -61.2808 | -0.20599 | -0.082397 | 0.004577 | -0.036621 | -0.35248 | -0.19684 | -0.091552 | 0.21057 | 58.9783 | 58.58 | 123.4543 | 123.7244 | 0.004577 | 123.7152 | 63.7756 | -0.19684 | 123.7244 | 0.004577 | 63.7756 | 123.4543 | 123.7152 | -124.0128 | -124.0036
895.7188 | 124.1409 | -61.0886 | 62.7228 | 0.18181 | 0.0057699 | 0.0097818 | 0.002493 | 0.065161 | -0.00033333 | 0.068582 | -61.084 | 62.6587 | -61.2854 | -61.2076 | 62.1964 | 2.5681 | -2.0966 | -2.5864 | 62.6266 | -61.29 | -0.19684 | -0.064087 | 0.004578 | -0.11902 | -0.52643 | -0.20142 | -0.09613 | 0.20142 | 58.992 | 58.5022 | 123.2849 | 123.7473 | 0.004578 | 123.7152 | 63.6566 | -0.20142 | 123.7473 | 0.004578 | 63.6566 | 123.2849 | 123.7152 | -124.0082 | -124.0128
896.7188 | 124.1043 | -61.0565 | 62.7365 | 0.090256 | 0.0064107 | 0.0078592 | -0.0013522 | 0.062812 | -0.0028967 | 0.071786 | -61.1298 | 62.6724 | -61.2946 | -61.2534 | 62.1643 | 2.5726 | -2.092 | -2.6917 | 62.6495 | -61.2762 | -0.23804 | -0.064087 | -0.073242 | -0.19684 | -0.5722 | -0.21973 | -0.086975 | 0.16479 | 58.9645 | 58.3649 | 123.2208 | 123.7289 | -0.073242 | 123.7061 | 63.6292 | -0.21973 | 123.7289 | -0.073242 | 63.6292 | 123.2208 | 123.7061 | -124.0311 | -124.0128
897.7188 | 124.118 | -61.0703 | 62.7548 | 0.074997 | 0.0057699 | 0.0097818 | -0.00049776 | 0.063666 | -0.00033333 | 0.068795 | -61.1023 | 62.645 | -61.2625 | -61.2442 | 62.1689 | 2.6093 | -2.1469 | -2.7191 | 62.6312 | -61.3083 | -0.19226 | -0.10986 | -0.032044 | -0.17395 | -0.58594 | -0.23804 | -0.1236 | 0.16022 | 58.9233 | 58.3511 | 123.2391 | 123.7152 | -0.032044 | 123.7015 | 63.6795 | -0.23804 | 123.7152 | -0.032044 | 63.6795 | 123.2391 | 123.7015 | -124.0173 | -124.0631
898.7188 | 124.1272 | -61.0565 | 62.7319 | 0.12077 | 0.0038473 | 0.0061502 | 0.001852 | 0.063025 | -0.00097413 | 0.06965 | -61.1069 | 62.6404 | -61.2625 | -61.235 | 62.1735 | 2.6276 | -2.1835 | -2.7649 | 62.6038 | -61.29 | -0.20599 | -0.091553 | -0.050354 | -0.17853 | -0.55847 | -0.23346 | -0.12817 | 0.15564 | 58.873 | 58.2916 | 123.23 | 123.6969 | -0.050354 | 123.6603 | 63.6841 | -0.23346 | 123.6969 | -0.050354 | 63.6841 | 123.23 | 123.6603 | -123.9944 | -124.0219
899.7188 | 124.1272 | -61.0886 | 62.7731 | 0.04448 | 0.0044881 | 0.0055094 | -0.0022068 | 0.061957 | -0.0048193 | 0.068368 | -61.1526 | 62.6175 | -61.2671 | -61.2625 | 62.146 | 2.6779 | -2.1561 | -2.8381 | 62.6358 | -61.2717 | -0.17853 | -0.15564 | -0.064087 | -0.17395 | -0.62714 | -0.1831 | -0.13733 | 0.11444 | 58.9325 | 58.2504 | 123.2346 | 123.7061 | -0.064087 | 123.7244 | 63.7665 | -0.1831 | 123.7061 | -0.064087 | 63.7665 | 123.2346 | 123.7244 | -124.0402 | -124.0448
900.7188 | 124.1364 | -61.0565 | 62.7502 | 0.15892 | 0.0064107 | 0.0042276 | 0.0027066 | 0.064093 | -0.0026831 | 0.068154 | -61.0748 | 62.6358 | -61.2717 | -61.1984 | 62.1826 | 2.71 | -2.2842 | -2.8748 | 62.6358 | -61.2946 | -0.21515 | -0.11444 | -0.01831 | -0.14191 | -0.56763 | -0.23804 | -0.11444 | 0.19684 | 58.7723 | 58.1818 | 123.2391 | 123.6923 | -0.01831 | 123.6923 | 63.7665 | -0.23804 | 123.6923 | -0.01831 | 63.7665 | 123.2391 | 123.6923 | -124.0219 | -124.0448
901.7188 | 124.1684 | -61.0748 | 62.7594 | 0.15129 | 0.0047019 | 0.0072184 | 0.0029202 | 0.063239 | -0.0048193 | 0.070931 | -61.084 | 62.6816 | -61.2671 | -61.1984 | 62.1735 | 2.7191 | -2.3392 | -2.9343 | 62.6495 | -61.2762 | -0.19226 | -0.077819 | -0.009155 | -0.1236 | -0.58594 | -0.20142 | -0.10986 | 0.18311 | 58.7357 | 58.1406 | 123.2483 | 123.7564 | -0.009155 | 123.7244 | 63.7939 | -0.20142 | 123.7564 | -0.009155 | 63.7939 | 123.2483 | 123.7244 | -124.0265 | -124.0356
902.7188 | 124.1592 | -61.0565 | 62.7136 | -0.10811 | 0.0061971 | 0.0078592 | 0.00099764 | 0.064093 | -0.0028967 | 0.069009 | -61.1069 | 62.6404 | -61.2671 | -61.1893 | 62.2009 | 2.742 | -2.3621 | -2.9892 | 62.6495 | -61.2534 | -0.21057 | -0.073242 | -0.050354 | -0.13275 | -0.5127 | -0.19684 | -0.064087 | 0.16022 | 58.6945 | 58.0673 | 123.2574 | 123.6969 | -0.050354 | 123.7061 | 63.7985 | -0.19684 | 123.6969 | -0.050354 | 63.7985 | 123.2574 | 123.7061 | -123.9807 | -123.967
903.7188 | 124.1501 | -61.0611 | 62.7548 | 0.18944 | 0.0042745 | 0.0070048 | 0.00078404 | 0.063452 | -0.00097413 | 0.069436 | -61.084 | 62.6495 | -61.2717 | -61.2259 | 62.1506 | 2.7054 | -2.3529 | -3.0258 | 62.6404 | -61.2808 | -0.21057 | -0.10529 | -0.022888 | -0.16479 | -0.60425 | -0.21973 | -0.11444 | 0.18768 | 58.7082 | 58.0353 | 123.2117 | 123.7106 | -0.022888 | 123.7015 | 63.7665 | -0.21973 | 123.7106 | -0.022888 | 63.7665 | 123.2117 | 123.7015 | -124.0265 | -124.0356
904.7188 | 124.1364 | -61.0611 | 62.7457 | 0.13603 | 0.0057699 | 0.0080728 | 0.001852 | 0.064307 | -0.0026831 | 0.068368 | -61.0886 | 62.6633 | -61.2579 | -61.2305 | 62.178 | 2.7374 | -2.4124 | -3.0716 | 62.6404 | -61.2717 | -0.19684 | -0.082398 | -0.027466 | -0.16937 | -0.56763 | -0.21057 | -0.10529 | 0.16937 | 58.6487 | 57.9895 | 123.2391 | 123.7244 | -0.027466 | 123.7015 | 63.7985 | -0.21057 | 123.7244 | -0.027466 | 63.7985 | 123.2391 | 123.7015 | -124.0036 | -124.0173
905.7188 | 124.1272 | -61.0519 | 62.7365 | 0.18181 | 0.0066245 | 0.010636 | -0.0013522 | 0.065589 | -0.0031103 | 0.068582 | -61.0977 | 62.6358 | -61.2534 | -61.2259 | 62.1643 | 2.774 | -2.4582 | -3.1219 | 62.6312 | -61.29 | -0.20142 | -0.10071 | -0.045776 | -0.17395 | -0.5722 | -0.23804 | -0.10529 | 0.15564 | 58.5938 | 57.93 | 123.2162 | 123.6877 | -0.045776 | 123.6832 | 63.826 | -0.23804 | 123.6877 | -0.045776 | 63.826 | 123.2162 | 123.6832 | -123.9899 | -124.0265
906.7188 | 124.1135 | -61.0428 | 62.7274 | 0.15129 | 0.0076925 | 0.0085 | 0.0016384 | 0.063025 | -0.0028967 | 0.069222 | -61.0886 | 62.645 | -61.2488 | -61.2122 | 62.1643 | 2.7924 | -2.4994 | -3.1769 | 62.6312 | -61.2625 | -0.20599 | -0.082398 | -0.045776 | -0.16937 | -0.56305 | -0.21973 | -0.09613 | 0.16022 | 58.5434 | 57.8659 | 123.2071 | 123.6877 | -0.045776 | 123.674 | 63.8351 | -0.21973 | 123.6877 | -0.045776 | 63.8351 | 123.2071 | 123.674 | -123.9761 | -123.9899
907.7188 | 124.1226 | -61.0291 | 62.7457 | 0.12077 | 0.0051291 | 0.005723 | 0.0012112 | 0.062384 | -0.0031103 | 0.068582 | -61.0748 | 62.6816 | -61.2671 | -61.2076 | 62.1735 | 2.8107 | -2.536 | -3.2227 | 62.6495 | -61.2762 | -0.23804 | -0.064087 | -0.045776 | -0.17853 | -0.5722 | -0.24719 | -0.096131 | 0.19226 | 58.493 | 57.8064 | 123.2025 | 123.7106 | -0.045776 | 123.6786 | 63.8397 | -0.24719 | 123.7106 | -0.045776 | 63.8397 | 123.2025 | 123.6786 | -124.0128 | -124.0219
908.7188 | 124.1684 | -61.0336 | 62.7228 | 0.24284 | 0.0059835 | 0.0097818 | 0.00078404 | 0.061316 | -0.0024695 | 0.069222 | -61.0565 | 62.6862 | -61.2534 | -61.203 | 62.2467 | 2.8473 | -2.6093 | -3.2272 | 62.6266 | -61.2579 | -0.21973 | -0.036621 | -0.022889 | -0.16937 | -0.47607 | -0.22431 | -0.09613 | 0.19684 | 58.4244 | 57.8064 | 123.2803 | 123.7198 | -0.022889 | 123.6603 | 63.8809 | -0.22431 | 123.7198 | -0.022889 | 63.8809 | 123.2803 | 123.6603 | -123.9761 | -123.9807
909.7188 | 124.1821 | -61.0565 | 62.7274 | 0.15129 | 0.0068381 | 0.011277 | 0.00014304 | 0.065589 | -0.0033239 | 0.070931 | -61.0565 | 62.6678 | -61.2671 | -61.2122 | 62.2467 | 2.8519 | -2.6321 | -3.241 | 62.6724 | -61.2671 | -0.21057 | -0.059509 | 0 | -0.15564 | -0.48065 | -0.21057 | -0.054932 | 0.21057 | 58.4244 | 57.8156 | 123.3032 | 123.7244 | 0 | 123.7289 | 63.9084 | -0.21057 | 123.7244 | 0 | 63.9084 | 123.3032 | 123.7289 | -123.9944 | -123.9944
910.7188 | 124.1272 | -61.0474 | 62.796 | 0.090256 | 0.0057699 | 0.005723 | -7.0562e-05 | 0.063452 | 9.4068e-05 | 0.069222 | -61.1206 | 62.6495 | -61.2442 | -61.2488 | 62.1368 | 2.8061 | -2.5406 | -3.3554 | 62.6816 | -61.2579 | -0.19684 | -0.14649 | -0.073242 | -0.20142 | -0.65918 | -0.21057 | -0.11444 | 0.1236 | 58.5068 | 57.692 | 123.1842 | 123.6969 | -0.073242 | 123.7289 | 63.8535 | -0.21057 | 123.6969 | -0.073242 | 63.8535 | 123.1842 | 123.7289 | -124.0402 | -124.054
911.7188 | 124.1135 | -61.0657 | 62.7457 | 0.14366 | 0.0049155 | 0.011064 | -7.0562e-05 | 0.062812 | -0.0022559 | 0.068582 | -61.1252 | 62.6633 | -61.2762 | -61.2396 | 62.1185 | 2.8198 | -2.5772 | -3.4103 | 62.677 | -61.2671 | -0.21057 | -0.082398 | -0.059509 | -0.17395 | -0.62714 | -0.20142 | -0.068665 | 0.15106 | 58.4885 | 57.6553 | 123.1842 | 123.7289 | -0.059509 | 123.7427 | 63.8855 | -0.20142 | 123.7289 | -0.059509 | 63.8855 | 123.1842 | 123.7427 | -124.0219 | -124.0128
912.7188 | 124.0997 | -61.0336 | 62.8006 | 0.12077 | 0.0066245 | 0.009141 | -0.0011386 | 0.062384 | -0.0014013 | 0.069436 | -61.1298 | 62.6678 | -61.2396 | -61.2305 | 62.1414 | 2.8244 | -2.6367 | -3.4882 | 62.6404 | -61.2854 | -0.20599 | -0.13275 | -0.096131 | -0.19684 | -0.65918 | -0.25177 | -0.16022 | 0.10986 | 58.3969 | 57.5455 | 123.175 | 123.7015 | -0.096131 | 123.674 | 63.858 | -0.25177 | 123.7015 | -0.096131 | 63.858 | 123.175 | 123.674 | -124.0402 | -124.086
913.7188 | 124.1043 | -61.0657 | 62.764 | 0.13603 | 0.0038473 | 0.0052958 | -0.00028416 | 0.059394 | -0.0028967 | 0.067941 | -61.1206 | 62.6541 | -61.2534 | -61.2167 | 62.1323 | 2.8473 | -2.6138 | -3.5065 | 62.6816 | -61.2625 | -0.18768 | -0.10986 | -0.054931 | -0.15106 | -0.63171 | -0.19684 | -0.082397 | 0.13275 | 58.4518 | 57.5592 | 123.1979 | 123.7198 | -0.054931 | 123.7473 | 63.913 | -0.19684 | 123.7198 | -0.054931 | 63.913 | 123.1979 | 123.7473 | -124.0173 | -124.0265
914.7188 | 124.1638 | -61.0382 | 62.7594 | -0.054703 | 0.0040609 | 0.0059366 | 0.00035684 | 0.062384 | -0.0020421 | 0.067727 | -61.1252 | 62.6816 | -61.2671 | -61.2167 | 62.1231 | 2.8656 | -2.6184 | -3.5065 | 62.6862 | -61.2579 | -0.22888 | -0.077819 | -0.086975 | -0.17853 | -0.63629 | -0.21973 | -0.073242 | 0.14191 | 58.4198 | 57.5317 | 123.1613 | 123.7198 | -0.086975 | 123.7244 | 63.9038 | -0.21973 | 123.7198 | -0.086975 | 63.9038 | 123.1613 | 123.7244 | -124.0265 | -124.0173
915.7188 | 124.1135 | -61.0382 | 62.7457 | 0.15892 | 0.0027791 | 0.009141 | 0.00099764 | 0.06388 | -0.00076053 | 0.067727 | -61.084 | 62.6266 | -61.2625 | -61.2213 | 62.146 | 2.861 | -2.7466 | -3.5202 | 62.645 | -61.2717 | -0.2243 | -0.11902 | -0.045776 | -0.18311 | -0.59967 | -0.23346 | -0.10071 | 0.17853 | 58.2916 | 57.518 | 123.1842 | 123.6649 | -0.045776 | 123.6832 | 63.8992 | -0.23346 | 123.6649 | -0.045776 | 63.8992 | 123.1842 | 123.6832 | -124.0082 | -124.0173
916.7188 | 124.1135 | -61.0382 | 62.7502 | 0.14366 | 0.0049155 | 0.004014 | -0.00071136 | 0.063666 | -0.0014013 | 0.068795 | -61.0703 | 62.645 | -61.2396 | -61.2122 | 62.1368 | 2.8702 | -2.7603 | -3.566 | 62.6724 | -61.2625 | -0.20142 | -0.10529 | -0.032043 | -0.17395 | -0.6134 | -0.2243 | -0.07782 | 0.16937 | 58.2779 | 57.4722 | 123.175 | 123.6832 | -0.032043 | 123.7106 | 63.9084 | -0.2243 | 123.6832 | -0.032043 | 63.9084 | 123.175 | 123.7106 | -123.9899 | -124.0128
917.7188 | 124.118 | -61.0428 | 62.7777 | -0.024185 | 0.0055563 | 0.01085 | -0.001566 | 0.060248 | -0.00097413 | 0.067086 | -61.1298 | 62.6495 | -61.2625 | -61.2076 | 62.1277 | 2.916 | -2.7283 | -3.598 | 62.6816 | -61.2442 | -0.21973 | -0.12817 | -0.086975 | -0.16479 | -0.65002 | -0.20142 | -0.09613 | 0.13275 | 58.3145 | 57.4448 | 123.1705 | 123.6923 | -0.086975 | 123.7244 | 63.9587 | -0.20142 | 123.6923 | -0.086975 | 63.9587 | 123.1705 | 123.7244 | -124.0402 | -124.0219
918.7188 | 124.1501 | -61.0382 | 62.796 | -0.031814 | 0.0044881 | 0.009141 | -0.0013522 | 0.061316 | -0.0024695 | 0.0673 | -61.1114 | 62.6816 | -61.2579 | -61.2259 | 62.1323 | 2.9205 | -2.7557 | -3.6209 | 62.6633 | -61.2442 | -0.21973 | -0.11444 | -0.073242 | -0.18768 | -0.66376 | -0.20599 | -0.13275 | 0.14649 | 58.2825 | 57.4173 | 123.1705 | 123.7198 | -0.073242 | 123.7015 | 63.9587 | -0.20599 | 123.7198 | -0.073242 | 63.9587 | 123.1705 | 123.7015 | -124.054 | -124.0402
919.7188 | 124.1318 | -61.0291 | 62.7731 | -0.0089264 | 0.0042745 | 0.005723 | -0.00092496 | 0.060462 | -0.00076053 | 0.066232 | -61.1023 | 62.6587 | -61.2442 | -61.2167 | 62.1368 | 2.9251 | -2.8061 | -3.6713 | 62.6633 | -61.2442 | -0.21515 | -0.11444 | -0.073242 | -0.18768 | -0.63629 | -0.21515 | -0.10986 | 0.14191 | 58.223 | 57.3578 | 123.1659 | 123.6877 | -0.073242 | 123.6923 | 63.9542 | -0.21515 | 123.6877 | -0.073242 | 63.9542 | 123.1659 | 123.6923 | -124.0173 | -124.0173
920.7188 | 124.1318 | -61.0611 | 62.8052 | 0.013962 | 0.0051291 | 0.0082864 | -0.0024204 | 0.062384 | -0.00097413 | 0.070077 | -61.1023 | 62.6678 | -61.2442 | -61.2122 | 62.1414 | 2.9663 | -2.8427 | -3.7125 | 62.6907 | -61.2259 | -0.18311 | -0.13733 | -0.041199 | -0.15106 | -0.66376 | -0.16479 | -0.11444 | 0.14191 | 58.2184 | 57.3486 | 123.2025 | 123.7289 | -0.041199 | 123.7518 | 64.0274 | -0.16479 | 123.7289 | -0.041199 | 64.0274 | 123.2025 | 123.7518 | -124.0494 | -124.0311
921.7188 | 124.1226 | -61.0336 | 62.796 | -0.031814 | 0.0038473 | 0.0033732 | 0.00014304 | 0.060462 | -0.0022559 | 0.069436 | -61.1023 | 62.6862 | -61.2442 | -61.1938 | 62.1323 | 2.98 | -2.9022 | -3.7582 | 62.677 | -61.2625 | -0.21057 | -0.10986 | -0.068665 | -0.16022 | -0.66376 | -0.22888 | -0.11902 | 0.14191 | 58.1314 | 57.2754 | 123.1659 | 123.7198 | -0.068665 | 123.7106 | 64.0137 | -0.22888 | 123.7198 | -0.068665 | 64.0137 | 123.1659 | 123.7106 | -124.0402 | -124.0585
922.7188 | 124.118 | -61.0291 | 62.8052 | 0.13603 | 0.0061971 | 0.0082864 | -0.0011386 | 0.062598 | -0.00054693 | 0.068154 | -61.1069 | 62.6495 | -61.2534 | -61.235 | 62.1231 | 2.9709 | -2.9572 | -3.8315 | 62.6678 | -61.2579 | -0.2243 | -0.15564 | -0.07782 | -0.20599 | -0.68207 | -0.22888 | -0.13733 | 0.14648 | 58.0719 | 57.1976 | 123.1522 | 123.6786 | -0.07782 | 123.6969 | 63.9999 | -0.22888 | 123.6786 | -0.07782 | 63.9999 | 123.1522 | 123.6969 | -124.0585 | -124.0631
923.7188 | 124.2371 | -61.0153 | 62.8006 | 0.10551 | 0.0051291 | 0.0046548 | -0.00092496 | 0.061957 | -0.0011877 | 0.06965 | -61.1114 | 62.6587 | -61.2488 | -61.2122 | 62.114 | 2.9984 | -2.9755 | -3.8681 | 62.6678 | -61.2396 | -0.23346 | -0.14191 | -0.09613 | -0.19684 | -0.68664 | -0.2243 | -0.13275 | 0.13733 | 58.0399 | 57.1472 | 123.1293 | 123.674 | -0.09613 | 123.6832 | 64.0137 | -0.2243 | 123.674 | -0.09613 | 64.0137 | 123.1293 | 123.6832 | -124.0494 | -124.0402
924.7188 | 124.1455 | -61.0153 | 62.7869 | -0.17677 | 0.0044881 | 0.0082864 | -0.0030612 | 0.061743 | -0.0033239 | 0.067513 | -61.0245 | 62.6678 | -61.2213 | -60.8459 | 62.2559 | 2.8473 | -3.0167 | -3.7628 | 62.6953 | -61.2396 | -0.20599 | -0.11902 | -0.009155 | 0.16937 | -0.53101 | -0.2243 | -0.091553 | 0.19684 | 57.9987 | 57.2525 | 123.2712 | 123.6832 | -0.009155 | 123.7106 | 63.8626 | -0.2243 | 123.6832 | -0.009155 | 63.8626 | 123.2712 | 123.7106 | -124.0082 | -124.0265
925.7188 | 124.1867 | -61.0107 | 62.7914 | -0.077591 | 0.0057699 | 0.0082864 | -0.0037022 | 0.062384 | -0.0018285 | 0.067727 | -61.0565 | 62.677 | -61.2259 | -61.1481 | 62.1643 | 3.0808 | -3.067 | -3.8589 | 62.6999 | -61.2488 | -0.21515 | -0.11444 | -0.045777 | -0.13733 | -0.62714 | -0.23804 | -0.091553 | 0.16937 | 57.9437 | 57.1518 | 123.175 | 123.6877 | -0.045777 | 123.7106 | 64.0915 | -0.23804 | 123.6877 | -0.045777 | 64.0915 | 123.175 | 123.7106 | -124.0173 | -124.0402
926.7188 | 124.173 | -60.9924 | 62.8143 | -0.08522 | 0.0038473 | 0.0089274 | -0.00092496 | 0.063025 | -0.0018285 | 0.068582 | -61.0565 | 62.677 | -61.2213 | -61.1755 | 62.1689 | 3.1128 | -3.1128 | -3.9139 | 62.6907 | -61.1984 | -0.22888 | -0.13733 | -0.064087 | -0.1831 | -0.64545 | -0.20599 | -0.1236 | 0.16479 | 57.8796 | 57.0786 | 123.1613 | 123.6694 | -0.064087 | 123.6832 | 64.1052 | -0.20599 | 123.6694 | -0.064087 | 64.1052 | 123.1613 | 123.6832 | -124.0356 | -124.0128
927.7188 | 124.1684 | -61.0153 | 62.7914 | -0.08522 | 0.0051291 | 0.010636 | -0.0013522 | 0.062384 | -0.0016149 | 0.070077 | -61.0382 | 62.6724 | -61.2076 | -61.1435 | 62.1643 | 3.1357 | -3.1723 | -3.9551 | 62.6953 | -61.2122 | -0.19226 | -0.11902 | -0.022888 | -0.12817 | -0.62714 | -0.19684 | -0.096131 | 0.16937 | 57.843 | 57.0602 | 123.1796 | 123.6877 | -0.022888 | 123.7106 | 64.151 | -0.19684 | 123.6877 | -0.022888 | 64.151 | 123.1796 | 123.7106 | -123.999 | -124.0036
928.7188 | 124.1638 | -61.0016 | 62.8006 | -0.031814 | 0.0051291 | 0.0042276 | -0.0011386 | 0.062384 | -0.00097413 | 0.071786 | -61.0565 | 62.6678 | -61.2259 | -61.1572 | 62.1506 | 3.1677 | -3.2135 | -4.0009 | 62.6816 | -61.2305 | -0.2243 | -0.13275 | -0.054932 | -0.15564 | -0.65002 | -0.22888 | -0.11902 | 0.16937 | 57.7881 | 57.0007 | 123.1522 | 123.6694 | -0.054932 | 123.6832 | 64.1693 | -0.22888 | 123.6694 | -0.054932 | 64.1693 | 123.1522 | 123.6832 | -124.0265 | -124.0311
929.7188 | 124.1226 | -61.0153 | 62.8006 | 0.04448 | 0.0040609 | 0.0089274 | 0.00014304 | 0.062384 | -0.00054693 | 0.069009 | -61.1023 | 62.677 | -61.2442 | -61.203 | 62.1094 | 3.1219 | -3.2272 | -4.1153 | 62.6724 | -61.235 | -0.22888 | -0.1236 | -0.086975 | -0.18768 | -0.69122 | -0.21973 | -0.12817 | 0.14191 | 57.7881 | 56.9 | 123.1247 | 123.6923 | -0.086975 | 123.6877 | 64.1373 | -0.21973 | 123.6923 | -0.086975 | 64.1373 | 123.1247 | 123.6877 | -124.0448 | -124.0356
930.7188 | 124.1455 | -60.9833 | 62.8006 | -0.10048 | 0.0036337 | 0.0087138 | -0.0013522 | 0.06153 | -0.0016149 | 0.06965 | -61.0703 | 62.677 | -61.2488 | -61.1481 | 62.1597 | 3.1906 | -3.2639 | -4.097 | 62.7182 | -61.2396 | -0.2655 | -0.1236 | -0.086975 | -0.1648 | -0.64087 | -0.25635 | -0.082397 | 0.17853 | 57.7194 | 56.8863 | 123.143 | 123.6603 | -0.086975 | 123.7015 | 64.1739 | -0.25635 | 123.6603 | -0.086975 | 64.1739 | 123.143 | 123.7015 | -124.0494 | -124.0402
931.7188 | 124.1776 | -60.9879 | 62.7914 | -0.08522 | 0.0044881 | 0.0070048 | -0.0019932 | 0.062812 | -0.00076053 | 0.067941 | -61.0107 | 62.6633 | -61.1984 | -61.116 | 62.1964 | 3.2043 | -3.3005 | -4.0878 | 62.6953 | -61.2167 | -0.21057 | -0.12817 | -0.022888 | -0.12817 | -0.59509 | -0.22888 | -0.096131 | 0.18768 | 57.6874 | 56.9 | 123.1842 | 123.6511 | -0.022888 | 123.6832 | 64.1922 | -0.22888 | 123.6511 | -0.022888 | 64.1922 | 123.1842 | 123.6832 | -123.9899 | -124.0082
932.7188 | 124.2096 | -61.0199 | 62.8189 | -0.069961 | 0.0036337 | 0.0078592 | -0.0019932 | 0.061103 | -0.0028967 | 0.068368 | -61.0199 | 62.6724 | -61.203 | -61.1206 | 62.2101 | 3.2547 | -3.3417 | -4.1199 | 62.6907 | -61.2305 | -0.18311 | -0.14648 | 0 | -0.10071 | -0.60883 | -0.21057 | -0.12817 | 0.18311 | 57.6782 | 56.9 | 123.23 | 123.6923 | 0 | 123.7106 | 64.2746 | -0.21057 | 123.6923 | 0 | 64.2746 | 123.23 | 123.7106 | -124.0219 | -124.0494
933.7188 | 124.1867 | -61.0016 | 62.796 | -0.039444 | 0.0066245 | 0.0099954 | -0.00049776 | 0.063666 | -0.0018285 | 0.068154 | -61.0153 | 62.6907 | -61.2213 | -61.1206 | 62.178 | 3.273 | -3.3966 | -4.1382 | 62.6953 | -61.2122 | -0.21973 | -0.10529 | -0.013733 | -0.11902 | -0.61798 | -0.21057 | -0.10071 | 0.20599 | 57.605 | 56.8634 | 123.1796 | 123.6923 | -0.013733 | 123.6969 | 64.2746 | -0.21057 | 123.6923 | -0.013733 | 64.2746 | 123.1796 | 123.6969 | -124.0173 | -124.0082
934.7188 | 124.1959 | -61.0016 | 62.8281 | -0.11574 | 0.0044881 | 0.009141 | -0.0013522 | 0.061743 | -0.0020421 | 0.068582 | -61.0062 | 62.6633 | -61.2213 | -61.1069 | 62.178 | 3.2822 | -3.4378 | -4.2252 | 62.6862 | -61.1984 | -0.21973 | -0.16479 | -0.004578 | -0.10529 | -0.65002 | -0.19684 | -0.14191 | 0.21515 | 57.5638 | 56.7764 | 123.1796 | 123.6649 | -0.004578 | 123.6877 | 64.2838 | -0.19684 | 123.6649 | -0.004578 | 64.2838 | 123.1796 | 123.6877 | -124.0494 | -124.0265
935.7188 | 124.1638 | -60.997 | 62.796 | -0.039444 | 0.0049155 | 0.0093546 | -0.0022068 | 0.063025 | 0.00052127 | 0.06965 | -61.0291 | 62.677 | -61.2396 | -61.1298 | 62.1735 | 3.2913 | -3.479 | -4.2892 | 62.6678 | -61.2213 | -0.24262 | -0.11902 | -0.032044 | -0.13275 | -0.62256 | -0.2243 | -0.12817 | 0.21057 | 57.518 | 56.7078 | 123.1705 | 123.674 | -0.032044 | 123.6649 | 64.2883 | -0.2243 | 123.674 | -0.032044 | 64.2883 | 123.1705 | 123.6649 | -124.0356 | -124.0173
936.7188 | 124.1455 | -61.0428 | 62.8098 | 0.021591 | 0.0051291 | 0.006791 | -0.00092496 | 0.064521 | 0.00052127 | 0.066873 | -61.0977 | 62.677 | -61.2305 | -61.1755 | 62.1002 | 3.2547 | -3.5019 | -4.3671 | 62.6999 | -61.2167 | -0.18768 | -0.13275 | -0.054931 | -0.13275 | -0.70953 | -0.17395 | -0.10986 | 0.13275 | 57.5409 | 56.6757 | 123.143 | 123.7198 | -0.054931 | 123.7427 | 64.2975 | -0.17395 | 123.7198 | -0.054931 | 64.2975 | 123.143 | 123.7427 | -124.0402 | -124.0265
937.7188 | 124.1638 | -61.0062 | 62.8143 | -0.11574 | 0.0047019 | 0.0059366 | -0.00049776 | 0.062384 | -0.0020421 | 0.067727 | -61.0336 | 62.6862 | -61.2076 | -61.1298 | 62.1414 | 3.3096 | -3.5568 | -4.3579 | 62.6816 | -61.2167 | -0.20142 | -0.12817 | -0.027465 | -0.1236 | -0.67291 | -0.21057 | -0.13275 | 0.17395 | 57.4493 | 56.6483 | 123.1476 | 123.6923 | -0.027465 | 123.6877 | 64.3158 | -0.21057 | 123.6923 | -0.027465 | 64.3158 | 123.1476 | 123.6877 | -124.0219 | -124.0311
938.7188 | 124.2371 | -61.0153 | 62.7869 | -0.19966 | 0.0051291 | 0.0076456 | -0.0022068 | 0.063452 | -0.0014013 | 0.067941 | -60.9787 | 62.6907 | -61.1984 | -61.1252 | 62.1552 | 3.4012 | -3.1998 | -4.6188 | 62.7228 | -61.1847 | -0.1831 | -0.09613 | 0.036621 | -0.10986 | -0.63171 | -0.16937 | -0.064087 | 0.21973 | 57.8156 | 56.3965 | 123.1705 | 123.7061 | 0.036621 | 123.7381 | 64.4165 | -0.16937 | 123.7061 | 0.036621 | 64.4165 | 123.1705 | 123.7381 | -123.9853 | -123.9716
939.7188 | 124.3195 | -60.9879 | 62.883 | -0.16151 | 0.0070517 | 0.0063638 | -0.00092496 | 0.061103 | -0.0011877 | 0.067941 | -60.9924 | 62.6678 | -61.1893 | -61.116 | 62.1735 | 3.3646 | -3.6163 | -4.4266 | 62.6907 | -61.1938 | -0.20142 | -0.21515 | -0.004578 | -0.12817 | -0.70953 | -0.20599 | -0.19226 | 0.19684 | 57.3715 | 56.5613 | 123.1613 | 123.6557 | -0.004578 | 123.6786 | 64.3524 | -0.20599 | 123.6557 | -0.004578 | 64.3524 | 123.1613 | 123.6786 | -124.0723 | -124.0768
940.7188 | 124.1776 | -61.0062 | 62.796 | -0.131 | 0.0059835 | 0.0065774 | -0.0022068 | 0.062812 | -0.0018285 | 0.067513 | -61.0062 | 62.6587 | -61.1984 | -61.1023 | 62.178 | 3.3966 | -3.6713 | -4.4586 | 62.6907 | -61.1893 | -0.19226 | -0.13733 | 0 | -0.09613 | -0.61798 | -0.1831 | -0.10529 | 0.19226 | 57.3349 | 56.5475 | 123.1842 | 123.6649 | 0 | 123.6969 | 64.4028 | -0.1831 | 123.6649 | 0 | 64.4028 | 123.1842 | 123.6969 | -123.9944 | -123.9853
941.7188 | 124.2004 | -61.0107 | 62.8052 | -0.12337 | 0.0034201 | 0.006791 | -0.0019932 | 0.063239 | -0.00033333 | 0.068368 | -61.0199 | 62.6907 | -61.203 | -61.0977 | 62.1826 | 3.4195 | -3.7308 | -4.4678 | 62.7182 | -61.1938 | -0.19226 | -0.11444 | -0.009155 | -0.086975 | -0.62256 | -0.18311 | -0.086975 | 0.18311 | 57.28 | 56.543 | 123.1934 | 123.7015 | -0.009155 | 123.7289 | 64.4302 | -0.18311 | 123.7015 | -0.009155 | 64.4302 | 123.1934 | 123.7289 | -124.0082 | -123.999
942.7188 | 124.1638 | -60.997 | 62.7914 | -0.13863 | 0.0091879 | 0.0070048 | -0.00071136 | 0.061743 | -0.0031103 | 0.0673 | -61.1847 | 62.6724 | -61.203 | -61.1481 | 62.1643 | 3.4149 | -3.717 | -4.5181 | 62.6907 | -61.2122 | -0.20599 | -0.11902 | -0.18768 | -0.15106 | -0.62714 | -0.21515 | -0.10071 | 0.018311 | 57.28 | 56.4789 | 123.1613 | 123.6694 | -0.18768 | 123.6877 | 64.4119 | -0.21515 | 123.6694 | -0.18768 | 64.4119 | 123.1613 | 123.6877 | -123.9944 | -124.0036
943.7188 | 124.1089 | -61.0336 | 62.8052 | 0.013962 | 0.0064107 | 0.0072184 | -0.0011386 | 0.063025 | -0.0031103 | 0.068795 | -61.084 | 62.7136 | -61.2396 | -61.171 | 62.0911 | 3.4012 | -3.7811 | -4.6326 | 62.7182 | -61.2167 | -0.20599 | -0.091553 | -0.050354 | -0.13733 | -0.71411 | -0.18311 | -0.086975 | 0.15564 | 57.2525 | 56.4011 | 123.1247 | 123.7473 | -0.050354 | 123.7518 | 64.4348 | -0.18311 | 123.7473 | -0.050354 | 64.4348 | 123.1247 | 123.7518 | -124.0448 | -124.0219
944.7188 | 124.1638 | -61.0474 | 62.8189 | -0.0012969 | 0.0049155 | 0.0061502 | -0.00071136 | 0.061103 | -0.00011953 | 0.067727 | -61.0565 | 62.6953 | -61.2442 | -61.1938 | 62.0819 | 3.4195 | -3.8361 | -4.7104 | 62.709 | -61.2122 | -0.19684 | -0.1236 | -0.009156 | -0.14649 | -0.737 | -0.1648 | -0.10986 | 0.18768 | 57.2113 | 56.337 | 123.1293 | 123.7427 | -0.009156 | 123.7564 | 64.4669 | -0.1648 | 123.7427 | -0.009156 | 64.4669 | 123.1293 | 123.7564 | -124.0631 | -124.0311
945.7188 | 124.1135 | -61.0016 | 62.8098 | -0.16914 | 0.0047019 | 0.0078592 | -0.0034886 | 0.061743 | -0.0018285 | 0.068154 | -60.9833 | 62.6862 | -61.2167 | -61.0977 | 62.1597 | 3.4927 | -3.4103 | -4.3533 | 62.7502 | -61.1755 | -0.21515 | -0.1236 | 0.018311 | -0.09613 | -0.65002 | -0.17395 | -0.059509 | 0.23346 | 57.5912 | 56.6483 | 123.1613 | 123.6877 | 0.018311 | 123.7518 | 64.4943 | -0.17395 | 123.6877 | 0.018311 | 64.4943 | 123.1613 | 123.7518 | -124.0265 | -123.9853
946.7188 | 124.2325 | -60.9695 | 62.883 | -0.1844 | 0.0053427 | 0.0076456 | -0.00092496 | 0.065161 | -0.0043921 | 0.069009 | -60.997 | 62.6678 | -61.2122 | -61.084 | 62.1597 | 3.4927 | -3.9139 | -4.6967 | 62.7045 | -61.203 | -0.24262 | -0.21515 | -0.027466 | -0.11444 | -0.72327 | -0.23346 | -0.17853 | 0.21515 | 57.0557 | 56.2729 | 123.1293 | 123.6374 | -0.027466 | 123.674 | 64.4623 | -0.23346 | 123.6374 | -0.027466 | 64.4623 | 123.1293 | 123.674 | -124.0952 | -124.086
947.7188 | 124.1501 | -60.9879 | 62.8555 | -0.30647 | 0.0049155 | 0.0044412 | 0.00057044 | 0.063452 | -0.0031103 | 0.067941 | -61.0107 | 62.7045 | -61.2076 | -61.1069 | 62.114 | 3.4973 | -3.9597 | -4.7836 | 62.6907 | -61.2122 | -0.21973 | -0.15106 | -0.022888 | -0.11902 | -0.74158 | -0.2243 | -0.1648 | 0.19684 | 57.0282 | 56.2042 | 123.1018 | 123.6923 | -0.022888 | 123.6786 | 64.4852 | -0.2243 | 123.6923 | -0.022888 | 64.4852 | 123.1018 | 123.6786 | -124.0631 | -124.0677
948.7188 | 124.1959 | -61.0107 | 62.8418 | -0.13863 | 0.0042745 | 0.0089274 | -0.00092496 | 0.062598 | -0.0020421 | 0.068582 | -60.997 | 62.6953 | -61.2076 | -61.0931 | 62.1552 | 3.5431 | -4.0466 | -4.834 | 62.7136 | -61.171 | -0.19684 | -0.14648 | 0.013733 | -0.082398 | -0.68665 | -0.16022 | -0.12817 | 0.21057 | 56.9641 | 56.1768 | 123.1659 | 123.7061 | 0.013733 | 123.7244 | 64.5538 | -0.16022 | 123.7061 | 0.013733 | 64.5538 | 123.1659 | 123.7244 | -124.0494 | -124.0128
949.7188 | 124.205 | -60.9787 | 62.8281 | -0.08522 | 0.0059835 | 0.0078592 | -0.001566 | 0.06153 | -0.0039649 | 0.068795 | -61.0153 | 62.709 | -61.203 | -61.1252 | 62.1231 | 3.5522 | -4.0878 | -4.8798 | 62.6999 | -61.1984 | -0.2243 | -0.11902 | -0.036621 | -0.14648 | -0.70496 | -0.21973 | -0.12817 | 0.18768 | 56.8909 | 56.0989 | 123.1018 | 123.6877 | -0.036621 | 123.6786 | 64.5309 | -0.21973 | 123.6877 | -0.036621 | 64.5309 | 123.1018 | 123.6786 | -124.0311 | -124.0265
950.7188 | 124.1501 | -60.9924 | 62.8235 | -0.024185 | 0.0051291 | 0.0095682 | -0.0024204 | 0.061316 | -0.0033239 | 0.068795 | -61.0703 | 62.6816 | -61.2122 | -61.1664 | 62.0682 | 3.5339 | -4.129 | -5.0079 | 62.6999 | -61.2122 | -0.21973 | -0.14191 | -0.077819 | -0.17395 | -0.75531 | -0.21973 | -0.1236 | 0.14191 | 56.8634 | 55.9845 | 123.0606 | 123.674 | -0.077819 | 123.6923 | 64.5264 | -0.21973 | 123.674 | -0.077819 | 64.5264 | 123.0606 | 123.6923 | -124.0356 | -124.0356
951.7188 | 124.1638 | -60.9924 | 62.796 | -0.09285 | 0.0040609 | 0.004014 | -0.0013522 | 0.063025 | -0.0026831 | 0.068795 | -61.0199 | 62.6862 | -61.2167 | -61.1389 | 62.1094 | 3.5706 | -4.1794 | -5.0034 | 62.6907 | -61.2122 | -0.2243 | -0.10986 | -0.027465 | -0.14648 | -0.68665 | -0.21973 | -0.10529 | 0.19684 | 56.8131 | 55.9891 | 123.1018 | 123.6786 | -0.027465 | 123.6832 | 64.563 | -0.21973 | 123.6786 | -0.027465 | 64.563 | 123.1018 | 123.6832 | -124.0128 | -124.0082
952.7188 | 124.1547 | -61.0062 | 62.8189 | -0.14626 | 0.0053427 | 0.010209 | 0.00099764 | 0.061743 | -0.0024695 | 0.070077 | -61.0016 | 62.6953 | -61.2122 | -61.1252 | 62.1185 | 3.598 | -4.1473 | -5.0171 | 62.7045 | -61.2122 | -0.20599 | -0.1236 | 0.004578 | -0.11902 | -0.70038 | -0.20599 | -0.11444 | 0.21057 | 56.8588 | 55.9891 | 123.1247 | 123.7015 | 0.004578 | 123.7106 | 64.6042 | -0.20599 | 123.7015 | 0.004578 | 64.6042 | 123.1247 | 123.7106 | -124.0311 | -124.0311
953.7188 | 124.324 | -60.9741 | 62.9059 | -0.15388 | 0.0051291 | 0.0055094 | 0.00078404 | 0.061316 | -0.0020421 | 0.067727 | -60.9833 | 62.6816 | -61.1984 | -61.0794 | 62.114 | 3.6438 | -4.2389 | -5.0354 | 62.6999 | -61.1618 | -0.2243 | -0.2243 | -0.009155 | -0.10529 | -0.79193 | -0.18768 | -0.20599 | 0.21515 | 56.7352 | 55.9387 | 123.0881 | 123.6557 | -0.009155 | 123.674 | 64.6179 | -0.18768 | 123.6557 | -0.009155 | 64.6179 | 123.0881 | 123.674 | -124.1043 | -124.0677
954.7188 | 124.2004 | -60.997 | 62.8326 | -0.20729 | 0.0038473 | 0.0061502 | -0.0017796 | 0.063025 | -0.00097413 | 0.067086 | -60.9924 | 62.6907 | -61.2122 | -61.0886 | 62.1277 | 3.6438 | -4.2892 | -5.1132 | 62.709 | -61.1938 | -0.21515 | -0.14191 | 0.004577 | -0.091553 | -0.70496 | -0.19684 | -0.1236 | 0.21973 | 56.7078 | 55.8838 | 123.1247 | 123.6877 | 0.004577 | 123.7061 | 64.6408 | -0.19684 | 123.6877 | 0.004577 | 64.6408 | 123.1247 | 123.7061 | -124.0448 | -124.0265
955.7188 | 124.2004 | -61.0016 | 62.8052 | -0.131 | 0.0053427 | 0.009141 | -0.0024204 | 0.06153 | -0.0024695 | 0.069009 | -60.9879 | 62.6862 | -61.2167 | -61.0977 | 62.1277 | 3.6942 | -4.3396 | -5.1498 | 62.7045 | -61.1893 | -0.21515 | -0.11902 | 0.013733 | -0.09613 | -0.67749 | -0.18768 | -0.10071 | 0.22888 | 56.662 | 55.8517 | 123.1293 | 123.6877 | 0.013733 | 123.7061 | 64.6957 | -0.18768 | 123.6877 | 0.013733 | 64.6957 | 123.1293 | 123.7061 | -124.0219 | -123.9944
956.7188 | 124.1318 | -61.0199 | 62.8418 | -0.069961 | 0.0044881 | 0.0087138 | -0.00071136 | 0.064734 | -0.00097413 | 0.069222 | -61.0474 | 62.6816 | -61.2167 | -61.1526 | 62.0773 | 3.6163 | -4.3945 | -5.2597 | 62.7045 | -61.2259 | -0.19684 | -0.16022 | -0.027466 | -0.13275 | -0.76447 | -0.20599 | -0.13733 | 0.16937 | 56.6254 | 55.7602 | 123.0972 | 123.7015 | -0.027466 | 123.7244 | 64.6362 | -0.20599 | 123.7015 | -0.027466 | 64.6362 | 123.0972 | 123.7244 | -124.0585 | -124.0677
957.7188 | 124.1089 | -61.0336 | 62.8555 | -0.26833 | 0.0061971 | 0.0099954 | 0.002493 | 0.062812 | 0.00052127 | 0.067727 | -61.0153 | 62.7411 | -61.203 | -61.1389 | 62.059 | 3.6255 | -4.2984 | -5.2689 | 62.7319 | -61.2213 | -0.16937 | -0.11444 | 0.01831 | -0.10529 | -0.79651 | -0.18768 | -0.1236 | 0.18768 | 56.7352 | 55.7648 | 123.0927 | 123.7747 | 0.01831 | 123.7656 | 64.6591 | -0.18768 | 123.7747 | 0.01831 | 64.6591 | 123.0927 | 123.7656 | -124.0585 | -124.0768
958.7188 | 124.1867 | -60.9695 | 62.8052 | -0.047073 | 0.0038473 | 0.005723 | -0.00049776 | 0.062384 | -0.0011877 | 0.068795 | -60.997 | 62.7045 | -61.2076 | -61.1069 | 62.1048 | 3.6758 | -4.454 | -5.2505 | 62.7411 | -61.1801 | -0.23804 | -0.10071 | -0.027466 | -0.13733 | -0.70038 | -0.21057 | -0.064087 | 0.21057 | 56.5155 | 55.719 | 123.0743 | 123.674 | -0.027466 | 123.7106 | 64.6454 | -0.21057 | 123.674 | -0.027466 | 64.6454 | 123.0743 | 123.7106 | -124.0128 | -123.9853
959.7188 | 124.1501 | -60.9924 | 62.8098 | -0.1844 | 0.0059835 | 0.0052958 | -0.001566 | 0.060248 | -0.0011877 | 0.068795 | -60.7132 | 62.7777 | -61.1572 | -61.0931 | 62.1597 | 3.6942 | -4.5181 | -5.2689 | 62.6999 | -61.203 | -0.16479 | -0.032043 | 0.27924 | -0.10071 | -0.65002 | -0.21057 | -0.10986 | 0.44403 | 56.4743 | 55.7236 | 123.1522 | 123.7701 | 0.27924 | 123.6923 | 64.6866 | -0.21057 | 123.7701 | 0.27924 | 64.6866 | 123.1522 | 123.6923 | -123.967 | -124.0128
960.7188 | 124.1501 | -60.997 | 62.8464 | -0.1844 | 0.0047019 | 0.0089274 | -0.0032748 | 0.061957 | -0.0018285 | 0.067941 | -60.9787 | 62.6907 | -61.1801 | -61.1343 | 62.1735 | 3.7354 | -4.6097 | -5.3192 | 62.7136 | -61.2259 | -0.18311 | -0.15564 | 0.01831 | -0.13733 | -0.67291 | -0.22888 | -0.13275 | 0.20142 | 56.3873 | 55.6778 | 123.1705 | 123.6877 | 0.01831 | 123.7106 | 64.7324 | -0.22888 | 123.6877 | 0.01831 | 64.7324 | 123.1705 | 123.7106 | -124.0265 | -124.0723
961.7188 | 124.0768 | -61.0474 | 62.8464 | -0.16914 | 0.0098287 | 0.005723 | 0.005911 | 0.06388 | -0.0026831 | 0.066659 | -60.9787 | 62.7914 | -61.2076 | -61.1572 | 62.027 | 3.653 | -4.5136 | -5.5618 | 62.7365 | -61.2625 | -0.16022 | -0.054932 | 0.068664 | -0.10986 | -0.8194 | -0.21515 | -0.10986 | 0.22888 | 56.5338 | 55.4855 | 123.0743 | 123.8388 | 0.068664 | 123.7839 | 64.7003 | -0.21515 | 123.8388 | 0.068664 | 64.7003 | 123.0743 | 123.7839 | -124.054 | -124.1089
962.7188 | 124.0631 | -61.0245 | 62.8464 | -0.10811 | 0.0076925 | 0.012345 | 0.0050564 | 0.067084 | -0.0033239 | 0.069222 | -61.0062 | 62.796 | -61.2213 | -61.1526 | 62.0224 | 3.6896 | -4.5685 | -5.6213 | 62.7502 | -61.2442 | -0.19684 | -0.050354 | 0.01831 | -0.12817 | -0.82398 | -0.21973 | -0.096131 | 0.21515 | 56.456 | 55.4031 | 123.0469 | 123.8205 | 0.01831 | 123.7747 | 64.7141 | -0.21973 | 123.8205 | 0.01831 | 64.7141 | 123.0469 | 123.7747 | -124.0677 | -124.0906
963.7188 | 124.1638 | -61.0062 | 62.8143 | -0.09285 | 0.0047019 | 0.009141 | -0.0039158 | 0.065375 | -0.0016149 | 0.069222 | -61.0428 | 62.7182 | -61.2213 | -61.1481 | 62.0544 | 3.7674 | -4.7241 | -5.6122 | 62.7411 | -61.1984 | -0.21515 | -0.09613 | -0.036621 | -0.14191 | -0.75989 | -0.19226 | -0.073242 | 0.17853 | 56.282 | 55.394 | 123.0606 | 123.7244 | -0.036621 | 123.7473 | 64.7736 | -0.19226 | 123.7244 | -0.036621 | 64.7736 | 123.0606 | 123.7473 | -124.0356 | -124.0128
964.7188 | 124.173 | -61.0245 | 62.8006 | -0.062332 | 0.0014975 | 0.009141 | -0.0013522 | 0.063239 | -0.00097413 | 0.071145 | -61.0565 | 62.709 | -61.235 | -61.171 | 62.0544 | 3.7811 | -4.7928 | -5.7037 | 62.6999 | -61.203 | -0.21057 | -0.091553 | -0.032044 | -0.14648 | -0.74616 | -0.17853 | -0.10071 | 0.17853 | 56.2317 | 55.3207 | 123.0789 | 123.7335 | -0.032044 | 123.7244 | 64.8056 | -0.17853 | 123.7335 | -0.032044 | 64.8056 | 123.0789 | 123.7244 | -124.0356 | -124.0036
965.7188 | 124.1455 | -60.965 | 62.8098 | -0.80238 | 0.0059835 | 0.011704 | 0.0012112 | 0.060889 | -0.0024695 | 0.068368 | -61.0519 | 62.6862 | -61.2122 | -61.0977 | 62.0956 | 3.8498 | -4.7836 | -5.69 | 62.7274 | -61.203 | -0.24719 | -0.1236 | -0.086975 | -0.13275 | -0.71411 | -0.23804 | -0.082397 | 0.16022 | 56.1813 | 55.275 | 123.0606 | 123.6511 | -0.086975 | 123.6923 | 64.8148 | -0.23804 | 123.6511 | -0.086975 | 64.8148 | 123.0606 | 123.6923 | -124.0219 | -124.0128
966.7188 | 124.1135 | -60.9924 | 62.8418 | -0.20729 | 0.0040609 | 0.0076456 | 0.00099764 | 0.062598 | -0.0022559 | 0.069009 | -60.9879 | 62.6907 | -61.1893 | -61.1298 | 62.0728 | 3.8498 | -4.7974 | -5.777 | 62.7228 | -61.2167 | -0.19684 | -0.15106 | 0.004578 | -0.13733 | -0.76904 | -0.2243 | -0.11902 | 0.20142 | 56.1951 | 55.2155 | 123.0652 | 123.6832 | 0.004578 | 123.7152 | 64.8422 | -0.2243 | 123.6832 | 0.004578 | 64.8422 | 123.0652 | 123.7152 | -124.0311 | -124.0585
967.7188 | 124.0723 | -61.0153 | 62.8601 | -0.16151 | 0.0083333 | 0.0087138 | 0.0048428 | 0.063452 | -0.0043921 | 0.0673 | -61.0336 | 62.8052 | -61.2259 | -61.2122 | 61.9812 | 3.7811 | -4.747 | -5.9189 | 62.7823 | -61.2625 | -0.21057 | -0.054931 | -0.01831 | -0.19684 | -0.87891 | -0.24719 | -0.077819 | 0.19226 | 56.2683 | 55.0964 | 122.9965 | 123.8205 | -0.01831 | 123.7976 | 64.7964 | -0.24719 | 123.8205 | -0.01831 | 64.7964 | 122.9965 | 123.7976 | -124.086 | -124.1226
968.7188 | 124.1318 | -60.9924 | 62.8189 | -0.20729 | 0.0029929 | 0.0065774 | -0.00071136 | 0.063666 | -0.0039649 | 0.069436 | -60.9924 | 62.6999 | -61.1938 | -61.1206 | 62.0682 | 3.9001 | -4.9393 | -5.8502 | 62.7274 | -61.1801 | -0.20142 | -0.11902 | 0 | -0.12817 | -0.75073 | -0.18768 | -0.091553 | 0.20142 | 56.0532 | 55.1422 | 123.0606 | 123.6923 | 0 | 123.7198 | 64.8926 | -0.18768 | 123.6923 | 0 | 64.8926 | 123.0606 | 123.7198 | -124.0128 | -123.999
969.7188 | 124.1592 | -60.9924 | 62.8143 | 0.65483 | 0.0047019 | 0.011918 | -0.0024204 | 0.063025 | -0.0018285 | 0.067513 | -60.9467 | 62.6953 | -61.2122 | -61.116 | 62.0636 | 3.9368 | -4.9988 | -5.9052 | 62.7457 | -61.1938 | -0.21973 | -0.11902 | 0.045777 | -0.1236 | -0.75073 | -0.20142 | -0.068664 | 0.2655 | 55.9937 | 55.0873 | 123.056 | 123.6877 | 0.045777 | 123.7381 | 64.9292 | -0.20142 | 123.6877 | 0.045777 | 64.9292 | 123.056 | 123.7381 | -124.0265 | -124.0082
970.7188 | 124.1501 | -60.9924 | 62.8235 | -0.016556 | 0.0036337 | 0.006791 | 0.00014304 | 0.062812 | -0.0022559 | 0.068795 | -61.0519 | 62.7182 | -61.2213 | -61.1801 | 62.0041 | 3.891 | -5.072 | -6.0333 | 62.709 | -61.203 | -0.22888 | -0.10529 | -0.059509 | -0.18768 | -0.8194 | -0.21057 | -0.11444 | 0.16937 | 55.9204 | 54.9591 | 122.9965 | 123.7106 | -0.059509 | 123.7015 | 64.8834 | -0.21057 | 123.7106 | -0.059509 | 64.8834 | 122.9965 | 123.7015 | -124.0448 | -124.0265
971.7188 | 124.1135 | -61.0062 | 62.8281 | -0.024185 | 0.0051291 | 0.0076456 | -0.00028416 | 0.06153 | -0.0020421 | 0.0673 | -61.0474 | 62.7182 | -61.2259 | -61.1801 | 61.9904 | 3.8727 | -5.1086 | -6.0745 | 62.7274 | -61.2305 | -0.21973 | -0.10986 | -0.041198 | -0.17395 | -0.83771 | -0.2243 | -0.10071 | 0.17853 | 55.8975 | 54.9316 | 122.9965 | 123.7244 | -0.041198 | 123.7335 | 64.8788 | -0.2243 | 123.7244 | -0.041198 | 64.8788 | 122.9965 | 123.7335 | -124.054 | -124.0585
972.7188 | 124.0952 | -61.0199 | 62.8372 | -0.13863 | 0.0061971 | 0.0065774 | 0.005911 | 0.064734 | -0.0043921 | 0.068368 | -60.997 | 62.8052 | -61.1984 | -61.1618 | 61.972 | 3.8864 | -5.0171 | -6.1111 | 62.764 | -61.2625 | -0.17853 | -0.032043 | 0.022888 | -0.14191 | -0.86517 | -0.24262 | -0.073242 | 0.20142 | 56.0028 | 54.9088 | 122.9919 | 123.8251 | 0.022888 | 123.7839 | 64.9063 | -0.24262 | 123.8251 | 0.022888 | 64.9063 | 122.9919 | 123.7839 | -124.0356 | -124.0997
973.7344 | 124.1501 | -61.0062 | 62.8052 | 0.17418 | 0.0055563 | 0.0095682 | 0.004202 | 0.068152 | -0.0035375 | 0.069222 | -61.0062 | 62.7228 | -61.235 | -61.1664 | 61.9858 | 3.891 | -5.2963 | -6.2119 | 62.709 | -61.2259 | -0.22888 | -0.082398 | 0 | -0.16022 | -0.8194 | -0.21973 | -0.096131 | 0.22888 | 55.7098 | 54.7943 | 122.9919 | 123.7289 | 0 | 123.7152 | 64.8972 | -0.21973 | 123.7289 | 0 | 64.8972 | 122.9919 | 123.7152 | -124.0402 | -124.0311
974.7188 | 124.1913 | -61.0107 | 62.8098 | -0.10048 | 0.0057699 | 0.006791 | -0.0032748 | 0.065589 | -0.0020421 | 0.068154 | -61.0016 | 62.6907 | -61.2213 | -61.1298 | 62.0407 | 4.01 | -5.278 | -6.1661 | 62.7411 | -61.203 | -0.21057 | -0.11902 | 0.009155 | -0.11902 | -0.76904 | -0.19226 | -0.068664 | 0.21973 | 55.7327 | 54.8447 | 123.0515 | 123.7015 | 0.009155 | 123.7518 | 65.0208 | -0.19226 | 123.7015 | 0.009155 | 65.0208 | 123.0515 | 123.7518 | -124.0311 | -124.0128
975.7188 | 124.1409 | -60.997 | 62.7823 | -0.17677 | 0.0032065 | 0.0089274 | -0.0017796 | 0.061743 | -0.0011877 | 0.068154 | -60.9558 | 62.6862 | -61.1847 | -61.2122 | 62.3016 | 4.3304 | -5.6442 | -6.459 | 62.7274 | -61.1938 | -0.18768 | -0.096131 | 0.041198 | -0.21515 | -0.48065 | -0.19684 | -0.054932 | 0.22888 | 55.3528 | 54.538 | 123.2986 | 123.6832 | 0.041198 | 123.7244 | 65.3275 | -0.19684 | 123.6832 | 0.041198 | 65.3275 | 123.2986 | 123.7244 | -123.967 | -123.9761
976.7188 | 124.205 | -60.9695 | 62.8326 | -0.10811 | 0.0057699 | 0.0065774 | -0.0019932 | 0.062171 | -0.0031103 | 0.069222 | -60.9833 | 62.6862 | -61.1847 | -61.0931 | 62.0636 | 4.0924 | -5.3833 | -6.2668 | 62.7319 | -61.1755 | -0.21515 | -0.14648 | -0.013733 | -0.1236 | -0.76904 | -0.20599 | -0.10071 | 0.20142 | 55.5862 | 54.7028 | 123.0331 | 123.6557 | -0.013733 | 123.7015 | 65.0619 | -0.20599 | 123.6557 | -0.013733 | 65.0619 | 123.0331 | 123.7015 | -124.0173 | -124.0082
977.7188 | 124.086 | -61.0016 | 62.8601 | -0.19966 | 0.0055563 | 0.0048684 | -7.0562e-05 | 0.061743 | -0.0033239 | 0.069436 | -60.9924 | 62.7365 | -61.1847 | -61.1435 | 61.9766 | 4.0283 | -5.3513 | -6.4087 | 62.7594 | -61.2213 | -0.1831 | -0.1236 | 0.009155 | -0.14191 | -0.88348 | -0.21973 | -0.10071 | 0.19226 | 55.6503 | 54.5929 | 122.9782 | 123.7381 | 0.009155 | 123.761 | 65.0299 | -0.21973 | 123.7381 | 0.009155 | 65.0299 | 122.9782 | 123.761 | -124.0448 | -124.0814
978.7188 | 124.1684 | -60.9787 | 62.8418 | -0.1844 | 0.0040609 | 0.0070048 | 0.0020656 | 0.064307 | -0.0022559 | 0.069436 | -60.9695 | 62.7228 | -61.1938 | -61.1343 | 61.9217 | 4.0741 | -5.4611 | -6.4545 | 62.7274 | -61.2076 | -0.21515 | -0.11902 | 0.009156 | -0.15564 | -0.9201 | -0.22888 | -0.11444 | 0.22431 | 55.5176 | 54.5242 | 122.9004 | 123.7015 | 0.009156 | 123.7061 | 65.0528 | -0.22888 | 123.7015 | 0.009156 | 65.0528 | 122.9004 | 123.7061 | -124.0356 | -124.0494
979.7188 | 124.2142 | -60.997 | 62.8006 | -0.16914 | 0.0034201 | 0.0072184 | 0.00014304 | 0.063452 | -0.0031103 | 0.068582 | -60.9558 | 62.709 | -61.1755 | -61.0977 | 62.0453 | 4.01 | -5.0674 | -6.5186 | 62.7869 | -61.1664 | -0.17853 | -0.091553 | 0.041198 | -0.10071 | -0.75531 | -0.16937 | -0.013733 | 0.21973 | 55.9296 | 54.4785 | 123.0423 | 123.7061 | 0.041198 | 123.7839 | 65.007 | -0.16937 | 123.7061 | 0.041198 | 65.007 | 123.0423 | 123.7839 | -123.9761 | -123.967
980.7188 | 124.2004 | -60.9924 | 62.8372 | -0.10811 | 0.0047019 | 0.0065774 | -0.00092496 | 0.063025 | -0.0022559 | 0.06965 | -60.9741 | 62.6862 | -61.1664 | -61.0886 | 62.0361 | 4.1565 | -5.6396 | -6.5369 | 62.7136 | -61.1984 | -0.17395 | -0.15106 | 0.018311 | -0.09613 | -0.80109 | -0.20599 | -0.1236 | 0.19226 | 55.3528 | 54.4556 | 123.0286 | 123.6786 | 0.018311 | 123.7061 | 65.1489 | -0.20599 | 123.6786 | 0.018311 | 65.1489 | 123.0286 | 123.7061 | -124.0036 | -124.0356
981.7188 | 124.1638 | -60.9512 | 62.8235 | -0.09285 | 0.0034201 | 0.0089274 | 0.00014304 | 0.064307 | -0.0018285 | 0.069436 | -61.0062 | 62.6999 | -61.2076 | -61.1069 | 62.0361 | 4.1428 | -5.6946 | -6.5826 | 62.7457 | -61.1938 | -0.25635 | -0.1236 | -0.054932 | -0.15564 | -0.78735 | -0.24262 | -0.077819 | 0.20142 | 55.2567 | 54.3686 | 122.9874 | 123.6511 | -0.054932 | 123.6969 | 65.094 | -0.24262 | 123.6511 | -0.054932 | 65.094 | 122.9874 | 123.6969 | -124.0311 | -124.0173
982.7188 | 124.0768 | -61.0336 | 62.8738 | -0.16151 | 0.0053427 | 0.012559 | 0.0061246 | 0.064093 | -0.00076053 | 0.067513 | -61.0245 | 62.8189 | -61.2305 | -61.1984 | 61.9217 | 4.0421 | -5.5618 | -6.7383 | 62.7777 | -61.2534 | -0.19684 | -0.054931 | 0.009155 | -0.16479 | -0.95215 | -0.21973 | -0.09613 | 0.20599 | 55.4718 | 54.2953 | 122.9553 | 123.8525 | 0.009155 | 123.8113 | 65.0757 | -0.21973 | 123.8525 | 0.009155 | 65.0757 | 122.9553 | 123.8113 | -124.1043 | -124.1272
983.7188 | 124.1455 | -60.9695 | 62.8235 | -0.077591 | 0.0057699 | 0.0059366 | -0.001566 | 0.062812 | -0.00076053 | 0.069436 | -60.9924 | 62.6953 | -61.203 | -61.1343 | 61.9949 | 4.1382 | -5.8182 | -6.7474 | 62.7457 | -61.1755 | -0.23346 | -0.12817 | -0.022889 | -0.16479 | -0.82855 | -0.20599 | -0.077819 | 0.21057 | 55.1514 | 54.2221 | 122.9645 | 123.6649 | -0.022889 | 123.7152 | 65.1077 | -0.20599 | 123.6649 | -0.022889 | 65.1077 | 122.9645 | 123.7152 | -124.0265 | -123.999
984.7188 | 124.1455 | -60.9924 | 62.8143 | 0.04448 | 0.0047019 | 0.0076456 | 0.00035684 | 0.063666 | -0.0016149 | 0.068368 | -60.9558 | 62.6953 | -61.1755 | -61.1069 | 62.0178 | 4.1702 | -5.8411 | -6.8024 | 62.7411 | -61.1801 | -0.1831 | -0.11902 | 0.036621 | -0.11444 | -0.79651 | -0.18768 | -0.073242 | 0.21973 | 55.1514 | 54.1901 | 123.0103 | 123.6877 | 0.036621 | 123.7335 | 65.1627 | -0.18768 | 123.6877 | 0.036621 | 65.1627 | 123.0103 | 123.7335 | -123.9899 | -123.9944
985.7188 | 124.1592 | -60.9924 | 62.8418 | 3.1496 | 0.0057699 | 0.0097818 | 0.0012112 | 0.06153 | -0.00054693 | 0.068368 | -60.9055 | 62.7045 | -61.203 | -61.0886 | 62.0407 | 4.2068 | -5.9097 | -6.8344 | 62.7365 | -61.1893 | -0.21057 | -0.13733 | 0.086975 | -0.09613 | -0.80109 | -0.19684 | -0.10529 | 0.29755 | 55.0827 | 54.158 | 123.0331 | 123.6969 | 0.086975 | 123.7289 | 65.1993 | -0.19684 | 123.6969 | 0.086975 | 65.1993 | 123.0331 | 123.7289 | -124.0448 | -124.0311
986.7188 | 124.1409 | -61.0016 | 62.8555 | -0.15388 | 0.0059835 | 0.0085 | -0.00071136 | 0.062171 | 9.4068e-05 | 0.0673 | -60.965 | 62.7182 | -61.1801 | -61.0931 | 61.9766 | 4.1702 | -5.8868 | -6.9122 | 62.7548 | -61.2167 | -0.17853 | -0.13733 | 0.036621 | -0.091553 | -0.87891 | -0.21515 | -0.10071 | 0.21515 | 55.1147 | 54.0894 | 122.9782 | 123.7198 | 0.036621 | 123.7564 | 65.1718 | -0.21515 | 123.7198 | 0.036621 | 65.1718 | 122.9782 | 123.7564 | -124.0356 | -124.0723
987.7344 | 124.0723 | -61.0382 | 62.8693 | -0.13863 | 0.0076925 | 0.0059366 | 0.008688 | 0.064093 | -0.0024695 | 0.070077 | -60.9695 | 62.8098 | -61.1801 | -61.1435 | 61.9263 | 4.0878 | -5.9052 | -7.0953 | 62.7869 | -61.2442 | -0.14191 | -0.05951 | 0.068665 | -0.10529 | -0.94299 | -0.20599 | -0.082398 | 0.21057 | 55.1331 | 53.9429 | 122.9645 | 123.848 | 0.068665 | 123.8251 | 65.126 | -0.20599 | 123.848 | 0.068665 | 65.126 | 122.9645 | 123.8251 | -124.0494 | -124.1135
988.7188 | 124.1364 | -61.0016 | 62.8189 | -0.077591 | 0.0025655 | 0.0059366 | -0.001566 | 0.064521 | -0.0016149 | 0.068582 | -61.0199 | 62.7182 | -61.2167 | -61.1435 | 61.9766 | 4.1748 | -6.0883 | -7.0816 | 62.7411 | -61.1801 | -0.21515 | -0.10071 | -0.01831 | -0.14191 | -0.84228 | -0.17853 | -0.07782 | 0.19684 | 54.9133 | 53.92 | 122.9782 | 123.7198 | -0.01831 | 123.7427 | 65.1764 | -0.17853 | 123.7198 | -0.01831 | 65.1764 | 122.9782 | 123.7427 | -124.0356 | -123.999
989.7188 | 124.1821 | -60.9558 | 62.8281 | -0.14626 | 0.0061971 | 0.009141 | -0.0022068 | 0.060889 | -0.0033239 | 0.06965 | -60.9787 | 62.6999 | -61.2122 | -61.1069 | 62.0041 | 4.2526 | -6.1386 | -7.0724 | 62.7136 | -61.203 | -0.25635 | -0.12817 | -0.022888 | -0.15106 | -0.82397 | -0.24719 | -0.11444 | 0.23346 | 54.8172 | 53.8834 | 122.9599 | 123.6557 | -0.022888 | 123.6694 | 65.2084 | -0.24719 | 123.6557 | -0.022888 | 65.2084 | 122.9599 | 123.6694 | -124.0402 | -124.0311
990.7188 | 124.1638 | -60.997 | 62.8235 | -0.054703 | 0.0036337 | 0.0059366 | -0.0013522 | 0.062171 | -0.0018285 | 0.067727 | -60.9833 | 62.6999 | -61.1664 | -61.1114 | 61.9812 | 4.2984 | -6.2347 | -7.164 | 62.7411 | -61.1893 | -0.16937 | -0.1236 | 0.013733 | -0.11444 | -0.84229 | -0.19226 | -0.082397 | 0.18311 | 54.7623 | 53.833 | 122.9782 | 123.6969 | 0.013733 | 123.7381 | 65.2954 | -0.19226 | 123.6969 | 0.013733 | 65.2954 | 122.9782 | 123.7381 | -123.9899 | -124.0128
991.7188 | 124.1089 | -61.0062 | 62.8372 | -0.0012969 | 0.0036337 | 0.0059366 | -0.0011386 | 0.061103 | -0.0022559 | 0.070931 | -61.0474 | 62.7045 | -61.1984 | -61.1847 | 61.908 | 4.2343 | -6.2622 | -7.3654 | 62.7182 | -61.2076 | -0.19226 | -0.13275 | -0.041198 | -0.17853 | -0.92926 | -0.20142 | -0.11902 | 0.15106 | 54.744 | 53.6407 | 122.9141 | 123.7106 | -0.041198 | 123.7244 | 65.2405 | -0.20142 | 123.7106 | -0.041198 | 65.2405 | 122.9141 | 123.7244 | -124.0356 | -124.0448
992.7188 | 124.1043 | -60.9924 | 62.8418 | 0.067368 | 0.0047019 | 0.0038004 | -0.0013522 | 0.061316 | -0.00054693 | 0.069222 | -61.0474 | 62.6816 | -61.2213 | -61.1938 | 61.8896 | 4.2572 | -6.34 | -7.4478 | 62.7228 | -61.1984 | -0.22888 | -0.16022 | -0.054931 | -0.20142 | -0.95215 | -0.20599 | -0.11902 | 0.17395 | 54.6524 | 53.5446 | 122.8821 | 123.674 | -0.054931 | 123.7152 | 65.2496 | -0.20599 | 123.674 | -0.054931 | 65.2496 | 122.8821 | 123.7152 | -124.0631 | -124.0402
993.7188 | 124.0997 | -61.0199 | 62.8235 | 0.013962 | 0.0055563 | 0.0082864 | -0.00028416 | 0.062171 | -0.0022559 | 0.069436 | -61.1481 | 62.7045 | -61.2122 | -61.1847 | 61.9217 | 4.2892 | -6.3812 | -7.5211 | 62.7411 | -61.2488 | -0.19226 | -0.11902 | -0.12817 | -0.16479 | -0.90179 | -0.22888 | -0.082397 | 0.064087 | 54.6387 | 53.4988 | 122.9416 | 123.7244 | -0.12817 | 123.761 | 65.3091 | -0.22888 | 123.7244 | -0.12817 | 65.3091 | 122.9416 | 123.761 | -124.0356 | -124.0723
994.7188 | 124.1867 | -60.9695 | 62.8372 | -0.1844 | 0.0042745 | 0.0038004 | -0.0022068 | 0.064948 | -0.0014013 | 0.067941 | -60.9604 | 62.7228 | -61.1801 | -61.0291 | 61.9583 | 4.2847 | -6.4087 | -7.4203 | 62.6999 | -61.1801 | -0.21057 | -0.11444 | 0.009155 | -0.05951 | -0.87891 | -0.21057 | -0.13733 | 0.21973 | 54.5609 | 53.5492 | 122.9279 | 123.6923 | 0.009155 | 123.6694 | 65.2542 | -0.21057 | 123.6923 | 0.009155 | 65.2542 | 122.9279 | 123.6694 | -124.0173 | -124.0173
995.7188 | 124.1409 | -60.9879 | 62.851 | -0.19966 | 0.0047019 | 0.0065774 | 0.0014248 | 0.062171 | -0.0020421 | 0.069222 | -60.9558 | 62.7136 | -61.1847 | -61.1114 | 61.9812 | 4.4037 | -6.4774 | -7.5485 | 62.7365 | -61.1755 | -0.19684 | -0.13733 | 0.032043 | -0.1236 | -0.86975 | -0.18768 | -0.11444 | 0.22888 | 54.5105 | 53.4393 | 122.9691 | 123.7015 | 0.032043 | 123.7244 | 65.3915 | -0.18768 | 123.7015 | 0.032043 | 65.3915 | 122.9691 | 123.7244 | -124.0356 | -124.0265
996.7188 | 124.118 | -61.0062 | 62.8326 | 1.4635 | 0.0053427 | 0.0093546 | -0.00071136 | 0.060675 | -0.00076053 | 0.071145 | -61.0062 | 62.709 | -61.2122 | -61.1984 | 61.8896 | 4.3442 | -6.5826 | -7.7042 | 62.7136 | -61.203 | -0.20599 | -0.1236 | 0 | -0.19226 | -0.94299 | -0.19684 | -0.11902 | 0.20599 | 54.4235 | 53.302 | 122.8958 | 123.7152 | 0 | 123.7198 | 65.3503 | -0.19684 | 123.7152 | 0 | 65.3503 | 122.8958 | 123.7198 | -124.0448 | -124.0356
997.7188 | 124.0997 | -60.997 | 62.8143 | -0.0012969 | 0.0044881 | 0.0072184 | 0.00014304 | 0.062384 | -0.0020421 | 0.06495 | -61.0336 | 62.7136 | -61.1893 | -61.0565 | 61.8851 | 4.2664 | -6.6055 | -7.8094 | 62.709 | -61.2076 | -0.19226 | -0.10071 | -0.036621 | -0.05951 | -0.92926 | -0.21057 | -0.10529 | 0.15564 | 54.3915 | 53.1876 | 122.8821 | 123.7106 | -0.036621 | 123.7061 | 65.2634 | -0.21057 | 123.7106 | -0.036621 | 65.2634 | 122.8821 | 123.7061 | -124.0036 | -124.0219
998.7188 | 124.0402 | -60.9787 | 62.8601 | 0.029221 | 0.0047019 | 0.0082864 | -0.00028416 | 0.062812 | -0.0024695 | 0.066445 | -61.0428 | 62.6999 | -61.2167 | -61.203 | 61.8759 | 4.39 | -6.7062 | -7.8461 | 62.709 | -61.1893 | -0.23804 | -0.16022 | -0.064087 | -0.2243 | -0.98419 | -0.21057 | -0.15106 | 0.17395 | 54.2725 | 53.1326 | 122.8546 | 123.6786 | -0.064087 | 123.6877 | 65.3687 | -0.21057 | 123.6786 | -0.064087 | 65.3687 | 122.8546 | 123.6877 | -124.0768 | -124.0494
999.7188 | 124.1272 | -60.9787 | 62.7914 | 0.13603 | 0.0068381 | 0.0072184 | -0.00071136 | 0.063452 | -0.0024695 | 0.06965 | -60.9879 | 62.6953 | -61.2167 | -61.1435 | 61.8988 | 4.422 | -6.8298 | -7.8964 | 62.6862 | -61.2076 | -0.23804 | -0.096131 | -0.009155 | -0.16479 | -0.89264 | -0.22888 | -0.10529 | 0.22888 | 54.1489 | 53.0823 | 122.8775 | 123.674 | -0.009155 | 123.6649 | 65.4007 | -0.22888 | 123.674 | -0.009155 | 65.4007 | 122.8775 | 123.6649 | -124.0082 | -123.999
1000.7188 | 124.0997 | -61.0107 | 62.8006 | 0.18181 | 0.0036337 | 0.011064 | -0.0017796 | 0.063239 | 9.4068e-05 | 0.068795 | -61.0107 | 62.7274 | -61.2122 | -61.1801 | 61.8713 | 4.4037 | -6.871 | -7.9971 | 62.7182 | -61.2305 | -0.20142 | -0.073242 | 0 | -0.16937 | -0.92926 | -0.21973 | -0.082397 | 0.20142 | 54.1397 | 53.0136 | 122.8821 | 123.7381 | 0 | 123.7289 | 65.4144 | -0.21973 | 123.7381 | 0 | 65.4144 | 122.8821 | 123.7289 | -124.0128 | -124.0311
1001.7188 | 124.1638 | -60.9924 | 62.8098 | 0.0063326 | 0.0051291 | 0.0080728 | -0.0037022 | 0.063025 | -0.0016149 | 0.069009 | -61.0382 | 62.709 | -61.1938 | -61.171 | 61.8896 | 4.422 | -6.8985 | -8.0338 | 62.7274 | -61.1984 | -0.20142 | -0.10071 | -0.045776 | -0.17853 | -0.9201 | -0.20599 | -0.082397 | 0.15564 | 54.0939 | 52.9587 | 122.8821 | 123.7015 | -0.045776 | 123.7198 | 65.4144 | -0.20599 | 123.7015 | -0.045776 | 65.4144 | 122.8821 | 123.7198 | -124.0036 | -124.0082
1002.7188 | 124.1089 | -60.9924 | 62.8235 | 0.12077 | 0.0064107 | 0.0031596 | -0.0019932 | 0.062171 | -0.0035375 | 0.068795 | -61.0382 | 62.7228 | -61.2259 | -61.203 | 61.8851 | 4.4632 | -6.9489 | -8.1024 | 62.7136 | -61.2213 | -0.23346 | -0.10071 | -0.045776 | -0.21057 | -0.93841 | -0.22888 | -0.10986 | 0.18768 | 54.0436 | 52.89 | 122.8775 | 123.7152 | -0.045776 | 123.7061 | 65.4556 | -0.22888 | 123.7152 | -0.045776 | 65.4556 | 122.8775 | 123.7061 | -124.0494 | -124.0448
1003.7188 | 124.1364 | -61.0062 | 62.8235 | -0.047073 | 0.0044881 | 0.0063638 | -0.001566 | 0.061957 | -0.0011877 | 0.070504 | -61.0291 | 62.6862 | -61.1938 | -61.1298 | 61.908 | 4.5136 | -7.0175 | -8.1253 | 62.7411 | -61.1755 | -0.18768 | -0.13733 | -0.022888 | -0.1236 | -0.91553 | -0.16937 | -0.082397 | 0.1648 | 53.9886 | 52.8809 | 122.9141 | 123.6923 | -0.022888 | 123.7473 | 65.5197 | -0.16937 | 123.6923 | -0.022888 | 65.5197 | 122.9141 | 123.7473 | -124.0173 | -123.999
1004.7188 | 124.1089 | -60.9833 | 62.8098 | 0.074997 | 0.0044881 | 0.010636 | -0.0013522 | 0.061103 | -0.0026831 | 0.06965 | -61.0016 | 62.6999 | -61.2122 | -61.1755 | 61.8713 | 4.4861 | -7.0953 | -8.2535 | 62.709 | -61.2213 | -0.22888 | -0.10986 | -0.018311 | -0.19226 | -0.93841 | -0.23804 | -0.10071 | 0.21057 | 53.8879 | 52.7298 | 122.8546 | 123.6832 | -0.018311 | 123.6923 | 65.4694 | -0.23804 | 123.6832 | -0.018311 | 65.4694 | 122.8546 | 123.6923 | -124.0219 | -124.0311
1005.7188 | 124.1776 | -60.9924 | 62.8006 | -0.21492 | 0.0061971 | 0.006791 | 0.003561 | 0.065375 | -0.00076053 | 0.070718 | -60.9879 | 62.6907 | -61.1938 | -61.1389 | 61.9034 | 4.5319 | -7.2327 | -8.2672 | 62.6907 | -61.203 | -0.20142 | -0.10986 | 0.004578 | -0.14648 | -0.89722 | -0.21057 | -0.10986 | 0.20599 | 53.7598 | 52.7252 | 122.8958 | 123.6832 | 0.004578 | 123.6832 | 65.5243 | -0.21057 | 123.6832 | 0.004578 | 65.5243 | 122.8958 | 123.6832 | -123.9944 | -124.0036
1006.7188 | 124.1364 | -60.9787 | 62.7914 | 0.14366 | 0.0059835 | 0.0097818 | 0.00014304 | 0.064307 | -0.0020421 | 0.068154 | -60.9055 | 62.6862 | -61.2213 | -61.084 | 61.8896 | 4.5227 | -7.2647 | -8.3405 | 62.6907 | -61.2076 | -0.24261 | -0.10529 | 0.073242 | -0.10529 | -0.90179 | -0.22888 | -0.10071 | 0.31586 | 53.714 | 52.6382 | 122.8683 | 123.6649 | 0.073242 | 123.6694 | 65.5014 | -0.22888 | 123.6649 | 0.073242 | 65.5014 | 122.8683 | 123.6694 | -124.0128 | -123.999
1007.7188 | 124.1684 | -61.0107 | 62.7869 | 0.17418 | 0.0049155 | 0.0061502 | -7.0562e-05 | 0.064948 | -0.00097413 | 0.069436 | -60.965 | 62.6999 | -61.2122 | -61.1343 | 61.8805 | 4.5914 | -7.3425 | -8.3908 | 62.7045 | -61.2076 | -0.20142 | -0.086975 | 0.045776 | -0.1236 | -0.90637 | -0.19684 | -0.082397 | 0.24719 | 53.6682 | 52.6199 | 122.8912 | 123.7106 | 0.045776 | 123.7152 | 65.6021 | -0.19684 | 123.7106 | 0.045776 | 65.6021 | 122.8912 | 123.7152 | -123.999 | -123.9944
1008.7188 | 124.0814 | -61.0016 | 62.796 | 0.17418 | 0.0068381 | 0.0044412 | -0.00092496 | 0.064093 | -0.0033239 | 0.069436 | -61.0016 | 62.677 | -61.1893 | -61.1847 | 61.8484 | 4.541 | -7.3242 | -8.4915 | 62.7274 | -61.2259 | -0.18768 | -0.11902 | 0 | -0.1831 | -0.94757 | -0.2243 | -0.068665 | 0.18768 | 53.6774 | 52.5101 | 122.85 | 123.6786 | 0 | 123.7289 | 65.5426 | -0.2243 | 123.6786 | 0 | 65.5426 | 122.85 | 123.7289 | -123.9853 | -124.0219
1009.7188 | 124.1547 | -60.9833 | 62.7914 | 0.090256 | 0.0068381 | 0.007432 | 0.001852 | 0.061957 | -0.0018285 | 0.070931 | -60.997 | 62.7136 | -61.2167 | -61.1618 | 61.853 | 4.5639 | -7.4387 | -8.5419 | 62.6907 | -61.2167 | -0.23346 | -0.07782 | -0.013733 | -0.17853 | -0.93842 | -0.23346 | -0.10071 | 0.21973 | 53.5446 | 52.4414 | 122.8363 | 123.6969 | -0.013733 | 123.674 | 65.5472 | -0.23346 | 123.6969 | -0.013733 | 65.5472 | 122.8363 | 123.674 | -124.0082 | -124.0082
1010.7188 | 124.0952 | -60.9833 | 62.8326 | 0.14366 | 0.0040609 | 0.0076456 | -0.0017796 | 0.063452 | 0.00030767 | 0.068795 | -61.0245 | 62.7045 | -61.2122 | -61.171 | 61.8484 | 4.5639 | -7.4295 | -8.638 | 62.7411 | -61.235 | -0.22888 | -0.12817 | -0.041199 | -0.18768 | -0.98419 | -0.25177 | -0.091553 | 0.18768 | 53.5538 | 52.3453 | 122.8317 | 123.6877 | -0.041199 | 123.7244 | 65.5472 | -0.25177 | 123.6877 | -0.041199 | 65.5472 | 122.8317 | 123.7244 | -124.0448 | -124.0677
1011.75 | 124.086 | -61.0107 | 62.8693 | -0.077591 | 0.0074789 | 0.010423 | 0.0067654 | 0.063239 | -0.0024695 | 0.067727 | -60.9604 | 62.8372 | -61.2076 | -61.1298 | 61.6653 | 4.3671 | -7.2052 | -8.6746 | 62.7731 | -61.2625 | -0.19684 | -0.032044 | 0.050354 | -0.11902 | -1.2039 | -0.25177 | -0.096131 | 0.24719 | 53.8055 | 52.3361 | 122.6761 | 123.848 | 0.050354 | 123.7839 | 65.3778 | -0.25177 | 123.848 | 0.050354 | 65.3778 | 122.6761 | 123.7839 | -124.0768 | -124.1318
1012.7188 | 124.1547 | -60.9787 | 62.7869 | 0.14366 | 0.0057699 | 0.007432 | 0.0029202 | 0.067298 | -0.0024695 | 0.068582 | -60.965 | 62.7411 | -61.2213 | -61.1298 | 61.8713 | 4.5868 | -7.6218 | -8.7845 | 62.7182 | -61.2076 | -0.24261 | -0.045776 | 0.013733 | -0.15106 | -0.91553 | -0.22888 | -0.068664 | 0.25635 | 53.3569 | 52.1942 | 122.85 | 123.7198 | 0.013733 | 123.6969 | 65.5655 | -0.22888 | 123.7198 | 0.013733 | 65.5655 | 122.85 | 123.6969 | -124.0082 | -123.9944
1013.7344 | 124.1821 | -60.965 | 62.8098 | -0.069961 | 0.0053427 | 0.0078592 | -0.0024204 | 0.061743 | -0.0022559 | 0.069009 | -60.9924 | 62.7182 | -61.2122 | -61.116 | 61.9125 | 4.6646 | -7.608 | -8.7479 | 62.7365 | -61.1755 | -0.24719 | -0.091552 | -0.027466 | -0.15106 | -0.89722 | -0.21057 | -0.073242 | 0.21973 | 53.3569 | 52.2171 | 122.8775 | 123.6832 | -0.027466 | 123.7015 | 65.6296 | -0.21057 | 123.6832 | -0.027466 | 65.6296 | 122.8775 | 123.7015 | -124.0219 | -123.9853
1014.7188 | 124.118 | -60.9833 | 62.8281 | 0.12077 | 0.0042745 | 0.010636 | -0.00071136 | 0.062812 | -0.0020421 | 0.069222 | -61.0199 | 62.709 | -61.1938 | -61.0474 | 61.8393 | 4.4952 | -7.6447 | -8.9813 | 62.7365 | -61.2076 | -0.21057 | -0.11902 | -0.036621 | -0.064087 | -0.98877 | -0.22431 | -0.091553 | 0.17395 | 53.3386 | 52.002 | 122.8226 | 123.6923 | -0.036621 | 123.7198 | 65.4785 | -0.22431 | 123.6923 | -0.036621 | 65.4785 | 122.8226 | 123.7198 | -124.0219 | -124.0356
1015.7188 | 124.1409 | -60.9879 | 62.8143 | -0.3141 | 0.0055563 | 0.01085 | 0.0014248 | 0.064521 | -0.00097413 | 0.070931 | -60.9879 | 62.7365 | -61.2122 | -61.1298 | 61.8439 | 4.6417 | -7.8323 | -8.9722 | 62.6953 | -61.203 | -0.2243 | -0.07782 | 0 | -0.14191 | -0.97046 | -0.21515 | -0.11902 | 0.2243 | 53.1555 | 52.0157 | 122.8317 | 123.7244 | 0 | 123.6832 | 65.6296 | -0.21515 | 123.7244 | 0 | 65.6296 | 122.8317 | 123.6832 | -124.0265 | -124.0173
1016.75 | 124.1821 | -60.9695 | 62.8143 | -0.22255 | 0.0021383 | 0.006791 | -0.0030612 | 0.063452 | 0.00094847 | 0.066873 | -60.9283 | 62.7182 | -61.1755 | -61.0703 | 61.6241 | 4.8386 | -7.457 | -9.2422 | 62.7823 | -61.1893 | -0.20599 | -0.09613 | 0.041198 | -0.10071 | -1.1902 | -0.21973 | -0.032043 | 0.24719 | 53.5126 | 51.7273 | 122.5937 | 123.6877 | 0.041198 | 123.7518 | 65.8081 | -0.21973 | 123.6877 | 0.041198 | 65.8081 | 122.5937 | 123.7518 | -123.9899 | -124.0036
1017.7188 | 124.2188 | -60.9879 | 62.8006 | 0.19707 | 0.0049155 | 0.0097818 | 0.0039882 | 0.063452 | -0.0026831 | 0.069863 | -60.9375 | 62.7228 | -61.203 | -61.1252 | 61.8347 | 4.7241 | -7.9514 | -9.1873 | 62.6862 | -61.2396 | -0.21515 | -0.07782 | 0.050354 | -0.13733 | -0.96588 | -0.25177 | -0.11444 | 0.2655 | 53.0365 | 51.8005 | 122.8226 | 123.7106 | 0.050354 | 123.674 | 65.712 | -0.25177 | 123.7106 | 0.050354 | 65.712 | 122.8226 | 123.674 | -124.0036 | -124.0402
1018.7188 | 124.118 | -60.997 | 62.8281 | 0.22758 | 0.0064107 | 0.0080728 | -0.00028416 | 0.064734 | -0.0011877 | 0.071145 | -60.9833 | 62.7182 | -61.2213 | -61.1755 | 61.8347 | 4.6967 | -7.9697 | -9.1736 | 62.7182 | -61.203 | -0.2243 | -0.10986 | 0.013733 | -0.17853 | -0.99335 | -0.20599 | -0.10986 | 0.23804 | 53.0273 | 51.8234 | 122.8317 | 123.7152 | 0.013733 | 123.7152 | 65.6937 | -0.20599 | 123.7152 | 0.013733 | 65.6937 | 122.8317 | 123.7152 | -124.0494 | -124.0311
1019.7188 | 124.1043 | -60.9924 | 62.8052 | 0.074997 | 0.0059835 | 0.0095682 | 0.00057044 | 0.062812 | -0.0022559 | 0.069222 | -61.0199 | 62.7365 | -61.1984 | -61.1801 | 61.8027 | 4.7287 | -7.9788 | -9.256 | 62.7319 | -61.2259 | -0.20599 | -0.068665 | -0.027465 | -0.18768 | -1.0025 | -0.23346 | -0.073242 | 0.17853 | 53.0136 | 51.7365 | 122.7951 | 123.7289 | -0.027465 | 123.7244 | 65.7211 | -0.23346 | 123.7289 | -0.027465 | 65.7211 | 122.7951 | 123.7244 | -124.0036 | -124.0311
1020.7188 | 124.1318 | -60.9787 | 62.8052 | 0.24284 | 0.0070517 | 0.011277 | 0.004202 | 0.063025 | 0.00073487 | 0.069436 | -61.0062 | 62.7869 | -61.2213 | -61.1526 | 61.7752 | 4.6921 | -8.075 | -9.3704 | 62.7136 | -61.2259 | -0.24261 | -0.018311 | -0.027466 | -0.17395 | -1.03 | -0.24719 | -0.091553 | 0.21515 | 52.9037 | 51.6083 | 122.7539 | 123.7656 | -0.027466 | 123.6923 | 65.6708 | -0.24719 | 123.7656 | -0.027466 | 65.6708 | 122.7539 | 123.6923 | -124.0265 | -124.0311
1021.7188 | 124.1638 | -60.9833 | 62.8052 | 0.32677 | 0.0064107 | 0.0070048 | 0.0044156 | 0.063666 | -0.0022559 | 0.070077 | -60.9467 | 62.7411 | -61.2122 | -61.1252 | 61.8347 | 4.7516 | -8.1848 | -9.407 | 62.7274 | -61.2259 | -0.22888 | -0.064087 | 0.036621 | -0.14191 | -0.97046 | -0.24262 | -0.07782 | 0.2655 | 52.7985 | 51.5762 | 122.818 | 123.7244 | 0.036621 | 123.7106 | 65.7349 | -0.24262 | 123.7244 | 0.036621 | 65.7349 | 122.818 | 123.7106 | -124.0173 | -124.0311
1022.7188 | 124.1089 | -60.9833 | 62.8281 | 0.17418 | 0.0034201 | 0.0035868 | -0.00092496 | 0.064521 | -0.0048193 | 0.067727 | -61.0245 | 62.6999 | -61.203 | -61.171 | 61.7935 | 4.7424 | -8.1665 | -9.4711 | 62.7457 | -61.2167 | -0.21973 | -0.12817 | -0.041199 | -0.18768 | -1.0345 | -0.23346 | -0.082397 | 0.17853 | 52.8168 | 51.5121 | 122.7768 | 123.6832 | -0.041199 | 123.7289 | 65.7257 | -0.23346 | 123.6832 | -0.041199 | 65.7257 | 122.7768 | 123.7289 | -124.0311 | -124.0448
1023.7188 | 124.0997 | -60.997 | 62.8143 | 0.18181 | 0.0076925 | 0.013627 | 0.0050564 | 0.066443 | -0.0016149 | 0.069222 | -61.0062 | 62.8189 | -61.1847 | -61.1938 | 61.7523 | 4.7058 | -8.2397 | -9.5581 | 62.7548 | -61.2625 | -0.18768 | 0.004578 | -0.009156 | -0.19684 | -1.062 | -0.2655 | -0.059509 | 0.17853 | 52.7573 | 51.4389 | 122.7493 | 123.8159 | -0.009156 | 123.7518 | 65.7028 | -0.2655 | 123.8159 | -0.009156 | 65.7028 | 122.7493 | 123.7518 | -123.999 | -124.0768
1024.7188 | 124.0768 | -60.997 | 62.8326 | 0.16655 | 0.0079061 | 0.0070048 | 0.0022794 | 0.065375 | 0.00094847 | 0.06965 | -61.0153 | 62.8235 | -61.235 | -61.2259 | 61.7386 | 4.6967 | -8.2489 | -9.6725 | 62.7777 | -61.2808 | -0.23804 | -0.009156 | -0.018311 | -0.22888 | -1.0941 | -0.28381 | -0.054932 | 0.21973 | 52.7481 | 51.3245 | 122.7356 | 123.8205 | -0.018311 | 123.7747 | 65.6937 | -0.28381 | 123.8205 | -0.018311 | 65.6937 | 122.7356 | 123.7747 | -124.0677 | -124.1135
1025.7188 | 124.1226 | -60.9787 | 62.8189 | 0.052109 | 0.0053427 | 0.012132 | -0.0030612 | 0.064734 | 0.00030767 | 0.070931 | -61.0107 | 62.7045 | -61.1938 | -61.1801 | 61.7844 | 4.7653 | -8.3542 | -9.6588 | 62.7548 | -61.2076 | -0.21515 | -0.11444 | -0.032043 | -0.20142 | -1.0345 | -0.22888 | -0.064087 | 0.18311 | 52.6245 | 51.3199 | 122.7631 | 123.6832 | -0.032043 | 123.7335 | 65.744 | -0.22888 | 123.6832 | -0.032043 | 65.744 | 122.7631 | 123.7335 | -124.0128 | -124.0265
1026.7188 | 124.0814 | -60.9924 | 62.8235 | 0.17418 | 0.0083333 | 0.010209 | 0.0022794 | 0.062598 | -0.0011877 | 0.068368 | -61.0291 | 62.7731 | -61.2167 | -61.1984 | 61.7386 | 4.7241 | -8.4091 | -9.7961 | 62.7548 | -61.2717 | -0.2243 | -0.050354 | -0.036621 | -0.20599 | -1.0849 | -0.27923 | -0.068664 | 0.18768 | 52.5833 | 51.1963 | 122.731 | 123.7656 | -0.036621 | 123.7473 | 65.7166 | -0.27923 | 123.7656 | -0.036621 | 65.7166 | 122.731 | 123.7473 | -124.0402 | -124.0952
1027.7188 | 124.0585 | -61.0199 | 62.851 | 0.12077 | 0.0085471 | 0.0093546 | 0.0050564 | 0.068793 | 9.4068e-05 | 0.066873 | -61.0382 | 62.8189 | -61.2122 | -60.9329 | 61.821 | 4.6463 | -8.2901 | -9.8511 | 62.8098 | -61.2671 | -0.19226 | -0.032043 | -0.018311 | 0.086975 | -1.03 | -0.24719 | -0.041199 | 0.17395 | 52.7298 | 51.1688 | 122.8409 | 123.8388 | -0.018311 | 123.8297 | 65.6662 | -0.24719 | 123.8388 | -0.018311 | 65.6662 | 122.8409 | 123.8297 | -124.0631 | -124.118
1028.7188 | 124.1318 | -60.9512 | 62.8326 | 0.090256 | 0.0068381 | 0.0065774 | -0.0028476 | 0.067298 | -0.00076053 | 0.069436 | -61.0016 | 62.7045 | -61.2167 | -61.1801 | 61.7615 | 4.8111 | -8.5602 | -9.906 | 62.7777 | -61.2122 | -0.2655 | -0.12817 | -0.050354 | -0.22888 | -1.0712 | -0.26093 | -0.054932 | 0.21515 | 52.3911 | 51.0452 | 122.7127 | 123.6557 | -0.050354 | 123.7289 | 65.7623 | -0.26093 | 123.6557 | -0.050354 | 65.7623 | 122.7127 | 123.7289 | -124.0494 | -124.0448
1029.7188 | 124.0723 | -60.9879 | 62.8464 | 0.19707 | 0.0079061 | 0.0072184 | 0.0065518 | 0.066443 | -0.0020421 | 0.070718 | -61.0107 | 62.8143 | -61.203 | -61.2076 | 61.7249 | 4.7745 | -8.5922 | -10.0388 | 62.764 | -61.2671 | -0.21515 | -0.032044 | -0.022888 | -0.21973 | -1.1215 | -0.27924 | -0.082398 | 0.19226 | 52.3956 | 50.9491 | 122.7127 | 123.8022 | -0.022888 | 123.7518 | 65.7623 | -0.27924 | 123.8022 | -0.022888 | 65.7623 | 122.7127 | 123.7518 | -124.0494 | -124.1135
1030.7188 | 124.1226 | -60.9558 | 62.8281 | 0.24284 | 0.0068381 | 0.011064 | 0.00099764 | 0.06623 | -0.0033239 | 0.069863 | -60.9787 | 62.7548 | -61.2076 | -61.1618 | 61.7706 | 4.8386 | -8.725 | -10.0433 | 62.7411 | -61.2488 | -0.25177 | -0.073242 | -0.022888 | -0.20599 | -1.0574 | -0.29297 | -0.086975 | 0.22888 | 52.2308 | 50.9125 | 122.7264 | 123.7106 | -0.022888 | 123.6969 | 65.7944 | -0.29297 | 123.7106 | -0.022888 | 65.7944 | 122.7264 | 123.6969 | -124.0356 | -124.0768
1031.7344 | 124.1272 | -60.9695 | 62.8372 | -0.0089264 | 0.0017111 | 0.0029458 | -0.0034886 | 0.065589 | -0.0033239 | 0.069436 | -60.9924 | 62.7457 | -61.1893 | -61.1526 | 61.7889 | 4.8752 | -8.7021 | -10.025 | 62.7502 | -61.2076 | -0.21973 | -0.091552 | -0.022889 | -0.18311 | -1.0483 | -0.23804 | -0.086975 | 0.19684 | 52.2675 | 50.9445 | 122.7585 | 123.7152 | -0.022889 | 123.7198 | 65.8447 | -0.23804 | 123.7152 | -0.022889 | 65.8447 | 122.7585 | 123.7198 | -124.0265 | -124.0448
1032.7188 | 124.0356 | -61.0336 | 62.8418 | 0.090256 | 0.010897 | 0.011277 | 0.0067654 | 0.06388 | 0.00094847 | 0.067513 | -60.9833 | 62.8555 | -61.203 | -61.2213 | 61.6974 | 4.7836 | -8.67 | -10.2722 | 62.7914 | -61.2808 | -0.16937 | 0.013733 | 0.050354 | -0.18768 | -1.1444 | -0.24719 | -0.050354 | 0.21973 | 52.3636 | 50.7614 | 122.731 | 123.8892 | 0.050354 | 123.8251 | 65.8173 | -0.24719 | 123.8892 | 0.050354 | 65.8173 | 122.731 | 123.8251 | -124.0448 | -124.1226
1033.7188 | 124.0265 | -61.0062 | 62.8464 | -0.0012969 | 0.0079061 | 0.014268 | 0.0061246 | 0.065589 | -0.0033239 | 0.069863 | -60.9833 | 62.8372 | -61.203 | -61.2167 | 61.7065 | 4.7974 | -8.7479 | -10.2997 | 62.7869 | -61.2442 | -0.19684 | -0.009156 | 0.022889 | -0.21057 | -1.1398 | -0.23804 | -0.05951 | 0.21973 | 52.2583 | 50.7065 | 122.7127 | 123.8434 | 0.022889 | 123.793 | 65.8035 | -0.23804 | 123.8434 | 0.022889 | 65.8035 | 122.7127 | 123.793 | -124.0494 | -124.0906
1034.7188 | 124.1592 | -60.965 | 62.8189 | 0.19707 | 0.0072653 | 0.007432 | -0.00071136 | 0.067939 | -0.0039649 | 0.070504 | -60.9375 | 62.7457 | -61.2259 | -61.1435 | 61.7661 | 4.9026 | -9.0179 | -10.3271 | 62.7365 | -61.1984 | -0.26093 | -0.073242 | 0.027466 | -0.17853 | -1.0529 | -0.23346 | -0.082398 | 0.28839 | 51.947 | 50.6378 | 122.731 | 123.7106 | 0.027466 | 123.7015 | 65.8676 | -0.23346 | 123.7106 | 0.027466 | 65.8676 | 122.731 | 123.7015 | -124.0448 | -124.0173
1035.7188 | 124.0356 | -61.0062 | 62.8601 | -0.024185 | 0.0081197 | 0.011704 | 0.00527 | 0.065802 | -0.0014013 | 0.068582 | -60.9695 | 62.8555 | -61.1893 | -61.2122 | 61.7065 | 4.8203 | -8.8943 | -10.4919 | 62.796 | -61.2625 | -0.1831 | -0.004577 | 0.036622 | -0.20599 | -1.1536 | -0.25635 | -0.064086 | 0.21973 | 52.1118 | 50.5142 | 122.7127 | 123.8617 | 0.036622 | 123.8022 | 65.8264 | -0.25635 | 123.8617 | 0.036622 | 65.8264 | 122.7127 | 123.8022 | -124.0494 | -124.1226
1036.7188 | 123.9944 | -61.0291 | 62.8326 | 0.074997 | 0.0098287 | 0.01555 | 0.0046292 | 0.066657 | -0.00076053 | 0.069436 | -61.0245 | 62.8464 | -61.2167 | -61.2579 | 61.6745 | 4.8248 | -8.9539 | -10.6201 | 62.8235 | -61.2671 | -0.18768 | 0.013733 | 0.004578 | -0.22888 | -1.1581 | -0.23804 | -0.009156 | 0.19226 | 52.0752 | 50.4089 | 122.7036 | 123.8754 | 0.004578 | 123.8525 | 65.8539 | -0.23804 | 123.8754 | 0.004578 | 65.8539 | 122.7036 | 123.8525 | -124.0494 | -124.0997
1037.7188 | 124.118 | -60.9924 | 62.8326 | 0.25047 | 0.0074789 | 0.012132 | -0.00028416 | 0.067725 | -0.0011877 | 0.070718 | -60.9695 | 62.7731 | -61.2213 | -61.1481 | 61.7569 | 4.953 | -9.2194 | -10.5789 | 62.7502 | -61.203 | -0.22888 | -0.05951 | 0.022889 | -0.15564 | -1.0757 | -0.21057 | -0.082398 | 0.25177 | 51.7731 | 50.4135 | 122.7493 | 123.7656 | 0.022889 | 123.7427 | 65.9454 | -0.21057 | 123.7656 | 0.022889 | 65.9454 | 122.7493 | 123.7427 | -124.054 | -124.0356
1038.7188 | 124.0219 | -61.0199 | 62.851 | -0.0089264 | 0.0072653 | 0.009141 | 0.002493 | 0.066443 | -0.00054693 | 0.070291 | -61.0428 | 62.851 | -61.2167 | -61.2259 | 61.6699 | 4.8752 | -9.1187 | -10.7437 | 62.7869 | -61.2579 | -0.19684 | 0 | -0.022889 | -0.20599 | -1.181 | -0.23804 | -0.064087 | 0.17395 | 51.9012 | 50.2762 | 122.6898 | 123.8708 | -0.022889 | 123.8068 | 65.8951 | -0.23804 | 123.8708 | -0.022889 | 65.8951 | 122.6898 | 123.8068 | -124.0677 | -124.1089
1039.7188 | 124.0585 | -60.997 | 62.8235 | -0.039444 | 0.0072653 | 0.011491 | 0.0046292 | 0.068579 | -0.0026831 | 0.067086 | -60.9512 | 62.8372 | -61.1893 | -61.1801 | 61.7111 | 4.921 | -9.1736 | -10.762 | 62.8143 | -61.2259 | -0.19226 | 0.013733 | 0.045776 | -0.18311 | -1.1124 | -0.22888 | -0.009155 | 0.23804 | 51.8234 | 50.235 | 122.7081 | 123.8342 | 0.045776 | 123.8113 | 65.918 | -0.22888 | 123.8342 | 0.045776 | 65.918 | 122.7081 | 123.8113 | -124.0128 | -124.0494
1040.7188 | 124.0585 | -60.9879 | 62.8464 | -0.10811 | 0.0081197 | 0.009141 | 0.0048428 | 0.068152 | -0.0022559 | 0.069222 | -60.9283 | 62.8555 | -61.1755 | -61.1526 | 61.7477 | 4.9896 | -9.2468 | -10.7895 | 62.8098 | -61.2259 | -0.18768 | 0.009155 | 0.059509 | -0.16479 | -1.0986 | -0.23804 | -0.036622 | 0.24719 | 51.741 | 50.1984 | 122.7356 | 123.8434 | 0.059509 | 123.7976 | 65.9775 | -0.23804 | 123.8434 | 0.059509 | 65.9775 | 122.7356 | 123.7976 | -124.0219 | -124.0723
1041.7188 | 124.0723 | -60.997 | 62.8601 | -0.062332 | 0.0098287 | 0.011918 | 0.003561 | 0.068793 | -0.0016149 | 0.069863 | -61.116 | 62.796 | -61.2213 | -61.1526 | 61.7432 | 5.0034 | -9.3246 | -10.8765 | 62.8098 | -61.2213 | -0.2243 | -0.064086 | -0.11902 | -0.15564 | -1.1169 | -0.2243 | -0.050354 | 0.10529 | 51.6724 | 50.1205 | 122.7402 | 123.793 | -0.11902 | 123.8068 | 66.0004 | -0.2243 | 123.793 | -0.11902 | 66.0004 | 122.7402 | 123.8068 | -124.0814 | -124.0814
1042.7188 | 124.0356 | -61.0016 | 62.8738 | -0.054703 | 0.0081197 | 0.010423 | 0.003561 | 0.068793 | -0.0026831 | 0.069436 | -60.9329 | 62.8601 | -61.2076 | -61.171 | 61.6974 | 5.0079 | -9.4208 | -11.0001 | 62.8189 | -61.235 | -0.20599 | -0.013733 | 0.068665 | -0.16937 | -1.1765 | -0.23346 | -0.054931 | 0.27466 | 51.5808 | 50.0015 | 122.699 | 123.8617 | 0.068665 | 123.8205 | 66.0095 | -0.23346 | 123.8617 | 0.068665 | 66.0095 | 122.699 | 123.8205 | -124.0814 | -124.1089
1043.7188 | 124.086 | -60.9879 | 62.8647 | -0.08522 | 0.0072653 | 0.0078592 | 0.0027066 | 0.068793 | -0.0022559 | 0.069436 | -60.9375 | 62.883 | -61.1984 | -61.1618 | 61.7157 | 5.04 | -9.4711 | -11.0275 | 62.8326 | -61.2305 | -0.21057 | 0.018311 | 0.050354 | -0.17395 | -1.149 | -0.24262 | -0.032043 | 0.26093 | 51.5167 | 49.9603 | 122.7036 | 123.8708 | 0.050354 | 123.8205 | 66.0278 | -0.24262 | 123.8708 | 0.050354 | 66.0278 | 122.7036 | 123.8205 | -124.0631 | -124.0952
1044.7344 | 124.0952 | -61.0016 | 62.8235 | 0.18944 | 0.0057699 | 0.0082864 | -0.0045566 | 0.06623 | -0.00076053 | 0.069222 | -60.9604 | 62.7274 | -61.2076 | -61.1984 | 61.7249 | 5.0446 | -9.6588 | -11.1191 | 62.7686 | -61.203 | -0.20599 | -0.09613 | 0.041199 | -0.19684 | -1.0986 | -0.20142 | -0.054931 | 0.24719 | 51.3428 | 49.8825 | 122.7264 | 123.7289 | 0.041199 | 123.7701 | 66.0461 | -0.20142 | 123.7289 | 0.041199 | 66.0461 | 122.7264 | 123.7701 | -124.0311 | -124.0265
1045.7188 | 124.0677 | -60.9787 | 62.8738 | -0.069961 | 0.0072653 | 0.0082864 | 0.0048428 | 0.06623 | -0.0031103 | 0.069863 | -60.9283 | 62.851 | -61.1801 | -61.1389 | 61.7203 | 5.0812 | -9.7733 | -11.174 | 62.7686 | -61.2579 | -0.20142 | -0.022888 | 0.050354 | -0.16022 | -1.1536 | -0.27924 | -0.10529 | 0.25177 | 51.2054 | 49.8047 | 122.699 | 123.8297 | 0.050354 | 123.7473 | 66.0599 | -0.27924 | 123.8297 | 0.050354 | 66.0599 | 122.699 | 123.7473 | -124.054 | -124.1318
1046.7188 | 124.0585 | -60.9787 | 62.8693 | -0.26833 | 0.0076925 | 0.0097818 | 0.002493 | 0.067084 | -0.0014013 | 0.067727 | -60.9741 | 62.8555 | -61.171 | -61.1755 | 61.6974 | 5.072 | -9.6451 | -11.2839 | 62.8555 | -61.2396 | -0.19226 | -0.013733 | 0.004578 | -0.19684 | -1.1719 | -0.26093 | -0.013733 | 0.19684 | 51.3336 | 49.6948 | 122.6761 | 123.8342 | 0.004578 | 123.8342 | 66.0507 | -0.26093 | 123.8342 | 0.004578 | 66.0507 | 122.6761 | 123.8342 | -124.0402 | -124.1089
1047.7188 | 124.0128 | -61.0062 | 62.8647 | -0.0012969 | 0.010683 | 0.011491 | 0.0022794 | 0.066443 | -0.0048193 | 0.070291 | -60.9467 | 62.8189 | -61.2122 | -61.203 | 61.6562 | 5.0537 | -9.7549 | -11.3937 | 62.8143 | -61.2488 | -0.20599 | -0.045776 | 0.05951 | -0.19684 | -1.2085 | -0.24261 | -0.050354 | 0.2655 | 51.2512 | 49.6124 | 122.6624 | 123.8251 | 0.05951 | 123.8205 | 66.0599 | -0.24261 | 123.8251 | 0.05951 | 66.0599 | 122.6624 | 123.8205 | -124.0768 | -124.1135
1048.7188 | 123.9716 | -60.9741 | 62.915 | -0.24544 | 0.0068381 | 0.007432 | -0.0028476 | 0.065802 | -0.0033239 | 0.070077 | -60.9924 | 62.8372 | -61.1984 | -61.1984 | 61.6562 | 5.0766 | -9.7092 | -11.4304 | 62.8647 | -61.2122 | -0.2243 | -0.07782 | -0.018311 | -0.2243 | -1.2589 | -0.23804 | -0.050354 | 0.20599 | 51.265 | 49.5438 | 122.6303 | 123.8113 | -0.018311 | 123.8388 | 66.0507 | -0.23804 | 123.8113 | -0.018311 | 66.0507 | 122.6303 | 123.8388 | -124.1135 | -124.1272
1049.7344 | 124.0311 | -61.0016 | 62.8418 | 0.16655 | 0.0081197 | 0.0089274 | 0.0014248 | 0.067298 | -0.0020421 | 0.069863 | -61.0016 | 62.8006 | -61.2396 | -61.2213 | 61.6196 | 5.0949 | -9.9472 | -11.586 | 62.8143 | -61.2305 | -0.23804 | -0.041199 | 0 | -0.21973 | -1.2222 | -0.22888 | -0.027466 | 0.23804 | 51.0544 | 49.4156 | 122.6212 | 123.8022 | 0 | 123.8159 | 66.0965 | -0.22888 | 123.8022 | 0 | 66.0965 | 122.6212 | 123.8159 | -124.0814 | -124.0723
1050.7188 | 124.0585 | -60.9604 | 62.8693 | -0.131 | 0.012392 | 0.0080728 | 0.0050564 | 0.066657 | -0.00097413 | 0.071359 | -60.9192 | 62.851 | -61.203 | -61.1664 | 61.6608 | 5.127 | -9.9838 | -11.5952 | 62.8326 | -61.2259 | -0.24262 | -0.018311 | 0.041199 | -0.20599 | -1.2085 | -0.2655 | -0.036621 | 0.28381 | 50.9766 | 49.3652 | 122.6212 | 123.8113 | 0.041199 | 123.793 | 66.0873 | -0.2655 | 123.8113 | 0.041199 | 66.0873 | 122.6212 | 123.793 | -124.0723 | -124.0952
1051.7188 | 124.0814 | -60.9879 | 62.8693 | -0.14626 | 0.0087607 | 0.0085 | 0.0016384 | 0.068366 | -0.00076053 | 0.070077 | -60.9238 | 62.8693 | -61.1893 | -61.1481 | 61.6928 | 5.1498 | -10.0388 | -11.6592 | 62.8372 | -61.2396 | -0.20142 | 0 | 0.064087 | -0.16022 | -1.1765 | -0.25177 | -0.032044 | 0.2655 | 50.9491 | 49.3286 | 122.6807 | 123.8571 | 0.064087 | 123.8251 | 66.1377 | -0.25177 | 123.8571 | 0.064087 | 66.1377 | 122.6807 | 123.8251 | -124.0585 | -124.1089
1052.7344 | 124.1364 | -60.965 | 62.8235 | 0.26573 | 0.0061971 | 0.011064 | -0.0032748 | 0.06687 | -0.0026831 | 0.070077 | -60.9238 | 62.7502 | -61.1938 | -61.1252 | 61.7203 | 5.1956 | -10.3317 | -11.7233 | 62.7594 | -61.1801 | -0.22888 | -0.073242 | 0.041199 | -0.16022 | -1.1032 | -0.21515 | -0.064087 | 0.27008 | 50.6332 | 49.2416 | 122.6852 | 123.7152 | 0.041199 | 123.7244 | 66.1606 | -0.21515 | 123.7152 | 0.041199 | 66.1606 | 122.6852 | 123.7244 | -124.0173 | -124.0036
1053.7188 | 123.9578 | -60.9787 | 62.8418 | -0.14626 | 0.0094015 | 0.011064 | 0.0044156 | 0.068366 | -0.0016149 | 0.070077 | -60.91 | 62.8418 | -61.1618 | -61.1481 | 61.6653 | 5.1819 | -10.2356 | -11.8378 | 62.8189 | -61.2534 | -0.1831 | 0 | 0.068665 | -0.16937 | -1.1765 | -0.27466 | -0.022888 | 0.25177 | 50.7431 | 49.1409 | 122.644 | 123.8205 | 0.068665 | 123.7976 | 66.1606 | -0.27466 | 123.8205 | 0.068665 | 66.1606 | 122.644 | 123.7976 | -124.0036 | -124.0952
1054.7344 | 124.0723 | -60.9467 | 62.8784 | -0.26833 | 0.0042745 | 0.0070048 | -0.0013522 | 0.063452 | -0.0031103 | 0.067727 | -60.9283 | 62.7823 | -61.1847 | -61.1343 | 61.7157 | 5.246 | -10.2814 | -11.8744 | 62.851 | -61.1893 | -0.23804 | -0.09613 | 0.01831 | -0.18768 | -1.1627 | -0.24262 | -0.027466 | 0.25635 | 50.6653 | 49.0723 | 122.6624 | 123.7289 | 0.01831 | 123.7976 | 66.1926 | -0.24262 | 123.7289 | 0.01831 | 66.1926 | 122.6624 | 123.7976 | -124.0631 | -124.0677
1055.7188 | 124.0311 | -60.9833 | 62.8967 | -0.20729 | 0.0049155 | 0.0070048 | 0.0012112 | 0.064734 | -0.0024695 | 0.070504 | -60.9375 | 62.8189 | -61.171 | -61.1664 | 61.6562 | 5.2048 | -10.2859 | -11.9751 | 62.8372 | -61.2122 | -0.18768 | -0.07782 | 0.045776 | -0.18311 | -1.2405 | -0.22888 | -0.05951 | 0.23346 | 50.6973 | 49.0082 | 122.6395 | 123.8022 | 0.045776 | 123.8205 | 66.188 | -0.22888 | 123.8022 | 0.045776 | 66.188 | 122.6395 | 123.8205 | -124.0677 | -124.1089
1056.7188 | 124.0631 | -60.997 | 62.915 | -0.2607 | 0.0064107 | 0.010209 | 0.001852 | 0.065589 | -0.00054693 | 0.069222 | -60.9604 | 62.851 | -61.1938 | -61.1984 | 61.6287 | 5.1773 | -10.3958 | -12.1033 | 62.8418 | -61.2213 | -0.19684 | -0.064087 | 0.036621 | -0.20142 | -1.2863 | -0.2243 | -0.073242 | 0.23346 | 50.6012 | 48.8937 | 122.6257 | 123.848 | 0.036621 | 123.8388 | 66.1743 | -0.2243 | 123.848 | 0.036621 | 66.1743 | 122.6257 | 123.8388 | -124.1089 | -124.1364
1057.7344 | 124.118 | -60.9695 | 62.8372 | -0.0089264 | 0.0051291 | 0.0063638 | -0.0064792 | 0.063239 | -0.0026831 | 0.069009 | -60.9787 | 62.7502 | -61.1847 | -61.171 | 61.6562 | 5.2551 | -10.6384 | -12.1811 | 62.7777 | -61.1664 | -0.21515 | -0.086975 | -0.009156 | -0.20142 | -1.181 | -0.19684 | -0.059509 | 0.20599 | 50.3311 | 48.7885 | 122.6257 | 123.7198 | -0.009156 | 123.7473 | 66.2247 | -0.19684 | 123.7198 | -0.009156 | 66.2247 | 122.6257 | 123.7473 | -124.0219 | -124.0036
1058.7188 | 124.0585 | -61.0016 | 62.883 | -0.062332 | 0.0094015 | 0.0082864 | 0.0063382 | 0.066016 | -0.0024695 | 0.067727 | -60.9055 | 62.8464 | -61.1801 | -61.1526 | 61.647 | 5.2322 | -10.6247 | -12.2589 | 62.8143 | -61.2488 | -0.17853 | -0.036621 | 0.09613 | -0.15106 | -1.236 | -0.24719 | -0.068665 | 0.27466 | 50.3769 | 48.7427 | 122.6486 | 123.848 | 0.09613 | 123.8159 | 66.2338 | -0.24719 | 123.848 | 0.09613 | 66.2338 | 122.6486 | 123.8159 | -124.0631 | -124.1318
1059.7188 | 124.0585 | -60.9695 | 62.8876 | -0.0012969 | 0.0076925 | 0.0097818 | 0.005911 | 0.066657 | -0.0028967 | 0.069222 | -60.91 | 62.883 | -61.1801 | -61.1435 | 61.6241 | 5.2277 | -10.7025 | -12.355 | 62.8693 | -61.2122 | -0.21057 | -0.004577 | 0.059509 | -0.17395 | -1.2634 | -0.24262 | -0.01831 | 0.27008 | 50.267 | 48.6145 | 122.5937 | 123.8525 | 0.059509 | 123.8388 | 66.1972 | -0.24262 | 123.8525 | 0.059509 | 66.1972 | 122.5937 | 123.8388 | -124.0677 | -124.0997
1060.7188 | 124.0219 | -60.9558 | 62.8967 | -0.131 | 0.0079061 | 0.0087138 | 0.00099764 | 0.065161 | -0.00097413 | 0.066445 | -60.965 | 62.8601 | -61.2122 | -61.171 | 61.6058 | 5.2094 | -10.6476 | -12.4649 | 62.8555 | -61.2076 | -0.25635 | -0.036622 | -0.009155 | -0.21515 | -1.2909 | -0.25177 | -0.041199 | 0.24719 | 50.3082 | 48.4909 | 122.5616 | 123.8159 | -0.009155 | 123.8113 | 66.1652 | -0.25177 | 123.8159 | -0.009155 | 66.1652 | 122.5616 | 123.8113 | -124.1089 | -124.1043
1061.7188 | 124.0265 | -60.9879 | 62.9013 | -1.4433 | 0.0083333 | 0.007432 | 0.00014304 | 0.065802 | -0.0028967 | 0.069436 | -61.1023 | 62.8601 | -61.1938 | -61.2167 | 61.5738 | 5.1956 | -10.7208 | -12.5153 | 62.8784 | -61.1938 | -0.20599 | -0.041199 | -0.11444 | -0.22888 | -1.3275 | -0.20599 | -0.022888 | 0.091553 | 50.267 | 48.4726 | 122.5616 | 123.848 | -0.11444 | 123.8663 | 66.1835 | -0.20599 | 123.848 | -0.11444 | 66.1835 | 122.5616 | 123.8663 | -124.0952 | -124.0952
1062.7344 | 124.0997 | -60.9604 | 62.8464 | 0.10551 | 0.0051291 | 0.010636 | -0.0045566 | 0.065375 | -0.0018285 | 0.070931 | -60.9695 | 62.7182 | -61.1984 | -61.171 | 61.6058 | 5.2277 | -11.0458 | -12.5565 | 62.8006 | -61.2167 | -0.23804 | -0.12817 | -0.009155 | -0.21057 | -1.2405 | -0.25635 | -0.045777 | 0.22888 | 49.9146 | 48.4039 | 122.5662 | 123.6786 | -0.009155 | 123.761 | 66.188 | -0.25635 | 123.6786 | -0.009155 | 66.188 | 122.5662 | 123.761 | -124.0448 | -124.0631
1063.7188 | 124.0677 | -60.9879 | 62.8967 | -0.19203 | 0.0094015 | 0.0063638 | 0.0031338 | 0.065802 | -0.0050329 | 0.067941 | -60.9375 | 62.8876 | -61.1847 | -61.171 | 61.6013 | 5.1956 | -10.881 | -12.6114 | 62.8464 | -61.2305 | -0.19684 | -0.009156 | 0.050354 | -0.18311 | -1.2955 | -0.24262 | -0.050354 | 0.24719 | 50.1068 | 48.3765 | 122.5891 | 123.8754 | 0.050354 | 123.8342 | 66.1835 | -0.24262 | 123.8754 | 0.050354 | 66.1835 | 122.5891 | 123.8342 | -124.0814 | -124.1272
1064.7188 | 124.0356 | -60.9833 | 62.8647 | 0.04448 | 0.0068381 | 0.0093546 | 0.0044156 | 0.065802 | -0.0014013 | 0.069436 | -60.9055 | 62.8464 | -61.1801 | -61.1938 | 61.5692 | 5.191 | -11.0367 | -12.7579 | 62.8601 | -61.2259 | -0.19684 | -0.01831 | 0.077819 | -0.21057 | -1.2955 | -0.24262 | -0.004578 | 0.27466 | 49.9466 | 48.2254 | 122.5525 | 123.8297 | 0.077819 | 123.8434 | 66.1743 | -0.24262 | 123.8297 | 0.077819 | 66.1743 | 122.5525 | 123.8434 | -124.0448 | -124.0906
1065.7188 | 124.0997 | -60.9924 | 62.9059 | -0.16151 | 0.0053427 | 0.013627 | 0.0027066 | 0.066016 | -0.0018285 | 0.069222 | -60.9055 | 62.8738 | -61.171 | -61.1298 | 61.6241 | 5.2505 | -11.0962 | -12.735 | 62.8235 | -61.2122 | -0.17853 | -0.032044 | 0.086975 | -0.13733 | -1.2817 | -0.21973 | -0.082398 | 0.2655 | 49.8962 | 48.2574 | 122.6166 | 123.8663 | 0.086975 | 123.8159 | 66.243 | -0.21973 | 123.8663 | 0.086975 | 66.243 | 122.6166 | 123.8159 | -124.0768 | -124.118
1066.7188 | 124.0494 | -60.965 | 62.8784 | 0.7235 | 0.0055563 | 0.0046548 | 0.0033474 | 0.067725 | -0.0020421 | 0.068368 | -60.7681 | 62.8464 | -61.1801 | -61.1252 | 61.6196 | 5.2002 | -11.1786 | -12.8311 | 62.8601 | -61.203 | -0.21515 | -0.032043 | 0.19684 | -0.16022 | -1.2589 | -0.23804 | -0.018311 | 0.41199 | 49.7864 | 48.1338 | 122.5845 | 123.8113 | 0.19684 | 123.8251 | 66.1652 | -0.23804 | 123.8113 | 0.19684 | 66.1652 | 122.5845 | 123.8251 | -124.0585 | -124.0814
1067.7188 | 124.2783 | -60.9238 | 62.9196 | -0.131 | 0.0066245 | 0.007432 | -0.0034886 | 0.06687 | -0.0011877 | 0.067513 | -60.8688 | 62.8235 | -61.1526 | -61.0382 | 61.6974 | 5.2643 | -11.3709 | -12.8082 | 62.8189 | -61.1618 | -0.22888 | -0.096131 | 0.054932 | -0.11444 | -1.2222 | -0.23804 | -0.10071 | 0.28381 | 49.5529 | 48.1155 | 122.6212 | 123.7473 | 0.054932 | 123.7427 | 66.188 | -0.23804 | 123.7473 | 0.054932 | 66.188 | 122.6212 | 123.7427 | -124.0723 | -124.0814
1068.7188 | 124.0494 | -60.9879 | 62.9242 | -0.16914 | 0.0072653 | 0.0072184 | 0.0029202 | 0.064521 | 9.4068e-05 | 0.068582 | -60.9329 | 62.8922 | -61.171 | -61.1664 | 61.5921 | 5.159 | -11.2656 | -13.0188 | 62.8418 | -61.2259 | -0.18311 | -0.032043 | 0.054932 | -0.17853 | -1.3321 | -0.23804 | -0.082397 | 0.23804 | 49.7223 | 47.9691 | 122.58 | 123.88 | 0.054932 | 123.8297 | 66.1469 | -0.23804 | 123.88 | 0.054932 | 66.1469 | 122.58 | 123.8297 | -124.0952 | -124.1501
1069.7344 | 124.0356 | -60.965 | 62.883 | 0.23521 | 0.0068381 | 0.013627 | 0.0065518 | 0.067298 | -0.0016149 | 0.069863 | -60.8871 | 62.8601 | -61.1664 | -61.1435 | 61.5784 | 5.1727 | -11.4532 | -13.0966 | 62.8418 | -61.2259 | -0.20142 | -0.022889 | 0.07782 | -0.17853 | -1.3046 | -0.26093 | -0.041199 | 0.27924 | 49.5117 | 47.8683 | 122.5433 | 123.8251 | 0.07782 | 123.8068 | 66.1377 | -0.26093 | 123.8251 | 0.07782 | 66.1377 | 122.5433 | 123.8068 | -124.0494 | -124.1089
1070.7188 | 124.0723 | -60.965 | 62.8738 | -0.11574 | 0.0079061 | 0.012773 | 0.0033474 | 0.067725 | -0.0020421 | 0.068154 | -60.8917 | 62.8738 | -61.1801 | -61.1618 | 61.5875 | 5.2002 | -11.5219 | -13.1561 | 62.851 | -61.2259 | -0.21515 | 0 | 0.073242 | -0.19684 | -1.2863 | -0.26093 | -0.022888 | 0.28839 | 49.4431 | 47.8088 | 122.5525 | 123.8388 | 0.073242 | 123.8159 | 66.1652 | -0.26093 | 123.8388 | 0.073242 | 66.1652 | 122.5525 | 123.8159 | -124.054 | -124.0997
1071.7188 | 124.1043 | -60.9604 | 62.8967 | -0.20729 | 0.0044881 | 0.010636 | 0.00078404 | 0.068366 | -0.0016149 | 0.070077 | -60.8963 | 62.8784 | -61.1938 | -61.1206 | 61.6013 | 5.1773 | -11.5494 | -13.2294 | 62.8693 | -61.2076 | -0.23346 | -0.018311 | 0.064087 | -0.16022 | -1.2955 | -0.24719 | -0.027466 | 0.29755 | 49.411 | 47.731 | 122.5616 | 123.8388 | 0.064087 | 123.8297 | 66.1377 | -0.24719 | 123.8388 | 0.064087 | 66.1377 | 122.5616 | 123.8297 | -124.0906 | -124.1043
1072.7344 | 124.1455 | -60.9283 | 62.8464 | 0.18181 | 0.0083333 | 0.013627 | -0.0019932 | 0.067511 | 9.4068e-05 | 0.070504 | -60.9146 | 62.8098 | -61.1664 | -61.116 | 61.5921 | 5.2048 | -11.8423 | -13.3072 | 62.7914 | -61.1847 | -0.23804 | -0.036622 | 0.013733 | -0.18768 | -1.2543 | -0.25635 | -0.054932 | 0.25177 | 49.086 | 47.6212 | 122.5204 | 123.7381 | 0.013733 | 123.7198 | 66.1331 | -0.25635 | 123.7381 | 0.013733 | 66.1331 | 122.5204 | 123.7198 | -124.0128 | -124.0311
1073.7188 | 124.0952 | -60.965 | 62.9059 | -0.19966 | 0.0072653 | 0.0093546 | 0.0016384 | 0.06388 | -0.0035375 | 0.067941 | -60.9192 | 62.8784 | -61.1847 | -61.1252 | 61.5784 | 5.1636 | -11.6959 | -13.3896 | 62.851 | -61.2213 | -0.21973 | -0.027466 | 0.045777 | -0.16022 | -1.3275 | -0.25635 | -0.054932 | 0.2655 | 49.2691 | 47.5754 | 122.5433 | 123.8434 | 0.045777 | 123.8159 | 66.1285 | -0.25635 | 123.8434 | 0.045777 | 66.1285 | 122.5433 | 123.8159 | -124.0906 | -124.1272
1074.7188 | 124.0768 | -60.9741 | 62.8647 | 0.17418 | 0.0081197 | 0.0078592 | -7.0562e-05 | 0.066657 | -0.0028967 | 0.068582 | -60.9695 | 62.8326 | -61.171 | -61.2076 | 61.5051 | 5.1086 | -11.8652 | -13.5773 | 62.8143 | -61.2259 | -0.19684 | -0.032043 | 0.004578 | -0.23346 | -1.3596 | -0.25177 | -0.050354 | 0.20142 | 49.1089 | 47.3969 | 122.4792 | 123.8068 | 0.004578 | 123.7885 | 66.0828 | -0.25177 | 123.8068 | 0.004578 | 66.0828 | 122.4792 | 123.7885 | -124.0356 | -124.0906
1075.7188 | 124.0311 | -60.9741 | 62.9196 | 0.03685 | 0.0061971 | 0.0044412 | -7.0562e-05 | 0.065589 | -0.0022559 | 0.068582 | -60.9238 | 62.8876 | -61.171 | -61.1664 | 61.5189 | 5.1132 | -11.792 | -13.5864 | 62.8784 | -61.203 | -0.19684 | -0.032044 | 0.050354 | -0.19226 | -1.4008 | -0.22888 | -0.041199 | 0.24719 | 49.1821 | 47.3877 | 122.493 | 123.8617 | 0.050354 | 123.8525 | 66.0873 | -0.22888 | 123.8617 | 0.050354 | 66.0873 | 122.493 | 123.8525 | -124.0906 | -124.1226
1076.7188 | 124.0723 | -60.9421 | 62.8967 | -0.12337 | 0.0070517 | 0.009141 | 0.0033474 | 0.065375 | -0.0014013 | 0.069436 | -60.8734 | 62.8922 | -61.1572 | -61.1114 | 61.5555 | 5.1773 | -11.9751 | -13.6047 | 62.8647 | -61.2122 | -0.21515 | -0.004578 | 0.068665 | -0.16937 | -1.3412 | -0.27008 | -0.032044 | 0.28381 | 48.967 | 47.3373 | 122.4976 | 123.8342 | 0.068665 | 123.8068 | 66.1194 | -0.27008 | 123.8342 | 0.068665 | 66.1194 | 122.4976 | 123.8068 | -124.054 | -124.1089
1077.7188 | 124.0448 | -60.9695 | 62.9242 | -0.12337 | 0.0074789 | 0.01555 | 0.003561 | 0.067511 | -0.00054693 | 0.070291 | -60.8826 | 62.8784 | -61.1801 | -61.1252 | 61.5417 | 5.1178 | -12.0483 | -13.7009 | 62.8693 | -61.2167 | -0.21057 | -0.045776 | 0.086975 | -0.15564 | -1.3824 | -0.24719 | -0.054931 | 0.29755 | 48.9212 | 47.2687 | 122.5113 | 123.848 | 0.086975 | 123.8388 | 66.0873 | -0.24719 | 123.848 | 0.086975 | 66.0873 | 122.5113 | 123.8388 | -124.1043 | -124.1409
1078.7188 | 123.9395 | -61.0291 | 62.8555 | 0.097885 | 0.0094015 | 0.0095682 | 0.0031338 | 0.067298 | -0.00097413 | 0.069436 | -60.9512 | 62.883 | -61.1847 | -61.235 | 61.4548 | 5.0262 | -12.1216 | -13.8519 | 62.8326 | -61.2396 | -0.15564 | 0.027466 | 0.07782 | -0.20599 | -1.4008 | -0.21057 | -0.022888 | 0.23346 | 48.9075 | 47.1771 | 122.4838 | 123.912 | 0.07782 | 123.8617 | 66.0553 | -0.21057 | 123.912 | 0.07782 | 66.0553 | 122.4838 | 123.8617 | -124.0402 | -124.0952
1079.7188 | 124.0356 | -61.0016 | 62.8876 | 0.18944 | 0.0085471 | 0.010636 | 0.0020656 | 0.067298 | 0.00030767 | 0.068368 | -60.9467 | 62.8784 | -61.1755 | -61.2259 | 61.4777 | 5.0446 | -12.2314 | -13.9206 | 62.8647 | -61.2167 | -0.17395 | -0.009155 | 0.054932 | -0.2243 | -1.4099 | -0.21515 | -0.022888 | 0.22888 | 48.7701 | 47.081 | 122.4792 | 123.88 | 0.054932 | 123.8663 | 66.0461 | -0.21515 | 123.88 | 0.054932 | 66.0461 | 122.4792 | 123.8663 | -124.0631 | -124.1043
1080.7188 | 124.0494 | -60.9833 | 62.9013 | -0.48958 | 0.0087607 | 0.0097818 | 0.0037746 | 0.068152 | -0.0011877 | 0.068795 | -60.8688 | 62.883 | -61.1481 | -61.1298 | 61.5372 | 5.0858 | -12.2955 | -13.9252 | 62.8464 | -61.203 | -0.1648 | -0.01831 | 0.11444 | -0.14649 | -1.3641 | -0.21973 | -0.054931 | 0.27924 | 48.6877 | 47.0581 | 122.5204 | 123.8663 | 0.11444 | 123.8297 | 66.069 | -0.21973 | 123.8663 | 0.11444 | 66.069 | 122.5204 | 123.8297 | -124.0494 | -124.1043
1081.7188 | 124.0494 | -60.9787 | 62.9059 | -0.21492 | 0.0094015 | 0.007432 | 0.00014304 | 0.065802 | -0.0018285 | 0.070504 | -60.9283 | 62.9013 | -61.1801 | -61.1664 | 61.4868 | 5.1041 | -12.2864 | -14.0167 | 62.9059 | -61.1984 | -0.20142 | -0.004578 | 0.050354 | -0.18768 | -1.4191 | -0.21973 | 0 | 0.25177 | 48.6923 | 46.962 | 122.4655 | 123.88 | 0.050354 | 123.8846 | 66.0828 | -0.21973 | 123.88 | 0.050354 | 66.0828 | 122.4655 | 123.8846 | -124.086 | -124.1043
1082.7188 | 124.0402 | -60.9833 | 62.9105 | -1.2983 | 0.0081197 | 0.012559 | 0.0039882 | 0.068579 | -0.0011877 | 0.070504 | -61.0245 | 62.8693 | -61.1847 | -61.2259 | 61.4182 | 5.0308 | -12.442 | -14.1678 | 62.8647 | -61.2259 | -0.20142 | -0.041198 | -0.041199 | -0.24262 | -1.4923 | -0.24262 | -0.045776 | 0.16022 | 48.5413 | 46.8155 | 122.4014 | 123.8525 | -0.041199 | 123.848 | 66.0141 | -0.24262 | 123.8525 | -0.041199 | 66.0141 | 122.4014 | 123.848 | -124.0952 | -124.1364
1083.7188 | 124.0814 | -60.9604 | 62.9196 | -0.16914 | 0.0072653 | 0.0072184 | 0.0039882 | 0.068152 | -0.0037511 | 0.070718 | -60.8917 | 62.883 | -61.1526 | -61.1343 | 61.5143 | 5.0995 | -12.4878 | -14.1174 | 62.8647 | -61.203 | -0.19226 | -0.036621 | 0.068664 | -0.17395 | -1.4053 | -0.24262 | -0.054932 | 0.26092 | 48.4726 | 46.843 | 122.4747 | 123.8434 | 0.068664 | 123.8251 | 66.0599 | -0.24262 | 123.8434 | 0.068664 | 66.0599 | 122.4747 | 123.8251 | -124.0723 | -124.1226
1084.7188 | 124.0906 | -60.9604 | 62.8647 | 0.13603 | 0.0072653 | 0.0046548 | 0.00014304 | 0.068152 | -0.0020421 | 0.070718 | -60.9375 | 62.8693 | -61.1847 | -61.1847 | 61.4456 | 5.0034 | -12.6572 | -14.3097 | 62.8235 | -61.203 | -0.2243 | 0.004578 | 0.022888 | -0.2243 | -1.4191 | -0.24262 | -0.041199 | 0.24719 | 48.3032 | 46.6507 | 122.406 | 123.8297 | 0.022888 | 123.7839 | 65.9637 | -0.24262 | 123.8297 | 0.022888 | 65.9637 | 122.406 | 123.7839 | -124.0494 | -124.0677
1085.7188 | 124.0768 | -60.9604 | 62.9059 | -0.10811 | 0.0089743 | 0.0080728 | 0.00078404 | 0.06687 | -0.0018285 | 0.06965 | -60.8643 | 62.8738 | -61.1526 | -61.1069 | 61.5005 | 5.072 | -12.7121 | -14.3188 | 62.8693 | -61.1938 | -0.19226 | -0.032044 | 0.09613 | -0.14648 | -1.4053 | -0.23346 | -0.036621 | 0.28839 | 48.2483 | 46.6415 | 122.4609 | 123.8342 | 0.09613 | 123.8297 | 66.0324 | -0.23346 | 123.8342 | 0.09613 | 66.0324 | 122.4609 | 123.8297 | -124.0585 | -124.0997
1086.7188 | 124.0448 | -60.965 | 62.8967 | 0.029221 | 0.0076925 | 0.0093546 | 0.0033474 | 0.069434 | -0.0020421 | 0.067941 | -60.8917 | 62.8784 | -61.1572 | -61.1755 | 61.4502 | 4.985 | -12.8128 | -14.5065 | 62.8693 | -61.2076 | -0.19226 | -0.018311 | 0.073242 | -0.21057 | -1.4465 | -0.24262 | -0.027466 | 0.2655 | 48.1522 | 46.4584 | 122.4152 | 123.8434 | 0.073242 | 123.8342 | 65.95 | -0.24262 | 123.8434 | 0.073242 | 65.95 | 122.4152 | 123.8342 | -124.054 | -124.1043
1087.7188 | 124.1089 | -60.9375 | 62.8647 | 0.12077 | 0.0070517 | 0.0085 | -0.0032748 | 0.066657 | -0.0026831 | 0.072 | -60.8734 | 62.7731 | -61.1664 | -61.1206 | 61.496 | 5.1041 | -13.0554 | -14.5203 | 62.8281 | -61.1664 | -0.22888 | -0.091553 | 0.064087 | -0.1831 | -1.3687 | -0.22888 | -0.036621 | 0.29297 | 47.8821 | 46.4172 | 122.4335 | 123.7106 | 0.064087 | 123.7656 | 66.0416 | -0.22888 | 123.7106 | 0.064087 | 66.0416 | 122.4335 | 123.7656 | -124.0311 | -124.0311
1088.7188 | 124.0768 | -60.9604 | 62.9105 | -0.054703 | 0.0079061 | 0.010423 | 0.001852 | 0.066443 | 0.0022303 | 0.067513 | -60.8505 | 62.8922 | -61.1435 | -61.1526 | 61.6196 | 5.0354 | -12.9456 | -14.5569 | 62.8738 | -61.2305 | -0.18311 | -0.01831 | 0.10986 | -0.19226 | -1.2909 | -0.27008 | -0.036621 | 0.29297 | 48.0148 | 46.4035 | 122.58 | 123.8525 | 0.10986 | 123.8342 | 65.9958 | -0.27008 | 123.8525 | 0.10986 | 65.9958 | 122.58 | 123.8342 | -124.054 | -124.1409
1089.7188 | 124.0173 | -60.9329 | 62.9059 | 0.03685 | 0.0098287 | 0.011064 | 0.00099764 | 0.070075 | -0.0018285 | 0.068582 | -60.8963 | 62.8784 | -61.1664 | -61.1938 | 61.4273 | 4.9484 | -13.0508 | -14.772 | 62.8967 | -61.2167 | -0.23346 | -0.027466 | 0.036621 | -0.26093 | -1.4786 | -0.28381 | -0.009155 | 0.27008 | 47.8821 | 46.1609 | 122.3602 | 123.8113 | 0.036621 | 123.8297 | 65.8813 | -0.28381 | 123.8113 | 0.036621 | 65.8813 | 122.3602 | 123.8297 | -124.0723 | -124.1226
1090.7188 | 124.0906 | -60.9421 | 62.8876 | -0.10048 | 0.0091879 | 0.0072184 | -7.0562e-05 | 0.06623 | -0.00033333 | 0.071145 | -60.8459 | 62.9013 | -61.1343 | -61.1114 | 61.4731 | 4.9988 | -13.1653 | -14.7675 | 62.8555 | -61.1847 | -0.19226 | 0.013733 | 0.096131 | -0.16937 | -1.4145 | -0.24261 | -0.032043 | 0.28839 | 47.7768 | 46.1746 | 122.4152 | 123.8434 | 0.096131 | 123.7976 | 65.9409 | -0.24261 | 123.8434 | 0.096131 | 65.9409 | 122.4152 | 123.7976 | -124.0219 | -124.0723
1091.7188 | 124.0631 | -60.9512 | 62.9013 | 1.99 | 0.0083333 | 0.0065774 | 0.0050564 | 0.067725 | -0.0026831 | 0.070291 | -60.7178 | 62.883 | -61.171 | -61.1023 | 61.5005 | 4.985 | -13.2614 | -14.8315 | 62.8967 | -61.2076 | -0.21973 | -0.01831 | 0.23346 | -0.15106 | -1.4008 | -0.25635 | -0.004577 | 0.45319 | 47.6898 | 46.1197 | 122.4518 | 123.8342 | 0.23346 | 123.848 | 65.9363 | -0.25635 | 123.8342 | 0.23346 | 65.9363 | 122.4518 | 123.848 | -124.0723 | -124.1089
1092.7188 | 124.0311 | -60.9604 | 62.8967 | 0.19707 | 0.0085471 | 0.016404 | 0.0022794 | 0.070075 | -0.0022559 | 0.070077 | -61.1343 | 62.8372 | -61.1984 | -61.1755 | 61.3403 | 4.8294 | -13.2889 | -15.0101 | 62.9059 | -61.1984 | -0.23804 | -0.05951 | -0.17395 | -0.21515 | -1.5564 | -0.23804 | 0.009155 | 0.064087 | 47.6715 | 45.9503 | 122.3007 | 123.7976 | -0.17395 | 123.8663 | 65.7898 | -0.23804 | 123.7976 | -0.17395 | 65.7898 | 122.3007 | 123.8663 | -124.0952 | -124.0952
1093.7188 | 124.0677 | -60.9055 | 62.9242 | -0.25307 | 0.0079061 | 0.0065774 | 0.0020656 | 0.06687 | -0.0048193 | 0.069009 | -60.8871 | 62.9105 | -61.1481 | -61.116 | 61.4365 | 4.921 | -13.3575 | -14.978 | 62.915 | -61.1938 | -0.24261 | -0.013733 | 0.018311 | -0.21057 | -1.4877 | -0.28839 | -0.009155 | 0.26093 | 47.5479 | 45.9274 | 122.3419 | 123.8159 | 0.018311 | 123.8205 | 65.8264 | -0.28839 | 123.8159 | 0.018311 | 65.8264 | 122.3419 | 123.8205 | -124.0723 | -124.118
1094.7188 | 124.0036 | -60.9604 | 62.9196 | 0.074997 | 0.0096151 | 0.0095682 | 0.002493 | 0.068579 | 0.00052127 | 0.067941 | -60.9192 | 62.8967 | -61.1801 | -61.2167 | 61.3495 | 4.8111 | -13.4903 | -15.184 | 62.883 | -61.1938 | -0.21973 | -0.022888 | 0.041199 | -0.25635 | -1.5701 | -0.23346 | -0.036621 | 0.26093 | 47.4701 | 45.7764 | 122.3099 | 123.8571 | 0.041199 | 123.8434 | 65.7715 | -0.23346 | 123.8571 | 0.041199 | 65.7715 | 122.3099 | 123.8434 | -124.0997 | -124.1135
1095.7188 | 124.0723 | -60.9283 | 62.915 | -0.077591 | 0.0089743 | 0.0078592 | 0.00099764 | 0.067084 | -0.0020421 | 0.068368 | -60.8368 | 62.8967 | -61.1572 | -61.1298 | 61.4685 | 4.9347 | -13.591 | -15.1154 | 62.8967 | -61.1984 | -0.22888 | -0.01831 | 0.091553 | -0.20142 | -1.4465 | -0.27008 | -0.01831 | 0.32043 | 47.3373 | 45.813 | 122.3969 | 123.8251 | 0.091553 | 123.8251 | 65.863 | -0.27008 | 123.8251 | 0.091553 | 65.863 | 122.3969 | 123.8251 | -124.0723 | -124.1135
1096.7188 | 124.0173 | -60.9283 | 62.9242 | -0.054703 | 0.0081197 | 0.007432 | 0.00014304 | 0.067084 | -0.00097413 | 0.070931 | -60.8734 | 62.9013 | -61.171 | -61.1435 | 61.409 | 4.8523 | -13.591 | -15.2115 | 62.9242 | -61.1755 | -0.24261 | -0.022888 | 0.054932 | -0.21515 | -1.5152 | -0.24719 | 0 | 0.29755 | 47.3373 | 45.7169 | 122.3373 | 123.8297 | 0.054932 | 123.8525 | 65.7806 | -0.24719 | 123.8297 | 0.054932 | 65.7806 | 122.3373 | 123.8525 | -124.0952 | -124.0997
1097.7188 | 124.0585 | -60.9375 | 62.9471 | -0.2607 | 0.0085471 | 0.0085 | 0.0020656 | 0.067939 | 0.0013757 | 0.070718 | -60.8093 | 62.8922 | -61.1526 | -61.116 | 61.409 | 4.8569 | -13.797 | -15.2527 | 62.883 | -61.1572 | -0.21515 | -0.054932 | 0.12817 | -0.17853 | -1.5381 | -0.21973 | -0.064087 | 0.34332 | 47.1405 | 45.6848 | 122.3465 | 123.8297 | 0.12817 | 123.8205 | 65.7944 | -0.21973 | 123.8297 | 0.12817 | 65.7944 | 122.3465 | 123.8205 | -124.0997 | -124.1043
1098.7188 | 124.0723 | -60.9238 | 62.915 | -0.047073 | 0.0059835 | 0.010636 | 0.0022794 | 0.068793 | -0.0033239 | 0.0673 | -60.9467 | 62.8784 | -61.171 | -61.1252 | 61.4273 | 4.8569 | -13.8748 | -15.3168 | 62.8967 | -61.1572 | -0.24719 | -0.036621 | -0.022888 | -0.20142 | -1.4877 | -0.23346 | -0.01831 | 0.2243 | 47.0489 | 45.607 | 122.3511 | 123.8022 | -0.022888 | 123.8205 | 65.7806 | -0.23346 | 123.8022 | -0.022888 | 65.7806 | 122.3511 | 123.8205 | -124.086 | -124.0723
1099.7188 | 124.0036 | -60.965 | 62.9196 | 0.15892 | 0.0057699 | 0.0132 | 0.00078404 | 0.06623 | -0.0024695 | 0.071572 | -60.9055 | 62.9059 | -61.1618 | -61.2488 | 61.3266 | 4.866 | -13.9664 | -15.5777 | 62.8876 | -61.1893 | -0.19684 | -0.013733 | 0.059509 | -0.28381 | -1.593 | -0.2243 | -0.032044 | 0.25635 | 46.9986 | 45.3873 | 122.2916 | 123.8708 | 0.059509 | 123.8525 | 65.831 | -0.2243 | 123.8708 | 0.059509 | 65.831 | 122.2916 | 123.8525 | -124.0814 | -124.1089
1100.7188 | 124.0356 | -60.9146 | 62.9333 | 0.3344 | 0.0061971 | 0.006791 | -0.0034886 | 0.06623 | -0.0024695 | 0.069436 | -60.8643 | 62.8876 | -61.1847 | -61.116 | 61.3724 | 4.8248 | -13.9343 | -15.5457 | 62.9288 | -61.171 | -0.27008 | -0.045777 | 0.050354 | -0.20142 | -1.561 | -0.25635 | -0.004578 | 0.32043 | 46.9803 | 45.369 | 122.287 | 123.8022 | 0.050354 | 123.8434 | 65.7394 | -0.25635 | 123.8022 | 0.050354 | 65.7394 | 122.287 | 123.8434 | -124.118 | -124.1043
1101.7188 | 124.0356 | -60.91 | 62.9654 | -0.29121 | 0.0049155 | 0.0076456 | 0.00035684 | 0.065161 | -0.0033239 | 0.071145 | -60.8871 | 62.8784 | -61.1481 | -61.2213 | 61.2076 | 4.6646 | -13.9664 | -15.6692 | 62.8967 | -61.2076 | -0.23804 | -0.086975 | 0.022888 | -0.31128 | -1.7578 | -0.29755 | -0.068664 | 0.26093 | 46.9437 | 45.2408 | 122.1176 | 123.7885 | 0.022888 | 123.8068 | 65.5746 | -0.29755 | 123.7885 | 0.022888 | 65.5746 | 122.1176 | 123.8068 | -124.1135 | -124.173
1102.7188 | 124.1318 | -60.9558 | 62.883 | 0.18944 | 0.0064107 | 0.0080728 | 0.001852 | 0.067511 | -0.00076053 | 0.06965 | -60.8597 | 62.8784 | -61.1389 | -61.1069 | 61.3998 | 4.8614 | -14.3646 | -15.6784 | 62.8418 | -61.1526 | -0.18311 | -0.004578 | 0.096131 | -0.15106 | -1.4832 | -0.19684 | -0.041199 | 0.27924 | 46.5912 | 45.2774 | 122.3557 | 123.8342 | 0.096131 | 123.7976 | 65.8173 | -0.19684 | 123.8342 | 0.096131 | 65.8173 | 122.3557 | 123.7976 | -124.0219 | -124.0356
1103.7188 | 124.0082 | -60.9329 | 62.9608 | -0.131 | 0.0079061 | 0.0063638 | 0.00035684 | 0.065161 | -0.00097413 | 0.070291 | -60.9009 | 62.9105 | -61.1526 | -61.1343 | 61.3632 | 4.8019 | -14.209 | -15.7837 | 62.9288 | -61.1664 | -0.21973 | -0.050354 | 0.032043 | -0.20142 | -1.5976 | -0.23346 | -0.032043 | 0.25177 | 46.7239 | 45.1492 | 122.2961 | 123.8434 | 0.032043 | 123.8617 | 65.7349 | -0.23346 | 123.8434 | 0.032043 | 65.7349 | 122.2961 | 123.8617 | -124.1135 | -124.1272
1104.7188 | 124.0768 | -60.9329 | 62.9379 | -0.13863 | 0.01047 | 0.0072184 | 0.0050564 | 0.06687 | -0.00033333 | 0.069009 | -60.8231 | 62.9059 | -61.1298 | -61.0931 | 61.3907 | 4.8157 | -14.36 | -15.834 | 62.9105 | -61.1389 | -0.19684 | -0.032043 | 0.10986 | -0.16022 | -1.5472 | -0.20599 | -0.027466 | 0.3067 | 46.5729 | 45.0989 | 122.3236 | 123.8388 | 0.10986 | 123.8434 | 65.7486 | -0.20599 | 123.8388 | 0.10986 | 65.7486 | 122.3236 | 123.8434 | -124.0677 | -124.0768
1105.7188 | 124.0906 | -60.878 | 62.9837 | -0.23781 | 0.0061971 | 0.0078592 | -0.00092496 | 0.066016 | 0.00052127 | 0.070931 | -60.878 | 62.8967 | -61.1343 | -61.1298 | 61.3266 | 4.7607 | -14.3463 | -15.9393 | 62.9517 | -61.1618 | -0.25635 | -0.086975 | 0 | -0.25177 | -1.6571 | -0.28381 | -0.032044 | 0.25635 | 46.5317 | 44.9387 | 122.2046 | 123.7747 | 0 | 123.8297 | 65.6387 | -0.28381 | 123.7747 | 0 | 65.6387 | 122.2046 | 123.8297 | -124.118 | -124.1455
1106.7188 | 124.0723 | -60.9192 | 62.9379 | -0.17677 | 0.0068381 | 0.0099954 | 0.0048428 | 0.064948 | -0.0037511 | 0.06965 | -60.8276 | 62.915 | -61.1206 | -61.084 | 61.3632 | 4.7882 | -14.4974 | -15.9943 | 62.9196 | -61.1526 | -0.20142 | -0.022888 | 0.091552 | -0.16479 | -1.5747 | -0.23346 | -0.01831 | 0.29297 | 46.4218 | 44.9249 | 122.2824 | 123.8342 | 0.091552 | 123.8388 | 65.7074 | -0.23346 | 123.8342 | 0.091552 | 65.7074 | 122.2824 | 123.8388 | -124.0585 | -124.0906
1107.7188 | 124.0082 | -60.9329 | 62.9333 | 0.059738 | 0.0085471 | 0.012559 | 0.0020656 | 0.067084 | -0.00033333 | 0.071145 | -60.8505 | 62.9196 | -61.1435 | -61.1343 | 61.2991 | 4.7241 | -14.6255 | -16.1362 | 62.9013 | -61.1755 | -0.21057 | -0.013733 | 0.082397 | -0.20142 | -1.6342 | -0.24262 | -0.032044 | 0.29297 | 46.3074 | 44.7968 | 122.2321 | 123.8525 | 0.082397 | 123.8342 | 65.657 | -0.24262 | 123.8525 | 0.082397 | 65.657 | 122.2321 | 123.8342 | -124.0768 | -124.1089
1108.7188 | 124.0082 | -60.9192 | 62.9425 | -0.27596 | 0.0061971 | 0.0072184 | -0.0028476 | 0.067084 | -0.0022559 | 0.06965 | -60.8688 | 62.9059 | -61.1343 | -61.1481 | 61.3998 | 4.9301 | -14.7995 | -16.3239 | 62.9471 | -61.1755 | -0.21515 | -0.036621 | 0.050354 | -0.22888 | -1.5427 | -0.25635 | 0.004578 | 0.2655 | 46.1197 | 44.5953 | 122.319 | 123.8251 | 0.050354 | 123.8663 | 65.8493 | -0.25635 | 123.8251 | 0.050354 | 65.8493 | 122.319 | 123.8663 | -124.0768 | -124.118
1109.7188 | 124.0723 | -60.8963 | 62.9059 | -0.2607 | 0.0074789 | 0.0082864 | -0.0022068 | 0.065802 | -0.0020421 | 0.070077 | -60.8002 | 62.8555 | -61.1114 | -61.0611 | 61.3861 | 4.7836 | -14.7812 | -16.1499 | 62.8876 | -61.1252 | -0.21515 | -0.050354 | 0.09613 | -0.16479 | -1.5198 | -0.22888 | -0.018311 | 0.31128 | 46.1151 | 44.7464 | 122.2824 | 123.7518 | 0.09613 | 123.7839 | 65.6799 | -0.22888 | 123.7518 | 0.09613 | 65.6799 | 122.2824 | 123.7839 | -124.0173 | -124.0311
1110.7188 | 124.0356 | -60.9283 | 62.9654 | -0.2607 | 0.0066245 | 0.0046548 | 0.0029202 | 0.064734 | -0.00011953 | 0.069436 | -60.8871 | 62.9196 | -61.1114 | -61.116 | 61.2991 | 4.6921 | -14.7903 | -16.3193 | 62.9059 | -61.1572 | -0.1831 | -0.045776 | 0.041199 | -0.18768 | -1.6663 | -0.22888 | -0.059509 | 0.2243 | 46.138 | 44.6091 | 122.2275 | 123.848 | 0.041199 | 123.8342 | 65.6204 | -0.22888 | 123.848 | 0.041199 | 65.6204 | 122.2275 | 123.8342 | -124.0768 | -124.1226
1111.7188 | 124.0356 | -60.9055 | 62.97 | -0.19966 | 0.0061971 | 0.0099954 | 0.0044156 | 0.065375 | -0.0014013 | 0.06965 | -60.9833 | 62.8967 | -61.1069 | -61.1801 | 61.2762 | 4.6829 | -14.8956 | -16.3971 | 62.9242 | -61.1435 | -0.20142 | -0.073242 | -0.077819 | -0.27466 | -1.6937 | -0.23804 | -0.045777 | 0.1236 | 46.0098 | 44.5084 | 122.1817 | 123.8022 | -0.077819 | 123.8297 | 65.5884 | -0.23804 | 123.8022 | -0.077819 | 65.5884 | 122.1817 | 123.8297 | -124.0768 | -124.1135
1112.7188 | 124.0768 | -60.9009 | 62.9745 | -0.047073 | 0.0066245 | 0.0085 | 0.0029202 | 0.066657 | -0.0016149 | 0.06965 | -60.7864 | 62.9333 | -61.1069 | -61.0382 | 61.3129 | 4.7058 | -15.0513 | -16.4291 | 62.8876 | -61.1755 | -0.20599 | -0.041198 | 0.11444 | -0.13733 | -1.6617 | -0.27466 | -0.086975 | 0.32044 | 45.8496 | 44.4717 | 122.2137 | 123.8342 | 0.11444 | 123.7885 | 65.6067 | -0.27466 | 123.8342 | 0.11444 | 65.6067 | 122.2137 | 123.7885 | -124.0814 | -124.1501
1113.7188 | 124.0997 | -60.9055 | 62.9517 | -0.25307 | 0.0042745 | 0.0089274 | -0.0019932 | 0.064948 | -0.0020421 | 0.069009 | -60.7956 | 62.8372 | -61.1298 | -61.0565 | 61.3541 | 4.7424 | -15.1337 | -16.4566 | 62.915 | -61.1206 | -0.2243 | -0.11444 | 0.10986 | -0.15106 | -1.5976 | -0.21515 | -0.036621 | 0.33417 | 45.7718 | 44.4489 | 122.2595 | 123.7427 | 0.10986 | 123.8205 | 65.6479 | -0.21515 | 123.7427 | 0.10986 | 65.6479 | 122.2595 | 123.8205 | -124.0814 | -124.0723
1114.7344 | 124.1592 | -60.9055 | 62.915 | 0.18181 | 0.0055563 | 0.007432 | -7.0562e-05 | 0.067725 | 9.4068e-05 | 0.068154 | -60.7819 | 62.8006 | -61.116 | -60.9055 | 61.4731 | 4.7974 | -15.4358 | -16.4978 | 62.8601 | -61.1206 | -0.21057 | -0.11444 | 0.1236 | 0 | -1.442 | -0.21515 | -0.054932 | 0.33417 | 45.4697 | 44.4077 | 122.3785 | 123.7061 | 0.1236 | 123.7656 | 65.7028 | -0.21515 | 123.7061 | 0.1236 | 65.7028 | 122.3785 | 123.7656 | -124.0311 | -124.0356
1115.7188 | 124.0585 | -60.9009 | 62.97 | -0.26833 | 0.0066245 | 0.0033732 | -7.0562e-05 | 0.065589 | -0.0020421 | 0.069436 | -60.8093 | 62.8647 | -61.1069 | -61.0931 | 61.3129 | 4.6829 | -15.2344 | -16.6672 | 62.915 | -61.1206 | -0.20599 | -0.10529 | 0.091553 | -0.19226 | -1.6571 | -0.21973 | -0.054932 | 0.29755 | 45.6665 | 44.2337 | 122.2137 | 123.7656 | 0.091553 | 123.8159 | 65.5838 | -0.21973 | 123.7656 | 0.091553 | 65.5838 | 122.2137 | 123.8159 | -124.0768 | -124.0906
1116.7188 | 124.1501 | -60.878 | 62.9105 | -0.16914 | 0.0055563 | 0.0087138 | -0.0045566 | 0.063666 | -0.0011877 | 0.066873 | -60.7636 | 62.8098 | -61.0794 | -60.9741 | 61.3815 | 4.7882 | -15.477 | -16.626 | 62.8601 | -61.1023 | -0.20142 | -0.10071 | 0.11444 | -0.09613 | -1.5289 | -0.2243 | -0.050354 | 0.31586 | 45.401 | 44.252 | 122.2595 | 123.6877 | 0.11444 | 123.7381 | 65.6662 | -0.2243 | 123.6877 | 0.11444 | 65.6662 | 122.2595 | 123.7381 | -123.9899 | -124.0128
1117.7188 | 124.0173 | -60.91 | 62.9654 | -0.35988 | 0.0076925 | 0.0082864 | 0.0037746 | 0.064307 | -0.0011877 | 0.071145 | -60.8139 | 62.915 | -61.1206 | -61.1114 | 61.2305 | 4.6738 | -15.3854 | -16.8549 | 62.9105 | -61.1343 | -0.21057 | -0.050354 | 0.09613 | -0.20142 | -1.7349 | -0.2243 | -0.054932 | 0.3067 | 45.5246 | 44.0552 | 122.1405 | 123.8251 | 0.09613 | 123.8205 | 65.5838 | -0.2243 | 123.8251 | 0.09613 | 65.5838 | 122.1405 | 123.8205 | -124.086 | -124.0997
1118.7188 | 124.0311 | -60.9192 | 62.9974 | -0.52773 | 0.0074789 | 0.0065774 | 0.002493 | 0.063452 | -0.0016149 | 0.069222 | -60.8505 | 62.9059 | -61.1298 | -61.084 | 61.2305 | 4.6463 | -15.4449 | -16.9235 | 62.9333 | -61.1298 | -0.21057 | -0.091553 | 0.068664 | -0.16479 | -1.767 | -0.21057 | -0.064087 | 0.27924 | 45.4742 | 43.9957 | 122.1497 | 123.8251 | 0.068664 | 123.8525 | 65.5655 | -0.21057 | 123.8251 | 0.068664 | 65.5655 | 122.1497 | 123.8525 | -124.1272 | -124.1272
1119.7188 | 124.0356 | -60.9009 | 62.9883 | -0.19203 | 0.0083333 | 0.011064 | 0.0016384 | 0.064521 | -0.00033333 | 0.069863 | -60.8093 | 62.9333 | -61.1023 | -61.084 | 61.2534 | 4.6555 | -15.5594 | -16.9922 | 62.9562 | -61.116 | -0.20142 | -0.054931 | 0.091553 | -0.1831 | -1.7349 | -0.21515 | -0.032043 | 0.29297 | 45.3415 | 43.9087 | 122.1542 | 123.8342 | 0.091553 | 123.8571 | 65.5563 | -0.21515 | 123.8342 | 0.091553 | 65.5563 | 122.1542 | 123.8571 | -124.0906 | -124.1043
1120.7188 | 124.0631 | -60.9375 | 62.9608 | -0.16914 | 0.0079061 | 0.0095682 | 0.005911 | 0.06388 | -0.0022559 | 0.068582 | -60.7498 | 62.9379 | -61.1069 | -61.0336 | 61.2625 | 4.6463 | -15.7104 | -17.0425 | 62.9242 | -61.1298 | -0.16937 | -0.022888 | 0.18768 | -0.09613 | -1.6983 | -0.19226 | -0.036621 | 0.35706 | 45.2271 | 43.895 | 122.2 | 123.8754 | 0.18768 | 123.8617 | 65.5838 | -0.19226 | 123.8754 | 0.18768 | 65.5838 | 122.2 | 123.8617 | -124.0677 | -124.0906
1121.7188 | 124.1409 | -60.8597 | 62.9379 | 0.097885 | 0.0055563 | 0.0093546 | -0.0034886 | 0.064307 | -0.00054693 | 0.069436 | -60.7361 | 62.8235 | -61.0931 | -60.9924 | 61.3266 | 4.7287 | -15.8981 | -17.0288 | 62.9013 | -61.0748 | -0.23346 | -0.11444 | 0.1236 | -0.13275 | -1.6113 | -0.21515 | -0.036621 | 0.35706 | 44.9615 | 43.8309 | 122.1863 | 123.6832 | 0.1236 | 123.761 | 65.5884 | -0.21515 | 123.6832 | 0.1236 | 65.5884 | 122.1863 | 123.761 | -124.0311 | -124.0128
1122.7188 | 124.0219 | -60.8917 | 62.9562 | -0.24544 | 0.0064107 | 0.0082864 | 0.00099764 | 0.063666 | -0.0016149 | 0.070077 | -60.8231 | 62.9013 | -61.0977 | -61.0886 | 61.2122 | 4.5959 | -15.7883 | -17.1936 | 62.915 | -61.1389 | -0.20599 | -0.054932 | 0.068665 | -0.19684 | -1.7441 | -0.24719 | -0.041199 | 0.27466 | 45.1035 | 43.6981 | 122.1039 | 123.793 | 0.068665 | 123.8068 | 65.4877 | -0.24719 | 123.793 | 0.068665 | 65.4877 | 122.1039 | 123.8068 | -124.054 | -124.0952
1123.7188 | 124.1592 | -60.8551 | 62.9654 | -3.9457 | 0.0057699 | 0.0050822 | -0.001566 | 0.064093 | -0.00033333 | 0.070291 | -60.9558 | 62.851 | -61.0657 | -61.0062 | 61.2442 | 4.7104 | -16.0172 | -17.1249 | 62.8693 | -61.0611 | -0.21057 | -0.11444 | -0.10071 | -0.15106 | -1.7212 | -0.20599 | -0.09613 | 0.10986 | 44.838 | 43.7302 | 122.0993 | 123.7061 | -0.10071 | 123.7244 | 65.5655 | -0.20599 | 123.7061 | -0.10071 | 65.5655 | 122.0993 | 123.7244 | -124.0311 | -124.0265
1124.7188 | 124.0311 | -60.8917 | 63.0066 | 0.34203 | 0.0070517 | 0.0089274 | 0.0029202 | 0.063239 | 9.4068e-05 | 0.068154 | -60.7773 | 62.9242 | -61.0931 | -61.0703 | 61.1893 | 4.5776 | -15.9439 | -17.363 | 62.9379 | -61.1526 | -0.20142 | -0.082398 | 0.11444 | -0.17853 | -1.8173 | -0.26092 | -0.068665 | 0.31586 | 44.9478 | 43.5287 | 122.081 | 123.8159 | 0.11444 | 123.8297 | 65.4694 | -0.26092 | 123.8159 | 0.11444 | 65.4694 | 122.081 | 123.8297 | -124.0997 | -124.1592
1125.7188 | 124.118 | -60.8459 | 62.9425 | -0.15388 | 0.0059835 | 0.005723 | -0.00028416 | 0.061957 | -0.0018285 | 0.070504 | -60.7407 | 62.8464 | -61.0703 | -60.9924 | 61.2671 | 4.6875 | -16.1728 | -17.2943 | 62.8876 | -61.0794 | -0.2243 | -0.09613 | 0.10529 | -0.14648 | -1.6754 | -0.23346 | -0.054932 | 0.32959 | 44.6732 | 43.5516 | 122.113 | 123.6923 | 0.10529 | 123.7335 | 65.5334 | -0.23346 | 123.6923 | 0.10529 | 65.5334 | 122.113 | 123.7335 | -124.0128 | -124.0219
1126.7188 | 124.0265 | -60.8734 | 62.9837 | -0.24544 | 0.0038473 | 0.0033732 | 0.0014248 | 0.064307 | -0.0014013 | 0.06965 | -60.7727 | 62.8784 | -61.0977 | -61.0611 | 61.203 | 4.6005 | -16.1545 | -17.4637 | 62.9425 | -61.116 | -0.2243 | -0.10529 | 0.10071 | -0.18768 | -1.7807 | -0.24262 | -0.041199 | 0.32501 | 44.7189 | 43.4097 | 122.0764 | 123.7518 | 0.10071 | 123.8159 | 65.4739 | -0.24262 | 123.7518 | 0.10071 | 65.4739 | 122.0764 | 123.8159 | -124.0814 | -124.0997
1127.7188 | 124.0128 | -60.9238 | 62.9745 | -0.27596 | 0.0070517 | 0.005723 | -0.00049776 | 0.063239 | -0.00097413 | 0.06965 | -60.8093 | 62.9013 | -61.1069 | -61.0931 | 61.171 | 4.7424 | -16.2827 | -17.7612 | 62.9562 | -61.1389 | -0.18311 | -0.073242 | 0.11444 | -0.16937 | -1.8036 | -0.21515 | -0.01831 | 0.29755 | 44.6411 | 43.1625 | 122.0947 | 123.8251 | 0.11444 | 123.88 | 65.6662 | -0.21515 | 123.8251 | 0.11444 | 65.6662 | 122.0947 | 123.88 | -124.0814 | -124.1135
1128.7188 | 124.0768 | -60.8643 | 62.9791 | -0.23018 | 0.0070517 | 0.0070048 | 0.0056972 | 0.067298 | -0.0037511 | 0.068154 | -60.7636 | 62.915 | -61.1023 | -61.0291 | 61.1801 | 4.5639 | -16.3101 | -17.5827 | 62.9517 | -61.1298 | -0.23804 | -0.064087 | 0.10071 | -0.16479 | -1.799 | -0.2655 | -0.027466 | 0.33874 | 44.5541 | 43.2816 | 122.0444 | 123.7793 | 0.10071 | 123.8159 | 65.4282 | -0.2655 | 123.7793 | 0.10071 | 65.4282 | 122.0444 | 123.8159 | -124.0814 | -124.1089
1129.7188 | 124.0036 | -60.8917 | 62.9929 | -0.25307 | 0.0042745 | 0.004014 | 0.0014248 | 0.066016 | -0.0031103 | 0.069436 | -60.8002 | 62.9288 | -61.1069 | -61.0886 | 61.1481 | 4.5364 | -16.3513 | -17.7109 | 62.9379 | -61.1023 | -0.21515 | -0.064087 | 0.091553 | -0.19684 | -1.8448 | -0.21057 | -0.054932 | 0.3067 | 44.5404 | 43.1808 | 122.0398 | 123.8205 | 0.091553 | 123.8297 | 65.4282 | -0.21057 | 123.8205 | 0.091553 | 65.4282 | 122.0398 | 123.8297 | -124.0997 | -124.0952
1130.7188 | 124.1043 | -60.8276 | 62.9883 | -0.23781 | 0.0040609 | 0.0082864 | -0.0022068 | 0.064521 | -0.0041785 | 0.071359 | -60.7315 | 62.8464 | -61.084 | -61.0062 | 61.2305 | 4.6417 | -16.5161 | -17.6376 | 62.915 | -61.084 | -0.25635 | -0.14191 | 0.096131 | -0.17853 | -1.7578 | -0.25635 | -0.073242 | 0.35248 | 44.3115 | 43.19 | 122.0581 | 123.674 | 0.096131 | 123.7427 | 65.4694 | -0.25635 | 123.674 | 0.096131 | 65.4694 | 122.0581 | 123.7427 | -124.0723 | -124.0723
1131.7188 | 124.1592 | -60.8597 | 62.97 | -0.1844 | 0.0055563 | 0.0048684 | -0.0022068 | 0.05918 | -0.0011877 | 0.072427 | -60.704 | 62.851 | -61.0794 | -61.2488 | 61.0748 | 4.7195 | -16.7221 | -17.775 | 62.8647 | -61.084 | -0.21973 | -0.11902 | 0.15564 | -0.3891 | -1.8951 | -0.2243 | -0.10529 | 0.37537 | 44.1376 | 43.0847 | 121.9345 | 123.7106 | 0.15564 | 123.7244 | 65.5792 | -0.2243 | 123.7106 | 0.15564 | 65.5792 | 121.9345 | 123.7244 | -124.0494 | -124.054
1132.7344 | 124.0128 | -60.9055 | 62.9745 | 0.090256 | 0.0081197 | 0.010636 | 0.005911 | 0.065589 | -0.0026831 | 0.070718 | -60.8002 | 62.9333 | -61.1023 | -61.1298 | 61.0565 | 4.4998 | -16.6351 | -17.981 | 62.9059 | -61.1572 | -0.19684 | -0.041198 | 0.10529 | -0.2243 | -1.918 | -0.25177 | -0.068664 | 0.30212 | 44.2703 | 42.9245 | 121.962 | 123.8388 | 0.10529 | 123.8113 | 65.4053 | -0.25177 | 123.8388 | 0.10529 | 65.4053 | 121.962 | 123.8113 | -124.0768 | -124.1318
1133.7188 | 124.0997 | -60.8414 | 62.9791 | -0.16151 | 0.0047019 | 0.0065774 | -0.0030612 | 0.063666 | -0.00054693 | 0.072 | -60.704 | 62.8326 | -61.0748 | -60.9879 | 61.2213 | 4.6921 | -16.7999 | -17.7933 | 62.8922 | -61.0657 | -0.23346 | -0.14648 | 0.13733 | -0.14648 | -1.7578 | -0.2243 | -0.086975 | 0.37079 | 44.0414 | 43.0481 | 122.0627 | 123.674 | 0.13733 | 123.7335 | 65.5334 | -0.2243 | 123.674 | 0.13733 | 65.5334 | 122.0627 | 123.7335 | -124.054 | -124.0448
1134.7188 | 124.0677 | -60.9009 | 62.9654 | -0.062332 | 0.0087607 | 0.0097818 | 0.0046292 | 0.065161 | -0.0016149 | 0.067513 | -60.7315 | 62.9517 | -61.0794 | -61.0199 | 61.2534 | 4.5456 | -16.7953 | -17.8574 | 62.8784 | -61.1481 | -0.17853 | -0.013733 | 0.16937 | -0.11902 | -1.712 | -0.24719 | -0.086975 | 0.3479 | 44.1055 | 43.0435 | 122.1542 | 123.8525 | 0.16937 | 123.7793 | 65.4465 | -0.24719 | 123.8525 | 0.16937 | 65.4465 | 122.1542 | 123.7793 | -124.0448 | -124.1135
1135.7188 | 124.0677 | -60.8551 | 62.9562 | -0.23781 | 0.0064107 | 0.0046548 | 0.00057044 | 0.064734 | -0.0039649 | 0.069222 | -60.7224 | 62.8601 | -61.0611 | -60.997 | 61.171 | 4.6783 | -16.832 | -17.9581 | 62.9196 | -61.0565 | -0.20599 | -0.096131 | 0.13275 | -0.14191 | -1.7853 | -0.20142 | -0.036621 | 0.33874 | 44.0231 | 42.897 | 122.0261 | 123.7152 | 0.13275 | 123.7747 | 65.5334 | -0.20142 | 123.7152 | 0.13275 | 65.5334 | 122.0261 | 123.7747 | -124.0173 | -124.0128
1136.7188 | 124.0402 | -60.9055 | 63.0066 | -0.21492 | 0.0081197 | 0.0099954 | 0.0022794 | 0.06388 | -0.0026831 | 0.069863 | -60.9192 | 62.9333 | -61.1069 | -61.0931 | 61.0794 | 4.6097 | -16.8365 | -18.1 | 62.9562 | -61.1069 | -0.20142 | -0.073242 | -0.013732 | -0.18768 | -1.9272 | -0.20142 | -0.050354 | 0.18768 | 44.0689 | 42.8055 | 121.9849 | 123.8388 | -0.013732 | 123.8617 | 65.5151 | -0.20142 | 123.8388 | -0.013732 | 65.5151 | 121.9849 | 123.8617 | -124.1135 | -124.1135
1137.7188 | 124.0173 | -60.8734 | 63.0112 | -0.23018 | 0.0070517 | 0.0082864 | -0.00071136 | 0.064307 | -0.00033333 | 0.070718 | -60.7407 | 62.915 | -61.0657 | -61.0519 | 61.0931 | 4.6463 | -16.9006 | -18.1091 | 62.9425 | -61.0748 | -0.19226 | -0.09613 | 0.13275 | -0.17853 | -1.918 | -0.20142 | -0.068664 | 0.32501 | 43.9728 | 42.7643 | 121.9666 | 123.7885 | 0.13275 | 123.8159 | 65.5197 | -0.20142 | 123.7885 | 0.13275 | 65.5197 | 121.9666 | 123.8159 | -124.0768 | -124.086
1138.7188 | 124.1226 | -60.8414 | 62.97 | -0.131 | 0.0066245 | 0.007432 | -0.0032748 | 0.063452 | -0.0011877 | 0.069222 | -60.7132 | 62.8693 | -61.0657 | -60.9787 | 61.1481 | 4.7287 | -17.1112 | -18.0954 | 62.9013 | -61.0748 | -0.2243 | -0.10071 | 0.12817 | -0.13733 | -1.8219 | -0.23346 | -0.068665 | 0.35248 | 43.7302 | 42.746 | 121.9894 | 123.7106 | 0.12817 | 123.7427 | 65.5701 | -0.23346 | 123.7106 | 0.12817 | 65.5701 | 121.9894 | 123.7427 | -124.0356 | -124.0448
1139.7188 | 124.054 | -60.8917 | 63.0157 | -0.13863 | 0.0059835 | 0.0065774 | 0.0044156 | 0.063025 | -0.00097413 | 0.069863 | -60.7727 | 62.9379 | -61.0794 | -61.0703 | 61.0336 | 4.6188 | -17.0151 | -18.2693 | 62.9471 | -61.0977 | -0.18768 | -0.07782 | 0.11902 | -0.17853 | -1.9821 | -0.20599 | -0.068664 | 0.3067 | 43.8766 | 42.6224 | 121.9254 | 123.8297 | 0.11902 | 123.8388 | 65.5106 | -0.20599 | 123.8297 | 0.11902 | 65.5106 | 121.9254 | 123.8388 | -124.0952 | -124.1135
1140.7188 | 124.0311 | -60.8917 | 62.9974 | -0.054703 | 0.0081197 | 0.011491 | 0.0033474 | 0.065161 | -0.0011877 | 0.068582 | -60.759 | 62.9333 | -61.0886 | -61.0657 | 61.0153 | 4.6188 | -17.0746 | -18.3334 | 62.9288 | -61.1023 | -0.19684 | -0.064087 | 0.13275 | -0.17395 | -1.9821 | -0.21057 | -0.068665 | 0.32959 | 43.8171 | 42.5583 | 121.907 | 123.8251 | 0.13275 | 123.8205 | 65.5106 | -0.21057 | 123.8251 | 0.13275 | 65.5106 | 121.907 | 123.8205 | -124.086 | -124.0997
1141.7188 | 124.1501 | -60.8368 | 62.9654 | -0.19203 | 0.0032065 | 0.0078592 | -0.0028476 | 0.065375 | -0.0061011 | 0.067086 | -60.672 | 62.8281 | -61.0428 | -60.7361 | 60.9283 | 4.4907 | -17.1707 | -18.2831 | 62.8876 | -61.0474 | -0.20599 | -0.13733 | 0.1648 | 0.10071 | -2.037 | -0.21057 | -0.07782 | 0.37079 | 43.6661 | 42.5537 | 121.7651 | 123.6649 | 0.1648 | 123.7244 | 65.3275 | -0.21057 | 123.6649 | 0.1648 | 65.3275 | 121.7651 | 123.7244 | -124.0082 | -124.0128
1142.7188 | 124.0082 | -60.9055 | 62.9654 | 0.059738 | 0.0083333 | 0.012345 | 0.0065518 | 0.064307 | 0.00030767 | 0.069222 | -60.759 | 62.9654 | -61.0748 | -61.1023 | 60.9787 | 4.6097 | -17.276 | -18.512 | 62.9196 | -61.1435 | -0.16937 | 0 | 0.14648 | -0.19684 | -1.9867 | -0.23804 | -0.045776 | 0.31586 | 43.6295 | 42.3935 | 121.8842 | 123.8708 | 0.14648 | 123.8251 | 65.5151 | -0.23804 | 123.8708 | 0.14648 | 65.5151 | 121.8842 | 123.8251 | -124.0402 | -124.1089
1143.7188 | 124.0723 | -60.8643 | 62.9883 | -0.14626 | 0.0096151 | 0.0132 | 0.0029202 | 0.065589 | -0.00011953 | 0.069436 | -60.7178 | 62.9608 | -61.0565 | -61.0107 | 61.0428 | 4.7012 | -17.3172 | -18.4525 | 62.9608 | -61.1114 | -0.19226 | -0.027466 | 0.14648 | -0.14648 | -1.9455 | -0.24719 | -0.027466 | 0.33875 | 43.5471 | 42.4118 | 121.907 | 123.8251 | 0.14648 | 123.8251 | 65.5655 | -0.24719 | 123.8251 | 0.14648 | 65.5655 | 121.907 | 123.8251 | -124.0448 | -124.0997
1144.7188 | 123.9899 | -60.9055 | 62.9745 | 0.13603 | 0.0089743 | 0.0087138 | 0.0054836 | 0.066016 | -0.00076053 | 0.067941 | -60.7636 | 62.9562 | -61.1206 | -61.116 | 60.9329 | 4.6097 | -17.3813 | -18.6447 | 62.9288 | -61.1206 | -0.21515 | -0.01831 | 0.14191 | -0.21057 | -2.0416 | -0.21515 | -0.045776 | 0.35705 | 43.5242 | 42.2607 | 121.8384 | 123.8617 | 0.14191 | 123.8342 | 65.5151 | -0.21515 | 123.8617 | 0.14191 | 65.5151 | 121.8384 | 123.8342 | -124.0952 | -124.0952
1145.7188 | 124.1135 | -60.8185 | 62.9471 | -0.062332 | 0.0023519 | 0.006791 | -0.0034886 | 0.06687 | -0.00076053 | 0.071786 | -60.7132 | 62.8464 | -61.0703 | -60.9924 | 61.0703 | 4.7974 | -17.5644 | -18.4799 | 62.8922 | -61.0382 | -0.25177 | -0.10071 | 0.10528 | -0.17395 | -1.8768 | -0.21973 | -0.054932 | 0.35705 | 43.2541 | 42.3386 | 121.8887 | 123.6649 | 0.10528 | 123.7106 | 65.6158 | -0.21973 | 123.6649 | 0.10528 | 65.6158 | 121.8887 | 123.7106 | -124.0173 | -123.9853
1146.7188 | 124.1409 | -60.8276 | 62.9608 | -0.35225 | 0.0042745 | 0.0080728 | -0.0028476 | 0.064521 | -0.0016149 | 0.067941 | -60.6857 | 62.8693 | -61.0474 | -60.9695 | 61.0565 | 4.7882 | -17.5735 | -18.4937 | 62.883 | -61.0794 | -0.21973 | -0.091552 | 0.14191 | -0.14191 | -1.9043 | -0.25177 | -0.077819 | 0.36163 | 43.2541 | 42.334 | 121.8842 | 123.6969 | 0.14191 | 123.7106 | 65.6158 | -0.25177 | 123.6969 | 0.14191 | 65.6158 | 121.8842 | 123.7106 | -124.0082 | -124.0402
1147.7188 | 124.0402 | -60.878 | 63.0066 | -0.047073 | 0.0076925 | 0.0065774 | 0.003561 | 0.063666 | 0.00073487 | 0.068368 | -60.7224 | 62.9562 | -61.0794 | -61.0657 | 60.9558 | 4.715 | -17.4408 | -18.6493 | 62.9196 | -61.1023 | -0.20142 | -0.050354 | 0.15564 | -0.18768 | -2.0508 | -0.2243 | -0.086975 | 0.35706 | 43.4372 | 42.2287 | 121.8338 | 123.8342 | 0.15564 | 123.7976 | 65.593 | -0.2243 | 123.8342 | 0.15564 | 65.593 | 121.8338 | 123.7976 | -124.086 | -124.1089
1148.7344 | 124.0402 | -60.8414 | 62.9791 | -0.19966 | 0.0083333 | 0.0080728 | 0.0071926 | 0.065802 | -0.0018285 | 0.069863 | -60.6812 | 62.9425 | -61.0611 | -61.0336 | 60.9558 | 4.747 | -17.5873 | -18.6676 | 62.9425 | -61.116 | -0.21973 | -0.036621 | 0.16022 | -0.19226 | -2.0233 | -0.27466 | -0.036621 | 0.37994 | 43.2541 | 42.1738 | 121.7972 | 123.7839 | 0.16022 | 123.7839 | 65.5884 | -0.27466 | 123.7839 | 0.16022 | 65.5884 | 121.7972 | 123.7839 | -124.0402 | -124.0952
1149.7188 | 124.0494 | -60.8643 | 63.002 | -0.21492 | 0.0057699 | 0.01085 | -0.0017796 | 0.067084 | -0.0048193 | 0.067727 | -60.7544 | 62.9288 | -61.0886 | -60.9283 | 60.7681 | 4.5914 | -17.482 | -18.7317 | 62.9654 | -61.0657 | -0.2243 | -0.073242 | 0.10986 | -0.064087 | -2.2339 | -0.20142 | -0.036621 | 0.33417 | 43.3823 | 42.1326 | 121.6324 | 123.793 | 0.10986 | 123.8297 | 65.4556 | -0.20142 | 123.793 | 0.10986 | 65.4556 | 121.6324 | 123.8297 | -124.0906 | -124.0677
1150.7188 | 124.1318 | -60.8368 | 62.9745 | 0.04448 | 0.0047019 | 0.0085 | -0.0017796 | 0.064521 | -0.00097413 | 0.068795 | -60.6628 | 62.8647 | -61.0657 | -60.965 | 61.0245 | 4.8706 | -17.7383 | -18.6172 | 62.915 | -61.0474 | -0.22888 | -0.10986 | 0.17395 | -0.12817 | -1.9501 | -0.21057 | -0.059509 | 0.40283 | 43.0984 | 42.2195 | 121.8613 | 123.7015 | 0.17395 | 123.7518 | 65.7074 | -0.21057 | 123.7015 | 0.17395 | 65.7074 | 121.8613 | 123.7518 | -124.0402 | -124.0219
1151.7188 | 124.0952 | -60.8368 | 62.9745 | -0.0089264 | 0.0049155 | 0.0078592 | -0.001566 | 0.06153 | -0.00076053 | 0.070077 | -60.7407 | 62.8418 | -61.0657 | -61.0336 | 60.9512 | 4.8157 | -17.7841 | -18.6905 | 62.8647 | -61.0382 | -0.22888 | -0.13275 | 0.09613 | -0.19684 | -2.0233 | -0.20142 | -0.10986 | 0.32501 | 43.0527 | 42.1463 | 121.788 | 123.6786 | 0.09613 | 123.7015 | 65.6525 | -0.20142 | 123.6786 | 0.09613 | 65.6525 | 121.788 | 123.7015 | -124.0402 | -124.0128
1152.7344 | 124.0402 | -60.8734 | 62.9883 | -0.12337 | 0.0074789 | 0.004014 | 0.0074062 | 0.063452 | -0.00054693 | 0.068795 | -60.6537 | 62.9745 | -61.0474 | -61.0107 | 60.9192 | 4.8111 | -17.7383 | -18.75 | 62.915 | -61.0931 | -0.17395 | -0.013733 | 0.21973 | -0.13733 | -2.0691 | -0.21973 | -0.073242 | 0.39368 | 43.1351 | 42.1234 | 121.7926 | 123.848 | 0.21973 | 123.7885 | 65.6845 | -0.21973 | 123.848 | 0.21973 | 65.6845 | 121.7926 | 123.7885 | -124.0356 | -124.0814
1153.7344 | 124.0173 | -60.8643 | 62.9974 | -0.13863 | 0.0059835 | 0.0089274 | 0.003561 | 0.064734 | -0.0014013 | 0.071359 | -60.7178 | 62.9654 | -61.0931 | -61.0519 | 60.8734 | 4.7791 | -17.688 | -18.8095 | 62.9608 | -61.0748 | -0.22888 | -0.032044 | 0.14648 | -0.18768 | -2.124 | -0.21057 | -0.036622 | 0.37537 | 43.1763 | 42.0547 | 121.7377 | 123.8297 | 0.14648 | 123.8251 | 65.6433 | -0.21057 | 123.8297 | 0.14648 | 65.6433 | 121.7377 | 123.8251 | -124.0906 | -124.0723
1154.7188 | 124.0311 | -60.878 | 63.0066 | -0.23781 | 0.0070517 | 0.0020914 | -0.00071136 | 0.062598 | -0.0018285 | 0.067086 | -60.7498 | 62.9196 | -61.0657 | -61.0428 | 60.8688 | 4.8019 | -17.7338 | -18.7912 | 62.9517 | -61.0519 | -0.18768 | -0.086975 | 0.12817 | -0.16479 | -2.1378 | -0.17395 | -0.054932 | 0.31586 | 43.1442 | 42.0868 | 121.7468 | 123.7976 | 0.12817 | 123.8297 | 65.6799 | -0.17395 | 123.7976 | 0.12817 | 65.6799 | 121.7468 | 123.8297 | -124.0723 | -124.0585
1155.7188 | 124.1043 | -60.8505 | 62.9608 | -0.14626 | 0.0055563 | 0.0072184 | -0.0032748 | 0.062171 | 0.0024439 | 0.070291 | -60.7315 | 62.8555 | -61.0519 | -61.0336 | 60.8734 | 4.8614 | -17.9169 | -18.782 | 62.9059 | -61.0611 | -0.20142 | -0.10528 | 0.11902 | -0.18311 | -2.0874 | -0.21057 | -0.054931 | 0.32043 | 42.9337 | 42.0685 | 121.7239 | 123.7061 | 0.11902 | 123.7564 | 65.712 | -0.21057 | 123.7061 | 0.11902 | 65.712 | 121.7239 | 123.7564 | -124.0128 | -124.0219
1156.7188 | 124.1272 | -60.8185 | 62.9608 | -0.28358 | 0.0057699 | 0.01085 | -0.0011386 | 0.061316 | -0.0026831 | 0.071572 | -60.8688 | 62.851 | -61.0474 | -61.0016 | 60.9512 | 4.9759 | -17.9214 | -18.6859 | 62.8967 | -61.0428 | -0.22888 | -0.10986 | -0.050354 | -0.18311 | -2.0096 | -0.22431 | -0.064086 | 0.17853 | 42.897 | 42.1326 | 121.7697 | 123.6694 | -0.050354 | 123.7152 | 65.7944 | -0.22431 | 123.6694 | -0.050354 | 65.7944 | 121.7697 | 123.7152 | -124.0082 | -124.0036
1157.7188 | 124.1547 | -60.8185 | 62.9425 | -0.077591 | 0.0036337 | 0.0055094 | -0.0019932 | 0.060462 | -0.00097413 | 0.070077 | -60.6812 | 62.8418 | -61.0519 | -60.9695 | 60.9009 | 4.9805 | -17.9718 | -18.7134 | 62.8738 | -61.0428 | -0.23346 | -0.10071 | 0.13733 | -0.15106 | -2.0416 | -0.22431 | -0.068665 | 0.37079 | 42.8467 | 42.1051 | 121.7194 | 123.6603 | 0.13733 | 123.6923 | 65.799 | -0.22431 | 123.6603 | 0.13733 | 65.799 | 121.7194 | 123.6923 | -123.9944 | -123.9853
1158.7188 | 124.0631 | -60.8597 | 62.9974 | -0.08522 | 0.0070517 | 0.0076456 | 0.0076198 | 0.061743 | -0.0035375 | 0.068368 | -60.6903 | 62.9608 | -61.0931 | -61.0245 | 60.8185 | 4.8752 | -17.8162 | -18.7958 | 62.9425 | -61.1023 | -0.23346 | -0.036622 | 0.16937 | -0.1648 | -2.179 | -0.24262 | -0.054932 | 0.40283 | 43.0435 | 42.0639 | 121.6782 | 123.8205 | 0.16937 | 123.8022 | 65.7349 | -0.24262 | 123.8205 | 0.16937 | 65.7349 | 121.6782 | 123.8022 | -124.0906 | -124.0997
1159.7188 | 124.0448 | -60.8505 | 62.97 | -0.21492 | 0.0068381 | 0.010209 | 0.0061246 | 0.066016 | -0.0020421 | 0.069436 | -60.6766 | 62.9196 | -61.0886 | -61.0062 | 60.8276 | 4.9255 | -17.894 | -18.7912 | 62.9242 | -61.0931 | -0.23804 | -0.050354 | 0.17395 | -0.15564 | -2.1423 | -0.24262 | -0.045777 | 0.41199 | 42.9565 | 42.0593 | 121.6782 | 123.7701 | 0.17395 | 123.7747 | 65.7761 | -0.24262 | 123.7701 | 0.17395 | 65.7761 | 121.6782 | 123.7747 | -124.0585 | -124.0631
1160.7188 | 124.1409 | -60.7956 | 63.0112 | -0.10811 | 0.0049155 | 0.012132 | -0.0022068 | 0.066016 | -0.0016149 | 0.069863 | -60.6171 | 62.8555 | -61.0428 | -60.9238 | 60.9055 | 5.0858 | -17.9993 | -18.6584 | 62.9059 | -61.0474 | -0.24719 | -0.15564 | 0.17853 | -0.12817 | -2.1057 | -0.25177 | -0.10529 | 0.42572 | 42.7963 | 42.1371 | 121.701 | 123.6511 | 0.17853 | 123.7015 | 65.8813 | -0.25177 | 123.6511 | 0.17853 | 65.8813 | 121.701 | 123.7015 | -124.054 | -124.0585
1161.7188 | 124.1318 | -60.8414 | 62.9517 | -0.08522 | 0.0034201 | 0.0072184 | -0.0013522 | 0.063452 | 0.00052127 | 0.072 | -60.6812 | 62.851 | -61.0611 | -61.0153 | 60.8231 | 5.0674 | -17.9993 | -18.7088 | 62.8876 | -61.0474 | -0.21973 | -0.10071 | 0.16022 | -0.17395 | -2.1286 | -0.20599 | -0.064087 | 0.37994 | 42.8421 | 42.1326 | 121.6644 | 123.6923 | 0.16022 | 123.7289 | 65.9088 | -0.20599 | 123.6923 | 0.16022 | 65.9088 | 121.6644 | 123.7289 | -124.0128 | -123.999
1162.7188 | 124.1364 | -60.8276 | 62.9883 | -0.13863 | 0.0059835 | 0.010636 | 0.0016384 | 0.064093 | -0.00054693 | 0.069009 | -60.6583 | 62.8372 | -61.0565 | -60.965 | 60.8231 | 5.1132 | -17.9626 | -18.6539 | 62.9059 | -61.0931 | -0.22888 | -0.15106 | 0.16937 | -0.13733 | -2.1652 | -0.2655 | -0.082397 | 0.39825 | 42.865 | 42.1738 | 121.6507 | 123.6649 | 0.16937 | 123.7335 | 65.9409 | -0.2655 | 123.6649 | 0.16937 | 65.9409 | 121.6507 | 123.7335 | -124.0448 | -124.0814
1163.7188 | 124.118 | -60.8551 | 62.9288 | 0.19707 | 0.0032065 | 0.0072184 | 0.0029202 | 0.062812 | -0.0020421 | 0.070291 | -60.6674 | 62.8464 | -61.0657 | -61.0153 | 60.7773 | 5.1132 | -18.0725 | -18.7042 | 62.8326 | -61.0886 | -0.21057 | -0.082397 | 0.18768 | -0.16022 | -2.1515 | -0.23346 | -0.09613 | 0.39825 | 42.7826 | 42.1509 | 121.6324 | 123.7015 | 0.18768 | 123.6877 | 65.9683 | -0.23346 | 123.7015 | 0.18768 | 65.9683 | 121.6324 | 123.6877 | -123.9944 | -124.0173
1164.7188 | 124.0723 | -60.8322 | 62.9791 | 0.65483 | 0.0096151 | 0.0095682 | 0.0071926 | 0.065802 | -0.00097413 | 0.070077 | -60.5896 | 62.8967 | -61.084 | -60.997 | 60.7498 | 5.1086 | -17.9352 | -18.6996 | 62.8922 | -61.0977 | -0.25177 | -0.082397 | 0.24261 | -0.16479 | -2.2293 | -0.2655 | -0.086975 | 0.49438 | 42.897 | 42.1326 | 121.582 | 123.7289 | 0.24261 | 123.7244 | 65.9409 | -0.2655 | 123.7289 | 0.24261 | 65.9409 | 121.582 | 123.7244 | -124.0631 | -124.0768
1165.7188 | 124.1318 | -60.8368 | 62.9196 | 0.21996 | 0.0076925 | 0.0099954 | 0.0046292 | 0.066443 | -0.00011953 | 0.069863 | -60.6262 | 62.8647 | -61.0977 | -61.0107 | 60.7773 | 5.1682 | -18.0908 | -18.6722 | 62.8876 | -61.0794 | -0.26093 | -0.054932 | 0.21057 | -0.17395 | -2.1423 | -0.24262 | -0.032044 | 0.4715 | 42.746 | 42.1646 | 121.6141 | 123.7015 | 0.21057 | 123.7244 | 66.0049 | -0.24262 | 123.7015 | 0.21057 | 66.0049 | 121.6141 | 123.7244 | -124.0173 | -123.999
1166.7188 | 124.0677 | -60.8505 | 62.9471 | 0.097885 | 0.0061971 | 0.0076456 | -0.0017796 | 0.06388 | -0.0011877 | 0.069222 | -60.6995 | 62.8693 | -61.084 | -61.0703 | 60.6903 | 5.1865 | -18.0176 | -18.6493 | 62.8601 | -61.0886 | -0.23346 | -0.07782 | 0.15106 | -0.21973 | -2.2568 | -0.23804 | -0.086976 | 0.38452 | 42.8329 | 42.2012 | 121.5408 | 123.7198 | 0.15106 | 123.7106 | 66.037 | -0.23804 | 123.7198 | 0.15106 | 66.037 | 121.5408 | 123.7106 | -124.0311 | -124.0356
1167.7188 | 124.1318 | -60.8322 | 62.9517 | -0.13863 | 0.0053427 | 0.0072184 | -0.0022068 | 0.062384 | -0.0016149 | 0.071145 | -60.6628 | 62.8326 | -61.0611 | -60.9741 | 60.7636 | 5.3009 | -17.9855 | -18.5257 | 62.8555 | -61.084 | -0.22888 | -0.11902 | 0.16937 | -0.14191 | -2.1881 | -0.25177 | -0.09613 | 0.39825 | 42.8467 | 42.3065 | 121.5958 | 123.6649 | 0.16937 | 123.6877 | 66.1331 | -0.25177 | 123.6649 | 0.16937 | 66.1331 | 121.5958 | 123.6877 | -124.0128 | -124.0356
1168.7188 | 124.1318 | -60.8505 | 62.9562 | 0.090256 | 0.0064107 | 0.0099954 | 0.00057044 | 0.063025 | 0.00073487 | 0.070504 | -60.6857 | 62.8418 | -61.0748 | -61.0474 | 60.6857 | 5.2643 | -17.926 | -18.5715 | 62.8647 | -61.0931 | -0.2243 | -0.11444 | 0.16479 | -0.19684 | -2.2705 | -0.24262 | -0.091553 | 0.3891 | 42.9245 | 42.2791 | 121.5363 | 123.6923 | 0.16479 | 123.7152 | 66.1148 | -0.24262 | 123.6923 | 0.16479 | 66.1148 | 121.5363 | 123.7152 | -124.0311 | -124.0494
1169.7188 | 124.0814 | -60.8688 | 62.9379 | 0.013962 | 0.0068381 | 0.004014 | 0.001852 | 0.066016 | -0.0035375 | 0.067727 | -60.6766 | 62.8738 | -61.0794 | -60.9604 | 60.5576 | 5.2597 | -17.9214 | -18.5806 | 62.8647 | -61.0703 | -0.21057 | -0.064087 | 0.19226 | -0.091553 | -2.3804 | -0.20142 | -0.073242 | 0.40283 | 42.9474 | 42.2882 | 121.4264 | 123.7427 | 0.19226 | 123.7335 | 66.1285 | -0.20142 | 123.7427 | 0.19226 | 66.1285 | 121.4264 | 123.7335 | -124.0173 | -124.0082
1170.7188 | 124.1272 | -60.8368 | 62.9288 | 0.9829 | 0.0074789 | 0.013413 | 0.0033474 | 0.066016 | -0.0016149 | 0.06965 | -60.5576 | 62.8693 | -61.0748 | -60.997 | 60.6812 | 5.3741 | -18.0038 | -18.4341 | 62.8189 | -61.1298 | -0.23804 | -0.059509 | 0.27924 | -0.16022 | -2.2476 | -0.29297 | -0.10986 | 0.51727 | 42.8329 | 42.4026 | 121.5179 | 123.7061 | 0.27924 | 123.6557 | 66.2109 | -0.29297 | 123.7061 | 0.27924 | 66.2109 | 121.5179 | 123.6557 | -124.0036 | -124.0585
1171.7188 | 124.1226 | -60.8551 | 62.9059 | 0.24284 | 0.0085471 | 0.010209 | 0.003561 | 0.063666 | -0.0016149 | 0.071572 | -60.6583 | 62.883 | -61.116 | -61.0428 | 60.6216 | 5.3925 | -17.9214 | -18.4067 | 62.8555 | -61.1343 | -0.26093 | -0.022888 | 0.19684 | -0.18768 | -2.2842 | -0.27923 | -0.050354 | 0.45776 | 42.9337 | 42.4484 | 121.4767 | 123.7381 | 0.19684 | 123.7106 | 66.2476 | -0.27923 | 123.7381 | 0.19684 | 66.2476 | 121.4767 | 123.7106 | -124.0219 | -124.0402
1172.7188 | 124.1135 | -60.8459 | 62.9196 | 0.24284 | 0.0059835 | 0.011704 | -0.00071136 | 0.06388 | -0.00097413 | 0.071359 | -60.6308 | 62.8601 | -61.0748 | -60.9924 | 60.6445 | 5.4932 | -17.9352 | -18.3243 | 62.8464 | -61.0977 | -0.22888 | -0.05951 | 0.21515 | -0.14648 | -2.2751 | -0.25177 | -0.073242 | 0.44403 | 42.9108 | 42.5217 | 121.4905 | 123.7061 | 0.21515 | 123.6923 | 66.3391 | -0.25177 | 123.7061 | 0.21515 | 66.3391 | 121.4905 | 123.6923 | -123.9944 | -124.0173
1173.7188 | 124.1409 | -60.8414 | 62.8922 | 0.16655 | 0.0059835 | 0.013627 | 0.0031338 | 0.063452 | 0.00030767 | 0.070931 | -60.7086 | 62.8235 | -61.0977 | -61.0062 | 60.6628 | 5.5618 | -17.9398 | -18.2968 | 62.8418 | -61.1023 | -0.25635 | -0.068665 | 0.13275 | -0.1648 | -2.2293 | -0.26093 | -0.050354 | 0.3891 | 42.9016 | 42.5446 | 121.5042 | 123.6649 | 0.13275 | 123.6832 | 66.4032 | -0.26093 | 123.6649 | 0.13275 | 66.4032 | 121.5042 | 123.6832 | -123.9899 | -123.9944
1174.7188 | 124.086 | -60.8505 | 62.9379 | 0.18181 | 0.0085471 | 0.0093546 | 0.00057044 | 0.063666 | 0.00030767 | 0.070931 | -60.6903 | 62.8738 | -61.0886 | -61.0428 | 60.5484 | 5.5389 | -17.7887 | -18.2602 | 62.8555 | -61.1298 | -0.23804 | -0.064087 | 0.16022 | -0.19226 | -2.3895 | -0.27924 | -0.082397 | 0.39825 | 43.0618 | 42.5903 | 121.3989 | 123.7244 | 0.16022 | 123.7061 | 66.3895 | -0.27924 | 123.7244 | 0.16022 | 66.3895 | 121.3989 | 123.7061 | -124.0265 | -124.0677
1175.7188 | 124.086 | -60.8917 | 62.9333 | 0.22758 | 0.0096151 | 0.0093546 | 0.0048428 | 0.066016 | 9.4068e-05 | 0.068582 | -60.672 | 62.9105 | -61.1252 | -61.0703 | 60.5301 | 5.5527 | -17.7429 | -18.2327 | 62.8464 | -61.1389 | -0.23346 | -0.022889 | 0.21973 | -0.17853 | -2.4033 | -0.24719 | -0.086975 | 0.45319 | 43.1488 | 42.659 | 121.4218 | 123.8022 | 0.21973 | 123.7381 | 66.4444 | -0.24719 | 123.8022 | 0.21973 | 66.4444 | 121.4218 | 123.7381 | -124.0585 | -124.0723
1176.7188 | 124.0906 | -60.8505 | 62.9471 | 0.12077 | 0.0068381 | 0.011491 | 0.0016384 | 0.066443 | -0.0016149 | 0.070077 | -60.672 | 62.8555 | -61.0886 | -61.0565 | 60.5621 | 5.6305 | -17.6697 | -18.1183 | 62.8601 | -61.1343 | -0.23804 | -0.091553 | 0.17853 | -0.20599 | -2.3849 | -0.28381 | -0.086976 | 0.41657 | 43.1808 | 42.7322 | 121.4127 | 123.7061 | 0.17853 | 123.7106 | 66.481 | -0.28381 | 123.7061 | 0.17853 | 66.481 | 121.4127 | 123.7106 | -124.0356 | -124.0814
1177.7188 | 124.1501 | -60.8505 | 62.9242 | 0.13603 | 0.0070517 | 0.010636 | 0.005911 | 0.064521 | -0.0018285 | 0.069009 | -60.6079 | 62.8693 | -61.0794 | -61.0016 | 60.4614 | 5.4977 | -17.5232 | -17.8619 | 62.8235 | -61.116 | -0.22888 | -0.054931 | 0.24262 | -0.15106 | -2.4628 | -0.2655 | -0.10071 | 0.4715 | 43.3273 | 42.9886 | 121.312 | 123.7198 | 0.24262 | 123.674 | 66.3483 | -0.2655 | 123.7198 | 0.24262 | 66.3483 | 121.312 | 123.674 | -124.0036 | -124.0402
1178.7188 | 123.9899 | -60.9055 | 62.9608 | 0.18181 | 0.0091879 | 0.0097818 | 0.0078336 | 0.06388 | -0.00054693 | 0.070931 | -60.6674 | 62.9242 | -61.1206 | -61.1298 | 60.4248 | 5.6488 | -17.4683 | -18.1046 | 62.8922 | -61.1801 | -0.21515 | -0.036621 | 0.23804 | -0.2243 | -2.536 | -0.27466 | -0.068664 | 0.45319 | 43.4372 | 42.8009 | 121.3303 | 123.8297 | 0.23804 | 123.7976 | 66.5543 | -0.27466 | 123.8297 | 0.23804 | 66.5543 | 121.3303 | 123.7976 | -124.0814 | -124.1409
1179.7188 | 124.0402 | -60.9238 | 62.9288 | 0.16655 | 0.0074789 | 0.011277 | 0.0027066 | 0.066443 | -0.00076053 | 0.070504 | -60.6766 | 62.9562 | -61.0977 | -61.0931 | 60.434 | 5.7266 | -17.514 | -17.981 | 62.8693 | -61.171 | -0.17395 | 0.027466 | 0.24719 | -0.16937 | -2.4948 | -0.24719 | -0.059509 | 0.42114 | 43.4097 | 42.9428 | 121.3577 | 123.88 | 0.24719 | 123.793 | 66.6504 | -0.24719 | 123.88 | 0.24719 | 66.6504 | 121.3577 | 123.793 | -124.0265 | -124.0997
1180.7188 | 124.0356 | -60.9238 | 62.9242 | 0.14366 | 0.0098287 | 0.011704 | 0.0020656 | 0.067084 | -0.0022559 | 0.071786 | -60.672 | 62.9471 | -61.1206 | -61.1069 | 60.4111 | 5.777 | -17.4271 | -17.9169 | 62.8922 | -61.171 | -0.19684 | 0.022889 | 0.25177 | -0.18311 | -2.5131 | -0.24719 | -0.032043 | 0.44861 | 43.4967 | 43.0069 | 121.3348 | 123.8708 | 0.25177 | 123.8159 | 66.7007 | -0.24719 | 123.8708 | 0.25177 | 66.7007 | 121.3348 | 123.8159 | -124.0448 | -124.0952
1181.7188 | 124.0356 | -60.91 | 62.9059 | 0.15129 | 0.0083333 | 0.010636 | 0.0054836 | 0.065161 | -0.0018285 | 0.070718 | -60.672 | 62.9196 | -61.116 | -61.1298 | 60.3882 | 5.8228 | -17.3309 | -17.8391 | 62.883 | -61.1572 | -0.20599 | 0.013733 | 0.23804 | -0.21973 | -2.5177 | -0.24719 | -0.022888 | 0.44403 | 43.5791 | 43.071 | 121.2982 | 123.8297 | 0.23804 | 123.793 | 66.7328 | -0.24719 | 123.8297 | 0.23804 | 66.7328 | 121.2982 | 123.793 | -124.0219 | -124.0631
1182.7188 | 124.0677 | -60.8871 | 62.9105 | 0.1284 | 0.0074789 | 0.0097818 | -0.0039158 | 0.065375 | -0.0035375 | 0.07264 | -60.6445 | 62.8143 | -61.0977 | -61.0703 | 60.4523 | 5.9647 | -17.3767 | -17.6468 | 62.8372 | -61.1252 | -0.21057 | -0.09613 | 0.24262 | -0.1831 | -2.4582 | -0.23804 | -0.073242 | 0.45319 | 43.5104 | 43.2404 | 121.3394 | 123.7015 | 0.24262 | 123.7244 | 66.8518 | -0.23804 | 123.7015 | 0.24262 | 66.8518 | 121.3394 | 123.7244 | -124.0082 | -124.0356
1183.7188 | 124.0128 | -60.9192 | 62.9517 | 0.15892 | 0.0070517 | 0.011491 | 0.0054836 | 0.065161 | -0.0016149 | 0.070291 | -60.9238 | 62.8738 | -61.1618 | -61.0977 | 60.2966 | 5.9418 | -17.1387 | -17.6697 | 62.883 | -61.1938 | -0.24261 | -0.07782 | -0.004578 | -0.17853 | -2.655 | -0.27466 | -0.068664 | 0.23804 | 43.7805 | 43.2495 | 121.2158 | 123.793 | -0.004578 | 123.8022 | 66.861 | -0.27466 | 123.793 | -0.004578 | 66.861 | 121.2158 | 123.8022 | -124.1135 | -124.1455
1184.7188 | 124.0677 | -60.9375 | 62.9105 | 0.12077 | 0.0087607 | 0.012132 | 0.0039882 | 0.065802 | -0.0018285 | 0.070718 | -60.6674 | 62.9288 | -61.1481 | -61.1389 | 60.347 | 6.0516 | -17.1432 | -17.5598 | 62.8693 | -61.1618 | -0.21057 | 0.018311 | 0.27008 | -0.20142 | -2.5635 | -0.2243 | -0.041198 | 0.48065 | 43.7943 | 43.3777 | 121.2845 | 123.8663 | 0.27008 | 123.8068 | 66.9891 | -0.2243 | 123.8663 | 0.27008 | 66.9891 | 121.2845 | 123.8068 | -124.0585 | -124.0723
1185.7188 | 124.0311 | -60.9375 | 62.9242 | 0.021591 | 0.0087607 | 0.014695 | 0.0061246 | 0.064307 | -0.0024695 | 0.068582 | -60.6262 | 62.915 | -61.1298 | -61.1206 | 60.3424 | 6.1157 | -16.9922 | -17.4362 | 62.8555 | -61.1847 | -0.19226 | -0.009155 | 0.31128 | -0.1831 | -2.5818 | -0.24719 | -0.068664 | 0.50354 | 43.9453 | 43.5013 | 121.2799 | 123.8525 | 0.31128 | 123.793 | 67.0532 | -0.24719 | 123.8525 | 0.31128 | 67.0532 | 121.2799 | 123.793 | -124.054 | -124.1089
1186.7188 | 123.9761 | -60.9192 | 62.9105 | 0.097885 | 0.0096151 | 0.0099954 | 0.0046292 | 0.068152 | 9.4068e-05 | 0.070931 | -60.672 | 62.9242 | -61.1435 | -61.1526 | 60.2783 | 6.1523 | -16.8823 | -17.363 | 62.8784 | -61.171 | -0.2243 | 0.013733 | 0.24719 | -0.23346 | -2.6321 | -0.25177 | -0.032043 | 0.4715 | 44.0369 | 43.5562 | 121.1975 | 123.8434 | 0.24719 | 123.7976 | 67.0715 | -0.25177 | 123.8434 | 0.24719 | 67.0715 | 121.1975 | 123.7976 | -124.054 | -124.0814
1187.7188 | 124.1226 | -60.8917 | 62.8967 | 0.17418 | 0.0081197 | 0.010209 | 0.00099764 | 0.067298 | -0.0018285 | 0.070291 | -60.6079 | 62.8235 | -61.1389 | -61.0611 | 60.3836 | 6.395 | -16.9968 | -17.0929 | 62.8143 | -61.1252 | -0.24719 | -0.073243 | 0.28381 | -0.16937 | -2.5131 | -0.23346 | -0.082398 | 0.53101 | 43.895 | 43.7988 | 121.2753 | 123.7152 | 0.28381 | 123.7061 | 67.2867 | -0.23346 | 123.7152 | 0.28381 | 67.2867 | 121.2753 | 123.7061 | -124.0356 | -124.0219
1188.7188 | 123.999 | -60.9512 | 62.9105 | 0.16655 | 0.0089743 | 0.012986 | 0.005911 | 0.066016 | -0.0024695 | 0.072 | -60.9604 | 62.8464 | -61.1938 | -61.1984 | 60.1868 | 6.3904 | -16.6489 | -17.1112 | 62.8784 | -61.1893 | -0.24262 | -0.064086 | -0.009155 | -0.24719 | -2.7237 | -0.23804 | -0.032043 | 0.23346 | 44.3024 | 43.84 | 121.138 | 123.7976 | -0.009155 | 123.8297 | 67.3416 | -0.23804 | 123.7976 | -0.009155 | 67.3416 | 121.138 | 123.8297 | -124.1043 | -124.0997
1189.7188 | 124.1135 | -60.9146 | 62.851 | 0.15129 | 0.0087607 | 0.011064 | 0.0016384 | 0.067298 | -0.0014013 | 0.071786 | -60.6125 | 62.8418 | -61.1206 | -61.0703 | 60.3287 | 6.5872 | -16.745 | -16.8457 | 62.8372 | -61.1389 | -0.20599 | -0.009155 | 0.30212 | -0.15564 | -2.5223 | -0.2243 | -0.013733 | 0.50812 | 44.1696 | 44.0689 | 121.2433 | 123.7564 | 0.30212 | 123.7518 | 67.5018 | -0.2243 | 123.7564 | 0.30212 | 67.5018 | 121.2433 | 123.7518 | -123.9716 | -123.9899
1190.7188 | 124.0402 | -60.9238 | 62.8922 | 0.074997 | 0.0070517 | 0.011491 | 0.00078404 | 0.067725 | 0.00052127 | 0.071359 | -60.64 | 62.8922 | -61.171 | -61.1526 | 60.228 | 6.5689 | -16.4795 | -16.8045 | 62.8555 | -61.1984 | -0.24719 | 0 | 0.28381 | -0.22888 | -2.6642 | -0.27466 | -0.036621 | 0.53101 | 44.4443 | 44.1193 | 121.1517 | 123.8159 | 0.28381 | 123.7793 | 67.4927 | -0.27466 | 123.8159 | 0.28381 | 67.4927 | 121.1517 | 123.7793 | -124.0631 | -124.0906
1191.7188 | 123.9166 | -60.9787 | 62.851 | 0.10551 | 0.0079061 | 0.0072184 | 0.0065518 | 0.066443 | -0.00076053 | 0.070931 | -60.6766 | 62.8876 | -61.1664 | -61.1664 | 60.1868 | 6.6238 | -16.333 | -16.6763 | 62.8601 | -61.2259 | -0.18768 | 0.036621 | 0.30212 | -0.18768 | -2.6642 | -0.24719 | 0.009155 | 0.48981 | 44.6457 | 44.3024 | 121.1655 | 123.8663 | 0.30212 | 123.8388 | 67.6025 | -0.24719 | 123.8663 | 0.30212 | 67.6025 | 121.1655 | 123.8388 | -124.0173 | -124.0768
1192.7188 | 124.1364 | -60.9192 | 62.8601 | 0.21233 | 0.0083333 | 0.007432 | 0.0014248 | 0.065161 | -0.00011953 | 0.070718 | -60.5804 | 62.8372 | -61.1389 | -61.0794 | 60.3836 | 6.7795 | -16.5848 | -16.127 | 62.7914 | -61.1755 | -0.21973 | -0.022888 | 0.33875 | -0.16022 | -2.4765 | -0.25635 | -0.068664 | 0.55847 | 44.3344 | 44.7922 | 121.3028 | 123.7564 | 0.33875 | 123.7106 | 67.6987 | -0.25635 | 123.7564 | 0.33875 | 67.6987 | 121.3028 | 123.7106 | -123.999 | -124.0356
1193.7188 | 124.0219 | -60.9467 | 62.8738 | 0.03685 | 0.010897 | 0.011277 | 0.0050564 | 0.067298 | -0.00076053 | 0.070718 | -60.6308 | 62.8784 | -61.1526 | -61.1252 | 60.1776 | 6.8939 | -15.8981 | -16.3055 | 62.8693 | -61.2076 | -0.20599 | 0.004578 | 0.31586 | -0.17853 | -2.6962 | -0.26093 | -0.004577 | 0.52185 | 45.0485 | 44.6411 | 121.1243 | 123.8251 | 0.31586 | 123.8159 | 67.8406 | -0.26093 | 123.8251 | 0.31586 | 67.8406 | 121.1243 | 123.8159 | -124.0265 | -124.0814
1194.7188 | 124.0173 | -60.9695 | 62.8876 | 0.074997 | 0.010256 | 0.0097818 | 0.004202 | 0.06687 | -0.00076053 | 0.07264 | -60.6857 | 62.8922 | -61.1801 | -61.1847 | 60.1456 | 6.9992 | -15.6601 | -16.1774 | 62.851 | -61.2076 | -0.21057 | 0.004578 | 0.28381 | -0.21515 | -2.742 | -0.23804 | -0.036621 | 0.49439 | 45.3094 | 44.7922 | 121.1151 | 123.8617 | 0.28381 | 123.8205 | 67.9688 | -0.23804 | 123.8617 | 0.28381 | 67.9688 | 121.1151 | 123.8205 | -124.0677 | -124.0952
1195.7188 | 124.0082 | -60.9741 | 62.8784 | -0.22255 | 0.0098287 | 0.0070048 | 0.0031338 | 0.066443 | -0.00054693 | 0.070718 | -60.6812 | 62.883 | -61.1801 | -61.203 | 60.1364 | 7.1091 | -15.5548 | -16.0584 | 62.8281 | -61.2305 | -0.20599 | 0.004578 | 0.29297 | -0.22888 | -2.742 | -0.25635 | -0.050354 | 0.49896 | 45.4193 | 44.9158 | 121.1105 | 123.8571 | 0.29297 | 123.8022 | 68.0832 | -0.25635 | 123.8571 | 0.29297 | 68.0832 | 121.1105 | 123.8022 | -124.0585 | -124.1089
1196.7188 | 124.0265 | -60.997 | 62.8693 | 0.03685 | 0.0083333 | 0.0095682 | 0.0031338 | 0.065802 | -0.0022559 | 0.070504 | -60.6766 | 62.8738 | -61.1847 | -61.1984 | 60.0998 | 7.1686 | -15.3992 | -15.9851 | 62.8281 | -61.2213 | -0.18768 | 0.004577 | 0.32043 | -0.20142 | -2.7695 | -0.2243 | -0.041199 | 0.50812 | 45.5978 | 45.0119 | 121.0968 | 123.8708 | 0.32043 | 123.8251 | 68.1656 | -0.2243 | 123.8708 | 0.32043 | 68.1656 | 121.0968 | 123.8251 | -124.054 | -124.0906
1197.7344 | 124.118 | -60.8871 | 62.8464 | -0.10048 | 0.0064107 | 0.009141 | -0.0069064 | 0.064948 | -0.00054693 | 0.071786 | -60.5896 | 62.7777 | -61.1801 | -61.0657 | 60.2234 | 7.4295 | -15.3717 | -15.6464 | 62.8235 | -61.1389 | -0.29297 | -0.068665 | 0.29755 | -0.17853 | -2.623 | -0.25177 | -0.022889 | 0.59052 | 45.5154 | 45.2408 | 121.1105 | 123.6649 | 0.29755 | 123.7106 | 68.3166 | -0.25177 | 123.6649 | 0.29755 | 68.3166 | 121.1105 | 123.7106 | -124.0265 | -123.9853
1198.7188 | 124.0219 | -60.9741 | 62.8601 | -0.76424 | 0.010256 | 0.0065774 | 0.0046292 | 0.066443 | -0.00076053 | 0.068582 | -60.7361 | 62.883 | -61.1847 | -61.2167 | 60.0494 | 7.3746 | -15.1062 | -15.7104 | 62.8281 | -61.2396 | -0.21057 | 0.022889 | 0.23804 | -0.24262 | -2.8107 | -0.2655 | -0.032043 | 0.44861 | 45.8679 | 45.2637 | 121.0236 | 123.8571 | 0.23804 | 123.8022 | 68.3487 | -0.2655 | 123.8571 | 0.23804 | 68.3487 | 121.0236 | 123.8022 | -124.0448 | -124.0997
1199.7188 | 124.0128 | -60.9695 | 62.8922 | 0.052109 | 0.0096151 | 0.013841 | 0.0065518 | 0.067298 | -0.0018285 | 0.070718 | -60.6171 | 62.8784 | -61.1938 | -61.2167 | 60.0586 | 7.4799 | -14.9323 | -15.5365 | 62.8281 | -61.2396 | -0.22431 | -0.013733 | 0.35248 | -0.24719 | -2.8336 | -0.27008 | -0.064087 | 0.57678 | 46.0373 | 45.433 | 121.0281 | 123.848 | 0.35248 | 123.7976 | 68.4494 | -0.27008 | 123.848 | 0.35248 | 68.4494 | 121.0281 | 123.7976 | -124.086 | -124.1318
1200.7188 | 123.9853 | -60.9833 | 62.883 | 0.12077 | 0.010256 | 0.0089274 | 0.0065518 | 0.067725 | -0.0011877 | 0.071359 | -60.6262 | 62.8647 | -61.1938 | -61.1938 | 60.0266 | 7.6035 | -14.7629 | -15.3442 | 62.8372 | -61.2579 | -0.21057 | -0.018311 | 0.35705 | -0.21057 | -2.8564 | -0.27466 | -0.045777 | 0.56763 | 46.2204 | 45.639 | 121.0098 | 123.848 | 0.35705 | 123.8205 | 68.5867 | -0.27466 | 123.848 | 0.35705 | 68.5867 | 121.0098 | 123.8205 | -124.0768 | -124.1409
1201.7188 | 124.054 | -60.997 | 62.8418 | 0.15129 | 0.0085471 | 0.0097818 | 0.0031338 | 0.066657 | 0.0018031 | 0.072 | -60.6537 | 62.8143 | -61.203 | -61.1984 | 60.0311 | 7.7637 | -14.653 | -15.1245 | 62.8143 | -61.2213 | -0.20599 | -0.027466 | 0.34332 | -0.20142 | -2.8107 | -0.2243 | -0.027466 | 0.54932 | 46.344 | 45.8725 | 121.0281 | 123.8113 | 0.34332 | 123.8113 | 68.7607 | -0.2243 | 123.8113 | 0.34332 | 68.7607 | 121.0281 | 123.8113 | -124.0448 | -124.0631
1202.7188 | 124.0952 | -60.9695 | 62.8143 | 0.13603 | 0.0070517 | 0.0093546 | -0.00049776 | 0.065375 | 0.00094847 | 0.07264 | -60.5942 | 62.7274 | -61.1893 | -61.1343 | 60.0677 | 7.9651 | -14.5386 | -14.8178 | 62.7823 | -61.1938 | -0.21973 | -0.086975 | 0.37537 | -0.16479 | -2.7466 | -0.22431 | -0.032043 | 0.59509 | 46.431 | 46.1517 | 121.0373 | 123.6969 | 0.37537 | 123.7518 | 68.9346 | -0.22431 | 123.6969 | 0.37537 | 68.9346 | 121.0373 | 123.7518 | -124.0036 | -124.0082
1203.7188 | 124.0448 | -60.9741 | 62.8418 | 0.11314 | 0.010897 | 0.011704 | 0.0039882 | 0.066443 | -0.00033333 | 0.070718 | -60.6537 | 62.8601 | -61.2167 | -61.2122 | 59.9625 | 8.0017 | -14.1998 | -14.7263 | 62.8006 | -61.2534 | -0.24262 | 0.01831 | 0.32043 | -0.23804 | -2.8793 | -0.27924 | -0.041199 | 0.56305 | 46.7743 | 46.2479 | 120.9366 | 123.8342 | 0.32043 | 123.7747 | 68.9758 | -0.27924 | 123.8342 | 0.32043 | 68.9758 | 120.9366 | 123.7747 | -124.0585 | -124.0952
1204.7188 | 124.054 | -60.9924 | 62.8281 | 0.18181 | 0.0087607 | 0.0065774 | 0.0076198 | 0.065161 | -0.00076053 | 0.070931 | -60.6583 | 62.8006 | -61.2305 | -61.2213 | 59.967 | 8.1573 | -13.9847 | -14.5157 | 62.8052 | -61.2717 | -0.23804 | -0.027466 | 0.33417 | -0.22888 | -2.861 | -0.27923 | -0.022888 | 0.5722 | 47.0078 | 46.4767 | 120.9595 | 123.793 | 0.33417 | 123.7976 | 69.1498 | -0.27923 | 123.793 | 0.33417 | 69.1498 | 120.9595 | 123.7976 | -124.0585 | -124.0997
1205.7188 | 124.0036 | -61.0062 | 62.8281 | 0.013962 | 0.0083333 | 0.010636 | 0.003561 | 0.064521 | -0.0024695 | 0.071359 | -60.6354 | 62.8418 | -61.2122 | -61.2305 | 59.935 | 8.3221 | -13.7466 | -14.3097 | 62.8052 | -61.29 | -0.20599 | 0.013733 | 0.37079 | -0.2243 | -2.8931 | -0.28381 | -0.022888 | 0.57678 | 47.2595 | 46.6965 | 120.9412 | 123.848 | 0.37079 | 123.8113 | 69.3283 | -0.28381 | 123.848 | 0.37079 | 69.3283 | 120.9412 | 123.8113 | -124.0402 | -124.118
1206.7188 | 123.9944 | -61.0199 | 62.851 | 0.067368 | 0.0096151 | 0.010636 | 0.0056972 | 0.067084 | -0.00076053 | 0.072427 | -60.6445 | 62.8372 | -61.2396 | -61.2442 | 59.903 | 8.4045 | -13.5132 | -14.0991 | 62.8006 | -61.2991 | -0.21973 | -0.013733 | 0.37537 | -0.22431 | -2.948 | -0.27924 | -0.050354 | 0.59509 | 47.5067 | 46.9208 | 120.9229 | 123.8571 | 0.37537 | 123.8205 | 69.4244 | -0.27924 | 123.8571 | 0.37537 | 69.4244 | 120.9229 | 123.8205 | -124.0906 | -124.1501
1207.7188 | 124.1226 | -61.0153 | 62.7823 | 0.059738 | 0.0057699 | 0.0097818 | -0.0017796 | 0.065802 | -0.0018285 | 0.073708 | -60.5621 | 62.6953 | -61.2488 | -61.1481 | 59.9991 | 8.6838 | -13.4399 | -13.7146 | 62.7457 | -61.2442 | -0.23346 | -0.086976 | 0.45319 | -0.13275 | -2.7832 | -0.22888 | -0.036621 | 0.68664 | 47.5754 | 47.3007 | 121.0144 | 123.7106 | 0.45319 | 123.761 | 69.6991 | -0.22888 | 123.7106 | 0.45319 | 69.6991 | 121.0144 | 123.761 | -124.0311 | -124.0265
1208.7188 | 124.0402 | -61.0016 | 62.8189 | 0.13603 | 0.0096151 | 0.014054 | 0.0039882 | 0.067511 | -0.0016149 | 0.072 | -60.6262 | 62.796 | -61.2396 | -61.2396 | 59.8846 | 8.7021 | -13.1149 | -13.6002 | 62.7686 | -61.2808 | -0.23804 | -0.022888 | 0.37537 | -0.23804 | -2.9343 | -0.27924 | -0.050354 | 0.6134 | 47.8867 | 47.4014 | 120.8862 | 123.7976 | 0.37537 | 123.7701 | 69.7037 | -0.27924 | 123.7976 | 0.37537 | 69.7037 | 120.8862 | 123.7701 | -124.0585 | -124.0997
1209.7188 | 124.0173 | -61.0107 | 62.8006 | 0.18944 | 0.010042 | 0.011491 | 0.0056972 | 0.064521 | -0.0026831 | 0.071359 | -60.6354 | 62.8098 | -61.2442 | -61.2488 | 59.8526 | 8.8577 | -12.9044 | -13.3804 | 62.7411 | -61.3083 | -0.23346 | 0.009155 | 0.37537 | -0.23804 | -2.948 | -0.29755 | -0.059509 | 0.60883 | 48.1064 | 47.6303 | 120.8633 | 123.8205 | 0.37537 | 123.7518 | 69.8685 | -0.29755 | 123.8205 | 0.37537 | 69.8685 | 120.8633 | 123.7518 | -124.0448 | -124.1089
1210.7188 | 124.0036 | -61.0336 | 62.8098 | 0.074997 | 0.0096151 | 0.010423 | 0.0039882 | 0.06623 | 0.0015893 | 0.074349 | -60.6308 | 62.8189 | -61.2534 | -61.2579 | 59.816 | 8.9996 | -12.7487 | -13.1287 | 62.7136 | -61.3174 | -0.21973 | 0.009156 | 0.40283 | -0.22431 | -2.9938 | -0.28381 | -0.09613 | 0.62256 | 48.2849 | 47.905 | 120.8496 | 123.8525 | 0.40283 | 123.7473 | 70.0333 | -0.28381 | 123.8525 | 0.40283 | 70.0333 | 120.8496 | 123.7473 | -124.0631 | -124.1272
1211.7188 | 123.9807 | -61.0611 | 62.7823 | 2.669 | 0.0074789 | 0.0095682 | 0.0022794 | 0.065161 | 0.00052127 | 0.071145 | -60.3516 | 62.796 | -61.2259 | -61.2442 | 59.8709 | 9.1324 | -12.4878 | -12.8815 | 62.7548 | -61.3083 | -0.16479 | 0.013733 | 0.70953 | -0.18311 | -2.9114 | -0.24719 | -0.027466 | 0.87433 | 48.5733 | 48.1796 | 120.932 | 123.8571 | 0.70953 | 123.8159 | 70.1935 | -0.24719 | 123.8571 | 0.70953 | 70.1935 | 120.932 | 123.8159 | -124.0082 | -124.0906
1212.7188 | 124.0494 | -61.0703 | 62.7731 | 0.12077 | 0.0096151 | 0.011491 | 0.0039882 | 0.066016 | 0.00030767 | 0.072 | -60.6308 | 62.7731 | -61.2671 | -61.2717 | 59.7839 | 9.3155 | -12.291 | -12.6022 | 62.7502 | -61.322 | -0.19684 | 0 | 0.43945 | -0.20142 | -2.9892 | -0.25177 | -0.022888 | 0.63629 | 48.7793 | 48.468 | 120.8542 | 123.8434 | 0.43945 | 123.8205 | 70.3857 | -0.25177 | 123.8434 | 0.43945 | 70.3857 | 120.8542 | 123.8205 | -124.0402 | -124.0952
1213.7188 | 124.0173 | -61.0336 | 62.7777 | 0.082626 | 0.011965 | 0.0093546 | 0.006979 | 0.064948 | 9.4068e-05 | 0.072854 | -60.5942 | 62.7914 | -61.2671 | -61.2534 | 59.7931 | 9.4391 | -12.0209 | -12.3322 | 62.7502 | -61.3266 | -0.23346 | 0.013733 | 0.43945 | -0.21973 | -2.9846 | -0.29297 | -0.027466 | 0.67291 | 49.0128 | 48.7015 | 120.8267 | 123.8251 | 0.43945 | 123.7839 | 70.4727 | -0.29297 | 123.8251 | 0.43945 | 70.4727 | 120.8267 | 123.7839 | -124.0448 | -124.1043
1214.7188 | 124.0082 | -61.0291 | 62.764 | -0.016556 | 0.010042 | 0.013413 | 0.0048428 | 0.066016 | -0.00097413 | 0.07264 | -60.5621 | 62.7869 | -61.29 | -61.235 | 59.7977 | 9.6313 | -11.7783 | -12.0392 | 62.7686 | -61.3266 | -0.26093 | 0.022888 | 0.46692 | -0.20599 | -2.9663 | -0.29755 | 0.004578 | 0.72784 | 49.2508 | 48.9899 | 120.8267 | 123.8159 | 0.46692 | 123.7976 | 70.6604 | -0.29755 | 123.8159 | 0.46692 | 70.6604 | 120.8267 | 123.7976 | -124.054 | -124.0906
1215.7188 | 123.967 | -61.0474 | 62.796 | 0.16655 | 0.0094015 | 0.010423 | 0.0029202 | 0.070288 | 0.00094847 | 0.070077 | -60.6491 | 62.7731 | -61.2762 | -61.2442 | 60.0723 | 9.9335 | -11.5952 | -11.7279 | 62.7686 | -61.322 | -0.22888 | -0.022889 | 0.39825 | -0.19684 | -2.7237 | -0.27466 | -0.027466 | 0.62714 | 49.4522 | 49.3195 | 121.1197 | 123.8205 | 0.39825 | 123.8159 | 70.9808 | -0.27466 | 123.8205 | 0.39825 | 70.9808 | 121.1197 | 123.8159 | -124.0723 | -124.118
1216.7188 | 123.9807 | -61.0886 | 62.7686 | 0.14366 | 0.011111 | 0.011704 | 0.0048428 | 0.067084 | -0.00011953 | 0.073495 | -60.6216 | 62.7594 | -61.3083 | -61.3358 | 59.6741 | 9.9701 | -11.3113 | -11.5768 | 62.7502 | -61.3403 | -0.21973 | -0.009156 | 0.46692 | -0.24719 | -3.0945 | -0.25177 | -0.018311 | 0.68665 | 49.7772 | 49.5117 | 120.7626 | 123.848 | 0.46692 | 123.8388 | 71.0587 | -0.25177 | 123.848 | 0.46692 | 71.0587 | 120.7626 | 123.8388 | -124.0768 | -124.1089
1217.7344 | 124.0952 | -61.0657 | 62.7686 | 0.04448 | 0.0057699 | 0.0087138 | -0.006052 | 0.064093 | 0.00030767 | 0.073495 | -60.6216 | 62.6587 | -61.2808 | -61.2625 | 59.7565 | 10.3226 | -11.1191 | -11.1877 | 62.6999 | -61.2762 | -0.21515 | -0.10986 | 0.44403 | -0.19684 | -3.0121 | -0.21057 | -0.068665 | 0.65918 | 49.9466 | 49.8779 | 120.8221 | 123.7244 | 0.44403 | 123.7656 | 71.3882 | -0.21057 | 123.7244 | 0.44403 | 71.3882 | 120.8221 | 123.7656 | -124.0494 | -124.0448
1218.7188 | 124.0082 | -61.0748 | 62.7686 | 0.021591 | 0.0089743 | 0.011918 | 0.0063382 | 0.064948 | 0.0013757 | 0.06965 | -60.5667 | 62.7777 | -61.2854 | -61.2946 | 59.697 | 10.437 | -10.7941 | -10.9589 | 62.7136 | -61.3541 | -0.21057 | 0.009155 | 0.50812 | -0.21973 | -3.0716 | -0.27924 | -0.054932 | 0.71869 | 50.2808 | 50.116 | 120.7718 | 123.8525 | 0.50812 | 123.7885 | 71.5118 | -0.27924 | 123.8525 | 0.50812 | 71.5118 | 120.7718 | 123.7885 | -124.054 | -124.1226
1219.7188 | 124.0128 | -61.1298 | 62.7274 | 0.0063326 | 0.0091879 | 0.015763 | 0.0063382 | 0.066443 | -0.0020421 | 0.069009 | -60.5667 | 62.7411 | -61.29 | -61.2671 | 59.6924 | 10.6155 | -10.5835 | -10.6522 | 62.7319 | -61.3449 | -0.16022 | 0.013733 | 0.56305 | -0.13733 | -3.035 | -0.21515 | 0.004578 | 0.72327 | 50.5463 | 50.4776 | 120.8221 | 123.8709 | 0.56305 | 123.8617 | 71.7453 | -0.21515 | 123.8709 | 0.56305 | 71.7453 | 120.8221 | 123.8617 | -124.0173 | -124.0723
1220.7188 | 124.0494 | -61.084 | 62.7411 | -0.13863 | 0.0089743 | 0.0095682 | 0.0039882 | 0.068152 | -0.00054693 | 0.072427 | -60.553 | 62.7502 | -61.3129 | -61.2396 | 59.7885 | 10.6613 | -10.2539 | -10.2036 | 62.6999 | -61.3403 | -0.22888 | 0.009155 | 0.53101 | -0.15564 | -2.9526 | -0.25635 | -0.041199 | 0.75989 | 50.8301 | 50.8804 | 120.8725 | 123.8342 | 0.53101 | 123.7839 | 71.7453 | -0.25635 | 123.8342 | 0.53101 | 71.7453 | 120.8725 | 123.7839 | -124.054 | -124.0814
1221.7188 | 124.0356 | -61.084 | 62.7777 | -0.09285 | 0.0089743 | 0.011277 | 0.0039882 | 0.067511 | -0.0018285 | 0.071572 | -60.5301 | 62.7457 | -61.2854 | -61.2717 | 59.6924 | 11.0138 | -10.0433 | -10.0525 | 62.7319 | -61.3541 | -0.20142 | -0.032043 | 0.55389 | -0.18768 | -3.0853 | -0.27008 | -0.045776 | 0.75531 | 51.0406 | 51.0315 | 120.7764 | 123.8297 | 0.55389 | 123.8159 | 72.0978 | -0.27008 | 123.8297 | 0.55389 | 72.0978 | 120.7764 | 123.8159 | -124.0631 | -124.1318
1222.7188 | 124.0906 | -61.0977 | 62.6953 | 0.15892 | 0.012179 | 0.009141 | 0.0014248 | 0.070502 | 0.00094847 | 0.072854 | -60.6079 | 62.6907 | -61.3312 | -61.3174 | 59.6375 | 11.1694 | -9.8694 | -9.8328 | 62.6907 | -61.3586 | -0.23346 | -0.004577 | 0.48981 | -0.21973 | -3.0579 | -0.26093 | -0.004577 | 0.72327 | 51.2283 | 51.265 | 120.7352 | 123.7885 | 0.48981 | 123.7885 | 72.2672 | -0.26093 | 123.7885 | 0.48981 | 72.2672 | 120.7352 | 123.7885 | -124.0265 | -124.054
1223.7188 | 124.0173 | -61.1114 | 62.7411 | -0.039444 | 0.010256 | 0.014909 | 0.0048428 | 0.066016 | -0.00097413 | 0.073708 | -60.5301 | 62.7182 | -61.3083 | -61.2762 | 59.642 | 11.3709 | -9.5444 | -9.5169 | 62.7045 | -61.3724 | -0.19684 | -0.022888 | 0.58136 | -0.1648 | -3.0991 | -0.26093 | -0.036621 | 0.7782 | 51.5671 | 51.5945 | 120.7535 | 123.8297 | 0.58136 | 123.8159 | 72.4823 | -0.26093 | 123.8297 | 0.58136 | 72.4823 | 120.7535 | 123.8159 | -124.0494 | -124.1135
1224.7188 | 124.0448 | -61.1252 | 62.709 | -1.3593 | 0.010256 | 0.014268 | 0.0037746 | 0.067939 | -0.00076053 | 0.07264 | -60.585 | 62.7045 | -61.2946 | -61.2625 | 59.6283 | 11.586 | -9.2514 | -9.2285 | 62.677 | -61.3678 | -0.16937 | -0.004577 | 0.54016 | -0.13733 | -3.0807 | -0.24262 | -0.032043 | 0.70953 | 51.8738 | 51.8967 | 120.7535 | 123.8297 | 0.54016 | 123.8022 | 72.7112 | -0.24262 | 123.8297 | 0.54016 | 72.7112 | 120.7535 | 123.8022 | -124.0036 | -124.0768
1225.7188 | 124.0448 | -61.1023 | 62.7045 | -0.062332 | 0.0098287 | 0.014909 | 0.0033474 | 0.065802 | 9.4068e-05 | 0.072213 | -60.5255 | 62.7045 | -61.322 | -61.3403 | 59.4543 | 11.6089 | -8.8943 | -8.9767 | 62.6678 | -61.4136 | -0.21973 | 0 | 0.57678 | -0.23804 | -3.2501 | -0.31128 | -0.036621 | 0.79651 | 52.2079 | 52.1255 | 120.5566 | 123.8068 | 0.57678 | 123.7701 | 72.7112 | -0.31128 | 123.8068 | 0.57678 | 72.7112 | 120.5566 | 123.7701 | -124.0265 | -124.118
1226.7188 | 124.0585 | -61.1572 | 62.6953 | -0.11574 | 0.011324 | 0.011277 | 0.001852 | 0.066657 | -0.00011953 | 0.071145 | -60.5392 | 62.7182 | -61.322 | -61.2854 | 59.5963 | 11.9247 | -8.7296 | -8.6746 | 62.6907 | -61.377 | -0.16479 | 0.022889 | 0.61798 | -0.12817 | -3.0991 | -0.21973 | -0.004577 | 0.78278 | 52.4277 | 52.4826 | 120.7535 | 123.8754 | 0.61798 | 123.848 | 73.082 | -0.21973 | 123.8754 | 0.61798 | 73.082 | 120.7535 | 123.848 | -124.0173 | -124.0723
1227.7188 | 124.0356 | -61.1114 | 62.7182 | -0.17677 | 0.0094015 | 0.013627 | 0.00099764 | 0.06687 | -0.0020421 | 0.074349 | -60.5576 | 62.7045 | -61.3449 | -61.3312 | 59.5551 | 12.085 | -8.3679 | -8.4503 | 62.709 | -61.377 | -0.23346 | -0.013733 | 0.55389 | -0.21973 | -3.1631 | -0.2655 | -0.009156 | 0.78735 | 52.7435 | 52.6611 | 120.6665 | 123.8159 | 0.55389 | 123.8205 | 73.1964 | -0.2655 | 123.8159 | 0.55389 | 73.1964 | 120.6665 | 123.8205 | -124.0631 | -124.0952
1228.7188 | 124.0128 | -61.1389 | 62.7228 | -0.23018 | 0.0094015 | 0.012559 | 0.0029202 | 0.067511 | -0.00033333 | 0.074136 | -60.5621 | 62.6724 | -61.3449 | -61.3403 | 59.5551 | 12.2635 | -8.139 | -8.2031 | 62.7274 | -61.3998 | -0.20599 | -0.050354 | 0.57678 | -0.20142 | -3.1677 | -0.26093 | 0.004578 | 0.78278 | 52.9999 | 52.9358 | 120.694 | 123.8113 | 0.57678 | 123.8663 | 73.4024 | -0.26093 | 123.8113 | 0.57678 | 73.4024 | 120.694 | 123.8663 | -124.0677 | -124.1226
1229.7188 | 124.0723 | -61.1252 | 62.6678 | -0.077591 | 0.0096151 | 0.011918 | 0.004202 | 0.068579 | -0.0016149 | 0.072854 | -60.5209 | 62.6816 | -61.3495 | -61.2991 | 59.5551 | 12.4512 | -7.9422 | -7.9056 | 62.6907 | -61.409 | -0.2243 | 0.013733 | 0.60425 | -0.17395 | -3.1128 | -0.28381 | 0.022888 | 0.82855 | 53.183 | 53.2196 | 120.6802 | 123.8068 | 0.60425 | 123.8159 | 73.5764 | -0.28381 | 123.8068 | 0.60425 | 73.5764 | 120.6802 | 123.8159 | -124.0173 | -124.0768
1230.7188 | 124.0494 | -61.1481 | 62.6816 | -0.14626 | 0.0087607 | 0.014482 | 0.0029202 | 0.067511 | 0.00030767 | 0.072854 | -60.498 | 62.677 | -61.3678 | -61.2946 | 59.5322 | 12.5793 | -7.6492 | -7.6218 | 62.6907 | -61.409 | -0.21973 | -0.004578 | 0.65002 | -0.14648 | -3.1494 | -0.26093 | 0.009155 | 0.86975 | 53.4988 | 53.5263 | 120.6802 | 123.8251 | 0.65002 | 123.8388 | 73.7274 | -0.26093 | 123.8251 | 0.65002 | 73.7274 | 120.6802 | 123.8388 | -124.0494 | -124.0906
1231.7188 | 124.0311 | -61.1572 | 62.6724 | -0.12337 | 0.010683 | 0.012132 | 0.0027066 | 0.067725 | -0.0028967 | 0.07264 | -60.5118 | 62.677 | -61.3724 | -61.3174 | 59.5139 | 12.7716 | -7.3792 | -7.3837 | 62.6907 | -61.4136 | -0.21515 | 0.004578 | 0.64545 | -0.16022 | -3.1586 | -0.25635 | 0.018311 | 0.86059 | 53.7781 | 53.7735 | 120.6711 | 123.8342 | 0.64545 | 123.848 | 73.9288 | -0.25635 | 123.8342 | 0.64545 | 73.9288 | 120.6711 | 123.848 | -124.0448 | -124.086
1232.7188 | 124.0448 | -61.1435 | 62.6587 | 0.18181 | 0.010683 | 0.0132 | 0.00099764 | 0.069007 | 0.00073487 | 0.074563 | -60.5759 | 62.6266 | -61.3998 | -61.3907 | 59.4498 | 12.886 | -7.251 | -7.1594 | 62.6038 | -61.4227 | -0.25635 | -0.032043 | 0.56763 | -0.24719 | -3.2089 | -0.27923 | -0.054931 | 0.82397 | 53.8925 | 53.9841 | 120.5933 | 123.7701 | 0.56763 | 123.7473 | 74.0295 | -0.27923 | 123.7701 | 0.56763 | 74.0295 | 120.5933 | 123.7473 | -124.0585 | -124.0814
1233.7188 | 124.0631 | -61.1526 | 62.6816 | -0.16151 | 0.011538 | 0.011491 | 0.0029202 | 0.06687 | 0.00030767 | 0.07264 | -60.5392 | 62.6816 | -61.3953 | -61.3312 | 59.4818 | 13.1241 | -6.9672 | -6.9122 | 62.645 | -61.4182 | -0.24262 | 0 | 0.6134 | -0.17853 | -3.1998 | -0.2655 | -0.036622 | 0.85602 | 54.1855 | 54.2404 | 120.6345 | 123.8342 | 0.6134 | 123.7976 | 74.2767 | -0.2655 | 123.8342 | 0.6134 | 74.2767 | 120.6345 | 123.7976 | -124.0768 | -124.0997
1234.7344 | 124.1272 | -61.171 | 62.6038 | 0.24284 | 0.0076925 | 0.011064 | 0.00057044 | 0.067298 | -0.0011877 | 0.074777 | -60.672 | 62.5076 | -61.4182 | -61.3495 | 59.5047 | 13.3621 | -6.9946 | -6.633 | 62.5626 | -61.4182 | -0.24719 | -0.096131 | 0.49896 | -0.17853 | -3.0991 | -0.24719 | -0.041199 | 0.74616 | 54.1763 | 54.538 | 120.6757 | 123.6786 | 0.49896 | 123.7335 | 74.5331 | -0.24719 | 123.6786 | 0.49896 | 74.5331 | 120.6757 | 123.7335 | -124.0219 | -124.0219
1235.7188 | 124.0723 | -61.1938 | 62.677 | -0.23018 | 0.0094015 | 0.0099954 | 0.0044156 | 0.065589 | -0.00033333 | 0.071786 | -60.5255 | 62.645 | -61.4044 | -61.3586 | 59.4543 | 13.4491 | -6.4819 | -6.3766 | 62.6724 | -61.409 | -0.21057 | -0.032044 | 0.66834 | -0.16479 | -3.2227 | -0.21515 | -0.004578 | 0.87891 | 54.7119 | 54.8172 | 120.6482 | 123.8388 | 0.66834 | 123.8663 | 74.6429 | -0.21515 | 123.8388 | 0.66834 | 74.6429 | 120.6482 | 123.8663 | -124.0814 | -124.086
1236.7188 | 124.0311 | -61.171 | 62.6541 | -0.054703 | 0.0083333 | 0.017259 | 0.0078336 | 0.069434 | -0.0011877 | 0.070077 | -60.5026 | 62.6083 | -61.3953 | -61.3266 | 59.4315 | 13.6642 | -6.2622 | -6.1478 | 62.6129 | -61.4594 | -0.2243 | -0.045777 | 0.66833 | -0.15564 | -3.2227 | -0.28839 | -0.041199 | 0.89264 | 54.9088 | 55.0232 | 120.6024 | 123.7793 | 0.66833 | 123.7839 | 74.8352 | -0.28839 | 123.7793 | 0.66833 | 74.8352 | 120.6024 | 123.7839 | -124.0494 | -124.1135
1237.7188 | 124.0082 | -61.1984 | 62.6175 | 0.21996 | 0.01282 | 0.010423 | 0.00527 | 0.067298 | -0.00097413 | 0.073922 | -60.5713 | 62.5763 | -61.441 | -61.4502 | 59.3399 | 13.7695 | -6.0333 | -6.0059 | 62.6175 | -61.4639 | -0.24262 | -0.041199 | 0.62714 | -0.25177 | -3.2776 | -0.2655 | 0 | 0.86975 | 55.1651 | 55.1926 | 120.5383 | 123.7747 | 0.62714 | 123.8159 | 74.968 | -0.2655 | 123.7747 | 0.62714 | 74.968 | 120.5383 | 123.8159 | -124.0585 | -124.0814
1238.7188 | 124.0494 | -61.203 | 62.6312 | 0.029221 | 0.010256 | 0.0093546 | 0.0044156 | 0.06687 | 0.00052127 | 0.072854 | -60.4614 | 62.6587 | -61.4182 | -61.3632 | 59.3903 | 14.0076 | -5.7266 | -5.658 | 62.6175 | -61.4685 | -0.21515 | 0.027465 | 0.74158 | -0.16022 | -3.241 | -0.2655 | -0.013733 | 0.95673 | 55.4764 | 55.545 | 120.5933 | 123.8617 | 0.74158 | 123.8205 | 75.2106 | -0.2655 | 123.8617 | 0.74158 | 75.2106 | 120.5933 | 123.8205 | -124.0494 | -124.0997
1239.7188 | 124.0677 | -61.1984 | 62.59 | 0.18181 | 0.01047 | 0.013841 | -0.002634 | 0.066443 | 0.0013757 | 0.073708 | -60.5347 | 62.5031 | -61.4273 | -61.409 | 59.3903 | 14.2044 | -5.5984 | -5.4108 | 62.5946 | -61.4182 | -0.22888 | -0.086975 | 0.66376 | -0.21057 | -3.1998 | -0.21973 | 0.004577 | 0.89264 | 55.6 | 55.7877 | 120.5887 | 123.7015 | 0.66376 | 123.793 | 75.4028 | -0.21973 | 123.7015 | 0.66376 | 75.4028 | 120.5887 | 123.793 | -124.0173 | -124.0082
1240.7188 | 124.0448 | -61.2122 | 62.6221 | -0.09285 | 0.0096151 | 0.011491 | 0.0056972 | 0.066443 | -0.00097413 | 0.071572 | -60.4752 | 62.6495 | -61.3998 | -61.3678 | 59.3674 | 14.3555 | -5.2231 | -5.1682 | 62.5809 | -61.4548 | -0.18768 | 0.027466 | 0.737 | -0.15564 | -3.2547 | -0.24262 | -0.041198 | 0.92468 | 55.9891 | 56.044 | 120.5795 | 123.8617 | 0.737 | 123.793 | 75.5676 | -0.24262 | 123.8617 | 0.737 | 75.5676 | 120.5795 | 123.793 | -124.0219 | -124.0768
1241.7188 | 124.054 | -61.2213 | 62.6221 | -0.1844 | 0.010042 | 0.0132 | 0.0056972 | 0.067939 | -0.0022559 | 0.070931 | -60.5164 | 62.6312 | -61.4319 | -61.3907 | 59.3445 | 14.4516 | -4.9164 | -4.953 | 62.5992 | -61.4777 | -0.21057 | 0.009156 | 0.70496 | -0.16937 | -3.2776 | -0.25635 | -0.022888 | 0.91553 | 56.3049 | 56.2683 | 120.5658 | 123.8525 | 0.70496 | 123.8205 | 75.6729 | -0.25635 | 123.8525 | 0.70496 | 75.6729 | 120.5658 | 123.8205 | -124.054 | -124.0997
1242.7188 | 123.9899 | -61.2488 | 62.5992 | 0.082626 | 0.010256 | 0.011491 | 0.005911 | 0.067939 | 9.4068e-05 | 0.072427 | -60.5621 | 62.59 | -61.4777 | -61.496 | 59.2346 | 14.6255 | -4.7424 | -4.8203 | 62.5854 | -61.5189 | -0.22888 | -0.009155 | 0.68664 | -0.24719 | -3.3646 | -0.27008 | -0.013733 | 0.91553 | 56.5063 | 56.4285 | 120.4834 | 123.8388 | 0.68664 | 123.8342 | 75.8743 | -0.27008 | 123.8388 | 0.68664 | 75.8743 | 120.4834 | 123.8342 | -124.0768 | -124.118
1243.7188 | 124.0356 | -61.235 | 62.6083 | 0.28099 | 0.0098287 | 0.012132 | 0.00527 | 0.068366 | -0.00011953 | 0.074136 | -60.4568 | 62.5763 | -61.4319 | -61.3998 | 59.3216 | 14.8911 | -4.5273 | -4.5319 | 62.558 | -61.5051 | -0.19684 | -0.032043 | 0.7782 | -0.1648 | -3.2867 | -0.27008 | -0.050354 | 0.97504 | 56.7078 | 56.7032 | 120.5566 | 123.8113 | 0.7782 | 123.793 | 76.1261 | -0.27008 | 123.8113 | 0.7782 | 76.1261 | 120.5566 | 123.793 | -124.0402 | -124.1135
1244.7344 | 124.0814 | -61.2167 | 62.5397 | 0.14366 | 0.0085471 | 0.013841 | 0.0012112 | 0.068152 | -0.00076053 | 0.074349 | -60.4797 | 62.4664 | -61.4685 | -61.3861 | 59.3536 | 15.1291 | -4.4495 | -4.2526 | 62.5168 | -61.4594 | -0.25177 | -0.073242 | 0.737 | -0.16937 | -3.186 | -0.24262 | -0.022888 | 0.98877 | 56.7673 | 56.9641 | 120.5704 | 123.6832 | 0.737 | 123.7335 | 76.3458 | -0.24262 | 123.6832 | 0.737 | 76.3458 | 120.5704 | 123.7335 | -124.0082 | -123.999
1245.7188 | 124.054 | -61.2442 | 62.5671 | -0.15388 | 0.0096151 | 0.014695 | 0.0061246 | 0.067084 | 9.4068e-05 | 0.073708 | -60.4477 | 62.5854 | -61.4273 | -61.4182 | 59.2987 | 15.2756 | -4.0466 | -4.0833 | 62.558 | -61.528 | -0.1831 | 0.01831 | 0.79651 | -0.17395 | -3.2684 | -0.28381 | -0.009156 | 0.97961 | 57.1976 | 57.1609 | 120.5429 | 123.8297 | 0.79651 | 123.8022 | 76.5198 | -0.28381 | 123.8297 | 0.79651 | 76.5198 | 120.5429 | 123.8022 | -123.9944 | -124.0952
1246.7188 | 124.0128 | -61.235 | 62.5717 | -0.11574 | 0.011111 | 0.015977 | 0.005911 | 0.068366 | 9.4068e-05 | 0.072854 | -60.4568 | 62.5717 | -61.441 | -61.4273 | 59.2758 | 15.4449 | -3.8269 | -3.8498 | 62.558 | -61.528 | -0.20599 | 0 | 0.7782 | -0.19226 | -3.2959 | -0.29297 | -0.013733 | 0.98419 | 57.4081 | 57.3853 | 120.5109 | 123.8068 | 0.7782 | 123.793 | 76.68 | -0.29297 | 123.8068 | 0.7782 | 76.68 | 120.5109 | 123.793 | -124.0128 | -124.0997
1247.7188 | 124.0173 | -61.2762 | 62.5763 | 0.17418 | 0.011751 | 0.011277 | 0.004202 | 0.067511 | -0.00054693 | 0.074136 | -60.553 | 62.5534 | -61.496 | -61.4914 | 59.198 | 15.5365 | -3.6255 | -3.6987 | 62.5442 | -61.5509 | -0.21973 | -0.022888 | 0.72327 | -0.21515 | -3.3783 | -0.27466 | -0.032044 | 0.94299 | 57.6508 | 57.5775 | 120.4742 | 123.8297 | 0.72327 | 123.8205 | 76.8127 | -0.27466 | 123.8297 | 0.72327 | 76.8127 | 120.4742 | 123.8205 | -124.0723 | -124.1272
1248.7188 | 124.0448 | -61.2534 | 62.5717 | -0.12337 | 0.011324 | 0.011491 | 0.0050564 | 0.067511 | -0.00011953 | 0.071572 | -60.4706 | 62.5809 | -61.4731 | -61.3998 | 59.2621 | 15.715 | -3.4195 | -3.4241 | 62.5305 | -61.5326 | -0.21973 | 0.009156 | 0.78278 | -0.14648 | -3.3096 | -0.27924 | -0.041198 | 1.0025 | 57.8339 | 57.8293 | 120.5154 | 123.8342 | 0.78278 | 123.7839 | 76.9684 | -0.27924 | 123.8342 | 0.78278 | 76.9684 | 120.5154 | 123.7839 | -124.0448 | -124.1043
1249.7344 | 124.0997 | -61.2534 | 62.5259 | -1.0847 | 0.010042 | 0.009141 | -0.0049838 | 0.065161 | 0.00030767 | 0.073495 | -60.5438 | 62.4847 | -61.4731 | -61.4685 | 59.2484 | 15.8707 | -3.2867 | -3.2181 | 62.5305 | -61.4777 | -0.21973 | -0.041199 | 0.70953 | -0.21515 | -3.2776 | -0.2243 | 0.004578 | 0.92926 | 57.9666 | 58.0353 | 120.5017 | 123.7381 | 0.70953 | 123.7839 | 77.124 | -0.2243 | 123.7381 | 0.70953 | 77.124 | 120.5017 | 123.7839 | -123.999 | -124.0036
1250.7188 | 123.9807 | -61.2991 | 62.5626 | -0.0012969 | 0.010683 | 0.011918 | 0.0080472 | 0.065802 | -0.0018285 | 0.070931 | -60.4935 | 62.5397 | -61.5097 | -61.4914 | 59.1568 | 15.9531 | -2.9709 | -3.0991 | 62.5397 | -61.5555 | -0.21057 | -0.022888 | 0.80566 | -0.19226 | -3.4058 | -0.25635 | -0.022888 | 1.0162 | 58.3282 | 58.2001 | 120.4559 | 123.8388 | 0.80566 | 123.8388 | 77.2522 | -0.25635 | 123.8388 | 0.80566 | 77.2522 | 120.4559 | 123.8388 | -124.0723 | -124.118
1251.7188 | 124.0036 | -61.2946 | 62.5397 | 0.013962 | 0.0098287 | 0.01555 | 0.0048428 | 0.066443 | -0.0022559 | 0.074136 | -60.4797 | 62.5534 | -61.4777 | -61.4914 | 59.1614 | 16.0767 | -2.7924 | -2.916 | 62.5351 | -61.5509 | -0.1831 | 0.013733 | 0.81482 | -0.19684 | -3.3783 | -0.25635 | -0.004578 | 0.99792 | 58.5022 | 58.3786 | 120.4559 | 123.848 | 0.81482 | 123.8297 | 77.3712 | -0.25635 | 123.848 | 0.81482 | 77.3712 | 120.4559 | 123.8297 | -124.0173 | -124.0906
1252.7188 | 124.1089 | -61.2625 | 62.5031 | 0.24284 | 0.0098287 | 0.0097818 | 0.0027066 | 0.065802 | -0.0028967 | 0.072427 | -60.4889 | 62.4893 | -61.5051 | -61.4548 | 59.2026 | 16.3284 | -2.7557 | -2.6733 | 62.4802 | -61.5326 | -0.24262 | -0.013733 | 0.77362 | -0.19226 | -3.3005 | -0.27008 | -0.022888 | 1.0162 | 58.5068 | 58.5892 | 120.4651 | 123.7518 | 0.77362 | 123.7427 | 77.5909 | -0.27008 | 123.7518 | 0.77362 | 77.5909 | 120.4651 | 123.7427 | -124.0082 | -124.0356
1253.7188 | 123.9716 | -61.2946 | 62.5305 | 0.052109 | 0.011965 | 0.013413 | 0.0082608 | 0.068152 | 0.00030767 | 0.071786 | -60.5026 | 62.558 | -61.5189 | -61.4822 | 59.1248 | 16.4017 | -2.4033 | -2.6001 | 62.5076 | -61.5692 | -0.2243 | 0.027465 | 0.79193 | -0.18768 | -3.4058 | -0.27466 | -0.022889 | 1.0162 | 58.8913 | 58.6945 | 120.4193 | 123.8525 | 0.79193 | 123.8022 | 77.6962 | -0.27466 | 123.8525 | 0.79193 | 77.6962 | 120.4193 | 123.8022 | -124.0494 | -124.0997
1254.7188 | 124.1455 | -61.2534 | 62.5122 | -0.12337 | 0.0072653 | 0.011704 | -0.001566 | 0.064734 | -0.00054693 | 0.073281 | -60.4202 | 62.4664 | -61.4914 | -61.4044 | 59.2758 | 16.7038 | -2.3209 | -2.1744 | 62.4847 | -61.5097 | -0.23804 | -0.045776 | 0.83313 | -0.15106 | -3.2364 | -0.25635 | -0.027466 | 1.0712 | 58.9325 | 59.079 | 120.5292 | 123.7198 | 0.83313 | 123.7381 | 77.9572 | -0.25635 | 123.7198 | 0.83313 | 77.9572 | 120.5292 | 123.7381 | -124.0036 | -124.0219
1255.7188 | 124.0082 | -61.3037 | 62.5351 | -0.077591 | 0.011965 | 0.011704 | 0.0084744 | 0.069648 | -0.00033333 | 0.07264 | -60.4065 | 62.5214 | -61.4914 | -61.4548 | 59.1568 | 16.7267 | -2.0325 | -2.1286 | 62.5351 | -61.5555 | -0.18768 | -0.013733 | 0.89722 | -0.15106 | -3.3783 | -0.25177 | 0 | 1.0849 | 59.2712 | 59.1751 | 120.4605 | 123.8251 | 0.89722 | 123.8388 | 78.0304 | -0.25177 | 123.8251 | 0.89722 | 78.0304 | 120.4605 | 123.8388 | -124.0265 | -124.0906
1256.7188 | 124.0494 | -61.29 | 62.5442 | -0.024185 | 0.011751 | 0.0093546 | 0.0063382 | 0.067511 | -0.0026831 | 0.073068 | -60.4111 | 62.5305 | -61.5143 | -61.4822 | 59.1385 | 16.832 | -1.8997 | -1.9775 | 62.5259 | -61.5601 | -0.2243 | -0.013732 | 0.87891 | -0.19226 | -3.4058 | -0.27008 | -0.01831 | 1.1032 | 59.3903 | 59.3124 | 120.4285 | 123.8205 | 0.87891 | 123.8159 | 78.1219 | -0.27008 | 123.8205 | 0.87891 | 78.1219 | 120.4285 | 123.8159 | -124.0585 | -124.1043
1257.7188 | 123.9212 | -61.3632 | 62.4939 | 0.097885 | 0.011111 | 0.01555 | 0.0037746 | 0.067725 | -0.00033333 | 0.073922 | -60.5026 | 62.5351 | -61.5646 | -61.5463 | 59.0607 | 16.8961 | -1.7532 | -1.9638 | 62.5031 | -61.5921 | -0.20142 | 0.041199 | 0.86059 | -0.18311 | -3.4332 | -0.22888 | 0.009156 | 1.062 | 59.61 | 59.3994 | 120.4239 | 123.8983 | 0.86059 | 123.8663 | 78.2593 | -0.22888 | 123.8983 | 0.86059 | 78.2593 | 120.4239 | 123.8663 | -124.0585 | -124.086
1258.7188 | 123.912 | -61.3358 | 62.471 | 0.12077 | 0.012179 | 0.01085 | 0.0048428 | 0.06623 | -0.00076053 | 0.072427 | -60.5026 | 62.5168 | -61.528 | -61.5555 | 59.0515 | 16.9968 | -1.5839 | -1.7761 | 62.4985 | -61.6058 | -0.19226 | 0.045777 | 0.83313 | -0.21973 | -3.4195 | -0.27008 | 0.027466 | 1.0254 | 59.7519 | 59.5596 | 120.3873 | 123.8525 | 0.83313 | 123.8342 | 78.3325 | -0.27008 | 123.8525 | 0.83313 | 78.3325 | 120.3873 | 123.8342 | -123.999 | -124.0768
1259.7188 | 123.9487 | -61.3724 | 62.4985 | 0.16655 | 0.01282 | 0.015122 | 0.0067654 | 0.06922 | 0.00030767 | 0.073281 | -60.5209 | 62.5031 | -61.5463 | -61.5555 | 59.024 | 17.1112 | -1.442 | -1.6342 | 62.4847 | -61.6104 | -0.17395 | 0.004578 | 0.85144 | -0.18311 | -3.4744 | -0.23804 | -0.013733 | 1.0254 | 59.9304 | 59.7382 | 120.3964 | 123.8754 | 0.85144 | 123.8571 | 78.4836 | -0.23804 | 123.8754 | 0.85144 | 78.4836 | 120.3964 | 123.8571 | -124.0448 | -124.1089
1260.7188 | 123.9716 | -61.3861 | 62.5076 | 0.097885 | 0.01282 | 0.013841 | 0.005911 | 0.068152 | 0.0018031 | 0.073708 | -60.5072 | 62.5214 | -61.5692 | -61.5692 | 59.0378 | 17.2623 | -1.268 | -1.4786 | 62.4527 | -61.6516 | -0.18311 | 0.013733 | 0.87891 | -0.18311 | -3.4698 | -0.2655 | -0.054931 | 1.062 | 60.1181 | 59.9075 | 120.4239 | 123.9075 | 0.87891 | 123.8388 | 78.6484 | -0.2655 | 123.9075 | 0.87891 | 78.6484 | 120.4239 | 123.8388 | -124.0768 | -124.1592
1261.7188 | 123.9349 | -61.3541 | 62.4619 | 0.097885 | 0.011324 | 0.014482 | 0.0071926 | 0.06623 | 0.00052127 | 0.073281 | -60.4935 | 62.4847 | -61.5601 | -61.5875 | 59.0195 | 17.363 | -1.1215 | -1.3412 | 62.4939 | -61.6058 | -0.20599 | 0.022888 | 0.8606 | -0.23346 | -3.4424 | -0.25177 | 0.032043 | 1.0666 | 60.2325 | 60.0128 | 120.3735 | 123.8388 | 0.8606 | 123.848 | 78.717 | -0.25177 | 123.8388 | 0.8606 | 78.717 | 120.3735 | 123.848 | -124.0219 | -124.0677
1262.7188 | 124.0036 | -61.3495 | 62.4985 | 0.18944 | 0.011324 | 0.014482 | 0.0031338 | 0.06687 | -0.00033333 | 0.072427 | -60.498 | 62.471 | -61.5784 | -61.5692 | 59.0149 | 17.5095 | -0.97961 | -1.1856 | 62.4619 | -61.615 | -0.22888 | -0.027466 | 0.85144 | -0.21973 | -3.4836 | -0.2655 | -0.036621 | 1.0803 | 60.3699 | 60.1639 | 120.3644 | 123.8205 | 0.85144 | 123.8113 | 78.8589 | -0.2655 | 123.8205 | 0.85144 | 78.8589 | 120.3644 | 123.8113 | -124.0768 | -124.1135
1263.7188 | 123.999 | -61.3358 | 62.5031 | 0.03685 | 0.011111 | 0.014054 | 0.0031338 | 0.067511 | -0.0016149 | 0.075204 | -60.4523 | 62.4985 | -61.528 | -61.5463 | 59.024 | 17.6376 | -0.81024 | -0.99792 | 62.4573 | -61.5921 | -0.19226 | -0.004578 | 0.88348 | -0.21057 | -3.479 | -0.25635 | -0.045777 | 1.0757 | 60.5255 | 60.3378 | 120.3598 | 123.8342 | 0.88348 | 123.793 | 78.9734 | -0.25635 | 123.8342 | 0.88348 | 78.9734 | 120.3598 | 123.793 | -124.0311 | -124.0952
1264.7188 | 124.0036 | -61.3678 | 62.4939 | 0.18181 | 0.012606 | 0.01085 | 0.0029202 | 0.069007 | 0.00030767 | 0.073922 | -60.4706 | 62.4847 | -61.5921 | -61.5784 | 58.9874 | 17.7292 | -0.65918 | -0.91095 | 62.4847 | -61.6241 | -0.2243 | -0.009155 | 0.89722 | -0.21057 | -3.5065 | -0.25635 | -0.009155 | 1.1215 | 60.7086 | 60.4568 | 120.3552 | 123.8525 | 0.89722 | 123.8525 | 79.097 | -0.25635 | 123.8525 | 0.89722 | 79.097 | 120.3552 | 123.8525 | -124.086 | -124.118
1265.7188 | 124.0219 | -61.3541 | 62.4985 | 0.41832 | 0.011965 | 0.0076456 | 0.005911 | 0.069007 | -0.0016149 | 0.076699 | -60.4477 | 62.4802 | -61.5509 | -61.5784 | 58.96 | 17.807 | -0.50354 | -0.75989 | 62.4802 | -61.6196 | -0.19684 | -0.01831 | 0.90637 | -0.2243 | -3.5385 | -0.2655 | -0.01831 | 1.1032 | 60.8505 | 60.5942 | 120.314 | 123.8342 | 0.90637 | 123.8342 | 79.1611 | -0.2655 | 123.8342 | 0.90637 | 79.1611 | 120.314 | 123.8342 | -124.0494 | -124.118
1266.7188 | 123.9944 | -61.3632 | 62.4802 | 0.50224 | 0.014956 | 0.0082864 | 0.0054836 | 0.067298 | 0.0018031 | 0.075845 | -60.4614 | 62.4756 | -61.5875 | -61.5967 | 58.9691 | 17.9214 | -0.3479 | -0.63171 | 62.4252 | -61.6196 | -0.2243 | -0.004578 | 0.90179 | -0.23346 | -3.511 | -0.25635 | -0.054932 | 1.1261 | 61.0153 | 60.7315 | 120.3323 | 123.8388 | 0.90179 | 123.7885 | 79.2847 | -0.25635 | 123.8388 | 0.90179 | 79.2847 | 120.3323 | 123.7885 | -124.0677 | -124.0997
1267.7188 | 124.0814 | -61.3678 | 62.471 | 0.18944 | 0.012179 | 0.011918 | 0.0039882 | 0.068579 | 0.0011621 | 0.073922 | -60.466 | 62.471 | -61.6013 | -61.5692 | 58.9691 | 18.0313 | -0.21515 | -0.46234 | 62.4252 | -61.615 | -0.23346 | 0 | 0.90179 | -0.20142 | -3.5019 | -0.24719 | -0.045776 | 1.1353 | 61.1526 | 60.9055 | 120.3369 | 123.8388 | 0.90179 | 123.793 | 79.3991 | -0.24719 | 123.8388 | 0.90179 | 79.3991 | 120.3369 | 123.793 | -124.0723 | -124.086
1268.7188 | 123.9899 | -61.3724 | 62.4802 | 0.15892 | 0.012179 | 0.013627 | 0.00527 | 0.06687 | 0.00030767 | 0.077767 | -60.4797 | 62.4802 | -61.5875 | -61.908 | 58.7219 | 18.306 | 0.07782 | -0.40741 | 62.4619 | -61.615 | -0.21515 | 0 | 0.89264 | -0.53558 | -3.7582 | -0.24262 | -0.018311 | 1.1078 | 61.4502 | 60.965 | 120.0943 | 123.8525 | 0.89264 | 123.8342 | 79.6783 | -0.24262 | 123.8525 | 0.89264 | 79.6783 | 120.0943 | 123.8342 | -124.0677 | -124.0952
1269.7188 | 123.999 | -61.3586 | 62.471 | 0.0063326 | 0.011751 | 0.014054 | 0.0067654 | 0.067725 | -0.0016149 | 0.07264 | -60.4202 | 62.471 | -61.5601 | -61.5692 | 58.96 | 18.1961 | 0.12817 | -0.17853 | 62.4573 | -61.647 | -0.20142 | 0 | 0.93842 | -0.21057 | -3.511 | -0.28839 | -0.013733 | 1.1398 | 61.4868 | 61.1801 | 120.3186 | 123.8297 | 0.93842 | 123.8159 | 79.5547 | -0.28839 | 123.8297 | 0.93842 | 79.5547 | 120.3186 | 123.8159 | -124.0311 | -124.118
1270.7188 | 123.9395 | -61.3678 | 62.4573 | 0.067368 | 0.011965 | 0.012986 | 0.00527 | 0.065589 | 9.4068e-05 | 0.074349 | -60.4706 | 62.471 | -61.5921 | -61.6104 | 58.9005 | 18.2373 | 0.27466 | -0.10529 | 62.4207 | -61.6791 | -0.2243 | 0.013733 | 0.89722 | -0.24262 | -3.5568 | -0.31128 | -0.036621 | 1.1215 | 61.6425 | 61.2625 | 120.2682 | 123.8388 | 0.89722 | 123.7885 | 79.6051 | -0.31128 | 123.8388 | 0.89722 | 79.6051 | 120.2682 | 123.7885 | -124.0494 | -124.1364
1271.7188 | 124.0265 | -61.3815 | 62.4664 | 2.0663 | 0.011965 | 0.0093546 | 0.0022794 | 0.067084 | -0.0024695 | 0.073281 | -60.1868 | 62.4069 | -61.6196 | -61.5875 | 58.9325 | 18.3701 | 0.37994 | 0.032043 | 62.439 | -61.6745 | -0.23804 | -0.05951 | 1.1948 | -0.20599 | -3.5339 | -0.29297 | -0.027466 | 1.4328 | 61.7615 | 61.4136 | 120.314 | 123.7885 | 1.1948 | 123.8205 | 79.7516 | -0.29297 | 123.7885 | 1.1948 | 79.7516 | 120.314 | 123.8205 | -124.086 | -124.1409
1272.7188 | 124.0952 | -61.3403 | 62.3978 | 0.15892 | 0.0098287 | 0.013413 | -0.0013522 | 0.065589 | 0.00030767 | 0.075204 | -60.3699 | 62.3703 | -61.5509 | -61.5234 | 58.992 | 18.5303 | 0.32501 | 0.27466 | 62.3978 | -61.5829 | -0.21057 | -0.027466 | 0.97046 | -0.18311 | -3.4058 | -0.24262 | 0 | 1.181 | 61.6653 | 61.615 | 120.3323 | 123.7106 | 0.97046 | 123.7381 | 79.8706 | -0.24262 | 123.7106 | 0.97046 | 79.8706 | 120.3323 | 123.7381 | -123.9487 | -123.9807
1273.7188 | 123.9624 | -61.3998 | 62.4573 | 0.097885 | 0.01282 | 0.015763 | 0.00527 | 0.065589 | 0.00094847 | 0.073922 | -60.4523 | 62.4664 | -61.5967 | -61.6333 | 58.8547 | 18.4982 | 0.59967 | 0.28381 | 62.4344 | -61.6791 | -0.19684 | 0.009156 | 0.94757 | -0.23346 | -3.6026 | -0.27924 | -0.022888 | 1.1444 | 61.9995 | 61.6837 | 120.2545 | 123.8663 | 0.94757 | 123.8342 | 79.8981 | -0.27924 | 123.8663 | 0.94757 | 79.8981 | 120.2545 | 123.8342 | -124.054 | -124.1364
1274.7188 | 123.9853 | -61.3495 | 62.4756 | 0.097885 | 0.0085471 | 0.017899 | 0.0078336 | 0.064948 | -0.0018285 | 0.072854 | -60.434 | 62.4756 | -61.6241 | -61.6104 | 58.8638 | 18.5577 | 0.6958 | 0.37537 | 62.4344 | -61.6608 | -0.27466 | 0 | 0.91553 | -0.26093 | -3.6118 | -0.31128 | -0.041199 | 1.1902 | 62.0453 | 61.7249 | 120.2133 | 123.8251 | 0.91553 | 123.7839 | 79.9072 | -0.31128 | 123.8251 | 0.91553 | 79.9072 | 120.2133 | 123.7839 | -124.0997 | -124.1364
1275.7188 | 123.9944 | -61.3815 | 62.471 | 0.03685 | 0.012392 | 0.013841 | 0.0065518 | 0.064734 | 0.00073487 | 0.074563 | -60.4202 | 62.4573 | -61.6058 | -61.5829 | 58.8913 | 18.6539 | 0.81482 | 0.49439 | 62.4115 | -61.6653 | -0.2243 | -0.013733 | 0.9613 | -0.20142 | -3.5797 | -0.28381 | -0.059509 | 1.1856 | 62.1964 | 61.8759 | 120.2728 | 123.8388 | 0.9613 | 123.793 | 80.0354 | -0.28381 | 123.8388 | 0.9613 | 80.0354 | 120.2728 | 123.793 | -124.0768 | -124.1364
1276.7188 | 124.0356 | -61.3907 | 62.4573 | -0.131 | 0.013033 | 0.012986 | 0.0061246 | 0.067725 | 0.00030767 | 0.073922 | -60.3424 | 62.4527 | -61.5921 | -61.5326 | 58.9325 | 18.75 | 0.90179 | 0.67291 | 62.4207 | -61.6425 | -0.20142 | -0.004577 | 1.0483 | -0.14191 | -3.5248 | -0.25177 | -0.036621 | 1.2497 | 62.2925 | 62.0636 | 120.3232 | 123.8434 | 1.0483 | 123.8113 | 80.1407 | -0.25177 | 123.8434 | 1.0483 | 80.1407 | 120.3232 | 123.8113 | -124.0494 | -124.0997
1277.7188 | 123.9624 | -61.4044 | 62.4435 | 0.090256 | 0.01047 | 0.014054 | 0.0067654 | 0.069434 | -0.0020421 | 0.074349 | -60.4202 | 62.4527 | -61.615 | -61.6287 | 58.8409 | 18.7225 | 1.0437 | 0.68207 | 62.4207 | -61.6562 | -0.21057 | 0.009156 | 0.98419 | -0.2243 | -3.6026 | -0.25177 | -0.022888 | 1.1948 | 62.4481 | 62.0865 | 120.2454 | 123.8571 | 0.98419 | 123.8251 | 80.127 | -0.25177 | 123.8571 | 0.98419 | 80.127 | 120.2454 | 123.8251 | -124.0585 | -124.0997
1278.7188 | 123.9716 | -61.3953 | 62.4481 | 0.082626 | 0.013674 | 0.012773 | 0.0082608 | 0.067298 | 0.0011621 | 0.074349 | -60.3973 | 62.4481 | -61.6104 | -61.6058 | 58.8547 | 18.8095 | 1.1353 | 0.81482 | 62.439 | -61.6516 | -0.21515 | 0 | 0.99792 | -0.21057 | -3.5934 | -0.25635 | -0.009155 | 1.2131 | 62.5305 | 62.2101 | 120.2499 | 123.8434 | 0.99792 | 123.8342 | 80.2048 | -0.25635 | 123.8434 | 0.99792 | 80.2048 | 120.2499 | 123.8342 | -124.0585 | -124.0997
1279.7188 | 123.9624 | -61.377 | 62.4527 | 0.013962 | 0.015383 | 0.013841 | 0.0065518 | 0.068793 | -0.0028967 | 0.07499 | -60.3882 | 62.4435 | -61.5921 | -61.6058 | 58.8684 | 18.8644 | 1.2131 | 0.92468 | 62.439 | -61.6653 | -0.21515 | -0.009156 | 0.98877 | -0.22888 | -3.5843 | -0.28839 | -0.013733 | 1.2039 | 62.59 | 62.3016 | 120.2454 | 123.8205 | 0.98877 | 123.8159 | 80.2414 | -0.28839 | 123.8205 | 0.98877 | 80.2414 | 120.2454 | 123.8159 | -124.0448 | -124.118
1280.7188 | 123.9899 | -61.3861 | 62.439 | -0.024185 | 0.013888 | 0.014695 | 0.0061246 | 0.067939 | -0.0014013 | 0.072854 | -60.3516 | 62.4252 | -61.6013 | -61.5921 | 58.873 | 18.9377 | 1.2909 | 1.0208 | 62.4115 | -61.6562 | -0.21515 | -0.013733 | 1.0345 | -0.20599 | -3.566 | -0.27008 | -0.027466 | 1.2497 | 62.677 | 62.4069 | 120.2591 | 123.8113 | 1.0345 | 123.7976 | 80.3238 | -0.27008 | 123.8113 | 1.0345 | 80.3238 | 120.2591 | 123.7976 | -124.0402 | -124.0952
1281.7188 | 124.0311 | -61.3953 | 62.439 | -0.039444 | 0.010897 | 0.018113 | 0.0031338 | 0.06623 | -0.0016149 | 0.073708 | -60.3561 | 62.4344 | -61.5784 | -61.5646 | 58.8593 | 19.0109 | 1.355 | 1.1124 | 62.4298 | -61.6425 | -0.18311 | -0.004578 | 1.0391 | -0.16937 | -3.5797 | -0.24719 | -0.009155 | 1.2222 | 62.7502 | 62.5076 | 120.2545 | 123.8297 | 1.0391 | 123.8251 | 80.4062 | -0.24719 | 123.8297 | 1.0391 | 80.4062 | 120.2545 | 123.8251 | -124.0173 | -124.0814
1282.7188 | 124.0585 | -61.377 | 62.4435 | -0.131 | 0.011751 | 0.014909 | 0.0037746 | 0.068152 | 0.0015893 | 0.074563 | -60.3241 | 62.4435 | -61.5875 | -61.5555 | 58.8776 | 19.0842 | 1.506 | 1.2634 | 62.4298 | -61.647 | -0.21057 | 0 | 1.0529 | -0.17853 | -3.566 | -0.27008 | -0.013732 | 1.2634 | 62.883 | 62.6404 | 120.2545 | 123.8205 | 1.0529 | 123.8068 | 80.4611 | -0.27008 | 123.8205 | 1.0529 | 80.4611 | 120.2545 | 123.8068 | -124.0311 | -124.0906
1283.7188 | 124.0356 | -61.3861 | 62.4298 | -0.062332 | 0.01581 | 0.012345 | 0.0033474 | 0.069007 | 0.00030767 | 0.071359 | -60.4706 | 62.4161 | -61.6196 | -61.5509 | 58.873 | 19.1116 | 1.5976 | 1.3321 | 62.4298 | -61.6287 | -0.23346 | -0.013733 | 0.91553 | -0.16479 | -3.5568 | -0.24262 | 0 | 1.149 | 62.9837 | 62.7182 | 120.2591 | 123.8022 | 0.91553 | 123.8159 | 80.4977 | -0.24262 | 123.8022 | 0.91553 | 80.4977 | 120.2591 | 123.8159 | -124.0494 | -124.0585
1284.7188 | 124.0265 | -61.3907 | 62.4435 | -0.024185 | 0.011111 | 0.012559 | 0.003561 | 0.067084 | -0.0011877 | 0.071786 | -60.3333 | 62.4527 | -61.6104 | -61.5829 | 58.8409 | 19.1437 | 1.7075 | 1.3733 | 62.4344 | -61.6425 | -0.21973 | 0.009156 | 1.0574 | -0.19226 | -3.6026 | -0.25177 | -0.009155 | 1.2772 | 63.0981 | 62.764 | 120.2316 | 123.8434 | 1.0574 | 123.8251 | 80.5344 | -0.25177 | 123.8434 | 1.0574 | 80.5344 | 120.2316 | 123.8251 | -124.054 | -124.086
1285.7188 | 124.0219 | -61.3815 | 62.4481 | -0.039444 | 0.013888 | 0.012773 | 0.0044156 | 0.066443 | -0.00011953 | 0.073281 | -60.3333 | 62.4527 | -61.6196 | -61.5646 | 58.8501 | 19.1895 | 1.7853 | 1.4511 | 62.4069 | -61.6791 | -0.23804 | 0.004578 | 1.0483 | -0.1831 | -3.598 | -0.29755 | -0.041199 | 1.2863 | 63.1668 | 62.8326 | 120.2316 | 123.8342 | 1.0483 | 123.7885 | 80.571 | -0.29755 | 123.8342 | 1.0483 | 80.571 | 120.2316 | 123.7885 | -124.0677 | -124.1272
1286.7188 | 124.0265 | -61.3953 | 62.4115 | -0.10811 | 0.013888 | 0.012773 | 0.0048428 | 0.06623 | 0.00073487 | 0.075845 | -60.3195 | 62.4527 | -61.6241 | -61.5646 | 58.8181 | 19.2307 | 1.8539 | 1.5335 | 62.4023 | -61.6791 | -0.22888 | 0.041199 | 1.0757 | -0.16937 | -3.5934 | -0.28381 | -0.009155 | 1.3046 | 63.2492 | 62.9288 | 120.2133 | 123.848 | 1.0757 | 123.7976 | 80.6259 | -0.28381 | 123.848 | 1.0757 | 80.6259 | 120.2133 | 123.7976 | -124.0356 | -124.0906
1287.7188 | 124.1226 | -61.3815 | 62.3795 | 0.1284 | 0.011538 | 0.0099954 | -0.00049776 | 0.067511 | 0.00094847 | 0.074777 | -60.3149 | 62.3199 | -61.6196 | -61.5555 | 58.8501 | 19.3268 | 1.7807 | 1.6708 | 62.3474 | -61.6287 | -0.23804 | -0.05951 | 1.0666 | -0.17395 | -3.5294 | -0.24719 | -0.032044 | 1.3046 | 63.1622 | 63.0524 | 120.2316 | 123.7015 | 1.0666 | 123.7289 | 80.7083 | -0.24719 | 123.7015 | 1.0666 | 80.7083 | 120.2316 | 123.7289 | -123.999 | -124.0082
1288.7188 | 124.0448 | -61.4044 | 62.4435 | -0.09285 | 0.011751 | 0.0132 | 0.0061246 | 0.06623 | 0.00052127 | 0.073068 | -60.4477 | 62.3886 | -61.6241 | -61.5646 | 58.8089 | 19.3222 | 2.0142 | 1.7258 | 62.4069 | -61.6699 | -0.21973 | -0.054931 | 0.95673 | -0.16022 | -3.6346 | -0.2655 | -0.036621 | 1.1765 | 63.4186 | 63.1302 | 120.2133 | 123.793 | 0.95673 | 123.8113 | 80.7266 | -0.2655 | 123.793 | 0.95673 | 80.7266 | 120.2133 | 123.8113 | -124.0677 | -124.1135
1289.7188 | 124.0494 | -61.3953 | 62.4664 | -0.22255 | 0.010683 | 0.012132 | 0.0061246 | 0.06623 | 0.0018031 | 0.073495 | -60.3058 | 62.439 | -61.5875 | -61.5417 | 58.8135 | 19.3588 | 2.1469 | 1.8173 | 62.4481 | -61.647 | -0.19226 | -0.027466 | 1.0895 | -0.14648 | -3.653 | -0.25177 | -0.018311 | 1.2817 | 63.5422 | 63.2126 | 120.2087 | 123.8342 | 1.0895 | 123.8434 | 80.7541 | -0.25177 | 123.8342 | 1.0895 | 80.7541 | 120.2087 | 123.8434 | -124.054 | -124.1135
1290.7188 | 124.0265 | -61.377 | 62.4481 | -0.2607 | 0.013247 | 0.015122 | 0.0067654 | 0.067298 | 0.00073487 | 0.073922 | -60.3241 | 62.439 | -61.6058 | -61.5692 | 58.7906 | 19.3771 | 2.2156 | 1.886 | 62.4298 | -61.6653 | -0.22888 | -0.009155 | 1.0529 | -0.19226 | -3.6575 | -0.28839 | -0.01831 | 1.2817 | 63.5925 | 63.2629 | 120.1675 | 123.8159 | 1.0529 | 123.8068 | 80.7541 | -0.28839 | 123.8159 | 1.0529 | 80.7541 | 120.1675 | 123.8068 | -124.054 | -124.1135
1291.7188 | 124.0082 | -61.4044 | 62.4115 | -0.047073 | 0.013674 | 0.018327 | 0.0054836 | 0.067298 | -0.0018285 | 0.073068 | -60.2966 | 62.4344 | -61.615 | -61.6013 | 58.7769 | 19.3909 | 2.2202 | 1.8951 | 62.4298 | -61.6608 | -0.21057 | 0.022888 | 1.1078 | -0.19684 | -3.6346 | -0.25635 | 0.018311 | 1.3184 | 63.6246 | 63.2996 | 120.1813 | 123.8388 | 1.1078 | 123.8342 | 80.7953 | -0.25635 | 123.8388 | 1.1078 | 80.7953 | 120.1813 | 123.8342 | -124.0265 | -124.0723
1292.7344 | 124.1043 | -61.3953 | 62.3657 | 0.13603 | 0.0098287 | 0.011277 | -0.0011386 | 0.065161 | -0.0014013 | 0.076486 | -60.3195 | 62.3016 | -61.6425 | -61.5601 | 58.8043 | 19.4595 | 2.1194 | 2.0142 | 62.3474 | -61.6379 | -0.24719 | -0.064087 | 1.0757 | -0.1648 | -3.5614 | -0.24261 | -0.018311 | 1.3229 | 63.5147 | 63.4094 | 120.1996 | 123.6969 | 1.0757 | 123.7427 | 80.8548 | -0.24261 | 123.6969 | 1.0757 | 80.8548 | 120.1996 | 123.7427 | -124.0082 | -124.0036
1293.7188 | 124.0036 | -61.3953 | 62.4344 | 0.2047 | 0.013674 | 0.014695 | 0.0056972 | 0.064307 | -0.0011877 | 0.073922 | -60.2646 | 62.4298 | -61.6013 | -61.5646 | 58.7494 | 19.4366 | 2.3071 | 1.9913 | 62.4207 | -61.6562 | -0.20599 | -0.004577 | 1.1307 | -0.16937 | -3.685 | -0.26093 | -0.013733 | 1.3367 | 63.7024 | 63.3865 | 120.1447 | 123.8251 | 1.1307 | 123.8159 | 80.8319 | -0.26093 | 123.8251 | 1.1307 | 80.8319 | 120.1447 | 123.8159 | -124.0356 | -124.0906
1294.7188 | 124.0494 | -61.3907 | 62.4069 | 0.99815 | 0.01282 | 0.014268 | 0.0071926 | 0.067511 | -0.0011877 | 0.075417 | -60.2051 | 62.3886 | -61.6196 | -61.5555 | 58.754 | 19.4778 | 2.3849 | 2.092 | 62.4023 | -61.6791 | -0.22888 | -0.01831 | 1.1856 | -0.16479 | -3.653 | -0.28839 | -0.004577 | 1.4145 | 63.7756 | 63.4827 | 120.1447 | 123.7793 | 1.1856 | 123.793 | 80.8685 | -0.28839 | 123.7793 | 1.1856 | 80.8685 | 120.1447 | 123.793 | -124.0265 | -124.086
1295.7188 | 124.0448 | -61.3953 | 62.4481 | -0.077591 | 0.0089743 | 0.014482 | 0.0063382 | 0.064948 | 0.00073487 | 0.072213 | -60.2875 | 62.4252 | -61.6241 | -61.6013 | 58.7677 | 19.5419 | 2.4673 | 2.1881 | 62.4115 | -61.6791 | -0.22888 | -0.022888 | 1.1078 | -0.20599 | -3.6804 | -0.28381 | -0.036621 | 1.3367 | 63.8626 | 63.5834 | 120.163 | 123.8205 | 1.1078 | 123.8068 | 80.9372 | -0.28381 | 123.8205 | 1.1078 | 80.9372 | 120.163 | 123.8068 | -124.0723 | -124.1272
1296.7188 | 124.0402 | -61.3815 | 62.4252 | -0.21492 | 0.011111 | 0.010636 | 0.004202 | 0.06687 | -0.00011953 | 0.074136 | -60.3012 | 62.4481 | -61.6287 | -61.5692 | 58.7494 | 19.5374 | 2.536 | 2.2247 | 62.4115 | -61.6653 | -0.24719 | 0.022888 | 1.0803 | -0.18768 | -3.6758 | -0.28381 | -0.013733 | 1.3275 | 63.9175 | 63.6063 | 120.1309 | 123.8297 | 1.0803 | 123.793 | 80.9189 | -0.28381 | 123.8297 | 1.0803 | 80.9189 | 120.1309 | 123.793 | -124.054 | -124.0906
1297.7188 | 124.0585 | -61.3815 | 62.4527 | -0.19966 | 0.014742 | 0.012132 | 0.0046292 | 0.068579 | 0.00030767 | 0.071145 | -60.2966 | 62.4252 | -61.6287 | -61.5829 | 58.7311 | 19.5602 | 2.6276 | 2.2797 | 62.4207 | -61.6425 | -0.24719 | -0.027466 | 1.0849 | -0.20142 | -3.7216 | -0.26093 | -0.032044 | 1.3321 | 64.0091 | 63.6612 | 120.1126 | 123.8068 | 1.0849 | 123.8022 | 80.9418 | -0.26093 | 123.8068 | 1.0849 | 80.9418 | 120.1126 | 123.8022 | -124.0814 | -124.0952
1298.7188 | 124.0494 | -61.4136 | 62.4069 | -0.13863 | 0.010897 | 0.015763 | 0.0074062 | 0.068579 | -0.0018285 | 0.073495 | -60.26 | 62.4252 | -61.6241 | -61.5784 | 58.7082 | 19.5602 | 2.6184 | 2.33 | 62.3978 | -61.7065 | -0.21057 | 0.018311 | 1.1536 | -0.1648 | -3.6987 | -0.29297 | -0.009155 | 1.3641 | 64.032 | 63.7436 | 120.1218 | 123.8388 | 1.1536 | 123.8113 | 80.9738 | -0.29297 | 123.8388 | 1.1536 | 80.9738 | 120.1218 | 123.8113 | -124.0311 | -124.1135
1299.7188 | 124.0494 | -61.4365 | 62.4207 | -0.13863 | 0.013247 | 0.017472 | 0.0061246 | 0.068793 | 0.00094847 | 0.074777 | -60.3012 | 62.3886 | -61.647 | -61.5738 | 58.7128 | 19.606 | 2.6596 | 2.3849 | 62.384 | -61.6837 | -0.21057 | -0.032043 | 1.1353 | -0.13733 | -3.7079 | -0.24719 | -0.036621 | 1.3458 | 64.0961 | 63.8214 | 120.1492 | 123.8251 | 1.1353 | 123.8205 | 81.0425 | -0.24719 | 123.8251 | 1.1353 | 81.0425 | 120.1492 | 123.8205 | -124.0677 | -124.1043
1300.7188 | 124.0402 | -61.4136 | 62.4161 | -0.024185 | 0.012606 | 0.019395 | 0.0067654 | 0.066016 | -0.00097413 | 0.073281 | -60.4431 | 62.3749 | -61.6699 | -61.5692 | 58.7311 | 19.6701 | 2.7786 | 2.4628 | 62.384 | -61.6791 | -0.25635 | -0.041199 | 0.97046 | -0.15564 | -3.685 | -0.2655 | -0.032044 | 1.2268 | 64.1922 | 63.8763 | 120.1447 | 123.7885 | 0.97046 | 123.7976 | 81.0837 | -0.2655 | 123.7885 | 0.97046 | 81.0837 | 120.1447 | 123.7976 | -124.086 | -124.0952
1301.7188 | 124.0723 | -61.4182 | 62.4207 | -0.039444 | 0.012392 | 0.011491 | 0.005911 | 0.068366 | 0.00052127 | 0.076699 | -60.2554 | 62.4023 | -61.6379 | -61.5784 | 58.7952 | 19.6289 | 2.861 | 2.4902 | 62.4069 | -61.6745 | -0.21973 | -0.01831 | 1.1627 | -0.16022 | -3.6255 | -0.25635 | -0.013733 | 1.3824 | 64.2792 | 63.9084 | 120.2133 | 123.8205 | 1.1627 | 123.8251 | 81.0471 | -0.25635 | 123.8205 | 1.1627 | 81.0471 | 120.2133 | 123.8251 | -124.0585 | -124.0952
1302.7188 | 124.0219 | -61.4365 | 62.3978 | 0.13603 | 0.01282 | 0.011918 | 0.0037746 | 0.066657 | 0.00073487 | 0.074136 | -60.3424 | 62.3749 | -61.6516 | -61.6653 | 58.6212 | 19.6335 | 2.8198 | 2.4811 | 62.4023 | -61.6974 | -0.21515 | -0.022888 | 1.0941 | -0.22888 | -3.7766 | -0.26093 | 0.004578 | 1.3092 | 64.2563 | 63.9175 | 120.0577 | 123.8113 | 1.0941 | 123.8388 | 81.0699 | -0.26093 | 123.8113 | 1.0941 | 81.0699 | 120.0577 | 123.8388 | -124.0494 | -124.0952
1303.7188 | 124.0311 | -61.4273 | 62.4161 | -0.19203 | 0.011538 | 0.010423 | 0.0065518 | 0.065802 | -0.0026831 | 0.073495 | -60.3149 | 62.4252 | -61.6516 | -61.5829 | 58.6716 | 19.6793 | 2.98 | 2.6001 | 62.4069 | -61.6791 | -0.2243 | 0.009155 | 1.1124 | -0.15564 | -3.7445 | -0.25177 | -0.009156 | 1.3367 | 64.4073 | 64.0274 | 120.0989 | 123.8525 | 1.1124 | 123.8342 | 81.1066 | -0.25177 | 123.8525 | 1.1124 | 81.1066 | 120.0989 | 123.8342 | -124.0677 | -124.0952
1304.7188 | 124.0448 | -61.4273 | 62.439 | -0.16914 | 0.011965 | 0.012986 | 0.003561 | 0.065375 | 0.0011621 | 0.073708 | -60.3058 | 62.4023 | -61.6379 | -61.6058 | 58.6487 | 19.6747 | 3.0075 | 2.6184 | 62.4115 | -61.6791 | -0.21057 | -0.036621 | 1.1215 | -0.17853 | -3.7903 | -0.25177 | -0.027466 | 1.3321 | 64.4348 | 64.0457 | 120.076 | 123.8297 | 1.1215 | 123.8388 | 81.102 | -0.25177 | 123.8297 | 1.1215 | 81.102 | 120.076 | 123.8388 | -124.0768 | -124.118
1305.7188 | 124.0494 | -61.409 | 62.4069 | -0.069961 | 0.012606 | 0.014482 | 0.0048428 | 0.067939 | -0.0011877 | 0.078835 | -60.4202 | 62.3795 | -61.6608 | -61.5738 | 58.6624 | 19.7388 | 2.9938 | 2.71 | 62.384 | -61.6837 | -0.25177 | -0.027465 | 0.98877 | -0.16479 | -3.7445 | -0.27466 | -0.022888 | 1.2405 | 64.4028 | 64.119 | 120.0714 | 123.7885 | 0.98877 | 123.793 | 81.1478 | -0.27466 | 123.7885 | 0.98877 | 81.1478 | 120.0714 | 123.793 | -124.0677 | -124.0906
1306.7188 | 124.0448 | -61.4136 | 62.4207 | -0.19203 | 0.013033 | 0.014909 | 0.0071926 | 0.068152 | -0.00097413 | 0.076058 | -60.2554 | 62.3932 | -61.647 | -61.7706 | 58.5388 | 19.8212 | 2.9846 | 2.7557 | 62.3611 | -61.6608 | -0.23346 | -0.027466 | 1.1581 | -0.35706 | -3.8818 | -0.24719 | -0.059509 | 1.3916 | 64.3982 | 64.1693 | 119.9524 | 123.8068 | 1.1581 | 123.7747 | 81.2347 | -0.24719 | 123.8068 | 1.1581 | 81.2347 | 119.9524 | 123.7747 | -124.0677 | -124.0814
1307.7188 | 124.1272 | -61.4044 | 62.352 | 0.2047 | 0.010683 | 0.014695 | 0.0031338 | 0.068793 | 0.00073487 | 0.074777 | -60.2921 | 62.3245 | -61.6837 | -61.5921 | 58.6533 | 19.7662 | 2.8885 | 2.8152 | 62.3337 | -61.6608 | -0.27924 | -0.027466 | 1.1124 | -0.18768 | -3.6987 | -0.25635 | -0.018311 | 1.3916 | 64.2929 | 64.2197 | 120.0577 | 123.7289 | 1.1124 | 123.7381 | 81.1707 | -0.25635 | 123.7289 | 1.1124 | 81.1707 | 120.0577 | 123.7381 | -124.0356 | -124.0128
1308.7188 | 124.054 | -61.409 | 62.3978 | -0.10048 | 0.013247 | 0.014268 | 0.005911 | 0.064093 | -0.00054693 | 0.073922 | -60.228 | 62.3932 | -61.6196 | -61.5784 | 58.6533 | 19.7708 | 3.1082 | 2.8931 | 62.384 | -61.6928 | -0.21057 | -0.004578 | 1.181 | -0.16937 | -3.7445 | -0.28381 | -0.013733 | 1.3916 | 64.5172 | 64.3021 | 120.0623 | 123.8022 | 1.181 | 123.793 | 81.1798 | -0.28381 | 123.8022 | 1.181 | 81.1798 | 120.0623 | 123.793 | -124.0173 | -124.0906
1309.7188 | 124.0311 | -61.4319 | 62.4023 | -0.20729 | 0.014529 | 0.0095682 | 0.0061246 | 0.067298 | -0.00097413 | 0.074136 | -60.2417 | 62.3886 | -61.6653 | -61.5784 | 58.6487 | 19.78 | 3.1586 | 2.9343 | 62.384 | -61.6653 | -0.23346 | -0.013733 | 1.1902 | -0.14648 | -3.7537 | -0.23346 | -0.018311 | 1.4236 | 64.5905 | 64.3662 | 120.0806 | 123.8205 | 1.1902 | 123.8159 | 81.2119 | -0.23346 | 123.8205 | 1.1902 | 81.2119 | 120.0806 | 123.8159 | -124.0677 | -124.0677
1310.7188 | 124.0356 | -61.4182 | 62.4023 | -0.26833 | 0.011965 | 0.017686 | 0.0048428 | 0.065802 | -0.00097413 | 0.073922 | -60.2509 | 62.4023 | -61.6333 | -61.5921 | 58.6121 | 19.7983 | 3.2776 | 2.9892 | 62.3932 | -61.6653 | -0.21515 | 0 | 1.1673 | -0.17395 | -3.7903 | -0.24719 | -0.009156 | 1.3824 | 64.6957 | 64.4073 | 120.0302 | 123.8205 | 1.1673 | 123.8113 | 81.2164 | -0.24719 | 123.8205 | 1.1673 | 81.2164 | 120.0302 | 123.8113 | -124.0356 | -124.0677
1311.7188 | 123.9716 | -61.4502 | 62.3978 | 0.97527 | 0.012606 | 0.012773 | 0.0020656 | 0.065802 | 0.00052127 | 0.075631 | -60.3653 | 62.3795 | -61.6562 | -61.6425 | 58.6166 | 19.7983 | 3.3875 | 2.9755 | 62.3978 | -61.6745 | -0.20599 | -0.01831 | 1.0849 | -0.19226 | -3.7811 | -0.22431 | 0 | 1.2909 | 64.8376 | 64.4257 | 120.0668 | 123.8297 | 1.0849 | 123.848 | 81.2485 | -0.22431 | 123.8297 | 1.0849 | 81.2485 | 120.0668 | 123.848 | -124.054 | -124.0723
1312.7188 | 124.0494 | -61.4365 | 62.3795 | -0.19966 | 0.011751 | 0.010423 | 0.0054836 | 0.065375 | 0.00030767 | 0.07264 | -60.2325 | 62.4023 | -61.6379 | -61.5875 | 58.6166 | 19.7983 | 3.2913 | 3.0258 | 62.3886 | -61.6608 | -0.20142 | 0.022888 | 1.2039 | -0.15106 | -3.7628 | -0.22431 | 0.009155 | 1.4053 | 64.7278 | 64.4623 | 120.0531 | 123.8388 | 1.2039 | 123.8251 | 81.2347 | -0.22431 | 123.8388 | 1.2039 | 81.2347 | 120.0531 | 123.8251 | -124.0173 | -124.0402
1313.7188 | 124.0265 | -61.4273 | 62.4069 | -0.19966 | 0.011751 | 0.010423 | 0.0056972 | 0.065802 | -0.0011877 | 0.074349 | -60.2417 | 62.384 | -61.6562 | -61.5829 | 58.6075 | 19.8486 | 3.3829 | 3.1082 | 62.3795 | -61.6699 | -0.22888 | -0.022888 | 1.1856 | -0.15564 | -3.7994 | -0.24262 | -0.027465 | 1.4145 | 64.8102 | 64.5355 | 120.0348 | 123.8113 | 1.1856 | 123.8068 | 81.2759 | -0.24262 | 123.8113 | 1.1856 | 81.2759 | 120.0348 | 123.8068 | -124.0631 | -124.0768
1314.7188 | 124.0448 | -61.4273 | 62.4115 | -0.1844 | 0.014956 | 0.015122 | 0.0046292 | 0.066657 | -0.00097413 | 0.075417 | -60.2509 | 62.4115 | -61.6425 | -61.5921 | 58.5938 | 19.8212 | 3.3829 | 3.0762 | 62.3978 | -61.6791 | -0.21515 | 0 | 1.1765 | -0.16479 | -3.8177 | -0.25177 | -0.013733 | 1.3916 | 64.8102 | 64.5035 | 120.0211 | 123.8388 | 1.1765 | 123.8251 | 81.2485 | -0.25177 | 123.8388 | 1.1765 | 81.2485 | 120.0211 | 123.8251 | -124.054 | -124.0906
1315.7188 | 124.0219 | -61.4044 | 62.4069 | -0.131 | 0.01047 | 0.015336 | 0.0046292 | 0.06687 | 0.0013757 | 0.073922 | -60.2692 | 62.3978 | -61.6241 | -61.5921 | 58.5846 | 19.8441 | 3.4698 | 3.1128 | 62.3932 | -61.6745 | -0.21973 | -0.009155 | 1.1353 | -0.18768 | -3.8223 | -0.27008 | -0.013733 | 1.355 | 64.8743 | 64.5172 | 119.989 | 123.8022 | 1.1353 | 123.7976 | 81.2485 | -0.27008 | 123.8022 | 1.1353 | 81.2485 | 119.989 | 123.7976 | -124.0311 | -124.0814
1316.7188 | 124.0173 | -61.4365 | 62.4344 | -0.16151 | 0.012179 | 0.014268 | 0.0056972 | 0.064307 | -0.0014013 | 0.074136 | -60.2783 | 62.4161 | -61.6333 | -61.6104 | 58.5709 | 19.8898 | 3.5385 | 3.1219 | 62.3932 | -61.6562 | -0.19684 | -0.01831 | 1.1581 | -0.17395 | -3.8635 | -0.21973 | -0.041199 | 1.355 | 64.975 | 64.5584 | 120.0073 | 123.8525 | 1.1581 | 123.8297 | 81.3263 | -0.21973 | 123.8525 | 1.1581 | 81.3263 | 120.0073 | 123.8297 | -124.0677 | -124.0906
1317.7188 | 123.9853 | -61.4319 | 62.3932 | -0.069961 | 0.014101 | 0.012345 | 0.0067654 | 0.066657 | -0.00011953 | 0.074349 | -60.2325 | 62.3566 | -61.6379 | -61.6287 | 58.5251 | 19.8807 | 3.5065 | 3.1448 | 62.3749 | -61.6974 | -0.20599 | -0.036621 | 1.1993 | -0.19684 | -3.8681 | -0.2655 | -0.01831 | 1.4053 | 64.9384 | 64.5767 | 119.957 | 123.7885 | 1.1993 | 123.8068 | 81.3126 | -0.2655 | 123.7885 | 1.1993 | 81.3126 | 119.957 | 123.8068 | -124.0311 | -124.0906
1318.7188 | 123.9807 | -61.441 | 62.3978 | -0.23781 | 0.010042 | 0.009141 | 0.00057044 | 0.067084 | 0.0013757 | 0.074563 | -60.2829 | 62.3886 | -61.6333 | -61.6241 | 58.5114 | 19.8669 | 3.6118 | 3.1815 | 62.4115 | -61.6562 | -0.19226 | -0.009155 | 1.1581 | -0.18311 | -3.8864 | -0.21515 | 0.013733 | 1.3504 | 65.0528 | 64.6225 | 119.9524 | 123.8297 | 1.1581 | 123.8525 | 81.308 | -0.21515 | 123.8297 | 1.1581 | 81.308 | 119.9524 | 123.8525 | -124.0311 | -124.054
1319.7188 | 124.0173 | -61.4182 | 62.4023 | -0.25307 | 0.012179 | 0.011704 | 0.0080472 | 0.06687 | -0.0026831 | 0.077767 | -60.2463 | 62.3795 | -61.647 | -61.5967 | 58.5342 | 19.8944 | 3.6072 | 3.2639 | 62.3932 | -61.6837 | -0.22888 | -0.022888 | 1.1719 | -0.17853 | -3.8681 | -0.2655 | -0.009156 | 1.4008 | 65.0253 | 64.682 | 119.9524 | 123.7976 | 1.1719 | 123.8113 | 81.3126 | -0.2655 | 123.7976 | 1.1719 | 81.3126 | 119.9524 | 123.8113 | -124.0494 | -124.086
1320.7188 | 124.0356 | -61.4365 | 62.4115 | -0.24544 | 0.01282 | 0.0097818 | 0.0044156 | 0.065375 | -0.00097413 | 0.073922 | -60.2509 | 62.4161 | -61.6608 | -61.6058 | 58.5342 | 20.0043 | 3.6804 | 3.2913 | 62.3978 | -61.6791 | -0.22431 | 0.004578 | 1.1856 | -0.16937 | -3.8773 | -0.24262 | -0.013733 | 1.4099 | 65.1169 | 64.7278 | 119.9707 | 123.8525 | 1.1856 | 123.8342 | 81.4407 | -0.24262 | 123.8525 | 1.1856 | 81.4407 | 119.9707 | 123.8342 | -124.0723 | -124.0906
1321.7188 | 124.0036 | -61.4136 | 62.4207 | -0.131 | 0.012392 | 0.010423 | 0.005911 | 0.066016 | -0.0014013 | 0.076058 | -60.2509 | 62.3703 | -61.647 | -61.6241 | 58.5297 | 19.9539 | 3.6987 | 3.3234 | 62.3978 | -61.6974 | -0.23346 | -0.050354 | 1.1627 | -0.21057 | -3.891 | -0.28381 | -0.022888 | 1.3962 | 65.1123 | 64.7369 | 119.9432 | 123.7839 | 1.1627 | 123.8113 | 81.3675 | -0.28381 | 123.7839 | 1.1627 | 81.3675 | 119.9432 | 123.8113 | -124.0677 | -124.118
1322.7188 | 123.9899 | -61.441 | 62.384 | -0.56587 | 0.012606 | 0.010423 | 0.0067654 | 0.067084 | -0.00097413 | 0.076058 | -60.2554 | 62.3474 | -61.6653 | -61.6745 | 58.4564 | 19.9265 | 3.6621 | 3.273 | 62.3749 | -61.7111 | -0.2243 | -0.036621 | 1.1856 | -0.23346 | -3.9276 | -0.27008 | -0.009155 | 1.4099 | 65.1031 | 64.7141 | 119.8975 | 123.7885 | 1.1856 | 123.8159 | 81.3675 | -0.27008 | 123.7885 | 1.1856 | 81.3675 | 119.8975 | 123.8159 | -124.0494 | -124.0952
1323.7188 | 124.0036 | -61.4456 | 62.4023 | -0.16151 | 0.011965 | 0.011704 | 0.0082608 | 0.064948 | 0.0015893 | 0.076486 | -60.2554 | 62.3978 | -61.6653 | -61.6516 | 58.4885 | 19.9585 | 3.7582 | 3.3646 | 62.3932 | -61.702 | -0.21973 | -0.004578 | 1.1902 | -0.20599 | -3.9139 | -0.25635 | -0.009156 | 1.4099 | 65.2039 | 64.8102 | 119.9341 | 123.8434 | 1.1902 | 123.8388 | 81.4041 | -0.25635 | 123.8434 | 1.1902 | 81.4041 | 119.9341 | 123.8388 | -124.0677 | -124.1043
1324.7188 | 123.9716 | -61.4365 | 62.4252 | -0.23781 | 0.010042 | 0.0097818 | 0.00057044 | 0.065375 | 0.00030767 | 0.076058 | -60.2554 | 62.3337 | -61.6287 | -61.6241 | 58.5068 | 19.9539 | 3.7674 | 3.3783 | 62.3978 | -61.6699 | -0.19226 | -0.091553 | 1.181 | -0.18768 | -3.9185 | -0.23346 | -0.027466 | 1.3733 | 65.2039 | 64.8148 | 119.9432 | 123.7701 | 1.181 | 123.8342 | 81.3904 | -0.23346 | 123.7701 | 1.181 | 81.3904 | 119.9432 | 123.8342 | -124.054 | -124.0952
1325.7344 | 124.0173 | -61.4319 | 62.3703 | 0.11314 | 0.01346 | 0.012345 | 0.0065518 | 0.067725 | -0.00097413 | 0.076699 | -60.2646 | 62.3566 | -61.6791 | -61.6745 | 58.429 | 20.0317 | 3.6987 | 3.3325 | 62.3383 | -61.6837 | -0.24719 | -0.013733 | 1.1673 | -0.24262 | -3.9413 | -0.25177 | -0.032043 | 1.4145 | 65.1306 | 64.7644 | 119.8608 | 123.7885 | 1.1673 | 123.7701 | 81.4636 | -0.25177 | 123.7885 | 1.1673 | 81.4636 | 119.8608 | 123.7701 | -124.0494 | -124.054
1326.7188 | 124.0036 | -61.409 | 62.3886 | -0.21492 | 0.013033 | 0.014054 | 0.0056972 | 0.067084 | -0.0018285 | 0.072427 | -60.228 | 62.3749 | -61.6745 | -61.6196 | 58.4976 | 19.9997 | 3.7949 | 3.447 | 62.3978 | -61.6928 | -0.2655 | -0.013733 | 1.181 | -0.21057 | -3.891 | -0.28381 | 0.009155 | 1.4465 | 65.2039 | 64.856 | 119.9066 | 123.7839 | 1.181 | 123.8068 | 81.4087 | -0.28381 | 123.7839 | 1.181 | 81.4087 | 119.9066 | 123.8068 | -124.0631 | -124.0814
1327.7188 | 124.0128 | -61.4319 | 62.3932 | 0.63957 | 0.01282 | 0.014482 | 0.0084744 | 0.068793 | 0.0011621 | 0.073708 | -60.1456 | 62.3703 | -61.6562 | -61.5921 | 58.493 | 20.0088 | 3.7628 | 3.4515 | 62.3795 | -61.6837 | -0.2243 | -0.022888 | 1.2863 | -0.16022 | -3.9001 | -0.25177 | -0.013732 | 1.5106 | 65.1947 | 64.8834 | 119.9249 | 123.8022 | 1.2863 | 123.8113 | 81.4407 | -0.25177 | 123.8022 | 1.2863 | 81.4407 | 119.9249 | 123.8113 | -124.0494 | -124.0768
1328.7188 | 124.0082 | -61.4227 | 62.4207 | -0.22255 | 0.011111 | 0.011918 | 0.0061246 | 0.067298 | -0.00011953 | 0.072 | -60.2325 | 62.3657 | -61.647 | -61.6196 | 58.4702 | 19.9814 | 3.8681 | 3.4927 | 62.3886 | -61.6837 | -0.22431 | -0.054931 | 1.1902 | -0.19684 | -3.9505 | -0.26093 | -0.032043 | 1.4145 | 65.2908 | 64.9155 | 119.8929 | 123.7885 | 1.1902 | 123.8113 | 81.4041 | -0.26093 | 123.7885 | 1.1902 | 81.4041 | 119.8929 | 123.8113 | -124.0677 | -124.1043
1329.7188 | 124.0036 | -61.4319 | 62.4161 | -0.20729 | 0.013033 | 0.014909 | 0.0037746 | 0.066657 | 0.00073487 | 0.073922 | -60.2417 | 62.3611 | -61.6974 | -61.6241 | 58.4564 | 19.9265 | 3.8773 | 3.4424 | 62.4023 | -61.6745 | -0.2655 | -0.054932 | 1.1902 | -0.19226 | -3.9597 | -0.24262 | -0.013733 | 1.4557 | 65.3091 | 64.8743 | 119.8883 | 123.793 | 1.1902 | 123.8342 | 81.3583 | -0.24262 | 123.793 | 1.1902 | 81.3583 | 119.8883 | 123.8342 | -124.1135 | -124.0906
1330.7344 | 124.0997 | -61.4136 | 62.3245 | 2.402 | 0.012179 | 0.012559 | 0.0012112 | 0.066443 | -0.00076053 | 0.074563 | -60.0769 | 62.2787 | -61.6516 | -61.5555 | 58.5434 | 20.1096 | 3.6072 | 3.5156 | 62.2879 | -61.6516 | -0.23804 | -0.045776 | 1.3367 | -0.14191 | -3.7811 | -0.23804 | -0.036621 | 1.5747 | 65.0208 | 64.9292 | 119.957 | 123.6923 | 1.3367 | 123.7015 | 81.5231 | -0.23804 | 123.6923 | 1.3367 | 81.5231 | 119.957 | 123.7015 | -123.9761 | -123.9761
1331.7188 | 123.9716 | -61.4456 | 62.4207 | -0.2607 | 0.011324 | 0.011277 | 0.0056972 | 0.062171 | -0.00076053 | 0.075845 | -60.2188 | 62.3657 | -61.6379 | -61.6333 | 58.4656 | 20.0088 | 3.9047 | 3.511 | 62.3611 | -61.6928 | -0.19226 | -0.054931 | 1.2268 | -0.18768 | -3.9551 | -0.24719 | -0.059509 | 1.4191 | 65.3503 | 64.9567 | 119.9112 | 123.8113 | 1.2268 | 123.8068 | 81.4545 | -0.24719 | 123.8113 | 1.2268 | 81.4545 | 119.9112 | 123.8068 | -124.0585 | -124.1135
1332.7188 | 124.0311 | -61.4319 | 62.3978 | -0.131 | 0.013674 | 0.0097818 | 0.0076198 | 0.065802 | -0.00076053 | 0.074563 | -60.1685 | 62.3611 | -61.6333 | -61.5829 | 58.4656 | 20.0363 | 3.8589 | 3.5294 | 62.3611 | -61.702 | -0.20142 | -0.036621 | 1.2634 | -0.15106 | -3.9322 | -0.27008 | -0.036621 | 1.4648 | 65.2908 | 64.9612 | 119.8975 | 123.793 | 1.2634 | 123.793 | 81.4682 | -0.27008 | 123.793 | 1.2634 | 81.4682 | 119.8975 | 123.793 | -124.0311 | -124.0997
1333.7188 | 124.0082 | -61.4319 | 62.3978 | -0.22255 | 0.011111 | 0.011277 | 0.0054836 | 0.064734 | -0.00033333 | 0.075845 | -60.228 | 62.3566 | -61.6562 | -61.6241 | 58.4061 | 19.9997 | 4.0421 | 3.5797 | 62.4069 | -61.6882 | -0.2243 | -0.041199 | 1.2039 | -0.19226 | -3.9917 | -0.25635 | 0.009155 | 1.4282 | 65.4739 | 65.0116 | 119.838 | 123.7885 | 1.2039 | 123.8388 | 81.4316 | -0.25635 | 123.7885 | 1.2039 | 81.4316 | 119.838 | 123.8388 | -124.054 | -124.086
1334.7188 | 123.999 | -61.4182 | 62.3932 | -0.17677 | 0.010256 | 0.011704 | 0.0046292 | 0.064948 | -0.00076053 | 0.074136 | -60.2371 | 62.3886 | -61.6608 | -61.6241 | 58.4335 | 20.0317 | 4.0375 | 3.5751 | 62.4023 | -61.6745 | -0.24262 | -0.004577 | 1.181 | -0.20599 | -3.9597 | -0.25635 | 0.009156 | 1.4236 | 65.4556 | 64.9933 | 119.8517 | 123.8068 | 1.181 | 123.8205 | 81.4499 | -0.25635 | 123.8068 | 1.181 | 81.4499 | 119.8517 | 123.8205 | -124.054 | -124.0677
1335.7188 | 123.9578 | -61.4639 | 62.4023 | 0.03685 | 0.01282 | 0.012986 | 0.0093288 | 0.067084 | 0.00030767 | 0.074777 | -60.2097 | 62.3703 | -61.6653 | -61.6699 | 58.3557 | 19.986 | 3.9963 | 3.5156 | 62.3795 | -61.6974 | -0.20142 | -0.032044 | 1.2543 | -0.20599 | -4.0466 | -0.23346 | -0.022888 | 1.4557 | 65.4602 | 64.9796 | 119.8196 | 123.8342 | 1.2543 | 123.8434 | 81.4499 | -0.23346 | 123.8342 | 1.2543 | 81.4499 | 119.8196 | 123.8434 | -124.0677 | -124.0997
1336.7188 | 123.999 | -61.4365 | 62.384 | -0.51247 | 0.012179 | 0.0095682 | 0.0037746 | 0.065161 | -0.0014013 | 0.075204 | -60.2554 | 62.3474 | -61.6928 | -61.647 | 58.3923 | 20.0592 | 4.0878 | 3.5797 | 62.384 | -61.6791 | -0.25635 | -0.036621 | 1.181 | -0.21057 | -3.9917 | -0.24262 | 0 | 1.4374 | 65.5243 | 65.0162 | 119.8288 | 123.7839 | 1.181 | 123.8205 | 81.4957 | -0.24262 | 123.7839 | 1.181 | 81.4957 | 119.8288 | 123.8205 | -124.0768 | -124.0631
1337.7188 | 123.9899 | -61.4685 | 62.3886 | 0.03685 | 0.010897 | 0.014054 | 0.0076198 | 0.065161 | 0.00094847 | 0.073922 | -60.2097 | 62.3566 | -61.6699 | -61.6608 | 58.3786 | 20.0867 | 4.1107 | 3.6118 | 62.352 | -61.6928 | -0.20142 | -0.032044 | 1.2588 | -0.19226 | -4.01 | -0.2243 | -0.036621 | 1.4603 | 65.5792 | 65.0803 | 119.8471 | 123.8251 | 1.2588 | 123.8205 | 81.5552 | -0.2243 | 123.8251 | 1.2588 | 81.5552 | 119.8471 | 123.8205 | -124.0585 | -124.0814
1338.7188 | 124.0265 | -61.4227 | 62.4069 | -0.28358 | 0.0098287 | 0.0087138 | 0.00078404 | 0.066443 | -0.0031103 | 0.073922 | -60.2051 | 62.3199 | -61.647 | -61.6058 | 58.4015 | 20.1096 | 4.1931 | 3.6621 | 62.3978 | -61.6425 | -0.22431 | -0.086975 | 1.2177 | -0.18311 | -4.0054 | -0.21973 | -0.009155 | 1.442 | 65.6158 | 65.0848 | 119.8242 | 123.7427 | 1.2177 | 123.8205 | 81.5323 | -0.21973 | 123.7427 | 1.2177 | 81.5323 | 119.8242 | 123.8205 | -124.054 | -124.0494
1339.7188 | 123.9716 | -61.4502 | 62.4207 | -0.22255 | 0.011324 | 0.0061502 | 0.0033474 | 0.064948 | -0.0011877 | 0.074563 | -60.228 | 62.3566 | -61.6608 | -61.6241 | 58.3649 | 20.0729 | 4.4128 | 3.8635 | 62.4252 | -61.6745 | -0.21057 | -0.064087 | 1.2222 | -0.17395 | -4.0558 | -0.22431 | 0.004578 | 1.4328 | 65.863 | 65.3137 | 119.8151 | 123.8068 | 1.2222 | 123.8754 | 81.5231 | -0.22431 | 123.8068 | 1.2222 | 81.5231 | 119.8151 | 123.8754 | -124.0814 | -124.0952
1340.7188 | 124.1089 | -61.4365 | 62.3337 | 0.15892 | 0.0098287 | 0.0132 | 0.0029202 | 0.064307 | -0.0016149 | 0.076699 | -60.1639 | 62.2742 | -61.6333 | -61.5967 | 58.4015 | 20.1645 | 3.9185 | 3.6987 | 62.2833 | -61.6699 | -0.19684 | -0.059509 | 1.2726 | -0.16022 | -3.9322 | -0.23346 | -0.050354 | 1.4694 | 65.3549 | 65.1352 | 119.838 | 123.7106 | 1.2726 | 123.7198 | 81.601 | -0.23346 | 123.7106 | 1.2726 | 81.601 | 119.838 | 123.7198 | -123.967 | -124.0036
1341.7188 | 123.999 | -61.4594 | 62.3886 | -0.024185 | 0.011111 | 0.011277 | 0.0044156 | 0.064734 | -0.00033333 | 0.073495 | -60.2234 | 62.3749 | -61.6562 | -61.6379 | 58.3328 | 20.05 | 4.2526 | 3.653 | 62.3474 | -61.702 | -0.19684 | -0.013733 | 1.236 | -0.17853 | -4.0558 | -0.24261 | -0.041199 | 1.4328 | 65.712 | 65.1123 | 119.7922 | 123.8342 | 1.236 | 123.8068 | 81.5094 | -0.24261 | 123.8342 | 1.236 | 81.5094 | 119.7922 | 123.8068 | -124.0448 | -124.0906
1342.7188 | 124.0219 | -61.4639 | 62.3749 | -0.069961 | 0.011751 | 0.011704 | 0.0089016 | 0.063666 | -0.00054693 | 0.076058 | -60.141 | 62.3611 | -61.6699 | -61.5967 | 58.3649 | 20.0821 | 4.2068 | 3.7125 | 62.3291 | -61.6699 | -0.20599 | -0.013733 | 1.3229 | -0.13275 | -4.01 | -0.20599 | -0.045776 | 1.5289 | 65.6708 | 65.1764 | 119.8288 | 123.8251 | 1.3229 | 123.793 | 81.546 | -0.20599 | 123.8251 | 1.3229 | 81.546 | 119.8288 | 123.793 | -124.0448 | -124.0448
1343.7188 | 123.9716 | -61.4273 | 62.3886 | -0.19966 | 0.014315 | 0.012986 | 0.0039882 | 0.067084 | 0.00094847 | 0.073708 | -60.3333 | 62.3337 | -61.6928 | -61.6653 | 58.3603 | 20.1233 | 4.3488 | 3.7491 | 62.3978 | -61.6608 | -0.2655 | -0.054932 | 1.0941 | -0.23804 | -4.0283 | -0.23346 | 0.009155 | 1.3596 | 65.7761 | 65.1764 | 119.7876 | 123.761 | 1.0941 | 123.8251 | 81.5506 | -0.23346 | 123.761 | 1.0941 | 81.5506 | 119.7876 | 123.8251 | -124.0814 | -124.0494
1344.7188 | 123.9716 | -61.409 | 62.4344 | -0.23018 | 0.011324 | 0.012559 | 0.008688 | 0.065802 | -0.0024695 | 0.072213 | -60.3104 | 62.352 | -61.6333 | -61.6974 | 58.3191 | 20.1233 | 4.3167 | 3.7491 | 62.3749 | -61.6837 | -0.2243 | -0.082397 | 1.0986 | -0.28839 | -4.1153 | -0.27466 | -0.059509 | 1.3229 | 65.7257 | 65.1581 | 119.7281 | 123.761 | 1.0986 | 123.7839 | 81.5323 | -0.27466 | 123.761 | 1.0986 | 81.5323 | 119.7281 | 123.7839 | -124.0677 | -124.118
1345.7188 | 123.9899 | -61.441 | 62.3886 | -0.27596 | 0.012392 | 0.0132 | 0.0031338 | 0.065161 | 9.4068e-05 | 0.073708 | -60.1639 | 62.2925 | -61.647 | -61.615 | 58.3466 | 20.1553 | 4.3076 | 3.8086 | 62.3886 | -61.6516 | -0.20599 | -0.096131 | 1.2772 | -0.17395 | -4.0421 | -0.21057 | 0 | 1.4832 | 65.7486 | 65.2496 | 119.7876 | 123.7335 | 1.2772 | 123.8297 | 81.5964 | -0.21057 | 123.7335 | 1.2772 | 81.5964 | 119.7876 | 123.8297 | -124.0356 | -124.0402
1346.7188 | 124.0265 | -61.4594 | 62.3749 | -0.25307 | 0.0091879 | 0.010636 | 0.0039882 | 0.062812 | 0.00030767 | 0.075204 | -60.1456 | 62.2971 | -61.6699 | -61.5921 | 58.342 | 20.2011 | 4.3121 | 3.8223 | 62.3795 | -61.6653 | -0.21057 | -0.07782 | 1.3138 | -0.13275 | -4.0329 | -0.20599 | 0.004578 | 1.5244 | 65.7715 | 65.2817 | 119.8013 | 123.7564 | 1.3138 | 123.8388 | 81.6605 | -0.20599 | 123.7564 | 1.3138 | 81.6605 | 119.8013 | 123.8388 | -124.0448 | -124.0402
1347.7188 | 124.0082 | -61.4777 | 62.3932 | -0.069961 | 0.011324 | 0.016618 | 0.0093288 | 0.063239 | -0.0022559 | 0.074563 | -60.1364 | 62.352 | -61.6699 | -61.6333 | 58.2962 | 20.0958 | 4.303 | 3.8269 | 62.3474 | -61.702 | -0.19226 | -0.041198 | 1.3412 | -0.15564 | -4.097 | -0.2243 | -0.045776 | 1.5335 | 65.7806 | 65.3046 | 119.7739 | 123.8297 | 1.3412 | 123.8251 | 81.5735 | -0.2243 | 123.8297 | 1.3412 | 81.5735 | 119.7739 | 123.8251 | -124.0631 | -124.0952
1348.7188 | 123.9761 | -61.4548 | 62.3978 | -0.23781 | 0.012392 | 0.017686 | 0.0054836 | 0.066443 | -0.0014013 | 0.073708 | -60.1822 | 62.3703 | -61.6699 | -61.6287 | 58.3008 | 20.05 | 4.3304 | 3.7903 | 62.3749 | -61.6928 | -0.21515 | -0.027466 | 1.2726 | -0.17395 | -4.097 | -0.23804 | -0.022888 | 1.4877 | 65.7852 | 65.2451 | 119.7556 | 123.8251 | 1.2726 | 123.8297 | 81.5048 | -0.23804 | 123.8251 | 1.2726 | 81.5048 | 119.7556 | 123.8297 | -124.0677 | -124.0906
1349.7188 | 123.9761 | -61.4365 | 62.3749 | 0.18944 | 0.011965 | 0.011918 | 0.0050564 | 0.065589 | 0.00094847 | 0.075204 | -60.1685 | 62.3383 | -61.6516 | -61.6425 | 58.2825 | 20.0821 | 4.3762 | 3.8132 | 62.3795 | -61.702 | -0.21515 | -0.036621 | 1.268 | -0.20599 | -4.0924 | -0.2655 | 0.004578 | 1.4832 | 65.8127 | 65.2496 | 119.7189 | 123.7747 | 1.268 | 123.8159 | 81.5186 | -0.2655 | 123.7747 | 1.268 | 81.5186 | 119.7189 | 123.8159 | -124.0265 | -124.0768
1350.7188 | 123.9853 | -61.441 | 62.3795 | -0.5735 | 0.011965 | 0.0085 | 0.006979 | 0.064307 | -0.0033239 | 0.075204 | -60.3424 | 62.3657 | -61.6928 | -61.6608 | 58.3008 | 20.1187 | 4.3625 | 3.8086 | 62.4023 | -61.702 | -0.25177 | -0.013733 | 1.0986 | -0.21973 | -4.0787 | -0.26093 | 0.022888 | 1.3504 | 65.8035 | 65.2496 | 119.7418 | 123.8068 | 1.0986 | 123.8434 | 81.5598 | -0.26093 | 123.8068 | 1.0986 | 81.5598 | 119.7418 | 123.8434 | -124.0723 | -124.0814
1351.7188 | 123.9716 | -61.4639 | 62.384 | -0.24544 | 0.013247 | 0.012559 | 0.0067654 | 0.062812 | -0.00076053 | 0.07499 | -60.3195 | 62.3611 | -61.647 | -61.6745 | 58.2596 | 20.1691 | 4.4312 | 3.8818 | 62.352 | -61.7111 | -0.18311 | -0.022888 | 1.1444 | -0.21057 | -4.1245 | -0.24719 | -0.032043 | 1.3275 | 65.8951 | 65.3458 | 119.7235 | 123.8251 | 1.1444 | 123.8159 | 81.633 | -0.24719 | 123.8251 | 1.1444 | 81.633 | 119.7235 | 123.8159 | -124.0311 | -124.0952
1352.7188 | 124.0128 | -61.441 | 62.3566 | -0.23018 | 0.01346 | 0.011704 | 0.0078336 | 0.065802 | -0.0016149 | 0.075204 | -60.1227 | 62.3611 | -61.6379 | -61.6013 | 58.2962 | 20.192 | 4.3671 | 3.9276 | 62.3428 | -61.6653 | -0.19684 | 0.004578 | 1.3184 | -0.16022 | -4.0604 | -0.2243 | -0.013733 | 1.5152 | 65.8081 | 65.3687 | 119.7372 | 123.8022 | 1.3184 | 123.7839 | 81.633 | -0.2243 | 123.8022 | 1.3184 | 81.633 | 119.7372 | 123.7839 | -123.9944 | -124.0219
1353.7188 | 124.0082 | -61.4456 | 62.3978 | -0.22255 | 0.011324 | 0.0087138 | 0.0044156 | 0.065375 | -0.0014013 | 0.074349 | -60.1547 | 62.3154 | -61.6333 | -61.5875 | 58.3145 | 20.1599 | 4.4037 | 3.9413 | 62.3566 | -61.6882 | -0.18768 | -0.082397 | 1.2909 | -0.14191 | -4.0833 | -0.24261 | -0.041199 | 1.4786 | 65.8493 | 65.387 | 119.7601 | 123.761 | 1.2909 | 123.8022 | 81.6055 | -0.24261 | 123.761 | 1.2909 | 81.6055 | 119.7601 | 123.8022 | -124.0311 | -124.086
1354.7188 | 123.9532 | -61.4777 | 62.3978 | -0.30647 | 0.01282 | 0.015763 | 0.0063382 | 0.063666 | 0.00094847 | 0.072854 | -60.173 | 62.3566 | -61.6653 | -61.6333 | 58.2458 | 20.1141 | 4.4083 | 3.8818 | 62.3657 | -61.6837 | -0.18768 | -0.041199 | 1.3046 | -0.15564 | -4.1519 | -0.20599 | -0.032043 | 1.4923 | 65.8859 | 65.3595 | 119.7235 | 123.8342 | 1.3046 | 123.8434 | 81.5918 | -0.20599 | 123.8342 | 1.3046 | 81.5918 | 119.7235 | 123.8434 | -124.0631 | -124.0814
1355.7188 | 123.9761 | -61.4456 | 62.3749 | 0.1284 | 0.01282 | 0.010209 | 0.0056972 | 0.064734 | -0.00033333 | 0.076058 | -60.1593 | 62.3474 | -61.6882 | -61.6562 | 58.255 | 20.1599 | 4.4586 | 3.8864 | 62.3886 | -61.702 | -0.24261 | -0.027466 | 1.2863 | -0.21057 | -4.1199 | -0.25635 | 0.013733 | 1.5289 | 65.9042 | 65.332 | 119.7006 | 123.793 | 1.2863 | 123.8342 | 81.6055 | -0.25635 | 123.793 | 1.2863 | 81.6055 | 119.7006 | 123.8342 | -124.0631 | -124.0768
1356.7188 | 123.9944 | -61.4594 | 62.4023 | -1.9315 | 0.010042 | 0.017259 | 0.0071926 | 0.06623 | -0.00076053 | 0.074777 | -60.3012 | 62.3657 | -61.6791 | -61.6608 | 58.2001 | 20.1324 | 4.5502 | 3.9459 | 62.3795 | -61.702 | -0.21973 | -0.036621 | 1.1581 | -0.20142 | -4.2023 | -0.24261 | -0.022888 | 1.3779 | 66.0095 | 65.4053 | 119.6594 | 123.8251 | 1.1581 | 123.8388 | 81.5918 | -0.24261 | 123.8251 | 1.1581 | 81.5918 | 119.6594 | 123.8388 | -124.0814 | -124.1043
1357.7188 | 124.054 | -61.4731 | 62.3703 | -0.55824 | 0.011751 | 0.014909 | 0.0082608 | 0.065589 | 0.00030767 | 0.073708 | -60.1181 | 62.3383 | -61.6837 | -61.5784 | 58.2596 | 20.2377 | 4.4083 | 3.9917 | 62.3566 | -61.6791 | -0.21057 | -0.032043 | 1.355 | -0.10529 | -4.1107 | -0.20599 | -0.013733 | 1.5656 | 65.8813 | 65.4648 | 119.7327 | 123.8113 | 1.355 | 123.8297 | 81.7108 | -0.20599 | 123.8113 | 1.355 | 81.7108 | 119.7327 | 123.8297 | -124.054 | -124.0494
1358.7188 | 123.9761 | -61.4777 | 62.3795 | -0.22255 | 0.0085471 | 0.014482 | 0.0029202 | 0.064948 | -0.0028967 | 0.076058 | -60.1868 | 62.3291 | -61.6699 | -61.647 | 58.2138 | 20.0363 | 4.7745 | 4.1428 | 62.4252 | -61.647 | -0.19226 | -0.050354 | 1.2909 | -0.16937 | -4.1656 | -0.16937 | 0.045776 | 1.4832 | 66.2521 | 65.6204 | 119.6915 | 123.8068 | 1.2909 | 123.9029 | 81.514 | -0.16937 | 123.8068 | 1.2909 | 81.514 | 119.6915 | 123.9029 | -124.0494 | -124.0265
1359.7188 | 124.0128 | -61.4319 | 62.3978 | -0.2607 | 0.012392 | 0.01085 | 0.0027066 | 0.065161 | -0.0022559 | 0.075631 | -60.1364 | 62.2971 | -61.6425 | -61.5875 | 58.2962 | 20.2103 | 4.4815 | 4.0649 | 62.3474 | -61.647 | -0.21057 | -0.10071 | 1.2955 | -0.15564 | -4.1016 | -0.21515 | -0.050354 | 1.506 | 65.9134 | 65.4968 | 119.7281 | 123.7289 | 1.2955 | 123.7793 | 81.6422 | -0.21515 | 123.7289 | 1.2955 | 81.6422 | 119.7281 | 123.7793 | -124.0402 | -124.0448
1360.7188 | 123.9624 | -61.4502 | 62.4207 | -0.15388 | 0.011111 | 0.010209 | 0.0037746 | 0.065375 | 0.00030767 | 0.07499 | -60.173 | 62.3337 | -61.6516 | -61.6562 | 58.1955 | 20.05 | 4.5502 | 4.0054 | 62.3795 | -61.6791 | -0.20142 | -0.086975 | 1.2772 | -0.20599 | -4.2252 | -0.22888 | -0.041198 | 1.4786 | 66.0004 | 65.4556 | 119.6457 | 123.7839 | 1.2772 | 123.8297 | 81.5002 | -0.22888 | 123.7839 | 1.2772 | 81.5002 | 119.6457 | 123.8297 | -124.0723 | -124.0997
1361.7188 | 123.9578 | -61.4777 | 62.4207 | -0.74898 | 0.011965 | 0.012773 | 0.0082608 | 0.063239 | 9.4068e-05 | 0.076486 | -60.2188 | 62.3108 | -61.6791 | -61.6287 | 58.1955 | 20.1096 | 4.6005 | 3.9917 | 62.3611 | -61.6882 | -0.20142 | -0.10986 | 1.2588 | -0.15106 | -4.2252 | -0.21057 | -0.059509 | 1.4603 | 66.0782 | 65.4694 | 119.6732 | 123.7885 | 1.2588 | 123.8388 | 81.5872 | -0.21057 | 123.7885 | 1.2588 | 81.5872 | 119.6732 | 123.8388 | -124.0997 | -124.1089
1362.7188 | 123.9807 | -61.4594 | 62.3749 | -0.0012969 | 0.01346 | 0.01085 | 0.010611 | 0.066657 | -0.00097413 | 0.074563 | -60.1318 | 62.3383 | -61.6791 | -61.647 | 58.1314 | 20.0409 | 4.4769 | 3.9597 | 62.3383 | -61.7111 | -0.21973 | -0.036621 | 1.3275 | -0.18768 | -4.2435 | -0.25177 | -0.036621 | 1.5472 | 65.9363 | 65.419 | 119.5908 | 123.7976 | 1.3275 | 123.7976 | 81.5002 | -0.25177 | 123.7976 | 1.3275 | 81.5002 | 119.5908 | 123.7976 | -124.054 | -124.086
1363.7188 | 124.0036 | -61.4502 | 62.3795 | -0.1844 | 0.012392 | 0.010636 | 0.0074062 | 0.065589 | -0.0014013 | 0.075417 | -60.1822 | 62.3383 | -61.6974 | -61.5326 | 58.0124 | 19.9768 | 4.6646 | 3.978 | 62.3657 | -61.6882 | -0.24719 | -0.041199 | 1.268 | -0.082398 | -4.3671 | -0.23804 | -0.013733 | 1.5152 | 66.1148 | 65.4282 | 119.4626 | 123.7885 | 1.268 | 123.8159 | 81.427 | -0.23804 | 123.7885 | 1.268 | 81.427 | 119.4626 | 123.8159 | -124.0768 | -124.0677
1364.7188 | 124.0585 | -61.4502 | 62.4298 | -0.16151 | 0.0096151 | 0.012986 | 0.0048428 | 0.064734 | 0.00052127 | 0.074777 | -60.1685 | 62.352 | -61.6699 | -61.6425 | 58.1497 | 20.0775 | 4.6463 | 4.0421 | 62.3886 | -61.6745 | -0.21973 | -0.07782 | 1.2817 | -0.19226 | -4.2801 | -0.22431 | -0.041199 | 1.5015 | 66.0965 | 65.4922 | 119.5999 | 123.8022 | 1.2817 | 123.8388 | 81.5277 | -0.22431 | 123.8022 | 1.2817 | 81.5277 | 119.5999 | 123.8388 | -124.0997 | -124.1043
1365.7188 | 123.999 | -61.4456 | 62.3978 | -0.24544 | 0.012392 | 0.014695 | 0.0050564 | 0.065802 | 0.00030767 | 0.075417 | -60.173 | 62.3337 | -61.6608 | -61.6562 | 58.1543 | 20.0775 | 4.6097 | 4.01 | 62.3566 | -61.6837 | -0.21515 | -0.064087 | 1.2726 | -0.21057 | -4.2435 | -0.23804 | -0.041199 | 1.4877 | 66.0553 | 65.4556 | 119.5999 | 123.7793 | 1.2726 | 123.8022 | 81.5231 | -0.23804 | 123.7793 | 1.2726 | 81.5231 | 119.5999 | 123.8022 | -124.0585 | -124.0814
1366.7188 | 124.0494 | -61.4273 | 62.3795 | -0.26833 | 0.0070517 | 0.012345 | 0.0031338 | 0.064307 | -0.0024695 | 0.074349 | -60.0952 | 62.2787 | -61.6287 | -61.5601 | 58.2138 | 20.1553 | 4.5547 | 4.1473 | 62.3337 | -61.6608 | -0.20142 | -0.10071 | 1.3321 | -0.13275 | -4.1656 | -0.23346 | -0.045777 | 1.5335 | 65.9821 | 65.5746 | 119.6411 | 123.7061 | 1.3321 | 123.761 | 81.5826 | -0.23346 | 123.7061 | 1.3321 | 81.5826 | 119.6411 | 123.761 | -124.0082 | -124.0402
1367.7188 | 123.999 | -61.4456 | 62.4023 | -0.26833 | 0.011965 | 0.010209 | 0.0071926 | 0.063239 | -0.00011953 | 0.077554 | -60.2509 | 62.3428 | -61.6562 | -61.6745 | 58.1223 | 20.0684 | 4.6326 | 4.0009 | 62.384 | -61.6974 | -0.21057 | -0.05951 | 1.1948 | -0.22888 | -4.2801 | -0.25177 | -0.018311 | 1.4053 | 66.0782 | 65.4465 | 119.5679 | 123.7885 | 1.1948 | 123.8297 | 81.514 | -0.25177 | 123.7885 | 1.1948 | 81.514 | 119.5679 | 123.8297 | -124.0585 | -124.0997
1368.7188 | 123.9853 | -61.4319 | 62.384 | -0.21492 | 0.0091879 | 0.013627 | 0.00527 | 0.065589 | -0.0014013 | 0.073922 | -60.1639 | 62.3245 | -61.6837 | -61.6974 | 58.2413 | 20.2515 | 4.4724 | 3.9093 | 62.3566 | -61.6928 | -0.25177 | -0.059509 | 1.268 | -0.2655 | -4.1428 | -0.26093 | -0.027466 | 1.5198 | 65.9042 | 65.3412 | 119.6732 | 123.7564 | 1.268 | 123.7885 | 81.6834 | -0.26093 | 123.7564 | 1.268 | 81.6834 | 119.6732 | 123.7885 | -124.0677 | -124.0768
1369.7188 | 123.9716 | -61.4365 | 62.4023 | -0.16151 | 0.010897 | 0.0089274 | 0.0046292 | 0.063452 | 9.4068e-05 | 0.074777 | -60.1593 | 62.3245 | -61.6608 | -61.647 | 58.1085 | 20.0226 | 4.6921 | 4.0329 | 62.3657 | -61.6791 | -0.22431 | -0.07782 | 1.2772 | -0.21057 | -4.2938 | -0.24262 | -0.036621 | 1.5015 | 66.1285 | 65.4694 | 119.545 | 123.761 | 1.2772 | 123.8022 | 81.459 | -0.24262 | 123.761 | 1.2772 | 81.459 | 119.545 | 123.8022 | -124.0631 | -124.0814
1370.7188 | 124.0128 | -61.4548 | 62.3703 | -0.28358 | 0.010897 | 0.014054 | 0.0063382 | 0.06388 | -0.00097413 | 0.076699 | -60.1639 | 62.3245 | -61.6608 | -61.6516 | 58.1131 | 20.0317 | 4.6371 | 4.01 | 62.3703 | -61.647 | -0.20599 | -0.045776 | 1.2909 | -0.19684 | -4.2572 | -0.19226 | 0 | 1.4969 | 66.0919 | 65.4648 | 119.5679 | 123.7793 | 1.2909 | 123.8251 | 81.4865 | -0.19226 | 123.7793 | 1.2909 | 81.4865 | 119.5679 | 123.8251 | -124.0311 | -124.0173
1371.7188 | 123.9899 | -61.4319 | 62.4207 | -0.27596 | 0.0094015 | 0.010636 | 0.0037746 | 0.065161 | -0.0011877 | 0.075204 | -60.1364 | 62.3245 | -61.6562 | -61.6379 | 58.1177 | 20.0729 | 4.66 | 4.0329 | 62.3703 | -61.6516 | -0.2243 | -0.09613 | 1.2955 | -0.20599 | -4.303 | -0.21973 | -0.050354 | 1.5198 | 66.0919 | 65.4648 | 119.5496 | 123.7564 | 1.2955 | 123.8022 | 81.5048 | -0.21973 | 123.7564 | 1.2955 | 81.5048 | 119.5496 | 123.8022 | -124.0768 | -124.0723
1372.7188 | 124.0265 | -61.4685 | 62.3886 | -0.039444 | 0.011111 | 0.014268 | 0.0074062 | 0.063239 | -0.00033333 | 0.075845 | -60.1639 | 62.3428 | -61.6791 | -61.6013 | 58.0948 | 20.105 | 4.5914 | 4.0604 | 62.3428 | -61.6928 | -0.21057 | -0.045777 | 1.3046 | -0.13275 | -4.2938 | -0.2243 | -0.045777 | 1.5152 | 66.0599 | 65.5289 | 119.5633 | 123.8113 | 1.3046 | 123.8113 | 81.5735 | -0.2243 | 123.8113 | 1.3046 | 81.5735 | 119.5633 | 123.8113 | -124.0677 | -124.0814
1373.7188 | 124.118 | -61.3907 | 62.3611 | -0.42091 | 0.0094015 | 0.011918 | 0.0022794 | 0.067298 | -0.0014013 | 0.076913 | -60.1135 | 62.2513 | -61.6196 | -61.5326 | 58.1818 | 20.1096 | 4.5593 | 4.184 | 62.3199 | -61.647 | -0.22888 | -0.10986 | 1.2772 | -0.14191 | -4.1794 | -0.25635 | -0.041199 | 1.506 | 65.95 | 65.5746 | 119.5724 | 123.642 | 1.2772 | 123.7106 | 81.5002 | -0.25635 | 123.642 | 1.2772 | 81.5002 | 119.5724 | 123.7106 | -123.9807 | -124.0082
1374.7188 | 124.0906 | -61.4044 | 62.3795 | -0.23781 | 0.01047 | 0.011491 | 0.004202 | 0.063452 | -0.00011953 | 0.076272 | -60.0952 | 62.265 | -61.6425 | -61.5692 | 58.1223 | 20.0592 | 4.6143 | 4.1107 | 62.3199 | -61.6745 | -0.23804 | -0.11444 | 1.3092 | -0.1648 | -4.2572 | -0.27008 | -0.05951 | 1.5472 | 66.0187 | 65.5151 | 119.5267 | 123.6694 | 1.3092 | 123.7244 | 81.4636 | -0.27008 | 123.6694 | 1.3092 | 81.4636 | 119.5267 | 123.7244 | -124.0219 | -124.054
1375.7188 | 123.9899 | -61.4456 | 62.4023 | -0.24544 | 0.010683 | 0.01085 | 0.0048428 | 0.062812 | -0.00054693 | 0.075417 | -60.1089 | 62.3016 | -61.6379 | -61.6241 | 58.049 | 19.931 | 4.6371 | 3.9963 | 62.3703 | -61.6791 | -0.19226 | -0.10071 | 1.3367 | -0.17853 | -4.3533 | -0.23346 | -0.032044 | 1.5289 | 66.0828 | 65.4419 | 119.4946 | 123.7473 | 1.3367 | 123.8159 | 81.3766 | -0.23346 | 123.7473 | 1.3367 | 81.3766 | 119.4946 | 123.8159 | -124.0402 | -124.0814
1376.7188 | 124.0219 | -61.4273 | 62.4069 | -0.28358 | 0.010042 | 0.013413 | 0.0056972 | 0.063452 | -0.0033239 | 0.074349 | -60.1044 | 62.2879 | -61.6516 | -61.6013 | 58.0856 | 20.0912 | 4.6646 | 4.01 | 62.3611 | -61.6608 | -0.2243 | -0.11902 | 1.3229 | -0.17395 | -4.3213 | -0.23346 | -0.045776 | 1.5472 | 66.0919 | 65.4373 | 119.5129 | 123.7152 | 1.3229 | 123.7885 | 81.5186 | -0.23346 | 123.7152 | 1.3229 | 81.5186 | 119.5129 | 123.7885 | -124.0585 | -124.0677
1377.7188 | 124.0356 | -61.4319 | 62.3657 | -0.077591 | 0.012606 | 0.014268 | 0.01232 | 0.066443 | -0.0024695 | 0.074349 | -60.0815 | 62.3474 | -61.6608 | -61.5875 | 58.0582 | 19.8715 | 4.6051 | 4.1199 | 62.3291 | -61.702 | -0.22888 | -0.018311 | 1.3504 | -0.15564 | -4.3076 | -0.27008 | -0.036621 | 1.5793 | 66.037 | 65.5518 | 119.4901 | 123.7793 | 1.3504 | 123.761 | 81.3034 | -0.27008 | 123.7793 | 1.3504 | 81.3034 | 119.4901 | 123.761 | -124.0265 | -124.0677
1378.7188 | 124.054 | -61.4182 | 62.3566 | -0.22255 | 0.0098287 | 0.009141 | 0.0046292 | 0.061743 | -0.0011877 | 0.074136 | -60.0632 | 62.2696 | -61.6516 | -61.5646 | 58.1039 | 19.986 | 4.6005 | 4.0512 | 62.3383 | -61.647 | -0.23346 | -0.086975 | 1.355 | -0.14648 | -4.2526 | -0.22888 | -0.01831 | 1.5884 | 66.0187 | 65.4694 | 119.5221 | 123.6877 | 1.355 | 123.7564 | 81.4041 | -0.22888 | 123.6877 | 1.355 | 81.4041 | 119.5221 | 123.7564 | -124.0082 | -124.0036
1379.7188 | 124.0814 | -61.4044 | 62.3566 | -0.17677 | 0.0087607 | 0.01555 | 0.001852 | 0.064093 | -0.00033333 | 0.074349 | -60.0494 | 62.2696 | -61.647 | -61.5509 | 58.4244 | 20.3018 | 4.2252 | 3.9093 | 62.3383 | -61.6516 | -0.24262 | -0.086975 | 1.355 | -0.14648 | -3.9322 | -0.24719 | -0.01831 | 1.5976 | 65.6296 | 65.3137 | 119.8288 | 123.674 | 1.355 | 123.7427 | 81.7062 | -0.24719 | 123.674 | 1.355 | 81.7062 | 119.8288 | 123.7427 | -124.0036 | -124.0082
1380.7188 | 124.1455 | -61.4044 | 62.352 | -0.10811 | 0.011751 | 0.012559 | 0.0029202 | 0.065161 | -0.0022559 | 0.074563 | -60.0449 | 62.233 | -61.615 | -61.5143 | 58.1223 | 20.1004 | 4.5547 | 4.0878 | 62.3108 | -61.6013 | -0.21057 | -0.11902 | 1.3596 | -0.10986 | -4.2297 | -0.19684 | -0.041199 | 1.5701 | 65.9592 | 65.4922 | 119.5267 | 123.6374 | 1.3596 | 123.7152 | 81.5048 | -0.19684 | 123.6374 | 1.3596 | 81.5048 | 119.5267 | 123.7152 | -123.967 | -123.9532
1381.7188 | 124.0952 | -61.3907 | 62.3749 | 0.30388 | 0.0089743 | 0.017472 | 0.005911 | 0.060889 | -0.0022559 | 0.075204 | -60.0815 | 62.2513 | -61.6516 | -61.5326 | 58.1085 | 19.9768 | 4.541 | 4.0924 | 62.3016 | -61.6516 | -0.26093 | -0.1236 | 1.3092 | -0.14191 | -4.2664 | -0.26093 | -0.073242 | 1.5701 | 65.9317 | 65.4831 | 119.4992 | 123.642 | 1.3092 | 123.6923 | 81.3675 | -0.26093 | 123.642 | 1.3092 | 81.3675 | 119.4992 | 123.6923 | -124.0265 | -124.0265
1382.7188 | 124.0036 | -61.4456 | 62.3749 | -0.077591 | 0.012179 | 0.014909 | 0.013601 | 0.064307 | -0.0016149 | 0.07499 | -60.0449 | 62.3383 | -61.647 | -61.5967 | 58.017 | 19.8898 | 4.6188 | 3.9917 | 62.3108 | -61.7157 | -0.20142 | -0.036621 | 1.4008 | -0.15106 | -4.3579 | -0.27008 | -0.064087 | 1.6022 | 66.0645 | 65.4373 | 119.4626 | 123.7839 | 1.4008 | 123.7564 | 81.3355 | -0.27008 | 123.7839 | 1.4008 | 81.3355 | 119.4626 | 123.7564 | -124.0219 | -124.0906
1383.7188 | 124.086 | -61.3998 | 62.3657 | -0.131 | 0.01047 | 0.014268 | 0.0016384 | 0.06388 | -0.00097413 | 0.074349 | -60.0861 | 62.2559 | -61.6608 | -61.5417 | 58.0948 | 19.9814 | 4.5639 | 4.0878 | 62.3245 | -61.6013 | -0.26093 | -0.10986 | 1.3138 | -0.14191 | -4.2709 | -0.20142 | -0.041199 | 1.5747 | 65.9637 | 65.4877 | 119.4946 | 123.6557 | 1.3138 | 123.7244 | 81.3812 | -0.20142 | 123.6557 | 1.3138 | 81.3812 | 119.4946 | 123.7244 | -124.0265 | -123.967
1384.7188 | 124.1043 | -61.3861 | 62.3611 | -0.15388 | 0.0070517 | 0.010636 | 0.005911 | 0.063452 | -0.0024695 | 0.075417 | -60.0632 | 62.2559 | -61.6333 | -61.5326 | 58.0627 | 20.0134 | 4.5136 | 4.0329 | 62.2742 | -61.647 | -0.24719 | -0.10529 | 1.3229 | -0.14648 | -4.2984 | -0.26093 | -0.086975 | 1.5701 | 65.8997 | 65.419 | 119.4489 | 123.642 | 1.3229 | 123.6603 | 81.3995 | -0.26093 | 123.642 | 1.3229 | 81.3995 | 119.4489 | 123.6603 | -123.9944 | -124.0082
1385.7188 | 124.1135 | -61.4136 | 62.3657 | 0.21996 | 0.010256 | 0.0095682 | 0.0061246 | 0.06388 | -0.00097413 | 0.07499 | -60.0769 | 62.2513 | -61.6287 | -61.5189 | 58.0444 | 19.931 | 4.5547 | 4.1153 | 62.3108 | -61.6104 | -0.21515 | -0.11444 | 1.3367 | -0.10529 | -4.3213 | -0.19684 | -0.054932 | 1.5518 | 65.9683 | 65.5289 | 119.458 | 123.6649 | 1.3367 | 123.7244 | 81.3446 | -0.19684 | 123.6649 | 1.3367 | 81.3446 | 119.458 | 123.7244 | -123.9944 | -123.9761
1386.7188 | 124.1272 | -61.4044 | 62.3428 | -0.054703 | 0.010042 | 0.0082864 | 0.0020656 | 0.062171 | 9.4068e-05 | 0.076486 | -60.054 | 62.233 | -61.6379 | -61.5326 | 58.0765 | 19.9722 | 4.4861 | 4.0787 | 62.2833 | -61.6287 | -0.23346 | -0.10986 | 1.3504 | -0.12817 | -4.2664 | -0.2243 | -0.059509 | 1.5839 | 65.8905 | 65.4831 | 119.4809 | 123.6374 | 1.3504 | 123.6877 | 81.3766 | -0.2243 | 123.6374 | 1.3504 | 81.3766 | 119.4809 | 123.6877 | -123.9807 | -123.9716
1387.7188 | 124.1135 | -61.4044 | 62.3474 | -0.17677 | 0.0085471 | 0.0072184 | 0.0039882 | 0.061316 | -0.0020421 | 0.073281 | -60.0128 | 62.2284 | -61.6333 | -61.5189 | 58.0261 | 19.7617 | 5.0308 | 4.2709 | 62.3657 | -61.5875 | -0.22888 | -0.11902 | 1.3916 | -0.11444 | -4.3213 | -0.18311 | 0.018311 | 1.6205 | 66.4352 | 65.6754 | 119.4305 | 123.6328 | 1.3916 | 123.7701 | 81.1661 | -0.18311 | 123.6328 | 1.3916 | 81.1661 | 119.4305 | 123.7701 | -123.9807 | -123.9349
1388.7188 | 124.1135 | -61.4273 | 62.3657 | -0.34462 | 0.0083333 | 0.01085 | 0.0054836 | 0.061316 | -0.0022559 | 0.076913 | -60.0403 | 62.2696 | -61.6379 | -61.528 | 58.0078 | 19.9127 | 4.5364 | 4.0787 | 62.3016 | -61.6562 | -0.21057 | -0.096131 | 1.387 | -0.10071 | -4.3579 | -0.22888 | -0.064087 | 1.5976 | 65.9637 | 65.506 | 119.4351 | 123.6969 | 1.387 | 123.7289 | 81.34 | -0.22888 | 123.6969 | 1.387 | 81.34 | 119.4351 | 123.7289 | -124.0036 | -124.0219
1389.7188 | 124.0814 | -61.4044 | 62.3795 | 2.8979 | 0.01047 | 0.012559 | 0.0067654 | 0.061957 | -0.0024695 | 0.073495 | -59.9945 | 62.2375 | -61.6562 | -61.5189 | 58.0444 | 19.8898 | 4.5456 | 4.1016 | 62.3062 | -61.6241 | -0.25177 | -0.14191 | 1.4099 | -0.11444 | -4.335 | -0.21973 | -0.073243 | 1.6617 | 65.95 | 65.506 | 119.4489 | 123.642 | 1.4099 | 123.7106 | 81.2943 | -0.21973 | 123.642 | 1.4099 | 81.2943 | 119.4489 | 123.7106 | -124.0356 | -124.0036
1390.7188 | 124.1043 | -61.3907 | 62.3245 | -0.17677 | 0.010683 | 0.0093546 | 0.0063382 | 0.056617 | 0.00094847 | 0.075631 | -60.0357 | 62.2467 | -61.6516 | -61.7752 | 57.9437 | 19.9402 | 4.454 | 4.0375 | 62.2513 | -61.647 | -0.26093 | -0.07782 | 1.355 | -0.38452 | -4.3808 | -0.25635 | -0.073242 | 1.6159 | 65.8447 | 65.4282 | 119.3344 | 123.6374 | 1.355 | 123.642 | 81.3309 | -0.25635 | 123.6374 | 1.355 | 81.3309 | 119.3344 | 123.642 | -123.9761 | -123.9716
1391.7188 | 124.2004 | -61.377 | 62.4023 | -0.13863 | 0.0079061 | 0.0085 | 0.0033474 | 0.06153 | -0.00011953 | 0.074563 | -60.0357 | 62.2238 | -61.6425 | -61.5143 | 58.0307 | 19.8807 | 4.5502 | 4.0604 | 62.2971 | -61.6241 | -0.2655 | -0.17853 | 1.3412 | -0.13733 | -4.3716 | -0.24719 | -0.10529 | 1.6068 | 65.9271 | 65.4373 | 119.4077 | 123.6008 | 1.3412 | 123.674 | 81.2576 | -0.24719 | 123.6008 | 1.3412 | 81.2576 | 119.4077 | 123.674 | -124.0448 | -124.0265
1392.7188 | 124.0173 | -61.4227 | 62.4527 | -0.24544 | 0.012179 | 0.011704 | 0.0095424 | 0.062384 | -0.00054693 | 0.075204 | -60.1227 | 62.3428 | -61.6608 | -61.6196 | 57.9254 | 19.7433 | 4.7379 | 3.9276 | 62.3428 | -61.6745 | -0.23804 | -0.10986 | 1.3 | -0.19684 | -4.5273 | -0.25177 | -0.10986 | 1.5381 | 66.1606 | 65.3503 | 119.3481 | 123.7656 | 1.3 | 123.7656 | 81.1661 | -0.25177 | 123.7656 | 1.3 | 81.1661 | 119.3481 | 123.7656 | -124.1135 | -124.1272
1393.7188 | 124.0768 | -61.3953 | 62.3657 | -0.047073 | 0.010256 | 0.010636 | 0.0014248 | 0.063452 | 0.0015893 | 0.076486 | -60.0998 | 62.2238 | -61.6608 | -61.5875 | 57.9529 | 19.8532 | 4.66 | 4.0695 | 62.2925 | -61.6562 | -0.2655 | -0.14191 | 1.2955 | -0.19226 | -4.4128 | -0.26093 | -0.073243 | 1.561 | 66.0553 | 65.4648 | 119.3481 | 123.6191 | 1.2955 | 123.6877 | 81.2485 | -0.26093 | 123.6191 | 1.2955 | 81.2485 | 119.3481 | 123.6877 | -124.0265 | -124.0219
1394.7188 | 124.0723 | -61.4044 | 62.3657 | -0.0089264 | 0.011538 | 0.014909 | 0.002493 | 0.061316 | -0.00011953 | 0.075845 | -60.0998 | 62.2055 | -61.647 | -61.5829 | 57.9163 | 19.7479 | 4.541 | 3.9688 | 62.265 | -61.6562 | -0.24262 | -0.16022 | 1.3046 | -0.17853 | -4.4495 | -0.25177 | -0.10071 | 1.5472 | 65.9454 | 65.3732 | 119.3207 | 123.6099 | 1.3046 | 123.6694 | 81.1523 | -0.25177 | 123.6099 | 1.3046 | 81.1523 | 119.3207 | 123.6694 | -124.0128 | -124.0219
1395.7188 | 124.0631 | -61.3907 | 62.4344 | -0.15388 | 0.011538 | 0.0132 | 0.0046292 | 0.063025 | 0.0013757 | 0.073281 | -60.022 | 62.2467 | -61.6379 | -61.4914 | 58.0078 | 19.7845 | 4.5593 | 4.0741 | 62.2559 | -61.6425 | -0.24719 | -0.18768 | 1.3687 | -0.10071 | -4.4266 | -0.25177 | -0.17853 | 1.6159 | 65.95 | 65.4648 | 119.3985 | 123.6374 | 1.3687 | 123.6465 | 81.1752 | -0.25177 | 123.6374 | 1.3687 | 81.1752 | 119.3985 | 123.6465 | -124.0723 | -124.0768
1396.7188 | 124.1455 | -61.377 | 62.352 | -0.17677 | 0.0096151 | 0.010636 | 0.0046292 | 0.060248 | -0.0024695 | 0.073708 | -60.0403 | 62.2284 | -61.6379 | -61.5143 | 57.9941 | 19.812 | 4.5502 | 4.1153 | 62.2787 | -61.6379 | -0.26093 | -0.1236 | 1.3367 | -0.13733 | -4.3579 | -0.26093 | -0.073242 | 1.5976 | 65.9271 | 65.4922 | 119.371 | 123.6053 | 1.3367 | 123.6557 | 81.189 | -0.26093 | 123.6053 | 1.3367 | 81.189 | 119.371 | 123.6557 | -123.9899 | -123.9899
1397.7188 | 123.9624 | -61.4273 | 62.3886 | 0.15892 | 0.010897 | 0.014909 | 0.0099698 | 0.061316 | 0.00094847 | 0.073708 | -60.0723 | 62.3428 | -61.6653 | -61.615 | 57.8476 | 19.6106 | 4.6875 | 3.891 | 62.3108 | -61.6791 | -0.23804 | -0.045777 | 1.355 | -0.18768 | -4.541 | -0.25177 | -0.07782 | 1.593 | 66.1148 | 65.3183 | 119.2749 | 123.7701 | 1.355 | 123.7381 | 81.0379 | -0.25177 | 123.7701 | 1.355 | 81.0379 | 119.2749 | 123.7381 | -124.054 | -124.0677
1398.7188 | 124.1135 | -61.3907 | 62.352 | -0.11574 | 0.0081197 | 0.012773 | 0.0027066 | 0.061957 | -0.00011953 | 0.075631 | -60.0632 | 62.233 | -61.6379 | -61.5326 | 57.8934 | 19.7067 | 4.4861 | 3.9963 | 62.3016 | -61.615 | -0.24719 | -0.11902 | 1.3275 | -0.14191 | -4.4586 | -0.2243 | -0.050354 | 1.5747 | 65.8768 | 65.387 | 119.2841 | 123.6237 | 1.3275 | 123.6923 | 81.0974 | -0.2243 | 123.6237 | 1.3275 | 81.0974 | 119.2841 | 123.6923 | -123.9899 | -123.967
1399.7188 | 124.086 | -61.4227 | 62.3703 | -0.062332 | 0.010256 | 0.0093546 | 0.0050564 | 0.061316 | 0.00094847 | 0.076272 | -60.0632 | 62.2513 | -61.6379 | -61.5509 | 57.9117 | 19.6747 | 4.4403 | 3.9276 | 62.2696 | -61.6425 | -0.21515 | -0.11902 | 1.3596 | -0.12817 | -4.4586 | -0.21973 | -0.10071 | 1.5747 | 65.863 | 65.3503 | 119.3344 | 123.674 | 1.3596 | 123.6923 | 81.0974 | -0.21973 | 123.674 | 1.3596 | 81.0974 | 119.3344 | 123.6923 | -124.0082 | -124.0128
1400.7188 | 124.0585 | -61.4182 | 62.3611 | -0.024185 | 0.0094015 | 0.0080728 | 0.003561 | 0.06388 | 0.0015893 | 0.076913 | -59.9304 | 62.2467 | -61.615 | -61.6104 | 57.8567 | 19.6198 | 4.4861 | 3.8727 | 62.265 | -61.6608 | -0.19684 | -0.11444 | 1.4877 | -0.19226 | -4.5044 | -0.24262 | -0.09613 | 1.6846 | 65.9042 | 65.2908 | 119.2749 | 123.6649 | 1.4877 | 123.6832 | 81.0379 | -0.24262 | 123.6649 | 1.4877 | 81.0379 | 119.2749 | 123.6832 | -123.9761 | -124.0219
1401.7188 | 124.0265 | -61.4227 | 62.3474 | 0.021591 | 0.01047 | 0.012345 | 0.0048428 | 0.063025 | 0.00073487 | 0.076272 | -60.1044 | 62.2375 | -61.6333 | -61.6562 | 57.9987 | 19.7296 | 4.3076 | 3.8452 | 62.2833 | -61.6379 | -0.21057 | -0.10986 | 1.3184 | -0.23346 | -4.3488 | -0.21515 | -0.064087 | 1.5289 | 65.7303 | 65.2679 | 119.4214 | 123.6603 | 1.3184 | 123.7061 | 81.1523 | -0.21515 | 123.6603 | 1.3184 | 81.1523 | 119.4214 | 123.7061 | -123.9807 | -123.9853
1402.7188 | 124.1043 | -61.409 | 62.3383 | -0.069961 | 0.01047 | 0.015122 | 0.003561 | 0.059821 | 9.4068e-05 | 0.072427 | -60.0494 | 62.233 | -61.6653 | -61.5372 | 57.9025 | 19.6655 | 4.4586 | 3.9688 | 62.2925 | -61.647 | -0.25635 | -0.10529 | 1.3596 | -0.12817 | -4.4357 | -0.23804 | -0.045777 | 1.6159 | 65.8676 | 65.3778 | 119.3115 | 123.642 | 1.3596 | 123.7015 | 81.0745 | -0.23804 | 123.642 | 1.3596 | 81.0745 | 119.3115 | 123.7015 | -124.0036 | -123.9853
1403.7188 | 124.0997 | -61.3998 | 62.3611 | -0.10048 | 0.0061971 | 0.015122 | 0.0046292 | 0.060675 | 0.0011621 | 0.073922 | -60.0769 | 62.2101 | -61.647 | -61.5417 | 57.843 | 19.6106 | 4.4724 | 3.9368 | 62.2787 | -61.6241 | -0.24719 | -0.15106 | 1.3229 | -0.14191 | -4.5181 | -0.22431 | -0.082397 | 1.5701 | 65.8722 | 65.3366 | 119.2429 | 123.6099 | 1.3229 | 123.6786 | 81.0104 | -0.22431 | 123.6099 | 1.3229 | 81.0104 | 119.2429 | 123.6786 | -124.0082 | -123.9853
1404.7188 | 124.0952 | -61.3907 | 62.3749 | -0.031814 | 0.0091879 | 0.011918 | 0.0031338 | 0.060462 | -0.00054693 | 0.077126 | -60.0723 | 62.2238 | -61.6379 | -61.5555 | 57.843 | 19.5831 | 4.4357 | 3.9322 | 62.2833 | -61.6379 | -0.24719 | -0.15106 | 1.3184 | -0.16479 | -4.5319 | -0.24719 | -0.091553 | 1.5656 | 65.8264 | 65.3229 | 119.2337 | 123.6145 | 1.3184 | 123.674 | 80.9738 | -0.24719 | 123.6145 | 1.3184 | 80.9738 | 119.2337 | 123.674 | -124.0128 | -124.0128
1405.7188 | 124.0814 | -61.4273 | 62.3749 | -0.0012969 | 0.0098287 | 0.011277 | 0.0033474 | 0.060889 | -0.0020421 | 0.076486 | -60.0815 | 62.2467 | -61.647 | -61.5875 | 57.811 | 19.5557 | 4.4769 | 3.9047 | 62.265 | -61.6196 | -0.21973 | -0.12817 | 1.3458 | -0.16022 | -4.5639 | -0.19226 | -0.10986 | 1.5656 | 65.9042 | 65.332 | 119.2383 | 123.674 | 1.3458 | 123.6923 | 80.983 | -0.19226 | 123.674 | 1.3458 | 80.983 | 119.2383 | 123.6923 | -124.0219 | -123.9944
1406.7188 | 124.0448 | -61.4227 | 62.3611 | 0.059738 | 0.011111 | 0.0089274 | 0.002493 | 0.060248 | 0.00052127 | 0.074563 | -60.1089 | 62.2513 | -61.6699 | -61.5829 | 57.8018 | 19.574 | 4.4952 | 3.891 | 62.2696 | -61.6333 | -0.24719 | -0.10986 | 1.3138 | -0.16022 | -4.5593 | -0.21057 | -0.091553 | 1.561 | 65.918 | 65.3137 | 119.2245 | 123.674 | 1.3138 | 123.6923 | 80.9967 | -0.21057 | 123.674 | 1.3138 | 80.9967 | 119.2245 | 123.6923 | -124.0311 | -123.9944
1407.7188 | 124.0448 | -61.3998 | 62.3749 | -0.23781 | 0.0094015 | 0.0087138 | 0.0078336 | 0.060248 | 0.00052127 | 0.075204 | -60.0128 | 62.2696 | -61.6287 | -61.5417 | 57.8339 | 19.519 | 4.5868 | 3.9505 | 62.2971 | -61.6562 | -0.22888 | -0.10529 | 1.387 | -0.14191 | -4.541 | -0.25635 | -0.07782 | 1.6159 | 65.9866 | 65.3503 | 119.2337 | 123.6694 | 1.387 | 123.6969 | 80.9189 | -0.25635 | 123.6694 | 1.387 | 80.9189 | 119.2337 | 123.6969 | -124.0036 | -124.0311
1408.7188 | 124.0311 | -61.409 | 62.3383 | 0.24284 | 0.010683 | 0.0093546 | 0.0056972 | 0.065589 | 0.0015893 | 0.074563 | -60.0723 | 62.2238 | -61.6608 | -61.5738 | 57.7652 | 19.4504 | 4.3991 | 3.8818 | 62.2421 | -61.6425 | -0.25177 | -0.11444 | 1.3367 | -0.16479 | -4.5731 | -0.23346 | -0.096131 | 1.5884 | 65.8081 | 65.2908 | 119.1742 | 123.6328 | 1.3367 | 123.6511 | 80.8594 | -0.23346 | 123.6328 | 1.3367 | 80.8594 | 119.1742 | 123.6511 | -123.999 | -123.9807
1409.7188 | 124.0585 | -61.4044 | 62.3383 | -0.031814 | 0.011538 | 0.011491 | 0.0039882 | 0.061957 | -0.00011953 | 0.075417 | -60.0815 | 62.2375 | -61.6608 | -61.5875 | 57.756 | 19.4092 | 4.4678 | 3.9185 | 62.3016 | -61.6333 | -0.25635 | -0.10071 | 1.3229 | -0.18311 | -4.5822 | -0.22888 | -0.036621 | 1.5793 | 65.8722 | 65.3229 | 119.1605 | 123.642 | 1.3229 | 123.7061 | 80.8136 | -0.22888 | 123.642 | 1.3229 | 80.8136 | 119.1605 | 123.7061 | -123.999 | -123.9716
1410.7188 | 124.0448 | -61.409 | 62.3566 | 0.38017 | 0.013033 | 0.01085 | 0.0016384 | 0.060889 | 0.0011621 | 0.076913 | -60.0677 | 62.2833 | -61.6425 | -61.6058 | 57.7835 | 19.4595 | 4.4632 | 3.8956 | 62.2696 | -61.647 | -0.23346 | -0.073242 | 1.3412 | -0.19684 | -4.5731 | -0.23804 | -0.086975 | 1.5747 | 65.8722 | 65.3046 | 119.1925 | 123.6923 | 1.3412 | 123.6786 | 80.8685 | -0.23804 | 123.6923 | 1.3412 | 80.8685 | 119.1925 | 123.6786 | -123.999 | -124.0036
1411.7344 | 124.0219 | -61.4456 | 62.3932 | -0.25307 | 0.014315 | 0.0132 | 0.011251 | 0.06388 | 0.00073487 | 0.07499 | -60.0449 | 62.3474 | -61.6425 | -61.5829 | 57.724 | 19.3909 | 4.7012 | 3.9505 | 62.3337 | -61.6974 | -0.19684 | -0.045776 | 1.4008 | -0.13733 | -4.6692 | -0.25177 | -0.059509 | 1.5976 | 66.1469 | 65.3961 | 119.1696 | 123.793 | 1.4008 | 123.7793 | 80.8365 | -0.25177 | 123.793 | 1.4008 | 80.8365 | 119.1696 | 123.7793 | -124.0356 | -124.0906
1412.7188 | 124.0997 | -61.3953 | 62.3428 | -0.069961 | 0.0089743 | 0.0097818 | 0.00099764 | 0.061316 | -0.0011877 | 0.073708 | -60.0449 | 62.2559 | -61.6562 | -61.5417 | 57.7881 | 19.4504 | 4.4907 | 4.0146 | 62.2696 | -61.6058 | -0.26093 | -0.086975 | 1.3504 | -0.14648 | -4.5547 | -0.21057 | -0.073242 | 1.6113 | 65.8859 | 65.4099 | 119.1833 | 123.6511 | 1.3504 | 123.6649 | 80.8456 | -0.21057 | 123.6511 | 1.3504 | 80.8456 | 119.1833 | 123.6649 | -123.999 | -123.9487
1413.7188 | 124.0631 | -61.4319 | 62.3749 | 0.10551 | 0.0091879 | 0.010209 | 0.0037746 | 0.062598 | 0.00052127 | 0.076058 | -60.0906 | 62.265 | -61.6379 | -61.5921 | 57.7057 | 19.3588 | 4.4815 | 3.9185 | 62.2604 | -61.6425 | -0.20599 | -0.10986 | 1.3412 | -0.16022 | -4.6692 | -0.21057 | -0.11444 | 1.5472 | 65.9134 | 65.3503 | 119.1376 | 123.6969 | 1.3412 | 123.6923 | 80.7907 | -0.21057 | 123.6969 | 1.3412 | 80.7907 | 119.1376 | 123.6923 | -124.0128 | -124.0173
1414.7188 | 124.086 | -61.4044 | 62.3337 | 0.19707 | 0.012392 | 0.012986 | 0.006979 | 0.063239 | 9.4068e-05 | 0.075204 | -59.9945 | 62.2513 | -61.6516 | -61.5555 | 57.724 | 19.3909 | 4.4083 | 3.9368 | 62.2421 | -61.6425 | -0.24719 | -0.082397 | 1.4099 | -0.15106 | -4.6097 | -0.23804 | -0.091553 | 1.6571 | 65.8127 | 65.3412 | 119.1284 | 123.6557 | 1.4099 | 123.6465 | 80.7953 | -0.23804 | 123.6557 | 1.4099 | 80.7953 | 119.1284 | 123.6465 | -123.9853 | -123.9761
1415.7188 | 124.0814 | -61.4044 | 62.3199 | -0.10811 | 0.010256 | 0.014482 | 0.0063382 | 0.063666 | -0.00097413 | 0.074563 | -60.0128 | 62.2421 | -61.6196 | -61.5509 | 57.7057 | 19.3771 | 4.4037 | 3.9139 | 62.233 | -61.647 | -0.21515 | -0.07782 | 1.3916 | -0.14648 | -4.6143 | -0.24262 | -0.086975 | 1.6068 | 65.8081 | 65.3183 | 119.1101 | 123.6465 | 1.3916 | 123.6374 | 80.7816 | -0.24262 | 123.6465 | 1.3916 | 80.7816 | 119.1101 | 123.6374 | -123.9395 | -123.967
1416.7188 | 124.1135 | -61.3815 | 62.3611 | -0.14626 | 0.0089743 | 0.016191 | 0.0056972 | 0.061316 | -0.0020421 | 0.076058 | -59.9899 | 62.2559 | -61.6379 | -61.5005 | 57.7698 | 19.4504 | 4.4769 | 4.0146 | 62.2559 | -61.6425 | -0.25635 | -0.10529 | 1.3916 | -0.11902 | -4.5914 | -0.26093 | -0.10529 | 1.6479 | 65.8585 | 65.3961 | 119.1513 | 123.6374 | 1.3916 | 123.6374 | 80.8319 | -0.26093 | 123.6374 | 1.3916 | 80.8319 | 119.1513 | 123.6374 | -123.999 | -124.0036
1417.7188 | 124.054 | -61.409 | 62.3428 | 0.082626 | 0.012606 | 0.013841 | 0.00527 | 0.062384 | 0.00030767 | 0.076272 | -60.0632 | 62.2421 | -61.647 | -61.6013 | 57.5912 | 19.3405 | 4.5273 | 3.8773 | 62.2559 | -61.6425 | -0.23804 | -0.10071 | 1.3458 | -0.19226 | -4.7516 | -0.23346 | -0.086975 | 1.5839 | 65.9363 | 65.2863 | 119.0002 | 123.6511 | 1.3458 | 123.6649 | 80.7495 | -0.23346 | 123.6511 | 1.3458 | 80.7495 | 119.0002 | 123.6649 | -123.9899 | -123.9853
1418.7188 | 124.054 | -61.4227 | 62.3657 | 0.17418 | 0.010256 | 0.014695 | 0.00527 | 0.062384 | -0.00033333 | 0.07499 | -60.0494 | 62.2238 | -61.6791 | -61.5829 | 57.6782 | 19.3771 | 4.4266 | 3.8498 | 62.2467 | -61.6608 | -0.25635 | -0.14191 | 1.3733 | -0.16022 | -4.6875 | -0.23804 | -0.11902 | 1.6296 | 65.8493 | 65.2725 | 119.101 | 123.6465 | 1.3733 | 123.6694 | 80.7999 | -0.23804 | 123.6465 | 1.3733 | 80.7999 | 119.101 | 123.6694 | -124.0448 | -124.0265
1419.7188 | 124.0631 | -61.4365 | 62.3199 | 0.15129 | 0.01346 | 0.011277 | 0.0067654 | 0.063452 | 0.0011621 | 0.076486 | -60.0174 | 62.2147 | -61.6608 | -61.5921 | 57.6645 | 19.3405 | 4.39 | 3.8635 | 62.2421 | -61.6608 | -0.22431 | -0.10529 | 1.4191 | -0.15564 | -4.6555 | -0.22431 | -0.07782 | 1.6434 | 65.8264 | 65.3 | 119.101 | 123.6511 | 1.4191 | 123.6786 | 80.777 | -0.22431 | 123.6511 | 1.4191 | 80.777 | 119.101 | 123.6786 | -123.9807 | -123.9807
1420.7188 | 124.0585 | -61.4227 | 62.3062 | 0.1284 | 0.0085471 | 0.015763 | 0.0063382 | 0.062598 | -0.00097413 | 0.07499 | -60.0128 | 62.233 | -61.647 | -61.5601 | 57.6279 | 19.3039 | 4.3579 | 3.8177 | 62.2284 | -61.6608 | -0.22431 | -0.073242 | 1.4099 | -0.13733 | -4.6783 | -0.23804 | -0.077819 | 1.6342 | 65.7806 | 65.2405 | 119.0506 | 123.6557 | 1.4099 | 123.6511 | 80.7266 | -0.23804 | 123.6557 | 1.4099 | 80.7266 | 119.0506 | 123.6511 | -123.9532 | -123.967
1421.7344 | 123.9807 | -61.4273 | 62.3932 | -0.24544 | 0.012606 | 0.011704 | 0.0089016 | 0.060889 | 0.00052127 | 0.073495 | -60.0632 | 62.3383 | -61.6425 | -61.6104 | 57.5867 | 19.2123 | 4.5868 | 3.7949 | 62.3291 | -61.6745 | -0.21515 | -0.054931 | 1.3641 | -0.18311 | -4.8065 | -0.24719 | -0.064086 | 1.5793 | 66.0141 | 65.2222 | 119.014 | 123.7656 | 1.3641 | 123.7564 | 80.6396 | -0.24719 | 123.7656 | 1.3641 | 80.6396 | 119.014 | 123.7564 | -124.0356 | -124.0677
1422.7188 | 124.0494 | -61.4182 | 62.3474 | 0.18181 | 0.0089743 | 0.010636 | 0.0046292 | 0.061957 | 0.00030767 | 0.076486 | -60.0586 | 62.2375 | -61.6653 | -61.5921 | 57.5409 | 19.249 | 4.3762 | 3.8406 | 62.2604 | -61.6241 | -0.24719 | -0.10986 | 1.3596 | -0.17395 | -4.8065 | -0.20599 | -0.086975 | 1.6067 | 65.7944 | 65.2588 | 118.959 | 123.6557 | 1.3596 | 123.6786 | 80.6671 | -0.20599 | 123.6557 | 1.3596 | 80.6671 | 118.959 | 123.6786 | -124.0128 | -123.9716
1423.7188 | 124.0494 | -61.3998 | 62.3428 | 0.19707 | 0.011965 | 0.0076456 | 0.0074062 | 0.06388 | 0.00052127 | 0.077554 | -60.022 | 62.2559 | -61.6562 | -61.5829 | 57.5317 | 19.2352 | 4.3213 | 3.7949 | 62.2513 | -61.6608 | -0.25635 | -0.086975 | 1.3779 | -0.18311 | -4.8111 | -0.26093 | -0.091552 | 1.6342 | 65.7211 | 65.1947 | 118.9316 | 123.6557 | 1.3779 | 123.6511 | 80.6351 | -0.26093 | 123.6557 | 1.3779 | 80.6351 | 118.9316 | 123.6511 | -123.999 | -124.0036
1424.7188 | 124.0631 | -61.4456 | 62.3428 | 0.082626 | 0.0098287 | 0.0132 | 0.0076198 | 0.06153 | -0.00033333 | 0.07734 | -60.0174 | 62.2604 | -61.6745 | -61.5784 | 57.4997 | 19.2261 | 4.2801 | 3.7903 | 62.2375 | -61.6837 | -0.22888 | -0.082397 | 1.4282 | -0.13275 | -4.8431 | -0.23804 | -0.10529 | 1.6571 | 65.7257 | 65.2359 | 118.9453 | 123.7061 | 1.4282 | 123.6832 | 80.6717 | -0.23804 | 123.7061 | 1.4282 | 80.6717 | 118.9453 | 123.6832 | -124.0173 | -124.0265
1425.7188 | 124.0585 | -61.4182 | 62.3337 | 0.13603 | 0.0098287 | 0.014054 | 0.0067654 | 0.062598 | 0.0018031 | 0.076486 | -59.9899 | 62.2559 | -61.6287 | -61.5601 | 57.5546 | 19.2673 | 4.3213 | 3.7399 | 62.2604 | -61.6608 | -0.21057 | -0.07782 | 1.4282 | -0.14191 | -4.7791 | -0.24262 | -0.073242 | 1.6388 | 65.7394 | 65.1581 | 118.9728 | 123.674 | 1.4282 | 123.6786 | 80.6854 | -0.24262 | 123.674 | 1.4282 | 80.6854 | 118.9728 | 123.6786 | -123.9624 | -123.9944
1426.7188 | 123.9716 | -61.441 | 62.4023 | -0.23781 | 0.011538 | 0.011491 | 0.0071926 | 0.060248 | 0.00030767 | 0.075845 | -60.054 | 62.3474 | -61.6608 | -61.6928 | 57.4585 | 19.1849 | 4.5593 | 3.804 | 62.3337 | -61.6882 | -0.21973 | -0.054932 | 1.387 | -0.25177 | -4.9438 | -0.24719 | -0.068665 | 1.6068 | 66.0004 | 65.2451 | 118.8995 | 123.7885 | 1.387 | 123.7747 | 80.6259 | -0.24719 | 123.7885 | 1.387 | 80.6259 | 118.8995 | 123.7747 | -124.0631 | -124.0906
1427.7188 | 124.086 | -61.3861 | 62.3566 | -0.16914 | 0.0089743 | 0.0078592 | 0.0039882 | 0.062384 | -0.00054693 | 0.075631 | -59.9442 | 62.2604 | -61.6241 | -61.496 | 57.7194 | 19.5236 | 4.1656 | 3.5751 | 62.2925 | -61.6013 | -0.23804 | -0.09613 | 1.442 | -0.10986 | -4.6371 | -0.21515 | -0.064087 | 1.68 | 65.5518 | 64.9612 | 119.1055 | 123.6465 | 1.442 | 123.6786 | 80.9097 | -0.21515 | 123.6465 | 1.442 | 80.9097 | 119.1055 | 123.6786 | -123.9807 | -123.9578
1428.7188 | 124.0814 | -61.3998 | 62.3337 | 0.2047 | 0.013674 | 0.010636 | 0.0091152 | 0.064093 | -0.00097413 | 0.077767 | -59.9991 | 62.2742 | -61.6608 | -61.5692 | 57.4631 | 19.249 | 4.3488 | 3.8177 | 62.2604 | -61.6745 | -0.26093 | -0.059509 | 1.4008 | -0.16937 | -4.8706 | -0.27466 | -0.073242 | 1.6617 | 65.7486 | 65.2176 | 118.8629 | 123.674 | 1.4008 | 123.6603 | 80.6488 | -0.27466 | 123.674 | 1.4008 | 80.6488 | 118.8629 | 123.6603 | -123.9944 | -124.0082
1429.7188 | 124.0814 | -61.4273 | 62.3154 | 0.18944 | 0.013033 | 0.013841 | 0.0095424 | 0.066443 | -0.0011877 | 0.07499 | -60.0266 | 62.2833 | -61.6333 | -61.5829 | 57.431 | 19.2535 | 4.3442 | 3.7445 | 62.2421 | -61.6699 | -0.20599 | -0.032044 | 1.4008 | -0.15564 | -4.8843 | -0.24262 | -0.073243 | 1.6068 | 65.7715 | 65.1718 | 118.8583 | 123.7106 | 1.4008 | 123.6694 | 80.6808 | -0.24262 | 123.7106 | 1.4008 | 80.6808 | 118.8583 | 123.6694 | -123.9487 | -123.9853
1430.7188 | 124.0952 | -61.4044 | 62.3428 | 0.11314 | 0.011538 | 0.013627 | 0.0067654 | 0.064734 | -0.0031103 | 0.075631 | -59.9808 | 62.2467 | -61.6516 | -61.5509 | 57.4539 | 19.2673 | 4.3396 | 3.8498 | 62.2604 | -61.647 | -0.24719 | -0.09613 | 1.4236 | -0.14648 | -4.8889 | -0.24262 | -0.082397 | 1.6708 | 65.744 | 65.2542 | 118.8583 | 123.6511 | 1.4236 | 123.6649 | 80.6717 | -0.24262 | 123.6511 | 1.4236 | 80.6717 | 118.8583 | 123.6649 | -123.9944 | -123.9899
1431.7188 | 124.0768 | -61.3953 | 62.3337 | 0.27336 | 0.010256 | 0.014909 | 0.0063382 | 0.062598 | -0.0016149 | 0.075631 | -59.9762 | 62.2467 | -61.647 | -61.5463 | 57.4402 | 19.2764 | 4.3121 | 3.7857 | 62.2375 | -61.6562 | -0.25177 | -0.086975 | 1.4191 | -0.15106 | -4.8935 | -0.26093 | -0.09613 | 1.6708 | 65.7074 | 65.181 | 118.8354 | 123.642 | 1.4191 | 123.6328 | 80.6717 | -0.26093 | 123.642 | 1.4191 | 80.6717 | 118.8354 | 123.6328 | -123.9807 | -123.9899
1432.7188 | 124.1089 | -61.3815 | 62.3703 | -0.047073 | 0.010683 | 0.010636 | 0.0050564 | 0.060675 | 0.0015893 | 0.075417 | -60.0037 | 62.2375 | -61.6562 | -61.5189 | 57.518 | 19.3314 | 4.3808 | 3.8635 | 62.2833 | -61.6425 | -0.27466 | -0.13275 | 1.3779 | -0.13733 | -4.8523 | -0.26093 | -0.086975 | 1.6525 | 65.7623 | 65.2451 | 118.8995 | 123.6191 | 1.3779 | 123.6649 | 80.7129 | -0.26093 | 123.6191 | 1.3779 | 80.7129 | 118.8995 | 123.6649 | -124.0265 | -124.0128
1433.7188 | 124.0723 | -61.3998 | 62.3337 | 0.91423 | 0.013033 | 0.012986 | 0.008688 | 0.063025 | -0.00011953 | 0.079263 | -59.8526 | 62.2421 | -61.6379 | -61.528 | 57.4173 | 19.2215 | 4.2526 | 3.8086 | 62.2467 | -61.6608 | -0.23804 | -0.091553 | 1.5472 | -0.12817 | -4.9164 | -0.26093 | -0.086975 | 1.7853 | 65.6525 | 65.2084 | 118.8171 | 123.642 | 1.5472 | 123.6465 | 80.6213 | -0.26093 | 123.642 | 1.5472 | 80.6213 | 118.8171 | 123.6465 | -123.9716 | -123.9944
1434.7188 | 124.0723 | -61.3953 | 62.3291 | 0.23521 | 0.012606 | 0.014909 | 0.0061246 | 0.060675 | 0.0013757 | 0.07734 | -59.9808 | 62.2604 | -61.647 | -61.5555 | 57.4265 | 19.281 | 4.2664 | 3.8177 | 62.265 | -61.6653 | -0.25177 | -0.068665 | 1.4145 | -0.16022 | -4.9026 | -0.27008 | -0.064087 | 1.6663 | 65.6616 | 65.213 | 118.8217 | 123.6557 | 1.4145 | 123.6603 | 80.6763 | -0.27008 | 123.6557 | 1.4145 | 80.6763 | 118.8217 | 123.6603 | -123.9761 | -123.9944
1435.7188 | 124.0723 | -61.4044 | 62.3245 | 0.21996 | 0.012606 | 0.017259 | 0.006979 | 0.065589 | 0.00030767 | 0.079476 | -59.9762 | 62.2513 | -61.6791 | -61.7661 | 57.3441 | 19.2719 | 4.335 | 3.772 | 62.265 | -61.6745 | -0.27466 | -0.073242 | 1.4282 | -0.36163 | -4.9805 | -0.27008 | -0.059509 | 1.7029 | 65.7394 | 65.1764 | 118.7485 | 123.6557 | 1.4282 | 123.6694 | 80.6763 | -0.27008 | 123.6557 | 1.4282 | 80.6763 | 118.7485 | 123.6694 | -124.0036 | -123.999
1436.7188 | 124.0952 | -61.4182 | 62.3383 | 0.1284 | 0.011538 | 0.015122 | 0.0054836 | 0.063239 | -0.00033333 | 0.076913 | -60.0082 | 62.2559 | -61.6608 | -61.5417 | 57.3669 | 19.2535 | 4.3991 | 3.8589 | 62.233 | -61.6653 | -0.24262 | -0.082398 | 1.4099 | -0.1236 | -4.9713 | -0.24719 | -0.10529 | 1.6525 | 65.8173 | 65.2771 | 118.7851 | 123.674 | 1.4099 | 123.6511 | 80.6717 | -0.24719 | 123.674 | 1.4099 | 80.6717 | 118.7851 | 123.6511 | -123.999 | -124.0036
1437.7188 | 124.0402 | -61.4273 | 62.3657 | 0.090256 | 0.011111 | 0.012559 | 0.00527 | 0.061316 | 0.00094847 | 0.077554 | -60.0082 | 62.2467 | -61.6379 | -61.6058 | 57.2159 | 19.1254 | 4.3716 | 3.7491 | 62.2604 | -61.6425 | -0.21057 | -0.11902 | 1.4191 | -0.17853 | -5.1498 | -0.21515 | -0.10529 | 1.6296 | 65.799 | 65.1764 | 118.6432 | 123.674 | 1.4191 | 123.6877 | 80.5527 | -0.21515 | 123.674 | 1.4191 | 80.5527 | 118.6432 | 123.6877 | -124.0036 | -124.0082
1438.7188 | 124.0906 | -61.4044 | 62.3199 | 0.11314 | 0.0096151 | 0.012986 | 0.008688 | 0.065161 | 0.00030767 | 0.07499 | -59.9625 | 62.2604 | -61.647 | -61.5417 | 57.3486 | 19.1254 | 4.303 | 3.8132 | 62.2559 | -61.6425 | -0.24262 | -0.059509 | 1.442 | -0.13733 | -4.9713 | -0.23804 | -0.064087 | 1.6846 | 65.7074 | 65.2176 | 118.7531 | 123.6649 | 1.442 | 123.6603 | 80.5298 | -0.23804 | 123.6649 | 1.442 | 80.5298 | 118.7531 | 123.6603 | -123.967 | -123.9624
1439.7188 | 124.1043 | -61.3907 | 62.3337 | 0.2581 | 0.0089743 | 0.014909 | 0.0089016 | 0.063452 | 0.00094847 | 0.076058 | -59.9945 | 62.2513 | -61.6425 | -61.5372 | 57.2754 | 19.1483 | 4.2984 | 3.8406 | 62.2467 | -61.6516 | -0.25177 | -0.082397 | 1.3962 | -0.14648 | -5.0583 | -0.26093 | -0.086975 | 1.6479 | 65.6891 | 65.2313 | 118.6661 | 123.642 | 1.3962 | 123.6374 | 80.5389 | -0.26093 | 123.642 | 1.3962 | 80.5389 | 118.6661 | 123.6374 | -123.9761 | -123.9853
1440.7188 | 124.1226 | -61.3907 | 62.3337 | 0.34966 | 0.010042 | 0.014482 | 0.0091152 | 0.061743 | -0.00097413 | 0.07499 | -59.9533 | 62.2787 | -61.6333 | -61.5601 | 57.28 | 19.2444 | 4.3488 | 3.7811 | 62.2467 | -61.647 | -0.24262 | -0.054931 | 1.4374 | -0.16937 | -5.0537 | -0.25635 | -0.086975 | 1.68 | 65.7394 | 65.1718 | 118.6707 | 123.6694 | 1.4374 | 123.6374 | 80.6351 | -0.25635 | 123.6694 | 1.4374 | 80.6351 | 118.6707 | 123.6374 | -123.967 | -123.9807
1441.7188 | 124.0906 | -61.409 | 62.3199 | 0.44121 | 0.012392 | 0.014909 | 0.0093288 | 0.063025 | 0.00030767 | 0.075631 | -59.9258 | 62.2604 | -61.6608 | -61.5372 | 57.3303 | 19.2032 | 4.3259 | 3.8269 | 62.2421 | -61.647 | -0.25177 | -0.059509 | 1.4832 | -0.12817 | -4.9896 | -0.23804 | -0.07782 | 1.7349 | 65.7349 | 65.2359 | 118.7393 | 123.6694 | 1.4832 | 123.6511 | 80.6122 | -0.23804 | 123.6694 | 1.4832 | 80.6122 | 118.7393 | 123.6511 | -123.9807 | -123.967
1442.7188 | 124.0814 | -61.3953 | 62.3245 | 0.19707 | 0.011751 | 0.011704 | 0.0078336 | 0.065161 | -0.0018285 | 0.079049 | -59.9808 | 62.2787 | -61.6699 | -61.5509 | 57.2662 | 19.1071 | 4.2709 | 3.7765 | 62.2467 | -61.6379 | -0.27466 | -0.045776 | 1.4145 | -0.15564 | -5.0583 | -0.24261 | -0.07782 | 1.6891 | 65.6662 | 65.1718 | 118.6615 | 123.674 | 1.4145 | 123.642 | 80.5023 | -0.24261 | 123.674 | 1.4145 | 80.5023 | 118.6615 | 123.642 | -123.9944 | -123.9624
1443.7188 | 124.1226 | -61.4227 | 62.3199 | 0.17418 | 0.012606 | 0.01854 | 0.0097562 | 0.063666 | -0.0020421 | 0.076486 | -60.1501 | 62.2192 | -61.6745 | -61.5692 | 57.2525 | 19.1162 | 4.2389 | 3.7949 | 62.2604 | -61.6608 | -0.25177 | -0.10071 | 1.2726 | -0.14649 | -5.0674 | -0.23804 | -0.059509 | 1.5244 | 65.6616 | 65.2176 | 118.6752 | 123.642 | 1.2726 | 123.6832 | 80.5389 | -0.23804 | 123.642 | 1.2726 | 80.5389 | 118.6752 | 123.6832 | -123.9944 | -123.9807
1444.7188 | 124.054 | -61.4136 | 62.3062 | 0.12077 | 0.011111 | 0.016191 | 0.0033474 | 0.063666 | 0.00073487 | 0.074777 | -59.9945 | 62.2559 | -61.6379 | -61.5692 | 57.2662 | 19.162 | 4.3442 | 3.7765 | 62.265 | -61.6333 | -0.2243 | -0.050354 | 1.4191 | -0.15564 | -5.04 | -0.21973 | -0.041198 | 1.6434 | 65.7578 | 65.1901 | 118.6798 | 123.6694 | 1.4191 | 123.6786 | 80.5756 | -0.21973 | 123.6694 | 1.4191 | 80.5756 | 118.6798 | 123.6786 | -123.9441 | -123.9395
1445.7188 | 124.0723 | -61.3998 | 62.3383 | 0.11314 | 0.012392 | 0.011491 | 0.0084744 | 0.062384 | 0.0011621 | 0.076272 | -59.9854 | 62.233 | -61.6425 | -61.5738 | 57.3029 | 19.1483 | 4.3808 | 3.7903 | 62.2375 | -61.6653 | -0.24262 | -0.10529 | 1.4145 | -0.17395 | -5.0354 | -0.2655 | -0.10071 | 1.6571 | 65.7806 | 65.1901 | 118.7027 | 123.6328 | 1.4145 | 123.6374 | 80.5481 | -0.2655 | 123.6328 | 1.4145 | 80.5481 | 118.7027 | 123.6374 | -123.9807 | -124.0036
1446.7188 | 124.086 | -61.3998 | 62.3337 | 0.18181 | 0.013033 | 0.012986 | 0.0074062 | 0.062598 | -0.00033333 | 0.076699 | -59.9533 | 62.2696 | -61.6379 | -61.5509 | 57.2708 | 19.0796 | 4.2709 | 3.7308 | 62.265 | -61.6562 | -0.23804 | -0.064087 | 1.4465 | -0.15106 | -5.0629 | -0.25635 | -0.068664 | 1.6846 | 65.6708 | 65.1306 | 118.6707 | 123.6694 | 1.4465 | 123.6649 | 80.4794 | -0.25635 | 123.6694 | 1.4465 | 80.4794 | 118.6707 | 123.6649 | -123.9716 | -123.9899
1447.7188 | 124.0768 | -61.3815 | 62.3978 | -0.14626 | 0.0081197 | 0.013413 | 0.0046292 | 0.061743 | 0.00030767 | 0.075631 | -59.9396 | 62.2467 | -61.6287 | -61.4914 | 57.2617 | 19.2307 | 4.3442 | 3.8269 | 62.2971 | -61.6058 | -0.24719 | -0.15106 | 1.442 | -0.10986 | -5.1361 | -0.2243 | -0.10071 | 1.6891 | 65.7257 | 65.2084 | 118.6432 | 123.6282 | 1.442 | 123.6786 | 80.6122 | -0.2243 | 123.6282 | 1.442 | 80.6122 | 118.6432 | 123.6786 | -124.0265 | -124.0036
1448.7188 | 124.054 | -61.4044 | 62.352 | 0.15129 | 0.011965 | 0.012986 | 0.0078336 | 0.064307 | -0.00054693 | 0.077554 | -59.9625 | 62.2513 | -61.6333 | -61.5509 | 57.2021 | 18.9514 | 4.2801 | 3.7354 | 62.2696 | -61.6562 | -0.22888 | -0.10071 | 1.442 | -0.14648 | -5.1498 | -0.25177 | -0.082398 | 1.6708 | 65.6845 | 65.1398 | 118.6066 | 123.6557 | 1.442 | 123.674 | 80.3558 | -0.25177 | 123.6557 | 1.442 | 80.3558 | 118.6066 | 123.674 | -123.9853 | -124.0082
1449.7188 | 124.0814 | -61.409 | 62.2696 | 0.2047 | 0.013247 | 0.0132 | 0.0095424 | 0.063452 | -0.0011877 | 0.078408 | -59.8938 | 62.2284 | -61.6196 | -61.5509 | 57.2708 | 19.0109 | 4.2618 | 3.7399 | 62.2604 | -61.6608 | -0.21057 | -0.041198 | 1.5152 | -0.14191 | -4.9988 | -0.25177 | -0.009155 | 1.7258 | 65.6708 | 65.1489 | 118.6798 | 123.6374 | 1.5152 | 123.6694 | 80.4199 | -0.25177 | 123.6374 | 1.5152 | 80.4199 | 118.6798 | 123.6694 | -123.8892 | -123.9304
1450.7188 | 124.0768 | -61.3953 | 62.3474 | 0.14366 | 0.011751 | 0.011918 | 0.0074062 | 0.063666 | 0.00052127 | 0.077126 | -59.9304 | 62.2513 | -61.6516 | -61.5555 | 57.1243 | 18.9835 | 4.2572 | 3.7674 | 62.2421 | -61.6379 | -0.25635 | -0.09613 | 1.4648 | -0.16022 | -5.2231 | -0.24261 | -0.10529 | 1.7212 | 65.6525 | 65.1627 | 118.5196 | 123.6465 | 1.4648 | 123.6374 | 80.3787 | -0.24261 | 123.6465 | 1.4648 | 80.3787 | 118.5196 | 123.6374 | -123.999 | -123.9853
1451.7188 | 124.0494 | -61.3907 | 62.3383 | 0.15892 | 0.0091879 | 0.012132 | 0.0050564 | 0.062171 | 0.00073487 | 0.076272 | -59.9762 | 62.2192 | -61.6425 | -61.5921 | 57.1106 | 19.0887 | 4.2709 | 3.6255 | 62.2559 | -61.6425 | -0.25177 | -0.11902 | 1.4145 | -0.20142 | -5.2277 | -0.25177 | -0.082398 | 1.6663 | 65.6616 | 65.0162 | 118.5013 | 123.6099 | 1.4145 | 123.6465 | 80.4794 | -0.25177 | 123.6099 | 1.4145 | 80.4794 | 118.5013 | 123.6465 | -123.9807 | -123.9807
1452.7188 | 124.0402 | -61.3724 | 62.3291 | 0.1284 | 0.010683 | 0.014695 | 0.00527 | 0.06153 | -0.0011877 | 0.077767 | -60.0266 | 62.2375 | -61.6287 | -61.5967 | 57.1198 | 18.8782 | 4.2206 | 3.6301 | 62.2559 | -61.6516 | -0.25635 | -0.091553 | 1.3458 | -0.22431 | -5.2094 | -0.27924 | -0.073243 | 1.6022 | 65.593 | 65.0024 | 118.4921 | 123.6099 | 1.3458 | 123.6282 | 80.2505 | -0.27924 | 123.6099 | 1.3458 | 80.2505 | 118.4921 | 123.6282 | -123.9578 | -123.9807
1453.7188 | 124.0311 | -61.3907 | 62.3383 | 0.16655 | 0.010897 | 0.0095682 | 0.0067654 | 0.061743 | -0.00097413 | 0.07734 | -59.9487 | 62.2467 | -61.6562 | -61.5921 | 57.0923 | 18.8828 | 4.2206 | 3.6621 | 62.2787 | -61.6516 | -0.2655 | -0.091553 | 1.442 | -0.20142 | -5.246 | -0.26093 | -0.059509 | 1.7075 | 65.6113 | 65.0528 | 118.483 | 123.6374 | 1.442 | 123.6694 | 80.2734 | -0.26093 | 123.6374 | 1.442 | 80.2734 | 118.483 | 123.6694 | -123.9944 | -123.9899
1454.7188 | 124.0494 | -61.3907 | 62.3611 | 0.15129 | 0.0098287 | 0.011918 | 0.0061246 | 0.063025 | -0.00033333 | 0.07734 | -59.9442 | 62.2513 | -61.6516 | -61.5829 | 57.0969 | 18.9011 | 4.2114 | 3.6621 | 62.2742 | -61.6425 | -0.26093 | -0.10986 | 1.4465 | -0.19226 | -5.2643 | -0.25177 | -0.086975 | 1.7075 | 65.6021 | 65.0528 | 118.4875 | 123.642 | 1.4465 | 123.6649 | 80.2917 | -0.25177 | 123.642 | 1.4465 | 80.2917 | 118.4875 | 123.6649 | -124.0128 | -124.0036
1455.7188 | 124.0631 | -61.409 | 62.3337 | 0.15129 | 0.011111 | 0.0099954 | 0.0044156 | 0.062812 | 0.00094847 | 0.07499 | -59.9533 | 62.2467 | -61.6425 | -61.5784 | 57.1381 | 18.8278 | 4.2068 | 3.6575 | 62.2421 | -61.6379 | -0.23346 | -0.086975 | 1.4557 | -0.16937 | -5.1956 | -0.22888 | -0.091553 | 1.6891 | 65.6158 | 65.0665 | 118.5471 | 123.6557 | 1.4557 | 123.6511 | 80.2368 | -0.22888 | 123.6557 | 1.4557 | 80.2368 | 118.5471 | 123.6511 | -123.9761 | -123.9716
1456.7188 | 124.0906 | -61.3953 | 62.3154 | 1.4941 | 0.0094015 | 0.012559 | 0.006979 | 0.063452 | 0.00052127 | 0.077554 | -59.8022 | 62.2513 | -61.6379 | -61.5051 | 57.1747 | 18.8278 | 4.0833 | 3.6713 | 62.2421 | -61.6333 | -0.24261 | -0.064087 | 1.593 | -0.10986 | -5.1407 | -0.23804 | -0.073243 | 1.8356 | 65.4785 | 65.0665 | 118.5699 | 123.6465 | 1.593 | 123.6374 | 80.2231 | -0.23804 | 123.6465 | 1.593 | 80.2231 | 118.5699 | 123.6374 | -123.9532 | -123.9487
1457.7188 | 124.0768 | -61.377 | 62.3657 | -0.26833 | 0.0091879 | 0.0132 | 0.0054836 | 0.062598 | 0.0011621 | 0.076486 | -59.9075 | 62.2925 | -61.5875 | -61.5097 | 57.1793 | 18.9194 | 4.2343 | 3.717 | 62.2971 | -61.6287 | -0.21057 | -0.073243 | 1.4694 | -0.13275 | -5.1865 | -0.25177 | -0.068665 | 1.68 | 65.6113 | 65.094 | 118.5562 | 123.6694 | 1.4694 | 123.674 | 80.2963 | -0.25177 | 123.6694 | 1.4694 | 80.2963 | 118.5562 | 123.674 | -123.9532 | -123.9944
1458.7188 | 124.0631 | -61.4227 | 62.3886 | 0.14366 | 0.0098287 | 0.011064 | 0.00527 | 0.06153 | 0.00094847 | 0.075417 | -59.9625 | 62.265 | -61.6608 | -61.5875 | 57.1106 | 18.8141 | 4.2206 | 3.5843 | 62.265 | -61.647 | -0.23804 | -0.1236 | 1.4603 | -0.1648 | -5.278 | -0.22431 | -0.1236 | 1.6983 | 65.6433 | 65.007 | 118.5333 | 123.6877 | 1.4603 | 123.6877 | 80.2368 | -0.22431 | 123.6877 | 1.4603 | 80.2368 | 118.5333 | 123.6877 | -124.0494 | -124.0356
1459.7188 | 124.0219 | -61.4044 | 62.3703 | 0.12077 | 0.010256 | 0.01085 | 0.0061246 | 0.061743 | 0.0013757 | 0.075845 | -59.9854 | 62.2559 | -61.6516 | -61.6013 | 57.1014 | 18.7729 | 4.248 | 3.6346 | 62.2513 | -61.6516 | -0.24719 | -0.11444 | 1.4191 | -0.19684 | -5.2689 | -0.24719 | -0.11902 | 1.6663 | 65.6525 | 65.0391 | 118.5059 | 123.6603 | 1.4191 | 123.6557 | 80.1773 | -0.24719 | 123.6603 | 1.4191 | 80.1773 | 118.5059 | 123.6557 | -124.0219 | -124.0219
1460.7188 | 124.0402 | -61.409 | 62.3566 | 0.16655 | 0.0091879 | 0.014054 | 0.00527 | 0.06388 | -0.0014013 | 0.077767 | -59.967 | 62.2467 | -61.6562 | -61.5784 | 57.0694 | 18.8095 | 4.1519 | 3.5889 | 62.2787 | -61.6516 | -0.24719 | -0.10986 | 1.442 | -0.16937 | -5.2872 | -0.24261 | -0.077819 | 1.6891 | 65.5609 | 64.9979 | 118.4784 | 123.6557 | 1.442 | 123.6877 | 80.2185 | -0.24261 | 123.6557 | 1.442 | 80.2185 | 118.4784 | 123.6877 | -124.0128 | -124.0082
1461.7188 | 124.0402 | -61.3998 | 62.3611 | -0.0012969 | 0.0094015 | 0.012345 | 0.0076198 | 0.063025 | 0.00094847 | 0.075204 | -59.9487 | 62.2559 | -61.6379 | -61.3861 | 57.1655 | 18.6951 | 4.1428 | 3.5339 | 62.2787 | -61.6425 | -0.23804 | -0.10529 | 1.4511 | 0.013733 | -5.1956 | -0.24262 | -0.082397 | 1.6891 | 65.5426 | 64.9338 | 118.5654 | 123.6557 | 1.4511 | 123.6786 | 80.0949 | -0.24262 | 123.6557 | 1.4511 | 80.0949 | 118.5654 | 123.6786 | -123.999 | -124.0036
1462.7188 | 124.0906 | -61.3815 | 62.352 | -0.1844 | 0.010042 | 0.0095682 | 0.0020656 | 0.061316 | 0.0015893 | 0.076272 | -59.8663 | 62.2742 | -61.6241 | -61.5051 | 57.1609 | 18.7592 | 4.1199 | 3.7262 | 62.2742 | -61.615 | -0.24262 | -0.07782 | 1.5152 | -0.1236 | -5.191 | -0.23346 | -0.07782 | 1.7578 | 65.5014 | 65.1077 | 118.5425 | 123.6557 | 1.5152 | 123.6557 | 80.1407 | -0.23346 | 123.6557 | 1.5152 | 80.1407 | 118.5425 | 123.6557 | -123.9761 | -123.967
1463.7188 | 124.1089 | -61.3907 | 62.3474 | 0.013962 | 0.011965 | 0.0132 | 0.0078336 | 0.063452 | 0.00052127 | 0.075204 | -59.9167 | 62.2467 | -61.6287 | -61.528 | 57.0831 | 18.7225 | 3.9459 | 3.5156 | 62.2742 | -61.6425 | -0.23804 | -0.10071 | 1.474 | -0.13733 | -5.2643 | -0.25177 | -0.073242 | 1.712 | 65.3366 | 64.9063 | 118.4738 | 123.6374 | 1.474 | 123.6649 | 80.1132 | -0.25177 | 123.6374 | 1.474 | 80.1132 | 118.4738 | 123.6649 | -123.9761 | -123.9899
1464.7188 | 124.0677 | -61.3907 | 62.352 | 0.1284 | 0.012179 | 0.0093546 | 0.0082608 | 0.061957 | -0.00097413 | 0.076272 | -59.9304 | 62.2101 | -61.6379 | -61.5646 | 57.0374 | 18.7134 | 4.0787 | 3.511 | 62.2604 | -61.6653 | -0.24719 | -0.14191 | 1.4603 | -0.17395 | -5.3146 | -0.27466 | -0.091553 | 1.7075 | 65.4694 | 64.9017 | 118.428 | 123.6008 | 1.4603 | 123.6511 | 80.1041 | -0.27466 | 123.6008 | 1.4603 | 80.1041 | 118.428 | 123.6511 | -123.9899 | -124.0173
1465.7188 | 124.0723 | -61.3953 | 62.3657 | 0.11314 | 0.010897 | 0.0082864 | 0.0056972 | 0.063239 | -0.00033333 | 0.079263 | -59.9579 | 62.2513 | -61.6196 | -61.5875 | 57.0923 | 18.6584 | 4.0878 | 3.5019 | 62.3016 | -61.615 | -0.2243 | -0.11444 | 1.4374 | -0.19226 | -5.2734 | -0.21973 | -0.064087 | 1.6617 | 65.4831 | 64.8972 | 118.4875 | 123.6465 | 1.4374 | 123.6969 | 80.0537 | -0.21973 | 123.6465 | 1.4374 | 80.0537 | 118.4875 | 123.6969 | -123.9853 | -123.9807
1466.7188 | 124.0677 | -61.3998 | 62.3657 | 0.082626 | 0.010897 | 0.012132 | 0.005911 | 0.061316 | 0.0013757 | 0.077554 | -59.9579 | 62.2513 | -61.647 | -61.5875 | 56.987 | 18.6676 | 4.0924 | 3.4973 | 62.2925 | -61.6379 | -0.24719 | -0.11444 | 1.442 | -0.18768 | -5.3787 | -0.23804 | -0.073243 | 1.6891 | 65.4922 | 64.8972 | 118.3868 | 123.6511 | 1.442 | 123.6923 | 80.0674 | -0.23804 | 123.6511 | 1.442 | 80.0674 | 118.3868 | 123.6923 | -124.0128 | -124.0036
1467.7188 | 124.0631 | -61.3815 | 62.3749 | 0.18181 | 0.0091879 | 0.01085 | 0.0056972 | 0.060034 | -0.00033333 | 0.075204 | -59.9808 | 62.2559 | -61.6425 | -61.5646 | 57.0099 | 18.6172 | 4.1016 | 3.4698 | 62.2833 | -61.6104 | -0.26093 | -0.11902 | 1.4008 | -0.1831 | -5.365 | -0.22888 | -0.091553 | 1.6617 | 65.4831 | 64.8514 | 118.3914 | 123.6374 | 1.4008 | 123.6649 | 79.9988 | -0.22888 | 123.6374 | 1.4008 | 79.9988 | 118.3914 | 123.6649 | -124.0173 | -123.9853
1468.7188 | 124.0494 | -61.4227 | 62.352 | 0.16655 | 0.011324 | 0.014482 | 0.0044156 | 0.062812 | 0.00073487 | 0.075204 | -60.0174 | 62.2513 | -61.6196 | -61.5784 | 56.9138 | 18.5532 | 4.1565 | 3.5202 | 62.265 | -61.6333 | -0.19684 | -0.10071 | 1.4053 | -0.15564 | -5.4382 | -0.21057 | -0.086975 | 1.6022 | 65.5792 | 64.9429 | 118.3365 | 123.674 | 1.4053 | 123.6877 | 79.9759 | -0.21057 | 123.674 | 1.4053 | 79.9759 | 118.3365 | 123.6877 | -123.9716 | -123.9853
1469.7188 | 124.0448 | -61.409 | 62.3428 | 0.12077 | 0.012606 | 0.012986 | 0.0050564 | 0.061316 | 0.0013757 | 0.075631 | -59.9945 | 62.2513 | -61.6425 | -61.5738 | 56.9046 | 18.5669 | 4.2023 | 3.5202 | 62.2925 | -61.615 | -0.23346 | -0.091552 | 1.4145 | -0.16479 | -5.4382 | -0.20599 | -0.050354 | 1.6479 | 65.6113 | 64.9292 | 118.3136 | 123.6603 | 1.4145 | 123.7015 | 79.9759 | -0.20599 | 123.6603 | 1.4145 | 79.9759 | 118.3136 | 123.7015 | -123.9853 | -123.9578
1470.7188 | 124.0814 | -61.3861 | 62.3566 | 0.14366 | 0.011111 | 0.013841 | 0.0050564 | 0.061743 | 0.00073487 | 0.077126 | -59.9304 | 62.2147 | -61.6425 | -61.5463 | 56.9412 | 18.5349 | 4.0466 | 3.5294 | 62.2513 | -61.647 | -0.25635 | -0.14191 | 1.4557 | -0.16022 | -5.4153 | -0.26093 | -0.10528 | 1.712 | 65.4327 | 64.9155 | 118.3273 | 123.6008 | 1.4557 | 123.6374 | 79.921 | -0.26093 | 123.6008 | 1.4557 | 79.921 | 118.3273 | 123.6374 | -123.999 | -124.0036
1471.7188 | 124.0631 | -61.3953 | 62.3566 | 0.074997 | 0.010042 | 0.011277 | 0.0050564 | 0.062812 | 0.0024439 | 0.074777 | -59.9533 | 62.2421 | -61.6241 | -61.5646 | 56.9366 | 18.4799 | 4.1428 | 3.4744 | 62.2742 | -61.6196 | -0.22888 | -0.11444 | 1.442 | -0.16937 | -5.4199 | -0.2243 | -0.082397 | 1.6708 | 65.538 | 64.8697 | 118.3319 | 123.6374 | 1.442 | 123.6694 | 79.8752 | -0.2243 | 123.6374 | 1.442 | 79.8752 | 118.3319 | 123.6694 | -123.9807 | -123.9761
1472.7188 | 123.9853 | -61.3998 | 62.4069 | -0.21492 | 0.01047 | 0.010209 | 0.0091152 | 0.062812 | -0.00097413 | 0.075204 | -59.903 | 62.3062 | -61.6241 | -61.5646 | 56.9778 | 18.5303 | 4.2801 | 3.4836 | 62.2879 | -61.6287 | -0.22431 | -0.10071 | 1.4969 | -0.16479 | -5.4291 | -0.22888 | -0.11902 | 1.7212 | 65.6799 | 64.8834 | 118.3777 | 123.7061 | 1.4969 | 123.6877 | 79.9301 | -0.22888 | 123.7061 | 1.4969 | 79.9301 | 118.3777 | 123.6877 | -124.0311 | -124.0356
1473.7188 | 124.0585 | -61.4044 | 62.3657 | 0.013962 | 0.010683 | 0.012559 | 0.0046292 | 0.06153 | -0.0014013 | 0.077981 | -59.9304 | 62.2696 | -61.6058 | -61.5601 | 56.9275 | 18.5303 | 4.1061 | 3.4698 | 62.2604 | -61.6196 | -0.20142 | -0.096131 | 1.474 | -0.15564 | -5.4382 | -0.21515 | -0.10529 | 1.6754 | 65.5106 | 64.8743 | 118.3319 | 123.674 | 1.474 | 123.6649 | 79.9347 | -0.21515 | 123.674 | 1.474 | 79.9347 | 118.3319 | 123.6649 | -123.9716 | -123.9853
1474.7188 | 124.0952 | -61.3861 | 62.3657 | -0.016556 | 0.0087607 | 0.011918 | 0.0048428 | 0.063452 | 0.00094847 | 0.07734 | -59.9304 | 62.2696 | -61.6104 | -61.5509 | 56.8863 | 18.4662 | 4.097 | 3.447 | 62.2604 | -61.6013 | -0.22431 | -0.096131 | 1.4557 | -0.16479 | -5.4794 | -0.21515 | -0.10529 | 1.68 | 65.4831 | 64.8331 | 118.2724 | 123.6557 | 1.4557 | 123.6465 | 79.8523 | -0.21515 | 123.6557 | 1.4557 | 79.8523 | 118.2724 | 123.6465 | -123.9761 | -123.967
1475.7188 | 124.0723 | -61.3861 | 62.3611 | -0.039444 | 0.010256 | 0.011491 | 0.0050564 | 0.060889 | 0.00030767 | 0.076913 | -59.9533 | 62.265 | -61.6333 | -61.5463 | 56.8359 | 18.4387 | 4.0924 | 3.4241 | 62.2971 | -61.6104 | -0.24719 | -0.09613 | 1.4328 | -0.16022 | -5.5252 | -0.22431 | -0.064087 | 1.68 | 65.4785 | 64.8102 | 118.222 | 123.6511 | 1.4328 | 123.6832 | 79.8248 | -0.22431 | 123.6511 | 1.4328 | 79.8248 | 118.222 | 123.6832 | -123.9944 | -123.9716
1476.7188 | 124.0585 | -61.3861 | 62.3886 | -0.031814 | 0.010683 | 0.012132 | 0.0037746 | 0.059821 | 0.0013757 | 0.079049 | -59.935 | 62.2696 | -61.6333 | -61.5417 | 56.8817 | 18.3929 | 4.0878 | 3.479 | 62.2833 | -61.6196 | -0.24719 | -0.11902 | 1.4511 | -0.15564 | -5.5069 | -0.23346 | -0.10529 | 1.6983 | 65.4739 | 64.8651 | 118.2678 | 123.6557 | 1.4511 | 123.6694 | 79.7791 | -0.23346 | 123.6557 | 1.4511 | 79.7791 | 118.2678 | 123.6694 | -124.0219 | -124.0082
1477.7188 | 124.086 | -61.3678 | 62.3978 | 2.8826 | 0.011965 | 0.0082864 | 0.00527 | 0.06153 | 0.0018031 | 0.075204 | -59.7839 | 62.2787 | -61.6241 | -61.4777 | 56.8954 | 18.4525 | 4.0649 | 3.479 | 62.3108 | -61.5967 | -0.25635 | -0.11902 | 1.5839 | -0.10986 | -5.5023 | -0.22888 | -0.086975 | 1.8402 | 65.4327 | 64.8468 | 118.2632 | 123.6465 | 1.5839 | 123.6786 | 79.8203 | -0.22888 | 123.6465 | 1.5839 | 79.8203 | 118.2632 | 123.6786 | -124.0219 | -123.9944
1478.7188 | 124.0631 | -61.3586 | 62.3795 | -0.054703 | 0.0089743 | 0.011277 | 0.0048428 | 0.060248 | 9.4068e-05 | 0.077981 | -59.9213 | 62.2421 | -61.6241 | -61.5417 | 56.9183 | 18.4387 | 4.0833 | 3.4836 | 62.2879 | -61.615 | -0.2655 | -0.13733 | 1.4374 | -0.1831 | -5.4611 | -0.25635 | -0.091553 | 1.7029 | 65.4419 | 64.8422 | 118.277 | 123.6008 | 1.4374 | 123.6465 | 79.7974 | -0.25635 | 123.6008 | 1.4374 | 79.7974 | 118.277 | 123.6465 | -124.0036 | -123.9944
1479.7188 | 124.0677 | -61.3495 | 62.384 | -0.38277 | 0.0089743 | 0.011491 | 0.0065518 | 0.060034 | 9.4068e-05 | 0.074777 | -59.8892 | 62.2833 | -61.6196 | -61.4777 | 56.9229 | 18.4113 | 4.0787 | 3.5065 | 62.2925 | -61.5967 | -0.27008 | -0.10071 | 1.4603 | -0.12817 | -5.4611 | -0.24719 | -0.091553 | 1.7303 | 65.4282 | 64.856 | 118.2724 | 123.6328 | 1.4603 | 123.642 | 79.7607 | -0.24719 | 123.6328 | 1.4603 | 79.7607 | 118.2724 | 123.642 | -124.0036 | -123.9807
1480.7188 | 124.0997 | -61.3724 | 62.3795 | -0.09285 | 0.010683 | 0.011918 | 0.0050564 | 0.061316 | 9.4068e-05 | 0.075204 | -59.8663 | 62.2742 | -61.6058 | -61.4456 | 56.9641 | 18.3929 | 3.978 | 3.4195 | 62.2971 | -61.5784 | -0.23346 | -0.10529 | 1.506 | -0.073243 | -5.4153 | -0.20599 | -0.082398 | 1.7395 | 65.3503 | 64.7919 | 118.3365 | 123.6465 | 1.506 | 123.6694 | 79.7653 | -0.20599 | 123.6465 | 1.506 | 79.7653 | 118.3365 | 123.6694 | -123.9853 | -123.9578
1481.7188 | 124.1043 | -61.3495 | 62.3978 | -0.14626 | 0.0089743 | 0.011064 | 0.0061246 | 0.062171 | -0.00033333 | 0.075845 | -59.7839 | 62.2467 | -61.6196 | -61.4502 | 56.9138 | 18.3746 | 4.01 | 3.4149 | 62.2879 | -61.5921 | -0.27008 | -0.15106 | 1.5656 | -0.10071 | -5.484 | -0.24261 | -0.10986 | 1.8356 | 65.3595 | 64.7644 | 118.2632 | 123.5962 | 1.5656 | 123.6374 | 79.7241 | -0.24261 | 123.5962 | 1.5656 | 79.7241 | 118.2632 | 123.6374 | -124.0173 | -123.9899
1482.7188 | 124.1226 | -61.3449 | 62.4527 | -0.17677 | 0.010042 | 0.0099954 | 0.0039882 | 0.060034 | 0.0026575 | 0.077126 | -59.8434 | 62.2421 | -61.6013 | -61.4365 | 56.9138 | 18.3929 | 4.0009 | 3.4195 | 62.2971 | -61.5829 | -0.25635 | -0.21057 | 1.5015 | -0.091552 | -5.5389 | -0.23804 | -0.15564 | 1.7578 | 65.3458 | 64.7644 | 118.2587 | 123.587 | 1.5015 | 123.642 | 79.7379 | -0.23804 | 123.587 | 1.5015 | 79.7379 | 118.2587 | 123.642 | -124.054 | -124.0356
1483.7188 | 124.0768 | -61.3632 | 62.3795 | -0.077591 | 0.011111 | 0.011918 | 0.0063382 | 0.060675 | 9.4068e-05 | 0.07734 | -59.8709 | 62.2696 | -61.5967 | -61.5097 | 56.8817 | 18.3426 | 3.8773 | 3.3463 | 62.2925 | -61.5875 | -0.23346 | -0.10986 | 1.4923 | -0.14648 | -5.4977 | -0.2243 | -0.086976 | 1.7258 | 65.2405 | 64.7095 | 118.2449 | 123.6328 | 1.4923 | 123.6557 | 79.7058 | -0.2243 | 123.6328 | 1.4923 | 79.7058 | 118.2449 | 123.6557 | -123.9761 | -123.967
1484.7188 | 124.0814 | -61.3586 | 62.3749 | -0.062332 | 0.011111 | 0.0072184 | 0.0039882 | 0.060675 | 0.0013757 | 0.076913 | -59.9075 | 62.2696 | -61.6104 | -61.528 | 56.8588 | 18.338 | 3.9871 | 3.4332 | 62.2696 | -61.6104 | -0.25177 | -0.10529 | 1.4511 | -0.16937 | -5.5161 | -0.25177 | -0.10529 | 1.7029 | 65.3458 | 64.7919 | 118.2175 | 123.6282 | 1.4511 | 123.6282 | 79.6967 | -0.25177 | 123.6282 | 1.4511 | 79.6967 | 118.2175 | 123.6282 | -123.9853 | -123.9853
1485.7188 | 124.1638 | -61.3403 | 62.3978 | -0.15388 | 0.010683 | 0.0099954 | 0.0037746 | 0.062171 | -0.00033333 | 0.075845 | -59.8022 | 62.2787 | -61.6058 | -61.4822 | 56.813 | 18.3655 | 4.0695 | 3.5294 | 62.2696 | -61.5967 | -0.2655 | -0.11902 | 1.5381 | -0.14191 | -5.5847 | -0.25635 | -0.12817 | 1.8036 | 65.4099 | 64.8697 | 118.1534 | 123.6191 | 1.5381 | 123.6099 | 79.7058 | -0.25635 | 123.6191 | 1.5381 | 79.7058 | 118.1534 | 123.6099 | -124.0036 | -123.9944
1486.7188 | 124.0448 | -61.3724 | 62.3932 | -0.19203 | 0.0087607 | 0.0132 | 0.0054836 | 0.062384 | 0.0015893 | 0.076913 | -59.8663 | 62.2925 | -61.5829 | -61.4822 | 56.7764 | 18.2602 | 4.0787 | 3.4561 | 62.3016 | -61.5921 | -0.21057 | -0.10071 | 1.506 | -0.10986 | -5.6168 | -0.21973 | -0.091552 | 1.7166 | 65.451 | 64.8285 | 118.1488 | 123.6649 | 1.506 | 123.674 | 79.6326 | -0.21973 | 123.6649 | 1.506 | 79.6326 | 118.1488 | 123.674 | -123.9761 | -123.9853
1487.7188 | 124.0356 | -61.4044 | 62.4115 | -0.069961 | 0.012392 | 0.018754 | 0.01296 | 0.065802 | -0.0020421 | 0.077767 | -59.8755 | 62.3566 | -61.6425 | -61.5463 | 56.7307 | 18.2098 | 4.0237 | 3.2867 | 62.3383 | -61.6287 | -0.23804 | -0.054932 | 1.5289 | -0.14191 | -5.6808 | -0.2243 | -0.073242 | 1.767 | 65.4282 | 64.6912 | 118.1351 | 123.761 | 1.5289 | 123.7427 | 79.6143 | -0.2243 | 123.761 | 1.5289 | 79.6143 | 118.1351 | 123.7427 | -124.054 | -124.0402
1488.7188 | 124.0356 | -61.3632 | 62.384 | -0.21492 | 0.0089743 | 0.012986 | 0.003561 | 0.062384 | 0.00094847 | 0.077981 | -59.8343 | 62.3062 | -61.6241 | -61.496 | 56.7764 | 18.2373 | 3.9871 | 3.4378 | 62.3199 | -61.6013 | -0.26093 | -0.07782 | 1.5289 | -0.13275 | -5.6076 | -0.23804 | -0.064087 | 1.7899 | 65.3503 | 64.801 | 118.1396 | 123.6694 | 1.5289 | 123.6832 | 79.6005 | -0.23804 | 123.6694 | 1.5289 | 79.6005 | 118.1396 | 123.6832 | -124.0082 | -123.9853
1489.7188 | 124.0768 | -61.3541 | 62.384 | -0.19203 | 0.0098287 | 0.014695 | 0.0084744 | 0.062598 | -0.00076053 | 0.076699 | -59.8389 | 62.2787 | -61.5967 | -61.496 | 56.8039 | 18.2877 | 4.0054 | 3.4882 | 62.2971 | -61.6013 | -0.24262 | -0.10529 | 1.5152 | -0.14191 | -5.5801 | -0.24719 | -0.086975 | 1.7578 | 65.3595 | 64.8422 | 118.158 | 123.6328 | 1.5152 | 123.6511 | 79.6417 | -0.24719 | 123.6328 | 1.5152 | 79.6417 | 118.158 | 123.6511 | -123.9807 | -123.9853
1490.7188 | 124.0952 | -61.3724 | 62.3978 | -0.131 | 0.0098287 | 0.0080728 | 0.0048428 | 0.062171 | 9.4068e-05 | 0.077981 | -59.7977 | 62.2787 | -61.5967 | -61.4777 | 56.781 | 18.306 | 3.9047 | 3.4561 | 62.2971 | -61.5738 | -0.22431 | -0.11902 | 1.5747 | -0.10529 | -5.6168 | -0.20142 | -0.10071 | 1.799 | 65.2771 | 64.8285 | 118.1534 | 123.6511 | 1.5747 | 123.6694 | 79.6783 | -0.20142 | 123.6511 | 1.5747 | 79.6783 | 118.1534 | 123.6694 | -123.9944 | -123.9716
1491.7188 | 124.0631 | -61.3586 | 62.3932 | -0.25307 | 0.0096151 | 0.013413 | 0.0050564 | 0.058112 | -0.00054693 | 0.074136 | -59.8572 | 62.2879 | -61.5875 | -61.4731 | 56.8085 | 18.3655 | 3.9276 | 3.3691 | 62.3016 | -61.6013 | -0.22888 | -0.10529 | 1.5015 | -0.11444 | -5.5847 | -0.24261 | -0.091552 | 1.7303 | 65.2863 | 64.7278 | 118.1671 | 123.6465 | 1.5015 | 123.6603 | 79.7241 | -0.24261 | 123.6465 | 1.5015 | 79.7241 | 118.1671 | 123.6603 | -123.9807 | -123.9944
1492.7188 | 124.0082 | -61.377 | 62.4207 | -0.24544 | 0.012606 | 0.0099954 | 0.006979 | 0.061743 | -0.00097413 | 0.077554 | -59.8206 | 62.3199 | -61.6058 | -61.5189 | 56.6299 | 18.1778 | 4.0009 | 3.3142 | 62.3566 | -61.615 | -0.22888 | -0.10071 | 1.5564 | -0.14191 | -5.7907 | -0.23804 | -0.064087 | 1.7853 | 65.3778 | 64.6912 | 118.0069 | 123.6969 | 1.5564 | 123.7335 | 79.5547 | -0.23804 | 123.6969 | 1.5564 | 79.5547 | 118.0069 | 123.7335 | -124.0265 | -124.0356
1493.7188 | 124.0128 | -61.3998 | 62.4298 | -0.23018 | 0.012606 | 0.0099954 | 0.0071926 | 0.06153 | 9.4068e-05 | 0.076699 | -59.9075 | 62.3062 | -61.5921 | -61.5143 | 56.749 | 18.1732 | 4.1336 | 3.3737 | 62.3383 | -61.6241 | -0.19226 | -0.1236 | 1.4923 | -0.11444 | -5.6808 | -0.22431 | -0.091553 | 1.6846 | 65.5334 | 64.7736 | 118.1488 | 123.7061 | 1.4923 | 123.7381 | 79.5731 | -0.22431 | 123.7061 | 1.4923 | 79.5731 | 118.1488 | 123.7381 | -124.0219 | -124.054
1494.7188 | 123.999 | -61.3815 | 62.3978 | -0.27596 | 0.0085471 | 0.0099954 | 0.0089016 | 0.061316 | -0.00011953 | 0.075845 | -59.8343 | 62.3154 | -61.5967 | -61.5326 | 56.749 | 18.1366 | 4.0146 | 3.3371 | 62.3154 | -61.5875 | -0.21515 | -0.082397 | 1.5472 | -0.15106 | -5.6488 | -0.20599 | -0.082397 | 1.7624 | 65.3961 | 64.7186 | 118.1305 | 123.6969 | 1.5472 | 123.6969 | 79.5181 | -0.20599 | 123.6969 | 1.5472 | 79.5181 | 118.1305 | 123.6969 | -123.9944 | -123.9853
1495.7188 | 124.0219 | -61.3724 | 62.4207 | -0.32936 | 0.011965 | 0.0097818 | 0.005911 | 0.060675 | -0.00076053 | 0.07734 | -59.7977 | 62.3016 | -61.615 | -61.5189 | 56.6254 | 18.0634 | 4.0421 | 3.3417 | 62.3383 | -61.615 | -0.24262 | -0.11902 | 1.5747 | -0.14648 | -5.7953 | -0.24262 | -0.082397 | 1.8173 | 65.4144 | 64.7141 | 117.9977 | 123.674 | 1.5747 | 123.7106 | 79.4357 | -0.24262 | 123.674 | 1.5747 | 79.4357 | 117.9977 | 123.7106 | -124.0356 | -124.0356
1496.7188 | 124.0219 | -61.3724 | 62.4023 | -0.22255 | 0.010897 | 0.014268 | 0.0078336 | 0.060675 | 9.4068e-05 | 0.079049 | -59.8434 | 62.3199 | -61.6013 | -61.5097 | 56.6345 | 18.1137 | 4.0237 | 3.3554 | 62.3245 | -61.5875 | -0.22888 | -0.082398 | 1.5289 | -0.13733 | -5.7678 | -0.21515 | -0.07782 | 1.7578 | 65.3961 | 64.7278 | 118.0069 | 123.6923 | 1.5289 | 123.6969 | 79.4861 | -0.21515 | 123.6923 | 1.5289 | 79.4861 | 118.0069 | 123.6969 | -124.0036 | -123.9899
1497.7188 | 123.9716 | -61.4182 | 62.4023 | 0.021591 | 0.015597 | 0.015336 | 0.011679 | 0.063452 | -0.00011953 | 0.077981 | -59.9121 | 62.3795 | -61.6425 | -61.6379 | 56.4926 | 17.9489 | 3.9413 | 3.1036 | 62.3383 | -61.6653 | -0.2243 | -0.022888 | 1.506 | -0.21973 | -5.9097 | -0.24719 | -0.064087 | 1.7303 | 65.3595 | 64.5218 | 117.9108 | 123.7976 | 1.506 | 123.7564 | 79.3671 | -0.24719 | 123.7976 | 1.506 | 79.3671 | 117.9108 | 123.7564 | -124.0448 | -124.0677
1498.7188 | 124.0952 | -61.3541 | 62.384 | -0.20729 | 0.012179 | 0.0072184 | 0.005911 | 0.066443 | -0.00033333 | 0.077767 | -59.7839 | 62.3016 | -61.6013 | -61.4594 | 56.6528 | 18.0817 | 3.9368 | 3.3554 | 62.2971 | -61.5967 | -0.24719 | -0.082397 | 1.5701 | -0.10529 | -5.7312 | -0.24262 | -0.086975 | 1.8173 | 65.2908 | 64.7095 | 118.0069 | 123.6557 | 1.5701 | 123.6511 | 79.4357 | -0.24262 | 123.6557 | 1.5701 | 79.4357 | 118.0069 | 123.6511 | -123.9853 | -123.9807
1499.7188 | 123.9578 | -61.409 | 62.4161 | -0.22255 | 0.011538 | 0.010209 | 0.0074062 | 0.063452 | -0.00097413 | 0.07499 | -59.8526 | 62.3245 | -61.5967 | -61.5692 | 56.694 | 18.0542 | 4.0512 | 3.1952 | 62.3611 | -61.6241 | -0.18768 | -0.091553 | 1.5564 | -0.16022 | -5.722 | -0.21515 | -0.054932 | 1.7441 | 65.4602 | 64.6042 | 118.103 | 123.7335 | 1.5564 | 123.7701 | 79.4632 | -0.21515 | 123.7335 | 1.5564 | 79.4632 | 118.103 | 123.7701 | -124.0128 | -124.0402
1500.7188 | 123.9807 | -61.3998 | 62.4161 | -0.29121 | 0.01047 | 0.014482 | 0.0080472 | 0.063025 | -0.00076053 | 0.075631 | -59.8389 | 62.3108 | -61.6287 | -61.5509 | 56.5887 | 17.981 | 4.1016 | 3.2913 | 62.3474 | -61.6058 | -0.22888 | -0.10529 | 1.561 | -0.15106 | -5.8273 | -0.20599 | -0.068665 | 1.7899 | 65.5014 | 64.6912 | 117.9886 | 123.7106 | 1.561 | 123.7473 | 79.3808 | -0.20599 | 123.7106 | 1.561 | 79.3808 | 117.9886 | 123.7473 | -124.0448 | -124.0219
1501.7188 | 123.9716 | -61.3998 | 62.439 | -0.2607 | 0.012179 | 0.011918 | 0.008688 | 0.061103 | -0.00033333 | 0.078622 | -59.8663 | 62.3337 | -61.6241 | -61.5463 | 56.5887 | 18.013 | 4.0741 | 3.2593 | 62.3428 | -61.5967 | -0.22431 | -0.10529 | 1.5335 | -0.14648 | -5.8502 | -0.19684 | -0.096131 | 1.7578 | 65.4739 | 64.6591 | 117.9886 | 123.7335 | 1.5335 | 123.7427 | 79.4128 | -0.19684 | 123.7335 | 1.5335 | 79.4128 | 117.9886 | 123.7427 | -124.0631 | -124.0356
1502.7344 | 124.0082 | -61.3998 | 62.3795 | 0.1284 | 0.012392 | 0.015122 | 0.011465 | 0.064948 | -0.00097413 | 0.07734 | -59.8251 | 62.3383 | -61.6425 | -61.6013 | 56.5201 | 17.9764 | 4.0009 | 3.2135 | 62.2971 | -61.6516 | -0.24262 | -0.041199 | 1.5747 | -0.20142 | -5.8594 | -0.25177 | -0.082398 | 1.8173 | 65.4007 | 64.6133 | 117.9199 | 123.7381 | 1.5747 | 123.6969 | 79.3762 | -0.25177 | 123.7381 | 1.5747 | 79.3762 | 117.9199 | 123.6969 | -124.0219 | -124.0311
1503.7188 | 124.0265 | -61.3495 | 62.3886 | -0.2607 | 0.011111 | 0.014054 | 0.0063382 | 0.062598 | 0.0026575 | 0.076272 | -59.8068 | 62.3108 | -61.6058 | -61.5189 | 56.6116 | 17.9947 | 4.0283 | 3.2776 | 62.3062 | -61.6013 | -0.25635 | -0.07782 | 1.5427 | -0.16937 | -5.777 | -0.25177 | -0.082398 | 1.799 | 65.3778 | 64.6271 | 117.9611 | 123.6603 | 1.5427 | 123.6557 | 79.3442 | -0.25177 | 123.6603 | 1.5427 | 79.3442 | 117.9611 | 123.6557 | -123.9944 | -123.9899
1504.7188 | 124.0677 | -61.3586 | 62.3932 | -0.21492 | 0.0034201 | 0.0097818 | 0.0029202 | 0.063025 | 0.0011621 | 0.078622 | -59.5596 | 62.3383 | -61.5509 | -61.4639 | 56.6162 | 18.1549 | 3.978 | 3.4515 | 62.3062 | -61.5921 | -0.19226 | -0.054931 | 1.799 | -0.10529 | -5.777 | -0.23346 | -0.086975 | 1.9913 | 65.3366 | 64.8102 | 117.9749 | 123.6969 | 1.799 | 123.6649 | 79.5136 | -0.23346 | 123.6969 | 1.799 | 79.5136 | 117.9749 | 123.6649 | -123.9441 | -123.9853
1505.7188 | 124.1043 | -61.3678 | 62.3795 | -0.21492 | 0.0081197 | 0.0099954 | 0.005911 | 0.061957 | -0.0022559 | 0.078195 | -59.7427 | 62.2833 | -61.6058 | -61.2946 | 56.2592 | 17.7612 | 4.0604 | 3.3554 | 62.2742 | -61.5784 | -0.23804 | -0.096131 | 1.6251 | 0.073242 | -6.1203 | -0.21057 | -0.10529 | 1.8631 | 65.4282 | 64.7232 | 117.627 | 123.6511 | 1.6251 | 123.642 | 79.129 | -0.21057 | 123.6511 | 1.6251 | 79.129 | 117.627 | 123.642 | -123.9853 | -123.9578
1506.7188 | 123.967 | -61.3678 | 62.4344 | -0.29121 | 0.012179 | 0.0132 | 0.0074062 | 0.060889 | -0.0014013 | 0.076486 | -59.848 | 62.3474 | -61.6058 | -61.5555 | 56.4423 | 17.9214 | 3.9963 | 3.273 | 62.3566 | -61.615 | -0.23804 | -0.086975 | 1.5198 | -0.18768 | -5.9921 | -0.24719 | -0.07782 | 1.7578 | 65.3641 | 64.6408 | 117.8101 | 123.7152 | 1.5198 | 123.7244 | 79.2892 | -0.24719 | 123.7152 | 1.5198 | 79.2892 | 117.8101 | 123.7244 | -124.0402 | -124.0494
1507.7344 | 124.0265 | -61.3815 | 62.352 | 0.16655 | 0.0098287 | 0.014268 | 0.003561 | 0.063452 | 0.0011621 | 0.081399 | -59.8434 | 62.2421 | -61.6241 | -61.5509 | 56.4285 | 17.8665 | 3.8086 | 3.2181 | 62.2696 | -61.6104 | -0.24262 | -0.10986 | 1.5381 | -0.16937 | -5.9235 | -0.22888 | -0.082398 | 1.7807 | 65.1901 | 64.5996 | 117.8101 | 123.6237 | 1.5381 | 123.6511 | 79.248 | -0.22888 | 123.6237 | 1.5381 | 79.248 | 117.8101 | 123.6511 | -123.9761 | -123.9624
1508.7188 | 123.999 | -61.3815 | 62.4252 | -0.24544 | 0.013247 | 0.012345 | 0.010397 | 0.058966 | 0.00052127 | 0.078835 | -59.8022 | 62.3062 | -61.6058 | -61.5189 | 56.5842 | 17.9169 | 3.9459 | 3.3234 | 62.3337 | -61.6013 | -0.2243 | -0.11902 | 1.5793 | -0.13733 | -5.8411 | -0.21973 | -0.091553 | 1.8036 | 65.3275 | 64.7049 | 117.9657 | 123.6877 | 1.5793 | 123.7152 | 79.2984 | -0.21973 | 123.6877 | 1.5793 | 79.2984 | 117.9657 | 123.7152 | -124.0311 | -124.0265
1509.7188 | 124.0631 | -61.3724 | 62.4023 | -0.25307 | 0.010042 | 0.013627 | 0.0067654 | 0.062812 | 0.0022303 | 0.075845 | -59.7931 | 62.2971 | -61.615 | -61.5051 | 56.4697 | 17.8619 | 3.8681 | 3.1815 | 62.352 | -61.6058 | -0.24262 | -0.10529 | 1.5793 | -0.13275 | -5.9326 | -0.23346 | -0.050354 | 1.8219 | 65.2405 | 64.5538 | 117.8421 | 123.6694 | 1.5793 | 123.7244 | 79.2343 | -0.23346 | 123.6694 | 1.5793 | 79.2343 | 117.8421 | 123.7244 | -124.0173 | -124.0082
1510.7188 | 124.0677 | -61.3678 | 62.4207 | -0.19966 | 0.0098287 | 0.010423 | 0.0065518 | 0.061743 | -0.00011953 | 0.076272 | -59.7702 | 62.3108 | -61.6104 | -61.4914 | 56.4972 | 17.8345 | 3.7354 | 3.1357 | 62.3474 | -61.5784 | -0.24262 | -0.10986 | 1.5976 | -0.1236 | -5.9235 | -0.21057 | -0.073242 | 1.8402 | 65.1031 | 64.5035 | 117.865 | 123.6786 | 1.5976 | 123.7152 | 79.2023 | -0.21057 | 123.6786 | 1.5976 | 79.2023 | 117.865 | 123.7152 | -124.0311 | -123.999
1511.7188 | 123.9853 | -61.3266 | 62.3978 | -0.16914 | 0.011965 | 0.014909 | 0.006979 | 0.061743 | -0.0014013 | 0.076699 | -59.761 | 62.3016 | -61.5875 | -61.4777 | 56.5292 | 17.8391 | 3.6346 | 3.5431 | 62.3428 | -61.5463 | -0.26093 | -0.09613 | 1.5656 | -0.15106 | -5.8685 | -0.21973 | -0.054932 | 1.8265 | 64.9612 | 64.8697 | 117.8558 | 123.6282 | 1.5656 | 123.6694 | 79.1656 | -0.21973 | 123.6282 | 1.5656 | 79.1656 | 117.8558 | 123.6694 | -123.9853 | -123.9441
1512.7344 | 124.086 | -61.3907 | 62.3657 | 0.2047 | 0.010683 | 0.015336 | 0.011251 | 0.066016 | 0.0028711 | 0.076699 | -59.7702 | 62.3154 | -61.615 | -61.528 | 56.369 | 17.8207 | 3.5706 | 3.0258 | 62.2559 | -61.6241 | -0.2243 | -0.050354 | 1.6205 | -0.13733 | -5.9967 | -0.23346 | -0.10986 | 1.8448 | 64.9612 | 64.4165 | 117.7597 | 123.7061 | 1.6205 | 123.6465 | 79.2114 | -0.23346 | 123.7061 | 1.6205 | 79.2114 | 117.7597 | 123.6465 | -123.9807 | -123.9899
1513.7188 | 124.0219 | -61.3632 | 62.4252 | -0.23781 | 0.010042 | 0.014054 | 0.0080472 | 0.060675 | 0.0028711 | 0.076699 | -59.8114 | 62.3245 | -61.6104 | -61.5143 | 56.3141 | 17.7658 | 3.7949 | 2.9709 | 62.3749 | -61.5921 | -0.24719 | -0.10071 | 1.5518 | -0.15106 | -6.1111 | -0.22888 | -0.050354 | 1.799 | 65.1581 | 64.3341 | 117.6773 | 123.6877 | 1.5518 | 123.7381 | 79.129 | -0.22888 | 123.6877 | 1.5518 | 79.129 | 117.6773 | 123.7381 | -124.0356 | -124.0173
1514.7188 | 124.0173 | -61.3449 | 62.4298 | -0.2607 | 0.0081197 | 0.011277 | 0.0084744 | 0.063239 | 0.00052127 | 0.076913 | -59.7519 | 62.3062 | -61.6013 | -61.5005 | 56.3553 | 17.7109 | 3.6942 | 2.9572 | 62.352 | -61.5829 | -0.25635 | -0.1236 | 1.593 | -0.15564 | -6.0745 | -0.23804 | -0.07782 | 1.8494 | 65.0391 | 64.3021 | 117.7002 | 123.6511 | 1.593 | 123.6969 | 79.0558 | -0.23804 | 123.6511 | 1.593 | 79.0558 | 117.7002 | 123.6969 | -124.0311 | -124.0128
1515.7188 | 124.0128 | -61.3586 | 62.4344 | -0.19966 | 0.01047 | 0.012773 | 0.0084744 | 0.063452 | 0.0018031 | 0.076913 | -59.7977 | 62.3291 | -61.6013 | -61.4914 | 56.3736 | 17.7383 | 3.7125 | 2.9205 | 62.3337 | -61.5921 | -0.24261 | -0.10529 | 1.561 | -0.13275 | -6.0608 | -0.23346 | -0.10071 | 1.8036 | 65.0711 | 64.2792 | 117.7322 | 123.6877 | 1.561 | 123.6923 | 79.097 | -0.23346 | 123.6877 | 1.561 | 79.097 | 117.7322 | 123.6923 | -124.0356 | -124.0265
1516.7188 | 124.0356 | -61.3815 | 62.4298 | -0.21492 | 0.01047 | 0.013627 | 0.0071926 | 0.063025 | -0.0016149 | 0.077981 | -59.7839 | 62.3245 | -61.5875 | -61.496 | 56.2866 | 17.7567 | 3.7582 | 2.9343 | 62.3428 | -61.5967 | -0.20599 | -0.10529 | 1.5976 | -0.11444 | -6.1432 | -0.21515 | -0.086976 | 1.8036 | 65.1398 | 64.3158 | 117.6682 | 123.7061 | 1.5976 | 123.7244 | 79.1382 | -0.21515 | 123.7061 | 1.5976 | 79.1382 | 117.6682 | 123.7244 | -124.0173 | -124.0265
1517.7344 | 124.0494 | -61.3678 | 62.3703 | 0.14366 | 0.012606 | 0.010423 | 0.0084744 | 0.063239 | 0.0015893 | 0.075631 | -59.7702 | 62.3108 | -61.6058 | -61.528 | 56.2363 | 17.7475 | 3.5294 | 2.8793 | 62.3154 | -61.615 | -0.23804 | -0.059509 | 1.5976 | -0.16022 | -6.134 | -0.24719 | -0.054931 | 1.8356 | 64.8972 | 64.2471 | 117.6041 | 123.6786 | 1.5976 | 123.6832 | 79.1153 | -0.24719 | 123.6786 | 1.5976 | 79.1153 | 117.6041 | 123.6832 | -123.9761 | -123.9853
1518.7188 | 124.0494 | -61.3586 | 62.3978 | -0.23781 | 0.010897 | 0.015763 | 0.0056972 | 0.061103 | 0.00073487 | 0.076486 | -59.7519 | 62.2604 | -61.5692 | -61.3083 | 56.5659 | 17.9718 | 3.2639 | 2.9388 | 62.3062 | -61.5875 | -0.21057 | -0.13733 | 1.6068 | 0.050354 | -5.8319 | -0.22888 | -0.091553 | 1.8173 | 64.6225 | 64.2975 | 117.9245 | 123.6191 | 1.6068 | 123.6649 | 79.3304 | -0.22888 | 123.6191 | 1.6068 | 79.3304 | 117.9245 | 123.6649 | -123.967 | -123.9853
1519.7188 | 124.0677 | -61.3312 | 62.3795 | -0.16151 | 0.010256 | 0.0087138 | 0.0054836 | 0.06388 | 0.00052127 | 0.078408 | -59.7473 | 62.2833 | -61.6013 | -61.4502 | 56.3049 | 17.894 | 3.6621 | 3.154 | 62.3199 | -61.5967 | -0.27008 | -0.096131 | 1.5839 | -0.11902 | -6.0745 | -0.2655 | -0.05951 | 1.8539 | 64.9933 | 64.4852 | 117.6361 | 123.6145 | 1.5839 | 123.6511 | 79.2252 | -0.2655 | 123.6145 | 1.5839 | 79.2252 | 117.6361 | 123.6511 | -123.9807 | -123.9761
1520.7188 | 124.0128 | -61.3632 | 62.4298 | -0.23781 | 0.012392 | 0.010209 | 0.0089016 | 0.06153 | 0.00030767 | 0.077126 | -59.7885 | 62.3062 | -61.6058 | -61.5189 | 56.2317 | 17.7658 | 3.8223 | 2.9755 | 62.3703 | -61.6013 | -0.24262 | -0.1236 | 1.5747 | -0.15564 | -6.1981 | -0.23804 | -0.05951 | 1.8173 | 65.1855 | 64.3387 | 117.5949 | 123.6694 | 1.5747 | 123.7335 | 79.129 | -0.23804 | 123.6694 | 1.5747 | 79.129 | 117.5949 | 123.7335 | -124.0356 | -124.0311
1521.7188 | 124.0219 | -61.377 | 62.4298 | -0.20729 | 0.010897 | 0.0087138 | 0.0061246 | 0.06153 | -0.0018285 | 0.076058 | -59.8114 | 62.3062 | -61.615 | -61.5005 | 56.3004 | 17.926 | 3.8132 | 3.035 | 62.3337 | -61.6058 | -0.23804 | -0.1236 | 1.5656 | -0.1236 | -6.1295 | -0.22888 | -0.096131 | 1.8036 | 65.1901 | 64.4119 | 117.6773 | 123.6832 | 1.5656 | 123.7106 | 79.303 | -0.22888 | 123.6832 | 1.5656 | 79.303 | 117.6773 | 123.7106 | -124.0448 | -124.0356
1522.7188 | 123.9807 | -61.3861 | 62.4115 | -0.039444 | 0.010683 | 0.016191 | 0.017233 | 0.063025 | -0.00033333 | 0.077126 | -59.7473 | 62.4069 | -61.5967 | -61.5234 | 56.2317 | 17.7383 | 3.7354 | 2.8748 | 62.352 | -61.6379 | -0.21057 | -0.004578 | 1.6388 | -0.13733 | -6.1798 | -0.25177 | -0.059509 | 1.8494 | 65.1215 | 64.2609 | 117.6178 | 123.793 | 1.6388 | 123.7381 | 79.1244 | -0.25177 | 123.793 | 1.6388 | 79.1244 | 117.6178 | 123.7381 | -124.0082 | -124.0494
1523.7188 | 124.0631 | -61.3449 | 62.3978 | -0.1844 | 0.010256 | 0.015122 | 0.004202 | 0.062812 | 0.00073487 | 0.07969 | -59.7656 | 62.2833 | -61.5921 | -61.496 | 56.3095 | 17.7521 | 3.7354 | 3.0487 | 62.3108 | -61.5921 | -0.24719 | -0.11444 | 1.5793 | -0.15106 | -6.0883 | -0.24719 | -0.086975 | 1.8265 | 65.0803 | 64.3936 | 117.6544 | 123.6282 | 1.5793 | 123.6557 | 79.097 | -0.24719 | 123.6282 | 1.5793 | 79.097 | 117.6544 | 123.6557 | -123.9899 | -123.9899
1524.7188 | 124.0494 | -61.3678 | 62.4069 | -0.29884 | 0.010683 | 0.0099954 | 0.0046292 | 0.062171 | -0.0014013 | 0.077126 | -59.7519 | 62.2879 | -61.6196 | -61.4777 | 56.282 | 17.775 | 3.7811 | 3.1723 | 62.2925 | -61.5921 | -0.25177 | -0.11902 | 1.6159 | -0.10986 | -6.1249 | -0.2243 | -0.11444 | 1.8677 | 65.1489 | 64.5401 | 117.6498 | 123.6557 | 1.6159 | 123.6603 | 79.1428 | -0.2243 | 123.6557 | 1.6159 | 79.1428 | 117.6498 | 123.6603 | -124.0265 | -123.999
1525.7188 | 124.118 | -61.3312 | 62.3978 | -0.10048 | 0.0076925 | 0.0076456 | 0.0065518 | 0.061957 | 0.0015893 | 0.078408 | -59.7702 | 62.2742 | -61.5921 | -61.4777 | 56.2408 | 17.7795 | 3.7399 | 3.1128 | 62.3108 | -61.5738 | -0.26093 | -0.1236 | 1.561 | -0.14648 | -6.1569 | -0.24262 | -0.086975 | 1.8219 | 65.0711 | 64.444 | 117.572 | 123.6053 | 1.561 | 123.642 | 79.1107 | -0.24262 | 123.6053 | 1.561 | 79.1107 | 117.572 | 123.642 | -123.9899 | -123.9716
1526.7188 | 124.0997 | -61.3358 | 62.3932 | -0.09285 | 0.0094015 | 0.011277 | 0.0063382 | 0.06153 | -0.00033333 | 0.077767 | -59.7748 | 62.2971 | -61.5967 | -61.4777 | 56.2408 | 17.8802 | 3.804 | 3.1448 | 62.3154 | -61.6058 | -0.26093 | -0.09613 | 1.561 | -0.14191 | -6.1523 | -0.27008 | -0.077819 | 1.8219 | 65.1398 | 64.4806 | 117.5766 | 123.6328 | 1.561 | 123.6511 | 79.216 | -0.27008 | 123.6328 | 1.561 | 79.216 | 117.5766 | 123.6511 | -123.9899 | -123.999
1527.7188 | 123.9944 | -61.3815 | 62.4161 | -0.12337 | 0.011751 | 0.016404 | 0.012533 | 0.063025 | 0.00073487 | 0.078195 | -59.7656 | 62.384 | -61.6058 | -61.5097 | 56.1813 | 17.7063 | 3.9001 | 3.0808 | 62.3566 | -61.6516 | -0.2243 | -0.032044 | 1.6159 | -0.12817 | -6.2347 | -0.27008 | -0.05951 | 1.8402 | 65.2817 | 64.4623 | 117.5629 | 123.7656 | 1.6159 | 123.7381 | 79.0878 | -0.27008 | 123.7656 | 1.6159 | 79.0878 | 117.5629 | 123.7381 | -124.0219 | -124.0677
1528.7188 | 124.0677 | -61.3312 | 62.3749 | -1.3593 | 0.0098287 | 0.011704 | 0.0050564 | 0.062171 | -0.00033333 | 0.078195 | -59.8663 | 62.265 | -61.5921 | -61.4639 | 56.2134 | 17.9031 | 3.8086 | 3.2684 | 62.3245 | -61.5921 | -0.26093 | -0.10986 | 1.4648 | -0.13275 | -6.1615 | -0.26093 | -0.050354 | 1.7258 | 65.1398 | 64.5996 | 117.5446 | 123.5962 | 1.4648 | 123.6557 | 79.2343 | -0.26093 | 123.5962 | 1.4648 | 79.2343 | 117.5446 | 123.6557 | -123.967 | -123.967
1529.7188 | 124.0723 | -61.3678 | 62.3886 | -0.19203 | 0.012392 | 0.01085 | -0.00049776 | 0.060034 | 0.0022303 | 0.077554 | -59.7336 | 62.2742 | -61.6058 | -61.6653 | 56.1813 | 17.8024 | 3.6346 | 3.0716 | 62.3108 | -61.5692 | -0.23804 | -0.11444 | 1.6342 | -0.29755 | -6.2073 | -0.20142 | -0.07782 | 1.8723 | 65.0024 | 64.4394 | 117.5491 | 123.642 | 1.6342 | 123.6786 | 79.1702 | -0.20142 | 123.642 | 1.6342 | 79.1702 | 117.5491 | 123.6786 | -123.9944 | -123.9578
1530.7188 | 124.0585 | -61.3541 | 62.3978 | -0.16151 | 0.01047 | 0.015977 | 0.0054836 | 0.061743 | -0.00076053 | 0.078408 | -59.7244 | 62.2879 | -61.5738 | -61.4456 | 56.0715 | 17.6697 | 3.7765 | 3.1036 | 62.3291 | -61.5646 | -0.21973 | -0.10986 | 1.6296 | -0.091553 | -6.3263 | -0.21057 | -0.068664 | 1.8494 | 65.1306 | 64.4577 | 117.4255 | 123.642 | 1.6296 | 123.6832 | 79.0237 | -0.21057 | 123.642 | 1.6296 | 79.0237 | 117.4255 | 123.6832 | -123.9716 | -123.9624
1531.7188 | 124.0997 | -61.3174 | 62.3978 | -0.077591 | 0.011111 | 0.01085 | 0.0029202 | 0.059394 | 0.00030767 | 0.079049 | -59.7427 | 62.3154 | -61.6104 | -61.4594 | 56.2088 | 17.6834 | 3.6484 | 3.0121 | 62.3154 | -61.5509 | -0.29297 | -0.082397 | 1.5747 | -0.14191 | -6.189 | -0.23346 | -0.082397 | 1.8677 | 64.9658 | 64.3295 | 117.5262 | 123.6328 | 1.5747 | 123.6328 | 79.0009 | -0.23346 | 123.6328 | 1.5747 | 79.0009 | 117.5262 | 123.6328 | -124.0082 | -123.9487
1532.7188 | 124.0036 | -61.3907 | 62.4573 | -0.1844 | 0.01282 | 0.017045 | 0.0084744 | 0.061957 | 0.0011621 | 0.077981 | -59.7748 | 62.3932 | -61.5921 | -61.5372 | 55.9937 | 17.5369 | 3.804 | 2.9114 | 62.3657 | -61.6516 | -0.20142 | -0.064087 | 1.6159 | -0.14648 | -6.4636 | -0.26093 | -0.091552 | 1.8173 | 65.1947 | 64.3021 | 117.3843 | 123.7839 | 1.6159 | 123.7564 | 78.9276 | -0.26093 | 123.7839 | 1.6159 | 78.9276 | 117.3843 | 123.7564 | -124.0494 | -124.1089
1533.7188 | 124.0219 | -61.3586 | 62.3795 | -0.09285 | 0.011111 | 0.012345 | 0.0061246 | 0.064093 | -0.00033333 | 0.077767 | -59.8343 | 62.2696 | -61.6333 | -61.5646 | 56.0852 | 17.6422 | 3.6758 | 2.7924 | 62.2971 | -61.5646 | -0.27466 | -0.10986 | 1.5244 | -0.20599 | -6.2943 | -0.20599 | -0.082398 | 1.799 | 65.0345 | 64.151 | 117.4438 | 123.6282 | 1.5244 | 123.6557 | 79.0009 | -0.20599 | 123.6282 | 1.5244 | 79.0009 | 117.4438 | 123.6557 | -124.0128 | -123.9441
1534.7188 | 124.1043 | -61.3449 | 62.3978 | -0.08522 | 0.010683 | 0.012132 | 0.0044156 | 0.061103 | 0.0011621 | 0.079049 | -59.7244 | 62.3016 | -61.5921 | -61.4548 | 56.1172 | 17.7933 | 3.6255 | 2.9755 | 62.3199 | -61.5601 | -0.24719 | -0.09613 | 1.6205 | -0.10986 | -6.2805 | -0.21515 | -0.07782 | 1.8677 | 64.9704 | 64.3204 | 117.4622 | 123.6465 | 1.6205 | 123.6649 | 79.1382 | -0.21515 | 123.6465 | 1.6205 | 79.1382 | 117.4622 | 123.6649 | -123.9899 | -123.9578
1535.7188 | 124.0768 | -61.3358 | 62.3978 | -0.062332 | 0.0094015 | 0.012559 | 0.0054836 | 0.060889 | 0.0022303 | 0.078622 | -59.7473 | 62.2696 | -61.5738 | -61.4822 | 56.0669 | 17.7246 | 3.5843 | 2.8931 | 62.3154 | -61.5738 | -0.23804 | -0.12817 | 1.5884 | -0.14648 | -6.3309 | -0.23804 | -0.082397 | 1.8265 | 64.92 | 64.2288 | 117.4026 | 123.6053 | 1.5884 | 123.6511 | 79.0604 | -0.23804 | 123.6053 | 1.5884 | 79.0604 | 117.4026 | 123.6511 | -123.9716 | -123.9716
1536.7188 | 124.0906 | -61.3358 | 62.4023 | -0.077591 | 0.011538 | 0.013627 | 0.006979 | 0.060462 | 0.00030767 | 0.078835 | -59.7931 | 62.2742 | -61.6058 | -61.4914 | 55.9799 | 17.7338 | 3.6072 | 2.829 | 62.3108 | -61.5967 | -0.27008 | -0.12817 | 1.5427 | -0.15564 | -6.4224 | -0.26093 | -0.091553 | 1.8127 | 64.9429 | 64.1647 | 117.3157 | 123.6099 | 1.5427 | 123.6465 | 79.0695 | -0.26093 | 123.6099 | 1.5427 | 79.0695 | 117.3157 | 123.6465 | -124.0082 | -123.999
1537.7188 | 124.0906 | -61.3403 | 62.4298 | -0.19966 | 0.01047 | 0.009141 | 0.005911 | 0.061957 | 9.4068e-05 | 0.075631 | -59.7748 | 62.2833 | -61.5692 | -61.4548 | 56.0989 | 17.8024 | 3.5843 | 2.8885 | 62.2971 | -61.5555 | -0.22888 | -0.14649 | 1.5656 | -0.11444 | -6.3309 | -0.21515 | -0.13275 | 1.7944 | 64.9246 | 64.2288 | 117.4393 | 123.6237 | 1.5656 | 123.6374 | 79.1428 | -0.21515 | 123.6237 | 1.5656 | 79.1428 | 117.4393 | 123.6374 | -123.999 | -123.9853
1538.7188 | 124.0723 | -61.3632 | 62.3978 | 0.013962 | 0.011324 | 0.014482 | 0.0054836 | 0.060675 | 0.0039393 | 0.079263 | -59.7839 | 62.2833 | -61.5967 | -61.5143 | 55.957 | 17.7795 | 3.6118 | 2.8244 | 62.3245 | -61.5829 | -0.23346 | -0.11444 | 1.5793 | -0.15106 | -6.4407 | -0.21973 | -0.073242 | 1.8127 | 64.975 | 64.1876 | 117.3203 | 123.6465 | 1.5793 | 123.6877 | 79.1428 | -0.21973 | 123.6465 | 1.5793 | 79.1428 | 117.3203 | 123.6877 | -123.9944 | -123.9807
1539.7188 | 124.0311 | -61.3678 | 62.3978 | 0.074997 | 0.012392 | 0.011918 | 0.004202 | 0.061743 | 0.00094847 | 0.076486 | -59.7977 | 62.2925 | -61.5967 | -61.5417 | 55.9113 | 17.5415 | 3.5339 | 2.6642 | 62.3428 | -61.5784 | -0.22888 | -0.10529 | 1.5701 | -0.17395 | -6.4865 | -0.21057 | -0.054932 | 1.799 | 64.9017 | 64.032 | 117.2791 | 123.6603 | 1.5701 | 123.7106 | 78.9093 | -0.21057 | 123.6603 | 1.5701 | 78.9093 | 117.2791 | 123.7106 | -123.9944 | -123.9761
1540.7188 | 124.0402 | -61.3449 | 62.3886 | 0.30388 | 0.010897 | 0.009141 | 0.003561 | 0.062384 | 9.4068e-05 | 0.077554 | -59.8022 | 62.2833 | -61.6058 | -61.5326 | 55.9158 | 17.4728 | 3.5568 | 2.7557 | 62.3108 | -61.5921 | -0.26093 | -0.10529 | 1.5427 | -0.18768 | -6.4728 | -0.24719 | -0.07782 | 1.8036 | 64.9017 | 64.1006 | 117.2607 | 123.6282 | 1.5427 | 123.6557 | 78.8177 | -0.24719 | 123.6282 | 1.5427 | 78.8177 | 117.2607 | 123.6557 | -123.9944 | -123.9807
1541.7188 | 124.0448 | -61.3358 | 62.3886 | -0.062332 | 0.011111 | 0.0093546 | 0.005911 | 0.060462 | 0.0011621 | 0.077126 | -59.7977 | 62.2879 | -61.6058 | -61.5051 | 55.8426 | 17.5049 | 3.566 | 2.8244 | 62.3245 | -61.5646 | -0.27008 | -0.10071 | 1.5381 | -0.16937 | -6.546 | -0.22888 | -0.064087 | 1.8082 | 64.9017 | 64.1602 | 117.1783 | 123.6237 | 1.5381 | 123.6603 | 78.8406 | -0.22888 | 123.6237 | 1.5381 | 78.8406 | 117.1783 | 123.6603 | -123.9944 | -123.9532
1542.7188 | 124.054 | -61.3403 | 62.439 | -0.1844 | 0.012179 | 0.011491 | 0.0084744 | 0.060248 | 0.0011621 | 0.077126 | -59.7198 | 62.3062 | -61.5738 | -61.4685 | 56.0165 | 17.5507 | 3.5202 | 2.7466 | 62.3245 | -61.5738 | -0.23346 | -0.13275 | 1.6205 | -0.12817 | -6.4224 | -0.23346 | -0.11444 | 1.8539 | 64.8605 | 64.0869 | 117.3569 | 123.6465 | 1.6205 | 123.6649 | 78.891 | -0.23346 | 123.6465 | 1.6205 | 78.891 | 117.3569 | 123.6649 | -124.0128 | -124.0128
1543.7188 | 124.0356 | -61.3724 | 62.4069 | -0.016556 | 0.011324 | 0.011064 | 0.00527 | 0.060889 | 9.4068e-05 | 0.078408 | -59.7885 | 62.2833 | -61.5921 | -61.5189 | 55.838 | 17.5232 | 3.4698 | 2.6367 | 62.3154 | -61.5784 | -0.21973 | -0.1236 | 1.5839 | -0.14648 | -6.5689 | -0.20599 | -0.091552 | 1.8036 | 64.8422 | 64.0091 | 117.2104 | 123.6557 | 1.5839 | 123.6877 | 78.8956 | -0.20599 | 123.6557 | 1.5839 | 78.8956 | 117.2104 | 123.6877 | -123.999 | -123.9853
1544.7188 | 124.0311 | -61.3541 | 62.4069 | -0.054703 | 0.010256 | 0.011704 | 0.0063382 | 0.061743 | -0.0014013 | 0.078195 | -59.8068 | 62.3062 | -61.615 | -61.528 | 55.8563 | 17.3813 | 3.4836 | 2.6825 | 62.3108 | -61.5692 | -0.26093 | -0.10071 | 1.5472 | -0.17395 | -6.5506 | -0.21515 | -0.09613 | 1.8082 | 64.8376 | 64.0366 | 117.2104 | 123.6603 | 1.5472 | 123.6649 | 78.7354 | -0.21515 | 123.6603 | 1.5472 | 78.7354 | 117.2104 | 123.6649 | -124.0219 | -123.9761
1545.7188 | 124.0356 | -61.3495 | 62.3978 | -0.024185 | 0.010683 | 0.014482 | 0.0089016 | 0.060889 | -0.00054693 | 0.076699 | -59.7519 | 62.2925 | -61.5646 | -61.5463 | 55.6 | 17.1753 | 3.4103 | 2.6138 | 62.3245 | -61.6058 | -0.21515 | -0.10529 | 1.5976 | -0.19684 | -6.7978 | -0.25635 | -0.073242 | 1.8127 | 64.7598 | 63.9633 | 116.9495 | 123.642 | 1.5976 | 123.674 | 78.5248 | -0.25635 | 123.642 | 1.5976 | 78.5248 | 116.9495 | 123.674 | -123.9624 | -124.0036
1546.7188 | 124.0173 | -61.3586 | 62.3886 | 0.17418 | 0.011111 | 0.011064 | 0.006979 | 0.061103 | 0.00030767 | 0.078835 | -59.8114 | 62.2559 | -61.6104 | -61.5372 | 55.7007 | 17.2806 | 3.4195 | 2.7283 | 62.2925 | -61.5967 | -0.25177 | -0.13275 | 1.5472 | -0.17853 | -6.6879 | -0.23804 | -0.096131 | 1.799 | 64.7781 | 64.0869 | 117.0593 | 123.6145 | 1.5472 | 123.6511 | 78.6392 | -0.23804 | 123.6145 | 1.5472 | 78.6392 | 117.0593 | 123.6511 | -123.999 | -123.9853
1547.7188 | 124.0814 | -61.3403 | 62.3978 | -0.062332 | 0.0076925 | 0.011704 | 0.006979 | 0.059821 | 0.0043665 | 0.081185 | -59.7244 | 62.3108 | -61.5784 | -61.4777 | 55.8197 | 17.276 | 3.4378 | 2.8107 | 62.3016 | -61.5463 | -0.23804 | -0.086975 | 1.6159 | -0.13733 | -6.5781 | -0.20599 | -0.09613 | 1.8539 | 64.7781 | 64.151 | 117.16 | 123.6511 | 1.6159 | 123.642 | 78.6163 | -0.20599 | 123.6511 | 1.6159 | 78.6163 | 117.16 | 123.642 | -123.9761 | -123.9441
1548.7188 | 124.0265 | -61.3449 | 62.4115 | 0.67772 | 0.011538 | 0.0097818 | 0.0056972 | 0.061743 | 0.0018031 | 0.079476 | -59.761 | 62.2879 | -61.5875 | -61.5234 | 55.5725 | 17.1066 | 3.5019 | 2.7145 | 62.3062 | -61.5646 | -0.24261 | -0.1236 | 1.5839 | -0.17853 | -6.839 | -0.21973 | -0.10529 | 1.8265 | 64.8468 | 64.0594 | 116.9174 | 123.6328 | 1.5839 | 123.6511 | 78.4515 | -0.21973 | 123.6328 | 1.5839 | 78.4515 | 116.9174 | 123.6511 | -123.999 | -123.9761
1549.7188 | 124.0356 | -61.3586 | 62.4023 | 0.029221 | 0.0091879 | 0.014695 | 0.0050564 | 0.061103 | 0.00094847 | 0.076913 | -59.7748 | 62.2879 | -61.6058 | -61.4273 | 55.5496 | 17.2485 | 3.511 | 2.7008 | 62.2925 | -61.5784 | -0.24719 | -0.11444 | 1.5839 | -0.068664 | -6.8527 | -0.21973 | -0.10986 | 1.8311 | 64.8697 | 64.0594 | 116.9083 | 123.6465 | 1.5839 | 123.6511 | 78.6072 | -0.21973 | 123.6465 | 1.5839 | 78.6072 | 116.9083 | 123.6511 | -124.0082 | -123.9807
1550.7188 | 124.0356 | -61.3449 | 62.3978 | 0.067368 | 0.011324 | 0.010209 | 0.006979 | 0.060462 | 0.00052127 | 0.07734 | -59.7427 | 62.2925 | -61.6104 | -61.5326 | 55.6686 | 17.1158 | 3.5339 | 2.8427 | 62.3291 | -61.5921 | -0.2655 | -0.10529 | 1.6022 | -0.18768 | -6.7291 | -0.24719 | -0.068664 | 1.8677 | 64.8788 | 64.1876 | 117.0136 | 123.6374 | 1.6022 | 123.674 | 78.4607 | -0.24719 | 123.6374 | 1.6022 | 78.4607 | 117.0136 | 123.674 | -124.0082 | -123.9899
1551.7188 | 124.0402 | -61.3678 | 62.384 | 0.16655 | 0.011538 | 0.013627 | 0.0050564 | 0.063025 | -0.00076053 | 0.07734 | -59.7473 | 62.2742 | -61.5921 | -61.5417 | 55.6137 | 17.1707 | 3.5706 | 2.8244 | 62.3154 | -61.5921 | -0.2243 | -0.10986 | 1.6205 | -0.17395 | -6.7703 | -0.2243 | -0.068664 | 1.8448 | 64.9384 | 64.1922 | 116.9815 | 123.642 | 1.6205 | 123.6832 | 78.5385 | -0.2243 | 123.642 | 1.6205 | 78.5385 | 116.9815 | 123.6832 | -123.9761 | -123.9761
1552.7188 | 124.1135 | -61.3312 | 62.4069 | -0.10048 | 0.011111 | 0.013627 | 0.0061246 | 0.061957 | -0.00033333 | 0.077126 | -59.6191 | 62.2787 | -61.5875 | -61.4548 | 55.7877 | 17.3172 | 3.5202 | 3.0258 | 62.3108 | -61.5463 | -0.25635 | -0.12817 | 1.712 | -0.1236 | -6.6193 | -0.21515 | -0.09613 | 1.9684 | 64.8514 | 64.357 | 117.1188 | 123.6099 | 1.712 | 123.642 | 78.6484 | -0.21515 | 123.6099 | 1.712 | 78.6484 | 117.1188 | 123.642 | -123.9944 | -123.9532
1553.7188 | 124.0631 | -61.3403 | 62.3703 | 0.15892 | 0.014529 | 0.012773 | 0.0078336 | 0.062812 | 0.0015893 | 0.077554 | -59.6878 | 62.2513 | -61.6058 | -61.4868 | 55.6778 | 17.2165 | 3.36 | 2.7695 | 62.2971 | -61.5875 | -0.2655 | -0.11902 | 1.6525 | -0.14648 | -6.6925 | -0.24719 | -0.073242 | 1.918 | 64.7003 | 64.1098 | 117.0181 | 123.5916 | 1.6525 | 123.6374 | 78.5568 | -0.24719 | 123.5916 | 1.6525 | 78.5568 | 117.0181 | 123.6374 | -123.9761 | -123.9578
1554.7188 | 124.0631 | -61.3266 | 62.3886 | 0.15129 | 0.01282 | 0.014482 | 0.0071926 | 0.060248 | 0.0030847 | 0.078835 | -59.7336 | 62.2604 | -61.6104 | -61.5143 | 55.6824 | 17.0517 | 3.4149 | 2.8198 | 62.2833 | -61.5875 | -0.28381 | -0.12817 | 1.593 | -0.18768 | -6.7062 | -0.26093 | -0.10529 | 1.8768 | 64.7415 | 64.1464 | 117.009 | 123.587 | 1.593 | 123.6099 | 78.3783 | -0.26093 | 123.587 | 1.593 | 78.3783 | 117.009 | 123.6099 | -123.999 | -123.9761
1555.7188 | 124.0265 | -61.3678 | 62.3886 | 0.090256 | 0.011538 | 0.011918 | 0.0054836 | 0.06153 | 0.0011621 | 0.080117 | -59.7931 | 62.2925 | -61.5784 | -61.5189 | 55.5679 | 16.983 | 3.5019 | 2.8885 | 62.2925 | -61.5921 | -0.21057 | -0.096131 | 1.5747 | -0.15106 | -6.8207 | -0.2243 | -0.096131 | 1.7853 | 64.8697 | 64.2563 | 116.9357 | 123.6603 | 1.5747 | 123.6603 | 78.3508 | -0.2243 | 123.6603 | 1.5747 | 78.3508 | 116.9357 | 123.6603 | -123.967 | -123.9807
1556.7188 | 124.0494 | -61.3495 | 62.3886 | 0.097885 | 0.010897 | 0.013413 | 0.0056972 | 0.063239 | 0.0018031 | 0.080117 | -59.6924 | 62.3016 | -61.6058 | -61.5326 | 55.5222 | 17.0746 | 3.4607 | 2.8931 | 62.2925 | -61.5784 | -0.25635 | -0.086975 | 1.6571 | -0.18311 | -6.8665 | -0.22888 | -0.096131 | 1.9135 | 64.8102 | 64.2426 | 116.8716 | 123.6511 | 1.6571 | 123.642 | 78.4241 | -0.22888 | 123.6511 | 1.6571 | 78.4241 | 116.8716 | 123.642 | -123.9944 | -123.967
1557.7188 | 124.0311 | -61.3266 | 62.4161 | -0.19966 | 0.011751 | 0.014909 | 0.0084744 | 0.061743 | -0.0011877 | 0.078195 | -59.6466 | 62.3291 | -61.5692 | -61.4731 | 55.6046 | 17.189 | 3.5706 | 2.8702 | 62.3062 | -61.5784 | -0.24262 | -0.086975 | 1.68 | -0.14648 | -6.8115 | -0.25177 | -0.10986 | 1.9226 | 64.8972 | 64.1968 | 116.9312 | 123.6557 | 1.68 | 123.6328 | 78.5156 | -0.25177 | 123.6557 | 1.68 | 78.5156 | 116.9312 | 123.6328 | -123.9853 | -123.9944
1558.7188 | 124.0768 | -61.3358 | 62.3795 | 0.1284 | 0.010897 | 0.012132 | 0.0071926 | 0.06388 | 0.00052127 | 0.07969 | -59.7061 | 62.2787 | -61.6013 | -61.528 | 55.5862 | 17.1341 | 3.4698 | 2.9297 | 62.2971 | -61.6058 | -0.2655 | -0.10071 | 1.6296 | -0.19226 | -6.7932 | -0.27008 | -0.082398 | 1.8951 | 64.8056 | 64.2654 | 116.922 | 123.6145 | 1.6296 | 123.6328 | 78.4698 | -0.27008 | 123.6145 | 1.6296 | 78.4698 | 116.922 | 123.6328 | -123.9807 | -123.9853
1559.7188 | 124.0448 | -61.3541 | 62.3428 | 0.13603 | 0.013888 | 0.0097818 | 0.0095424 | 0.062598 | 0.0024439 | 0.078835 | -59.697 | 62.2971 | -61.6379 | -61.5097 | 55.5954 | 17.0425 | 3.4012 | 2.9617 | 62.2696 | -61.6058 | -0.28381 | -0.045776 | 1.6571 | -0.15564 | -6.7474 | -0.25177 | -0.073242 | 1.9409 | 64.7552 | 64.3158 | 116.9495 | 123.6511 | 1.6571 | 123.6237 | 78.3966 | -0.25177 | 123.6511 | 1.6571 | 78.3966 | 116.9495 | 123.6237 | -123.9807 | -123.9487
1560.7188 | 124.0723 | -61.3449 | 62.3795 | 0.21233 | 0.013674 | 0.016618 | 0.0099698 | 0.063666 | 0.0013757 | 0.078408 | -59.61 | 62.2971 | -61.5784 | -61.5646 | 55.307 | 17.0288 | 3.5843 | 2.9297 | 62.2971 | -61.5601 | -0.23346 | -0.082398 | 1.7349 | -0.21973 | -7.0724 | -0.21515 | -0.082398 | 1.9684 | 64.9292 | 64.2746 | 116.6519 | 123.642 | 1.7349 | 123.642 | 78.3737 | -0.21515 | 123.642 | 1.7349 | 78.3737 | 116.6519 | 123.642 | -123.9578 | -123.9395
1561.7188 | 124.0585 | -61.3403 | 62.3611 | 0.15129 | 0.010683 | 0.014909 | 0.0091152 | 0.063025 | 0.00052127 | 0.078622 | -59.697 | 62.2879 | -61.6058 | -61.5005 | 55.6137 | 17.0746 | 3.4195 | 2.9022 | 62.3016 | -61.6058 | -0.2655 | -0.073242 | 1.6434 | -0.16022 | -6.7474 | -0.2655 | -0.059509 | 1.9089 | 64.7598 | 64.2426 | 116.954 | 123.6282 | 1.6434 | 123.642 | 78.4149 | -0.2655 | 123.6282 | 1.6434 | 78.4149 | 116.954 | 123.642 | -123.967 | -123.967
1562.7188 | 124.0265 | -61.3541 | 62.3932 | 0.14366 | 0.011751 | 0.011277 | 0.0050564 | 0.061316 | 0.0015893 | 0.080117 | -59.6878 | 62.3016 | -61.6104 | -61.5509 | 55.5771 | 17.0609 | 3.4927 | 2.9251 | 62.3016 | -61.6241 | -0.25635 | -0.091552 | 1.6663 | -0.19684 | -6.8161 | -0.27008 | -0.091552 | 1.9226 | 64.8468 | 64.2792 | 116.9312 | 123.6557 | 1.6663 | 123.6557 | 78.4149 | -0.27008 | 123.6557 | 1.6663 | 78.4149 | 116.9312 | 123.6557 | -124.0036 | -124.0173
1563.7188 | 124.0311 | -61.3861 | 62.3886 | 0.11314 | 0.011751 | 0.012559 | 0.006979 | 0.060675 | 0.0015893 | 0.077981 | -59.6649 | 62.2742 | -61.6196 | -61.5372 | 55.4535 | 16.9739 | 3.4515 | 2.8244 | 62.2787 | -61.615 | -0.23346 | -0.11444 | 1.7212 | -0.15106 | -6.9351 | -0.22888 | -0.10986 | 1.9547 | 64.8376 | 64.2105 | 116.8396 | 123.6603 | 1.7212 | 123.6649 | 78.36 | -0.22888 | 123.6603 | 1.7212 | 78.36 | 116.8396 | 123.6649 | -124.0082 | -124.0036
1564.7188 | 124.0356 | -61.3586 | 62.3749 | 0.12077 | 0.01346 | 0.0089274 | 0.006979 | 0.060889 | 0.00052127 | 0.080117 | -59.697 | 62.2971 | -61.5967 | -61.5051 | 55.4626 | 17.0746 | 3.392 | 2.8152 | 62.3154 | -61.6196 | -0.23804 | -0.07782 | 1.6617 | -0.14648 | -6.9122 | -0.26093 | -0.059509 | 1.8997 | 64.7507 | 64.1739 | 116.8213 | 123.6557 | 1.6617 | 123.674 | 78.4332 | -0.26093 | 123.6557 | 1.6617 | 78.4332 | 116.8213 | 123.674 | -123.9716 | -123.9944
1565.7188 | 124.0494 | -61.3449 | 62.352 | 0.097885 | 0.01346 | 0.014909 | 0.0065518 | 0.062384 | 0.00052127 | 0.077767 | -59.6741 | 62.2742 | -61.5967 | -61.5097 | 55.4169 | 17.038 | 3.4424 | 2.8748 | 62.2971 | -61.6241 | -0.25177 | -0.07782 | 1.6708 | -0.16479 | -6.9351 | -0.27924 | -0.054932 | 1.9226 | 64.7873 | 64.2197 | 116.7618 | 123.6191 | 1.6708 | 123.642 | 78.3829 | -0.27924 | 123.6191 | 1.6708 | 78.3829 | 116.7618 | 123.642 | -123.9487 | -123.9761
1566.7188 | 124.0448 | -61.3449 | 62.384 | 0.13603 | 0.0098287 | 0.014268 | 0.0084744 | 0.062812 | 0.0026575 | 0.077981 | -59.6375 | 62.3245 | -61.5692 | -61.5005 | 55.3711 | 16.8137 | 3.2959 | 2.6505 | 62.3016 | -61.5921 | -0.2243 | -0.059509 | 1.7075 | -0.15564 | -7.0129 | -0.24719 | -0.082397 | 1.9318 | 64.6408 | 63.9954 | 116.716 | 123.6694 | 1.7075 | 123.6465 | 78.1586 | -0.24719 | 123.6694 | 1.7075 | 78.1586 | 116.716 | 123.6465 | -123.9532 | -123.9761
1567.7188 | 124.0906 | -61.3266 | 62.4252 | -0.22255 | 0.011111 | 0.0095682 | 0.0063382 | 0.062171 | 0.00094847 | 0.079263 | -59.6237 | 62.3108 | -61.5692 | -61.441 | 55.5084 | 16.8457 | 3.4378 | 2.9709 | 62.3154 | -61.5738 | -0.24262 | -0.11444 | 1.7029 | -0.11444 | -6.9168 | -0.24719 | -0.10986 | 1.9455 | 64.7644 | 64.2975 | 116.835 | 123.6374 | 1.7029 | 123.642 | 78.1723 | -0.24719 | 123.6374 | 1.7029 | 78.1723 | 116.835 | 123.642 | -123.9944 | -123.999
1568.7188 | 124.0677 | -61.3495 | 62.3611 | 0.16655 | 0.011324 | 0.0072184 | 0.0091152 | 0.061743 | 0.0013757 | 0.079263 | -59.642 | 62.2879 | -61.5784 | -61.5051 | 55.4214 | 16.7725 | 3.3142 | 2.8152 | 62.3154 | -61.5875 | -0.22888 | -0.073242 | 1.7075 | -0.15564 | -6.9397 | -0.23804 | -0.045776 | 1.9363 | 64.6637 | 64.1647 | 116.7709 | 123.6374 | 1.7075 | 123.6649 | 78.1219 | -0.23804 | 123.6374 | 1.7075 | 78.1219 | 116.7709 | 123.6649 | -123.9395 | -123.9487
1569.7188 | 124.0356 | -61.3495 | 62.3703 | 0.1284 | 0.011751 | 0.014268 | 0.0056972 | 0.062171 | 0.0028711 | 0.078622 | -59.6695 | 62.2879 | -61.6013 | -61.5463 | 55.3848 | 16.7679 | 3.4012 | 2.742 | 62.3154 | -61.5967 | -0.25177 | -0.082397 | 1.68 | -0.19684 | -6.9855 | -0.24719 | -0.054931 | 1.9318 | 64.7507 | 64.0915 | 116.7343 | 123.6374 | 1.68 | 123.6649 | 78.1174 | -0.24719 | 123.6374 | 1.68 | 78.1174 | 116.7343 | 123.6649 | -123.9716 | -123.967
1570.7188 | 124.0082 | -61.377 | 62.3795 | 0.097885 | 0.013674 | 0.010209 | 0.0056972 | 0.062384 | 0.0018031 | 0.080331 | -59.6878 | 62.265 | -61.5921 | -61.5372 | 55.2887 | 16.9739 | 3.4515 | 2.7878 | 62.3062 | -61.5967 | -0.21515 | -0.11444 | 1.6891 | -0.16022 | -7.0908 | -0.21973 | -0.073243 | 1.9043 | 64.8285 | 64.1647 | 116.6656 | 123.642 | 1.6891 | 123.6832 | 78.3508 | -0.21973 | 123.642 | 1.6891 | 78.3508 | 116.6656 | 123.6832 | -123.9716 | -123.9761
1571.7188 | 124.0311 | -61.3449 | 62.3932 | 0.2047 | 0.012179 | 0.012345 | 0.0082608 | 0.061103 | -0.0024695 | 0.078835 | -59.6603 | 62.2879 | -61.6058 | -61.5234 | 55.3436 | 16.8411 | 3.3325 | 2.6688 | 62.2925 | -61.5738 | -0.26093 | -0.10529 | 1.6846 | -0.17853 | -7.0496 | -0.22888 | -0.10071 | 1.9455 | 64.6774 | 64.0137 | 116.6885 | 123.6328 | 1.6846 | 123.6374 | 78.186 | -0.22888 | 123.6328 | 1.6846 | 78.186 | 116.6885 | 123.6374 | -123.999 | -123.967
1572.7188 | 124.0677 | -61.3495 | 62.4023 | -0.08522 | 0.012179 | 0.010209 | 0.0063382 | 0.062812 | 0.0011621 | 0.080331 | -59.6054 | 62.2879 | -61.5875 | -61.4594 | 55.4077 | 16.8732 | 3.4241 | 2.7969 | 62.3062 | -61.5601 | -0.23804 | -0.11444 | 1.7441 | -0.10986 | -6.9946 | -0.21057 | -0.096131 | 1.9821 | 64.7736 | 64.1464 | 116.7572 | 123.6374 | 1.7441 | 123.6557 | 78.2227 | -0.21057 | 123.6374 | 1.7441 | 78.2227 | 116.7572 | 123.6557 | -123.9899 | -123.9624
1573.7188 | 124.0265 | -61.3495 | 62.3932 | 0.17418 | 0.01346 | 0.010209 | 0.010397 | 0.064734 | 0.0028711 | 0.079263 | -59.6558 | 62.2833 | -61.5829 | -61.5234 | 55.3619 | 16.7221 | 3.3279 | 2.6367 | 62.3016 | -61.5875 | -0.23346 | -0.10986 | 1.6937 | -0.17395 | -7.0312 | -0.23804 | -0.091552 | 1.9272 | 64.6774 | 63.9862 | 116.7114 | 123.6328 | 1.6937 | 123.6511 | 78.0716 | -0.23804 | 123.6328 | 1.6937 | 78.0716 | 116.7114 | 123.6511 | -123.9761 | -123.9807
1574.7188 | 124.086 | -61.3678 | 62.3749 | 0.22758 | 0.015383 | 0.017686 | 0.010611 | 0.061103 | 0.0030847 | 0.079049 | -59.8114 | 62.2467 | -61.6013 | -61.5097 | 55.2841 | 16.8823 | 3.4012 | 2.6276 | 62.2742 | -61.5829 | -0.23346 | -0.12817 | 1.5564 | -0.14191 | -7.0908 | -0.21515 | -0.10071 | 1.7899 | 64.769 | 63.9954 | 116.6519 | 123.6145 | 1.5564 | 123.642 | 78.2501 | -0.21515 | 123.6145 | 1.5564 | 78.2501 | 116.6519 | 123.642 | -123.9761 | -123.9578
1575.7188 | 124.0128 | -61.3403 | 62.3749 | 0.15129 | 0.011111 | 0.013841 | 0.006979 | 0.062171 | 0.00094847 | 0.078622 | -59.642 | 62.2787 | -61.5921 | -61.5005 | 55.2658 | 16.7221 | 3.3096 | 2.6505 | 62.3108 | -61.5829 | -0.25177 | -0.09613 | 1.6983 | -0.16022 | -7.1091 | -0.24262 | -0.064087 | 1.9501 | 64.65 | 63.9908 | 116.6061 | 123.6191 | 1.6983 | 123.6511 | 78.0624 | -0.24262 | 123.6191 | 1.6983 | 78.0624 | 116.6061 | 123.6511 | -123.967 | -123.9578
1576.7188 | 124.0402 | -61.3358 | 62.384 | 0.16655 | 0.011751 | 0.01085 | 0.0054836 | 0.06153 | -0.00097413 | 0.081399 | -59.6649 | 62.3016 | -61.5829 | -61.528 | 55.2521 | 16.7999 | 3.5202 | 2.71 | 62.3154 | -61.5921 | -0.24719 | -0.082397 | 1.6708 | -0.19226 | -7.132 | -0.25635 | -0.068664 | 1.918 | 64.856 | 64.0457 | 116.5878 | 123.6374 | 1.6708 | 123.6511 | 78.1357 | -0.25635 | 123.6374 | 1.6708 | 78.1357 | 116.5878 | 123.6511 | -123.967 | -123.9761
1577.7188 | 123.999 | -61.3312 | 62.4207 | -0.024185 | 0.012179 | 0.014268 | 0.006979 | 0.064093 | 0.0037257 | 0.079263 | -59.6924 | 62.3016 | -61.5875 | -61.5417 | 55.307 | 16.777 | 3.4058 | 2.6596 | 62.3062 | -61.6058 | -0.25635 | -0.11902 | 1.6388 | -0.21057 | -7.1136 | -0.27466 | -0.11444 | 1.8951 | 64.7369 | 63.9908 | 116.6382 | 123.6328 | 1.6388 | 123.6374 | 78.1082 | -0.27466 | 123.6328 | 1.6388 | 78.1082 | 116.6382 | 123.6374 | -124.0082 | -124.0265
1578.7188 | 124.0173 | -61.3403 | 62.3886 | 0.18944 | 0.011965 | 0.010209 | 0.006979 | 0.060675 | 0.00052127 | 0.078408 | -59.642 | 62.2833 | -61.5967 | -61.528 | 55.1285 | 16.6626 | 3.447 | 2.6321 | 62.2833 | -61.5784 | -0.25635 | -0.10529 | 1.6983 | -0.18768 | -7.2601 | -0.23804 | -0.10529 | 1.9547 | 64.7873 | 63.9725 | 116.4688 | 123.6237 | 1.6983 | 123.6237 | 78.0029 | -0.23804 | 123.6237 | 1.6983 | 78.0029 | 116.4688 | 123.6237 | -123.9853 | -123.967
1579.7188 | 124.0265 | -61.3541 | 62.4069 | 0.21996 | 0.012392 | 0.012132 | 0.0084744 | 0.060034 | 0.0022303 | 0.07969 | -59.6329 | 62.2787 | -61.5967 | -61.5234 | 55.1056 | 16.7496 | 3.3783 | 2.6321 | 62.2971 | -61.5875 | -0.24262 | -0.12817 | 1.7212 | -0.16937 | -7.3013 | -0.23346 | -0.10986 | 1.9638 | 64.7324 | 63.9862 | 116.4597 | 123.6328 | 1.7212 | 123.6511 | 78.1036 | -0.23346 | 123.6328 | 1.7212 | 78.1036 | 116.4597 | 123.6511 | -124.0036 | -123.9944
1580.7188 | 124.0677 | -61.3541 | 62.3749 | 0.097885 | 0.01282 | 0.014054 | 0.0078336 | 0.062171 | -0.00033333 | 0.078622 | -59.5734 | 62.2833 | -61.5921 | -61.4777 | 55.0095 | 16.6306 | 3.241 | 2.7283 | 62.2971 | -61.5829 | -0.23804 | -0.091553 | 1.7807 | -0.1236 | -7.3654 | -0.22888 | -0.07782 | 2.0187 | 64.595 | 64.0823 | 116.3635 | 123.6374 | 1.7807 | 123.6511 | 77.9846 | -0.22888 | 123.6374 | 1.7807 | 77.9846 | 116.3635 | 123.6511 | -123.967 | -123.9578
1581.7188 | 124.0768 | -61.3449 | 62.3795 | 0.3878 | 0.013033 | 0.011064 | 0.0097562 | 0.06388 | 0.00030767 | 0.080331 | -59.6054 | 62.3199 | -61.5601 | -61.4731 | 55.0232 | 16.5619 | 3.2455 | 2.623 | 62.3108 | -61.5784 | -0.21515 | -0.05951 | 1.7395 | -0.12817 | -7.3563 | -0.23346 | -0.068665 | 1.9547 | 64.5905 | 63.9679 | 116.3681 | 123.6649 | 1.7395 | 123.6557 | 77.9068 | -0.23346 | 123.6649 | 1.7395 | 77.9068 | 116.3681 | 123.6557 | -123.9395 | -123.9578
1582.7188 | 124.0631 | -61.3266 | 62.4023 | -0.1844 | 0.010897 | 0.01555 | 0.0056972 | 0.063025 | 9.4068e-05 | 0.078835 | -59.5596 | 62.3291 | -61.5417 | -61.4365 | 55.0095 | 16.4703 | 3.3508 | 2.71 | 62.3703 | -61.5646 | -0.21515 | -0.073242 | 1.767 | -0.10986 | -7.3929 | -0.23804 | -0.032044 | 1.9821 | 64.6774 | 64.0366 | 116.3361 | 123.6557 | 1.767 | 123.6969 | 77.7969 | -0.23804 | 123.6557 | 1.767 | 77.7969 | 116.3361 | 123.6969 | -123.9441 | -123.967
1583.7188 | 124.0402 | -61.3312 | 62.4069 | 0.17418 | 0.011965 | 0.0076456 | 0.0078336 | 0.060889 | 0.0018031 | 0.080117 | -59.6237 | 62.3154 | -61.5967 | -61.5097 | 54.9225 | 16.3742 | 3.4058 | 2.6917 | 62.3245 | -61.5784 | -0.2655 | -0.091552 | 1.7075 | -0.17853 | -7.4844 | -0.24719 | -0.082397 | 1.973 | 64.7369 | 64.0228 | 116.2537 | 123.6465 | 1.7075 | 123.6557 | 77.7054 | -0.24719 | 123.6465 | 1.7075 | 77.7054 | 116.2537 | 123.6557 | -124.0036 | -123.9853
1584.7188 | 124.0311 | -61.3403 | 62.4023 | 0.04448 | 0.011324 | 0.01085 | 0.0074062 | 0.060889 | -0.00054693 | 0.079476 | -59.6466 | 62.3016 | -61.6058 | -61.528 | 55.0598 | 16.5161 | 3.4149 | 2.7466 | 62.3016 | -61.5829 | -0.2655 | -0.10071 | 1.6937 | -0.18768 | -7.3425 | -0.24262 | -0.10071 | 1.9592 | 64.7552 | 64.0869 | 116.4001 | 123.642 | 1.6937 | 123.642 | 77.8564 | -0.24262 | 123.642 | 1.6937 | 77.8564 | 116.4001 | 123.642 | -124.0082 | -123.9853
1585.7188 | 124.0356 | -61.3358 | 62.3978 | -0.016556 | 0.010897 | 0.016831 | 0.0078336 | 0.062384 | 0.0022303 | 0.078408 | -59.5734 | 62.3108 | -61.5875 | -61.5234 | 54.982 | 16.3422 | 3.3417 | 2.6367 | 62.3383 | -61.5784 | -0.25177 | -0.086975 | 1.7624 | -0.18768 | -7.4158 | -0.24262 | -0.059509 | 2.0142 | 64.6774 | 63.9725 | 116.3177 | 123.6465 | 1.7624 | 123.674 | 77.6779 | -0.24262 | 123.6465 | 1.7624 | 77.6779 | 116.3177 | 123.674 | -123.9853 | -123.9761
1586.7188 | 124.0128 | -61.3312 | 62.3886 | 0.029221 | 0.011751 | 0.011918 | 0.0048428 | 0.060675 | 0.0028711 | 0.079263 | -59.6146 | 62.2925 | -61.5875 | -61.5189 | 55.0003 | 16.4017 | 3.3966 | 2.7283 | 62.3199 | -61.5509 | -0.25635 | -0.096131 | 1.7166 | -0.18768 | -7.3883 | -0.21973 | -0.068665 | 1.973 | 64.7278 | 64.0594 | 116.3315 | 123.6237 | 1.7166 | 123.6511 | 77.7328 | -0.21973 | 123.6237 | 1.7166 | 77.7328 | 116.3315 | 123.6511 | -123.9761 | -123.9395
1587.7188 | 124.086 | -61.3129 | 62.384 | -0.17677 | 0.0096151 | 0.012132 | 0.0067654 | 0.061316 | -0.0011877 | 0.075417 | -59.4818 | 62.3199 | -61.5555 | -61.1298 | 55.1514 | 16.127 | 3.2501 | 2.8244 | 62.3062 | -61.5646 | -0.24262 | -0.064087 | 1.8311 | 0.1831 | -7.2327 | -0.25177 | -0.07782 | 2.0737 | 64.563 | 64.1373 | 116.4642 | 123.6328 | 1.8311 | 123.6191 | 77.4399 | -0.25177 | 123.6328 | 1.8311 | 77.4399 | 116.4642 | 123.6191 | -123.9395 | -123.9487
1588.7188 | 124.0448 | -61.3174 | 62.4023 | 0.14366 | 0.011324 | 0.010636 | 0.0097562 | 0.061957 | 0.0030847 | 0.080544 | -59.6283 | 62.2833 | -61.5875 | -61.5189 | 54.8172 | 16.3376 | 3.3417 | 2.6688 | 62.3062 | -61.5555 | -0.27008 | -0.11902 | 1.6891 | -0.20142 | -7.5851 | -0.23804 | -0.096131 | 1.9592 | 64.6591 | 63.9862 | 116.1346 | 123.6008 | 1.6891 | 123.6237 | 77.655 | -0.23804 | 123.6008 | 1.6891 | 77.655 | 116.1346 | 123.6237 | -123.9899 | -123.9578
1589.7188 | 124.0265 | -61.3403 | 62.4115 | 0.021591 | 0.0098287 | 0.013627 | 0.0054836 | 0.059607 | 0.0024439 | 0.080758 | -59.61 | 62.3062 | -61.5692 | -61.4822 | 54.8538 | 16.3284 | 3.3463 | 2.742 | 62.3383 | -61.5555 | -0.22888 | -0.10529 | 1.7303 | -0.14191 | -7.5577 | -0.21515 | -0.073242 | 1.9592 | 64.6866 | 64.0823 | 116.1942 | 123.6465 | 1.7303 | 123.6786 | 77.6688 | -0.21515 | 123.6465 | 1.7303 | 77.6688 | 116.1942 | 123.6786 | -123.9807 | -123.967
1590.7188 | 124.0723 | -61.3174 | 62.4023 | -0.0012969 | 0.011965 | 0.012345 | 0.0050564 | 0.061957 | 0.0013757 | 0.078835 | -59.6008 | 62.3108 | -61.5692 | -61.4685 | 54.7989 | 16.1591 | 3.2455 | 2.7374 | 62.3291 | -61.5646 | -0.25177 | -0.091553 | 1.7166 | -0.15106 | -7.6035 | -0.24719 | -0.073242 | 1.9684 | 64.563 | 64.0549 | 116.1163 | 123.6282 | 1.7166 | 123.6465 | 77.4765 | -0.24719 | 123.6282 | 1.7166 | 77.4765 | 116.1163 | 123.6465 | -123.9716 | -123.967
1591.7188 | 124.0356 | -61.3083 | 62.4161 | -0.12337 | 0.013033 | 0.012345 | 0.0048428 | 0.061957 | 0.0035121 | 0.077767 | -59.5505 | 62.3062 | -61.5692 | -61.4685 | 54.7119 | 16.1407 | 3.2501 | 2.6688 | 62.3245 | -61.5509 | -0.26093 | -0.10986 | 1.7578 | -0.16022 | -7.7042 | -0.24261 | -0.091553 | 2.0187 | 64.5584 | 63.9771 | 116.0202 | 123.6145 | 1.7578 | 123.6328 | 77.449 | -0.24261 | 123.6145 | 1.7578 | 77.449 | 116.0202 | 123.6328 | -123.9853 | -123.967
1592.7188 | 124.0631 | -61.2991 | 62.4664 | -0.16914 | 0.010897 | 0.015977 | 0.0080472 | 0.061103 | 0.0022303 | 0.080117 | -59.4498 | 62.2879 | -61.5326 | -61.4044 | 54.9133 | 16.2598 | 3.2547 | 2.7283 | 62.3199 | -61.5463 | -0.23346 | -0.17853 | 1.8494 | -0.10529 | -7.5531 | -0.24719 | -0.14648 | 2.0828 | 64.5538 | 64.0274 | 116.2125 | 123.587 | 1.8494 | 123.6191 | 77.5589 | -0.24719 | 123.587 | 1.8494 | 77.5589 | 116.2125 | 123.6191 | -123.999 | -124.0128
1593.7188 | 123.9853 | -61.3266 | 62.4573 | -0.1844 | 0.013247 | 0.010636 | 0.011679 | 0.06388 | 0.0013757 | 0.079049 | -59.5963 | 62.4161 | -61.5921 | -61.5097 | 54.57 | 16.0538 | 3.3005 | 2.5314 | 62.3795 | -61.5921 | -0.2655 | -0.041198 | 1.7303 | -0.18311 | -7.8873 | -0.2655 | -0.077819 | 1.9958 | 64.6271 | 63.858 | 115.8966 | 123.7427 | 1.7303 | 123.7061 | 77.3804 | -0.2655 | 123.7427 | 1.7303 | 77.3804 | 115.8966 | 123.7061 | -124.0494 | -124.0494
1594.7188 | 124.0494 | -61.3174 | 62.4023 | -0.024185 | 0.011751 | 0.010209 | 0.0067654 | 0.062598 | 0.0020167 | 0.079049 | -59.6008 | 62.2833 | -61.5555 | -61.4685 | 54.6661 | 16.1636 | 3.3096 | 2.6505 | 62.3428 | -61.5234 | -0.23804 | -0.11902 | 1.7166 | -0.15106 | -7.7362 | -0.20599 | -0.05951 | 1.9547 | 64.6271 | 63.9679 | 115.9836 | 123.6008 | 1.7166 | 123.6603 | 77.4811 | -0.20599 | 123.6008 | 1.7166 | 77.4811 | 115.9836 | 123.6603 | -123.9578 | -123.9258
1595.7188 | 124.0906 | -61.3129 | 62.4069 | -0.10048 | 0.013247 | 0.011277 | 0.0046292 | 0.061103 | 0.0032983 | 0.079049 | -59.4681 | 62.3199 | -61.5601 | -61.4227 | 54.689 | 16.2094 | 3.1815 | 2.6321 | 62.3337 | -61.5372 | -0.24719 | -0.086975 | 1.8448 | -0.10986 | -7.7179 | -0.2243 | -0.073242 | 2.092 | 64.4943 | 63.945 | 116.0019 | 123.6328 | 1.8448 | 123.6465 | 77.5223 | -0.2243 | 123.6328 | 1.8448 | 77.5223 | 116.0019 | 123.6465 | -123.967 | -123.9441
1596.7188 | 124.0356 | -61.2946 | 62.4298 | -0.54298 | 0.01282 | 0.009141 | 0.0039882 | 0.060034 | 0.0015893 | 0.07969 | -59.523 | 62.3154 | -61.5509 | -61.4365 | 54.6844 | 16.1041 | 3.1403 | 2.5589 | 62.3566 | -61.5326 | -0.25635 | -0.11444 | 1.7715 | -0.14191 | -7.7454 | -0.23804 | -0.073243 | 2.0279 | 64.4348 | 63.8535 | 115.979 | 123.6099 | 1.7715 | 123.6511 | 77.3987 | -0.23804 | 123.6099 | 1.7715 | 77.3987 | 115.979 | 123.6511 | -123.9807 | -123.9624
1597.7188 | 123.9716 | -61.3495 | 62.4756 | -0.16914 | 0.014529 | 0.014695 | 0.010611 | 0.063025 | 0.0018031 | 0.07969 | -59.5505 | 62.4252 | -61.5784 | -61.5097 | 54.6021 | 15.9851 | 3.2959 | 2.4811 | 62.3978 | -61.5875 | -0.22888 | -0.050354 | 1.799 | -0.16022 | -7.8735 | -0.23804 | -0.07782 | 2.0279 | 64.6454 | 63.8306 | 115.9515 | 123.7747 | 1.799 | 123.7473 | 77.3346 | -0.23804 | 123.7747 | 1.799 | 77.3346 | 115.9515 | 123.7473 | -124.054 | -124.0631
1598.7188 | 124.0036 | -61.3312 | 62.4435 | 1.5093 | 0.014529 | 0.017045 | 0.014883 | 0.066443 | -0.0020421 | 0.077767 | -59.3765 | 62.3886 | -61.5875 | -61.4685 | 54.744 | 16.1682 | 3.2089 | 2.4536 | 62.3749 | -61.5829 | -0.25635 | -0.054931 | 1.9547 | -0.13733 | -7.6996 | -0.25177 | -0.068664 | 2.211 | 64.5401 | 63.7848 | 116.0751 | 123.7198 | 1.9547 | 123.7061 | 77.4994 | -0.25177 | 123.7198 | 1.9547 | 77.4994 | 116.0751 | 123.7061 | -124.0311 | -124.0265
1599.7188 | 124.0448 | -61.3129 | 62.4252 | -0.11574 | 0.013033 | 0.012559 | 0.005911 | 0.065802 | -0.00076053 | 0.080544 | -59.4818 | 62.3474 | -61.5692 | -61.4456 | 54.8584 | 16.1957 | 3.1265 | 2.5131 | 62.3611 | -61.5234 | -0.25635 | -0.07782 | 1.8311 | -0.13275 | -7.5668 | -0.21057 | -0.064087 | 2.0874 | 64.4394 | 63.826 | 116.1713 | 123.6603 | 1.8311 | 123.674 | 77.5085 | -0.21057 | 123.6603 | 1.8311 | 77.5085 | 116.1713 | 123.674 | -123.9944 | -123.9487
1600.7188 | 124.054 | -61.3312 | 62.4298 | -0.1844 | 0.011111 | 0.013627 | 0.0074062 | 0.063452 | 9.4068e-05 | 0.078835 | -59.5551 | 62.3291 | -61.5601 | -61.4456 | 54.7028 | 16.0995 | 3.241 | 2.536 | 62.352 | -61.5417 | -0.22888 | -0.10071 | 1.7761 | -0.11444 | -7.7271 | -0.21057 | -0.07782 | 2.005 | 64.5721 | 63.8672 | 116.0339 | 123.6603 | 1.7761 | 123.6832 | 77.4307 | -0.21057 | 123.6603 | 1.7761 | 77.4307 | 116.0339 | 123.6832 | -123.9899 | -123.9716
1601.7188 | 124.0997 | -61.3083 | 62.4435 | -0.21492 | 0.01047 | 0.015336 | 0.012106 | 0.064521 | -0.00097413 | 0.079476 | -59.4315 | 62.3383 | -61.5417 | -61.4319 | 54.6341 | 16.0263 | 3.0853 | 2.504 | 62.3428 | -61.5509 | -0.23346 | -0.10529 | 1.8768 | -0.1236 | -7.8094 | -0.24261 | -0.10071 | 2.1103 | 64.3936 | 63.8123 | 115.9424 | 123.6465 | 1.8768 | 123.6511 | 77.3346 | -0.24261 | 123.6465 | 1.8768 | 77.3346 | 115.9424 | 123.6511 | -123.9853 | -123.9944
1602.7188 | 123.9624 | -61.3541 | 62.4481 | 0.059738 | 0.015383 | 0.013413 | 0.012106 | 0.062384 | 0.0041529 | 0.078622 | -59.5367 | 62.3932 | -61.5738 | -61.5326 | 54.6753 | 16.008 | 3.1494 | 2.4307 | 62.4069 | -61.5967 | -0.21973 | -0.054932 | 1.8173 | -0.17853 | -7.7728 | -0.24262 | -0.041199 | 2.037 | 64.5035 | 63.7848 | 116.0294 | 123.7473 | 1.8173 | 123.761 | 77.3621 | -0.24262 | 123.7473 | 1.8173 | 77.3621 | 116.0294 | 123.761 | -124.0219 | -124.0448
1603.7344 | 123.9258 | -61.3724 | 62.4619 | 0.021591 | 0.01346 | 0.016191 | 0.013601 | 0.064734 | -0.0016149 | 0.077981 | -59.5459 | 62.4207 | -61.5875 | -61.5646 | 54.5151 | 15.8157 | 3.1265 | 2.4261 | 62.3886 | -61.615 | -0.21515 | -0.041199 | 1.8265 | -0.19226 | -7.9468 | -0.24262 | -0.073242 | 2.0416 | 64.4989 | 63.7985 | 115.8875 | 123.793 | 1.8265 | 123.761 | 77.1881 | -0.24262 | 123.793 | 1.8265 | 77.1881 | 115.8875 | 123.761 | -124.0494 | -124.0768
1604.7188 | 123.9532 | -61.3403 | 62.4619 | -0.21492 | 0.013888 | 0.017472 | 0.010397 | 0.063452 | 0.0015893 | 0.079263 | -59.5596 | 62.4023 | -61.6013 | -61.528 | 54.6387 | 15.9393 | 3.1723 | 2.3575 | 62.4161 | -61.5692 | -0.26093 | -0.059509 | 1.7807 | -0.18768 | -7.8232 | -0.22888 | -0.045776 | 2.0416 | 64.5126 | 63.6978 | 115.979 | 123.7427 | 1.7807 | 123.7564 | 77.2797 | -0.22888 | 123.7427 | 1.7807 | 77.2797 | 115.979 | 123.7564 | -124.0631 | -124.0311
1605.7188 | 123.9532 | -61.3495 | 62.4847 | -0.23781 | 0.013247 | 0.014695 | 0.008688 | 0.064307 | 0.00030767 | 0.080758 | -59.5642 | 62.4023 | -61.5829 | -61.528 | 54.7211 | 15.8615 | 3.2272 | 2.4307 | 62.439 | -61.5692 | -0.23346 | -0.082397 | 1.7853 | -0.17853 | -7.7637 | -0.21973 | -0.045776 | 2.0187 | 64.5767 | 63.7802 | 116.0706 | 123.7518 | 1.7853 | 123.7885 | 77.211 | -0.21973 | 123.7518 | 1.7853 | 77.211 | 116.0706 | 123.7885 | -124.0677 | -124.054
1606.7188 | 123.9899 | -61.3174 | 62.5626 | -0.22255 | 0.014742 | 0.012773 | 0.010183 | 0.063452 | 0.0011621 | 0.080331 | -59.5779 | 62.3978 | -61.5829 | -61.5372 | 54.5105 | 15.9119 | 3.1311 | 2.3026 | 62.4115 | -61.5555 | -0.2655 | -0.1648 | 1.7395 | -0.21973 | -8.0521 | -0.23804 | -0.15106 | 2.005 | 64.4485 | 63.62 | 115.8279 | 123.7152 | 1.7395 | 123.7289 | 77.2293 | -0.23804 | 123.7152 | 1.7395 | 77.2293 | 115.8279 | 123.7289 | -124.1455 | -124.118
1607.7188 | 123.8892 | -61.3312 | 62.4619 | -0.15388 | 0.012392 | 0.015763 | 0.0095424 | 0.064093 | -0.00011953 | 0.079904 | -59.5459 | 62.3886 | -61.5692 | -61.5463 | 54.4464 | 15.8615 | 3.2639 | 2.5497 | 62.4344 | -61.5738 | -0.23804 | -0.073242 | 1.7853 | -0.21515 | -8.0154 | -0.24262 | -0.027466 | 2.0233 | 64.595 | 63.8809 | 115.7776 | 123.7198 | 1.7853 | 123.7656 | 77.1927 | -0.24262 | 123.7198 | 1.7853 | 77.1927 | 115.7776 | 123.7656 | -124.0311 | -124.0356
1608.7188 | 123.9395 | -61.3861 | 62.4527 | 0.12077 | 0.01346 | 0.012345 | 0.014456 | 0.06388 | 0.0020167 | 0.080758 | -59.4955 | 62.4344 | -61.5921 | -61.5875 | 54.3823 | 15.6647 | 3.1448 | 2.4353 | 62.4161 | -61.6104 | -0.20599 | -0.018311 | 1.8906 | -0.20142 | -8.0704 | -0.22431 | -0.036621 | 2.0966 | 64.5309 | 63.8214 | 115.7684 | 123.8205 | 1.8906 | 123.8022 | 77.0508 | -0.22431 | 123.8205 | 1.8906 | 77.0508 | 115.7684 | 123.8022 | -124.0448 | -124.0631
1609.7188 | 123.9532 | -61.3586 | 62.4664 | -0.23781 | 0.01282 | 0.0087138 | 0.006979 | 0.061316 | -0.00054693 | 0.080544 | -59.4864 | 62.4115 | -61.5875 | -61.6974 | 54.4098 | 15.8249 | 3.1082 | 2.3163 | 62.4435 | -61.5967 | -0.22888 | -0.054932 | 1.8723 | -0.33874 | -8.0566 | -0.23804 | -0.022889 | 2.1011 | 64.4669 | 63.6749 | 115.7684 | 123.7701 | 1.8723 | 123.8022 | 77.1835 | -0.23804 | 123.7701 | 1.8723 | 77.1835 | 115.7684 | 123.8022 | -124.054 | -124.0631
1610.7188 | 123.9761 | -61.3449 | 62.4893 | -0.14626 | 0.015383 | 0.015122 | 0.011465 | 0.06623 | -0.00011953 | 0.079476 | -59.491 | 62.4252 | -61.5875 | -61.496 | 54.6112 | 15.8981 | 3.0167 | 2.2705 | 62.4435 | -61.5784 | -0.24261 | -0.064087 | 1.8539 | -0.15106 | -7.8781 | -0.23346 | -0.045777 | 2.0966 | 64.3616 | 63.6154 | 115.9561 | 123.7701 | 1.8539 | 123.7885 | 77.243 | -0.23346 | 123.7701 | 1.8539 | 77.243 | 115.9561 | 123.7885 | -124.0768 | -124.0677
1611.7188 | 123.9716 | -61.322 | 62.471 | -0.16151 | 0.014101 | 0.013627 | 0.010183 | 0.06687 | 9.4068e-05 | 0.080758 | -59.4498 | 62.439 | -61.5646 | -61.5189 | 54.4647 | 15.509 | 3.0029 | 2.3163 | 62.4298 | -61.5646 | -0.24262 | -0.032043 | 1.8723 | -0.19684 | -8.0063 | -0.24262 | -0.041198 | 2.1149 | 64.325 | 63.6383 | 115.7867 | 123.761 | 1.8723 | 123.7518 | 76.8311 | -0.24262 | 123.761 | 1.8723 | 76.8311 | 115.7867 | 123.7518 | -124.0356 | -124.0356
1612.7188 | 123.9349 | -61.3632 | 62.4481 | 0.18181 | 0.016024 | 0.016618 | 0.012106 | 0.065589 | 0.00052127 | 0.082253 | -59.5322 | 62.4298 | -61.5967 | -61.5646 | 54.4281 | 15.4633 | 2.8976 | 2.2522 | 62.4023 | -61.6241 | -0.23346 | -0.01831 | 1.8311 | -0.20142 | -8.02 | -0.26093 | -0.045776 | 2.0645 | 64.2609 | 63.6154 | 115.7913 | 123.793 | 1.8311 | 123.7656 | 76.8265 | -0.26093 | 123.793 | 1.8311 | 76.8265 | 115.7913 | 123.7656 | -124.0448 | -124.0723
1613.7188 | 123.9807 | -61.3678 | 62.4252 | -0.13863 | 0.012392 | 0.021745 | 0.010611 | 0.06623 | 0.0028711 | 0.080544 | -59.4818 | 62.4435 | -61.5692 | -61.5143 | 54.483 | 15.6509 | 3.0167 | 2.4307 | 62.4344 | -61.6013 | -0.20142 | 0.01831 | 1.886 | -0.14648 | -7.9422 | -0.23346 | 0.009155 | 2.0874 | 64.3845 | 63.7985 | 115.8508 | 123.8113 | 1.886 | 123.8022 | 77.0187 | -0.23346 | 123.8113 | 1.886 | 77.0187 | 115.8508 | 123.8022 | -123.9944 | -124.0265
1614.7188 | 123.9578 | -61.3312 | 62.4481 | -0.15388 | 0.015169 | 0.017045 | 0.011892 | 0.067298 | 9.4068e-05 | 0.07969 | -59.4681 | 62.4527 | -61.5784 | -61.5234 | 54.4052 | 15.6281 | 3.0533 | 2.4033 | 62.4527 | -61.5967 | -0.24719 | 0.004578 | 1.8631 | -0.19226 | -8.0429 | -0.2655 | 0.004578 | 2.1103 | 64.3845 | 63.7344 | 115.7364 | 123.7839 | 1.8631 | 123.7839 | 76.9592 | -0.2655 | 123.7839 | 1.8631 | 76.9592 | 115.7364 | 123.7839 | -124.0265 | -124.0448
1615.7188 | 123.9624 | -61.3358 | 62.471 | 0.41832 | 0.013674 | 0.014909 | 0.0084744 | 0.064948 | 9.4068e-05 | 0.082467 | -59.3994 | 62.4481 | -61.6058 | -61.5372 | 54.3274 | 15.5869 | 3.0899 | 2.3026 | 62.4481 | -61.6104 | -0.27008 | -0.022888 | 1.9363 | -0.20142 | -8.1436 | -0.27466 | -0.022888 | 2.2064 | 64.4257 | 63.6383 | 115.6631 | 123.7839 | 1.9363 | 123.7839 | 76.9226 | -0.27466 | 123.7839 | 1.9363 | 76.9226 | 115.6631 | 123.7839 | -124.0768 | -124.0814
1616.7188 | 123.9578 | -61.3541 | 62.4847 | -0.23781 | 0.017733 | 0.014054 | 0.0099698 | 0.067725 | 0.0015893 | 0.082253 | -59.5779 | 62.4619 | -61.5601 | -61.528 | 54.4144 | 15.5777 | 2.9938 | 2.2842 | 62.4298 | -61.5738 | -0.20599 | -0.022888 | 1.7761 | -0.17395 | -8.0704 | -0.21973 | -0.054931 | 1.9821 | 64.3478 | 63.6383 | 115.7684 | 123.8159 | 1.7761 | 123.7839 | 76.9318 | -0.21973 | 123.8159 | 1.7761 | 76.9318 | 115.7684 | 123.7839 | -124.0448 | -124.0585
1617.7188 | 124.0036 | -61.377 | 62.3886 | 0.11314 | 0.01581 | 0.01854 | 0.0095424 | 0.067939 | 0.0013757 | 0.080117 | -59.6146 | 62.4344 | -61.6104 | -61.6196 | 54.2725 | 15.4907 | 2.948 | 2.211 | 62.4207 | -61.615 | -0.23346 | 0.045776 | 1.7624 | -0.24262 | -8.1161 | -0.23804 | 0.032043 | 1.9959 | 64.325 | 63.588 | 115.6494 | 123.8113 | 1.7624 | 123.7976 | 76.8677 | -0.23804 | 123.8113 | 1.7624 | 76.8677 | 115.6494 | 123.7976 | -123.999 | -124.0036
1618.7188 | 123.9716 | -61.3586 | 62.4619 | -0.14626 | 0.012392 | 0.016404 | 0.010397 | 0.067511 | -0.00076053 | 0.080544 | -59.3903 | 62.4664 | -61.5601 | -61.4868 | 54.4052 | 15.7059 | 2.8748 | 2.3666 | 62.4115 | -61.5921 | -0.20142 | 0.004578 | 1.9684 | -0.12817 | -8.0566 | -0.23346 | -0.050354 | 2.1698 | 64.2334 | 63.7253 | 115.7639 | 123.8251 | 1.9684 | 123.7701 | 77.0645 | -0.23346 | 123.8251 | 1.9684 | 77.0645 | 115.7639 | 123.7701 | -124.0219 | -124.054
1619.7188 | 123.999 | -61.3495 | 62.4207 | -0.054703 | 0.013888 | 0.014482 | 0.010824 | 0.067298 | 0.0020167 | 0.079263 | -59.4131 | 62.4573 | -61.5646 | -61.5005 | 54.3869 | 15.7288 | 2.9526 | 2.4078 | 62.3795 | -61.6058 | -0.21515 | 0.036621 | 1.9363 | -0.15106 | -8.0338 | -0.25635 | -0.041198 | 2.1515 | 64.3021 | 63.7573 | 115.7364 | 123.8068 | 1.9363 | 123.7289 | 77.0782 | -0.25635 | 123.8068 | 1.9363 | 77.0782 | 115.7364 | 123.7289 | -123.9853 | -124.0265
1620.7188 | 123.9624 | -61.322 | 62.4344 | -0.19203 | 0.01346 | 0.017259 | 0.012533 | 0.065589 | 0.00052127 | 0.081185 | -59.4315 | 62.4161 | -61.5509 | -61.4914 | 54.3549 | 15.7654 | 2.9114 | 2.3758 | 62.4252 | -61.615 | -0.22888 | -0.01831 | 1.8906 | -0.16937 | -8.0795 | -0.29297 | -0.009155 | 2.1194 | 64.2334 | 63.6978 | 115.6769 | 123.7381 | 1.8906 | 123.7473 | 77.0874 | -0.29297 | 123.7381 | 1.8906 | 77.0874 | 115.6769 | 123.7473 | -123.9853 | -124.0494
1621.7188 | 123.9807 | -61.3449 | 62.4527 | -0.22255 | 0.014315 | 0.01555 | 0.010397 | 0.066657 | -0.00033333 | 0.079049 | -59.3491 | 62.4573 | -61.5692 | -61.496 | 54.3594 | 15.7654 | 2.8061 | 2.2293 | 62.4115 | -61.6104 | -0.2243 | 0.004577 | 1.9958 | -0.15106 | -8.0933 | -0.2655 | -0.041199 | 2.2202 | 64.151 | 63.5742 | 115.7043 | 123.8022 | 1.9958 | 123.7564 | 77.1103 | -0.2655 | 123.8022 | 1.9958 | 77.1103 | 115.7043 | 123.7564 | -124.0219 | -124.0631
1622.7188 | 123.9349 | -61.3403 | 62.4252 | -0.5735 | 0.014529 | 0.019608 | 0.0091152 | 0.067725 | 0.0030847 | 0.082894 | -59.4269 | 62.4481 | -61.5784 | -61.5875 | 54.126 | 15.3534 | 2.7878 | 2.1194 | 62.4298 | -61.6104 | -0.23804 | 0.022888 | 1.9135 | -0.24719 | -8.2993 | -0.27008 | 0.004578 | 2.1515 | 64.1281 | 63.4598 | 115.4663 | 123.7885 | 1.9135 | 123.7701 | 76.6937 | -0.27008 | 123.7885 | 1.9135 | 76.6937 | 115.4663 | 123.7701 | -124.0036 | -124.0356
1623.7188 | 123.9716 | -61.3449 | 62.4344 | -0.12337 | 0.017306 | 0.017259 | 0.010824 | 0.066016 | 0.00052127 | 0.082894 | -59.4177 | 62.4664 | -61.5601 | -61.4868 | 54.4235 | 15.5365 | 2.9022 | 2.2934 | 62.4481 | -61.5829 | -0.21515 | 0.032044 | 1.9272 | -0.14191 | -8.0109 | -0.23804 | 0.013733 | 2.1423 | 64.2471 | 63.6383 | 115.7684 | 123.8113 | 1.9272 | 123.793 | 76.8814 | -0.23804 | 123.8113 | 1.9272 | 76.8814 | 115.7684 | 123.793 | -123.9944 | -124.0173
1624.7188 | 124.0128 | -61.3495 | 62.4344 | -0.14626 | 0.016451 | 0.020036 | 0.011038 | 0.066016 | 0.0020167 | 0.080758 | -59.491 | 62.439 | -61.5738 | -61.5005 | 54.0619 | 15.3122 | 2.8976 | 2.1881 | 62.4069 | -61.6241 | -0.2243 | 0.004578 | 1.8585 | -0.15106 | -8.3725 | -0.27466 | -0.027466 | 2.0828 | 64.2471 | 63.5376 | 115.4114 | 123.7885 | 1.8585 | 123.7564 | 76.6617 | -0.27466 | 123.7885 | 1.8585 | 76.6617 | 115.4114 | 123.7564 | -124.0082 | -124.0585
1625.7188 | 123.8754 | -61.3586 | 62.439 | -0.054703 | 0.014101 | 0.014695 | 0.011679 | 0.066016 | 0.0022303 | 0.081185 | -59.3903 | 62.4344 | -61.5738 | -61.5051 | 54.3869 | 15.4816 | 2.8473 | 2.2842 | 62.4481 | -61.5921 | -0.21515 | -0.004578 | 1.9684 | -0.14648 | -8.0521 | -0.23346 | 0.009155 | 2.1835 | 64.2059 | 63.6429 | 115.7455 | 123.793 | 1.9684 | 123.8068 | 76.8402 | -0.23346 | 123.793 | 1.9684 | 76.8402 | 115.7455 | 123.8068 | -124.0128 | -124.0311
1626.7188 | 124.0036 | -61.3129 | 62.4481 | -0.054703 | 0.014529 | 0.011704 | 0.0095424 | 0.066443 | -0.0018285 | 0.078408 | -59.3857 | 62.4847 | -61.5692 | -61.496 | 54.2953 | 15.4724 | 2.774 | 2.1149 | 62.4344 | -61.5738 | -0.25635 | 0.036621 | 1.9272 | -0.18311 | -8.1528 | -0.26093 | -0.013733 | 2.1835 | 64.0869 | 63.4277 | 115.6082 | 123.7976 | 1.9272 | 123.7473 | 76.7853 | -0.26093 | 123.7976 | 1.9272 | 76.7853 | 115.6082 | 123.7473 | -124.0173 | -124.0219
1627.7188 | 123.9349 | -61.3403 | 62.4481 | -0.031814 | 0.015169 | 0.019822 | 0.01296 | 0.066443 | 0.0013757 | 0.081613 | -59.4131 | 62.4481 | -61.5738 | -61.5463 | 54.126 | 15.3076 | 2.6962 | 2.0233 | 62.4573 | -61.6196 | -0.23346 | 0 | 1.9272 | -0.20599 | -8.3221 | -0.27924 | 0.009155 | 2.1606 | 64.0366 | 63.3636 | 115.4663 | 123.7885 | 1.9272 | 123.7976 | 76.6479 | -0.27924 | 123.7885 | 1.9272 | 76.6479 | 115.4663 | 123.7976 | -124.0219 | -124.0677
1628.7188 | 123.9899 | -61.3129 | 62.4573 | -0.10048 | 0.016451 | 0.018113 | 0.011892 | 0.067725 | 0.0035121 | 0.082253 | -59.3765 | 62.4664 | -61.5738 | -61.4914 | 54.3274 | 15.2756 | 2.5909 | 1.9409 | 62.4481 | -61.5829 | -0.26093 | 0.009156 | 1.9363 | -0.17853 | -8.1299 | -0.27008 | -0.009155 | 2.1973 | 63.9038 | 63.2538 | 115.6403 | 123.7793 | 1.9363 | 123.761 | 76.5884 | -0.27008 | 123.7793 | 1.9363 | 76.5884 | 115.6403 | 123.761 | -124.0311 | -124.0402
1629.7188 | 123.9807 | -61.3403 | 62.4756 | -0.21492 | 0.014956 | 0.017472 | 0.0099698 | 0.067298 | 0.0028711 | 0.080544 | -59.2987 | 62.4435 | -61.5738 | -61.5143 | 54.1489 | 15.1794 | 2.7328 | 2.005 | 62.4619 | -61.6058 | -0.23346 | -0.032044 | 2.0416 | -0.17395 | -8.3267 | -0.2655 | -0.013733 | 2.2751 | 64.0732 | 63.3453 | 115.4892 | 123.7839 | 2.0416 | 123.8022 | 76.5198 | -0.2655 | 123.7839 | 2.0416 | 76.5198 | 115.4892 | 123.8022 | -124.0494 | -124.0814
1630.7188 | 123.9807 | -61.3174 | 62.4756 | -0.19203 | 0.014101 | 0.017472 | 0.0097562 | 0.064734 | 0.0026575 | 0.081613 | -59.3536 | 62.471 | -61.5463 | -61.5005 | 54.1489 | 15.2435 | 2.5818 | 2.0462 | 62.4664 | -61.5829 | -0.22888 | -0.004578 | 1.9638 | -0.1831 | -8.3267 | -0.2655 | -0.009155 | 2.1927 | 63.8992 | 63.3636 | 115.4663 | 123.7885 | 1.9638 | 123.7839 | 76.561 | -0.2655 | 123.7885 | 1.9638 | 76.561 | 115.4663 | 123.7839 | -124.0219 | -124.0585
1631.7188 | 123.9761 | -61.3266 | 62.4664 | -0.15388 | 0.012392 | 0.017472 | 0.011679 | 0.066016 | 0.0013757 | 0.081399 | -59.3308 | 62.4573 | -61.5417 | -61.4914 | 54.1306 | 15.1382 | 2.2842 | 1.8814 | 62.4207 | -61.615 | -0.21515 | -0.009156 | 1.9958 | -0.16479 | -8.3359 | -0.28839 | -0.045777 | 2.211 | 63.6108 | 63.208 | 115.4572 | 123.7839 | 1.9958 | 123.7473 | 76.4648 | -0.28839 | 123.7839 | 1.9958 | 76.4648 | 115.4572 | 123.7473 | -124.0082 | -124.0814
1632.7188 | 123.9624 | -61.3678 | 62.4756 | 0.067368 | 0.01581 | 0.016191 | 0.012747 | 0.065589 | 0.0020167 | 0.081399 | -59.3719 | 62.471 | -61.5738 | -61.5555 | 53.952 | 14.9139 | 2.6321 | 1.8402 | 62.4298 | -61.6013 | -0.20599 | -0.004578 | 1.9958 | -0.18768 | -8.5236 | -0.23346 | -0.045776 | 2.2018 | 63.9999 | 63.208 | 115.3198 | 123.8388 | 1.9958 | 123.7976 | 76.2817 | -0.23346 | 123.8388 | 1.9958 | 76.2817 | 115.3198 | 123.7976 | -124.0494 | -124.0768
1633.7188 | 123.9899 | -61.3174 | 62.4619 | -0.062332 | 0.013033 | 0.015763 | 0.0095424 | 0.068579 | 0.0030847 | 0.081399 | -59.3765 | 62.4664 | -61.5509 | -61.496 | 53.9337 | 15.1611 | 2.536 | 1.799 | 62.4664 | -61.5738 | -0.23346 | 0.004578 | 1.9409 | -0.17853 | -8.5281 | -0.25635 | 0.004578 | 2.1744 | 63.8535 | 63.1165 | 115.2512 | 123.7839 | 1.9409 | 123.7839 | 76.4786 | -0.25635 | 123.7839 | 1.9409 | 76.4786 | 115.2512 | 123.7839 | -124.0128 | -124.0356
1634.7188 | 124.0128 | -61.3037 | 62.4847 | -0.23018 | 0.01581 | 0.017259 | 0.010397 | 0.068579 | 0.0018031 | 0.082253 | -59.3536 | 62.4847 | -61.5509 | -61.4731 | 53.9658 | 15.2527 | 2.5772 | 1.8539 | 62.4527 | -61.5875 | -0.24719 | 0 | 1.9501 | -0.16937 | -8.519 | -0.28381 | -0.032043 | 2.1973 | 63.8809 | 63.1577 | 115.2695 | 123.7885 | 1.9501 | 123.7564 | 76.5564 | -0.28381 | 123.7885 | 1.9501 | 76.5564 | 115.2695 | 123.7564 | -124.0356 | -124.0723
1635.7188 | 123.9944 | -61.322 | 62.4619 | -0.19966 | 0.015383 | 0.018113 | 0.011251 | 0.067939 | 0.00052127 | 0.081613 | -59.2987 | 62.4435 | -61.5601 | -61.4731 | 53.952 | 15.2344 | 2.536 | 1.8311 | 62.4527 | -61.5829 | -0.23804 | -0.018311 | 2.0233 | -0.15106 | -8.5098 | -0.26093 | -0.009155 | 2.2614 | 63.858 | 63.1531 | 115.274 | 123.7656 | 2.0233 | 123.7747 | 76.5564 | -0.26093 | 123.7656 | 2.0233 | 76.5564 | 115.274 | 123.7747 | -124.0219 | -124.0448
1636.7188 | 123.9716 | -61.3449 | 62.4802 | -0.16151 | 0.013674 | 0.014054 | 0.0099698 | 0.06623 | 0.0018031 | 0.080972 | -59.3674 | 62.4756 | -61.5555 | -61.5326 | 53.8605 | 15.2023 | 2.623 | 1.7624 | 62.4664 | -61.6104 | -0.21057 | -0.004578 | 1.9775 | -0.18768 | -8.6197 | -0.2655 | -0.013733 | 2.1881 | 63.9679 | 63.1073 | 115.2054 | 123.8205 | 1.9775 | 123.8113 | 76.5472 | -0.2655 | 123.8205 | 1.9775 | 76.5472 | 115.2054 | 123.8113 | -124.0356 | -124.0906
1637.7344 | 124.0402 | -61.2946 | 62.4023 | 0.19707 | 0.015383 | 0.018968 | 0.0076198 | 0.067298 | 0.0018031 | 0.082681 | -59.285 | 62.3611 | -61.5738 | -61.4777 | 54.0298 | 15.3305 | 2.3438 | 1.7303 | 62.4023 | -61.5784 | -0.27924 | -0.041199 | 2.0096 | -0.1831 | -8.3725 | -0.28381 | 0 | 2.2888 | 63.6383 | 63.0249 | 115.3244 | 123.6557 | 2.0096 | 123.6969 | 76.6251 | -0.28381 | 123.6557 | 2.0096 | 76.6251 | 115.3244 | 123.6969 | -123.9761 | -123.9807
1638.7188 | 123.999 | -61.322 | 62.471 | -0.14626 | 0.013888 | 0.019395 | 0.011679 | 0.064307 | 0.0028711 | 0.08204 | -59.2667 | 62.4573 | -61.5509 | -61.4914 | 53.9429 | 15.1291 | 2.6138 | 1.8036 | 62.439 | -61.6104 | -0.22888 | -0.013733 | 2.0554 | -0.16937 | -8.5281 | -0.28839 | -0.032043 | 2.2842 | 63.9359 | 63.1256 | 115.2649 | 123.7793 | 2.0554 | 123.761 | 76.4511 | -0.28839 | 123.7793 | 2.0554 | 76.4511 | 115.2649 | 123.761 | -124.0219 | -124.0814
1639.7188 | 123.9761 | -61.3312 | 62.4664 | -0.1844 | 0.013674 | 0.018327 | 0.011465 | 0.066443 | -0.00033333 | 0.082894 | -59.2575 | 62.4756 | -61.5509 | -61.4777 | 53.7918 | 15.2206 | 2.5177 | 1.7441 | 62.4619 | -61.5829 | -0.21973 | 0.009155 | 2.0737 | -0.14648 | -8.6746 | -0.25177 | -0.004578 | 2.2934 | 63.8489 | 63.0753 | 115.123 | 123.8068 | 2.0737 | 123.793 | 76.5518 | -0.25177 | 123.8068 | 2.0737 | 76.5518 | 115.123 | 123.793 | -124.0173 | -124.0494
1640.7188 | 124.0219 | -61.2946 | 62.4664 | -0.23781 | 0.014101 | 0.014695 | 0.0095424 | 0.067511 | 0.0015893 | 0.08204 | -59.285 | 62.4664 | -61.5646 | -61.4868 | 53.8513 | 15.1199 | 2.5772 | 1.7487 | 62.4527 | -61.5829 | -0.27008 | 0 | 2.0096 | -0.19226 | -8.6151 | -0.28839 | -0.013733 | 2.2797 | 63.8718 | 63.0432 | 115.1459 | 123.761 | 2.0096 | 123.7473 | 76.4145 | -0.28839 | 123.761 | 2.0096 | 76.4145 | 115.1459 | 123.7473 | -124.0311 | -124.0494
1641.7188 | 123.9807 | -61.3174 | 62.4756 | -0.23018 | 0.016665 | 0.018113 | 0.0091152 | 0.068152 | -0.00011953 | 0.079263 | -59.2529 | 62.4435 | -61.5555 | -61.4685 | 53.9841 | 15.3397 | 2.7924 | 1.8997 | 62.4985 | -61.5829 | -0.23804 | -0.032044 | 2.0645 | -0.15106 | -8.4915 | -0.2655 | 0.022888 | 2.3026 | 64.1098 | 63.2172 | 115.3015 | 123.761 | 2.0645 | 123.8159 | 76.6571 | -0.2655 | 123.761 | 2.0645 | 76.6571 | 115.3015 | 123.8159 | -124.0311 | -124.0585
1642.7188 | 124.0082 | -61.3403 | 62.4893 | -0.24544 | 0.013888 | 0.014482 | 0.011038 | 0.066016 | -0.0020421 | 0.081826 | -59.23 | 62.4573 | -61.5463 | -61.4914 | 53.7918 | 15.1703 | 2.6184 | 1.8356 | 62.4664 | -61.5646 | -0.20599 | -0.032044 | 2.1103 | -0.15106 | -8.6975 | -0.2243 | -0.022888 | 2.3163 | 63.9587 | 63.176 | 115.1321 | 123.7976 | 2.1103 | 123.8068 | 76.5106 | -0.2243 | 123.7976 | 2.1103 | 76.5106 | 115.1321 | 123.8068 | -124.0356 | -124.054
1643.7188 | 123.9395 | -61.3083 | 62.4756 | -0.45906 | 0.013033 | 0.015763 | 0.006979 | 0.064307 | 0.0018031 | 0.082467 | -59.3674 | 62.4619 | -61.5738 | -61.5326 | 53.8467 | 15.1749 | 2.6825 | 1.7395 | 62.4619 | -61.5875 | -0.2655 | -0.013733 | 1.9409 | -0.2243 | -8.6288 | -0.27923 | -0.013733 | 2.2064 | 63.9908 | 63.0478 | 115.155 | 123.7701 | 1.9409 | 123.7701 | 76.4832 | -0.27923 | 123.7701 | 1.9409 | 76.4832 | 115.155 | 123.7701 | -124.0494 | -124.0631
1644.7188 | 123.967 | -61.3037 | 62.4756 | -0.19203 | 0.014956 | 0.013627 | 0.0091152 | 0.06623 | 0.00073487 | 0.082253 | -59.3353 | 62.4802 | -61.5372 | -61.496 | 53.8788 | 15.1245 | 2.6733 | 1.8448 | 62.4802 | -61.5875 | -0.23346 | 0.004578 | 1.9684 | -0.19226 | -8.5968 | -0.28381 | 0.004578 | 2.2018 | 63.9771 | 63.1485 | 115.1825 | 123.7839 | 1.9684 | 123.7839 | 76.4282 | -0.28381 | 123.7839 | 1.9684 | 76.4282 | 115.1825 | 123.7839 | -124.0128 | -124.0631
1645.7188 | 124.0082 | -61.3174 | 62.4481 | -0.19203 | 0.016024 | 0.016618 | 0.0091152 | 0.068152 | 0.0032983 | 0.08204 | -59.317 | 62.4573 | -61.5372 | -61.4777 | 53.9612 | 14.9963 | 2.4948 | 1.7441 | 62.4619 | -61.5921 | -0.21973 | 0.009155 | 2.0004 | -0.16022 | -8.4869 | -0.27466 | 0.013733 | 2.2202 | 63.8123 | 63.0615 | 115.2786 | 123.7747 | 2.0004 | 123.7793 | 76.3138 | -0.27466 | 123.7747 | 2.0004 | 76.3138 | 115.2786 | 123.7793 | -123.9853 | -124.0402
1646.7188 | 123.9578 | -61.322 | 62.4664 | -0.14626 | 0.016238 | 0.016404 | 0.010183 | 0.06623 | 0.0035121 | 0.079904 | -59.3308 | 62.4527 | -61.5509 | -61.4777 | 53.9474 | 14.9597 | 2.5589 | 1.8127 | 62.4573 | -61.5829 | -0.22888 | -0.013733 | 1.9913 | -0.15564 | -8.519 | -0.26093 | -0.009156 | 2.2202 | 63.8809 | 63.1348 | 115.2695 | 123.7747 | 1.9913 | 123.7793 | 76.2817 | -0.26093 | 123.7747 | 1.9913 | 76.2817 | 115.2695 | 123.7793 | -124.0173 | -124.0494
1647.7188 | 123.9807 | -61.3266 | 62.4115 | 0.16655 | 0.017092 | 0.012345 | 0.0097562 | 0.067939 | 0.0032983 | 0.08204 | -59.2667 | 62.4298 | -61.5875 | -61.5463 | 53.8834 | 14.946 | 2.3941 | 1.8219 | 62.4252 | -61.5738 | -0.26093 | 0.018311 | 2.0599 | -0.21973 | -8.5281 | -0.24719 | 0.013733 | 2.3209 | 63.7207 | 63.1485 | 115.21 | 123.7564 | 2.0599 | 123.7518 | 76.2726 | -0.24719 | 123.7564 | 2.0599 | 76.2726 | 115.21 | 123.7518 | -123.999 | -123.9853
1648.7188 | 124.0082 | -61.3037 | 62.4893 | -0.29884 | 0.01581 | 0.013413 | 0.011251 | 0.064307 | 0.0018031 | 0.081613 | -59.2667 | 62.4664 | -61.5601 | -61.4868 | 53.6636 | 14.9597 | 2.4445 | 1.8219 | 62.4619 | -61.5738 | -0.25635 | -0.022888 | 2.037 | -0.1831 | -8.8257 | -0.27008 | -0.027466 | 2.2934 | 63.7482 | 63.1256 | 114.9673 | 123.7701 | 2.037 | 123.7656 | 76.2634 | -0.27008 | 123.7701 | 2.037 | 76.2634 | 114.9673 | 123.7656 | -124.0494 | -124.0631
1649.7188 | 123.9761 | -61.29 | 62.4802 | -0.15388 | 0.014956 | 0.01555 | 0.010611 | 0.06687 | 0.0015893 | 0.079904 | -59.2804 | 62.4527 | -61.5234 | -61.4914 | 53.7918 | 14.7629 | 2.4719 | 1.9821 | 62.4847 | -61.5646 | -0.23346 | -0.027466 | 2.0096 | -0.20142 | -8.6884 | -0.27466 | 0.004577 | 2.243 | 63.7619 | 63.2721 | 115.0818 | 123.7427 | 2.0096 | 123.7747 | 76.0529 | -0.27466 | 123.7427 | 2.0096 | 76.0529 | 115.0818 | 123.7747 | -124.0036 | -124.0448
1650.7188 | 123.9395 | -61.3037 | 62.4847 | 0.059738 | 0.015383 | 0.014695 | 0.0050564 | 0.06687 | -0.0016149 | 0.080972 | -59.3719 | 62.4847 | -61.5463 | -61.5326 | 53.5995 | 14.8315 | 2.3941 | 1.6159 | 62.4847 | -61.5509 | -0.24262 | 0 | 1.9318 | -0.22888 | -8.8852 | -0.24719 | 0 | 2.1744 | 63.6978 | 62.9196 | 114.9033 | 123.7885 | 1.9318 | 123.7885 | 76.1353 | -0.24719 | 123.7885 | 1.9318 | 76.1353 | 114.9033 | 123.7885 | -124.0311 | -124.0356
1651.7188 | 123.967 | -61.322 | 62.4847 | -0.19966 | 0.017092 | 0.012986 | 0.0089016 | 0.065375 | 0.0028711 | 0.08204 | -59.2438 | 62.4573 | -61.5463 | -61.5051 | 53.7186 | 14.8361 | 2.4078 | 1.8036 | 62.4847 | -61.6013 | -0.22431 | -0.027466 | 2.0782 | -0.18311 | -8.7662 | -0.27924 | 0 | 2.3026 | 63.7299 | 63.1256 | 115.0406 | 123.7793 | 2.0782 | 123.8068 | 76.1581 | -0.27924 | 123.7793 | 2.0782 | 76.1581 | 115.0406 | 123.8068 | -124.0311 | -124.086
1652.7188 | 123.9304 | -61.3403 | 62.471 | 0.55565 | 0.017306 | 0.017045 | 0.0095424 | 0.069007 | 0.0024439 | 0.083108 | -59.3079 | 62.4527 | -61.5417 | -61.5738 | 53.746 | 14.9872 | 2.2659 | 1.5839 | 62.439 | -61.6058 | -0.20142 | -0.01831 | 2.0325 | -0.23346 | -8.725 | -0.2655 | -0.032043 | 2.2339 | 63.6063 | 62.9242 | 115.0864 | 123.793 | 2.0325 | 123.7793 | 76.3275 | -0.2655 | 123.793 | 2.0325 | 76.3275 | 115.0864 | 123.7793 | -124.0128 | -124.0768
1653.7188 | 123.999 | -61.3037 | 62.471 | -0.19966 | 0.016878 | 0.015336 | 0.011465 | 0.065375 | 0.0032983 | 0.082467 | -59.2484 | 62.4893 | -61.5601 | -61.4822 | 53.9017 | 15.0375 | 2.3987 | 1.799 | 62.4756 | -61.5875 | -0.25635 | 0.018311 | 2.0554 | -0.17853 | -8.5693 | -0.28381 | 0.004578 | 2.3117 | 63.7024 | 63.1027 | 115.2054 | 123.793 | 2.0554 | 123.7793 | 76.3412 | -0.28381 | 123.793 | 2.0554 | 76.3412 | 115.2054 | 123.7793 | -124.0311 | -124.0585
1654.7188 | 123.967 | -61.3083 | 62.471 | -0.15388 | 0.013674 | 0.017899 | 0.0095424 | 0.064734 | 0.0013757 | 0.079904 | -59.2346 | 62.4802 | -61.5555 | -61.4914 | 53.8925 | 15.0558 | 2.3117 | 1.7487 | 62.4802 | -61.5829 | -0.24719 | 0.009156 | 2.0737 | -0.1831 | -8.5785 | -0.27466 | 0.009156 | 2.3209 | 63.62 | 63.0569 | 115.2008 | 123.7885 | 2.0737 | 123.7885 | 76.3641 | -0.27466 | 123.7885 | 2.0737 | 76.3641 | 115.2008 | 123.7885 | -124.0265 | -124.054
1655.7188 | 123.9807 | -61.3129 | 62.4847 | -0.16151 | 0.013033 | 0.016404 | 0.010397 | 0.06922 | 0.0020167 | 0.079263 | -59.285 | 62.4619 | -61.5555 | -61.4822 | 53.6728 | 14.9231 | 2.4216 | 1.7715 | 62.4664 | -61.5875 | -0.24262 | -0.022888 | 2.0279 | -0.16937 | -8.812 | -0.27466 | -0.01831 | 2.2705 | 63.7344 | 63.0844 | 114.9857 | 123.7747 | 2.0279 | 123.7793 | 76.236 | -0.27466 | 123.7747 | 2.0279 | 76.236 | 114.9857 | 123.7793 | -124.0402 | -124.0723
1656.7188 | 123.9578 | -61.3037 | 62.4893 | -0.15388 | 0.014101 | 0.015336 | 0.0080472 | 0.066016 | 0.0039393 | 0.083535 | -59.2529 | 62.4802 | -61.5326 | -61.496 | 53.6774 | 14.9551 | 2.3163 | 1.7395 | 62.4619 | -61.5646 | -0.22888 | -0.009155 | 2.0508 | -0.19226 | -8.812 | -0.26093 | -0.027466 | 2.2797 | 63.62 | 63.0432 | 114.9811 | 123.7839 | 2.0508 | 123.7656 | 76.2588 | -0.26093 | 123.7839 | 2.0508 | 76.2588 | 114.9811 | 123.7656 | -124.0219 | -124.054
1657.7188 | 124.0631 | -61.322 | 62.4207 | 0.23521 | 0.014742 | 0.011277 | 0.0071926 | 0.067511 | 0.0015893 | 0.082253 | -59.1751 | 62.3611 | -61.5509 | -61.3998 | 53.7598 | 15.0375 | 2.037 | 1.7532 | 62.4023 | -61.5463 | -0.22888 | -0.059509 | 2.1469 | -0.07782 | -8.6609 | -0.22431 | -0.01831 | 2.3758 | 63.3591 | 63.0753 | 115.0818 | 123.6832 | 2.1469 | 123.7244 | 76.3596 | -0.22431 | 123.6832 | 2.1469 | 76.3596 | 115.0818 | 123.7244 | -123.9716 | -123.967
1658.7188 | 123.9395 | -61.2946 | 62.4756 | 0.067368 | 0.017519 | 0.014054 | 0.0076198 | 0.064521 | 0.0013757 | 0.080972 | -59.1522 | 62.4619 | -61.5555 | -61.5234 | 53.5309 | 14.8956 | 2.3712 | 1.7944 | 62.4619 | -61.6013 | -0.26093 | -0.013733 | 2.1423 | -0.22888 | -8.9447 | -0.3067 | -0.013733 | 2.4033 | 63.6658 | 63.089 | 114.8254 | 123.7564 | 2.1423 | 123.7564 | 76.1902 | -0.3067 | 123.7564 | 2.1423 | 76.1902 | 114.8254 | 123.7564 | -124.0311 | -124.0768
1659.7188 | 123.9716 | -61.2946 | 62.4985 | -0.13863 | 0.01581 | 0.017259 | 0.01232 | 0.065802 | 0.0024439 | 0.081399 | -59.1568 | 62.4756 | -61.5509 | -61.4914 | 53.421 | 14.7171 | 2.2659 | 1.7487 | 62.4664 | -61.5601 | -0.25635 | -0.022888 | 2.1378 | -0.19684 | -9.0775 | -0.2655 | -0.032043 | 2.3941 | 63.5605 | 63.0432 | 114.7156 | 123.7701 | 2.1378 | 123.761 | 76.0117 | -0.2655 | 123.7701 | 2.1378 | 76.0117 | 114.7156 | 123.761 | -124.0494 | -124.0585
1660.7188 | 123.9716 | -61.3083 | 62.4985 | -0.19966 | 0.014529 | 0.019181 | 0.0076198 | 0.065375 | 0.0028711 | 0.08204 | -59.198 | 62.4664 | -61.5601 | -61.5005 | 53.4988 | 14.8132 | 2.2476 | 1.7395 | 62.4847 | -61.5784 | -0.25177 | -0.032043 | 2.1103 | -0.19226 | -8.9996 | -0.27008 | -0.013733 | 2.3621 | 63.5559 | 63.0478 | 114.8071 | 123.7747 | 2.1103 | 123.793 | 76.1215 | -0.27008 | 123.7747 | 2.1103 | 76.1215 | 114.8071 | 123.793 | -124.0585 | -124.0768
1661.7188 | 123.9395 | -61.3037 | 62.4893 | -0.17677 | 0.013674 | 0.015336 | 0.0093288 | 0.065161 | 0.00052127 | 0.080117 | -59.198 | 62.4481 | -61.528 | -61.5234 | 53.4805 | 14.6713 | 2.2293 | 1.6434 | 62.4802 | -61.5509 | -0.2243 | -0.041199 | 2.1057 | -0.21973 | -9.0088 | -0.24719 | -0.009155 | 2.33 | 63.533 | 62.9471 | 114.7842 | 123.7518 | 2.1057 | 123.7839 | 75.975 | -0.24719 | 123.7518 | 2.1057 | 75.975 | 114.7842 | 123.7839 | -124.0173 | -124.0402
1662.7188 | 123.9899 | -61.3129 | 62.4802 | -0.20729 | 0.014742 | 0.017259 | 0.010611 | 0.065375 | 0.0018031 | 0.082894 | -59.285 | 62.471 | -61.528 | -61.4731 | 53.5538 | 14.6576 | 2.2476 | 1.6846 | 62.4664 | -61.5463 | -0.21515 | -0.009156 | 2.0279 | -0.16022 | -8.9264 | -0.23346 | -0.013733 | 2.243 | 63.5605 | 62.9974 | 114.8666 | 123.7839 | 2.0279 | 123.7793 | 75.9705 | -0.23346 | 123.7839 | 2.0279 | 75.9705 | 114.8666 | 123.7793 | -124.0082 | -124.0265
1663.7188 | 123.9349 | -61.3083 | 62.4893 | -0.24544 | 0.014956 | 0.014268 | 0.010824 | 0.067725 | 0.0022303 | 0.082894 | -59.1797 | 62.4573 | -61.5372 | -61.4914 | 53.4805 | 14.6896 | 2.2751 | 1.5884 | 62.4893 | -61.5875 | -0.22888 | -0.032044 | 2.1286 | -0.1831 | -9.0088 | -0.27923 | 0 | 2.3575 | 63.5834 | 62.8967 | 114.7888 | 123.7656 | 2.1286 | 123.7976 | 75.9979 | -0.27923 | 123.7656 | 2.1286 | 75.9979 | 114.7888 | 123.7976 | -124.0265 | -124.0768
1664.7188 | 123.9578 | -61.2854 | 62.4893 | -0.24544 | 0.014529 | 0.013413 | 0.006979 | 0.064521 | 0.0024439 | 0.080117 | -59.1751 | 62.4435 | -61.5189 | -61.4777 | 53.5904 | 14.6805 | 2.2385 | 1.6754 | 62.4619 | -61.5463 | -0.23346 | -0.045777 | 2.1103 | -0.19226 | -8.8989 | -0.26093 | -0.027466 | 2.3438 | 63.5239 | 62.9608 | 114.8758 | 123.7289 | 2.1103 | 123.7473 | 75.9659 | -0.26093 | 123.7289 | 2.1103 | 75.9659 | 114.8758 | 123.7473 | -124.0082 | -124.0356
1665.7188 | 123.9487 | -61.3083 | 62.4985 | -0.14626 | 0.01346 | 0.015122 | 0.0095424 | 0.061743 | 0.0024439 | 0.082894 | -59.2575 | 62.4298 | -61.5326 | -61.528 | 53.6591 | 14.7125 | 2.2522 | 1.7166 | 62.4664 | -61.5784 | -0.2243 | -0.068664 | 2.0508 | -0.21973 | -8.8394 | -0.27008 | -0.032043 | 2.2751 | 63.5605 | 63.0249 | 114.9673 | 123.7381 | 2.0508 | 123.7747 | 76.0208 | -0.27008 | 123.7381 | 2.0508 | 76.0208 | 114.9673 | 123.7747 | -124.0311 | -124.0768
1666.7188 | 123.9349 | -61.3174 | 62.5076 | -0.45143 | 0.014956 | 0.011918 | 0.0099698 | 0.063025 | 0.0011621 | 0.080972 | -59.2209 | 62.4435 | -61.5509 | -61.5097 | 53.6407 | 14.7034 | 2.2888 | 1.6296 | 62.4802 | -61.5555 | -0.23346 | -0.064087 | 2.0966 | -0.19226 | -8.8669 | -0.23804 | -0.027465 | 2.33 | 63.6063 | 62.9471 | 114.9582 | 123.761 | 2.0966 | 123.7976 | 76.0208 | -0.23804 | 123.761 | 2.0966 | 76.0208 | 114.9582 | 123.7976 | -124.0585 | -124.0631
1667.7188 | 123.9853 | -61.29 | 62.5031 | -0.19966 | 0.016878 | 0.017686 | 0.01232 | 0.06388 | 0.0035121 | 0.08204 | -59.1431 | 62.4573 | -61.5509 | -61.4822 | 53.5995 | 14.6576 | 2.1103 | 1.5472 | 62.4664 | -61.5509 | -0.26093 | -0.045777 | 2.1469 | -0.19226 | -8.9035 | -0.26093 | -0.036621 | 2.4078 | 63.4003 | 62.8372 | 114.8895 | 123.7473 | 2.1469 | 123.7564 | 75.9476 | -0.26093 | 123.7473 | 2.1469 | 75.9476 | 114.8895 | 123.7564 | -124.054 | -124.054
1668.7188 | 123.9304 | -61.3083 | 62.4939 | -0.16914 | 0.01581 | 0.017259 | 0.0076198 | 0.064307 | 0.0013757 | 0.081613 | -59.1431 | 62.4481 | -61.528 | -61.2991 | 53.595 | 14.6805 | 2.124 | 1.6754 | 62.4664 | -61.5601 | -0.21973 | -0.045776 | 2.1652 | 0.009156 | -8.8989 | -0.25177 | -0.027465 | 2.3849 | 63.4323 | 62.9837 | 114.9033 | 123.7564 | 2.1652 | 123.7747 | 75.9888 | -0.25177 | 123.7564 | 2.1652 | 75.9888 | 114.9033 | 123.7747 | -124.0219 | -124.054
1669.7188 | 123.912 | -61.2762 | 62.5351 | -0.24544 | 0.014742 | 0.013413 | 0.0074062 | 0.066016 | -0.00011953 | 0.083108 | -59.4498 | 62.4435 | -61.5326 | -61.5051 | 53.4531 | 14.7675 | 2.1332 | 1.5335 | 62.4893 | -61.5509 | -0.25635 | -0.091553 | 1.8265 | -0.22888 | -9.082 | -0.27466 | -0.045776 | 2.0828 | 63.4094 | 62.8098 | 114.7293 | 123.7198 | 1.8265 | 123.7656 | 76.0437 | -0.27466 | 123.7198 | 1.8265 | 76.0437 | 114.7293 | 123.7656 | -124.0677 | -124.086
1670.7188 | 123.9258 | -61.3129 | 62.4985 | -0.19203 | 0.013674 | 0.018113 | 0.0095424 | 0.063239 | 0.00030767 | 0.083108 | -59.1568 | 62.4344 | -61.5555 | -61.5097 | 53.3752 | 14.6667 | 2.005 | 1.4145 | 62.471 | -61.5417 | -0.24262 | -0.064087 | 2.1561 | -0.19684 | -9.1232 | -0.22888 | -0.027466 | 2.3987 | 63.3179 | 62.7274 | 114.6881 | 123.7473 | 2.1561 | 123.7839 | 75.9796 | -0.22888 | 123.7473 | 2.1561 | 75.9796 | 114.6881 | 123.7839 | -124.054 | -124.0402
1671.7188 | 124.0173 | -61.2762 | 62.4893 | -0.1844 | 0.01346 | 0.014268 | 0.0061246 | 0.064521 | 0.0013757 | 0.081613 | -59.1843 | 62.3886 | -61.5143 | -61.4182 | 53.4073 | 14.9872 | 1.8951 | 1.5656 | 62.4527 | -61.5326 | -0.23804 | -0.10071 | 2.092 | -0.14191 | -9.082 | -0.25635 | -0.036621 | 2.33 | 63.1714 | 62.8418 | 114.6835 | 123.6649 | 2.092 | 123.7289 | 76.2634 | -0.25635 | 123.6649 | 2.092 | 76.2634 | 114.6835 | 123.7289 | -124.0036 | -124.0219
1672.7188 | 123.9761 | -61.3174 | 62.4664 | -0.16151 | 0.016665 | 0.012986 | 0.015524 | 0.064521 | -0.00054693 | 0.081613 | -59.0744 | 62.471 | -61.5417 | -61.4548 | 53.3249 | 14.6988 | 1.9913 | 1.6617 | 62.4664 | -61.5601 | -0.2243 | 0.004577 | 2.243 | -0.13733 | -9.1415 | -0.24262 | 0 | 2.4673 | 63.3087 | 62.9791 | 114.6423 | 123.7885 | 2.243 | 123.7839 | 76.0162 | -0.24262 | 123.7885 | 2.243 | 76.0162 | 114.6423 | 123.7839 | -124.0082 | -124.0265
1673.7188 | 123.9075 | -61.3037 | 62.4985 | -0.3141 | 0.014101 | 0.012345 | 0.010824 | 0.065802 | -0.00033333 | 0.083108 | -59.1019 | 62.4619 | -61.5692 | -61.496 | 53.2608 | 14.7766 | 2.0691 | 1.4969 | 62.4802 | -61.5463 | -0.2655 | -0.036621 | 2.2018 | -0.19226 | -9.2377 | -0.24262 | -0.01831 | 2.4673 | 63.3728 | 62.8006 | 114.5645 | 123.7656 | 2.2018 | 123.7839 | 76.0803 | -0.24262 | 123.7656 | 2.2018 | 76.0803 | 114.5645 | 123.7839 | -124.0677 | -124.0448
1674.7188 | 123.9349 | -61.2991 | 62.5259 | -0.19966 | 0.014742 | 0.016404 | 0.0084744 | 0.065802 | 0.0030847 | 0.078622 | -59.2392 | 62.4619 | -61.5417 | -61.5372 | 53.1738 | 14.566 | 2.1423 | 1.6205 | 62.4847 | -61.5555 | -0.24262 | -0.064087 | 2.0599 | -0.23804 | -9.3521 | -0.25635 | -0.041199 | 2.3026 | 63.4415 | 62.9196 | 114.473 | 123.761 | 2.0599 | 123.7839 | 75.8652 | -0.25635 | 123.761 | 2.0599 | 75.8652 | 114.473 | 123.7839 | -124.0677 | -124.0814
1675.7188 | 123.9258 | -61.3037 | 62.4985 | -0.22255 | 0.014315 | 0.015336 | 0.0089016 | 0.063452 | 0.00030767 | 0.079904 | -59.1751 | 62.4435 | -61.5372 | -61.5326 | 53.2745 | 15.0421 | 1.8082 | 1.3092 | 62.4893 | -61.5646 | -0.23346 | -0.054932 | 2.1286 | -0.22888 | -9.2239 | -0.26093 | -0.009155 | 2.3621 | 63.1119 | 62.6129 | 114.5782 | 123.7473 | 2.1286 | 123.793 | 76.3458 | -0.26093 | 123.7473 | 2.1286 | 76.3458 | 114.5782 | 123.793 | -124.0356 | -124.0631
1676.7188 | 123.9944 | -61.2579 | 62.5031 | -0.26833 | 0.014101 | 0.01854 | 0.0089016 | 0.065589 | 0.00052127 | 0.081399 | -59.2484 | 62.439 | -61.5417 | -61.5051 | 53.3798 | 14.7491 | 2.037 | 1.4465 | 62.4802 | -61.5646 | -0.28381 | -0.064087 | 2.0096 | -0.24719 | -9.1232 | -0.3067 | -0.022888 | 2.2934 | 63.295 | 62.7045 | 114.6378 | 123.6969 | 2.0096 | 123.7381 | 76.0071 | -0.3067 | 123.6969 | 2.0096 | 76.0071 | 114.6378 | 123.7381 | -124.0448 | -124.0677
1677.7188 | 123.9441 | -61.3037 | 62.5031 | -0.039444 | 0.017519 | 0.015122 | 0.01296 | 0.064948 | 0.0032983 | 0.082894 | -59.0515 | 62.4664 | -61.5417 | -61.4685 | 53.1235 | 14.566 | 1.8356 | 1.2817 | 62.4573 | -61.5692 | -0.23804 | -0.036621 | 2.2522 | -0.16479 | -9.3796 | -0.2655 | -0.045777 | 2.4902 | 63.1393 | 62.5854 | 114.4272 | 123.7701 | 2.2522 | 123.761 | 75.8698 | -0.2655 | 123.7701 | 2.2522 | 75.8698 | 114.4272 | 123.761 | -124.0448 | -124.0723
1678.7188 | 123.9853 | -61.2762 | 62.4847 | -0.23018 | 0.014101 | 0.012559 | 0.005911 | 0.06623 | 0.0030847 | 0.083322 | -59.1476 | 62.4069 | -61.5097 | -61.4319 | 53.1418 | 14.6027 | 1.8951 | 1.4603 | 62.4527 | -61.5143 | -0.23346 | -0.07782 | 2.1286 | -0.15564 | -9.343 | -0.23804 | -0.032043 | 2.3621 | 63.1714 | 62.7365 | 114.418 | 123.6832 | 2.1286 | 123.7289 | 75.8789 | -0.23804 | 123.6832 | 2.1286 | 75.8789 | 114.418 | 123.7289 | -123.9944 | -123.999
1679.7188 | 123.8846 | -61.3083 | 62.5168 | -0.23781 | 0.013888 | 0.015977 | 0.012533 | 0.064093 | 9.4068e-05 | 0.083962 | -59.2804 | 62.4527 | -61.5509 | -61.5097 | 53.1326 | 14.4699 | 1.9272 | 1.3962 | 62.4664 | -61.5372 | -0.24261 | -0.064087 | 2.0279 | -0.20142 | -9.3842 | -0.22888 | -0.050354 | 2.2705 | 63.2355 | 62.7045 | 114.4409 | 123.761 | 2.0279 | 123.7747 | 75.7782 | -0.22888 | 123.761 | 2.0279 | 75.7782 | 114.4409 | 123.7747 | -124.0677 | -124.054
1680.7188 | 123.9349 | -61.3174 | 62.4802 | -0.20729 | 0.016451 | 0.014482 | 0.0067654 | 0.06388 | 0.0028711 | 0.080972 | -59.0973 | 62.4481 | -61.5417 | -61.5463 | 53.4073 | 14.6439 | 2.0233 | 1.4923 | 62.4619 | -61.5417 | -0.2243 | -0.032044 | 2.2202 | -0.22888 | -9.0729 | -0.2243 | -0.018311 | 2.4445 | 63.3408 | 62.8098 | 114.7247 | 123.7656 | 2.2202 | 123.7793 | 75.9613 | -0.2243 | 123.7656 | 2.2202 | 75.9613 | 114.7247 | 123.7793 | -124.0219 | -124.0219
1681.7188 | 123.9441 | -61.322 | 62.4985 | -0.22255 | 0.013674 | 0.017045 | 0.0091152 | 0.063452 | 0.0028711 | 0.083322 | -59.111 | 62.4344 | -61.5234 | -61.5005 | 53.2425 | 14.6393 | 2.2156 | 1.1307 | 62.5122 | -61.5234 | -0.20142 | -0.064087 | 2.211 | -0.17853 | -9.256 | -0.20142 | 0.013733 | 2.4124 | 63.5376 | 62.4527 | 114.5645 | 123.7564 | 2.211 | 123.8342 | 75.9613 | -0.20142 | 123.7564 | 2.211 | 75.9613 | 114.5645 | 123.8342 | -124.0219 | -124.0219
1682.7188 | 123.9487 | -61.2808 | 62.558 | -0.22255 | 0.014101 | 0.015336 | 0.010611 | 0.063025 | 0.0013757 | 0.081826 | -59.0973 | 62.4481 | -61.5555 | -61.496 | 53.1921 | 14.4104 | 2.0874 | 1.4236 | 62.4664 | -61.5509 | -0.27466 | -0.10986 | 2.1835 | -0.21515 | -9.3658 | -0.27008 | -0.091552 | 2.4582 | 63.3682 | 62.7045 | 114.473 | 123.7289 | 2.1835 | 123.7473 | 75.6912 | -0.27008 | 123.7289 | 2.1835 | 75.6912 | 114.473 | 123.7473 | -124.1135 | -124.1089
1683.7188 | 123.9624 | -61.3129 | 62.5305 | -0.25307 | 0.01346 | 0.013627 | 0.008688 | 0.062598 | 0.0013757 | 0.083322 | -59.166 | 62.439 | -61.5417 | -61.5005 | 53.183 | 14.5157 | 1.9821 | 1.4465 | 62.4802 | -61.5326 | -0.22888 | -0.091553 | 2.1469 | -0.18768 | -9.3475 | -0.21973 | -0.050354 | 2.3758 | 63.295 | 62.7594 | 114.4958 | 123.7518 | 2.1469 | 123.793 | 75.8286 | -0.21973 | 123.7518 | 2.1469 | 75.8286 | 114.4958 | 123.793 | -124.0723 | -124.0631
1684.7344 | 124.0219 | -61.2762 | 62.439 | 0.21996 | 0.018587 | 0.01555 | 0.01232 | 0.065589 | 0.0028711 | 0.082681 | -59.1293 | 62.3978 | -61.5463 | -61.4548 | 53.215 | 14.5111 | 1.7487 | 1.442 | 62.4023 | -61.5417 | -0.27008 | -0.041199 | 2.1469 | -0.17853 | -9.2239 | -0.2655 | -0.036621 | 2.417 | 63.0249 | 62.7182 | 114.4913 | 123.674 | 2.1469 | 123.6786 | 75.7874 | -0.2655 | 123.674 | 2.1469 | 75.7874 | 114.4913 | 123.6786 | -123.9853 | -123.9807
1685.7188 | 123.967 | -61.3083 | 62.5076 | -2.1375 | 0.014315 | 0.015336 | 0.012533 | 0.064093 | -0.00076053 | 0.080117 | -59.2026 | 62.4527 | -61.5234 | -61.5005 | 53.0914 | 14.3784 | 1.9089 | 1.3596 | 62.4893 | -61.5509 | -0.21515 | -0.054931 | 2.1057 | -0.19226 | -9.4162 | -0.24261 | -0.01831 | 2.3209 | 63.2172 | 62.6678 | 114.3997 | 123.761 | 2.1057 | 123.7976 | 75.6866 | -0.24261 | 123.761 | 2.1057 | 75.6866 | 114.3997 | 123.7976 | -124.0311 | -124.0585
1686.7188 | 123.9212 | -61.29 | 62.5122 | -0.2607 | 0.014529 | 0.015336 | 0.0095424 | 0.064093 | 0.0018031 | 0.08204 | -59.0881 | 62.4573 | -61.5189 | -61.4822 | 53.1235 | 14.4424 | 1.973 | 1.4923 | 62.471 | -61.5509 | -0.22888 | -0.054932 | 2.2018 | -0.19226 | -9.3887 | -0.26093 | -0.041199 | 2.4307 | 63.2629 | 62.7823 | 114.4135 | 123.7473 | 2.2018 | 123.761 | 75.7324 | -0.26093 | 123.7473 | 2.2018 | 75.7324 | 114.4135 | 123.761 | -124.0311 | -124.0631
1687.7188 | 123.8937 | -61.3129 | 62.4573 | 0.03685 | 0.01816 | 0.014054 | 0.01531 | 0.065375 | 0.0030847 | 0.082467 | -59.0195 | 62.4527 | -61.5417 | -61.5417 | 53.1555 | 14.4287 | 1.8311 | 1.2589 | 62.471 | -61.5601 | -0.22888 | -0.004577 | 2.2934 | -0.22888 | -9.3018 | -0.24719 | 0.013733 | 2.5223 | 63.1439 | 62.5717 | 114.4684 | 123.7656 | 2.2934 | 123.7839 | 75.7416 | -0.24719 | 123.7656 | 2.2934 | 75.7416 | 114.4684 | 123.7839 | -123.999 | -124.0173
1688.7188 | 124.0036 | -61.2625 | 62.5076 | -0.19966 | 0.013674 | 0.017686 | 0.0097562 | 0.064093 | 0.00094847 | 0.083108 | -59.1156 | 62.4481 | -61.528 | -61.4868 | 53.3569 | 14.3509 | 1.8951 | 1.4008 | 62.4893 | -61.5417 | -0.2655 | -0.059509 | 2.1469 | -0.2243 | -9.1507 | -0.27924 | -0.01831 | 2.4124 | 63.1577 | 62.6633 | 114.6194 | 123.7106 | 2.1469 | 123.7518 | 75.6134 | -0.27924 | 123.7106 | 2.1469 | 75.6134 | 114.6194 | 123.7518 | -124.0356 | -124.0494
1689.7344 | 123.8892 | -61.322 | 62.4985 | 0.15892 | 0.01581 | 0.015977 | 0.013815 | 0.07392 | 0.0052209 | 0.078835 | -59.1064 | 62.4664 | -61.5417 | -61.4456 | 53.3936 | 14.3143 | 1.8539 | 1.387 | 62.4619 | -61.5738 | -0.21973 | -0.032043 | 2.2156 | -0.1236 | -9.1049 | -0.25177 | -0.036621 | 2.4353 | 63.176 | 62.709 | 114.7156 | 123.7885 | 2.2156 | 123.7839 | 75.6363 | -0.25177 | 123.7885 | 2.2156 | 75.6363 | 114.7156 | 123.7839 | -124.0402 | -124.0723
1690.7188 | 123.9349 | -61.2854 | 62.4847 | -0.21492 | 0.014742 | 0.017686 | 0.0089016 | 0.064948 | 0.0018031 | 0.082467 | -58.96 | 62.4298 | -61.5463 | -61.4914 | 53.334 | 14.328 | 1.9272 | 1.3229 | 62.4939 | -61.5234 | -0.26093 | -0.054931 | 2.3254 | -0.20599 | -9.1507 | -0.23804 | 0.009155 | 2.5864 | 63.2126 | 62.6083 | 114.6194 | 123.7152 | 2.3254 | 123.7793 | 75.6134 | -0.23804 | 123.7152 | 2.3254 | 75.6134 | 114.6194 | 123.7793 | -124.0311 | -124.0082
1691.7188 | 124.054 | -61.2808 | 62.4756 | -0.17677 | 0.012606 | 0.014695 | 0.0065518 | 0.063025 | 0.0030847 | 0.081613 | -58.873 | 62.3749 | -61.496 | -61.4136 | 53.3249 | 14.4424 | 1.8082 | 1.5198 | 62.4252 | -61.5189 | -0.21515 | -0.10071 | 2.4078 | -0.13275 | -9.1507 | -0.23804 | -0.050354 | 2.623 | 63.089 | 62.8006 | 114.6057 | 123.6557 | 2.4078 | 123.7061 | 75.7233 | -0.23804 | 123.6557 | 2.4078 | 75.7233 | 114.6057 | 123.7061 | -123.9716 | -123.9944
1692.7188 | 123.9899 | -61.29 | 62.4847 | -0.12337 | 0.016238 | 0.016191 | 0.014242 | 0.065802 | 0.0011621 | 0.081185 | -59.0149 | 62.4756 | -61.5143 | -61.4319 | 53.3157 | 14.4608 | 1.7807 | 1.3458 | 62.471 | -61.5692 | -0.2243 | -0.009155 | 2.2751 | -0.14191 | -9.169 | -0.27924 | -0.013733 | 2.4994 | 63.0707 | 62.6358 | 114.6057 | 123.7656 | 2.2751 | 123.761 | 75.7507 | -0.27924 | 123.7656 | 2.2751 | 75.7507 | 114.6057 | 123.761 | -123.999 | -124.054
1693.7188 | 123.9395 | -61.3037 | 62.5076 | -0.1844 | 0.014956 | 0.016404 | 0.0082608 | 0.064307 | 0.0024439 | 0.084176 | -59.0607 | 62.4344 | -61.528 | -61.4868 | 52.858 | 14.1632 | 1.7761 | 1.2589 | 62.4893 | -61.5234 | -0.2243 | -0.073242 | 2.243 | -0.1831 | -9.6497 | -0.21973 | -0.01831 | 2.4673 | 63.0798 | 62.5626 | 114.1617 | 123.7381 | 2.243 | 123.793 | 75.4669 | -0.21973 | 123.7381 | 2.243 | 75.4669 | 114.1617 | 123.793 | -124.0356 | -124.0311
1694.7344 | 123.9304 | -61.322 | 62.4481 | 0.12077 | 0.016024 | 0.014268 | 0.012533 | 0.065589 | 0.0030847 | 0.083322 | -59.0424 | 62.4435 | -61.5555 | -61.528 | 53.1876 | 14.3372 | 1.8265 | 1.3779 | 62.439 | -61.5692 | -0.23346 | -0.004578 | 2.2797 | -0.20599 | -9.2606 | -0.24719 | -0.009155 | 2.5131 | 63.1485 | 62.6999 | 114.5096 | 123.7656 | 2.2797 | 123.761 | 75.6592 | -0.24719 | 123.7656 | 2.2797 | 75.6592 | 114.5096 | 123.761 | -124.0036 | -124.0173
1695.7188 | 123.9578 | -61.2991 | 62.4847 | -0.2607 | 0.014742 | 0.016618 | 0.0080472 | 0.063025 | -0.00054693 | 0.081399 | -59.2346 | 62.4298 | -61.4914 | -61.4777 | 53.1647 | 14.2731 | 1.9913 | 1.3275 | 62.4619 | -61.528 | -0.19226 | -0.054931 | 2.0645 | -0.17853 | -9.3201 | -0.22888 | -0.022888 | 2.2568 | 63.2904 | 62.6266 | 114.4638 | 123.7289 | 2.0645 | 123.761 | 75.5722 | -0.22888 | 123.7289 | 2.0645 | 75.5722 | 114.4638 | 123.761 | -123.9761 | -124.0128
1696.7188 | 123.9578 | -61.2808 | 62.4756 | -0.26833 | 0.014315 | 0.014695 | 0.010183 | 0.06153 | 0.0020167 | 0.08204 | -59.0149 | 62.3978 | -61.5143 | -61.4594 | 53.2516 | 14.2181 | 1.9226 | 1.3321 | 62.471 | -61.5051 | -0.23346 | -0.07782 | 2.2659 | -0.17853 | -9.2239 | -0.2243 | -0.004578 | 2.4994 | 63.2034 | 62.6129 | 114.5325 | 123.6786 | 2.2659 | 123.7518 | 75.499 | -0.2243 | 123.6786 | 2.2659 | 75.499 | 114.5325 | 123.7518 | -123.9899 | -123.9807
1697.7188 | 123.9716 | -61.2671 | 62.5259 | -0.25307 | 0.013888 | 0.015336 | 0.0099698 | 0.061103 | 0.0015893 | 0.08204 | -58.9874 | 62.4023 | -61.5189 | -61.4365 | 53.2928 | 14.5752 | 1.7761 | 1.2543 | 62.4527 | -61.5189 | -0.25177 | -0.1236 | 2.2797 | -0.16937 | -9.2331 | -0.25177 | -0.073242 | 2.5314 | 63.0432 | 62.5214 | 114.5599 | 123.6694 | 2.2797 | 123.7198 | 75.8423 | -0.25177 | 123.6694 | 2.2797 | 75.8423 | 114.5599 | 123.7198 | -124.0448 | -124.0448
1698.7188 | 124.0585 | -61.2579 | 62.4847 | -0.19203 | 0.013674 | 0.016404 | 0.012533 | 0.062384 | 0.0024439 | 0.082253 | -59.1614 | 62.3749 | -61.4731 | -61.4456 | 53.1692 | 14.566 | 1.6388 | 1.1673 | 62.4161 | -61.496 | -0.21515 | -0.10986 | 2.0966 | -0.18768 | -9.3155 | -0.23804 | -0.068664 | 2.3117 | 62.8967 | 62.4252 | 114.4272 | 123.6328 | 2.0966 | 123.674 | 75.824 | -0.23804 | 123.6328 | 2.0966 | 75.824 | 114.4272 | 123.674 | -123.9578 | -123.9807
1699.7188 | 123.999 | -61.3312 | 62.4664 | 0.15892 | 0.017092 | 0.01555 | 0.017874 | 0.062171 | 0.0018031 | 0.084603 | -59.079 | 62.4207 | -61.5601 | -61.5051 | 53.0411 | 14.3738 | 1.6983 | 1.1215 | 62.4069 | -61.5921 | -0.22888 | -0.045777 | 2.2522 | -0.17395 | -9.4254 | -0.26093 | -0.05951 | 2.4811 | 63.0295 | 62.4527 | 114.3723 | 123.7518 | 2.2522 | 123.7381 | 75.705 | -0.26093 | 123.7518 | 2.2522 | 75.705 | 114.3723 | 123.7381 | -124.0265 | -124.0585
1700.7188 | 123.9624 | -61.2854 | 62.4939 | -0.24544 | 0.01346 | 0.013627 | 0.010397 | 0.063452 | 0.0022303 | 0.08439 | -58.9279 | 62.4023 | -61.4822 | -61.4502 | 53.3798 | 14.5981 | 1.7944 | 1.181 | 62.4573 | -61.5234 | -0.19684 | -0.091552 | 2.3575 | -0.16479 | -9.1141 | -0.23804 | -0.036621 | 2.5543 | 63.0798 | 62.4664 | 114.6652 | 123.6877 | 2.3575 | 123.7427 | 75.8835 | -0.23804 | 123.6877 | 2.3575 | 75.8835 | 114.6652 | 123.7427 | -123.9761 | -124.0173
1701.7188 | 124.0082 | -61.2671 | 62.4939 | -0.2607 | 0.013247 | 0.012345 | 0.011038 | 0.063025 | 0.0022303 | 0.082467 | -58.9554 | 62.3978 | -61.4731 | -61.4182 | 53.4348 | 14.4699 | 1.7075 | 1.1215 | 62.4435 | -61.496 | -0.20599 | -0.09613 | 2.3117 | -0.15106 | -9.0591 | -0.22888 | -0.050354 | 2.5177 | 62.9745 | 62.3886 | 114.7018 | 123.6649 | 2.3117 | 123.7106 | 75.737 | -0.22888 | 123.6649 | 2.3117 | 75.737 | 114.7018 | 123.7106 | -123.967 | -123.9899
1702.7188 | 123.9761 | -61.2854 | 62.4802 | -0.13863 | 0.014956 | 0.017045 | 0.015524 | 0.063239 | 0.0020167 | 0.083108 | -59.0378 | 62.4573 | -61.5189 | -61.4502 | 53.4164 | 14.4516 | 1.8997 | 1.355 | 62.4344 | -61.5555 | -0.23346 | -0.022889 | 2.2476 | -0.16479 | -9.0637 | -0.27008 | -0.045777 | 2.4811 | 63.1851 | 62.6404 | 114.7018 | 123.7427 | 2.2476 | 123.7198 | 75.737 | -0.27008 | 123.7427 | 2.2476 | 75.737 | 114.7018 | 123.7198 | -123.999 | -124.0356
1703.7188 | 124.0494 | -61.2717 | 62.4802 | -0.16914 | 0.012392 | 0.015336 | 0.006979 | 0.064734 | -0.00054693 | 0.082681 | -59.0652 | 62.4023 | -61.5326 | -61.3907 | 53.5538 | 14.6118 | 1.7441 | 1.4008 | 62.3978 | -61.5005 | -0.26093 | -0.07782 | 2.2064 | -0.11902 | -8.9264 | -0.22888 | -0.082398 | 2.4673 | 63.0157 | 62.6724 | 114.8254 | 123.674 | 2.2064 | 123.6694 | 75.8835 | -0.22888 | 123.674 | 2.2064 | 75.8835 | 114.8254 | 123.6694 | -124.0128 | -123.9807
1704.7188 | 124.0677 | -61.2488 | 62.4664 | -0.23781 | 0.015169 | 0.014909 | 0.0082608 | 0.061957 | 0.0018031 | 0.080758 | -58.9966 | 62.3657 | -61.5143 | -61.3953 | 53.5538 | 14.4699 | 1.7029 | 1.5472 | 62.4023 | -61.5189 | -0.2655 | -0.10071 | 2.2522 | -0.14648 | -8.9127 | -0.27008 | -0.064087 | 2.5177 | 62.9517 | 62.796 | 114.8026 | 123.6145 | 2.2522 | 123.6511 | 75.7187 | -0.27008 | 123.6145 | 2.2522 | 75.7187 | 114.8026 | 123.6511 | -123.9807 | -123.9853
1705.7188 | 124.0585 | -61.2488 | 62.4619 | -0.09285 | 0.014742 | 0.014482 | 0.0089016 | 0.062812 | 0.0018031 | 0.082894 | -58.9737 | 62.352 | -61.4914 | -61.3815 | 53.6179 | 14.4745 | 1.6296 | 1.442 | 62.3978 | -61.4731 | -0.24262 | -0.10986 | 2.2751 | -0.13275 | -8.844 | -0.2243 | -0.064087 | 2.5177 | 62.8784 | 62.6907 | 114.8666 | 123.6008 | 2.2751 | 123.6465 | 75.7233 | -0.2243 | 123.6008 | 2.2751 | 75.7233 | 114.8666 | 123.6465 | -123.9532 | -123.9349
1706.7188 | 124.0402 | -61.2671 | 62.4664 | -0.22255 | 0.011965 | 0.015977 | 0.0078336 | 0.059394 | -0.00011953 | 0.081826 | -58.6349 | 62.4161 | -61.4731 | -61.3907 | 53.6453 | 14.5111 | 1.6388 | 1.3229 | 62.4023 | -61.5189 | -0.20599 | -0.050354 | 2.6321 | -0.1236 | -8.8211 | -0.25177 | -0.064087 | 2.8381 | 62.9059 | 62.59 | 114.9124 | 123.6832 | 2.6321 | 123.6694 | 75.7782 | -0.25177 | 123.6832 | 2.6321 | 75.7782 | 114.9124 | 123.6694 | -123.9395 | -123.9853
1707.7188 | 124.0311 | -61.2671 | 62.4893 | -0.13863 | 0.012606 | 0.012132 | 0.010824 | 0.062171 | 0.00094847 | 0.084176 | -58.9966 | 62.3611 | -61.5189 | -61.3861 | 53.3798 | 14.5065 | 1.8585 | 1.5427 | 62.3978 | -61.5005 | -0.25177 | -0.12817 | 2.2705 | -0.11902 | -9.1095 | -0.23346 | -0.091553 | 2.5223 | 63.1256 | 62.8098 | 114.6469 | 123.6282 | 2.2705 | 123.6649 | 75.7736 | -0.23346 | 123.6282 | 2.2705 | 75.7736 | 114.6469 | 123.6649 | -124.0082 | -123.9899
1708.7188 | 124.0402 | -61.2717 | 62.471 | -0.20729 | 0.011324 | 0.012986 | 0.010183 | 0.062598 | 0.00030767 | 0.083322 | -58.9142 | 62.3566 | -61.4822 | -61.3815 | 53.4485 | 14.447 | 1.6663 | 1.4511 | 62.4069 | -61.4914 | -0.21057 | -0.11444 | 2.3575 | -0.10986 | -9.0225 | -0.21973 | -0.064087 | 2.5681 | 62.9379 | 62.7228 | 114.7202 | 123.6282 | 2.3575 | 123.6786 | 75.7187 | -0.21973 | 123.6282 | 2.3575 | 75.7187 | 114.7202 | 123.6786 | -123.9532 | -123.9624
1709.7188 | 124.0311 | -61.2488 | 62.4756 | -0.23018 | 0.014315 | 0.014054 | 0.011465 | 0.061316 | 0.0011621 | 0.08439 | -58.9417 | 62.3566 | -61.496 | -61.377 | 53.3844 | 14.1632 | 1.6388 | 1.3641 | 62.4023 | -61.4914 | -0.24719 | -0.11902 | 2.3071 | -0.12817 | -9.0912 | -0.24262 | -0.073242 | 2.5543 | 62.8876 | 62.6129 | 114.6332 | 123.6053 | 2.3071 | 123.6511 | 75.412 | -0.24262 | 123.6053 | 2.3071 | 75.412 | 114.6332 | 123.6511 | -123.9716 | -123.967
1710.7188 | 123.9899 | -61.2579 | 62.4802 | -0.24544 | 0.013888 | 0.015977 | 0.011892 | 0.060462 | 0.0018031 | 0.079476 | -58.8684 | 62.4023 | -61.5051 | -61.409 | 53.2425 | 14.2914 | 1.767 | 1.3138 | 62.4664 | -61.5005 | -0.24719 | -0.07782 | 2.3895 | -0.15106 | -9.2377 | -0.24261 | -0.013733 | 2.6367 | 63.0249 | 62.5717 | 114.5004 | 123.6603 | 2.3895 | 123.7244 | 75.5493 | -0.24261 | 123.6603 | 2.3895 | 75.5493 | 114.5004 | 123.7244 | -123.9853 | -123.9807
1711.7188 | 124.0265 | -61.2579 | 62.471 | 2.936 | 0.01581 | 0.011064 | 0.010824 | 0.062384 | 0.00094847 | 0.083535 | -58.9279 | 62.3474 | -61.5326 | -61.3724 | 53.4531 | 14.5157 | 1.8219 | 1.6296 | 62.4161 | -61.4777 | -0.27466 | -0.1236 | 2.33 | -0.11444 | -9.0179 | -0.21973 | -0.054931 | 2.6047 | 63.0798 | 62.8876 | 114.711 | 123.6053 | 2.33 | 123.674 | 75.7736 | -0.21973 | 123.6053 | 2.33 | 75.7736 | 114.711 | 123.674 | -124.0036 | -123.9487
1712.7188 | 123.9304 | -61.2991 | 62.4939 | -0.99312 | 0.013674 | 0.015122 | 0.016806 | 0.063025 | 0.0015893 | 0.082253 | -58.9828 | 62.4527 | -61.5646 | -61.4777 | 53.3936 | 14.2502 | 1.9455 | 1.5518 | 62.4573 | -61.5646 | -0.2655 | -0.041198 | 2.3163 | -0.17853 | -9.1003 | -0.2655 | -0.036621 | 2.5818 | 63.2446 | 62.851 | 114.6927 | 123.7518 | 2.3163 | 123.7564 | 75.5493 | -0.2655 | 123.7518 | 2.3163 | 75.5493 | 114.6927 | 123.7564 | -124.0585 | -124.0585
1713.7188 | 124.0448 | -61.2488 | 62.4619 | -0.20729 | 0.014742 | 0.015122 | 0.0054836 | 0.064093 | 0.0045801 | 0.082894 | -58.8684 | 62.3657 | -61.5005 | -61.5051 | 53.3524 | 14.241 | 1.593 | 1.6296 | 62.3932 | -61.5234 | -0.25177 | -0.09613 | 2.3804 | -0.25635 | -9.1095 | -0.27466 | -0.068665 | 2.6321 | 62.8418 | 62.8784 | 114.6011 | 123.6145 | 2.3804 | 123.642 | 75.4898 | -0.27466 | 123.6145 | 2.3804 | 75.4898 | 114.6011 | 123.642 | -123.9624 | -123.9853
1714.7188 | 124.0494 | -61.2488 | 62.4802 | -0.16151 | 0.015383 | 0.011491 | 0.0097562 | 0.060675 | -0.00033333 | 0.083108 | -58.8593 | 62.3703 | -61.496 | -61.3724 | 53.1784 | 14.296 | 1.7761 | 1.4877 | 62.4023 | -61.4914 | -0.24719 | -0.10986 | 2.3895 | -0.1236 | -9.3018 | -0.24262 | -0.07782 | 2.6367 | 63.0249 | 62.7365 | 114.4272 | 123.6191 | 2.3895 | 123.6511 | 75.5447 | -0.24262 | 123.6191 | 2.3895 | 75.5447 | 114.4272 | 123.6511 | -123.9761 | -123.9716
1715.7188 | 124.0402 | -61.2488 | 62.4756 | -0.15388 | 0.012179 | 0.015763 | 0.011251 | 0.062598 | 0.0024439 | 0.082681 | -58.8089 | 62.3611 | -61.5189 | -61.3907 | 53.2013 | 14.3234 | 1.7029 | 1.5793 | 62.4344 | -61.5005 | -0.27008 | -0.11444 | 2.4399 | -0.14191 | -9.2743 | -0.25177 | -0.041199 | 2.71 | 62.9517 | 62.8281 | 114.4501 | 123.6099 | 2.4399 | 123.6832 | 75.5722 | -0.25177 | 123.6099 | 2.4399 | 75.5722 | 114.4501 | 123.6832 | -123.9944 | -123.9761
1716.7188 | 124.0219 | -61.2717 | 62.4481 | -0.25307 | 0.013033 | 0.017259 | 0.0084744 | 0.06153 | 0.0020167 | 0.080117 | -58.7997 | 62.3474 | -61.5005 | -61.3861 | 53.2013 | 14.3921 | 1.6479 | 1.4465 | 62.3978 | -61.5189 | -0.22888 | -0.10071 | 2.4719 | -0.11444 | -9.2468 | -0.24719 | -0.050354 | 2.7008 | 62.9196 | 62.7182 | 114.473 | 123.6191 | 2.4719 | 123.6694 | 75.6638 | -0.24719 | 123.6191 | 2.4719 | 75.6638 | 114.473 | 123.6694 | -123.9487 | -123.967
1717.7188 | 123.9258 | -61.2946 | 62.5214 | -0.14626 | 0.014742 | 0.016404 | 0.013601 | 0.062171 | 0.00052127 | 0.08204 | -58.8455 | 62.4435 | -61.5234 | -61.4594 | 53.1555 | 13.9938 | 1.8265 | 1.5244 | 62.471 | -61.5417 | -0.22888 | -0.07782 | 2.449 | -0.16479 | -9.3658 | -0.24719 | -0.050354 | 2.6779 | 63.121 | 62.8189 | 114.4501 | 123.7381 | 2.449 | 123.7656 | 75.2884 | -0.24719 | 123.7381 | 2.449 | 75.2884 | 114.4501 | 123.7656 | -124.0448 | -124.0631
1718.7188 | 124.0356 | -61.2442 | 62.4847 | -0.15388 | 0.013888 | 0.011277 | 0.010611 | 0.062598 | 0.00030767 | 0.083749 | -58.8226 | 62.3566 | -61.5051 | -61.3861 | 53.3661 | 14.0533 | 1.6205 | 1.5289 | 62.4344 | -61.4914 | -0.26093 | -0.12817 | 2.4216 | -0.14191 | -9.1187 | -0.24719 | -0.050354 | 2.6825 | 62.8647 | 62.7731 | 114.6103 | 123.6008 | 2.4216 | 123.6786 | 75.2975 | -0.24719 | 123.6008 | 2.4216 | 75.2975 | 114.6103 | 123.6786 | -123.9899 | -123.9761
1719.7188 | 124.0723 | -61.2488 | 62.4573 | -0.13863 | 0.012392 | 0.013627 | 0.0082608 | 0.062812 | 0.0013757 | 0.079263 | -58.8638 | 62.3795 | -61.4914 | -61.3678 | 53.2059 | 14.2639 | 1.5884 | 1.5244 | 62.4161 | -61.4822 | -0.24262 | -0.077819 | 2.3849 | -0.11902 | -9.2514 | -0.23346 | -0.041198 | 2.6276 | 62.8372 | 62.7731 | 114.4547 | 123.6282 | 2.3849 | 123.6649 | 75.5127 | -0.23346 | 123.6282 | 2.3849 | 75.5127 | 114.4547 | 123.6649 | -123.9487 | -123.9395
1720.7188 | 124.054 | -61.2488 | 62.4802 | -0.20729 | 0.014101 | 0.013413 | 0.010183 | 0.062598 | 0.0032983 | 0.082467 | -58.7952 | 62.3795 | -61.5005 | -61.3678 | 53.4164 | 14.2548 | 1.5518 | 1.4694 | 62.3978 | -61.4914 | -0.25177 | -0.10071 | 2.4536 | -0.11902 | -9.0637 | -0.24262 | -0.082398 | 2.7054 | 62.8006 | 62.7182 | 114.6652 | 123.6282 | 2.4536 | 123.6465 | 75.5035 | -0.24262 | 123.6282 | 2.4536 | 75.5035 | 114.6652 | 123.6465 | -123.9807 | -123.9716
1721.7188 | 123.967 | -61.2717 | 62.471 | -0.23781 | 0.013247 | 0.014054 | 0.011251 | 0.062171 | -0.00097413 | 0.08204 | -58.9279 | 62.3703 | -61.5005 | -61.4273 | 53.421 | 14.241 | 1.6891 | 1.4694 | 62.4252 | -61.496 | -0.22888 | -0.10071 | 2.3438 | -0.15564 | -9.05 | -0.22431 | -0.045776 | 2.5726 | 62.9608 | 62.7411 | 114.6927 | 123.642 | 2.3438 | 123.6969 | 75.5127 | -0.22431 | 123.642 | 2.3438 | 75.5127 | 114.6927 | 123.6969 | -123.9716 | -123.967
1722.7188 | 123.9578 | -61.2579 | 62.4939 | -0.24544 | 0.015169 | 0.013841 | 0.0084744 | 0.059607 | 0.0013757 | 0.082894 | -58.9371 | 62.3703 | -61.528 | -61.4136 | 53.4302 | 14.1815 | 1.7899 | 1.5564 | 62.439 | -61.5189 | -0.27008 | -0.1236 | 2.3209 | -0.15564 | -9.0637 | -0.26092 | -0.054931 | 2.5909 | 63.0478 | 62.8143 | 114.6881 | 123.6282 | 2.3209 | 123.6969 | 75.4395 | -0.26092 | 123.6282 | 2.3209 | 75.4395 | 114.6881 | 123.6969 | -124.0219 | -124.0128
1723.7188 | 123.9807 | -61.2579 | 62.4893 | -0.2607 | 0.014742 | 0.014268 | 0.010611 | 0.062384 | 0.0013757 | 0.082467 | -58.8684 | 62.3795 | -61.5143 | -61.4136 | 53.2104 | 14.1907 | 1.6617 | 1.5152 | 62.4161 | -61.5143 | -0.25635 | -0.10986 | 2.3895 | -0.15564 | -9.2789 | -0.25635 | -0.073242 | 2.6459 | 62.9196 | 62.7731 | 114.4684 | 123.6374 | 2.3895 | 123.674 | 75.4486 | -0.25635 | 123.6374 | 2.3895 | 75.4486 | 114.4684 | 123.674 | -124.0036 | -124.0036
1724.7188 | 124.0082 | -61.2488 | 62.5031 | -0.24544 | 0.014529 | 0.017472 | 0.011465 | 0.06388 | 0.0020167 | 0.082253 | -58.7997 | 62.3703 | -61.496 | -61.3861 | 52.9678 | 13.8702 | 1.7075 | 1.5793 | 62.4298 | -61.5051 | -0.24719 | -0.13275 | 2.449 | -0.13733 | -9.5352 | -0.25635 | -0.073242 | 2.6962 | 62.9562 | 62.8281 | 114.2166 | 123.6191 | 2.449 | 123.6786 | 75.119 | -0.25635 | 123.6191 | 2.449 | 75.119 | 114.2166 | 123.6786 | -123.999 | -124.0082
1725.7188 | 124.0173 | -61.2671 | 62.5076 | -0.19203 | 0.013033 | 0.014268 | 0.01296 | 0.062384 | 0.0020167 | 0.081613 | -58.9142 | 62.3932 | -61.5234 | -61.4044 | 53.1555 | 14.0579 | 1.7624 | 1.6617 | 62.4207 | -61.5189 | -0.25635 | -0.11444 | 2.3529 | -0.13733 | -9.3521 | -0.25177 | -0.086975 | 2.6093 | 63.0295 | 62.9288 | 114.4226 | 123.6603 | 2.3529 | 123.6877 | 75.325 | -0.25177 | 123.6603 | 2.3529 | 75.325 | 114.4226 | 123.6877 | -124.0311 | -124.0265
1726.7188 | 124.0402 | -61.2625 | 62.4802 | -0.22255 | 0.013674 | 0.0078592 | 0.010397 | 0.062384 | -0.00011953 | 0.084176 | -58.5571 | 62.4161 | -61.4502 | -61.3953 | 53.1509 | 13.9206 | 1.5381 | 1.6022 | 62.3978 | -61.4731 | -0.18768 | -0.064087 | 2.7054 | -0.13275 | -9.3292 | -0.21057 | -0.082398 | 2.8931 | 62.8006 | 62.8647 | 114.4135 | 123.6786 | 2.7054 | 123.6603 | 75.1831 | -0.21057 | 123.6786 | 2.7054 | 75.1831 | 114.4135 | 123.6603 | -123.9304 | -123.9532
1727.7188 | 123.9441 | -61.2808 | 62.4939 | -0.15388 | 0.018587 | 0.01555 | 0.01766 | 0.063452 | 0.0041529 | 0.083749 | -58.7952 | 62.4802 | -61.5189 | -61.4182 | 53.0914 | 13.9526 | 1.7212 | 1.3962 | 62.4207 | -61.5372 | -0.23804 | -0.013732 | 2.4857 | -0.13733 | -9.4025 | -0.25635 | -0.073242 | 2.7237 | 63.002 | 62.677 | 114.3723 | 123.761 | 2.4857 | 123.7015 | 75.2335 | -0.25635 | 123.761 | 2.4857 | 75.2335 | 114.3723 | 123.7015 | -124.0128 | -124.0311
1728.7188 | 123.9212 | -61.2854 | 62.5031 | -0.2607 | 0.013247 | 0.015763 | 0.013388 | 0.065589 | 0.0011621 | 0.08204 | -58.8821 | 62.4252 | -61.5143 | -61.441 | 53.0045 | 13.9114 | 1.8906 | 1.387 | 62.4802 | -61.5189 | -0.22888 | -0.07782 | 2.4033 | -0.15564 | -9.4986 | -0.23346 | -0.022888 | 2.6321 | 63.176 | 62.6724 | 114.2899 | 123.7106 | 2.4033 | 123.7656 | 75.1968 | -0.23346 | 123.7106 | 2.4033 | 75.1968 | 114.2899 | 123.7656 | -124.0173 | -124.0219
1729.7188 | 123.9304 | -61.2717 | 62.5214 | -0.29884 | 0.016024 | 0.014695 | 0.011038 | 0.064307 | 0.0015893 | 0.081399 | -58.6624 | 62.3978 | -61.5051 | -61.441 | 53.0685 | 13.9938 | 1.7899 | 1.5381 | 62.4435 | -61.5143 | -0.23346 | -0.1236 | 2.6093 | -0.16937 | -9.4528 | -0.24262 | -0.07782 | 2.8427 | 63.0615 | 62.8098 | 114.3402 | 123.6694 | 2.6093 | 123.7152 | 75.2655 | -0.24262 | 123.6694 | 2.6093 | 75.2655 | 114.3402 | 123.7152 | -124.0265 | -124.0356
1730.7188 | 123.9441 | -61.2991 | 62.4985 | -0.28358 | 0.016024 | 0.01854 | 0.010611 | 0.063452 | 0.00094847 | 0.081185 | -58.6853 | 62.4069 | -61.5097 | -61.4365 | 53.1189 | 13.9847 | 1.799 | 1.3779 | 62.4069 | -61.5097 | -0.21057 | -0.091553 | 2.6138 | -0.13733 | -9.3796 | -0.21057 | -0.091553 | 2.8244 | 63.0981 | 62.677 | 114.418 | 123.7061 | 2.6138 | 123.7061 | 75.2838 | -0.21057 | 123.7061 | 2.6138 | 75.2838 | 114.418 | 123.7061 | -124.0082 | -124.0082
1731.7188 | 123.9395 | -61.2808 | 62.5076 | -0.22255 | 0.016024 | 0.015977 | 0.010183 | 0.062171 | 0.0015893 | 0.083749 | -58.6395 | 62.4069 | -61.5005 | -61.4227 | 53.0823 | 14.0488 | 1.712 | 1.4053 | 62.4344 | -61.5143 | -0.21973 | -0.10071 | 2.6413 | -0.14191 | -9.4254 | -0.23346 | -0.073242 | 2.861 | 62.9929 | 62.6862 | 114.3631 | 123.6877 | 2.6413 | 123.7152 | 75.3296 | -0.23346 | 123.6877 | 2.6413 | 75.3296 | 114.3631 | 123.7152 | -124.0082 | -124.0219
1732.7188 | 123.9807 | -61.2854 | 62.5488 | -0.25307 | 0.014529 | 0.019822 | 0.013601 | 0.060675 | 0.0015893 | 0.080972 | -58.9371 | 62.4344 | -61.5143 | -61.4685 | 52.7756 | 13.6276 | 1.6571 | 1.3458 | 62.4481 | -61.5234 | -0.22888 | -0.11444 | 2.3483 | -0.18311 | -9.7733 | -0.23804 | -0.10071 | 2.5772 | 62.9425 | 62.6312 | 114.061 | 123.7198 | 2.3483 | 123.7335 | 74.913 | -0.23804 | 123.7198 | 2.3483 | 74.913 | 114.061 | 123.7335 | -124.0631 | -124.0723
1733.7188 | 124.0631 | -61.2671 | 62.4619 | 0.62431 | 0.015169 | 0.014482 | 0.0089016 | 0.063025 | 0.0013757 | 0.081826 | -58.6624 | 62.3703 | -61.4777 | -61.377 | 52.8351 | 13.591 | 1.3321 | 1.3 | 62.4207 | -61.4777 | -0.21057 | -0.091553 | 2.6047 | -0.10986 | -9.6268 | -0.21057 | -0.041199 | 2.8152 | 62.5992 | 62.5671 | 114.1022 | 123.6374 | 2.6047 | 123.6877 | 74.8581 | -0.21057 | 123.6374 | 2.6047 | 74.8581 | 114.1022 | 123.6877 | -123.9395 | -123.9395
1734.7188 | 124.0036 | -61.2534 | 62.4939 | -0.25307 | 0.014315 | 0.013841 | 0.011892 | 0.06153 | 0.0030847 | 0.082894 | -58.6578 | 62.3886 | -61.4685 | -61.4044 | 52.9724 | 13.7924 | 1.6113 | 1.3138 | 62.439 | -61.5097 | -0.21515 | -0.10529 | 2.5955 | -0.15106 | -9.5215 | -0.25635 | -0.054931 | 2.8107 | 62.8647 | 62.5671 | 114.2258 | 123.642 | 2.5955 | 123.6923 | 75.0458 | -0.25635 | 123.642 | 2.5955 | 75.0458 | 114.2258 | 123.6923 | -123.9624 | -124.0036
1735.7188 | 123.9441 | -61.2671 | 62.5351 | -0.11574 | 0.016238 | 0.018113 | 0.01232 | 0.062384 | 0.00073487 | 0.080972 | -58.7311 | 62.4619 | -61.4868 | -61.4685 | 52.7847 | 13.2431 | 1.5152 | 0.95673 | 62.4664 | -61.5097 | -0.21973 | -0.073242 | 2.536 | -0.20142 | -9.7504 | -0.24261 | -0.068664 | 2.7557 | 62.7823 | 62.2238 | 114.0518 | 123.7289 | 2.536 | 123.7335 | 74.5102 | -0.24261 | 123.7289 | 2.536 | 74.5102 | 114.0518 | 123.7335 | -124.0219 | -124.0448
1736.7188 | 123.9029 | -61.2808 | 62.5122 | -0.29884 | 0.016878 | 0.01555 | 0.01232 | 0.061957 | 0.0022303 | 0.084603 | -58.7402 | 62.4481 | -61.5234 | -61.4639 | 52.6794 | 13.3209 | 1.5015 | 1.0162 | 62.4664 | -61.5372 | -0.24261 | -0.064087 | 2.5406 | -0.18311 | -9.8328 | -0.25635 | -0.045776 | 2.7832 | 62.7823 | 62.2971 | 113.9603 | 123.7289 | 2.5406 | 123.7473 | 74.6017 | -0.25635 | 123.7289 | 2.5406 | 74.6017 | 113.9603 | 123.7473 | -124.0356 | -124.0494
1737.7188 | 123.9395 | -61.2946 | 62.4893 | -0.024185 | 0.016451 | 0.024308 | 0.017447 | 0.065375 | 0.0026575 | 0.08204 | -58.5709 | 62.4756 | -61.4868 | -61.4227 | 52.5101 | 13.2019 | 1.4832 | 1.0666 | 62.4527 | -61.528 | -0.19226 | -0.013733 | 2.7237 | -0.12817 | -9.9792 | -0.23346 | -0.036621 | 2.916 | 62.7777 | 62.3611 | 113.8046 | 123.7701 | 2.7237 | 123.7473 | 74.4965 | -0.23346 | 123.7701 | 2.7237 | 74.4965 | 113.8046 | 123.7473 | -123.9761 | -124.0173
1738.7188 | 123.9258 | -61.2854 | 62.5122 | -0.24544 | 0.013888 | 0.014695 | 0.008688 | 0.063452 | 0.0028711 | 0.084176 | -58.6624 | 62.4435 | -61.5326 | -61.4456 | 52.739 | 13.4811 | 1.4877 | 0.93842 | 62.4756 | -61.5143 | -0.24719 | -0.068665 | 2.623 | -0.16022 | -9.7733 | -0.22888 | -0.036621 | 2.8702 | 62.7731 | 62.2238 | 114.0244 | 123.7289 | 2.623 | 123.761 | 74.7665 | -0.22888 | 123.7289 | 2.623 | 74.7665 | 114.0244 | 123.761 | -124.0448 | -124.0265
1739.7188 | 123.9166 | -61.2579 | 62.5214 | -0.22255 | 0.015169 | 0.015122 | 0.011465 | 0.062812 | 0.0026575 | 0.083962 | -58.7906 | 62.4252 | -61.5097 | -61.4594 | 52.6382 | 13.3942 | 1.506 | 1.2131 | 62.4664 | -61.5143 | -0.25177 | -0.09613 | 2.4673 | -0.20142 | -9.8831 | -0.25635 | -0.054931 | 2.7191 | 62.764 | 62.471 | 113.8962 | 123.6832 | 2.4673 | 123.7244 | 74.6521 | -0.25635 | 123.6832 | 2.4673 | 74.6521 | 113.8962 | 123.7244 | -124.0311 | -124.0356
1740.7188 | 124.0448 | -61.2625 | 62.4985 | -0.16914 | 0.014742 | 0.012559 | 0.0082608 | 0.063025 | 0.0015893 | 0.083322 | -58.4473 | 62.384 | -61.4822 | -61.3815 | 52.771 | 13.4766 | 1.4511 | 1.2222 | 62.4435 | -61.4868 | -0.21973 | -0.11444 | 2.8152 | -0.11902 | -9.7275 | -0.2243 | -0.054932 | 3.035 | 62.7136 | 62.4847 | 114.0335 | 123.6465 | 2.8152 | 123.7061 | 74.7391 | -0.2243 | 123.6465 | 2.8152 | 74.7391 | 114.0335 | 123.7061 | -123.9807 | -123.9853
1741.7188 | 123.9532 | -61.2808 | 62.5122 | -0.20729 | 0.016665 | 0.013627 | 0.0099698 | 0.063025 | 0.0030847 | 0.081613 | -58.699 | 62.4344 | -61.4868 | -61.4639 | 52.6199 | 13.2248 | 1.4374 | 1.0254 | 62.4619 | -61.528 | -0.20599 | -0.07782 | 2.5818 | -0.18311 | -9.8923 | -0.24719 | -0.050354 | 2.7878 | 62.7182 | 62.3062 | 113.9008 | 123.7152 | 2.5818 | 123.7427 | 74.5056 | -0.24719 | 123.7152 | 2.5818 | 74.5056 | 113.9008 | 123.7427 | -123.999 | -124.0402
1742.7188 | 123.9441 | -61.2762 | 62.4939 | -0.15388 | 0.016451 | 0.021104 | 0.015524 | 0.064734 | 0.0011621 | 0.083962 | -58.6578 | 62.4802 | -61.5097 | -61.441 | 52.7023 | 13.2385 | 1.5198 | 1.236 | 62.4847 | -61.5143 | -0.23346 | -0.013732 | 2.6184 | -0.16479 | -9.7916 | -0.23804 | -0.009155 | 2.8519 | 62.796 | 62.5122 | 113.9786 | 123.7564 | 2.6184 | 123.761 | 74.5148 | -0.23804 | 123.7564 | 2.6184 | 74.5148 | 113.9786 | 123.761 | -124.0036 | -124.0082
1743.7188 | 123.912 | -61.2671 | 62.5259 | -0.23018 | 0.017947 | 0.015336 | 0.0080472 | 0.064948 | 0.0011621 | 0.083322 | -58.548 | 62.4756 | -61.5463 | -61.5326 | 52.803 | 13.2294 | 1.4145 | 1.1673 | 62.5031 | -61.5463 | -0.27924 | -0.050354 | 2.7191 | -0.2655 | -9.7229 | -0.27924 | -0.022888 | 2.9984 | 62.6816 | 62.4344 | 114.0701 | 123.7427 | 2.7191 | 123.7701 | 74.4965 | -0.27924 | 123.7427 | 2.7191 | 74.4965 | 114.0701 | 123.7701 | -124.0723 | -124.0723
1744.7188 | 123.9532 | -61.2808 | 62.5168 | -0.19966 | 0.014742 | 0.01555 | 0.012106 | 0.066016 | 0.00052127 | 0.083749 | -58.8409 | 62.4481 | -61.5143 | -61.6196 | 52.5513 | 13.2431 | 1.5472 | 1.0483 | 62.4756 | -61.5417 | -0.23346 | -0.068665 | 2.4399 | -0.33875 | -9.9655 | -0.26093 | -0.041199 | 2.6733 | 62.8281 | 62.3291 | 113.8321 | 123.7289 | 2.4399 | 123.7564 | 74.5239 | -0.26093 | 123.7289 | 2.4399 | 74.5239 | 113.8321 | 123.7564 | -124.0311 | -124.0585
1745.7188 | 123.9075 | -61.2762 | 62.5259 | -0.1844 | 0.016878 | 0.014054 | 0.010397 | 0.063239 | 0.0054347 | 0.083108 | -58.4885 | 62.4481 | -61.5372 | -61.2717 | 52.8076 | 13.0875 | 1.4145 | 1.2268 | 62.4802 | -61.5555 | -0.26093 | -0.07782 | 2.7878 | 0.004578 | -9.7183 | -0.27924 | -0.045776 | 3.0487 | 62.6907 | 62.5031 | 114.0839 | 123.7244 | 2.7878 | 123.7564 | 74.3637 | -0.27924 | 123.7244 | 2.7878 | 74.3637 | 114.0839 | 123.7564 | -124.0631 | -124.0814
1746.7188 | 123.912 | -61.2762 | 62.5076 | -0.23018 | 0.016451 | 0.016618 | 0.0084744 | 0.064521 | 0.0020167 | 0.08439 | -58.6761 | 62.4527 | -61.528 | -61.5051 | 52.9083 | 13.4766 | 1.3229 | 1.3687 | 62.4847 | -61.5326 | -0.25177 | -0.054931 | 2.6001 | -0.22888 | -9.5993 | -0.25635 | -0.022888 | 2.8519 | 62.5992 | 62.645 | 114.1846 | 123.7289 | 2.6001 | 123.761 | 74.7528 | -0.25635 | 123.7289 | 2.6001 | 74.7528 | 114.1846 | 123.761 | -124.0356 | -124.0402
1747.7188 | 123.8892 | -61.3129 | 62.4847 | 0.067368 | 0.017306 | 0.01854 | 0.016806 | 0.064307 | 0.00094847 | 0.081826 | -58.548 | 62.471 | -61.5326 | -61.5234 | 52.858 | 13.2523 | 1.6159 | 1.2085 | 62.4344 | -61.5784 | -0.21973 | -0.013733 | 2.7649 | -0.21057 | -9.6268 | -0.2655 | -0.050354 | 2.9846 | 62.9288 | 62.5214 | 114.1708 | 123.7839 | 2.7649 | 123.7473 | 74.5651 | -0.2655 | 123.7839 | 2.7649 | 74.5651 | 114.1708 | 123.7473 | -124.0173 | -124.0631
1748.7188 | 123.8434 | -61.2717 | 62.5214 | -0.25307 | 0.016451 | 0.015977 | 0.010824 | 0.063666 | 0.00052127 | 0.084176 | -58.6395 | 62.4893 | -61.5372 | -61.4777 | 52.5146 | 13.1516 | 1.4236 | 1.3046 | 62.4985 | -61.496 | -0.2655 | -0.032043 | 2.6321 | -0.20599 | -10.0067 | -0.22431 | -0.022888 | 2.8976 | 62.6953 | 62.5763 | 113.7863 | 123.761 | 2.6321 | 123.7701 | 74.4232 | -0.22431 | 123.761 | 2.6321 | 74.4232 | 113.7863 | 123.7701 | -124.0585 | -124.0173
1749.7188 | 123.9349 | -61.2854 | 62.5259 | -0.23018 | 0.019228 | 0.020036 | 0.012533 | 0.064521 | 0.00073487 | 0.08204 | -58.58 | 62.4664 | -61.5143 | -61.4731 | 52.5284 | 13.298 | 1.6205 | 1.4374 | 62.4847 | -61.5372 | -0.22888 | -0.059509 | 2.7054 | -0.18768 | -9.9976 | -0.25177 | -0.041199 | 2.9343 | 62.9059 | 62.7228 | 113.8138 | 123.7518 | 2.7054 | 123.7701 | 74.5834 | -0.25177 | 123.7518 | 2.7054 | 74.5834 | 113.8138 | 123.7701 | -124.0402 | -124.0631
1750.7188 | 123.9304 | -61.2625 | 62.4985 | -0.19966 | 0.015169 | 0.015336 | 0.011038 | 0.064734 | 0.00073487 | 0.082253 | -58.6212 | 62.5076 | -61.5189 | -61.4731 | 52.5742 | 13.3804 | 1.6159 | 1.2863 | 62.4802 | -61.5463 | -0.25635 | 0.009155 | 2.6413 | -0.21057 | -9.9243 | -0.28381 | -0.01831 | 2.8976 | 62.8784 | 62.5488 | 113.8367 | 123.7701 | 2.6413 | 123.7427 | 74.6429 | -0.28381 | 123.7701 | 2.6413 | 74.6429 | 113.8367 | 123.7427 | -124.0173 | -124.0448
1751.7188 | 123.9349 | -61.2625 | 62.4802 | -0.077591 | 0.017306 | 0.016191 | 0.011465 | 0.06623 | 0.0035121 | 0.083108 | -58.6029 | 62.4802 | -61.5326 | -61.5005 | 52.5879 | 13.385 | 1.6113 | 1.4374 | 62.4664 | -61.5372 | -0.27008 | 0 | 2.6596 | -0.23804 | -9.8923 | -0.27466 | -0.013733 | 2.9297 | 62.8738 | 62.6999 | 113.8504 | 123.7427 | 2.6596 | 123.7289 | 74.6475 | -0.27466 | 123.7427 | 2.6596 | 74.6475 | 113.8504 | 123.7289 | -124.0128 | -124.0173
1752.7188 | 123.8663 | -61.3403 | 62.4619 | 0.15129 | 0.017092 | 0.020249 | 0.014669 | 0.06687 | 0.00073487 | 0.081399 | -58.7036 | 62.4756 | -61.5555 | -61.5143 | 52.5192 | 13.1332 | 1.2726 | 1.2268 | 62.4481 | -61.5738 | -0.21515 | 0.013733 | 2.6367 | -0.17395 | -9.9426 | -0.23346 | -0.013733 | 2.8519 | 62.6129 | 62.5671 | 113.8596 | 123.8159 | 2.6367 | 123.7885 | 74.4736 | -0.23346 | 123.8159 | 2.6367 | 74.4736 | 113.8596 | 123.7885 | -124.0173 | -124.0356
1753.7188 | 123.9029 | -61.2717 | 62.5076 | -0.2607 | 0.016878 | 0.011277 | 0.011251 | 0.067298 | 0.0035121 | 0.084176 | -58.5205 | 62.4985 | -61.528 | -61.4777 | 52.6428 | 13.2751 | 1.5106 | 1.4282 | 62.4985 | -61.5326 | -0.25635 | -0.009155 | 2.7512 | -0.20599 | -9.8648 | -0.26093 | -0.009155 | 3.0075 | 62.7823 | 62.6999 | 113.9145 | 123.7701 | 2.7512 | 123.7701 | 74.5468 | -0.26093 | 123.7701 | 2.7512 | 74.5468 | 113.9145 | 123.7701 | -124.0356 | -124.0402
1754.7188 | 123.9395 | -61.2991 | 62.4985 | -0.28358 | 0.01346 | 0.017045 | 0.0089016 | 0.062812 | 0.00073487 | 0.082681 | -58.5846 | 62.4435 | -61.5234 | -61.4548 | 52.7206 | 13.2751 | 1.4282 | 1.387 | 62.4756 | -61.5051 | -0.2243 | -0.054932 | 2.7145 | -0.15564 | -9.7778 | -0.20599 | -0.022888 | 2.9388 | 62.7274 | 62.6862 | 114.0198 | 123.7427 | 2.7145 | 123.7747 | 74.5743 | -0.20599 | 123.7427 | 2.7145 | 74.5743 | 114.0198 | 123.7747 | -124.0219 | -124.0036
1755.7188 | 123.9441 | -61.2534 | 62.5488 | -0.24544 | 0.017519 | 0.019608 | 0.011892 | 0.063025 | 0.0011621 | 0.08204 | -58.667 | 62.4664 | -61.5189 | -61.4731 | 52.4551 | 13.0646 | 1.3779 | 1.2314 | 62.4893 | -61.5051 | -0.2655 | -0.082397 | 2.5864 | -0.21973 | -10.0937 | -0.25177 | -0.059509 | 2.8519 | 62.6312 | 62.4847 | 113.7085 | 123.7198 | 2.5864 | 123.7427 | 74.3179 | -0.25177 | 123.7198 | 2.5864 | 74.3179 | 113.7085 | 123.7427 | -124.0677 | -124.054
1756.7188 | 123.9395 | -61.2671 | 62.5351 | -0.031814 | 0.016878 | 0.016618 | 0.013388 | 0.064948 | 0.00030767 | 0.081826 | -58.5663 | 62.4985 | -61.5189 | -61.5051 | 52.4734 | 12.9135 | 1.3779 | 1.2405 | 62.5076 | -61.5326 | -0.25177 | -0.036621 | 2.7008 | -0.23804 | -10.0616 | -0.2655 | -0.027466 | 2.9526 | 62.645 | 62.5076 | 113.7405 | 123.7656 | 2.7008 | 123.7747 | 74.1806 | -0.2655 | 123.7656 | 2.7008 | 74.1806 | 113.7405 | 123.7747 | -124.054 | -124.0677
1757.7188 | 123.9304 | -61.29 | 62.4847 | 0.029221 | 0.018374 | 0.021317 | 0.01531 | 0.066016 | 0.0037257 | 0.085031 | -58.374 | 62.4802 | -61.5143 | -61.4914 | 52.4231 | 13.0829 | 1.387 | 1.1948 | 62.4573 | -61.5143 | -0.2243 | -0.004577 | 2.916 | -0.20142 | -10.0616 | -0.2243 | -0.027466 | 3.1403 | 62.677 | 62.4847 | 113.7131 | 123.7701 | 2.916 | 123.7473 | 74.3729 | -0.2243 | 123.7701 | 2.916 | 74.3729 | 113.7131 | 123.7473 | -123.999 | -123.999
1758.7188 | 123.9395 | -61.2717 | 62.5259 | -0.22255 | 0.01581 | 0.020677 | 0.010611 | 0.064521 | 0.0030847 | 0.08204 | -58.6807 | 62.4664 | -61.5326 | -61.4548 | 52.2354 | 13.0234 | 1.4694 | 1.1719 | 62.4847 | -61.5143 | -0.26093 | -0.059509 | 2.5909 | -0.18311 | -10.2905 | -0.24262 | -0.041199 | 2.8519 | 62.7411 | 62.4435 | 113.5071 | 123.7381 | 2.5909 | 123.7564 | 74.295 | -0.24262 | 123.7381 | 2.5909 | 74.295 | 113.5071 | 123.7564 | -124.0585 | -124.0402
1759.7188 | 123.9716 | -61.2625 | 62.5122 | -0.20729 | 0.017519 | 0.017472 | 0.010397 | 0.06388 | 0.0032983 | 0.082681 | -58.5159 | 62.4893 | -61.5234 | -61.4822 | 52.327 | 12.7899 | 1.6296 | 0.92468 | 62.5031 | -61.4914 | -0.26093 | -0.022888 | 2.7466 | -0.21973 | -10.1852 | -0.22888 | -0.009155 | 3.0075 | 62.8922 | 62.1872 | 113.5895 | 123.7518 | 2.7466 | 123.7656 | 74.0524 | -0.22888 | 123.7518 | 2.7466 | 74.0524 | 113.5895 | 123.7656 | -124.0356 | -124.0036
1760.7188 | 123.8983 | -61.2625 | 62.5351 | -0.19966 | 0.015383 | 0.017899 | 0.010824 | 0.066016 | 0.0020167 | 0.082253 | -58.5434 | 62.4527 | -61.528 | -61.4731 | 52.6108 | 12.973 | 1.474 | 1.2497 | 62.4985 | -61.496 | -0.2655 | -0.082397 | 2.7191 | -0.21057 | -9.9243 | -0.23346 | -0.036621 | 2.9846 | 62.7365 | 62.5122 | 113.8733 | 123.7152 | 2.7191 | 123.761 | 74.2355 | -0.23346 | 123.7152 | 2.7191 | 74.2355 | 113.8733 | 123.761 | -124.0631 | -124.0311
1761.7188 | 123.9441 | -61.2717 | 62.5168 | -0.25307 | 0.01581 | 0.022172 | 0.010397 | 0.064093 | 0.0013757 | 0.085885 | -58.6212 | 62.4847 | -61.4914 | -61.4731 | 52.327 | 12.9684 | 1.4053 | 1.0574 | 62.5076 | -61.528 | -0.21973 | -0.032044 | 2.6505 | -0.20142 | -10.1898 | -0.25635 | -0.009156 | 2.8702 | 62.677 | 62.3291 | 113.5986 | 123.7564 | 2.6505 | 123.7793 | 74.2401 | -0.25635 | 123.7564 | 2.6505 | 74.2401 | 113.5986 | 123.7793 | -124.0082 | -124.0448
1762.7188 | 123.9716 | -61.2762 | 62.4985 | -0.062332 | 0.017519 | 0.016618 | 0.015951 | 0.063239 | 0.0028711 | 0.083962 | -58.4839 | 62.5076 | -61.496 | -61.4365 | 52.4277 | 12.886 | 1.2817 | 1.2039 | 62.4573 | -61.5601 | -0.21973 | 0.009155 | 2.7924 | -0.16022 | -10.0708 | -0.28381 | -0.041199 | 3.0121 | 62.558 | 62.4802 | 113.7039 | 123.7839 | 2.7924 | 123.7335 | 74.1623 | -0.28381 | 123.7839 | 2.7924 | 74.1623 | 113.7039 | 123.7335 | -123.9944 | -124.0585
1763.7188 | 123.9258 | -61.2762 | 62.5214 | -0.19966 | 0.014529 | 0.014268 | 0.010397 | 0.06388 | 0.0013757 | 0.085031 | -58.5938 | 62.4847 | -61.5326 | -61.2625 | 52.6016 | 12.8174 | 1.4374 | 1.2909 | 62.4893 | -61.5417 | -0.25635 | -0.036621 | 2.6825 | 0.013733 | -9.9197 | -0.2655 | -0.032043 | 2.9388 | 62.7136 | 62.5671 | 113.8779 | 123.761 | 2.6825 | 123.7656 | 74.0936 | -0.2655 | 123.761 | 2.6825 | 74.0936 | 113.8779 | 123.7656 | -124.054 | -124.0631
1764.7188 | 123.9578 | -61.2625 | 62.5214 | -0.1844 | 0.016238 | 0.021531 | 0.0084744 | 0.06388 | 0.00094847 | 0.083749 | -58.6166 | 62.4756 | -61.528 | -61.4639 | 52.5421 | 12.8723 | 1.3641 | 1.1673 | 62.471 | -61.5234 | -0.2655 | -0.045776 | 2.6459 | -0.20142 | -9.9792 | -0.26093 | -0.050354 | 2.9114 | 62.6266 | 62.4298 | 113.8046 | 123.7381 | 2.6459 | 123.7335 | 74.1348 | -0.26093 | 123.7381 | 2.6459 | 74.1348 | 113.8046 | 123.7335 | -124.0494 | -124.0448
1765.7188 | 123.9212 | -61.2762 | 62.5397 | -0.27596 | 0.014315 | 0.017045 | 0.010611 | 0.063025 | 0.00073487 | 0.082467 | -58.5571 | 62.4481 | -61.5189 | -61.4548 | 52.4872 | 12.7075 | 1.3184 | 1.1993 | 62.5031 | -61.5189 | -0.24261 | -0.091553 | 2.7191 | -0.17853 | -10.0525 | -0.24261 | -0.036621 | 2.9617 | 62.5946 | 62.4756 | 113.7634 | 123.7244 | 2.7191 | 123.7793 | 73.9838 | -0.24261 | 123.7244 | 2.7191 | 73.9838 | 113.7634 | 123.7793 | -124.0585 | -124.0585
1766.7188 | 123.9395 | -61.2808 | 62.5214 | -0.27596 | 0.015169 | 0.017899 | 0.0095424 | 0.063666 | 0.0020167 | 0.083535 | -58.6121 | 62.4252 | -61.4731 | -61.4365 | 52.6337 | 12.7213 | 1.2314 | 1.149 | 62.4802 | -61.5143 | -0.19226 | -0.09613 | 2.6688 | -0.15564 | -9.8877 | -0.23346 | -0.041198 | 2.861 | 62.5122 | 62.4298 | 113.9145 | 123.7061 | 2.6688 | 123.761 | 74.0021 | -0.23346 | 123.7061 | 2.6688 | 74.0021 | 113.9145 | 123.761 | -123.9944 | -124.0356
1767.7188 | 123.9853 | -61.2671 | 62.4893 | -0.016556 | 0.016238 | 0.022599 | 0.017019 | 0.064307 | 9.4068e-05 | 0.082253 | -58.5617 | 62.4481 | -61.528 | -61.4319 | 52.7298 | 12.7213 | 1.1948 | 1.1902 | 62.471 | -61.5372 | -0.26093 | -0.041199 | 2.7054 | -0.16479 | -9.7595 | -0.27008 | -0.018311 | 2.9663 | 62.4619 | 62.4573 | 113.9969 | 123.7152 | 2.7054 | 123.7381 | 73.9883 | -0.27008 | 123.7152 | 2.7054 | 73.9883 | 113.9969 | 123.7381 | -124.0173 | -124.0265
1768.7188 | 124.0677 | -61.2259 | 62.4847 | -0.51247 | 0.015597 | 0.018113 | 0.0063382 | 0.063239 | 0.0015893 | 0.082467 | -58.5526 | 62.3795 | -61.5005 | -61.3678 | 52.8122 | 12.735 | 1.1124 | 1.3367 | 62.4527 | -61.4548 | -0.27466 | -0.10529 | 2.6733 | -0.14191 | -9.6725 | -0.22888 | -0.032043 | 2.948 | 62.3383 | 62.5626 | 114.0381 | 123.6053 | 2.6733 | 123.6786 | 73.9609 | -0.22888 | 123.6053 | 2.6733 | 73.9609 | 114.0381 | 123.6786 | -123.9853 | -123.9395
1769.7188 | 123.9899 | -61.2579 | 62.5076 | -0.22255 | 0.014101 | 0.018113 | 0.0095424 | 0.062598 | 0.00030767 | 0.082467 | -58.4473 | 62.4252 | -61.4868 | -61.377 | 52.6932 | 12.6297 | 1.1169 | 1.2589 | 62.4527 | -61.5143 | -0.22888 | -0.082397 | 2.8107 | -0.11902 | -9.8145 | -0.25635 | -0.054931 | 3.0395 | 62.3749 | 62.5168 | 113.9511 | 123.6832 | 2.8107 | 123.7106 | 73.8876 | -0.25635 | 123.6832 | 2.8107 | 73.8876 | 113.9511 | 123.7106 | -123.9944 | -124.0219
1770.7188 | 123.9212 | -61.2625 | 62.5259 | -0.2607 | 0.016878 | 0.017899 | 0.010824 | 0.063452 | 0.0024439 | 0.082894 | -58.5709 | 62.4207 | -61.4914 | -61.441 | 52.6337 | 12.5061 | 1.2863 | 1.3596 | 62.4573 | -61.5051 | -0.22888 | -0.10529 | 2.6917 | -0.17853 | -9.8923 | -0.24262 | -0.068665 | 2.9205 | 62.5488 | 62.6221 | 113.8962 | 123.6832 | 2.6917 | 123.7198 | 73.7686 | -0.24262 | 123.6832 | 2.6917 | 73.7686 | 113.8962 | 123.7198 | -124.0173 | -124.0311
1771.7188 | 123.9395 | -61.2534 | 62.5442 | -0.24544 | 0.016238 | 0.020036 | 0.011679 | 0.060462 | 0.0035121 | 0.083322 | -58.4885 | 62.4435 | -61.5051 | -61.4136 | 52.4826 | 12.3734 | 1.1215 | 1.1169 | 62.4756 | -61.4822 | -0.25177 | -0.10071 | 2.7649 | -0.16022 | -10.0616 | -0.22888 | -0.068664 | 3.0167 | 62.3749 | 62.3703 | 113.736 | 123.6969 | 2.7649 | 123.7289 | 73.6267 | -0.22888 | 123.6969 | 2.7649 | 73.6267 | 113.736 | 123.7289 | -124.0494 | -124.0265
1772.7188 | 123.9807 | -61.2305 | 62.5076 | -0.25307 | 0.016024 | 0.01555 | 0.011038 | 0.060889 | 0.0037257 | 0.082253 | -58.5754 | 62.4023 | -61.4822 | -61.4044 | 52.6657 | 12.561 | 1.0803 | 1.268 | 62.4527 | -61.4685 | -0.25177 | -0.10529 | 2.655 | -0.17395 | -9.8419 | -0.23804 | -0.054931 | 2.9068 | 62.3108 | 62.4985 | 113.8962 | 123.6328 | 2.655 | 123.6832 | 73.7915 | -0.23804 | 123.6328 | 2.655 | 73.7915 | 113.8962 | 123.6832 | -123.9899 | -123.9761
1773.7188 | 123.9899 | -61.2396 | 62.4847 | -0.17677 | 0.014315 | 0.020463 | 0.010397 | 0.059607 | 0.0024439 | 0.083108 | -58.4015 | 62.384 | -61.496 | -61.3861 | 52.5742 | 12.6755 | 0.92468 | 1.2955 | 62.471 | -61.4685 | -0.25635 | -0.10071 | 2.8381 | -0.14648 | -9.9106 | -0.22888 | -0.013733 | 3.0945 | 62.1643 | 62.5351 | 113.8138 | 123.6237 | 2.8381 | 123.7106 | 73.9151 | -0.22888 | 123.6237 | 2.8381 | 73.9151 | 113.8138 | 123.7106 | -123.9807 | -123.9532
1774.7188 | 124.0128 | -61.2488 | 62.4985 | -0.23018 | 0.011751 | 0.017045 | 0.0099698 | 0.063666 | 0.0011621 | 0.083535 | -58.548 | 62.3795 | -61.4639 | -61.3632 | 52.6199 | 12.8677 | 1.2634 | 1.4511 | 62.4435 | -61.4731 | -0.21515 | -0.11902 | 2.7008 | -0.11444 | -9.8785 | -0.2243 | -0.054932 | 2.916 | 62.5122 | 62.6999 | 113.8687 | 123.6282 | 2.7008 | 123.6923 | 74.1165 | -0.2243 | 123.6282 | 2.7008 | 74.1165 | 113.8687 | 123.6923 | -123.9624 | -123.9716
1775.7188 | 124.0311 | -61.322 | 62.5031 | 0.1284 | 0.017947 | 0.021745 | 0.016806 | 0.064521 | 0.0022303 | 0.082467 | -58.3328 | 62.4481 | -61.5097 | -61.4914 | 52.4872 | 12.6434 | 1.0712 | 0.90179 | 62.4344 | -61.5921 | -0.18768 | -0.054932 | 2.9892 | -0.16937 | -10.0159 | -0.27008 | -0.068665 | 3.1769 | 62.3932 | 62.2238 | 113.8092 | 123.7701 | 2.9892 | 123.7564 | 73.9655 | -0.27008 | 123.7701 | 2.9892 | 73.9655 | 113.8092 | 123.7564 | -124.0128 | -124.0952
1776.7188 | 124.0311 | -61.2213 | 62.4802 | -0.22255 | 0.013674 | 0.012132 | 0.0074062 | 0.062598 | 0.0045801 | 0.082681 | -58.3282 | 62.4344 | -61.4502 | -61.3541 | 52.7939 | 12.9822 | 1.03 | 1.4923 | 62.4207 | -61.4868 | -0.22888 | -0.045777 | 2.8931 | -0.13275 | -9.6863 | -0.2655 | -0.05951 | 3.1219 | 62.2513 | 62.7136 | 114.0152 | 123.6557 | 2.8931 | 123.642 | 74.2035 | -0.2655 | 123.6557 | 2.8931 | 74.2035 | 114.0152 | 123.642 | -123.9304 | -123.967
1777.7188 | 123.8846 | -61.2762 | 62.5122 | -0.20729 | 0.017306 | 0.015336 | 0.011038 | 0.063666 | 0.0035121 | 0.083322 | -58.4976 | 62.4252 | -61.4868 | -61.441 | 52.6932 | 12.7029 | 1.2085 | 1.3321 | 62.4756 | -61.5097 | -0.21057 | -0.086975 | 2.7786 | -0.16479 | -9.819 | -0.23346 | -0.036621 | 2.9892 | 62.4847 | 62.6083 | 113.9694 | 123.7015 | 2.7786 | 123.7518 | 73.9792 | -0.23346 | 123.7015 | 2.7786 | 73.9792 | 113.9694 | 123.7518 | -123.999 | -124.0219
1778.7188 | 124.0265 | -61.235 | 62.4756 | 0.04448 | 0.014529 | 0.015763 | 0.011038 | 0.06388 | 0.0015893 | 0.083322 | -58.461 | 62.4023 | -61.4731 | -61.3495 | 52.7206 | 12.6892 | 1.0391 | 1.4053 | 62.439 | -61.4822 | -0.23804 | -0.073242 | 2.774 | -0.11444 | -9.7549 | -0.24719 | -0.036621 | 3.0121 | 62.2742 | 62.6404 | 113.9557 | 123.6374 | 2.774 | 123.674 | 73.9243 | -0.24719 | 123.6374 | 2.774 | 73.9243 | 113.9557 | 123.674 | -123.9487 | -123.9578
1779.7188 | 124.0219 | -61.2213 | 62.4985 | -0.55824 | 0.016665 | 0.023026 | 0.0095424 | 0.060675 | 9.4068e-05 | 0.083749 | -58.6533 | 62.384 | -61.4822 | -61.3907 | 52.7023 | 12.8677 | 0.93842 | 1.3687 | 62.4344 | -61.4639 | -0.26093 | -0.11444 | 2.5681 | -0.16937 | -9.7961 | -0.24262 | -0.064087 | 2.829 | 62.1597 | 62.59 | 113.9236 | 123.6053 | 2.5681 | 123.6557 | 74.0891 | -0.24262 | 123.6053 | 2.5681 | 74.0891 | 113.9236 | 123.6557 | -123.9807 | -123.9624
1780.7188 | 123.9487 | -61.2625 | 62.5122 | -0.10048 | 0.017519 | 0.017472 | 0.02001 | 0.062812 | 0.0011621 | 0.082467 | -58.461 | 62.4847 | -61.4914 | -61.4365 | 52.6245 | 12.7762 | 1.3824 | 1.4603 | 62.4344 | -61.5417 | -0.22888 | -0.027466 | 2.8015 | -0.17395 | -9.8877 | -0.27924 | -0.07782 | 3.0304 | 62.645 | 62.7228 | 113.887 | 123.7473 | 2.8015 | 123.6969 | 74.0387 | -0.27924 | 123.7473 | 2.8015 | 74.0387 | 113.887 | 123.6969 | -124.0036 | -124.054
1781.7188 | 124.0768 | -61.2076 | 62.4847 | -0.08522 | 0.014315 | 0.014695 | 0.010183 | 0.06388 | 0.00052127 | 0.083962 | -58.4518 | 62.3657 | -61.4731 | -61.3403 | 52.7847 | 12.7899 | 1.0071 | 1.3367 | 62.4161 | -61.4685 | -0.2655 | -0.11902 | 2.7557 | -0.13275 | -9.7 | -0.26093 | -0.068664 | 3.0212 | 62.2147 | 62.5443 | 113.9923 | 123.5733 | 2.7557 | 123.6237 | 73.9975 | -0.26093 | 123.5733 | 2.7557 | 73.9975 | 113.9923 | 123.6237 | -123.9578 | -123.9532
1782.7188 | 123.9532 | -61.2808 | 62.5259 | -0.14626 | 0.016878 | 0.018113 | 0.018301 | 0.062598 | 0.0028711 | 0.083322 | -58.4335 | 62.4847 | -61.5005 | -61.4044 | 52.6154 | 12.4924 | 1.2589 | 1.2451 | 62.4619 | -61.5189 | -0.21973 | -0.041199 | 2.8473 | -0.1236 | -9.9106 | -0.23804 | -0.064087 | 3.067 | 62.5397 | 62.5259 | 113.8962 | 123.7656 | 2.8473 | 123.7427 | 73.7732 | -0.23804 | 123.7656 | 2.8473 | 73.7732 | 113.8962 | 123.7427 | -124.0265 | -124.0448
1783.7188 | 124.0723 | -61.2167 | 62.4435 | -0.077591 | 0.01581 | 0.01854 | 0.0080472 | 0.064521 | 0.0041529 | 0.083322 | -58.6624 | 62.3703 | -61.5097 | -61.3632 | 52.7527 | 12.4054 | 1.1169 | 1.442 | 62.4115 | -61.4502 | -0.29297 | -0.073242 | 2.5543 | -0.14648 | -9.6909 | -0.23346 | -0.032043 | 2.8473 | 62.3337 | 62.6587 | 113.9694 | 123.587 | 2.5543 | 123.6282 | 73.6221 | -0.23346 | 123.587 | 2.5543 | 73.6221 | 113.9694 | 123.6282 | -123.9532 | -123.8937
1784.7188 | 124.0356 | -61.1938 | 62.5397 | -0.11574 | 0.011965 | 0.014909 | 0.0097562 | 0.060034 | 9.4068e-05 | 0.083749 | -58.4061 | 62.3978 | -61.4639 | -61.322 | 52.8854 | 12.7441 | 0.93384 | 1.3046 | 62.4115 | -61.4685 | -0.27008 | -0.14191 | 2.7878 | -0.12817 | -9.6542 | -0.27466 | -0.12817 | 3.0579 | 62.1277 | 62.4985 | 114.0793 | 123.5916 | 2.7878 | 123.6053 | 73.938 | -0.27466 | 123.5916 | 2.7878 | 73.938 | 114.0793 | 123.6053 | -124.0036 | -124.0082
1785.7344 | 123.9487 | -61.2305 | 62.5031 | -0.08522 | 0.019869 | 0.017472 | 0.017019 | 0.063239 | 0.0022303 | 0.082894 | -58.4793 | 62.4619 | -61.4822 | -61.4777 | 52.4551 | 12.3138 | 1.0345 | 1.1078 | 62.439 | -61.5189 | -0.25177 | -0.041199 | 2.7512 | -0.24719 | -10.0479 | -0.28839 | -0.064087 | 3.0029 | 62.265 | 62.3383 | 113.6856 | 123.6923 | 2.7512 | 123.6694 | 73.5443 | -0.28839 | 123.6923 | 2.7512 | 73.5443 | 113.6856 | 123.6694 | -123.9853 | -124.0219
1786.7188 | 124.0448 | -61.2122 | 62.4847 | -0.09285 | 0.014956 | 0.011704 | 0.0074062 | 0.063025 | 0.0011621 | 0.082253 | -58.5388 | 62.3657 | -61.4822 | -61.3678 | 52.5604 | 12.3642 | 0.90179 | 1.2634 | 62.4115 | -61.4456 | -0.27008 | -0.11902 | 2.6733 | -0.15564 | -9.9243 | -0.23346 | -0.073242 | 2.9434 | 62.114 | 62.4756 | 113.7726 | 123.5779 | 2.6733 | 123.6237 | 73.5764 | -0.23346 | 123.5779 | 2.6733 | 73.5764 | 113.7726 | 123.6237 | -123.967 | -123.9304
1787.7188 | 123.9212 | -61.2717 | 62.5168 | -0.0089264 | 0.016024 | 0.015122 | 0.013174 | 0.062598 | 0.00052127 | 0.084176 | -58.4656 | 62.471 | -61.5417 | -61.4273 | 52.5833 | 12.6205 | 1.1261 | 1.1169 | 62.4664 | -61.5234 | -0.27008 | -0.045777 | 2.8061 | -0.15564 | -9.9335 | -0.25177 | -0.050354 | 3.0762 | 62.3978 | 62.3886 | 113.855 | 123.7427 | 2.8061 | 123.7381 | 73.8922 | -0.25177 | 123.7427 | 2.8061 | 73.8922 | 113.855 | 123.7381 | -124.0585 | -124.0402
1788.7188 | 124.0311 | -61.2396 | 62.4939 | 0.021591 | 0.01581 | 0.015763 | 0.0082608 | 0.063452 | 0.0013757 | 0.085244 | -58.3603 | 62.3749 | -61.5189 | -61.4273 | 52.565 | 12.4283 | 0.9201 | 1.0254 | 62.4298 | -61.4822 | -0.27924 | -0.11902 | 2.8793 | -0.18768 | -9.9289 | -0.24262 | -0.064086 | 3.1586 | 62.1597 | 62.265 | 113.8046 | 123.6145 | 2.8793 | 123.6694 | 73.6679 | -0.24262 | 123.6145 | 2.8793 | 73.6679 | 113.8046 | 123.6694 | -124.0128 | -123.9761
1789.7188 | 124.0402 | -61.2259 | 62.4664 | -0.10048 | 0.014956 | 0.016618 | 0.0099698 | 0.062384 | 0.0035121 | 0.084176 | -58.429 | 62.3886 | -61.4731 | -61.377 | 52.6749 | 12.442 | 0.5722 | 0.89722 | 62.4298 | -61.4731 | -0.24719 | -0.07782 | 2.7969 | -0.15106 | -9.7916 | -0.24719 | -0.036621 | 3.0441 | 61.7981 | 62.1231 | 113.9008 | 123.6145 | 2.7969 | 123.6557 | 73.6679 | -0.24719 | 123.6145 | 2.7969 | 73.6679 | 113.9008 | 123.6557 | -123.9395 | -123.9395
1790.7188 | 123.9395 | -61.2488 | 62.5488 | -0.131 | 0.01816 | 0.01555 | 0.016806 | 0.061316 | 0.0013757 | 0.082894 | -58.4656 | 62.4893 | -61.4868 | -61.4182 | 52.7206 | 12.323 | 0.9613 | 0.85144 | 62.4664 | -61.5234 | -0.23804 | -0.059509 | 2.7832 | -0.16937 | -9.8282 | -0.27466 | -0.082397 | 3.0212 | 62.2101 | 62.1002 | 113.9694 | 123.7381 | 2.7832 | 123.7152 | 73.5718 | -0.27466 | 123.7381 | 2.7832 | 73.5718 | 113.9694 | 123.7152 | -124.0356 | -124.0723
1791.7188 | 123.9212 | -61.1847 | 62.4664 | -0.15388 | 0.01282 | 0.013413 | 0.0091152 | 0.062598 | 0.0028711 | 0.085244 | -58.2413 | 62.3795 | -61.4639 | -61.3403 | 52.4918 | 12.3688 | 0.63629 | 0.99792 | 62.4619 | -61.4273 | -0.27924 | -0.086975 | 2.9434 | -0.15564 | -9.9747 | -0.24262 | -0.004578 | 3.2227 | 61.821 | 62.1826 | 113.6765 | 123.5641 | 2.9434 | 123.6465 | 73.5535 | -0.24262 | 123.5641 | 2.9434 | 73.5535 | 113.6765 | 123.6465 | -123.9304 | -123.8937
1792.7188 | 123.9349 | -61.2671 | 62.5397 | -0.28358 | 0.014956 | 0.016618 | 0.011038 | 0.059607 | 0.0041529 | 0.082894 | -58.2687 | 62.4298 | -61.4914 | -61.4182 | 52.5192 | 12.4741 | 0.92926 | 0.93384 | 62.471 | -61.4868 | -0.2243 | -0.10986 | 2.9984 | -0.15106 | -10.0204 | -0.21973 | -0.068665 | 3.2227 | 62.1964 | 62.2009 | 113.7863 | 123.6969 | 2.9984 | 123.7381 | 73.7412 | -0.21973 | 123.6969 | 2.9984 | 73.7412 | 113.7863 | 123.7381 | -124.0311 | -124.0265
1793.7188 | 124.1226 | -61.1801 | 62.5076 | -0.131 | 0.014956 | 0.013627 | 0.0099698 | 0.062598 | 0.0015893 | 0.084176 | -58.2184 | 62.3749 | -61.4685 | -61.3266 | 52.7481 | 12.4741 | 0.79651 | 0.98877 | 62.4252 | -61.4456 | -0.28839 | -0.13275 | 2.9617 | -0.14648 | -9.7595 | -0.2655 | -0.082397 | 3.2501 | 61.9766 | 62.1689 | 113.9282 | 123.555 | 2.9617 | 123.6053 | 73.6542 | -0.2655 | 123.555 | 2.9617 | 73.6542 | 113.9282 | 123.6053 | -123.9761 | -123.9532
1794.7188 | 123.9075 | -61.2076 | 62.4802 | -0.13863 | 0.015169 | 0.01854 | 0.011892 | 0.058325 | 9.4068e-05 | 0.082467 | -58.2916 | 62.3932 | -61.4868 | -61.3266 | 52.8168 | 12.6892 | 0.75531 | 1.3046 | 62.471 | -61.4273 | -0.27923 | -0.086976 | 2.916 | -0.11902 | -9.6634 | -0.21973 | -0.009156 | 3.1952 | 61.9629 | 62.5122 | 114.0244 | 123.6008 | 2.916 | 123.6786 | 73.8968 | -0.21973 | 123.6008 | 2.916 | 73.8968 | 114.0244 | 123.6786 | -123.967 | -123.9075
1795.7188 | 124.0448 | -61.235 | 62.471 | -0.062332 | 0.014315 | 0.01555 | 0.0095424 | 0.062812 | 0.0035121 | 0.084176 | -58.2733 | 62.3657 | -61.4777 | -61.3815 | 52.5696 | 12.5061 | 0.77362 | 0.97504 | 62.4252 | -61.4548 | -0.24262 | -0.10528 | 2.9617 | -0.14649 | -9.9014 | -0.21973 | -0.045776 | 3.2043 | 62.0087 | 62.2101 | 113.8046 | 123.6008 | 2.9617 | 123.6603 | 73.7412 | -0.21973 | 123.6008 | 2.9617 | 73.7412 | 113.8046 | 123.6603 | -123.9487 | -123.9258
1796.7188 | 124.0494 | -61.2259 | 62.4664 | -0.19203 | 0.016451 | 0.017899 | 0.012106 | 0.061103 | 0.00073487 | 0.082681 | -58.3466 | 62.3703 | -61.4685 | -61.3678 | 52.771 | 12.8082 | 0.75989 | 0.90179 | 62.4344 | -61.4639 | -0.24262 | -0.096131 | 2.8793 | -0.14191 | -9.6954 | -0.23804 | -0.032044 | 3.1219 | 61.9858 | 62.1277 | 113.9969 | 123.5962 | 2.8793 | 123.6603 | 74.0341 | -0.23804 | 123.5962 | 2.8793 | 74.0341 | 113.9969 | 123.6603 | -123.9349 | -123.9304
1797.7344 | 123.9349 | -61.2396 | 62.5122 | -0.15388 | 0.019442 | 0.022599 | 0.015951 | 0.065375 | 0.0024439 | 0.081399 | -58.2504 | 62.4802 | -61.4777 | -61.4044 | 52.5467 | 12.4969 | 0.95215 | 0.91095 | 62.4344 | -61.5051 | -0.23804 | -0.032043 | 2.9892 | -0.16479 | -9.9655 | -0.2655 | -0.07782 | 3.2272 | 62.1918 | 62.1506 | 113.7863 | 123.7198 | 2.9892 | 123.674 | 73.7366 | -0.2655 | 123.7198 | 2.9892 | 73.7366 | 113.7863 | 123.674 | -123.9899 | -124.0173
1798.7188 | 124.0036 | -61.2305 | 62.5168 | -0.16914 | 0.014742 | 0.017899 | 0.0093288 | 0.063452 | 0.0011621 | 0.084176 | -58.3374 | 62.3886 | -61.4868 | -61.3586 | 52.6428 | 12.4329 | 0.83771 | 1.0986 | 62.4527 | -61.441 | -0.25635 | -0.12817 | 2.8931 | -0.12817 | -9.874 | -0.21057 | -0.064087 | 3.1494 | 62.0682 | 62.3291 | 113.8733 | 123.6191 | 2.8931 | 123.6832 | 73.6633 | -0.21057 | 123.6191 | 2.8931 | 73.6633 | 113.8733 | 123.6832 | -124.0036 | -123.9578
1799.7188 | 123.9807 | -61.2167 | 62.4893 | -0.21492 | 0.015383 | 0.01854 | 0.010611 | 0.061743 | 0.0030847 | 0.082467 | -58.0765 | 62.3978 | -61.4777 | -61.3861 | 52.7985 | 12.4878 | 0.91553 | 1.03 | 62.4298 | -61.4868 | -0.26093 | -0.091553 | 3.1403 | -0.16937 | -9.6909 | -0.27008 | -0.059509 | 3.4012 | 62.1323 | 62.2467 | 114.0152 | 123.6145 | 3.1403 | 123.6465 | 73.7045 | -0.27008 | 123.6145 | 3.1403 | 73.7045 | 114.0152 | 123.6465 | -123.967 | -123.9761
1800.7188 | 123.9807 | -61.2076 | 62.5076 | -0.23018 | 0.015597 | 0.016618 | 0.010397 | 0.063025 | 0.0020167 | 0.084176 | -58.342 | 62.4069 | -61.4777 | -61.377 | 52.6062 | 12.4283 | 0.76446 | 1.0345 | 62.4298 | -61.4548 | -0.27008 | -0.10071 | 2.8656 | -0.16937 | -9.9014 | -0.24719 | -0.077819 | 3.1357 | 61.972 | 62.2421 | 113.8138 | 123.6145 | 2.8656 | 123.6374 | 73.6359 | -0.24719 | 123.6145 | 2.8656 | 73.6359 | 113.8138 | 123.6374 | -123.9853 | -123.9624
1801.7188 | 123.9807 | -61.2213 | 62.5305 | -0.2607 | 0.016878 | 0.020249 | 0.011465 | 0.061743 | 0.0022303 | 0.081399 | -58.4564 | 62.4207 | -61.4639 | -61.3953 | 52.5101 | 12.3413 | 0.80109 | 0.94757 | 62.4481 | -61.4731 | -0.24262 | -0.10986 | 2.7649 | -0.17395 | -10.0204 | -0.25177 | -0.082398 | 3.0075 | 62.0224 | 62.1689 | 113.7314 | 123.642 | 2.7649 | 123.6694 | 73.5626 | -0.25177 | 123.642 | 2.7649 | 73.5626 | 113.7314 | 123.6694 | -123.9944 | -124.0036
1802.7188 | 123.9258 | -61.2762 | 62.5122 | -0.031814 | 0.01816 | 0.014909 | 0.018728 | 0.064307 | 0.00073487 | 0.081185 | -58.3145 | 62.4756 | -61.5143 | -61.4227 | 52.5375 | 12.5977 | 0.95215 | 0.97046 | 62.471 | -61.5326 | -0.23804 | -0.036621 | 2.9617 | -0.14648 | -9.9747 | -0.25635 | -0.041199 | 3.1998 | 62.2284 | 62.2467 | 113.8138 | 123.7518 | 2.9617 | 123.7473 | 73.8739 | -0.25635 | 123.7518 | 2.9617 | 73.8739 | 113.8138 | 123.7473 | -124.0265 | -124.0448
1803.7188 | 123.9349 | -61.2488 | 62.4939 | -0.23781 | 0.017947 | 0.016191 | 0.012106 | 0.06388 | 0.00094847 | 0.085671 | -58.4427 | 62.4161 | -61.4914 | -61.3998 | 52.5192 | 12.5931 | 1.236 | 1.1444 | 62.4527 | -61.4822 | -0.24262 | -0.077819 | 2.8061 | -0.15106 | -9.9747 | -0.23346 | -0.041198 | 3.0487 | 62.4847 | 62.3932 | 113.768 | 123.6649 | 2.8061 | 123.7015 | 73.8419 | -0.23346 | 123.6649 | 2.8061 | 73.8419 | 113.768 | 123.7015 | -123.9853 | -123.9761
1804.7188 | 123.8846 | -61.2625 | 62.5351 | -0.21492 | 0.01581 | 0.017899 | 0.014669 | 0.064093 | 0.0035121 | 0.08439 | -58.4381 | 62.4985 | -61.4914 | -61.3129 | 52.6932 | 12.3322 | 0.99335 | 1.0437 | 62.4435 | -61.5097 | -0.22888 | -0.036621 | 2.8244 | -0.050354 | -9.8419 | -0.24719 | -0.091553 | 3.0533 | 62.2559 | 62.3062 | 113.9557 | 123.761 | 2.8244 | 123.7061 | 73.5947 | -0.24719 | 123.761 | 2.8244 | 73.5947 | 113.9557 | 123.7061 | -124.0265 | -124.0448
1805.7188 | 123.9258 | -61.2579 | 62.4985 | -0.19203 | 0.01581 | 0.022599 | 0.011892 | 0.059821 | 0.0020167 | 0.084817 | -58.4473 | 62.4985 | -61.5097 | -61.6058 | 52.3315 | 12.5061 | 1.0712 | 0.98877 | 62.4619 | -61.5326 | -0.25177 | 0 | 2.8107 | -0.3479 | -10.1669 | -0.27466 | -0.036621 | 3.0624 | 62.3291 | 62.2467 | 113.5895 | 123.7564 | 2.8107 | 123.7198 | 73.764 | -0.27466 | 123.7564 | 2.8107 | 73.764 | 113.5895 | 123.7198 | -124.0082 | -124.0311
1806.7188 | 123.9166 | -61.2671 | 62.5168 | -0.23018 | 0.018587 | 0.016191 | 0.013601 | 0.065375 | 0.0018031 | 0.083322 | -58.4885 | 62.4756 | -61.5143 | -61.4273 | 52.3453 | 12.4191 | 1.0849 | 1.0895 | 62.4802 | -61.5189 | -0.24719 | -0.041199 | 2.7786 | -0.16022 | -10.1715 | -0.25177 | -0.036621 | 3.0258 | 62.352 | 62.3566 | 113.6124 | 123.7427 | 2.7786 | 123.7473 | 73.6862 | -0.25177 | 123.7427 | 2.7786 | 73.6862 | 113.6124 | 123.7473 | -124.0311 | -124.0356
1807.7188 | 123.9578 | -61.2442 | 62.5214 | -0.08522 | 0.017733 | 0.019395 | 0.014669 | 0.066016 | 0.0035121 | 0.083962 | -58.4152 | 62.4939 | -61.4822 | -61.4136 | 52.4414 | 12.3779 | 0.99792 | 1.0666 | 62.4619 | -61.5097 | -0.23804 | -0.027466 | 2.829 | -0.16937 | -10.08 | -0.2655 | -0.059509 | 3.067 | 62.2421 | 62.3108 | 113.6856 | 123.7381 | 2.829 | 123.7061 | 73.6221 | -0.2655 | 123.7381 | 2.829 | 73.6221 | 113.6856 | 123.7061 | -124.0036 | -124.0311
1808.7188 | 123.9166 | -61.2534 | 62.5168 | -1.9392 | 0.018374 | 0.017686 | 0.01232 | 0.065161 | 0.0043665 | 0.083535 | -58.5068 | 62.4802 | -61.5189 | -61.4914 | 52.3956 | 12.4786 | 1.0803 | 1.1536 | 62.4893 | -61.4914 | -0.2655 | -0.036621 | 2.7466 | -0.23804 | -10.1212 | -0.23804 | -0.027466 | 3.0121 | 62.3337 | 62.4069 | 113.649 | 123.7335 | 2.7466 | 123.7427 | 73.732 | -0.23804 | 123.7335 | 2.7466 | 73.732 | 113.649 | 123.7427 | -124.0356 | -124.0082
1809.7188 | 123.912 | -61.2488 | 62.5351 | -0.22255 | 0.017519 | 0.020249 | 0.0089016 | 0.064948 | 0.0013757 | 0.083749 | -58.4839 | 62.4756 | -61.4731 | -61.4502 | 52.3041 | 12.3276 | 0.93842 | 1.1673 | 62.4756 | -61.4868 | -0.2243 | -0.059509 | 2.7649 | -0.20142 | -10.231 | -0.23804 | -0.059509 | 2.9892 | 62.1872 | 62.4161 | 113.5529 | 123.7244 | 2.7649 | 123.7244 | 73.5764 | -0.23804 | 123.7244 | 2.7649 | 73.5764 | 113.5529 | 123.7244 | -124.0082 | -124.0219
1810.7188 | 123.9212 | -61.2717 | 62.5168 | -0.09285 | 0.015597 | 0.016404 | 0.013388 | 0.065375 | 0.0028711 | 0.084176 | -58.4198 | 62.4847 | -61.5326 | -61.4456 | 52.5284 | 12.4237 | 0.9613 | 1.0162 | 62.4802 | -61.5372 | -0.26093 | -0.032044 | 2.8519 | -0.17395 | -9.9884 | -0.2655 | -0.036621 | 3.1128 | 62.233 | 62.2879 | 113.8 | 123.7564 | 2.8519 | 123.7518 | 73.6954 | -0.2655 | 123.7564 | 2.8519 | 73.6954 | 113.8 | 123.7518 | -124.0494 | -124.054
1811.7188 | 123.9349 | -61.2579 | 62.5076 | -0.22255 | 0.018374 | 0.01854 | 0.015951 | 0.06623 | 0.0022303 | 0.082253 | -58.4015 | 62.4985 | -61.4822 | -61.4182 | 52.359 | 12.1902 | 0.92468 | 1.0437 | 62.471 | -61.5372 | -0.2243 | -0.009155 | 2.8564 | -0.16022 | -10.1486 | -0.27923 | -0.036621 | 3.0808 | 62.1826 | 62.3016 | 113.6169 | 123.7564 | 2.8564 | 123.7289 | 73.4482 | -0.27923 | 123.7564 | 2.8564 | 73.4482 | 113.6169 | 123.7289 | -123.9899 | -124.0448
1812.7188 | 123.9624 | -61.2854 | 62.5259 | 0.15129 | 0.018374 | 0.015122 | 0.015951 | 0.067511 | 0.0013757 | 0.08439 | -58.493 | 62.5031 | -61.5234 | -61.5097 | 52.3407 | 12.323 | 0.73242 | 0.65918 | 62.3932 | -61.5829 | -0.23804 | -0.022888 | 2.7924 | -0.2243 | -10.1852 | -0.29755 | -0.13275 | 3.0304 | 62.0178 | 61.9446 | 113.6261 | 123.7885 | 2.7924 | 123.6786 | 73.6084 | -0.29755 | 123.7885 | 2.7924 | 73.6084 | 113.6261 | 123.6786 | -124.0494 | -124.1089
1813.7188 | 123.9395 | -61.2534 | 62.5259 | -0.13863 | 0.01816 | 0.019395 | 0.01531 | 0.065802 | -0.00033333 | 0.083535 | -58.461 | 62.4939 | -61.5005 | -61.4182 | 52.5742 | 12.5336 | 1.0071 | 1.0666 | 62.4985 | -61.5234 | -0.24719 | -0.032044 | 2.7924 | -0.16479 | -9.9518 | -0.27008 | -0.027466 | 3.0395 | 62.2604 | 62.3199 | 113.8275 | 123.7473 | 2.7924 | 123.7518 | 73.7869 | -0.27008 | 123.7473 | 2.7924 | 73.7869 | 113.8275 | 123.7518 | -124.0265 | -124.0494
1814.7188 | 123.9212 | -61.2488 | 62.5305 | -0.16914 | 0.017092 | 0.01555 | 0.014242 | 0.065161 | 0.0028711 | 0.084817 | -58.4061 | 62.4802 | -61.5143 | -61.4182 | 52.4918 | 12.4695 | 1.0483 | 1.1307 | 62.4893 | -61.5097 | -0.2655 | -0.050354 | 2.8427 | -0.16937 | -10.0388 | -0.26093 | -0.041199 | 3.1082 | 62.2971 | 62.3795 | 113.7405 | 123.7289 | 2.8427 | 123.7381 | 73.7183 | -0.26093 | 123.7289 | 2.8427 | 73.7183 | 113.7405 | 123.7381 | -124.0448 | -124.0402
1815.7188 | 123.9487 | -61.2717 | 62.5031 | -0.11574 | 0.01816 | 0.015977 | 0.012747 | 0.066443 | 0.00094847 | 0.081185 | -58.3099 | 62.4985 | -61.4685 | -61.4319 | 52.597 | 12.735 | 1.0162 | 1.0712 | 62.4847 | -61.496 | -0.19684 | -0.004578 | 2.9617 | -0.16022 | -9.906 | -0.22431 | -0.018311 | 3.1586 | 62.2879 | 62.3428 | 113.8687 | 123.7701 | 2.9617 | 123.7564 | 74.0067 | -0.22431 | 123.7701 | 2.9617 | 74.0067 | 113.8687 | 123.7564 | -123.9716 | -123.999
1816.7188 | 123.9212 | -61.2671 | 62.5259 | -0.53535 | 0.019228 | 0.015763 | 0.0095424 | 0.065161 | 0.00052127 | 0.085244 | -58.4518 | 62.4847 | -61.5143 | -61.5097 | 52.478 | 12.5473 | 1.1398 | 1.0254 | 62.4802 | -61.5234 | -0.24719 | -0.041199 | 2.8152 | -0.24261 | -10.0479 | -0.25635 | -0.045776 | 3.0624 | 62.4069 | 62.2925 | 113.7451 | 123.7518 | 2.8152 | 123.7473 | 73.8144 | -0.25635 | 123.7518 | 2.8152 | 73.8144 | 113.7451 | 123.7473 | -124.0402 | -124.0494
1817.7188 | 123.9578 | -61.2488 | 62.4802 | -0.16151 | 0.017947 | 0.017899 | 0.014669 | 0.065375 | 0.0032983 | 0.082894 | -58.3969 | 62.4847 | -61.5097 | -61.4136 | 52.5238 | 12.8632 | 1.1032 | 1.0529 | 62.4619 | -61.5189 | -0.26093 | 0.004577 | 2.8519 | -0.16479 | -9.9564 | -0.27008 | -0.018311 | 3.1128 | 62.352 | 62.3016 | 113.7726 | 123.7335 | 2.8519 | 123.7106 | 74.1119 | -0.27008 | 123.7335 | 2.8519 | 74.1119 | 113.7726 | 123.7106 | -123.9899 | -123.999
1818.7188 | 123.9349 | -61.2625 | 62.5076 | -0.09285 | 0.017519 | 0.018968 | 0.014242 | 0.065161 | 0.0015893 | 0.082253 | -58.4015 | 62.4893 | -61.4822 | -61.4182 | 52.4734 | 12.5931 | 1.0803 | 1.1719 | 62.4893 | -61.5143 | -0.21973 | -0.01831 | 2.861 | -0.15564 | -10.0342 | -0.25177 | -0.01831 | 3.0808 | 62.3428 | 62.4344 | 113.736 | 123.7518 | 2.861 | 123.7518 | 73.8556 | -0.25177 | 123.7518 | 2.861 | 73.8556 | 113.736 | 123.7518 | -123.9899 | -124.0219
1819.7188 | 123.9578 | -61.2717 | 62.5076 | -0.10811 | 0.018374 | 0.016191 | 0.014242 | 0.064307 | 0.0041529 | 0.084817 | -58.3511 | 62.4939 | -61.5051 | -61.4182 | 52.4368 | 12.5793 | 1.0437 | 1.1765 | 62.471 | -61.5143 | -0.23346 | -0.013733 | 2.9205 | -0.14648 | -10.0708 | -0.24262 | -0.036621 | 3.154 | 62.3154 | 62.4481 | 113.7085 | 123.7656 | 2.9205 | 123.7427 | 73.851 | -0.24262 | 123.7656 | 2.9205 | 73.851 | 113.7085 | 123.7427 | -124.0128 | -124.0219
1820.7188 | 123.9487 | -61.2579 | 62.4893 | -0.14626 | 0.019656 | 0.018113 | 0.015097 | 0.065802 | 0.0015893 | 0.083962 | -58.3008 | 62.4985 | -61.5234 | -61.409 | 52.446 | 12.6389 | 0.92468 | 1.0895 | 62.4802 | -61.5143 | -0.2655 | 0.009155 | 2.9572 | -0.15106 | -10.0433 | -0.25635 | -0.009155 | 3.2227 | 62.1826 | 62.3474 | 113.7039 | 123.7564 | 2.9572 | 123.7381 | 73.8968 | -0.25635 | 123.7564 | 2.9572 | 73.8968 | 113.7039 | 123.7381 | -124.0128 | -124.0036
1821.7188 | 123.9578 | -61.2717 | 62.4985 | -0.17677 | 0.019228 | 0.018968 | 0.012533 | 0.065375 | 0.0011621 | 0.084817 | -58.2321 | 62.5168 | -61.496 | -61.4044 | 52.4872 | 12.7991 | 1.0849 | 1.2085 | 62.4847 | -61.5189 | -0.22431 | 0.018311 | 3.0395 | -0.13275 | -10.0113 | -0.24719 | -0.013733 | 3.2639 | 62.3566 | 62.4802 | 113.7588 | 123.7885 | 3.0395 | 123.7564 | 74.0707 | -0.24719 | 123.7885 | 3.0395 | 74.0707 | 113.7588 | 123.7564 | -123.9944 | -124.0173
1822.7188 | 123.9532 | -61.29 | 62.4527 | 0.15129 | 0.017947 | 0.018113 | 0.011038 | 0.067939 | 0.0015893 | 0.084176 | -58.5068 | 62.471 | -61.528 | -61.4914 | 52.2491 | 12.5015 | 1.062 | 1.1169 | 62.471 | -61.5417 | -0.23804 | 0.01831 | 2.7832 | -0.20142 | -10.2036 | -0.25177 | 0.01831 | 3.0212 | 62.352 | 62.4069 | 113.5391 | 123.761 | 2.7832 | 123.761 | 73.7915 | -0.25177 | 123.761 | 2.7832 | 73.7915 | 113.5391 | 123.761 | -123.9807 | -123.9944
1823.7188 | 123.9075 | -61.2717 | 62.5305 | 0.059738 | 0.018801 | 0.018113 | 0.011465 | 0.064521 | 0.0037257 | 0.084603 | -58.3099 | 62.5031 | -61.5005 | -61.4639 | 52.3041 | 12.4191 | 0.93384 | 1.0025 | 62.5076 | -61.5143 | -0.22888 | -0.027466 | 2.9617 | -0.19226 | -10.2264 | -0.24262 | -0.022889 | 3.1906 | 62.2055 | 62.2742 | 113.5757 | 123.7747 | 2.9617 | 123.7793 | 73.6908 | -0.24262 | 123.7747 | 2.9617 | 73.6908 | 113.5757 | 123.7793 | -124.0311 | -124.0448
1824.7188 | 123.9578 | -61.2625 | 62.5122 | -0.23781 | 0.017947 | 0.01854 | 0.014029 | 0.065802 | 0.00094847 | 0.085671 | -58.3649 | 62.5122 | -61.5143 | -61.441 | 52.4002 | 12.7533 | 1.1124 | 1.1261 | 62.4939 | -61.528 | -0.25177 | 0 | 2.8976 | -0.17853 | -10.112 | -0.2655 | -0.018311 | 3.1494 | 62.3749 | 62.3886 | 113.6627 | 123.7747 | 2.8976 | 123.7564 | 74.0158 | -0.2655 | 123.7747 | 2.8976 | 74.0158 | 113.6627 | 123.7564 | -124.0265 | -124.0402
1825.7188 | 123.9578 | -61.2305 | 62.4893 | -0.047073 | 0.016665 | 0.020463 | 0.014029 | 0.066443 | 0.0022303 | 0.083322 | -58.3603 | 62.5122 | -61.4777 | -61.4044 | 52.3178 | 12.3276 | 0.98419 | 1.0712 | 62.4756 | -61.5326 | -0.24719 | 0.022888 | 2.8702 | -0.17395 | -10.1715 | -0.30212 | -0.013733 | 3.1174 | 62.2147 | 62.3016 | 113.5483 | 123.7427 | 2.8702 | 123.7061 | 73.558 | -0.30212 | 123.7427 | 2.8702 | 73.558 | 113.5483 | 123.7061 | -123.967 | -124.0219
1826.7188 | 123.9761 | -61.2305 | 62.5122 | -0.26833 | 0.018801 | 0.015977 | 0.01296 | 0.067725 | 0.0011621 | 0.082467 | -58.2687 | 62.5122 | -61.5005 | -61.4227 | 52.153 | 12.1582 | 0.94299 | 1.1124 | 62.4802 | -61.5189 | -0.27008 | 0 | 2.9617 | -0.19226 | -10.3592 | -0.28839 | -0.032043 | 3.2318 | 62.1735 | 62.3428 | 113.3835 | 123.7427 | 2.9617 | 123.7106 | 73.3887 | -0.28839 | 123.7427 | 2.9617 | 73.3887 | 113.3835 | 123.7106 | -124.0128 | -124.0311
1827.7188 | 123.9029 | -61.2808 | 62.4985 | 0.35728 | 0.019228 | 0.016831 | 0.012747 | 0.066657 | 0.0039393 | 0.086312 | -58.287 | 62.5031 | -61.5417 | -61.5097 | 52.2858 | 12.1857 | 0.81024 | 0.90179 | 62.471 | -61.5372 | -0.26093 | 0.004578 | 2.9938 | -0.22888 | -10.2127 | -0.25635 | -0.027466 | 3.2547 | 62.0911 | 62.1826 | 113.5666 | 123.7839 | 2.9938 | 123.7518 | 73.4665 | -0.25635 | 123.7839 | 2.9938 | 73.4665 | 113.5666 | 123.7518 | -124.0402 | -124.0356
1828.7188 | 123.9761 | -61.2579 | 62.4893 | -0.077591 | 0.017092 | 0.021531 | 0.014669 | 0.064521 | 0.0018031 | 0.083108 | -58.4656 | 62.5122 | -61.4868 | -61.3953 | 52.1622 | 12.2086 | 0.91095 | 1.0071 | 62.471 | -61.528 | -0.22888 | 0.022888 | 2.7924 | -0.13733 | -10.3271 | -0.27008 | -0.018311 | 3.0212 | 62.1689 | 62.265 | 113.4201 | 123.7701 | 2.7924 | 123.7289 | 73.4665 | -0.27008 | 123.7701 | 2.7924 | 73.4665 | 113.4201 | 123.7289 | -123.9761 | -124.0173
1829.7188 | 123.9349 | -61.2396 | 62.5122 | -0.14626 | 0.017519 | 0.016618 | 0.014456 | 0.065802 | 0.0026575 | 0.08204 | -58.3649 | 62.5031 | -61.4822 | -61.4182 | 52.4597 | 12.2131 | 1.0666 | 1.0529 | 62.4985 | -61.5189 | -0.24262 | -0.009155 | 2.8748 | -0.17853 | -10.0525 | -0.27924 | -0.013733 | 3.1174 | 62.3062 | 62.2925 | 113.6993 | 123.7427 | 2.8748 | 123.7381 | 73.4528 | -0.27924 | 123.7427 | 2.8748 | 73.4528 | 113.6993 | 123.7381 | -123.9944 | -124.0311
1830.7188 | 123.9212 | -61.2442 | 62.5214 | -0.20729 | 0.017306 | 0.018113 | 0.0095424 | 0.065802 | 0.0041529 | 0.086312 | -58.6166 | 62.5122 | -61.4777 | -61.4685 | 52.1988 | 12.0575 | 0.90637 | 0.9201 | 62.5122 | -61.5143 | -0.23346 | -0.009155 | 2.6276 | -0.2243 | -10.3226 | -0.27008 | -0.009155 | 2.861 | 62.1506 | 62.1643 | 113.443 | 123.7564 | 2.6276 | 123.7564 | 73.3017 | -0.27008 | 123.7564 | 2.6276 | 73.3017 | 113.443 | 123.7564 | -123.999 | -124.0356
1831.7188 | 123.9532 | -61.2213 | 62.5031 | -0.16151 | 0.019442 | 0.016404 | 0.010397 | 0.065375 | 0.00094847 | 0.08439 | -58.5388 | 62.5122 | -61.4868 | -61.4365 | 52.0798 | 12.117 | 0.95673 | 1.0117 | 62.5259 | -61.5051 | -0.2655 | 0.009155 | 2.6825 | -0.21515 | -10.4233 | -0.28381 | 0.022888 | 2.948 | 62.178 | 62.233 | 113.3011 | 123.7335 | 2.6825 | 123.7473 | 73.3383 | -0.28381 | 123.7335 | 2.6825 | 73.3383 | 113.3011 | 123.7473 | -123.9899 | -124.0082
1832.7188 | 123.9395 | -61.2762 | 62.5122 | -0.15388 | 0.018801 | 0.019822 | 0.013388 | 0.066016 | 0.0024439 | 0.081826 | -58.4015 | 62.4985 | -61.5005 | -61.4273 | 52.3453 | 12.0117 | 0.95215 | 0.92468 | 62.5076 | -61.5189 | -0.2243 | -0.013733 | 2.8748 | -0.15106 | -10.1669 | -0.24261 | -0.004578 | 3.0991 | 62.2284 | 62.2009 | 113.6215 | 123.7747 | 2.8748 | 123.7839 | 73.288 | -0.24261 | 123.7747 | 2.8748 | 73.288 | 113.6215 | 123.7839 | -124.0128 | -124.0311
1833.7188 | 123.9624 | -61.235 | 62.5122 | -0.11574 | 0.017306 | 0.020249 | 0.013174 | 0.064307 | 0.0018031 | 0.08439 | -58.4061 | 62.5122 | -61.5005 | -61.4136 | 52.4185 | 12.0987 | 0.85602 | 0.79651 | 62.5076 | -61.5143 | -0.2655 | 0 | 2.829 | -0.17853 | -10.0937 | -0.27924 | -0.004578 | 3.0945 | 62.0911 | 62.0316 | 113.6536 | 123.7473 | 2.829 | 123.7427 | 73.3337 | -0.27924 | 123.7473 | 2.829 | 73.3337 | 113.6536 | 123.7427 | -124.0128 | -124.0265
1834.7188 | 123.9761 | -61.2579 | 62.5076 | -0.2607 | 0.019442 | 0.020677 | 0.014456 | 0.06623 | 0.0015893 | 0.082681 | -58.342 | 62.4939 | -61.4822 | -61.4136 | 52.2537 | 12.3001 | 0.97961 | 0.92926 | 62.5031 | -61.5051 | -0.2243 | -0.013733 | 2.916 | -0.15564 | -10.2539 | -0.24719 | -0.004577 | 3.1403 | 62.2375 | 62.1872 | 113.5117 | 123.7518 | 2.916 | 123.761 | 73.558 | -0.24719 | 123.7518 | 2.916 | 73.558 | 113.5117 | 123.761 | -123.9899 | -124.0128
1835.7188 | 123.9853 | -61.2625 | 62.5076 | -0.24544 | 0.017947 | 0.016404 | 0.01296 | 0.06623 | 0.0013757 | 0.082253 | -58.3557 | 62.5076 | -61.5097 | -61.409 | 52.2354 | 12.03 | 0.87891 | 0.99792 | 62.4893 | -61.5005 | -0.24719 | 0 | 2.9068 | -0.14648 | -10.2722 | -0.23804 | -0.01831 | 3.154 | 62.1414 | 62.2604 | 113.4979 | 123.7701 | 2.9068 | 123.7518 | 73.2925 | -0.23804 | 123.7701 | 2.9068 | 73.2925 | 113.4979 | 123.7518 | -124.0173 | -124.0082
1836.7188 | 123.9624 | -61.2396 | 62.4939 | -0.23781 | 0.02051 | 0.019395 | 0.014029 | 0.065802 | 0.0018031 | 0.083749 | -58.2825 | 62.5031 | -61.4822 | -61.4227 | 52.24 | 11.9293 | 0.83771 | 0.89722 | 62.5076 | -61.5143 | -0.24262 | 0.009156 | 2.9572 | -0.1831 | -10.2539 | -0.27466 | 0.013733 | 3.1998 | 62.0773 | 62.1368 | 113.4796 | 123.7427 | 2.9572 | 123.7473 | 73.1689 | -0.27466 | 123.7427 | 2.9572 | 73.1689 | 113.4796 | 123.7473 | -123.9761 | -124.0082
1837.7188 | 123.9075 | -61.2579 | 62.4847 | 0.13603 | 0.01816 | 0.017472 | 0.01296 | 0.068152 | 0.0026575 | 0.088235 | -58.3878 | 62.4847 | -61.5097 | -61.7706 | 52.0706 | 12.1216 | 0.92926 | 0.82855 | 62.4939 | -61.5601 | -0.25177 | 0 | 2.8702 | -0.51269 | -10.4141 | -0.30212 | 0.009155 | 3.1219 | 62.1872 | 62.0865 | 113.3286 | 123.7427 | 2.8702 | 123.7518 | 73.3795 | -0.30212 | 123.7427 | 2.8702 | 73.3795 | 113.3286 | 123.7518 | -123.9944 | -124.0448
1838.7188 | 123.9441 | -61.2534 | 62.4939 | -0.19203 | 0.017519 | 0.018968 | 0.014029 | 0.068793 | 0.0013757 | 0.086312 | -58.3145 | 62.5076 | -61.4868 | -61.4182 | 52.2949 | 11.9339 | 0.91553 | 0.85602 | 62.5168 | -61.5189 | -0.23346 | 0.013733 | 2.9388 | -0.16479 | -10.199 | -0.2655 | 0.022889 | 3.1723 | 62.1689 | 62.1094 | 113.5483 | 123.761 | 2.9388 | 123.7701 | 73.1873 | -0.2655 | 123.761 | 2.9388 | 73.1873 | 113.5483 | 123.7701 | -123.9807 | -124.0128
1839.7188 | 123.967 | -61.2259 | 62.5168 | -0.19203 | 0.017306 | 0.021317 | 0.013601 | 0.067298 | 0.0054347 | 0.082894 | -58.2916 | 62.4847 | -61.5189 | -61.4182 | 52.4506 | 12.2726 | 0.6546 | 0.72784 | 62.5076 | -61.5234 | -0.29297 | -0.032044 | 2.9343 | -0.19226 | -10.0662 | -0.29755 | -0.009156 | 3.2272 | 61.8805 | 61.9537 | 113.6765 | 123.7106 | 2.9343 | 123.7335 | 73.4985 | -0.29755 | 123.7106 | 2.9343 | 73.4985 | 113.6765 | 123.7335 | -124.0356 | -124.0402
1840.7188 | 123.9258 | -61.2579 | 62.5031 | -0.13863 | 0.018801 | 0.017899 | 0.012533 | 0.067939 | 0.0011621 | 0.083535 | -58.3191 | 62.4985 | -61.4868 | -61.409 | 52.5284 | 12.1948 | 0.54474 | 0.68207 | 62.4939 | -61.528 | -0.22888 | -0.004578 | 2.9388 | -0.15106 | -9.9747 | -0.27008 | -0.009156 | 3.1677 | 61.8027 | 61.94 | 113.7863 | 123.7564 | 2.9388 | 123.7518 | 73.4528 | -0.27008 | 123.7564 | 2.9388 | 73.4528 | 113.7863 | 123.7518 | -123.9899 | -124.0311
1841.7188 | 123.9532 | -61.2625 | 62.5168 | -0.16151 | 0.018374 | 0.014909 | 0.012747 | 0.066657 | 0.0039393 | 0.085671 | -58.3557 | 62.5031 | -61.4868 | -61.4182 | 52.2995 | 12.1719 | 0.64087 | 0.61798 | 62.5076 | -61.5097 | -0.2243 | -0.013733 | 2.9068 | -0.15564 | -10.2173 | -0.24719 | -0.009156 | 3.1311 | 61.9034 | 61.8805 | 113.562 | 123.7656 | 2.9068 | 123.7701 | 73.4344 | -0.24719 | 123.7656 | 2.9068 | 73.4344 | 113.562 | 123.7701 | -124.0036 | -124.0265
1842.7188 | 123.8434 | -61.2671 | 62.4939 | 0.059738 | 0.018801 | 0.019822 | 0.014242 | 0.067939 | 0.0030847 | 0.085885 | -58.3008 | 62.4939 | -61.5143 | -61.528 | 51.9196 | 11.6959 | 0.67291 | 0.56305 | 62.4939 | -61.5234 | -0.24719 | 0 | 2.9663 | -0.26093 | -10.5743 | -0.25635 | 0 | 3.2135 | 61.94 | 61.8301 | 113.1866 | 123.761 | 2.9663 | 123.761 | 72.963 | -0.25635 | 123.761 | 2.9663 | 72.963 | 113.1866 | 123.761 | -124.0082 | -124.0173
1843.7188 | 123.9395 | -61.2762 | 62.5351 | -0.13863 | 0.01816 | 0.015122 | 0.011892 | 0.066443 | 0.0030847 | 0.083535 | -58.4015 | 62.5031 | -61.4639 | -61.4182 | 52.3132 | 11.7966 | 0.737 | 0.74616 | 62.4893 | -61.5097 | -0.18768 | -0.032043 | 2.8748 | -0.14191 | -10.2219 | -0.23346 | -0.045776 | 3.0624 | 62.0132 | 62.0224 | 113.5895 | 123.7793 | 2.8748 | 123.7656 | 73.0728 | -0.23346 | 123.7793 | 2.8748 | 73.0728 | 113.5895 | 123.7656 | -123.999 | -124.0448
1844.7188 | 123.9304 | -61.2488 | 62.5214 | -0.2607 | 0.017519 | 0.021745 | 0.0084744 | 0.064734 | 0.0043665 | 0.083322 | -58.4244 | 62.4985 | -61.4914 | -61.4502 | 52.4689 | 12.0438 | 0.94299 | 0.86517 | 62.5259 | -61.5326 | -0.24262 | -0.022888 | 2.8244 | -0.20142 | -10.0525 | -0.28381 | 0.004578 | 3.067 | 62.1918 | 62.114 | 113.7177 | 123.7473 | 2.8244 | 123.7747 | 73.2925 | -0.28381 | 123.7473 | 2.8244 | 73.2925 | 113.7177 | 123.7747 | -124.0128 | -124.054
1845.7188 | 123.9532 | -61.2579 | 62.5305 | -0.22255 | 0.017519 | 0.022172 | 0.013174 | 0.067298 | 0.0041529 | 0.084817 | -58.2596 | 62.5168 | -61.496 | -61.4136 | 52.327 | 12.085 | 0.70038 | 0.80109 | 62.4939 | -61.5189 | -0.23804 | -0.013733 | 2.9984 | -0.15564 | -10.2036 | -0.26092 | -0.036622 | 3.2364 | 61.9583 | 62.059 | 113.5849 | 123.7747 | 2.9984 | 123.7518 | 73.3429 | -0.26092 | 123.7747 | 2.9984 | 73.3429 | 113.5849 | 123.7518 | -124.0265 | -124.0494
1846.7188 | 123.9944 | -61.2717 | 62.5076 | -0.062332 | 0.019656 | 0.021317 | 0.013388 | 0.067084 | 0.0062891 | 0.087594 | -58.3374 | 62.4847 | -61.496 | -61.5143 | 52.4597 | 12.0621 | 0.65918 | 0.82855 | 62.5122 | -61.5234 | -0.22431 | -0.022888 | 2.9343 | -0.24262 | -10.0479 | -0.25177 | 0.004578 | 3.1586 | 61.9308 | 62.1002 | 113.7314 | 123.7564 | 2.9343 | 123.7839 | 73.3337 | -0.25177 | 123.7564 | 2.9343 | 73.3337 | 113.7314 | 123.7839 | -124.0036 | -124.0311
1847.7188 | 123.9029 | -61.2625 | 62.4985 | -0.024185 | 0.018801 | 0.017045 | 0.013388 | 0.065589 | 0.0041529 | 0.082253 | -58.3054 | 62.4939 | -61.5051 | -61.4456 | 52.24 | 11.8881 | 0.78278 | 0.7782 | 62.5031 | -61.5189 | -0.24262 | -0.004578 | 2.9572 | -0.18311 | -10.2585 | -0.25635 | 0.004578 | 3.1998 | 62.0453 | 62.0407 | 113.5025 | 123.7564 | 2.9572 | 123.7656 | 73.1506 | -0.25635 | 123.7564 | 2.9572 | 73.1506 | 113.5025 | 123.7656 | -124.0036 | -124.0173
1848.7188 | 123.9441 | -61.2534 | 62.5214 | -0.047073 | 0.017947 | 0.018113 | 0.012106 | 0.067511 | 0.0041529 | 0.085458 | -58.3832 | 62.4985 | -61.5143 | -61.4273 | 52.3178 | 11.879 | 0.68207 | 0.76904 | 62.5031 | -61.5417 | -0.26093 | -0.022888 | 2.8702 | -0.17395 | -10.2036 | -0.28839 | -0.01831 | 3.1311 | 61.9354 | 62.0224 | 113.5712 | 123.7518 | 2.8702 | 123.7564 | 73.1323 | -0.28839 | 123.7518 | 2.8702 | 73.1323 | 113.5712 | 123.7564 | -124.0356 | -124.0631
1849.7188 | 124.0402 | -61.2442 | 62.4756 | -0.131 | 0.017733 | 0.016404 | 0.013815 | 0.067084 | 0.0015893 | 0.084176 | -58.3786 | 62.5168 | -61.4914 | -61.4227 | 52.1667 | 11.8423 | 0.85144 | 0.95673 | 62.4985 | -61.5189 | -0.24719 | 0.041199 | 2.8656 | -0.17853 | -10.3088 | -0.27466 | 0.022888 | 3.1128 | 62.0956 | 62.2009 | 113.4109 | 123.761 | 2.8656 | 123.7427 | 73.0865 | -0.27466 | 123.761 | 2.8656 | 73.0865 | 113.4109 | 123.7427 | -123.967 | -123.9944
1850.7188 | 123.9441 | -61.2396 | 62.4985 | -0.16151 | 0.019015 | 0.018327 | 0.015097 | 0.066443 | 0.0039393 | 0.083322 | -58.3603 | 62.5031 | -61.5005 | -61.4044 | 52.2354 | 11.6776 | 0.84228 | 0.97046 | 62.5168 | -61.5189 | -0.26093 | 0.004578 | 2.8793 | -0.16479 | -10.2631 | -0.27924 | 0.018311 | 3.1403 | 62.0819 | 62.2101 | 113.475 | 123.7427 | 2.8793 | 123.7564 | 72.9172 | -0.27924 | 123.7427 | 2.8793 | 72.9172 | 113.475 | 123.7564 | -123.999 | -124.0173
1851.7188 | 123.9716 | -61.2488 | 62.5031 | -0.16914 | 0.018374 | 0.015763 | 0.011251 | 0.066016 | 0.0026575 | 0.084817 | -58.3511 | 62.5259 | -61.4868 | -61.4319 | 52.1942 | 11.7462 | 0.86975 | 1.03 | 62.5076 | -61.528 | -0.23804 | 0.022888 | 2.8976 | -0.18311 | -10.3088 | -0.27924 | 0.004577 | 3.1357 | 62.1185 | 62.2787 | 113.443 | 123.7747 | 2.8976 | 123.7564 | 72.995 | -0.27924 | 123.7747 | 2.8976 | 72.995 | 113.443 | 123.7564 | -123.9899 | -124.0311
1852.7188 | 123.8983 | -61.2488 | 62.5076 | 0.074997 | 0.017519 | 0.018968 | 0.014242 | 0.066016 | 0.0018031 | 0.085031 | -58.2825 | 62.5122 | -61.5326 | -61.4685 | 51.9791 | 11.5494 | 0.81024 | 0.92468 | 62.5122 | -61.5326 | -0.28381 | 0.004578 | 2.9663 | -0.21973 | -10.5286 | -0.28381 | 0.004578 | 3.2501 | 62.059 | 62.1735 | 113.2278 | 123.761 | 2.9663 | 123.761 | 72.7982 | -0.28381 | 123.761 | 2.9663 | 72.7982 | 113.2278 | 123.761 | -124.0402 | -124.0402
1853.7188 | 123.9349 | -61.2717 | 62.4985 | 0.013962 | 0.018801 | 0.020249 | 0.013174 | 0.06922 | 0.0020167 | 0.08439 | -58.3054 | 62.5031 | -61.4685 | -61.409 | 52.0706 | 11.5723 | 0.85144 | 1.0849 | 62.5031 | -61.5005 | -0.19684 | 0.004578 | 2.9663 | -0.13733 | -10.4279 | -0.22888 | 0.004578 | 3.1631 | 62.1231 | 62.3566 | 113.3423 | 123.7747 | 2.9663 | 123.7747 | 72.8439 | -0.22888 | 123.7747 | 2.9663 | 72.8439 | 113.3423 | 123.7747 | -123.967 | -123.999
1854.7188 | 123.9304 | -61.2579 | 62.5076 | -1.4204 | 0.017519 | 0.020463 | 0.012747 | 0.067298 | 0.0035121 | 0.08439 | -58.342 | 62.471 | -61.496 | -61.4227 | 52.1667 | 11.8515 | 0.91553 | 1.1444 | 62.5076 | -61.5097 | -0.23804 | -0.036621 | 2.916 | -0.16479 | -10.3409 | -0.25177 | 0 | 3.154 | 62.1735 | 62.4023 | 113.4247 | 123.7289 | 2.916 | 123.7656 | 73.1094 | -0.25177 | 123.7289 | 2.916 | 73.1094 | 113.4247 | 123.7656 | -124.0036 | -124.0173
1855.7188 | 123.9624 | -61.2625 | 62.5076 | -0.10811 | 0.019656 | 0.019608 | 0.014883 | 0.064948 | 0.00030767 | 0.083108 | -58.6624 | 62.4573 | -61.5417 | -61.4319 | 52.3087 | 12.1262 | 1.0071 | 1.2131 | 62.4939 | -61.5234 | -0.27924 | -0.050354 | 2.6001 | -0.16937 | -10.199 | -0.26093 | -0.013733 | 2.8793 | 62.2696 | 62.4756 | 113.5712 | 123.7198 | 2.6001 | 123.7564 | 73.3887 | -0.26093 | 123.7198 | 2.6001 | 73.3887 | 113.5712 | 123.7564 | -124.0494 | -124.0311
1856.7188 | 123.9395 | -61.2534 | 62.4939 | -0.11574 | 0.017306 | 0.020677 | 0.0097562 | 0.068366 | 0.0035121 | 0.084176 | -58.3969 | 62.5351 | -61.5189 | -61.4136 | 52.0844 | 11.8149 | 0.72327 | 1.0666 | 62.5214 | -61.5051 | -0.2655 | 0.041199 | 2.8564 | -0.16022 | -10.4095 | -0.25177 | 0.027466 | 3.1219 | 61.9766 | 62.3199 | 113.3377 | 123.7885 | 2.8564 | 123.7747 | 73.0682 | -0.25177 | 123.7885 | 2.8564 | 73.0682 | 113.3377 | 123.7747 | -124.0128 | -123.999
1857.7188 | 123.9441 | -61.2534 | 62.4481 | 0.2047 | 0.019015 | 0.018968 | 0.008688 | 0.068793 | 0.0026575 | 0.083322 | -58.374 | 62.4573 | -61.5234 | -61.5005 | 51.9974 | 11.8286 | 0.74158 | 1.0666 | 62.471 | -61.5097 | -0.27008 | 0.009155 | 2.8793 | -0.24719 | -10.4507 | -0.25635 | 0.022888 | 3.1494 | 61.9949 | 62.3199 | 113.2507 | 123.7106 | 2.8793 | 123.7244 | 73.082 | -0.25635 | 123.7106 | 2.8793 | 73.082 | 113.2507 | 123.7244 | -123.9716 | -123.9578
1858.7188 | 123.9624 | -61.2488 | 62.4893 | -0.13863 | 0.020724 | 0.018113 | 0.010611 | 0.064948 | 0.0037257 | 0.087594 | -58.3145 | 62.5076 | -61.4914 | -61.5921 | 51.8646 | 11.8195 | 0.94299 | 1.1169 | 62.4893 | -61.5234 | -0.24262 | 0.01831 | 2.9343 | -0.34332 | -10.6247 | -0.27466 | 0 | 3.1769 | 62.1918 | 62.3657 | 113.1134 | 123.7564 | 2.9343 | 123.7381 | 73.0682 | -0.27466 | 123.7564 | 2.9343 | 73.0682 | 113.1134 | 123.7381 | -123.9807 | -124.0128
1859.7188 | 123.9304 | -61.2534 | 62.5122 | -0.062332 | 0.017092 | 0.020677 | 0.014669 | 0.06623 | 0.0028711 | 0.08204 | -58.1772 | 62.5122 | -61.4868 | -61.4136 | 51.9836 | 11.6776 | 0.75531 | 1.1581 | 62.4619 | -61.5463 | -0.23346 | 0 | 3.0762 | -0.16022 | -10.5286 | -0.29297 | -0.050354 | 3.3096 | 62.0087 | 62.4115 | 113.237 | 123.7656 | 3.0762 | 123.7152 | 72.9309 | -0.29297 | 123.7656 | 3.0762 | 72.9309 | 113.237 | 123.7152 | -123.999 | -124.0585
1860.7188 | 123.9029 | -61.2579 | 62.5122 | -0.062332 | 0.018801 | 0.017899 | 0.011038 | 0.066657 | 0.0026575 | 0.082253 | -58.429 | 62.4939 | -61.4868 | -61.4273 | 52.1896 | 11.5356 | 0.8606 | 1.0757 | 62.5031 | -61.5463 | -0.22888 | -0.018311 | 2.829 | -0.16937 | -10.3226 | -0.28839 | -0.009155 | 3.0579 | 62.1185 | 62.3337 | 113.4476 | 123.7518 | 2.829 | 123.761 | 72.7936 | -0.28839 | 123.7518 | 2.829 | 72.7936 | 113.4476 | 123.761 | -123.999 | -124.0585
1861.7344 | 123.9807 | -61.2396 | 62.4664 | 0.10551 | 0.016024 | 0.017045 | 0.0078336 | 0.066016 | 0.0045801 | 0.086099 | -58.3786 | 62.3886 | -61.5097 | -61.4227 | 52.1713 | 11.6455 | 0.62714 | 1.0071 | 62.4344 | -61.5051 | -0.27008 | -0.07782 | 2.861 | -0.1831 | -10.2951 | -0.2655 | -0.032044 | 3.1311 | 61.8668 | 62.2467 | 113.4109 | 123.6282 | 2.861 | 123.674 | 72.8851 | -0.2655 | 123.6282 | 2.861 | 72.8851 | 113.4109 | 123.674 | -123.9761 | -123.9716
1862.7188 | 123.8983 | -61.2442 | 62.5122 | 0.18944 | 0.019442 | 0.02324 | 0.013601 | 0.064948 | 0.0043665 | 0.083749 | -58.5114 | 62.4985 | -61.5143 | -61.4914 | 51.7548 | 11.4716 | 0.57678 | 0.76904 | 62.4756 | -61.5601 | -0.27008 | -0.013733 | 2.7328 | -0.24719 | -10.7574 | -0.31586 | -0.036621 | 3.0029 | 61.821 | 62.0132 | 112.999 | 123.7427 | 2.7328 | 123.7198 | 72.7158 | -0.31586 | 123.7427 | 2.7328 | 72.7158 | 112.999 | 123.7198 | -124.0265 | -124.0723
1863.7188 | 123.9304 | -61.2259 | 62.4893 | 0.03685 | 0.017519 | 0.017899 | 0.015097 | 0.064734 | 0.0011621 | 0.08204 | -58.4061 | 62.4847 | -61.4868 | -61.409 | 52.0569 | 11.6409 | 0.75531 | 0.86975 | 62.4847 | -61.5463 | -0.26093 | -0.004578 | 2.8198 | -0.18311 | -10.4324 | -0.32044 | -0.004578 | 3.0807 | 61.9812 | 62.0956 | 113.2828 | 123.7106 | 2.8198 | 123.7106 | 72.8668 | -0.32044 | 123.7106 | 2.8198 | 72.8668 | 113.2828 | 123.7106 | -123.9761 | -124.0356
1864.7188 | 123.9441 | -61.2488 | 62.4985 | 0.48698 | 0.019015 | 0.01854 | 0.01296 | 0.06623 | 0.0030847 | 0.081185 | -58.4061 | 62.4939 | -61.4868 | -61.409 | 52.2034 | 11.6409 | 0.86517 | 1.0254 | 62.5031 | -61.5143 | -0.23804 | -0.004578 | 2.8427 | -0.16022 | -10.2951 | -0.2655 | 0.004578 | 3.0807 | 62.114 | 62.2742 | 113.4521 | 123.7427 | 2.8427 | 123.7518 | 72.8897 | -0.2655 | 123.7427 | 2.8427 | 72.8897 | 113.4521 | 123.7518 | -123.9853 | -124.0128
1865.7188 | 123.9304 | -61.2488 | 62.4802 | 0.0063326 | 0.020724 | 0.017045 | 0.014456 | 0.068152 | 0.00094847 | 0.084603 | -58.4747 | 62.471 | -61.5189 | -61.4182 | 52.1164 | 11.6913 | 0.8606 | 0.94299 | 62.5122 | -61.5326 | -0.27008 | -0.009156 | 2.774 | -0.16937 | -10.3638 | -0.28381 | 0.032043 | 3.0441 | 62.1094 | 62.1918 | 113.3652 | 123.7198 | 2.774 | 123.761 | 72.9401 | -0.28381 | 123.7198 | 2.774 | 72.9401 | 113.3652 | 123.761 | -123.999 | -124.0128
1866.7188 | 124.0448 | -61.2305 | 62.4573 | 0.16655 | 0.014315 | 0.015336 | 0.0093288 | 0.065802 | 0.0045801 | 0.08439 | -58.4198 | 62.3932 | -61.5097 | -61.3953 | 52.2125 | 11.4807 | 0.75073 | 1.0529 | 62.4344 | -61.4914 | -0.27924 | -0.064087 | 2.8107 | -0.16479 | -10.2448 | -0.26093 | -0.022888 | 3.0899 | 61.9812 | 62.2833 | 113.443 | 123.6237 | 2.8107 | 123.6649 | 72.7112 | -0.26093 | 123.6237 | 2.8107 | 72.7112 | 113.443 | 123.6649 | -123.967 | -123.9487
1867.7188 | 124.0128 | -61.235 | 62.439 | 0.04448 | 0.017733 | 0.024522 | 0.011465 | 0.065802 | 0.0022303 | 0.083749 | -58.786 | 62.4069 | -61.496 | -61.3998 | 52.1576 | 11.5311 | 0.71411 | 1.0391 | 62.4481 | -61.5372 | -0.26093 | -0.032044 | 2.449 | -0.1648 | -10.2814 | -0.30212 | 0.009155 | 2.71 | 61.9492 | 62.2742 | 113.3926 | 123.642 | 2.449 | 123.6832 | 72.7661 | -0.30212 | 123.642 | 2.449 | 72.7661 | 113.3926 | 123.6832 | -123.9349 | -123.9761
1868.7188 | 123.9166 | -61.2671 | 62.4847 | -0.031814 | 0.018587 | 0.015977 | 0.01531 | 0.064734 | 0.0032983 | 0.083962 | -58.4564 | 62.4985 | -61.5005 | -61.441 | 52.1576 | 11.3937 | 1.03 | 1.0071 | 62.4847 | -61.5372 | -0.23346 | 0.013733 | 2.8107 | -0.17395 | -10.3271 | -0.27008 | 0 | 3.0441 | 62.2971 | 62.2742 | 113.4247 | 123.7656 | 2.8107 | 123.7518 | 72.6608 | -0.27008 | 123.7656 | 2.8107 | 72.6608 | 113.4247 | 123.7518 | -123.9853 | -124.0219
1869.7188 | 123.9258 | -61.2625 | 62.5076 | -0.054703 | 0.019656 | 0.017472 | 0.014242 | 0.065589 | 0.0011621 | 0.083535 | -58.429 | 62.5122 | -61.4685 | -61.4319 | 52.0981 | 11.2747 | 0.75531 | 0.78735 | 62.4985 | -61.5326 | -0.20599 | 0.004578 | 2.8336 | -0.16937 | -10.4095 | -0.27008 | -0.009155 | 3.0396 | 62.0178 | 62.0499 | 113.3606 | 123.7747 | 2.8336 | 123.761 | 72.5372 | -0.27008 | 123.7747 | 2.8336 | 72.5372 | 113.3606 | 123.761 | -123.9761 | -124.0402
1870.7188 | 123.9395 | -61.2625 | 62.4847 | -0.0089264 | 0.019228 | 0.019608 | 0.012533 | 0.068152 | 0.0015893 | 0.083749 | -58.5022 | 62.4939 | -61.4777 | -61.4227 | 52.1027 | 11.1053 | 0.80566 | 0.88806 | 62.5168 | -61.5463 | -0.21515 | 0.009155 | 2.7603 | -0.16022 | -10.3821 | -0.28381 | 0.032044 | 2.9755 | 62.0682 | 62.1506 | 113.3652 | 123.7564 | 2.7603 | 123.7793 | 72.3679 | -0.28381 | 123.7564 | 2.7603 | 72.3679 | 113.3652 | 123.7793 | -123.9624 | -124.0311
1871.7344 | 123.9716 | -61.2076 | 62.4435 | 0.082626 | 0.013247 | 0.016404 | 0.003561 | 0.064521 | 0.0032983 | 0.082894 | -58.4747 | 62.3978 | -61.4777 | -61.4319 | 52.0386 | 11.4075 | 0.65002 | 0.94299 | 62.4756 | -61.4868 | -0.27008 | -0.045776 | 2.7328 | -0.2243 | -10.405 | -0.27923 | 0.032044 | 3.0029 | 61.8576 | 62.1506 | 113.2462 | 123.6053 | 2.7328 | 123.6832 | 72.6151 | -0.27923 | 123.6053 | 2.7328 | 72.6151 | 113.2462 | 123.6832 | -123.9212 | -123.9304
1872.7188 | 124.0311 | -61.2305 | 62.4527 | 0.23521 | 0.017306 | 0.014482 | 0.01232 | 0.064948 | 0.0043665 | 0.085671 | -58.3878 | 62.4207 | -61.5005 | -61.4273 | 51.915 | 11.1786 | 0.6546 | 0.95673 | 62.439 | -61.5509 | -0.27008 | -0.032044 | 2.8427 | -0.19684 | -10.5377 | -0.32043 | -0.013733 | 3.1128 | 61.8851 | 62.1872 | 113.1454 | 123.6511 | 2.8427 | 123.6694 | 72.4091 | -0.32043 | 123.6511 | 2.8427 | 72.4091 | 113.1454 | 123.6694 | -123.9532 | -124.0036
1873.7188 | 123.9441 | -61.2396 | 62.4985 | 0.10551 | 0.019869 | 0.019822 | 0.016806 | 0.064734 | 0.0030847 | 0.082894 | -58.4427 | 62.5031 | -61.4868 | -61.409 | 51.9974 | 11.1465 | 0.92468 | 1.0208 | 62.4573 | -61.5646 | -0.24719 | 0.004578 | 2.7969 | -0.16937 | -10.5011 | -0.32501 | -0.041199 | 3.0441 | 62.1643 | 62.2604 | 113.237 | 123.7427 | 2.7969 | 123.6969 | 72.3862 | -0.32501 | 123.7427 | 2.7969 | 72.3862 | 113.237 | 123.6969 | -123.9853 | -124.0631
1874.7188 | 123.8846 | -61.2625 | 62.4847 | 0.03685 | 0.017947 | 0.01854 | 0.013174 | 0.067084 | 0.0024439 | 0.083322 | -58.5022 | 62.5122 | -61.4777 | -61.441 | 52.1484 | 11.0916 | 0.79651 | 0.90179 | 62.4985 | -61.5326 | -0.21515 | 0.027466 | 2.7603 | -0.17853 | -10.3363 | -0.27008 | 0.013733 | 2.9755 | 62.059 | 62.1643 | 113.4109 | 123.7747 | 2.7603 | 123.761 | 72.3541 | -0.27008 | 123.7747 | 2.7603 | 72.3541 | 113.4109 | 123.761 | -123.9624 | -124.0173
1875.7188 | 123.9212 | -61.2717 | 62.4985 | 0.074997 | 0.019442 | 0.018327 | 0.012533 | 0.06687 | 0.0037257 | 0.082253 | -58.3786 | 62.4664 | -61.4868 | -61.4502 | 52.3087 | 11.2015 | 0.75531 | 0.95673 | 62.5076 | -61.5372 | -0.21515 | -0.032043 | 2.8931 | -0.17853 | -10.1898 | -0.2655 | 0.009155 | 3.1082 | 62.027 | 62.2284 | 113.5803 | 123.7381 | 2.8931 | 123.7793 | 72.4731 | -0.2655 | 123.7381 | 2.8931 | 72.4731 | 113.5803 | 123.7793 | -123.9853 | -124.0356
1876.7188 | 124.0219 | -61.2396 | 62.4756 | 0.34966 | 0.014956 | 0.01555 | 0.0061246 | 0.065589 | 0.0035121 | 0.084817 | -58.429 | 62.4619 | -61.4639 | -61.4319 | 52.3224 | 11.554 | 0.93842 | 1.1902 | 62.471 | -61.5097 | -0.2243 | -0.013733 | 2.8107 | -0.19226 | -10.1532 | -0.27008 | -0.004578 | 3.035 | 62.178 | 62.4298 | 113.562 | 123.7015 | 2.8107 | 123.7106 | 72.7936 | -0.27008 | 123.7015 | 2.8107 | 72.7936 | 113.562 | 123.7106 | -123.9395 | -123.9853
1877.7188 | 123.9029 | -61.235 | 62.4985 | -0.047073 | 0.019656 | 0.018968 | 0.014242 | 0.065589 | 0.0020167 | 0.082467 | -58.5251 | 62.4847 | -61.4868 | -61.409 | 52.0706 | 11.2061 | 0.89722 | 1.0483 | 62.4802 | -61.5555 | -0.25177 | -0.013733 | 2.71 | -0.17395 | -10.4279 | -0.32044 | -0.01831 | 2.9617 | 62.1323 | 62.2833 | 113.3057 | 123.7198 | 2.71 | 123.7152 | 72.4411 | -0.32044 | 123.7198 | 2.71 | 72.4411 | 113.3057 | 123.7152 | -123.9853 | -124.054
1878.7188 | 123.9441 | -61.2579 | 62.5031 | -0.024185 | 0.018587 | 0.017686 | 0.015738 | 0.06623 | 0.0022303 | 0.082681 | -58.4518 | 62.5076 | -61.5051 | -61.4136 | 52.3041 | 11.2381 | 1.0345 | 1.1078 | 62.4939 | -61.5326 | -0.24719 | 0.004577 | 2.8061 | -0.15564 | -10.199 | -0.27466 | -0.009156 | 3.0533 | 62.2925 | 62.3657 | 113.562 | 123.7656 | 2.8061 | 123.7518 | 72.496 | -0.27466 | 123.7656 | 2.8061 | 72.496 | 113.562 | 123.7518 | -124.0082 | -124.0356
1879.7188 | 123.9029 | -61.235 | 62.4756 | -0.13863 | 0.01581 | 0.018968 | 0.014029 | 0.066443 | 0.0022303 | 0.083535 | -58.4427 | 62.5076 | -61.4685 | -61.4365 | 52.3682 | 11.2106 | 1.0803 | 1.2314 | 62.471 | -61.5189 | -0.23346 | 0.032043 | 2.7924 | -0.20142 | -10.1074 | -0.28381 | -0.004578 | 3.0258 | 62.3154 | 62.4664 | 113.6032 | 123.7427 | 2.7924 | 123.7061 | 72.4457 | -0.28381 | 123.7427 | 2.7924 | 72.4457 | 113.6032 | 123.7061 | -123.9441 | -123.9944
1880.7188 | 123.9487 | -61.2305 | 62.4664 | 0.60905 | 0.019442 | 0.019608 | 0.012533 | 0.067298 | 0.0011621 | 0.082253 | -58.3374 | 62.4756 | -61.5097 | -61.4044 | 52.359 | 11.2381 | 1.1353 | 1.2497 | 62.5031 | -61.5326 | -0.27924 | 0.009155 | 2.8931 | -0.17395 | -10.1074 | -0.30212 | 0.036621 | 3.1723 | 62.3657 | 62.4802 | 113.5895 | 123.7061 | 2.8931 | 123.7335 | 72.4686 | -0.30212 | 123.7061 | 2.8931 | 72.4686 | 113.5895 | 123.7335 | -123.9761 | -123.999
1881.7188 | 123.9258 | -61.2717 | 62.5031 | -0.031814 | 0.015597 | 0.021958 | 0.014242 | 0.06687 | 0.0032983 | 0.08204 | -57.9163 | 62.5168 | -61.5051 | -61.4548 | 52.0752 | 11.1694 | 1.1536 | 1.2909 | 62.4985 | -61.528 | -0.23346 | 0.013733 | 3.3554 | -0.18311 | -10.4279 | -0.25635 | -0.004578 | 3.5889 | 62.4252 | 62.5626 | 113.3469 | 123.7885 | 3.3554 | 123.7701 | 72.4411 | -0.25635 | 123.7885 | 3.3554 | 72.4411 | 113.3469 | 123.7701 | -124.0082 | -124.0311
1882.7188 | 124.0128 | -61.2259 | 62.4344 | 0.2581 | 0.016451 | 0.019181 | 0.0097562 | 0.067511 | 0.0030847 | 0.083108 | -58.4793 | 62.4298 | -61.5097 | -61.3953 | 52.4826 | 11.467 | 1.062 | 1.2543 | 62.4207 | -61.5143 | -0.28381 | -0.004577 | 2.7466 | -0.16937 | -9.9518 | -0.28839 | -0.013733 | 3.0304 | 62.2879 | 62.4802 | 113.7085 | 123.6557 | 2.7466 | 123.6465 | 72.6929 | -0.28839 | 123.6557 | 2.7466 | 72.6929 | 113.7085 | 123.6465 | -123.9441 | -123.9487
1883.7188 | 123.912 | -61.2396 | 62.4939 | -0.077591 | 0.01816 | 0.018113 | 0.013388 | 0.065589 | 0.00073487 | 0.085244 | -58.287 | 62.5122 | -61.4914 | -61.4227 | 52.2995 | 11.1465 | 1.2177 | 1.2405 | 62.4756 | -61.5509 | -0.25177 | 0.018311 | 2.9526 | -0.1831 | -10.1944 | -0.31128 | -0.01831 | 3.2043 | 62.4573 | 62.4802 | 113.5391 | 123.7518 | 2.9526 | 123.7152 | 72.3862 | -0.31128 | 123.7518 | 2.9526 | 72.3862 | 113.5391 | 123.7152 | -123.9853 | -124.0448
1884.7188 | 123.9532 | -61.2625 | 62.4985 | -0.46669 | 0.019656 | 0.021531 | 0.015097 | 0.065375 | 0.00073487 | 0.084603 | -58.4198 | 62.4985 | -61.5143 | -61.409 | 52.6291 | 11.4807 | 1.0666 | 1.1581 | 62.471 | -61.5417 | -0.25177 | 0 | 2.8427 | -0.14648 | -9.8694 | -0.27924 | -0.027466 | 3.0945 | 62.3291 | 62.4207 | 113.8916 | 123.761 | 2.8427 | 123.7335 | 72.7432 | -0.27924 | 123.761 | 2.8427 | 72.7432 | 113.8916 | 123.7335 | -124.0128 | -124.0402
1885.7188 | 123.9349 | -61.2259 | 62.4939 | -0.19203 | 0.01816 | 0.017472 | 0.011679 | 0.065589 | 0.0013757 | 0.083962 | -58.3878 | 62.4939 | -61.4868 | -61.4365 | 52.5192 | 11.4487 | 1.1444 | 1.2955 | 62.5031 | -61.5143 | -0.26093 | 0 | 2.8381 | -0.21057 | -9.9747 | -0.28839 | 0.009156 | 3.0991 | 62.3703 | 62.5214 | 113.7451 | 123.7198 | 2.8381 | 123.7289 | 72.6746 | -0.28839 | 123.7198 | 2.8381 | 72.6746 | 113.7451 | 123.7289 | -123.9807 | -124.0082
1886.7188 | 123.9487 | -61.2625 | 62.4939 | -0.069961 | 0.016451 | 0.018327 | 0.011679 | 0.06623 | 0.00094847 | 0.085031 | -58.4198 | 62.5031 | -61.5097 | -61.4044 | 52.4323 | 11.4761 | 1.0941 | 1.2772 | 62.4893 | -61.5326 | -0.24719 | 0.009156 | 2.8427 | -0.14191 | -10.0616 | -0.27008 | -0.004577 | 3.0899 | 62.3566 | 62.5397 | 113.6948 | 123.7656 | 2.8427 | 123.7518 | 72.7386 | -0.27008 | 123.7656 | 2.8427 | 72.7386 | 113.6948 | 123.7518 | -124.0036 | -124.0265
1887.7188 | 123.9029 | -61.2671 | 62.5031 | 0.10551 | 0.01816 | 0.018968 | 0.011679 | 0.064734 | 0.0035121 | 0.085244 | -58.4747 | 62.4985 | -61.5097 | -61.5143 | 52.2263 | 11.3617 | 1.1032 | 1.0941 | 62.4893 | -61.5692 | -0.24261 | -0.004578 | 2.7924 | -0.24719 | -10.2768 | -0.30212 | -0.013733 | 3.035 | 62.3703 | 62.3611 | 113.4933 | 123.7656 | 2.7924 | 123.7564 | 72.6288 | -0.30212 | 123.7656 | 2.7924 | 72.6288 | 113.4933 | 123.7564 | -124.0128 | -124.0723
1888.7188 | 123.9258 | -61.2625 | 62.4893 | -0.09285 | 0.019228 | 0.018113 | 0.013174 | 0.069861 | 9.4068e-05 | 0.08439 | -58.5571 | 62.5214 | -61.4822 | -61.2946 | 52.1164 | 11.38 | 1.03 | 1.1581 | 62.4893 | -61.5326 | -0.21973 | 0.032043 | 2.7054 | -0.032044 | -10.3729 | -0.27008 | 0 | 2.9251 | 62.2925 | 62.4207 | 113.3789 | 123.7839 | 2.7054 | 123.7518 | 72.6425 | -0.27008 | 123.7839 | 2.7054 | 72.6425 | 113.3789 | 123.7518 | -123.9716 | -124.0219
1889.7188 | 123.9578 | -61.235 | 62.4985 | -0.131 | 0.016665 | 0.018327 | 0.010397 | 0.06687 | 0.0035121 | 0.083749 | -58.3328 | 62.4847 | -61.5051 | -61.409 | 52.2949 | 11.3663 | 0.95673 | 1.0895 | 62.5122 | -61.5234 | -0.27008 | -0.013733 | 2.9022 | -0.17395 | -10.2036 | -0.28839 | 0.013733 | 3.1723 | 62.1918 | 62.3245 | 113.53 | 123.7198 | 2.9022 | 123.7473 | 72.6013 | -0.28839 | 123.7198 | 2.9022 | 72.6013 | 113.53 | 123.7473 | -124.0036 | -124.0219
1890.7188 | 123.9075 | -61.2442 | 62.5076 | -0.11574 | 0.01581 | 0.018754 | 0.012533 | 0.065589 | 0.0032983 | 0.083749 | -58.3786 | 62.4939 | -61.4777 | -61.3998 | 52.3544 | 11.7188 | 1.0071 | 1.0895 | 62.4847 | -61.5234 | -0.23346 | -0.013733 | 2.8656 | -0.15564 | -10.1532 | -0.27923 | -0.022888 | 3.0991 | 62.2513 | 62.3337 | 113.5986 | 123.7381 | 2.8656 | 123.7289 | 72.963 | -0.27923 | 123.7381 | 2.8656 | 72.963 | 113.5986 | 123.7289 | -123.9853 | -124.0311
1891.7188 | 123.9761 | -61.235 | 62.5168 | -0.24544 | 0.019228 | 0.018113 | 0.011679 | 0.067298 | 0.00073487 | 0.084176 | -58.3237 | 62.5305 | -61.5097 | -61.4182 | 52.1439 | 11.6409 | 0.87433 | 1.0895 | 62.5122 | -61.5234 | -0.27466 | 0.013733 | 2.9114 | -0.18311 | -10.3729 | -0.28839 | -0.004578 | 3.186 | 62.1094 | 62.3245 | 113.3789 | 123.7656 | 2.9114 | 123.7473 | 72.876 | -0.28839 | 123.7656 | 2.9114 | 72.876 | 113.3789 | 123.7473 | -124.0265 | -124.0402
1892.7188 | 123.9166 | -61.2671 | 62.4756 | 0.03685 | 0.018801 | 0.020463 | 0.01296 | 0.064948 | 0.0032983 | 0.086312 | -58.4061 | 62.5076 | -61.496 | -61.4868 | 52.3178 | 11.7279 | 1.0574 | 1.0117 | 62.4573 | -61.5829 | -0.22888 | 0.032043 | 2.861 | -0.21973 | -10.1578 | -0.31586 | -0.018311 | 3.0899 | 62.3245 | 62.2787 | 113.5849 | 123.7747 | 2.861 | 123.7244 | 72.995 | -0.31586 | 123.7747 | 2.861 | 72.995 | 113.5849 | 123.7244 | -123.9716 | -124.0585
1893.7188 | 123.8937 | -61.2671 | 62.4985 | -0.22255 | 0.018374 | 0.01555 | 0.0093288 | 0.065802 | 0.0037257 | 0.084603 | -58.4152 | 62.5031 | -61.4822 | -61.4548 | 52.3087 | 11.7462 | 1.1124 | 1.0803 | 62.4893 | -61.528 | -0.21515 | 0.004578 | 2.8519 | -0.18768 | -10.1898 | -0.26093 | -0.009155 | 3.067 | 62.3795 | 62.3474 | 113.5757 | 123.7701 | 2.8519 | 123.7564 | 73.0133 | -0.26093 | 123.7701 | 2.8519 | 73.0133 | 113.5757 | 123.7564 | -123.9807 | -124.0265
1894.7188 | 123.9304 | -61.2534 | 62.4756 | -0.15388 | 0.016238 | 0.017045 | 0.010824 | 0.067298 | 0.00094847 | 0.085031 | -58.5342 | 62.5031 | -61.496 | -61.4044 | 52.2949 | 11.7188 | 1.0071 | 0.9613 | 62.5259 | -61.5143 | -0.24262 | 0.027466 | 2.7191 | -0.15106 | -10.1807 | -0.26093 | 0.050354 | 2.9617 | 62.2604 | 62.2147 | 113.5483 | 123.7564 | 2.7191 | 123.7793 | 72.9721 | -0.26093 | 123.7564 | 2.7191 | 72.9721 | 113.5483 | 123.7793 | -123.9716 | -123.9899
1895.7188 | 123.9441 | -61.2396 | 62.4939 | -0.23781 | 0.018374 | 0.018327 | 0.0099698 | 0.064093 | 0.0024439 | 0.084603 | -58.4244 | 62.5122 | -61.5005 | -61.4456 | 52.5238 | 12.0758 | 0.97046 | 0.93842 | 62.5122 | -61.5097 | -0.26093 | 0.018311 | 2.8152 | -0.20599 | -9.9701 | -0.27008 | 0.018311 | 3.0762 | 62.2101 | 62.178 | 113.7634 | 123.7518 | 2.8152 | 123.7518 | 73.3154 | -0.27008 | 123.7518 | 2.8152 | 73.3154 | 113.7634 | 123.7518 | -123.9944 | -124.0036
1896.7188 | 123.9075 | -61.2488 | 62.5122 | -0.2607 | 0.019015 | 0.01555 | 0.011251 | 0.065589 | 0.0015893 | 0.083108 | -58.4702 | 62.4985 | -61.4822 | -61.4594 | 52.4506 | 11.7142 | 0.90637 | 0.95215 | 62.5122 | -61.5189 | -0.23346 | -0.013733 | 2.7786 | -0.21057 | -10.0616 | -0.27008 | 0 | 3.0121 | 62.1552 | 62.2009 | 113.6993 | 123.7473 | 2.7786 | 123.761 | 72.963 | -0.27008 | 123.7473 | 2.7786 | 72.963 | 113.6993 | 123.761 | -123.9944 | -124.0311
1897.9844 | 123.9807 | -61.2305 | 62.4664 | 0.12077 | 0.01581 | 0.017686 | 0.004202 | 0.063666 | 0.0013757 | 0.085458 | -58.2916 | 62.3795 | -61.5189 | -61.4548 | 52.5284 | 11.9888 | 0.97046 | 1.0712 | 62.4527 | -61.5005 | -0.28839 | -0.086975 | 2.9388 | -0.2243 | -9.938 | -0.27008 | -0.013733 | 3.2272 | 62.2009 | 62.3016 | 113.7588 | 123.6099 | 2.9388 | 123.6832 | 73.2193 | -0.27008 | 123.6099 | 2.9388 | 73.2193 | 113.7588 | 123.6832 | -123.9853 | -123.967
1899.0781 | 124.1043 | -61.2625 | 62.4527 | 0.1284 | 0.016238 | 0.017259 | 0.011679 | 0.065589 | 0.0037257 | 0.082894 | -58.3649 | 62.3886 | -61.4914 | -61.3998 | 52.5879 | 12.0392 | 0.737 | 0.81482 | 62.4161 | -61.5234 | -0.22888 | -0.064087 | 2.8976 | -0.13733 | -9.8648 | -0.26093 | -0.036621 | 3.1265 | 61.9995 | 62.0773 | 113.8504 | 123.6511 | 2.8976 | 123.6786 | 73.3017 | -0.26093 | 123.6511 | 2.8976 | 73.3017 | 113.8504 | 123.6786 | -123.9441 | -123.9761
1900.0938 | 123.8892 | -61.2762 | 62.4619 | 0.2047 | 0.016665 | 0.014695 | 0.014883 | 0.064307 | 0.0039393 | 0.085244 | -58.4244 | 62.4435 | -61.5463 | -61.4777 | 52.1667 | 11.6913 | 0.85144 | 0.8606 | 62.4573 | -61.5189 | -0.27008 | -0.018311 | 2.8519 | -0.20142 | -10.2951 | -0.24261 | -0.004578 | 3.1219 | 62.1277 | 62.1368 | 113.443 | 123.7198 | 2.8519 | 123.7335 | 72.9675 | -0.24261 | 123.7198 | 2.8519 | 72.9675 | 113.443 | 123.7335 | -124.0082 | -123.9807
1901.375 | 123.9944 | -61.2167 | 62.439 | 0.21996 | 0.017306 | 0.017259 | 0.013815 | 0.06388 | 0.0030847 | 0.08439 | -58.6395 | 62.3199 | -61.5005 | -61.409 | 52.3682 | 11.7188 | 0.53101 | 0.84686 | 62.4252 | -61.4639 | -0.28381 | -0.11902 | 2.5772 | -0.19226 | -10.0708 | -0.24719 | -0.013733 | 2.861 | 61.7477 | 62.0636 | 113.5849 | 123.5367 | 2.5772 | 123.642 | 72.9355 | -0.24719 | 123.5367 | 2.5772 | 72.9355 | 113.5849 | 123.642 | -123.9395 | -123.9029
1901.9219 | 124.0082 | -61.2076 | 62.471 | -0.25307 | 0.013674 | 0.010636 | 0.0080472 | 0.063452 | -0.00033333 | 0.085031 | -57.9346 | 62.4481 | -61.4502 | -61.2991 | 52.2583 | 11.7142 | 0.72327 | 1.0666 | 62.4344 | -61.4639 | -0.24261 | -0.022888 | 3.273 | -0.091552 | -10.2127 | -0.25635 | -0.036621 | 3.5156 | 61.9308 | 62.2742 | 113.4659 | 123.6557 | 3.273 | 123.642 | 72.9218 | -0.25635 | 123.6557 | 3.273 | 72.9218 | 113.4659 | 123.642 | -123.9212 | -123.9349
1904.1562 | 123.9441 | -61.2534 | 62.4847 | -0.054703 | 0.01816 | 0.017472 | 0.016592 | 0.064307 | 0.0047937 | 0.081826 | -58.3054 | 62.4252 | -61.4868 | -61.4365 | 52.4368 | 11.8881 | 0.84686 | 0.83771 | 62.4573 | -61.5189 | -0.23346 | -0.059509 | 2.948 | -0.1831 | -10.0479 | -0.2655 | -0.027466 | 3.1815 | 62.1002 | 62.0911 | 113.6902 | 123.6786 | 2.948 | 123.7106 | 73.1415 | -0.2655 | 123.6786 | 2.948 | 73.1415 | 113.6902 | 123.7106 | -123.9716 | -124.0036
1905.0156 | 123.848 | -61.2534 | 62.4847 | 0.14366 | 0.016878 | 0.019395 | 0.014669 | 0.063239 | 0.0047937 | 0.084176 | -58.5068 | 62.4207 | -61.5509 | -61.5417 | 52.5787 | 11.9476 | 0.91553 | 0.98419 | 62.5031 | -61.5005 | -0.29755 | -0.064087 | 2.7466 | -0.28839 | -9.906 | -0.24719 | 0.018311 | 3.0441 | 62.1689 | 62.2375 | 113.8321 | 123.674 | 2.7466 | 123.7564 | 73.201 | -0.24719 | 123.674 | 2.7466 | 73.201 | 113.8321 | 123.7564 | -124.0356 | -123.9853
1905.7188 | 123.9075 | -61.235 | 62.4985 | -0.19966 | 0.015597 | 0.017259 | 0.011892 | 0.062384 | 0.0015893 | 0.084817 | -58.5159 | 62.4527 | -61.496 | -61.441 | 52.2263 | 11.7142 | 0.92926 | 0.97961 | 62.4893 | -61.5326 | -0.26093 | -0.045776 | 2.7191 | -0.20599 | -10.2722 | -0.29755 | -0.009155 | 2.98 | 62.1643 | 62.2147 | 113.4613 | 123.6877 | 2.7191 | 123.7244 | 72.9492 | -0.29755 | 123.6877 | 2.7191 | 72.9492 | 113.4613 | 123.7244 | -123.9944 | -124.0311
1908.7969 | 123.9212 | -61.2396 | 62.4939 | -0.29884 | 0.01581 | 0.012559 | 0.011465 | 0.063666 | 0.0022303 | 0.083322 | -58.4244 | 62.4481 | -61.4868 | -61.4502 | 52.3315 | 11.7508 | 0.98419 | 0.92468 | 62.5122 | -61.5189 | -0.24719 | -0.045776 | 2.8152 | -0.21057 | -10.1624 | -0.27924 | 0.018311 | 3.0624 | 62.2238 | 62.1643 | 113.5712 | 123.6877 | 2.8152 | 123.7518 | 72.9904 | -0.27924 | 123.6877 | 2.8152 | 72.9904 | 113.5712 | 123.7518 | -123.9807 | -124.0128
1910.8281 | 123.9624 | -61.2259 | 62.4527 | 0.090256 | 0.014529 | 0.015336 | 0.0065518 | 0.061316 | 0.0032983 | 0.083535 | -58.429 | 62.3749 | -61.5097 | -61.3998 | 52.2308 | 11.9019 | 0.98877 | 0.98419 | 62.439 | -61.4822 | -0.28381 | -0.07782 | 2.7969 | -0.17395 | -10.2219 | -0.25635 | -0.013733 | 3.0807 | 62.2147 | 62.2101 | 113.4567 | 123.6008 | 2.7969 | 123.6649 | 73.1277 | -0.25635 | 123.6008 | 2.7969 | 73.1277 | 113.4567 | 123.6649 | -123.9624 | -123.9349
1911.7188 | 123.88 | -61.2396 | 62.5214 | -0.23781 | 0.017519 | 0.015336 | 0.0089016 | 0.061957 | 0.0022303 | 0.08204 | -58.4427 | 62.4664 | -61.4868 | -61.5005 | 52.2034 | 11.7188 | 1.0483 | 0.88806 | 62.4756 | -61.5143 | -0.24719 | -0.054931 | 2.7969 | -0.26093 | -10.318 | -0.27466 | -0.045776 | 3.0441 | 62.2879 | 62.1277 | 113.443 | 123.7061 | 2.7969 | 123.7152 | 72.9584 | -0.27466 | 123.7061 | 2.7969 | 72.9584 | 113.443 | 123.7152 | -124.0082 | -124.0356
1912.7188 | 123.9166 | -61.2534 | 62.5351 | -0.26833 | 0.015383 | 0.0132 | 0.011251 | 0.064093 | 0.0026575 | 0.082681 | -58.3923 | 62.4435 | -61.4822 | -61.4136 | 52.2812 | 11.7004 | 1.0986 | 0.92926 | 62.4985 | -61.5143 | -0.22888 | -0.091553 | 2.861 | -0.16022 | -10.2539 | -0.26093 | -0.036621 | 3.0899 | 62.352 | 62.1826 | 113.5345 | 123.6969 | 2.861 | 123.7518 | 72.9538 | -0.26093 | 123.6969 | 2.861 | 72.9538 | 113.5345 | 123.7518 | -124.0173 | -124.0494
1913.7188 | 123.7976 | -61.2396 | 62.558 | -0.2607 | 0.017306 | 0.01555 | 0.012747 | 0.061957 | 0.0028711 | 0.082681 | -58.4839 | 62.4664 | -61.4777 | -61.4548 | 52.1118 | 11.7737 | 1.2085 | 1.1948 | 62.4939 | -61.4914 | -0.23804 | -0.091552 | 2.7557 | -0.21515 | -10.4462 | -0.25177 | -0.064087 | 2.9938 | 62.4481 | 62.4344 | 113.3514 | 123.7061 | 2.7557 | 123.7335 | 73.0133 | -0.25177 | 123.7061 | 2.7557 | 73.0133 | 113.3514 | 123.7335 | -124.0356 | -124.0494
1914.7344 | 123.9212 | -61.2717 | 62.4847 | 0.19707 | 0.018587 | 0.021745 | 0.014029 | 0.066443 | -0.00011953 | 0.082681 | -58.5571 | 62.4252 | -61.5417 | -61.4365 | 52.0386 | 11.6684 | 1.1581 | 0.85602 | 62.471 | -61.5417 | -0.27008 | -0.059509 | 2.7145 | -0.16479 | -10.4462 | -0.27008 | -0.013733 | 2.9846 | 62.4298 | 62.1277 | 113.3102 | 123.6969 | 2.7145 | 123.7427 | 72.9401 | -0.27008 | 123.6969 | 2.7145 | 72.9401 | 113.3102 | 123.7427 | -124.0265 | -124.0265
1915.7188 | 123.8983 | -61.2579 | 62.5031 | -0.23018 | 0.017519 | 0.017686 | 0.010611 | 0.064521 | 0.0041529 | 0.083962 | -58.5983 | 62.4573 | -61.4914 | -61.4548 | 52.1027 | 11.7462 | 1.2085 | 0.97046 | 62.5076 | -61.5189 | -0.23346 | -0.045777 | 2.6596 | -0.19684 | -10.4004 | -0.26092 | 0.004577 | 2.8931 | 62.4664 | 62.2284 | 113.3606 | 123.7152 | 2.6596 | 123.7656 | 73.0042 | -0.26092 | 123.7152 | 2.6596 | 73.0042 | 113.3606 | 123.7656 | -123.9944 | -124.0219
1916.7188 | 123.9029 | -61.2259 | 62.5397 | -0.30647 | 0.017306 | 0.014268 | 0.0097562 | 0.062598 | 0.00030767 | 0.080758 | -58.5846 | 62.4664 | -61.496 | -61.4502 | 52.121 | 11.6226 | 1.0803 | 0.82855 | 62.4847 | -61.5051 | -0.27008 | -0.073242 | 2.6413 | -0.2243 | -10.4187 | -0.27924 | -0.054932 | 2.9114 | 62.3062 | 62.0544 | 113.3469 | 123.6923 | 2.6413 | 123.7106 | 72.8485 | -0.27924 | 123.6923 | 2.6413 | 72.8485 | 113.3469 | 123.7106 | -124.0356 | -124.0448
1917.7188 | 123.88 | -61.2534 | 62.5259 | -0.25307 | 0.017733 | 0.017686 | 0.011892 | 0.062171 | 0.0028711 | 0.080331 | -58.493 | 62.4481 | -61.4731 | -61.4182 | 52.1896 | 11.7737 | 0.88348 | 0.77362 | 62.4939 | -61.5005 | -0.21973 | -0.07782 | 2.7603 | -0.16479 | -10.3363 | -0.24719 | -0.032044 | 2.98 | 62.1368 | 62.027 | 113.443 | 123.7015 | 2.7603 | 123.7473 | 73.027 | -0.24719 | 123.7015 | 2.7603 | 73.027 | 113.443 | 123.7473 | -123.999 | -124.0265
1918.7188 | 123.8983 | -61.2442 | 62.5214 | -0.26833 | 0.015383 | 0.015763 | 0.010611 | 0.06153 | 0.0015893 | 0.084176 | -58.5754 | 62.4481 | -61.4777 | -61.4319 | 52.1027 | 11.9659 | 0.99792 | 0.78278 | 62.471 | -61.4914 | -0.23346 | -0.073242 | 2.6688 | -0.18768 | -10.4187 | -0.24719 | -0.050354 | 2.9022 | 62.2421 | 62.027 | 113.3469 | 123.6923 | 2.6688 | 123.7152 | 73.2101 | -0.24719 | 123.6923 | 2.6688 | 73.2101 | 113.3469 | 123.7152 | -123.999 | -124.0128
1919.7188 | 123.9395 | -61.2579 | 62.4847 | 0.2581 | 0.017733 | 0.019608 | 0.017019 | 0.064093 | 9.4068e-05 | 0.083962 | -58.5159 | 62.4802 | -61.4777 | -61.3953 | 52.1851 | 12.236 | 1.0071 | 0.90637 | 62.4481 | -61.5143 | -0.21973 | -0.004577 | 2.742 | -0.13733 | -10.2997 | -0.25635 | -0.036621 | 2.9617 | 62.265 | 62.1643 | 113.443 | 123.7381 | 2.742 | 123.7061 | 73.494 | -0.25635 | 123.7381 | 2.742 | 73.494 | 113.443 | 123.7061 | -123.9624 | -123.999
1920.7188 | 123.8937 | -61.2625 | 62.5031 | -0.20729 | 0.016451 | 0.016404 | 0.010183 | 0.063666 | 0.0020167 | 0.082894 | -58.3923 | 62.4893 | -61.4822 | -61.5967 | 51.8738 | 12.0438 | 0.97046 | 0.82398 | 62.471 | -61.5143 | -0.21973 | -0.013733 | 2.8702 | -0.33417 | -10.6293 | -0.25177 | -0.032044 | 3.0899 | 62.233 | 62.0865 | 113.1363 | 123.7518 | 2.8702 | 123.7335 | 73.3063 | -0.25177 | 123.7518 | 2.8702 | 73.3063 | 113.1363 | 123.7335 | -123.9853 | -124.0173
1921.7188 | 123.9029 | -61.235 | 62.5214 | -0.24544 | 0.014956 | 0.01555 | 0.011892 | 0.064307 | 0.00073487 | 0.081826 | -58.4747 | 62.4207 | -61.4777 | -61.3998 | 52.24 | 12.1399 | 0.94757 | 0.89722 | 62.4847 | -61.5005 | -0.24262 | -0.10071 | 2.7603 | -0.1648 | -10.2814 | -0.2655 | -0.036621 | 3.0029 | 62.1826 | 62.1323 | 113.475 | 123.6557 | 2.7603 | 123.7198 | 73.3749 | -0.2655 | 123.6557 | 2.7603 | 73.3749 | 113.475 | 123.7198 | -123.999 | -124.0219
1922.7188 | 123.8342 | -61.2213 | 62.5214 | -0.23781 | 0.017092 | 0.015763 | 0.0099698 | 0.062171 | 0.00094847 | 0.084603 | -58.4976 | 62.4527 | -61.5097 | -61.4502 | 52.1988 | 12.4054 | 1.1719 | 1.0483 | 62.4802 | -61.496 | -0.28839 | -0.068664 | 2.7237 | -0.22888 | -10.3226 | -0.27466 | -0.041198 | 3.0121 | 62.3932 | 62.2696 | 113.4201 | 123.674 | 2.7237 | 123.7015 | 73.6267 | -0.27466 | 123.674 | 2.7237 | 73.6267 | 113.4201 | 123.7015 | -124.0311 | -124.0173
1923.7188 | 123.9075 | -61.2534 | 62.5534 | -0.29121 | 0.016451 | 0.014054 | 0.010183 | 0.062598 | 0.0013757 | 0.084817 | -58.5297 | 62.4619 | -61.5097 | -61.4548 | 52.4963 | 12.4008 | 1.0529 | 0.93384 | 62.4802 | -61.5005 | -0.25635 | -0.091553 | 2.7237 | -0.20142 | -10.0571 | -0.24719 | -0.073242 | 2.98 | 62.3062 | 62.1872 | 113.7497 | 123.7152 | 2.7237 | 123.7335 | 73.6542 | -0.24719 | 123.7152 | 2.7237 | 73.6542 | 113.7497 | 123.7335 | -124.0631 | -124.054
1924.7188 | 123.9532 | -61.2442 | 62.5031 | -0.047073 | 0.017092 | 0.015977 | 0.015097 | 0.064521 | 0.0020167 | 0.084603 | -58.2962 | 62.4939 | -61.4868 | -61.4182 | 52.3178 | 12.1262 | 0.9201 | 0.91553 | 62.4573 | -61.5234 | -0.24261 | -0.009156 | 2.948 | -0.17395 | -10.1852 | -0.27923 | -0.045777 | 3.1906 | 62.1643 | 62.1597 | 113.562 | 123.7381 | 2.948 | 123.7015 | 73.3704 | -0.27923 | 123.7381 | 2.948 | 73.3704 | 113.562 | 123.7015 | -123.9899 | -124.0265
1925.7188 | 123.8937 | -61.2579 | 62.5305 | -0.19966 | 0.015169 | 0.013841 | 0.010611 | 0.063666 | 0.0039393 | 0.08439 | -58.429 | 62.4573 | -61.5051 | -61.4548 | 52.4185 | 12.1674 | 0.86975 | 0.84228 | 62.4939 | -61.496 | -0.24719 | -0.073243 | 2.829 | -0.19684 | -10.112 | -0.23804 | -0.036622 | 3.0762 | 62.1277 | 62.1002 | 113.6765 | 123.7152 | 2.829 | 123.7518 | 73.4253 | -0.23804 | 123.7152 | 2.829 | 73.4253 | 113.6765 | 123.7518 | -124.0356 | -124.0265
1926.7188 | 123.8983 | -61.2442 | 62.5442 | -0.29121 | 0.015597 | 0.015336 | 0.01232 | 0.062384 | 0.0041529 | 0.082894 | -58.4702 | 62.4756 | -61.4914 | -61.4548 | 52.4048 | 12.3047 | 0.8606 | 0.73242 | 62.4756 | -61.5143 | -0.24719 | -0.068664 | 2.774 | -0.21057 | -10.1395 | -0.27008 | -0.068664 | 3.0212 | 62.1048 | 61.9766 | 113.649 | 123.7198 | 2.774 | 123.7198 | 73.5489 | -0.27008 | 123.7198 | 2.774 | 73.5489 | 113.649 | 123.7198 | -124.0356 | -124.0585
1927.7188 | 123.9075 | -61.2717 | 62.5214 | -0.12337 | 0.017519 | 0.016618 | 0.011465 | 0.064948 | 0.0011621 | 0.082681 | -58.4518 | 62.4847 | -61.496 | -61.4594 | 52.5513 | 12.3001 | 0.86975 | 0.6958 | 62.4527 | -61.5326 | -0.22431 | -0.036621 | 2.8198 | -0.18768 | -9.9701 | -0.26093 | -0.068664 | 3.0441 | 62.1414 | 61.9675 | 113.8229 | 123.7564 | 2.8198 | 123.7244 | 73.5718 | -0.26093 | 123.7564 | 2.8198 | 73.5718 | 113.8229 | 123.7244 | -124.0173 | -124.054
1928.7344 | 123.8892 | -61.2717 | 62.4893 | 0.1284 | 0.017519 | 0.016831 | 0.013815 | 0.065161 | -0.00054693 | 0.083535 | -58.461 | 62.4664 | -61.5326 | -61.4914 | 52.4918 | 12.5381 | 0.64545 | 0.52185 | 62.4619 | -61.528 | -0.26093 | -0.022888 | 2.8107 | -0.21973 | -9.9976 | -0.25635 | -0.027466 | 3.0716 | 61.9171 | 61.7935 | 113.7634 | 123.7381 | 2.8107 | 123.7335 | 73.8098 | -0.25635 | 123.7381 | 2.8107 | 73.8098 | 113.7634 | 123.7335 | -124.0219 | -124.0173
1929.7344 | 123.9304 | -61.2442 | 62.4756 | 0.19707 | 0.016451 | 0.014909 | 0.014883 | 0.065589 | 0.0018031 | 0.082253 | -58.6349 | 62.4527 | -61.5463 | -61.4731 | 52.4368 | 12.4924 | 0.56763 | 0.49896 | 62.4527 | -61.5417 | -0.30212 | -0.022888 | 2.6093 | -0.22888 | -10.0388 | -0.29755 | -0.022888 | 2.9114 | 61.8118 | 61.7432 | 113.681 | 123.6969 | 2.6093 | 123.6969 | 73.7366 | -0.29755 | 123.6969 | 2.6093 | 73.7366 | 113.681 | 123.6969 | -124.0219 | -124.0173
1930.7188 | 123.8846 | -61.2442 | 62.4985 | -0.19966 | 0.016878 | 0.014268 | 0.011679 | 0.066016 | 0.0020167 | 0.082894 | -58.6349 | 62.4664 | -61.5234 | -61.4777 | 52.4918 | 12.4146 | 0.66376 | 0.49896 | 62.5122 | -61.496 | -0.27923 | -0.032043 | 2.6093 | -0.23346 | -10.0067 | -0.25177 | 0.013733 | 2.8885 | 61.908 | 61.7432 | 113.736 | 123.7106 | 2.6093 | 123.7564 | 73.6588 | -0.25177 | 123.7106 | 2.6093 | 73.6588 | 113.736 | 123.7564 | -124.0219 | -123.9944
1931.7188 | 123.9212 | -61.2396 | 62.5031 | -0.26833 | 0.017306 | 0.016404 | 0.011038 | 0.063239 | 0.0018031 | 0.083322 | -58.255 | 62.5076 | -61.4548 | -61.4594 | 52.3315 | 12.5656 | 0.60883 | 0.49439 | 62.4802 | -61.5051 | -0.21515 | 0.004577 | 2.9846 | -0.21973 | -10.1715 | -0.2655 | -0.022888 | 3.1998 | 61.8484 | 61.734 | 113.5712 | 123.7473 | 2.9846 | 123.7198 | 73.8052 | -0.2655 | 123.7473 | 2.9846 | 73.8052 | 113.5712 | 123.7198 | -123.9578 | -124.0082
1932.7188 | 123.88 | -61.2671 | 62.5351 | -0.16151 | 0.017733 | 0.016618 | 0.010611 | 0.065802 | 0.0024439 | 0.083749 | -58.3649 | 62.4664 | -61.496 | -61.4548 | 52.4368 | 12.3917 | 0.73242 | 0.64545 | 62.4756 | -61.5051 | -0.22888 | -0.068664 | 2.9022 | -0.18768 | -10.0983 | -0.23804 | -0.059509 | 3.1311 | 61.9995 | 61.9125 | 113.7039 | 123.7335 | 2.9022 | 123.7427 | 73.6588 | -0.23804 | 123.7335 | 2.9022 | 73.6588 | 113.7039 | 123.7427 | -124.0311 | -124.0402
1933.7188 | 123.8892 | -61.2762 | 62.4573 | 0.2047 | 0.019656 | 0.019395 | 0.012747 | 0.067725 | 0.0032983 | 0.083108 | -58.5159 | 62.4573 | -61.5143 | -61.496 | 52.4139 | 12.5427 | 0.80566 | 0.62714 | 62.4435 | -61.5189 | -0.23804 | 0 | 2.7603 | -0.21973 | -10.0433 | -0.24261 | -0.013733 | 2.9984 | 62.0819 | 61.9034 | 113.6902 | 123.7335 | 2.7603 | 123.7198 | 73.819 | -0.24261 | 123.7335 | 2.7603 | 73.819 | 113.6902 | 123.7198 | -123.9716 | -123.9761
1934.7188 | 123.8754 | -61.2991 | 62.4802 | 0.097885 | 0.02051 | 0.014268 | 0.014883 | 0.064948 | 0.0013757 | 0.083535 | -58.429 | 62.471 | -61.5189 | -61.5005 | 52.4048 | 12.4374 | 0.62256 | 0.49896 | 62.4619 | -61.5372 | -0.21973 | -0.009156 | 2.8702 | -0.20142 | -10.0754 | -0.23804 | -0.018311 | 3.0899 | 61.9217 | 61.7981 | 113.7039 | 123.7701 | 2.8702 | 123.761 | 73.7366 | -0.23804 | 123.7701 | 2.8702 | 73.7366 | 113.7039 | 123.761 | -123.999 | -124.0173
1935.7188 | 123.9166 | -61.2488 | 62.5305 | -0.16151 | 0.017306 | 0.01854 | 0.012106 | 0.06623 | 0.0018031 | 0.081826 | -58.3694 | 62.4893 | -61.496 | -61.441 | 52.3773 | 12.6114 | 0.86975 | 0.72327 | 62.4847 | -61.5234 | -0.24719 | -0.041199 | 2.8793 | -0.19226 | -10.1532 | -0.27466 | -0.045777 | 3.1265 | 62.1185 | 61.972 | 113.6261 | 123.7381 | 2.8793 | 123.7335 | 73.8602 | -0.27466 | 123.7381 | 2.8793 | 73.8602 | 113.6261 | 123.7335 | -124.0265 | -124.054
1936.7188 | 123.9075 | -61.2488 | 62.4756 | -0.19966 | 0.017519 | 0.019181 | 0.010611 | 0.064948 | 0.0011621 | 0.082681 | -58.374 | 62.5076 | -61.5097 | -61.4548 | 52.5558 | 12.4786 | 0.75531 | 0.67749 | 62.4939 | -61.528 | -0.26093 | 0.032043 | 2.8748 | -0.20599 | -9.9197 | -0.27924 | 0.01831 | 3.1357 | 62.0041 | 61.9263 | 113.8046 | 123.7564 | 2.8748 | 123.7427 | 73.7274 | -0.27924 | 123.7564 | 2.8748 | 73.7274 | 113.8046 | 123.7427 | -123.9853 | -124.0036
1937.7188 | 123.9075 | -61.2396 | 62.4939 | -0.20729 | 0.016878 | 0.017472 | 0.01296 | 0.063666 | -0.00054693 | 0.081826 | -58.5251 | 62.4802 | -61.496 | -61.4456 | 52.446 | 12.5427 | 0.75531 | 0.67291 | 62.5031 | -61.5097 | -0.25635 | -0.013732 | 2.7145 | -0.20599 | -10.0479 | -0.27008 | 0.009156 | 2.9709 | 61.9949 | 61.9125 | 113.6856 | 123.7198 | 2.7145 | 123.7427 | 73.7823 | -0.27008 | 123.7198 | 2.7145 | 73.7823 | 113.6856 | 123.7427 | -123.9899 | -124.0036
1938.7188 | 123.9212 | -61.2717 | 62.471 | 0.1284 | 0.016665 | 0.020036 | 0.013174 | 0.065375 | 0.0018031 | 0.083108 | -58.5022 | 62.439 | -61.5234 | -61.496 | 52.5604 | 12.6801 | 0.80109 | 0.69122 | 62.4481 | -61.5555 | -0.25177 | -0.032043 | 2.7695 | -0.22431 | -9.9106 | -0.28381 | -0.022888 | 3.0212 | 62.0728 | 61.9629 | 113.8321 | 123.7106 | 2.7695 | 123.7198 | 73.9517 | -0.28381 | 123.7106 | 2.7695 | 73.9517 | 113.8321 | 123.7198 | -123.9944 | -124.0265
1939.7188 | 123.9075 | -61.2625 | 62.471 | 0.03685 | 0.017519 | 0.019822 | 0.015524 | 0.066016 | 0.0013757 | 0.082894 | -58.5068 | 62.4847 | -61.5234 | -61.4777 | 52.6016 | 12.7716 | 1.0208 | 0.79651 | 62.471 | -61.5417 | -0.26093 | 0.013733 | 2.7557 | -0.21515 | -9.8694 | -0.27924 | 0 | 3.0167 | 62.2833 | 62.059 | 113.8641 | 123.7473 | 2.7557 | 123.7335 | 74.0341 | -0.27924 | 123.7473 | 2.7557 | 74.0341 | 113.8641 | 123.7335 | -123.9944 | -124.0128
1940.7188 | 123.8892 | -61.2579 | 62.4802 | -1.9086 | 0.016451 | 0.017045 | 0.011251 | 0.064093 | 0.00073487 | 0.081826 | -58.4747 | 62.4756 | -61.5005 | -61.4914 | 52.684 | 12.9364 | 1.062 | 0.71869 | 62.5031 | -61.5005 | -0.24261 | -0.004578 | 2.7832 | -0.23346 | -9.7961 | -0.24261 | 0.022888 | 3.0258 | 62.3199 | 61.9766 | 113.942 | 123.7335 | 2.7832 | 123.761 | 74.1943 | -0.24261 | 123.7335 | 2.7832 | 74.1943 | 113.942 | 123.761 | -123.9807 | -123.9807
1941.7188 | 123.9029 | -61.2488 | 62.5168 | -0.27596 | 0.016238 | 0.020249 | 0.008688 | 0.064734 | 0.0024439 | 0.083108 | -58.4793 | 62.4985 | -61.5463 | -61.4731 | 52.7756 | 13.0188 | 1.1215 | 0.76446 | 62.4756 | -61.5326 | -0.29755 | -0.018311 | 2.7695 | -0.2243 | -9.7412 | -0.28381 | -0.041199 | 3.067 | 62.3703 | 62.0132 | 114.0244 | 123.7473 | 2.7695 | 123.7244 | 74.2676 | -0.28381 | 123.7473 | 2.7695 | 74.2676 | 114.0244 | 123.7244 | -124.0631 | -124.0494
1942.7188 | 123.9166 | -61.2579 | 62.5214 | -0.28358 | 0.018587 | 0.016191 | 0.011892 | 0.065161 | -0.0011877 | 0.081826 | -58.4564 | 62.4847 | -61.4868 | -61.322 | 52.4414 | 12.6572 | 1.062 | 0.74616 | 62.4847 | -61.5417 | -0.22888 | -0.036621 | 2.8015 | -0.064086 | -10.08 | -0.28381 | -0.036621 | 3.0304 | 62.3199 | 62.0041 | 113.6993 | 123.7427 | 2.8015 | 123.7427 | 73.9151 | -0.28381 | 123.7427 | 2.8015 | 73.9151 | 113.6993 | 123.7427 | -124.0082 | -124.0631
1943.7188 | 123.9029 | -61.2671 | 62.4939 | -0.16914 | 0.017519 | 0.019181 | 0.015097 | 0.06388 | 0.00073487 | 0.083749 | -58.6212 | 62.471 | -61.5189 | -61.5234 | 52.6291 | 12.6617 | 0.96588 | 0.74158 | 62.4435 | -61.528 | -0.25177 | -0.022888 | 2.6459 | -0.25635 | -9.8648 | -0.26093 | -0.050354 | 2.8976 | 62.233 | 62.0087 | 113.8962 | 123.7381 | 2.6459 | 123.7106 | 73.9288 | -0.26093 | 123.7381 | 2.6459 | 73.9288 | 113.8962 | 123.7106 | -124.0128 | -124.0219
1944.7188 | 123.8892 | -61.2625 | 62.4619 | 1.0897 | 0.01816 | 0.019608 | 0.013388 | 0.066016 | 0.0020167 | 0.082253 | -58.2458 | 62.4573 | -61.5417 | -61.4502 | 52.6794 | 12.6205 | 1.03 | 0.74616 | 62.4664 | -61.5463 | -0.27924 | -0.004578 | 3.0167 | -0.18768 | -9.7824 | -0.28381 | 0.004578 | 3.2959 | 62.2925 | 62.0087 | 113.942 | 123.7198 | 3.0167 | 123.7289 | 73.8831 | -0.28381 | 123.7198 | 3.0167 | 73.8831 | 113.942 | 123.7289 | -124.0036 | -124.0082
1945.7188 | 123.9212 | -61.2625 | 62.4802 | -0.14626 | 0.019015 | 0.017899 | 0.011892 | 0.066443 | 0.0020167 | 0.083749 | -58.5022 | 62.4527 | -61.5326 | -61.4731 | 52.9129 | 12.6526 | 1.1627 | 0.82398 | 62.4847 | -61.528 | -0.27008 | -0.027466 | 2.7603 | -0.21057 | -9.5673 | -0.2655 | 0.004577 | 3.0304 | 62.4252 | 62.0865 | 114.1754 | 123.7152 | 2.7603 | 123.7473 | 73.9151 | -0.2655 | 123.7152 | 2.7603 | 73.9151 | 114.1754 | 123.7473 | -124.0128 | -124.0082
1946.7188 | 123.9029 | -61.2488 | 62.4847 | -0.21492 | 0.017092 | 0.014482 | 0.010397 | 0.06388 | 0.0013757 | 0.082467 | -58.4381 | 62.4527 | -61.5326 | -61.4731 | 52.8076 | 12.6572 | 1.1169 | 0.76446 | 62.4802 | -61.4868 | -0.28381 | -0.032043 | 2.8107 | -0.2243 | -9.6771 | -0.23804 | -0.004577 | 3.0945 | 62.3657 | 62.0132 | 114.0564 | 123.7015 | 2.8107 | 123.7289 | 73.9059 | -0.23804 | 123.7015 | 2.8107 | 73.9059 | 114.0564 | 123.7289 | -124.0173 | -123.9716
1947.7188 | 123.9532 | -61.2488 | 62.4847 | -0.14626 | 0.017733 | 0.017472 | 0.012533 | 0.066657 | 0.0026575 | 0.080972 | -58.4198 | 62.4847 | -61.5189 | -61.409 | 52.8992 | 12.886 | 1.149 | 0.8606 | 62.4847 | -61.5372 | -0.27008 | 0 | 2.829 | -0.16022 | -9.5856 | -0.28839 | 0 | 3.0991 | 62.3978 | 62.1094 | 114.1479 | 123.7335 | 2.829 | 123.7335 | 74.1348 | -0.28839 | 123.7335 | 2.829 | 74.1348 | 114.1479 | 123.7335 | -124.0036 | -124.0219
1948.7188 | 123.8937 | -61.2579 | 62.4847 | -0.031814 | 0.017306 | 0.017045 | 0.011251 | 0.064734 | 0.0024439 | 0.081826 | -58.5022 | 62.5031 | -61.4914 | -61.4594 | 52.6749 | 12.616 | 1.03 | 0.69122 | 62.5031 | -61.5189 | -0.23346 | 0.018311 | 2.7557 | -0.20142 | -9.8099 | -0.26092 | 0.018311 | 2.9892 | 62.2879 | 61.9492 | 113.9328 | 123.761 | 2.7557 | 123.761 | 73.8739 | -0.26092 | 123.761 | 2.7557 | 73.8739 | 113.9328 | 123.761 | -123.9761 | -124.0036
1949.7188 | 123.88 | -61.2625 | 62.4664 | 0.059738 | 0.019656 | 0.019822 | 0.015097 | 0.06623 | 0.0028711 | 0.08439 | -58.4702 | 62.5076 | -61.528 | -61.4914 | 52.6886 | 12.6389 | 1.0254 | 0.64545 | 62.4619 | -61.5555 | -0.2655 | 0.041198 | 2.7924 | -0.22888 | -9.7778 | -0.29297 | -0.004578 | 3.0579 | 62.2879 | 61.908 | 113.9511 | 123.7701 | 2.7924 | 123.7244 | 73.9014 | -0.29297 | 123.7701 | 2.7924 | 73.9014 | 113.9511 | 123.7244 | -123.9944 | -124.0219
1950.7188 | 123.9349 | -61.2762 | 62.4756 | -0.13863 | 0.016451 | 0.022386 | 0.011038 | 0.064093 | 0.0015893 | 0.081613 | -58.5434 | 62.4802 | -61.4914 | -61.4273 | 52.5879 | 12.8448 | 1.0345 | 0.80109 | 62.471 | -61.5234 | -0.21515 | 0.004578 | 2.7328 | -0.15106 | -9.8877 | -0.24719 | -0.004578 | 2.948 | 62.3108 | 62.0773 | 113.8641 | 123.7564 | 2.7328 | 123.7473 | 74.1211 | -0.24719 | 123.7564 | 2.7328 | 74.1211 | 113.8641 | 123.7473 | -123.967 | -123.999
1951.7188 | 123.9166 | -61.2625 | 62.4847 | -0.13863 | 0.014956 | 0.018113 | 0.01531 | 0.067511 | 0.0035121 | 0.084176 | -58.4473 | 62.471 | -61.4868 | -61.4227 | 52.684 | 13.0234 | 1.0162 | 0.85144 | 62.4664 | -61.5189 | -0.2243 | -0.013733 | 2.8152 | -0.16022 | -9.8007 | -0.25635 | -0.01831 | 3.0395 | 62.2787 | 62.114 | 113.9465 | 123.7335 | 2.8152 | 123.7289 | 74.2859 | -0.25635 | 123.7335 | 2.8152 | 74.2859 | 113.9465 | 123.7289 | -123.9716 | -124.0036
1952.7188 | 123.912 | -61.2671 | 62.4893 | -0.08522 | 0.017947 | 0.021104 | 0.013815 | 0.068793 | 0.0024439 | 0.083749 | -58.548 | 62.4939 | -61.4868 | -61.4182 | 52.5009 | 12.8998 | 0.94757 | 0.75073 | 62.4802 | -61.5463 | -0.21973 | 0.004577 | 2.7191 | -0.15106 | -9.9884 | -0.27924 | -0.009155 | 2.9388 | 62.2147 | 62.0178 | 113.768 | 123.761 | 2.7191 | 123.7473 | 74.1669 | -0.27924 | 123.761 | 2.7191 | 74.1669 | 113.768 | 123.7473 | -123.9761 | -124.0356
1953.7188 | 123.9258 | -61.2442 | 62.4939 | -0.19966 | 0.017947 | 0.020036 | 0.011892 | 0.064521 | -0.00033333 | 0.083108 | -58.4473 | 62.4802 | -61.5189 | -61.441 | 52.5101 | 12.6846 | 1.1581 | 0.77362 | 62.4847 | -61.5097 | -0.27466 | -0.013732 | 2.7969 | -0.19684 | -9.9838 | -0.2655 | -0.009155 | 3.0716 | 62.4023 | 62.0178 | 113.7543 | 123.7244 | 2.7969 | 123.7289 | 73.9288 | -0.2655 | 123.7244 | 2.7969 | 73.9288 | 113.7543 | 123.7289 | -124.0128 | -124.0036
1954.7188 | 123.9624 | -61.2671 | 62.4344 | 0.14366 | 0.013674 | 0.021104 | 0.0063382 | 0.065802 | 0.0011621 | 0.084603 | -58.5114 | 62.3657 | -61.5097 | -61.4502 | 52.565 | 12.8036 | 0.89264 | 0.8194 | 62.3795 | -61.5189 | -0.24261 | -0.068664 | 2.7557 | -0.1831 | -9.8694 | -0.25177 | -0.054931 | 2.9984 | 62.1597 | 62.0865 | 113.8321 | 123.6328 | 2.7557 | 123.6465 | 74.0707 | -0.25177 | 123.6328 | 2.7557 | 74.0707 | 113.8321 | 123.6465 | -123.9441 | -123.9532
1955.7188 | 123.9578 | -61.2396 | 62.4573 | 0.2047 | 0.015169 | 0.014695 | 0.0082608 | 0.062171 | 0.0037257 | 0.085244 | -58.4747 | 62.384 | -61.5005 | -61.4365 | 52.4872 | 12.886 | 0.737 | 0.71869 | 62.3978 | -61.5234 | -0.26093 | -0.073242 | 2.7649 | -0.19684 | -9.9701 | -0.28381 | -0.059509 | 3.0258 | 61.9766 | 61.9583 | 113.7268 | 123.6237 | 2.7649 | 123.6374 | 74.1257 | -0.28381 | 123.6237 | 2.7649 | 74.1257 | 113.7268 | 123.6374 | -123.9578 | -123.9807
1956.7188 | 123.9304 | -61.2671 | 62.5031 | -0.23018 | 0.01816 | 0.016191 | 0.011679 | 0.061743 | 0.0043665 | 0.08439 | -58.5617 | 62.4802 | -61.5143 | -61.4502 | 52.478 | 12.8632 | 1.0345 | 0.66834 | 62.471 | -61.5555 | -0.24719 | -0.022888 | 2.7054 | -0.1831 | -10.025 | -0.28839 | -0.032044 | 2.9526 | 62.3016 | 61.9354 | 113.7451 | 123.7473 | 2.7054 | 123.7381 | 74.1302 | -0.28839 | 123.7473 | 2.7054 | 74.1302 | 113.7451 | 123.7381 | -124.0173 | -124.0585
1957.7188 | 123.9029 | -61.2671 | 62.471 | 2.7911 | 0.013674 | 0.015336 | 0.015097 | 0.063452 | -0.00097413 | 0.083962 | -58.3557 | 62.4527 | -61.5189 | -61.4777 | 52.5284 | 12.7441 | 0.89264 | 0.74616 | 62.4481 | -61.5646 | -0.25177 | -0.01831 | 2.9114 | -0.21057 | -9.9426 | -0.29755 | -0.022888 | 3.1631 | 62.1597 | 62.0132 | 113.7955 | 123.7198 | 2.9114 | 123.7152 | 74.0112 | -0.29755 | 123.7198 | 2.9114 | 74.0112 | 113.7955 | 123.7152 | -123.9899 | -124.0356
1958.7188 | 123.9487 | -61.2534 | 62.4985 | -0.17677 | 0.017519 | 0.014909 | 0.014456 | 0.065375 | 0.0015893 | 0.082681 | -58.4702 | 62.4847 | -61.496 | -61.4136 | 52.6428 | 12.9135 | 0.83771 | 0.70953 | 62.4893 | -61.5051 | -0.24262 | -0.013733 | 2.7832 | -0.16022 | -9.8557 | -0.25177 | -0.009155 | 3.0258 | 62.0911 | 61.9629 | 113.8962 | 123.7381 | 2.7832 | 123.7427 | 74.1669 | -0.25177 | 123.7381 | 2.7832 | 74.1669 | 113.8962 | 123.7427 | -123.9944 | -124.0036
1959.7188 | 123.9075 | -61.2854 | 62.4527 | 0.17418 | 0.016024 | 0.015336 | 0.01232 | 0.065375 | 0.0030847 | 0.083322 | -58.4518 | 62.4435 | -61.5326 | -61.5005 | 52.4963 | 12.8311 | 0.80566 | 0.62256 | 62.439 | -61.528 | -0.24719 | -0.009156 | 2.8336 | -0.21515 | -9.9564 | -0.24262 | -0.013733 | 3.0808 | 62.0911 | 61.908 | 113.7817 | 123.7289 | 2.8336 | 123.7244 | 74.1165 | -0.24262 | 123.7289 | 2.8336 | 74.1165 | 113.7817 | 123.7244 | -123.9853 | -123.9807
1960.7188 | 123.9441 | -61.2534 | 62.4847 | -0.20729 | 0.014742 | 0.018327 | 0.01296 | 0.065375 | 0.0024439 | 0.085244 | -58.548 | 62.4939 | -61.5189 | -61.4136 | 52.446 | 12.5061 | 1.0025 | 0.737 | 62.4847 | -61.5326 | -0.2655 | 0.009155 | 2.7054 | -0.16022 | -10.0388 | -0.27924 | 0 | 2.9709 | 62.2559 | 61.9904 | 113.6993 | 123.7473 | 2.7054 | 123.7381 | 73.7595 | -0.27924 | 123.7473 | 2.7054 | 73.7595 | 113.6993 | 123.7381 | -124.0036 | -124.0173
1961.7188 | 123.912 | -61.2717 | 62.471 | -0.077591 | 0.018801 | 0.017686 | 0.013815 | 0.065589 | 0.0037257 | 0.085458 | -58.4564 | 62.4756 | -61.4914 | -61.441 | 52.4368 | 12.5519 | 0.95673 | 0.72784 | 62.4802 | -61.5234 | -0.21973 | 0.004578 | 2.8152 | -0.16937 | -10.0342 | -0.25177 | 0.009156 | 3.035 | 62.2284 | 61.9995 | 113.7085 | 123.7473 | 2.8152 | 123.7518 | 73.8235 | -0.25177 | 123.7473 | 2.8152 | 73.8235 | 113.7085 | 123.7518 | -123.9624 | -123.9944
1962.7188 | 123.999 | -61.2396 | 62.4435 | 0.17418 | 0.017947 | 0.022599 | 0.010183 | 0.066016 | 0.0024439 | 0.083108 | -58.5068 | 62.439 | -61.5372 | -61.441 | 52.5421 | 12.7304 | 0.68665 | 0.68665 | 62.4344 | -61.528 | -0.29755 | -0.004577 | 2.7328 | -0.20142 | -9.9014 | -0.28839 | -0.009155 | 3.0304 | 61.9263 | 61.9263 | 113.7817 | 123.6786 | 2.7328 | 123.674 | 73.97 | -0.28839 | 123.6786 | 2.7328 | 73.97 | 113.7817 | 123.674 | -123.9807 | -123.9716
1963.7188 | 123.9258 | -61.2534 | 62.5031 | -0.16914 | 0.01816 | 0.015763 | 0.014456 | 0.065589 | -0.00011953 | 0.083322 | -58.5571 | 62.4756 | -61.4914 | -61.4365 | 52.6611 | 12.4786 | 1.1536 | 0.8194 | 62.5031 | -61.5509 | -0.23804 | -0.027466 | 2.6962 | -0.1831 | -9.8419 | -0.29755 | 0 | 2.9343 | 62.4069 | 62.0728 | 113.9145 | 123.7289 | 2.6962 | 123.7564 | 73.732 | -0.29755 | 123.7289 | 2.6962 | 73.732 | 113.9145 | 123.7564 | -123.9944 | -124.054
1964.7188 | 123.9395 | -61.2762 | 62.4573 | 0.17418 | 0.019869 | 0.014695 | 0.014029 | 0.067084 | 0.0032983 | 0.085244 | -58.58 | 62.4802 | -61.5326 | -61.4868 | 52.5101 | 12.7899 | 0.89264 | 0.66834 | 62.471 | -61.5463 | -0.25635 | 0.022889 | 2.6962 | -0.21057 | -9.9472 | -0.27008 | 0.013733 | 2.9526 | 62.1689 | 61.9446 | 113.7863 | 123.7564 | 2.6962 | 123.7473 | 74.0662 | -0.27008 | 123.7564 | 2.6962 | 74.0662 | 113.7863 | 123.7473 | -123.9899 | -124.0036
1965.7188 | 123.9578 | -61.2625 | 62.4619 | -0.17677 | 0.016878 | 0.020677 | 0.012106 | 0.066657 | 9.4068e-05 | 0.080972 | -58.5251 | 62.5076 | -61.4914 | -61.3953 | 52.5055 | 12.7075 | 0.7782 | 0.61798 | 62.4802 | -61.5234 | -0.22888 | 0.045776 | 2.7374 | -0.13275 | -9.9564 | -0.26093 | 0.018311 | 2.9663 | 62.0407 | 61.8805 | 113.768 | 123.7701 | 2.7374 | 123.7427 | 73.97 | -0.26093 | 123.7701 | 2.7374 | 73.97 | 113.768 | 123.7427 | -123.9532 | -123.9853
1966.7188 | 123.9487 | -61.2396 | 62.471 | -0.19966 | 0.01816 | 0.014695 | 0.013815 | 0.068579 | 0.0015893 | 0.082681 | -58.5434 | 62.4985 | -61.5143 | -61.409 | 52.5879 | 12.9272 | 0.9201 | 0.6546 | 62.4802 | -61.528 | -0.27466 | 0.027466 | 2.6962 | -0.16937 | -9.8831 | -0.28839 | 0.009156 | 2.9709 | 62.1597 | 61.8942 | 113.8275 | 123.7381 | 2.6962 | 123.7198 | 74.1669 | -0.28839 | 123.7381 | 2.6962 | 74.1669 | 113.8275 | 123.7198 | -123.9853 | -123.999
1967.7344 | 123.9487 | -61.2534 | 62.4161 | 0.090256 | 0.015597 | 0.015977 | 0.0046292 | 0.066443 | 9.4068e-05 | 0.086312 | -58.7723 | 62.3611 | -61.5097 | -61.441 | 52.7481 | 13.4399 | 0.57678 | 0.60425 | 62.4115 | -61.4731 | -0.25635 | -0.054932 | 2.4811 | -0.18768 | -9.668 | -0.21973 | -0.004578 | 2.7374 | 61.8301 | 61.8576 | 114.0015 | 123.6145 | 2.4811 | 123.6649 | 74.6933 | -0.21973 | 123.6145 | 2.4811 | 74.6933 | 114.0015 | 123.6649 | -123.9258 | -123.8892
1968.7188 | 123.9349 | -61.2717 | 62.4985 | -0.22255 | 0.019442 | 0.019181 | 0.012747 | 0.062384 | 0.0022303 | 0.081613 | -58.5388 | 62.5168 | -61.4639 | -61.4456 | 52.5101 | 13.1012 | 0.86517 | 0.56763 | 62.4802 | -61.5417 | -0.19226 | 0.018311 | 2.7328 | -0.17395 | -9.9884 | -0.27008 | -0.01831 | 2.9251 | 62.1368 | 61.8393 | 113.7817 | 123.7885 | 2.7328 | 123.7518 | 74.3729 | -0.27008 | 123.7885 | 2.7328 | 74.3729 | 113.7817 | 123.7518 | -123.9624 | -124.0402
1969.7188 | 123.8892 | -61.2625 | 62.4985 | -0.0089264 | 0.018587 | 0.015763 | 0.016165 | 0.065802 | 0.00052127 | 0.083322 | -58.5068 | 62.4756 | -61.4868 | -61.4456 | 52.5513 | 13.0234 | 0.8606 | 0.5722 | 62.4802 | -61.5463 | -0.2243 | -0.022888 | 2.7557 | -0.18311 | -9.9472 | -0.28381 | -0.01831 | 2.98 | 62.1231 | 61.8347 | 113.8138 | 123.7381 | 2.7557 | 123.7427 | 74.2859 | -0.28381 | 123.7381 | 2.7557 | 74.2859 | 113.8138 | 123.7427 | -123.9853 | -124.0448
1970.7188 | 123.9532 | -61.2625 | 62.4756 | -0.19203 | 0.019228 | 0.018327 | 0.011892 | 0.064093 | 9.4068e-05 | 0.081826 | -58.5297 | 62.4893 | -61.5051 | -61.4227 | 52.6382 | 12.9318 | 0.84228 | 0.70038 | 62.5031 | -61.5417 | -0.24262 | 0.013733 | 2.7328 | -0.16022 | -9.8373 | -0.27924 | 0.027466 | 2.9755 | 62.1048 | 61.9629 | 113.9008 | 123.7518 | 2.7328 | 123.7656 | 74.1943 | -0.27924 | 123.7518 | 2.7328 | 74.1943 | 113.9008 | 123.7656 | -123.9807 | -124.0173
1971.7188 | 123.9624 | -61.2579 | 62.4619 | -0.031814 | 0.017092 | 0.018754 | 0.014883 | 0.065161 | 0.0018031 | 0.08738 | -58.4747 | 62.4802 | -61.5097 | -61.5921 | 52.3361 | 13.3942 | 0.75989 | 0.62256 | 62.4756 | -61.5189 | -0.25177 | 0.018311 | 2.7832 | -0.33417 | -10.1257 | -0.26092 | 0.013733 | 3.035 | 62.0178 | 61.8805 | 113.5941 | 123.7381 | 2.7832 | 123.7335 | 74.6521 | -0.26092 | 123.7381 | 2.7832 | 74.6521 | 113.5941 | 123.7335 | -123.9716 | -123.9807
1972.7344 | 124.0082 | -61.2167 | 62.471 | -0.26833 | 0.014101 | 0.018113 | 0.0082608 | 0.064734 | 0.0024439 | 0.082681 | -58.6166 | 62.3795 | -61.4914 | -61.3724 | 52.5375 | 13.2706 | 0.64545 | 0.68665 | 62.4344 | -61.4594 | -0.27466 | -0.091552 | 2.6001 | -0.15564 | -9.9335 | -0.24262 | -0.036621 | 2.8748 | 61.8622 | 61.9034 | 113.7543 | 123.5962 | 2.6001 | 123.6511 | 74.4873 | -0.24262 | 123.5962 | 2.6001 | 74.4873 | 113.7543 | 123.6511 | -123.9624 | -123.9304
1973.7188 | 124.0036 | -61.2671 | 62.4847 | -0.077591 | 0.016878 | 0.014909 | 0.014242 | 0.064521 | 0.00052127 | 0.084176 | -58.4656 | 62.4619 | -61.5005 | -61.4136 | 52.5009 | 13.2339 | 0.78278 | 0.59509 | 62.4435 | -61.5417 | -0.23346 | -0.022888 | 2.8015 | -0.14648 | -9.9838 | -0.27466 | -0.041199 | 3.035 | 62.0499 | 61.8622 | 113.768 | 123.7289 | 2.8015 | 123.7106 | 74.501 | -0.27466 | 123.7289 | 2.8015 | 74.501 | 113.768 | 123.7106 | -123.9853 | -124.0265
1974.7188 | 123.9212 | -61.2762 | 62.4619 | 0.090256 | 0.017519 | 0.021531 | 0.013174 | 0.065802 | 0.0032983 | 0.084603 | -58.5754 | 62.4481 | -61.5326 | -61.4914 | 52.327 | 13.1012 | 0.79651 | 0.64545 | 62.4664 | -61.5372 | -0.25635 | -0.013733 | 2.7008 | -0.21515 | -10.1349 | -0.26093 | 0.004578 | 2.9572 | 62.0728 | 61.9217 | 113.6032 | 123.7244 | 2.7008 | 123.7427 | 74.3774 | -0.26093 | 123.7244 | 2.7008 | 74.3774 | 113.6032 | 123.7427 | -123.9944 | -123.999
1975.7188 | 123.88 | -61.2671 | 62.4664 | 0.029221 | 0.017306 | 0.017259 | 0.015738 | 0.067084 | 0.0024439 | 0.082681 | -58.5205 | 62.4619 | -61.5143 | -61.4731 | 52.272 | 13.0463 | 0.87433 | 0.82855 | 62.471 | -61.5555 | -0.24719 | -0.004578 | 2.7466 | -0.20599 | -10.1944 | -0.28839 | 0.004577 | 2.9938 | 62.1414 | 62.0956 | 113.5391 | 123.7289 | 2.7466 | 123.7381 | 74.3134 | -0.28839 | 123.7289 | 2.7466 | 74.3134 | 113.5391 | 123.7381 | -123.9807 | -124.0219
1976.7188 | 123.88 | -61.2854 | 62.4985 | 0.059738 | 0.019869 | 0.016404 | 0.014456 | 0.066657 | 0.00030767 | 0.083749 | -58.5022 | 62.4802 | -61.5326 | -61.4822 | 52.3041 | 13.3621 | 0.80566 | 0.62714 | 62.4481 | -61.5555 | -0.24719 | -0.01831 | 2.7832 | -0.19684 | -10.1944 | -0.27008 | -0.050354 | 3.0304 | 62.0911 | 61.9125 | 113.5895 | 123.7656 | 2.7832 | 123.7335 | 74.6475 | -0.27008 | 123.7656 | 2.7832 | 74.6475 | 113.5895 | 123.7335 | -124.0311 | -124.054
1977.7344 | 123.8022 | -61.2442 | 62.4527 | -0.15388 | 0.017947 | 0.018968 | 0.014029 | 0.066016 | 0.0020167 | 0.082253 | -58.4839 | 62.4619 | -61.5005 | -61.4227 | 52.5055 | 13.4491 | 0.72784 | 0.75073 | 62.4573 | -61.528 | -0.25635 | 0.009155 | 2.7603 | -0.17853 | -9.9472 | -0.28381 | 0.004577 | 3.0167 | 61.972 | 61.9949 | 113.7497 | 123.7061 | 2.7603 | 123.7015 | 74.6933 | -0.28381 | 123.7061 | 2.7603 | 74.6933 | 113.7497 | 123.7015 | -123.9532 | -123.9807
1978.7188 | 123.8846 | -61.2717 | 62.4527 | 0.0063326 | 0.017947 | 0.020036 | 0.013815 | 0.066016 | 0.0015893 | 0.083108 | -58.5663 | 62.4893 | -61.5234 | -61.4594 | 52.4643 | 13.4399 | 0.8194 | 0.79193 | 62.4893 | -61.5509 | -0.25177 | 0.036621 | 2.7054 | -0.18768 | -9.9884 | -0.27924 | 0.036621 | 2.9572 | 62.0911 | 62.0636 | 113.736 | 123.761 | 2.7054 | 123.761 | 74.7116 | -0.27924 | 123.761 | 2.7054 | 74.7116 | 113.736 | 123.761 | -123.9761 | -124.0036
1979.7188 | 123.8937 | -61.2717 | 62.4756 | 1.4559 | 0.017947 | 0.019608 | 0.010611 | 0.067511 | 0.0024439 | 0.084603 | -58.5114 | 62.5031 | -61.5143 | -61.528 | 52.5558 | 13.5132 | 0.77362 | 0.73242 | 62.4756 | -61.5601 | -0.24262 | 0.027466 | 2.7603 | -0.25635 | -9.9197 | -0.28839 | 0 | 3.0029 | 62.0453 | 62.0041 | 113.8275 | 123.7747 | 2.7603 | 123.7473 | 74.7849 | -0.28839 | 123.7747 | 2.7603 | 74.7849 | 113.8275 | 123.7473 | -123.9899 | -124.0356
1980.7188 | 123.8709 | -61.3083 | 62.4527 | 0.0063326 | 0.017733 | 0.020249 | 0.015524 | 0.067298 | 0.0022303 | 0.084603 | -58.4656 | 62.4527 | -61.528 | -61.5051 | 52.6154 | 13.6002 | 1.1719 | 0.95673 | 62.4619 | -61.5875 | -0.21973 | 0 | 2.8427 | -0.19684 | -9.8373 | -0.27923 | 0.009155 | 3.0624 | 62.4802 | 62.265 | 113.9236 | 123.761 | 2.8427 | 123.7701 | 74.9084 | -0.27923 | 123.761 | 2.8427 | 74.9084 | 113.9236 | 123.7701 | -123.9807 | -124.0402
1981.7188 | 123.9349 | -61.2579 | 62.4573 | -0.08522 | 0.019015 | 0.018327 | 0.011892 | 0.066016 | 0.0028711 | 0.083108 | -58.4152 | 62.4619 | -61.5417 | -61.4502 | 52.7252 | 13.6276 | 0.94299 | 0.87433 | 62.4527 | -61.5738 | -0.28381 | 0.004578 | 2.8427 | -0.19226 | -9.7321 | -0.31586 | -0.004577 | 3.1265 | 62.2009 | 62.1323 | 113.9832 | 123.7198 | 2.8427 | 123.7106 | 74.8856 | -0.31586 | 123.7198 | 2.8427 | 74.8856 | 113.9832 | 123.7106 | -123.999 | -124.0311
1982.7344 | 123.912 | -61.2442 | 62.4573 | -0.062332 | 0.020083 | 0.017045 | 0.012747 | 0.065589 | 0.0022303 | 0.084817 | -58.58 | 62.4619 | -61.5143 | -61.4594 | 52.6199 | 13.6185 | 0.737 | 0.76904 | 62.4664 | -61.5601 | -0.27008 | 0.004578 | 2.6642 | -0.21515 | -9.8373 | -0.31586 | 0.009156 | 2.9343 | 61.9812 | 62.0132 | 113.8641 | 123.7061 | 2.6642 | 123.7106 | 74.8627 | -0.31586 | 123.7061 | 2.6642 | 74.8627 | 113.8641 | 123.7106 | -123.9716 | -124.0173
1983.7188 | 123.9212 | -61.2625 | 62.4573 | -0.031814 | 0.01816 | 0.01555 | 0.012747 | 0.067511 | -0.00011953 | 0.085244 | -58.4839 | 62.4847 | -61.5005 | -61.4319 | 52.6016 | 13.7878 | 0.78735 | 0.83771 | 62.4756 | -61.5326 | -0.23804 | 0.027466 | 2.7786 | -0.16937 | -9.8557 | -0.27008 | 0.018311 | 3.0167 | 62.0499 | 62.1002 | 113.8641 | 123.7473 | 2.7786 | 123.7381 | 75.0504 | -0.27008 | 123.7473 | 2.7786 | 75.0504 | 113.8641 | 123.7381 | -123.9578 | -123.9899
1984.7188 | 123.9258 | -61.29 | 62.4161 | 0.18944 | 0.016451 | 0.017045 | 0.0099698 | 0.068152 | 0.0011621 | 0.083535 | -58.6304 | 62.4161 | -61.5509 | -61.4685 | 52.6611 | 13.6276 | 0.74616 | 0.79193 | 62.4527 | -61.5417 | -0.26093 | 0 | 2.6596 | -0.17853 | -9.7549 | -0.25177 | 0.036621 | 2.9205 | 62.0361 | 62.0819 | 113.9511 | 123.7061 | 2.6596 | 123.7427 | 74.9176 | -0.25177 | 123.7061 | 2.6596 | 74.9176 | 113.9511 | 123.7427 | -123.967 | -123.9578
1985.7188 | 123.88 | -61.322 | 62.4527 | 0.16655 | 0.018587 | 0.020677 | 0.010397 | 0.070288 | 0.0037257 | 0.084176 | -58.3649 | 62.4344 | -61.5738 | -61.4273 | 52.5833 | 13.8519 | 0.91095 | 0.81482 | 62.439 | -61.5601 | -0.25177 | -0.018311 | 2.9572 | -0.10529 | -9.8694 | -0.23804 | -0.013733 | 3.2089 | 62.233 | 62.1368 | 113.9053 | 123.7564 | 2.9572 | 123.761 | 75.174 | -0.23804 | 123.7564 | 2.9572 | 75.174 | 113.9053 | 123.761 | -124.0265 | -124.0128
1986.7188 | 123.912 | -61.2534 | 62.4664 | -0.024185 | 0.018587 | 0.016404 | 0.014029 | 0.067084 | 0.0011621 | 0.083322 | -58.4747 | 62.4802 | -61.496 | -61.4456 | 52.7023 | 13.8382 | 0.81024 | 0.82398 | 62.4847 | -61.5738 | -0.24262 | 0.013733 | 2.7786 | -0.19226 | -9.7641 | -0.32043 | 0.01831 | 3.0212 | 62.0636 | 62.0773 | 113.9557 | 123.7335 | 2.7786 | 123.7381 | 75.0916 | -0.32043 | 123.7335 | 2.7786 | 75.0916 | 113.9557 | 123.7381 | -123.9624 | -124.0402
1987.7344 | 123.8663 | -61.2717 | 62.4802 | -0.28358 | 0.016238 | 0.012559 | 0.0097562 | 0.06687 | 0.0047937 | 0.083108 | -58.5205 | 62.4893 | -61.5601 | -61.4822 | 52.6978 | 13.9252 | 0.78278 | 0.65002 | 62.4893 | -61.5601 | -0.28839 | 0.009155 | 2.7512 | -0.21057 | -9.7824 | -0.28839 | 0.009155 | 3.0396 | 62.0544 | 61.9217 | 113.9694 | 123.761 | 2.7512 | 123.761 | 75.1968 | -0.28839 | 123.761 | 2.7512 | 75.1968 | 113.9694 | 123.761 | -124.0402 | -124.0402
1988.7188 | 123.8983 | -61.2762 | 62.4802 | -0.0012969 | 0.016665 | 0.017259 | 0.012747 | 0.065802 | 0.0041529 | 0.082467 | -58.4473 | 62.4893 | -61.5005 | -61.4731 | 52.652 | 13.9343 | 0.73242 | 0.71869 | 62.4573 | -61.5601 | -0.2243 | 0.009155 | 2.829 | -0.19684 | -9.8282 | -0.28381 | -0.022889 | 3.0533 | 62.0087 | 61.9949 | 113.9282 | 123.7656 | 2.829 | 123.7335 | 75.2106 | -0.28381 | 123.7656 | 2.829 | 75.2106 | 113.9282 | 123.7335 | -123.9807 | -124.0402
1989.7188 | 123.9029 | -61.2991 | 62.4573 | 0.15892 | 0.018801 | 0.024522 | 0.013174 | 0.066443 | 0.0018031 | 0.084817 | -58.8776 | 62.3886 | -61.5875 | -61.5326 | 52.5467 | 13.7741 | 0.79193 | 0.66376 | 62.471 | -61.5738 | -0.28839 | -0.068664 | 2.4216 | -0.23346 | -9.9106 | -0.27466 | 0.013733 | 2.71 | 62.0911 | 61.9629 | 113.8458 | 123.6877 | 2.4216 | 123.7701 | 75.0732 | -0.27466 | 123.6877 | 2.4216 | 75.0732 | 113.8458 | 123.7701 | -124.0448 | -124.0311
1990.7188 | 123.9075 | -61.2579 | 62.471 | -0.062332 | 0.017519 | 0.018327 | 0.014669 | 0.066443 | 0.0035121 | 0.081399 | -58.4564 | 62.4756 | -61.5097 | -61.4365 | 52.5833 | 13.8199 | 0.80109 | 0.63629 | 62.4802 | -61.5555 | -0.25177 | 0.004578 | 2.8015 | -0.17853 | -9.8877 | -0.29755 | 0.009156 | 3.0533 | 62.059 | 61.8942 | 113.8412 | 123.7335 | 2.8015 | 123.7381 | 75.0778 | -0.29755 | 123.7335 | 2.8015 | 75.0778 | 113.8412 | 123.7381 | -123.9807 | -124.0265
1991.7188 | 123.9075 | -61.2717 | 62.471 | 0.0063326 | 0.016238 | 0.018113 | 0.011892 | 0.067298 | 0.00073487 | 0.082894 | -58.58 | 62.4893 | -61.5097 | -61.4456 | 52.6566 | 13.8016 | 0.72327 | 0.56763 | 62.471 | -61.5463 | -0.23804 | 0.018311 | 2.6917 | -0.17395 | -9.8145 | -0.27466 | 0 | 2.9297 | 61.9949 | 61.8393 | 113.9282 | 123.761 | 2.6917 | 123.7427 | 75.0732 | -0.27466 | 123.761 | 2.6917 | 75.0732 | 113.9282 | 123.7427 | -123.9807 | -124.0173
1992.7344 | 123.8846 | -61.2488 | 62.5122 | -0.1844 | 0.01816 | 0.017259 | 0.0063382 | 0.065161 | 0.0035121 | 0.083108 | -58.6212 | 62.4619 | -61.5051 | -61.4639 | 52.7206 | 13.7146 | 0.75531 | 0.61798 | 62.5076 | -61.528 | -0.25635 | -0.050354 | 2.6276 | -0.21515 | -9.7916 | -0.27924 | -0.004578 | 2.8839 | 62.0041 | 61.8668 | 113.9694 | 123.7106 | 2.6276 | 123.7564 | 74.9634 | -0.27924 | 123.7106 | 2.6276 | 74.9634 | 113.9694 | 123.7564 | -124.0173 | -124.0402
1993.7188 | 123.8846 | -61.2991 | 62.4939 | -0.80238 | 0.020296 | 0.021958 | 0.012747 | 0.065802 | 0.0039393 | 0.083535 | -58.6395 | 62.4435 | -61.5234 | -61.5234 | 52.7069 | 13.7146 | 0.62714 | 0.52185 | 62.4527 | -61.5875 | -0.2243 | -0.050354 | 2.6596 | -0.2243 | -9.787 | -0.28839 | -0.041198 | 2.8839 | 61.9263 | 61.821 | 114.006 | 123.7427 | 2.6596 | 123.7518 | 75.0137 | -0.28839 | 123.7427 | 2.6596 | 75.0137 | 114.006 | 123.7518 | -124.0173 | -124.0814
1994.7344 | 123.9807 | -61.2305 | 62.4252 | 0.10551 | 0.014101 | 0.017686 | 0.005911 | 0.065802 | 0.0022303 | 0.08439 | -58.5342 | 62.3795 | -61.528 | -61.409 | 52.7481 | 14.0854 | 0.38452 | 0.5722 | 62.4207 | -61.5189 | -0.29755 | -0.045776 | 2.6962 | -0.17853 | -9.6771 | -0.28839 | -0.004578 | 2.9938 | 61.615 | 61.8027 | 113.9786 | 123.6099 | 2.6962 | 123.6511 | 75.3159 | -0.28839 | 123.6099 | 2.6962 | 75.3159 | 113.9786 | 123.6511 | -123.9532 | -123.9441
1995.7188 | 123.88 | -61.2991 | 62.4527 | 0.052109 | 0.01816 | 0.016831 | 0.015097 | 0.065375 | 0.0020167 | 0.082681 | -58.5754 | 62.4756 | -61.5326 | -61.5005 | 52.5925 | 13.8016 | 0.9613 | 0.54932 | 62.4298 | -61.5646 | -0.23346 | 0.022888 | 2.7237 | -0.20142 | -9.8602 | -0.2655 | -0.022888 | 2.9572 | 62.2604 | 61.8484 | 113.8916 | 123.7747 | 2.7237 | 123.7289 | 75.1007 | -0.2655 | 123.7747 | 2.7237 | 75.1007 | 113.8916 | 123.7289 | -123.9853 | -124.0173
1996.7188 | 123.8113 | -61.2717 | 62.4664 | 0.15129 | 0.019869 | 0.017899 | 0.014242 | 0.065375 | 0.00030767 | 0.085458 | -58.6075 | 62.4527 | -61.5326 | -61.5097 | 52.446 | 13.9572 | 0.49896 | 0.6546 | 62.384 | -61.5967 | -0.26093 | -0.013733 | 2.6642 | -0.23804 | -10.0204 | -0.32501 | -0.082398 | 2.9251 | 61.7706 | 61.9263 | 113.7177 | 123.7244 | 2.6642 | 123.6557 | 75.2289 | -0.32501 | 123.7244 | 2.6642 | 75.2289 | 113.7177 | 123.6557 | -123.999 | -124.0631
1997.7188 | 123.8525 | -61.2671 | 62.4756 | 0.021591 | 0.017092 | 0.017472 | 0.014669 | 0.067725 | 0.0018031 | 0.083322 | -58.6075 | 62.4802 | -61.5189 | -61.4685 | 52.6382 | 13.7421 | 0.83771 | 0.59509 | 62.4619 | -61.5509 | -0.25177 | 0.004578 | 2.6596 | -0.20142 | -9.8373 | -0.28381 | -0.013733 | 2.9114 | 62.1048 | 61.8622 | 113.9053 | 123.7473 | 2.6596 | 123.7289 | 75.0092 | -0.28381 | 123.7473 | 2.6596 | 75.0092 | 113.9053 | 123.7289 | -123.9944 | -124.0265
1998.7188 | 123.8892 | -61.2762 | 62.4573 | 0.41069 | 0.01816 | 0.018968 | 0.014669 | 0.06687 | 0.00094847 | 0.083108 | -58.4427 | 62.471 | -61.5005 | -61.4365 | 52.533 | 13.9709 | 1.0254 | 0.73242 | 62.4527 | -61.5372 | -0.2243 | 0.013733 | 2.8336 | -0.16022 | -9.9243 | -0.26093 | -0.004577 | 3.0579 | 62.3016 | 62.0087 | 113.8092 | 123.7473 | 2.8336 | 123.7289 | 75.2472 | -0.26093 | 123.7473 | 2.8336 | 75.2472 | 113.8092 | 123.7289 | -123.9578 | -123.9944
1999.7188 | 123.8846 | -61.2946 | 62.4573 | -0.78712 | 0.019015 | 0.018968 | 0.01232 | 0.068579 | 0.0047937 | 0.085671 | -58.6624 | 62.439 | -61.528 | -61.5189 | 52.5696 | 13.7741 | 0.83313 | 0.56305 | 62.4756 | -61.5555 | -0.23346 | -0.01831 | 2.6321 | -0.2243 | -9.8877 | -0.26093 | 0.018311 | 2.8656 | 62.1277 | 61.8576 | 113.8641 | 123.7335 | 2.6321 | 123.7701 | 75.0687 | -0.26093 | 123.7335 | 2.6321 | 75.0687 | 113.8641 | 123.7701 | -123.9853 | -124.0128
2000.7188 | 123.8525 | -61.3037 | 62.4756 | 0.067368 | 0.016238 | 0.019822 | 0.01531 | 0.068366 | -0.00011953 | 0.085244 | -58.548 | 62.4756 | -61.5051 | -61.5326 | 52.5421 | 13.9297 | 0.89722 | 0.52185 | 62.4527 | -61.5829 | -0.20142 | 0 | 2.7557 | -0.22888 | -9.9335 | -0.27924 | -0.022888 | 2.9572 | 62.2009 | 61.8256 | 113.8458 | 123.7793 | 2.7557 | 123.7564 | 75.2335 | -0.27924 | 123.7793 | 2.7557 | 75.2335 | 113.8458 | 123.7564 | -123.9807 | -124.0585
2001.7188 | 123.9166 | -61.2488 | 62.4664 | -0.09285 | 0.017092 | 0.019395 | 0.015738 | 0.06623 | 0.0028711 | 0.080972 | -58.5434 | 62.4573 | -61.5097 | -61.5326 | 52.2675 | 13.8016 | 0.99335 | 0.72784 | 62.4481 | -61.5829 | -0.26093 | -0.009156 | 2.7054 | -0.28381 | -10.199 | -0.33417 | -0.018311 | 2.9663 | 62.2421 | 61.9766 | 113.5162 | 123.7061 | 2.7054 | 123.6969 | 75.0504 | -0.33417 | 123.7061 | 2.7054 | 75.0504 | 113.5162 | 123.6969 | -123.9761 | -124.0494
2002.7188 | 124.0036 | -61.2442 | 62.3978 | 0.23521 | 0.01581 | 0.016191 | 0.010183 | 0.065589 | 0.0035121 | 0.082253 | -58.5159 | 62.384 | -61.5372 | -61.4227 | 52.771 | 14.2548 | 0.737 | 0.81482 | 62.3978 | -61.5372 | -0.29297 | -0.013733 | 2.7283 | -0.17853 | -9.6268 | -0.29297 | 0 | 3.0212 | 61.9812 | 62.059 | 114.0152 | 123.6282 | 2.7283 | 123.642 | 75.499 | -0.29297 | 123.6282 | 2.7283 | 75.499 | 114.0152 | 123.642 | -123.9349 | -123.9349
2003.7188 | 123.8983 | -61.2808 | 62.439 | 0.082626 | 0.017733 | 0.019395 | 0.01296 | 0.065802 | 0.0018031 | 0.083108 | -58.5938 | 62.4619 | -61.5143 | -61.4868 | 52.6245 | 13.8977 | 0.92926 | 0.63629 | 62.4664 | -61.6058 | -0.23346 | 0.022888 | 2.6871 | -0.20599 | -9.8145 | -0.32501 | 0.027466 | 2.9205 | 62.2101 | 61.9171 | 113.9053 | 123.7427 | 2.6871 | 123.7473 | 75.1785 | -0.32501 | 123.7427 | 2.6871 | 75.1785 | 113.9053 | 123.7473 | -123.9532 | -124.0448
2004.7188 | 123.9075 | -61.2762 | 62.471 | -0.13863 | 0.017947 | 0.019395 | 0.013174 | 0.067084 | 0.0020167 | 0.085458 | -58.4335 | 62.471 | -61.5234 | -61.4456 | 52.6291 | 14.0488 | 1.0391 | 0.80109 | 62.4435 | -61.5555 | -0.24719 | 0 | 2.8427 | -0.16937 | -9.8419 | -0.27924 | -0.027466 | 3.0899 | 62.3154 | 62.0773 | 113.9053 | 123.7473 | 2.8427 | 123.7198 | 75.325 | -0.27924 | 123.7473 | 2.8427 | 75.325 | 113.9053 | 123.7198 | -123.9944 | -124.0265
2005.7344 | 124.0723 | -61.2625 | 62.4161 | 0.15892 | 0.015597 | 0.022386 | 0.008688 | 0.066443 | 0.0045801 | 0.08439 | -58.5342 | 62.3611 | -61.5234 | -61.4227 | 52.7252 | 14.1312 | 0.91095 | 0.79651 | 62.4023 | -61.528 | -0.26093 | -0.054932 | 2.7283 | -0.16022 | -9.6909 | -0.2655 | -0.013733 | 2.9892 | 62.1735 | 62.059 | 113.9877 | 123.6237 | 2.7283 | 123.6649 | 75.3937 | -0.2655 | 123.6237 | 2.7283 | 75.3937 | 113.9877 | 123.6649 | -123.9395 | -123.9441
2006.7188 | 123.9166 | -61.2396 | 62.4619 | -0.024185 | 0.019656 | 0.015977 | 0.014669 | 0.065375 | 0.0024439 | 0.082467 | -58.4244 | 62.439 | -61.528 | -61.4319 | 52.7298 | 13.9252 | 1.062 | 0.737 | 62.4664 | -61.5646 | -0.28839 | -0.022888 | 2.8152 | -0.19226 | -9.7321 | -0.32501 | 0.004578 | 3.1036 | 62.3016 | 61.9766 | 113.9694 | 123.6786 | 2.8152 | 123.7061 | 75.1648 | -0.32501 | 123.6786 | 2.8152 | 75.1648 | 113.9694 | 123.7061 | -123.9899 | -124.0265
2007.7188 | 123.9441 | -61.2717 | 62.471 | -0.10048 | 0.017092 | 0.019395 | 0.014029 | 0.067939 | 0.0018031 | 0.082467 | -58.5159 | 62.4481 | -61.5097 | -61.4456 | 52.4414 | 13.9114 | 1.181 | 0.80109 | 62.4619 | -61.5738 | -0.23804 | -0.022888 | 2.7557 | -0.17395 | -10.0296 | -0.30212 | -0.009155 | 2.9938 | 62.4527 | 62.0728 | 113.7131 | 123.7198 | 2.7557 | 123.7335 | 75.1831 | -0.30212 | 123.7198 | 2.7557 | 75.1831 | 113.7131 | 123.7335 | -123.9807 | -124.0448
2008.7344 | 124.0173 | -61.235 | 62.4069 | 0.23521 | 0.014315 | 0.015977 | 0.0054836 | 0.064948 | 0.0022303 | 0.082894 | -58.429 | 62.352 | -61.5646 | -61.3632 | 52.803 | 14.1586 | 0.86975 | 0.88348 | 62.4115 | -61.5143 | -0.32959 | -0.054931 | 2.8061 | -0.12817 | -9.6039 | -0.27924 | 0.004578 | 3.1357 | 62.1048 | 62.1185 | 114.0381 | 123.587 | 2.8061 | 123.6465 | 75.3937 | -0.27924 | 123.587 | 2.8061 | 75.3937 | 114.0381 | 123.6465 | -123.9716 | -123.9212
2009.7188 | 123.8754 | -61.2625 | 62.4619 | 0.074997 | 0.016238 | 0.01555 | 0.014456 | 0.064948 | 0.0018031 | 0.083535 | -58.5159 | 62.4435 | -61.5234 | -61.4731 | 52.7298 | 14.0396 | 1.0757 | 0.70953 | 62.4435 | -61.5784 | -0.26093 | -0.018311 | 2.7466 | -0.21057 | -9.7321 | -0.31586 | -0.018311 | 3.0075 | 62.3383 | 61.972 | 113.9923 | 123.7061 | 2.7466 | 123.7061 | 75.3021 | -0.31586 | 123.7061 | 2.7466 | 75.3021 | 113.9923 | 123.7061 | -123.9853 | -124.0402
2010.7188 | 123.9349 | -61.2625 | 62.4756 | -0.17677 | 0.016878 | 0.020036 | 0.011251 | 0.066443 | 0.0022303 | 0.081185 | -58.5068 | 62.4573 | -61.5051 | -61.409 | 52.6749 | 14.0121 | 1.0345 | 0.82398 | 62.4664 | -61.5555 | -0.24262 | -0.018311 | 2.7557 | -0.14648 | -9.8007 | -0.29297 | -0.009155 | 2.9984 | 62.2971 | 62.0865 | 113.9374 | 123.7198 | 2.7557 | 123.7289 | 75.2747 | -0.29297 | 123.7198 | 2.7557 | 75.2747 | 113.9374 | 123.7289 | -123.9807 | -124.0311
2011.7188 | 123.9166 | -61.3129 | 62.439 | 0.15129 | 0.016878 | 0.017899 | 0.011038 | 0.067084 | 0.0011621 | 0.082894 | -58.6166 | 62.4344 | -61.5738 | -61.528 | 52.7252 | 14.3555 | 1.0986 | 0.7782 | 62.4435 | -61.5463 | -0.26093 | -0.004578 | 2.6962 | -0.21515 | -9.7137 | -0.23346 | 0.004577 | 2.9572 | 62.4115 | 62.0911 | 114.0381 | 123.7473 | 2.6962 | 123.7564 | 75.6683 | -0.23346 | 123.7473 | 2.6962 | 75.6683 | 114.0381 | 123.7564 | -124.0128 | -123.9853
2012.7188 | 123.9395 | -61.29 | 62.4298 | -0.25307 | 0.01816 | 0.02089 | 0.013601 | 0.064521 | 0.00030767 | 0.082681 | -58.4656 | 62.4435 | -61.5372 | -61.4227 | 52.8717 | 14.5386 | 1.1581 | 0.95673 | 62.4481 | -61.5738 | -0.24719 | 0.013732 | 2.8244 | -0.13275 | -9.5581 | -0.28381 | 0.01831 | 3.0716 | 62.4481 | 62.2467 | 114.1617 | 123.7335 | 2.8244 | 123.7381 | 75.8286 | -0.28381 | 123.7335 | 2.8244 | 75.8286 | 114.1617 | 123.7381 | -123.967 | -124.0036
2013.7188 | 123.88 | -61.3129 | 62.4252 | -0.016556 | 0.019015 | 0.021104 | 0.012533 | 0.068366 | 0.0022303 | 0.082467 | -58.5159 | 62.4573 | -61.5509 | -61.4594 | 52.7847 | 14.4379 | 1.268 | 0.99792 | 62.439 | -61.5692 | -0.23804 | 0.032043 | 2.7969 | -0.14648 | -9.6405 | -0.25635 | 0.013733 | 3.035 | 62.5809 | 62.3108 | 114.0976 | 123.7701 | 2.7969 | 123.7518 | 75.7507 | -0.25635 | 123.7701 | 2.7969 | 75.7507 | 114.0976 | 123.7518 | -123.9761 | -123.9944
2014.7188 | 123.9212 | -61.2946 | 62.4344 | 0.15892 | 0.01816 | 0.022172 | 0.012747 | 0.067511 | 0.0045801 | 0.084176 | -58.5663 | 62.4481 | -61.5509 | -61.5784 | 52.5604 | 14.328 | 1.6983 | 1.0712 | 62.4481 | -61.5784 | -0.25635 | 0.013733 | 2.7283 | -0.28381 | -9.874 | -0.28381 | 0.013733 | 2.9846 | 62.9929 | 62.3657 | 113.855 | 123.7427 | 2.7283 | 123.7427 | 75.6226 | -0.28381 | 123.7427 | 2.7283 | 75.6226 | 113.855 | 123.7427 | -123.9853 | -124.0128
2015.7188 | 123.9029 | -61.2854 | 62.4161 | 0.39543 | 0.017092 | 0.015336 | 0.01232 | 0.06687 | 0.0054347 | 0.083108 | -58.5205 | 62.4298 | -61.5463 | -61.5143 | 52.7985 | 14.5523 | 1.2955 | 1.0483 | 62.4344 | -61.5738 | -0.26093 | 0.013733 | 2.7649 | -0.22888 | -9.6176 | -0.28839 | 0.01831 | 3.0258 | 62.5809 | 62.3337 | 114.0839 | 123.7152 | 2.7649 | 123.7198 | 75.8377 | -0.28839 | 123.7152 | 2.7649 | 75.8377 | 114.0839 | 123.7198 | -123.9624 | -123.9899
2016.7188 | 123.9212 | -61.2762 | 62.4573 | -0.14626 | 0.021364 | 0.018754 | 0.011465 | 0.06687 | 0.0020167 | 0.083322 | -58.5251 | 62.4619 | -61.5189 | -61.4365 | 52.7893 | 14.5569 | 1.3184 | 1.1353 | 62.471 | -61.5601 | -0.24261 | 0.004578 | 2.7512 | -0.16022 | -9.668 | -0.28381 | 0.013733 | 2.9938 | 62.5946 | 62.4115 | 114.0656 | 123.7381 | 2.7512 | 123.7473 | 75.8331 | -0.28381 | 123.7381 | 2.7512 | 75.8331 | 114.0656 | 123.7473 | -123.9761 | -124.0173
2017.7188 | 123.9487 | -61.29 | 62.3566 | 0.14366 | 0.015169 | 0.020036 | 0.0095424 | 0.06687 | 0.0050073 | 0.083108 | -58.5297 | 62.384 | -61.5189 | -61.4319 | 53.0273 | 14.9048 | 1.2131 | 1.1993 | 62.3978 | -61.5463 | -0.22888 | 0.027466 | 2.7603 | -0.14191 | -9.3292 | -0.25635 | 0.041199 | 2.9892 | 62.5031 | 62.4893 | 114.3173 | 123.674 | 2.7603 | 123.6877 | 76.1948 | -0.25635 | 123.674 | 2.7603 | 76.1948 | 114.3173 | 123.6877 | -123.8754 | -123.9029
2018.7188 | 123.8525 | -61.3129 | 62.4573 | -0.23781 | 0.015597 | 0.017259 | 0.0056972 | 0.062171 | 0.0041529 | 0.083322 | -58.6029 | 62.4481 | -61.528 | -61.5829 | 52.8717 | 14.6118 | 1.5289 | 1.2177 | 62.4527 | -61.5738 | -0.21515 | -0.009155 | 2.71 | -0.27008 | -9.5856 | -0.26093 | -0.004577 | 2.9251 | 62.8418 | 62.5305 | 114.1846 | 123.761 | 2.71 | 123.7656 | 75.9247 | -0.26093 | 123.761 | 2.71 | 75.9247 | 114.1846 | 123.7656 | -123.9853 | -124.0311
2019.7188 | 123.9441 | -61.2579 | 62.4527 | -0.1844 | 0.020083 | 0.014909 | 0.010611 | 0.064307 | 0.0024439 | 0.083535 | -58.5022 | 62.4481 | -61.5372 | -61.441 | 52.8992 | 14.7491 | 1.6342 | 1.4191 | 62.4573 | -61.5509 | -0.27923 | -0.004578 | 2.7557 | -0.1831 | -9.5535 | -0.29297 | 0.004577 | 3.035 | 62.8922 | 62.677 | 114.1571 | 123.7061 | 2.7557 | 123.7152 | 76.0071 | -0.29297 | 123.7061 | 2.7557 | 76.0071 | 114.1571 | 123.7152 | -123.9899 | -124.0036
2020.7344 | 123.88 | -61.3129 | 62.439 | 0.18944 | 0.016665 | 0.020249 | 0.01296 | 0.066657 | 0.0020167 | 0.08439 | -58.6853 | 62.4298 | -61.5509 | -61.528 | 52.7618 | 14.6118 | 1.4877 | 1.2451 | 62.4344 | -61.5738 | -0.23804 | -0.009155 | 2.6276 | -0.21515 | -9.6771 | -0.26093 | -0.004578 | 2.8656 | 62.8006 | 62.558 | 114.0747 | 123.7427 | 2.6276 | 123.7473 | 75.9247 | -0.26093 | 123.7427 | 2.6276 | 75.9247 | 114.0747 | 123.7473 | -123.9899 | -124.0128
2021.7188 | 123.9075 | -61.3037 | 62.471 | -0.23018 | 0.016024 | 0.015122 | 0.0084744 | 0.064948 | 0.0022303 | 0.083535 | -58.5709 | 62.4115 | -61.5326 | -61.4914 | 52.5925 | 14.9918 | 1.9592 | 1.3779 | 62.5031 | -61.528 | -0.22888 | -0.059509 | 2.7328 | -0.18768 | -9.8785 | -0.2243 | 0.032044 | 2.9617 | 63.2629 | 62.6816 | 113.8962 | 123.7152 | 2.7328 | 123.8068 | 76.2955 | -0.2243 | 123.7152 | 2.7328 | 76.2955 | 113.8962 | 123.8068 | -124.0036 | -123.999
2022.7188 | 123.8525 | -61.2854 | 62.4756 | -0.3904 | 0.016024 | 0.016404 | 0.012747 | 0.064734 | 0.0020167 | 0.082681 | -58.5205 | 62.4207 | -61.5326 | -61.5005 | 52.7985 | 14.9048 | 1.886 | 1.3275 | 62.4527 | -61.5509 | -0.24719 | -0.054932 | 2.7649 | -0.21515 | -9.6771 | -0.2655 | -0.022888 | 3.0121 | 63.1714 | 62.6129 | 114.0839 | 123.7061 | 2.7649 | 123.7381 | 76.1902 | -0.2655 | 123.7061 | 2.7649 | 76.1902 | 114.0839 | 123.7381 | -124.0082 | -124.0265
2023.7188 | 123.9349 | -61.29 | 62.4481 | -0.16151 | 0.018587 | 0.020249 | 0.013601 | 0.065161 | 0.0028711 | 0.084603 | -58.493 | 62.4298 | -61.5051 | -61.4227 | 52.7985 | 14.9963 | 1.9043 | 1.3962 | 62.4435 | -61.5463 | -0.21515 | -0.01831 | 2.7969 | -0.13275 | -9.6497 | -0.25635 | -0.004578 | 3.0121 | 63.1943 | 62.6862 | 114.0884 | 123.7198 | 2.7969 | 123.7335 | 76.2863 | -0.25635 | 123.7198 | 2.7969 | 76.2863 | 114.0884 | 123.7335 | -123.9532 | -123.9944
2024.7344 | 123.9258 | -61.3083 | 62.4023 | 0.14366 | 0.016665 | 0.020249 | 0.012747 | 0.065802 | 0.0041529 | 0.084176 | -58.5892 | 62.4207 | -61.5509 | -61.5189 | 52.8442 | 15.0192 | 1.7212 | 1.3412 | 62.3886 | -61.5829 | -0.24261 | 0.01831 | 2.7191 | -0.21057 | -9.5581 | -0.27466 | -0.013733 | 2.9617 | 63.0295 | 62.6495 | 114.1525 | 123.7289 | 2.7191 | 123.6969 | 76.3275 | -0.27466 | 123.7289 | 2.7191 | 76.3275 | 114.1525 | 123.6969 | -123.9532 | -123.9853
2025.7188 | 123.88 | -61.2671 | 62.4664 | -0.26833 | 0.016024 | 0.017259 | 0.0076198 | 0.062598 | 0.00073487 | 0.081826 | -58.5617 | 62.4115 | -61.5417 | -61.4868 | 52.8946 | 15.2115 | 1.9775 | 1.4282 | 62.471 | -61.5601 | -0.27466 | -0.054932 | 2.7054 | -0.21973 | -9.5718 | -0.29297 | 0.004577 | 2.98 | 63.2446 | 62.6953 | 114.1617 | 123.6786 | 2.7054 | 123.7381 | 76.4786 | -0.29297 | 123.6786 | 2.7054 | 76.4786 | 114.1617 | 123.7381 | -124.0082 | -124.0265
2026.7344 | 123.8937 | -61.3129 | 62.4344 | 0.0063326 | 0.020083 | 0.019822 | 0.016806 | 0.065375 | 0.0026575 | 0.083322 | -58.6304 | 62.439 | -61.5326 | -61.4777 | 52.7939 | 15.0833 | 1.8173 | 1.3046 | 62.3978 | -61.5738 | -0.21973 | 0.004578 | 2.6825 | -0.16479 | -9.6405 | -0.26093 | -0.036621 | 2.9022 | 63.1302 | 62.6175 | 114.1068 | 123.7518 | 2.6825 | 123.7106 | 76.3962 | -0.26093 | 123.7518 | 2.6825 | 76.3962 | 114.1068 | 123.7106 | -123.967 | -124.0082
2027.7188 | 123.9029 | -61.2671 | 62.4619 | -0.21492 | 0.015597 | 0.017259 | 0.011251 | 0.062812 | 0.0026575 | 0.08204 | -58.6304 | 62.4527 | -61.5372 | -61.4868 | 52.7985 | 14.9963 | 1.767 | 1.3092 | 62.4573 | -61.5372 | -0.27008 | -0.009155 | 2.6367 | -0.21973 | -9.6634 | -0.27008 | -0.004578 | 2.9068 | 63.0341 | 62.5763 | 114.0656 | 123.7198 | 2.6367 | 123.7244 | 76.2634 | -0.27008 | 123.7198 | 2.6367 | 76.2634 | 114.0656 | 123.7244 | -123.999 | -123.999
2028.7188 | 123.9761 | -61.2717 | 62.4435 | -0.10048 | 0.01346 | 0.015763 | 0.0076198 | 0.065589 | -0.00033333 | 0.083749 | -58.548 | 62.352 | -61.4868 | -61.409 | 52.89 | 15.2344 | 1.8311 | 1.506 | 62.4115 | -61.5097 | -0.21515 | -0.091552 | 2.7237 | -0.13733 | -9.5535 | -0.23804 | -0.032043 | 2.9388 | 63.1027 | 62.7777 | 114.1617 | 123.6237 | 2.7237 | 123.6832 | 76.506 | -0.23804 | 123.6237 | 2.7237 | 76.506 | 114.1617 | 123.6832 | -123.9304 | -123.9532
2029.7344 | 123.999 | -61.2579 | 62.4161 | -0.031814 | 0.014101 | 0.013841 | 0.005911 | 0.061103 | 0.0022303 | 0.082253 | -58.5434 | 62.3245 | -61.5555 | -61.4731 | 52.8671 | 15.3305 | 1.9226 | 1.5381 | 62.3703 | -61.5189 | -0.29755 | -0.091553 | 2.7145 | -0.21515 | -9.549 | -0.26092 | -0.045777 | 3.0121 | 63.1805 | 62.796 | 114.1251 | 123.5825 | 2.7145 | 123.6282 | 76.5884 | -0.26092 | 123.5825 | 2.7145 | 76.5884 | 114.1251 | 123.6282 | -123.9716 | -123.9349
2030.7188 | 124.0082 | -61.2488 | 62.4344 | 0.39543 | 0.014742 | 0.015763 | 0.0078336 | 0.061743 | -0.00054693 | 0.084176 | -58.6624 | 62.3383 | -61.528 | -61.4136 | 52.8625 | 15.4358 | 1.767 | 1.5198 | 62.384 | -61.5051 | -0.27924 | -0.09613 | 2.5864 | -0.16479 | -9.5718 | -0.25635 | -0.050354 | 2.8656 | 63.0157 | 62.7686 | 114.1113 | 123.587 | 2.5864 | 123.6328 | 76.6846 | -0.25635 | 123.587 | 2.5864 | 76.6846 | 114.1113 | 123.6328 | -123.9624 | -123.9395
2031.7188 | 123.9441 | -61.2579 | 62.4161 | -0.1844 | 0.012179 | 0.01555 | 0.0080472 | 0.059607 | 0.0035121 | 0.08204 | -58.4564 | 62.3337 | -61.4868 | -61.1847 | 53.2562 | 15.5685 | 1.3916 | 1.5015 | 62.3611 | -61.5143 | -0.22888 | -0.082398 | 2.8015 | 0.073243 | -9.1599 | -0.25635 | -0.054932 | 3.0304 | 62.6495 | 62.7594 | 114.5142 | 123.5916 | 2.8015 | 123.6191 | 76.8265 | -0.25635 | 123.5916 | 2.8015 | 76.8265 | 114.5142 | 123.6191 | -123.9029 | -123.9304
2032.7188 | 123.8983 | -61.2991 | 62.4435 | -0.19203 | 0.017519 | 0.017472 | 0.015097 | 0.063239 | 0.0037257 | 0.081613 | -58.699 | 62.4619 | -61.5234 | -61.4777 | 52.9449 | 15.2435 | 1.8448 | 1.4053 | 62.4344 | -61.5646 | -0.2243 | 0.018311 | 2.6001 | -0.17853 | -9.4986 | -0.2655 | -0.009155 | 2.8244 | 63.1439 | 62.7045 | 114.2441 | 123.761 | 2.6001 | 123.7335 | 76.5427 | -0.2655 | 123.761 | 2.6001 | 76.5427 | 114.2441 | 123.7335 | -123.967 | -124.0082
2033.7188 | 123.9853 | -61.2534 | 62.4298 | 0.60143 | 0.015597 | 0.015336 | 0.0082608 | 0.061103 | 0.00094847 | 0.083108 | -58.493 | 62.352 | -61.5189 | -61.3861 | 52.977 | 15.3809 | 1.6754 | 1.4694 | 62.3932 | -61.4868 | -0.2655 | -0.07782 | 2.7603 | -0.13275 | -9.4528 | -0.23346 | -0.036622 | 3.0258 | 62.9288 | 62.7228 | 114.2303 | 123.6053 | 2.7603 | 123.6465 | 76.6342 | -0.23346 | 123.6053 | 2.7603 | 76.6342 | 114.2303 | 123.6465 | -123.9487 | -123.9166
2034.7344 | 123.8754 | -61.2946 | 62.4344 | 0.04448 | 0.016665 | 0.016831 | 0.015738 | 0.065375 | 0.0013757 | 0.081826 | -58.493 | 62.4252 | -61.5555 | -61.496 | 52.7939 | 15.2618 | 1.8494 | 1.2863 | 62.4023 | -61.5738 | -0.26093 | -0.009155 | 2.8015 | -0.20142 | -9.6405 | -0.27924 | -0.032043 | 3.0624 | 63.1439 | 62.5809 | 114.0884 | 123.7198 | 2.8015 | 123.6969 | 76.5564 | -0.27924 | 123.7198 | 2.8015 | 76.5564 | 114.0884 | 123.6969 | -123.9899 | -124.0082
2035.7188 | 123.9166 | -61.2762 | 62.4344 | -0.13863 | 0.016024 | 0.01854 | 0.015951 | 0.063239 | 0.00052127 | 0.083108 | -58.4381 | 62.4573 | -61.528 | -61.4319 | 52.8946 | 15.4404 | 1.8219 | 1.3687 | 62.4481 | -61.5234 | -0.25177 | 0.022888 | 2.8381 | -0.15564 | -9.5398 | -0.24719 | 0.013733 | 3.0899 | 63.0981 | 62.645 | 114.1708 | 123.7335 | 2.8381 | 123.7244 | 76.7166 | -0.24719 | 123.7335 | 2.8381 | 76.7166 | 114.1708 | 123.7244 | -123.9624 | -123.9578
2036.7188 | 124.0585 | -61.2305 | 62.5031 | -0.16914 | 0.015383 | 0.012132 | 0.0078336 | 0.063666 | 0.00094847 | 0.082253 | -58.4976 | 62.3383 | -61.5326 | -61.3678 | 53.0594 | 15.3168 | 1.6983 | 1.4786 | 62.3886 | -61.4685 | -0.30212 | -0.16479 | 2.7328 | -0.13733 | -9.4437 | -0.23804 | -0.11444 | 3.035 | 62.9288 | 62.709 | 114.2899 | 123.5687 | 2.7328 | 123.6191 | 76.5472 | -0.23804 | 123.5687 | 2.7328 | 76.5472 | 114.2899 | 123.6191 | -124.0356 | -123.9716
2037.7188 | 124.0128 | -61.2625 | 62.4023 | -0.11574 | 0.014315 | 0.013413 | 0.0080472 | 0.060462 | 0.00052127 | 0.083322 | -58.5297 | 62.3016 | -61.4868 | -61.3724 | 53.1143 | 15.3488 | 1.6571 | 1.4877 | 62.3749 | -61.496 | -0.2243 | -0.10071 | 2.7328 | -0.10986 | -9.288 | -0.23346 | -0.027466 | 2.9572 | 62.9196 | 62.7502 | 114.3768 | 123.5641 | 2.7328 | 123.6374 | 76.6113 | -0.23346 | 123.5641 | 2.7328 | 76.6113 | 114.3768 | 123.6374 | -123.8892 | -123.8983
2038.7188 | 123.9166 | -61.2808 | 62.4435 | -0.29121 | 0.017519 | 0.013627 | 0.014669 | 0.063666 | 0.0024439 | 0.081185 | -58.4702 | 62.4573 | -61.5326 | -61.4365 | 52.9221 | 15.1566 | 1.8814 | 1.4145 | 62.439 | -61.5555 | -0.25177 | 0.013733 | 2.8107 | -0.15564 | -9.5215 | -0.27466 | -0.004577 | 3.0624 | 63.1622 | 62.6953 | 114.2029 | 123.7381 | 2.8107 | 123.7198 | 76.4374 | -0.27466 | 123.7381 | 2.8107 | 76.4374 | 114.2029 | 123.7198 | -123.9761 | -123.999
2039.7344 | 123.8709 | -61.3037 | 62.4344 | 0.0063326 | 0.019442 | 0.01854 | 0.016165 | 0.063452 | 0.0020167 | 0.080972 | -58.6121 | 62.4298 | -61.5372 | -61.5097 | 53.0777 | 15.2161 | 1.8677 | 1.2726 | 62.4161 | -61.5784 | -0.23346 | -0.004577 | 2.6917 | -0.20599 | -9.3567 | -0.27466 | -0.01831 | 2.9251 | 63.1714 | 62.5763 | 114.3814 | 123.7335 | 2.6917 | 123.7198 | 76.5198 | -0.27466 | 123.7335 | 2.6917 | 76.5198 | 114.3814 | 123.7198 | -123.9716 | -124.0128
2040.7188 | 123.8937 | -61.29 | 62.4573 | 0.14366 | 0.016024 | 0.016404 | 0.010397 | 0.064734 | 0.0018031 | 0.082467 | -58.6029 | 62.4481 | -61.5601 | -61.4868 | 53.009 | 15.2161 | 1.8265 | 1.2955 | 62.471 | -61.5646 | -0.27008 | -0.009155 | 2.6871 | -0.19684 | -9.4482 | -0.27466 | 0.013733 | 2.9572 | 63.1165 | 62.5854 | 114.299 | 123.7381 | 2.6871 | 123.761 | 76.506 | -0.27466 | 123.7381 | 2.6871 | 76.506 | 114.299 | 123.761 | -124.0173 | -124.0219
2041.7188 | 123.999 | -61.2488 | 62.4207 | -0.22255 | 0.013674 | 0.015763 | 0.012106 | 0.064093 | 0.0018031 | 0.083749 | -58.7265 | 62.3428 | -61.5005 | -61.4502 | 53.0045 | 15.3442 | 1.6983 | 1.4557 | 62.3932 | -61.4914 | -0.25177 | -0.07782 | 2.5223 | -0.20142 | -9.4162 | -0.24262 | -0.027466 | 2.774 | 62.9471 | 62.7045 | 114.2532 | 123.5916 | 2.5223 | 123.642 | 76.593 | -0.24262 | 123.5916 | 2.5223 | 76.593 | 114.2532 | 123.642 | -123.9212 | -123.912
2042.7188 | 123.9944 | -61.2396 | 62.4252 | -0.20729 | 0.014956 | 0.010209 | 0.0061246 | 0.059821 | 0.0060755 | 0.084176 | -58.4793 | 62.3245 | -61.5189 | -61.5463 | 52.7893 | 15.2298 | 1.5427 | 1.4832 | 62.3657 | -61.5189 | -0.27924 | -0.10071 | 2.7603 | -0.3067 | -9.6359 | -0.27924 | -0.059509 | 3.0396 | 62.7823 | 62.7228 | 114.0289 | 123.5641 | 2.7603 | 123.6053 | 76.4694 | -0.27924 | 123.5641 | 2.7603 | 76.4694 | 114.0289 | 123.6053 | -123.9441 | -123.9441
2043.7188 | 123.9349 | -61.2762 | 62.4573 | -0.23018 | 0.016451 | 0.014909 | 0.017019 | 0.063239 | 0.0011621 | 0.083535 | -58.5526 | 62.4115 | -61.5463 | -61.4319 | 52.4963 | 15.065 | 1.8494 | 1.3641 | 62.4115 | -61.5555 | -0.27008 | -0.045776 | 2.7237 | -0.15564 | -9.9609 | -0.27924 | -0.045776 | 2.9938 | 63.1256 | 62.6404 | 113.7726 | 123.6877 | 2.7237 | 123.6877 | 76.3412 | -0.27924 | 123.6877 | 2.7237 | 76.3412 | 113.7726 | 123.6877 | -124.0036 | -124.0128
2044.7188 | 123.9578 | -61.2671 | 62.4115 | -0.19203 | 0.015597 | 0.013841 | 0.0080472 | 0.062171 | 0.0011621 | 0.073922 | -58.8867 | 62.3383 | -61.5005 | -61.084 | 53.1647 | 15.2435 | 1.561 | 1.5564 | 62.3795 | -61.4914 | -0.23346 | -0.073242 | 2.3804 | 0.18311 | -9.2468 | -0.2243 | -0.032043 | 2.6138 | 62.8281 | 62.8235 | 114.4318 | 123.6053 | 2.3804 | 123.6465 | 76.5106 | -0.2243 | 123.6053 | 2.3804 | 76.5106 | 114.4318 | 123.6465 | -123.912 | -123.9029
2045.7188 | 123.8709 | -61.3174 | 62.4435 | 0.074997 | 0.017733 | 0.022386 | 0.018301 | 0.064093 | 0.00052127 | 0.08204 | -58.5159 | 62.4344 | -61.5326 | -61.5143 | 52.7252 | 15.0604 | 1.7761 | 1.2589 | 62.4298 | -61.5692 | -0.21515 | -0.009155 | 2.8015 | -0.19684 | -9.7183 | -0.25177 | -0.013732 | 3.0167 | 63.0936 | 62.5763 | 114.0427 | 123.7518 | 2.8015 | 123.7473 | 76.3779 | -0.25177 | 123.7518 | 2.8015 | 76.3779 | 114.0427 | 123.7473 | -123.9761 | -124.0128
2046.7188 | 124.0173 | -61.2625 | 62.4161 | -0.16914 | 0.013888 | 0.019608 | 0.0067654 | 0.06388 | 0.00094847 | 0.08439 | -58.5297 | 62.3337 | -61.5372 | -61.3724 | 52.8122 | 15.1428 | 2.3026 | 1.593 | 62.4802 | -61.4548 | -0.27466 | -0.082398 | 2.7328 | -0.10986 | -9.6039 | -0.19226 | 0.064087 | 3.0075 | 63.5651 | 62.8555 | 114.0747 | 123.5962 | 2.7328 | 123.7427 | 76.4053 | -0.19226 | 123.5962 | 2.7328 | 76.4053 | 114.0747 | 123.7427 | -123.9532 | -123.8709
2047.7188 | 123.8983 | -61.29 | 62.4756 | -0.25307 | 0.016665 | 0.0132 | 0.010824 | 0.060034 | 0.0026575 | 0.082467 | -58.4656 | 62.3611 | -61.5372 | -61.4594 | 52.9129 | 15.3305 | 1.9592 | 1.3962 | 62.3932 | -61.5372 | -0.24719 | -0.11444 | 2.8244 | -0.16937 | -9.5627 | -0.24719 | -0.082398 | 3.0716 | 63.2492 | 62.6862 | 114.2029 | 123.6511 | 2.8244 | 123.6832 | 76.6205 | -0.24719 | 123.6511 | 2.8244 | 76.6205 | 114.2029 | 123.6832 | -124.0128 | -124.0128
2048.7188 | 123.9166 | -61.2762 | 62.439 | 0.1284 | 0.016238 | 0.018113 | 0.014883 | 0.063025 | 0.0011621 | 0.081613 | -58.4518 | 62.4023 | -61.5509 | -61.441 | 52.9633 | 15.4861 | 1.8082 | 1.4648 | 62.3978 | -61.5463 | -0.27466 | -0.036621 | 2.8244 | -0.16479 | -9.4757 | -0.27008 | -0.041199 | 3.0991 | 63.0844 | 62.7411 | 114.2395 | 123.6786 | 2.8244 | 123.674 | 76.7624 | -0.27008 | 123.6786 | 2.8244 | 76.7624 | 114.2395 | 123.674 | -123.9899 | -123.9853
2049.7188 | 124.0082 | -61.2442 | 62.4207 | -0.21492 | 0.012392 | 0.019181 | 0.010824 | 0.063666 | 0.0013757 | 0.080544 | -58.5159 | 62.3245 | -61.5143 | -61.409 | 53.27 | 15.5136 | 1.9089 | 1.7349 | 62.4023 | -61.5051 | -0.27008 | -0.09613 | 2.7283 | -0.16479 | -9.1507 | -0.26093 | -0.01831 | 2.9984 | 63.1531 | 62.9791 | 114.5142 | 123.5687 | 2.7283 | 123.6465 | 76.7578 | -0.26093 | 123.5687 | 2.7283 | 76.7578 | 114.5142 | 123.6465 | -123.9349 | -123.9258
2050.7188 | 123.9075 | -61.3129 | 62.439 | -0.131 | 0.01581 | 0.018113 | 0.014669 | 0.064093 | 0.00094847 | 0.080544 | -58.5754 | 62.4344 | -61.5326 | -61.4227 | 53.0869 | 15.5594 | 1.9409 | 1.5335 | 62.4161 | -61.5555 | -0.21973 | -0.004578 | 2.7374 | -0.10986 | -9.3521 | -0.24262 | -0.022888 | 2.9572 | 63.2538 | 62.8464 | 114.3997 | 123.7473 | 2.7374 | 123.7289 | 76.8723 | -0.24262 | 123.7473 | 2.7374 | 76.8723 | 114.3997 | 123.7289 | -123.9716 | -123.9944
2051.7188 | 123.9487 | -61.2671 | 62.4939 | -0.23018 | 0.016238 | 0.013627 | 0.011038 | 0.062598 | -0.00097413 | 0.083322 | -58.8135 | 62.3978 | -61.528 | -61.4777 | 52.977 | 15.5685 | 2.0325 | 1.5289 | 62.439 | -61.528 | -0.26093 | -0.09613 | 2.4536 | -0.21057 | -9.5169 | -0.26093 | -0.054931 | 2.7145 | 63.2996 | 62.796 | 114.2441 | 123.6649 | 2.4536 | 123.7061 | 76.8356 | -0.26093 | 123.6649 | 2.4536 | 76.8356 | 114.2441 | 123.7061 | -124.0219 | -124.0219
2052.7188 | 123.9075 | -61.3083 | 62.4298 | -0.20729 | 0.016665 | 0.014268 | 0.010824 | 0.062384 | 0.0011621 | 0.081185 | -58.5388 | 62.4207 | -61.5417 | -61.4731 | 53.2333 | 15.6143 | 1.8951 | 1.4786 | 62.4207 | -61.5417 | -0.23346 | -0.009156 | 2.7695 | -0.16479 | -9.1965 | -0.23346 | -0.009156 | 3.0029 | 63.2034 | 62.7869 | 114.5416 | 123.7289 | 2.7695 | 123.7289 | 76.9226 | -0.23346 | 123.7289 | 2.7695 | 76.9226 | 114.5416 | 123.7289 | -123.9716 | -123.9716
2053.7344 | 123.8617 | -61.2991 | 62.4435 | 0.059738 | 0.018587 | 0.015763 | 0.015738 | 0.065589 | 0.0015893 | 0.081185 | -58.58 | 62.4161 | -61.5417 | -61.5097 | 53.0228 | 15.2847 | 1.6113 | 1.3229 | 62.4069 | -61.5738 | -0.24262 | -0.027465 | 2.7191 | -0.21057 | -9.4208 | -0.27466 | -0.036621 | 2.9617 | 62.9105 | 62.6221 | 114.3219 | 123.7152 | 2.7191 | 123.7061 | 76.5839 | -0.27466 | 123.7152 | 2.7191 | 76.5839 | 114.3219 | 123.7061 | -123.9853 | -124.0173
2054.7188 | 123.9304 | -61.2579 | 62.439 | -0.19966 | 0.016878 | 0.012345 | 0.0074062 | 0.065161 | 0.0020167 | 0.082467 | -58.6761 | 62.3795 | -61.5417 | -61.4136 | 53.2013 | 15.6509 | 1.561 | 1.4786 | 62.4161 | -61.4868 | -0.28381 | -0.059509 | 2.5818 | -0.15564 | -9.2377 | -0.22888 | -0.022888 | 2.8656 | 62.8189 | 62.7365 | 114.4592 | 123.6374 | 2.5818 | 123.674 | 76.9089 | -0.22888 | 123.6374 | 2.5818 | 76.9089 | 114.4592 | 123.674 | -123.9807 | -123.9258
2055.7188 | 123.9258 | -61.2762 | 62.4435 | -0.131 | 0.016665 | 0.012132 | 0.014883 | 0.065161 | 0.0020167 | 0.080758 | -58.5068 | 62.4344 | -61.5372 | -61.441 | 53.1372 | 15.4953 | 1.7029 | 1.4969 | 62.4115 | -61.5555 | -0.26093 | -0.009155 | 2.7695 | -0.16479 | -9.3063 | -0.27924 | -0.032043 | 3.0304 | 62.9791 | 62.7731 | 114.4135 | 123.7106 | 2.7695 | 123.6877 | 76.7715 | -0.27924 | 123.7106 | 2.7695 | 76.7715 | 114.4135 | 123.6877 | -123.9807 | -123.999
2056.7188 | 123.8892 | -61.2991 | 62.471 | -0.28358 | 0.014529 | 0.015336 | 0.0095424 | 0.064521 | 0.00094847 | 0.081613 | -58.5571 | 62.4023 | -61.5326 | -61.4777 | 53.2654 | 15.564 | 1.7258 | 1.3824 | 62.4527 | -61.5417 | -0.23346 | -0.068664 | 2.742 | -0.17853 | -9.2056 | -0.24262 | -0.01831 | 2.9755 | 63.0249 | 62.6816 | 114.5645 | 123.7015 | 2.742 | 123.7518 | 76.8631 | -0.24262 | 123.7015 | 2.742 | 76.8631 | 114.5645 | 123.7518 | -124.0036 | -124.0128
2057.7188 | 123.9624 | -61.2717 | 62.4481 | -0.24544 | 0.016451 | 0.016831 | 0.0089016 | 0.063025 | 0.00030767 | 0.083535 | -58.5022 | 62.3428 | -61.5372 | -61.4136 | 53.3981 | 15.7059 | 1.5472 | 1.4648 | 62.4023 | -61.5097 | -0.2655 | -0.10529 | 2.7695 | -0.14191 | -9.05 | -0.23804 | -0.045776 | 3.035 | 62.8189 | 62.7365 | 114.6698 | 123.6145 | 2.7695 | 123.674 | 76.9775 | -0.23804 | 123.6145 | 2.7695 | 76.9775 | 114.6698 | 123.674 | -123.9853 | -123.9578
2058.7188 | 123.9441 | -61.2946 | 62.4435 | -0.16151 | 0.016451 | 0.017259 | 0.01531 | 0.062171 | 0.0022303 | 0.082253 | -58.493 | 62.4344 | -61.5417 | -61.4548 | 53.3615 | 15.7516 | 1.8585 | 1.561 | 62.3932 | -61.5646 | -0.24719 | -0.009155 | 2.8015 | -0.16022 | -9.082 | -0.27008 | -0.050354 | 3.0487 | 63.1531 | 62.8555 | 114.6561 | 123.7289 | 2.8015 | 123.6877 | 77.0462 | -0.27008 | 123.7289 | 2.8015 | 77.0462 | 114.6561 | 123.6877 | -123.9853 | -124.0082
2059.7188 | 123.8937 | -61.2946 | 62.4619 | -0.26833 | 0.01581 | 0.015977 | 0.0093288 | 0.06388 | 0.0011621 | 0.083535 | -58.5846 | 62.3978 | -61.5601 | -61.4914 | 53.3386 | 15.9393 | 1.6434 | 1.4328 | 62.4298 | -61.5372 | -0.2655 | -0.064087 | 2.71 | -0.19684 | -9.1232 | -0.24261 | -0.032043 | 2.9755 | 62.9379 | 62.7274 | 114.6332 | 123.6923 | 2.71 | 123.7244 | 77.2339 | -0.24261 | 123.6923 | 2.71 | 77.2339 | 114.6332 | 123.7244 | -124.0219 | -123.999
2060.7188 | 123.9029 | -61.2717 | 62.4161 | -0.024185 | 0.017306 | 0.018968 | 0.017233 | 0.065161 | 0.00094847 | 0.082681 | -58.5663 | 62.4344 | -61.5417 | -61.4456 | 53.3249 | 15.7883 | 1.6663 | 1.4099 | 62.4115 | -61.5646 | -0.27008 | 0.01831 | 2.7054 | -0.17395 | -9.0912 | -0.29297 | -0.004578 | 2.9755 | 62.9379 | 62.6816 | 114.5966 | 123.7061 | 2.7054 | 123.6832 | 77.0599 | -0.29297 | 123.7061 | 2.7054 | 77.0599 | 114.5966 | 123.6832 | -123.9578 | -123.9807
2061.7188 | 123.8983 | -61.2946 | 62.4344 | -0.19966 | 0.015597 | 0.016618 | 0.008688 | 0.063239 | -0.00033333 | 0.083322 | -58.6761 | 62.3886 | -61.5234 | -61.4502 | 53.215 | 15.6006 | 1.5518 | 1.3504 | 62.4344 | -61.5417 | -0.22888 | -0.045776 | 2.6184 | -0.15564 | -9.2194 | -0.24719 | 0 | 2.8473 | 62.8464 | 62.645 | 114.5096 | 123.6832 | 2.6184 | 123.7289 | 76.8951 | -0.24719 | 123.6832 | 2.6184 | 76.8951 | 114.5096 | 123.7289 | -123.9578 | -123.9761
2062.7188 | 123.88 | -61.2854 | 62.4481 | -0.23781 | 0.014956 | 0.014909 | 0.010183 | 0.064521 | 0.0020167 | 0.083322 | -58.6258 | 62.3795 | -61.5326 | -61.4822 | 53.3844 | 16.0904 | 1.7212 | 1.4832 | 62.4207 | -61.5326 | -0.24719 | -0.068664 | 2.6596 | -0.19684 | -9.0637 | -0.24719 | -0.027466 | 2.9068 | 63.0066 | 62.7686 | 114.6698 | 123.6649 | 2.6596 | 123.7061 | 77.3758 | -0.24719 | 123.6649 | 2.6596 | 77.3758 | 114.6698 | 123.7061 | -123.9807 | -123.9807
2063.7344 | 123.8983 | -61.3266 | 62.4069 | 0.50987 | 0.017306 | 0.017259 | 0.014669 | 0.06388 | 0.0024439 | 0.081399 | -58.4702 | 62.4298 | -61.5646 | -61.5326 | 52.9266 | 15.5685 | 1.5015 | 1.4008 | 62.3932 | -61.5829 | -0.23804 | 0.022889 | 2.8564 | -0.20599 | -9.4803 | -0.25635 | -0.013733 | 3.0945 | 62.8281 | 62.7274 | 114.2532 | 123.7564 | 2.8564 | 123.7198 | 76.8951 | -0.25635 | 123.7564 | 2.8564 | 76.8951 | 114.2532 | 123.7198 | -123.9716 | -123.9899
2064.7188 | 123.9029 | -61.3037 | 62.4481 | -0.19966 | 0.014956 | 0.0132 | 0.0095424 | 0.063666 | 0.0030847 | 0.08439 | -58.6395 | 62.4207 | -61.5555 | -61.4914 | 53.1921 | 15.6601 | 1.8448 | 1.2634 | 62.4344 | -61.5463 | -0.25177 | -0.027466 | 2.6642 | -0.18768 | -9.256 | -0.24262 | -0.013733 | 2.916 | 63.1485 | 62.5671 | 114.4958 | 123.7244 | 2.6642 | 123.7381 | 76.9638 | -0.24262 | 123.7244 | 2.6642 | 76.9638 | 114.4958 | 123.7381 | -124.0036 | -123.9944
2065.7188 | 123.9349 | -61.2671 | 62.4481 | -0.09285 | 0.017519 | 0.021531 | 0.015951 | 0.067084 | 0.00094847 | 0.082467 | -58.5892 | 62.4115 | -61.528 | -61.3358 | 53.3295 | 15.6509 | 1.7212 | 1.5564 | 62.4069 | -61.5784 | -0.26093 | -0.036621 | 2.6779 | -0.068664 | -9.1187 | -0.31128 | -0.041199 | 2.9388 | 62.9883 | 62.8235 | 114.5966 | 123.6786 | 2.6779 | 123.674 | 76.918 | -0.31128 | 123.6786 | 2.6779 | 76.918 | 114.5966 | 123.674 | -123.9761 | -124.0265
2066.7188 | 123.9212 | -61.2671 | 62.4252 | -0.29121 | 0.016451 | 0.015977 | 0.0084744 | 0.062598 | -0.00033333 | 0.082681 | -58.4106 | 62.3657 | -61.5646 | -61.4273 | 53.2745 | 15.6784 | 1.7624 | 1.7075 | 62.4161 | -61.5234 | -0.29755 | -0.059509 | 2.8564 | -0.16022 | -9.1507 | -0.25635 | -0.009155 | 3.154 | 63.0295 | 62.9745 | 114.5416 | 123.6328 | 2.8564 | 123.6832 | 76.9455 | -0.25635 | 123.6328 | 2.8564 | 76.9455 | 114.5416 | 123.6832 | -123.9899 | -123.9487
2067.7188 | 123.9532 | -61.29 | 62.4481 | -0.20729 | 0.014956 | 0.015122 | 0.010183 | 0.063025 | -0.00011953 | 0.083749 | -58.5526 | 62.3932 | -61.5143 | -61.4182 | 53.3157 | 15.9027 | 1.767 | 1.7944 | 62.4069 | -61.5463 | -0.2243 | -0.054932 | 2.7374 | -0.12817 | -9.1324 | -0.25635 | -0.041199 | 2.9617 | 63.0569 | 63.0844 | 114.6057 | 123.6832 | 2.7374 | 123.6969 | 77.1927 | -0.25635 | 123.6832 | 2.7374 | 77.1927 | 114.6057 | 123.6969 | -123.9624 | -123.9944
2068.7188 | 123.9258 | -61.3083 | 62.4527 | -0.062332 | 0.017306 | 0.017899 | 0.01766 | 0.061743 | 0.00073487 | 0.084176 | -58.5114 | 62.4252 | -61.5372 | -61.4639 | 53.4302 | 15.7288 | 1.8173 | 1.712 | 62.4069 | -61.5921 | -0.22888 | -0.027466 | 2.7969 | -0.15564 | -9.0225 | -0.28381 | -0.045777 | 3.0258 | 63.1256 | 63.0203 | 114.7385 | 123.7335 | 2.7969 | 123.7152 | 77.037 | -0.28381 | 123.7335 | 2.7969 | 77.037 | 114.7385 | 123.7152 | -123.9899 | -124.0448
2069.7188 | 123.8846 | -61.2854 | 62.439 | -0.19203 | 0.014529 | 0.016191 | 0.011465 | 0.062812 | 0.0024439 | 0.08439 | -58.6578 | 62.4023 | -61.5784 | -61.4914 | 53.5583 | 15.8112 | 1.8951 | 1.7029 | 62.4161 | -61.5509 | -0.29297 | -0.036621 | 2.6276 | -0.20599 | -8.8806 | -0.2655 | -0.022888 | 2.9205 | 63.1805 | 62.9883 | 114.8438 | 123.6877 | 2.6276 | 123.7015 | 77.0966 | -0.2655 | 123.6877 | 2.6276 | 77.0966 | 114.8438 | 123.7015 | -124.0173 | -123.9899
2070.7188 | 123.8846 | -61.3083 | 62.4344 | 0.94475 | 0.015383 | 0.014695 | 0.013388 | 0.062384 | -0.0014013 | 0.082467 | -58.8409 | 62.4069 | -61.5784 | -61.4868 | 53.4897 | 15.8981 | 1.7532 | 1.593 | 62.4252 | -61.5509 | -0.27008 | -0.027466 | 2.4673 | -0.17853 | -8.9447 | -0.24261 | -0.009155 | 2.7374 | 63.0615 | 62.9013 | 114.798 | 123.7152 | 2.4673 | 123.7335 | 77.2064 | -0.24261 | 123.7152 | 2.4673 | 77.2064 | 114.798 | 123.7335 | -124.0128 | -123.9853
2071.7188 | 123.8892 | -61.2854 | 62.4573 | -0.33699 | 0.015383 | 0.019822 | 0.0084744 | 0.065161 | 0.0018031 | 0.081613 | -58.5754 | 62.384 | -61.5509 | -61.4822 | 53.4393 | 16.04 | 1.7944 | 1.7303 | 62.4435 | -61.5372 | -0.2655 | -0.073242 | 2.71 | -0.19684 | -9.0179 | -0.25177 | -0.013733 | 2.9755 | 63.0798 | 63.0157 | 114.7247 | 123.6694 | 2.71 | 123.7289 | 77.3254 | -0.25177 | 123.6694 | 2.71 | 77.3254 | 114.7247 | 123.7289 | -124.0082 | -123.9944
2072.7188 | 123.9212 | -61.2717 | 62.4619 | -0.20729 | 0.01816 | 0.019608 | 0.014029 | 0.062812 | 0.0024439 | 0.081826 | -58.6807 | 62.4481 | -61.5417 | -61.4914 | 53.4576 | 16.0355 | 1.7899 | 1.7944 | 62.4207 | -61.5601 | -0.27008 | -0.013733 | 2.5909 | -0.21973 | -9.0042 | -0.28839 | -0.041199 | 2.861 | 63.0615 | 63.0661 | 114.7293 | 123.7198 | 2.5909 | 123.6923 | 77.3071 | -0.28839 | 123.7198 | 2.5909 | 77.3071 | 114.7293 | 123.6923 | -124.0036 | -124.0219
2073.7188 | 123.9212 | -61.3083 | 62.4161 | -0.12337 | 0.016878 | 0.016404 | 0.016806 | 0.064093 | 0.0015893 | 0.082681 | -58.5846 | 62.4207 | -61.5509 | -61.4548 | 53.508 | 15.9485 | 1.9363 | 1.8906 | 62.3978 | -61.5601 | -0.24261 | 0.004577 | 2.7237 | -0.14648 | -8.9081 | -0.25177 | -0.018311 | 2.9663 | 63.2446 | 63.1989 | 114.8163 | 123.7289 | 2.7237 | 123.7061 | 77.2568 | -0.25177 | 123.7289 | 2.7237 | 77.2568 | 114.8163 | 123.7061 | -123.967 | -123.9761
2074.7188 | 123.8709 | -61.3037 | 62.4435 | -0.26833 | 0.015169 | 0.019822 | 0.0093288 | 0.063239 | -0.00054693 | 0.083108 | -58.5754 | 62.3886 | -61.5463 | -61.4685 | 53.3249 | 15.8432 | 1.8219 | 1.7624 | 62.4481 | -61.5234 | -0.24262 | -0.054931 | 2.7283 | -0.16479 | -9.1187 | -0.21973 | 0.004578 | 2.9709 | 63.1256 | 63.0661 | 114.6286 | 123.6923 | 2.7283 | 123.7518 | 77.1469 | -0.21973 | 123.6923 | 2.7283 | 77.1469 | 114.6286 | 123.7518 | -123.9899 | -123.967
2075.7188 | 123.8709 | -61.3266 | 62.4298 | 0.03685 | 0.019228 | 0.020036 | 0.015738 | 0.063666 | 0.00073487 | 0.082894 | -58.5342 | 62.4069 | -61.5417 | -61.5097 | 53.4073 | 15.8661 | 1.8402 | 1.7212 | 62.3978 | -61.5921 | -0.21515 | -0.022889 | 2.7924 | -0.18311 | -9.0225 | -0.2655 | -0.032044 | 3.0075 | 63.1668 | 63.0478 | 114.7339 | 123.7335 | 2.7924 | 123.7244 | 77.1927 | -0.2655 | 123.7335 | 2.7924 | 77.1927 | 114.7339 | 123.7244 | -123.9716 | -124.0219
2076.7188 | 123.88 | -61.3083 | 62.4252 | -0.25307 | 0.015597 | 0.014695 | 0.013388 | 0.062384 | 0.0022303 | 0.084817 | -58.699 | 62.4207 | -61.5738 | -61.496 | 53.5126 | 15.9073 | 1.9684 | 1.8082 | 62.4435 | -61.5738 | -0.2655 | -0.004578 | 2.6093 | -0.18768 | -8.9127 | -0.2655 | 0.01831 | 2.8748 | 63.2767 | 63.1165 | 114.8209 | 123.7289 | 2.6093 | 123.7518 | 77.2156 | -0.2655 | 123.7289 | 2.6093 | 77.2156 | 114.8209 | 123.7518 | -123.999 | -123.999
2077.7188 | 123.7976 | -61.2946 | 62.4573 | -0.22255 | 0.014742 | 0.011491 | 0.011465 | 0.064948 | -0.00097413 | 0.082894 | -58.5938 | 62.4161 | -61.5692 | -61.5097 | 53.5446 | 16.1224 | 2.1835 | 2.1378 | 62.4664 | -61.5097 | -0.27466 | -0.041198 | 2.7008 | -0.21515 | -8.9127 | -0.21515 | 0.009156 | 2.9755 | 63.4781 | 63.4323 | 114.8392 | 123.7106 | 2.7008 | 123.761 | 77.417 | -0.21515 | 123.7106 | 2.7008 | 77.417 | 114.8392 | 123.761 | -124.0265 | -123.967
2078.7188 | 123.8754 | -61.3312 | 62.4344 | 0.04448 | 0.019015 | 0.020677 | 0.016378 | 0.064521 | 0.0022303 | 0.083322 | -59.2072 | 62.4207 | -61.5555 | -61.5646 | 53.302 | 15.9119 | 2.1606 | 1.8723 | 62.4023 | -61.5829 | -0.2243 | -0.013733 | 2.124 | -0.23346 | -9.1324 | -0.25177 | -0.032043 | 2.3483 | 63.4918 | 63.2034 | 114.6332 | 123.7518 | 2.124 | 123.7335 | 77.243 | -0.25177 | 123.7518 | 2.124 | 77.243 | 114.6332 | 123.7335 | -123.9899 | -124.0173
2079.7188 | 123.8937 | -61.2991 | 62.4207 | -0.16914 | 0.017733 | 0.016831 | 0.011679 | 0.065589 | 0.0018031 | 0.081826 | -58.6304 | 62.3886 | -61.5463 | -61.5097 | 53.4805 | 16.0492 | 2.1561 | 1.9135 | 62.4344 | -61.5738 | -0.24719 | -0.032043 | 2.6688 | -0.21057 | -8.9401 | -0.27466 | 0.013733 | 2.916 | 63.4552 | 63.2126 | 114.7797 | 123.6877 | 2.6688 | 123.7335 | 77.3483 | -0.27466 | 123.6877 | 2.6688 | 77.3483 | 114.7797 | 123.7335 | -123.967 | -123.9944
2080.7188 | 123.8663 | -61.3037 | 62.4527 | -0.20729 | 0.01816 | 0.014909 | 0.010611 | 0.064307 | -0.00054693 | 0.080758 | -58.6853 | 62.4115 | -61.5601 | -61.5005 | 53.5172 | 16.0492 | 2.1103 | 1.8539 | 62.4252 | -61.5601 | -0.25635 | -0.041199 | 2.6184 | -0.19684 | -8.9355 | -0.25635 | -0.027466 | 2.8748 | 63.414 | 63.1577 | 114.8209 | 123.7152 | 2.6184 | 123.7289 | 77.3529 | -0.25635 | 123.7152 | 2.6184 | 77.3529 | 114.8209 | 123.7289 | -124.0128 | -124.0128
2081.7188 | 123.88 | -61.3129 | 62.4161 | -0.88631 | 0.016024 | 0.017045 | 0.010611 | 0.063025 | -0.0016149 | 0.083108 | -58.699 | 62.4161 | -61.5646 | -61.5005 | 53.4256 | 16.0126 | 2.037 | 1.8494 | 62.4069 | -61.5509 | -0.25177 | 0 | 2.6138 | -0.18768 | -8.9905 | -0.23804 | -0.009156 | 2.8656 | 63.3499 | 63.1622 | 114.7385 | 123.7289 | 2.6138 | 123.7198 | 77.3254 | -0.23804 | 123.7289 | 2.6138 | 77.3254 | 114.7385 | 123.7198 | -123.9807 | -123.967
2082.7188 | 123.8525 | -61.2946 | 62.4344 | -0.69557 | 0.017947 | 0.021531 | 0.013815 | 0.06388 | 0.00073487 | 0.082253 | -58.8318 | 62.3978 | -61.5829 | -61.5372 | 53.4531 | 16.0995 | 2.2842 | 2.0325 | 62.4252 | -61.5509 | -0.28839 | -0.036621 | 2.4628 | -0.24261 | -8.9813 | -0.25635 | -0.009155 | 2.7512 | 63.5788 | 63.327 | 114.7476 | 123.6923 | 2.4628 | 123.7198 | 77.3941 | -0.25635 | 123.6923 | 2.4628 | 77.3941 | 114.7476 | 123.7198 | -124.0173 | -123.9853
2083.7188 | 123.8937 | -61.3174 | 62.4298 | -0.22255 | 0.016024 | 0.015977 | 0.010824 | 0.064734 | 0.0013757 | 0.083535 | -58.4839 | 62.4252 | -61.5601 | -61.496 | 53.4027 | 16.1179 | 2.2522 | 2.0233 | 62.439 | -61.5692 | -0.24262 | -0.004578 | 2.8336 | -0.17853 | -9.0271 | -0.25177 | 0.009155 | 3.0762 | 63.5696 | 63.3408 | 114.7202 | 123.7427 | 2.8336 | 123.7564 | 77.4353 | -0.25177 | 123.7427 | 2.8336 | 77.4353 | 114.7202 | 123.7564 | -123.9899 | -123.999
2084.7188 | 123.9029 | -61.322 | 62.4481 | -0.19966 | 0.017092 | 0.016618 | 0.013174 | 0.064307 | 0.0013757 | 0.081185 | -58.6578 | 62.4069 | -61.5601 | -61.496 | 53.5309 | 16.3101 | 2.1194 | 1.9684 | 62.4207 | -61.5829 | -0.23804 | -0.041199 | 2.6642 | -0.17395 | -8.9172 | -0.26093 | -0.027466 | 2.9022 | 63.4415 | 63.2904 | 114.8529 | 123.7289 | 2.6642 | 123.7427 | 77.6321 | -0.26093 | 123.7289 | 2.6642 | 77.6321 | 114.8529 | 123.7427 | -124.0082 | -124.0311
2085.7188 | 123.9166 | -61.29 | 62.4207 | -0.20729 | 0.017947 | 0.018968 | 0.013815 | 0.06623 | 0.00094847 | 0.083322 | -58.6395 | 62.4023 | -61.5555 | -61.4502 | 53.4348 | 16.1728 | 2.2202 | 2.1011 | 62.4207 | -61.5829 | -0.2655 | -0.01831 | 2.6505 | -0.16022 | -8.9859 | -0.29297 | 0 | 2.916 | 63.5101 | 63.3911 | 114.7247 | 123.6923 | 2.6505 | 123.7106 | 77.4628 | -0.29297 | 123.6923 | 2.6505 | 77.4628 | 114.7247 | 123.7106 | -123.9761 | -124.0036
2086.7188 | 123.8754 | -61.3174 | 62.4481 | -0.1844 | 0.019869 | 0.017472 | 0.0089016 | 0.065375 | 0.00094847 | 0.083535 | -58.6121 | 62.4115 | -61.5555 | -61.5051 | 53.3569 | 16.0446 | 2.1881 | 2.0462 | 62.4298 | -61.5738 | -0.23804 | -0.036621 | 2.7054 | -0.18768 | -9.0912 | -0.25635 | -0.01831 | 2.9434 | 63.5056 | 63.3636 | 114.6744 | 123.7289 | 2.7054 | 123.7473 | 77.3621 | -0.25635 | 123.7289 | 2.7054 | 77.3621 | 114.6744 | 123.7473 | -124.0036 | -124.0219
2087.7188 | 123.8525 | -61.2946 | 62.4298 | -0.1844 | 0.01581 | 0.01555 | 0.011465 | 0.062812 | 0.0022303 | 0.082467 | -58.6807 | 62.4298 | -61.5463 | -61.5051 | 53.3615 | 16.0675 | 2.2385 | 2.0966 | 62.439 | -61.5372 | -0.25177 | 0 | 2.6138 | -0.21057 | -9.0683 | -0.24261 | 0.009155 | 2.8656 | 63.533 | 63.3911 | 114.6561 | 123.7244 | 2.6138 | 123.7335 | 77.3621 | -0.24261 | 123.7244 | 2.6138 | 77.3621 | 114.6561 | 123.7335 | -123.9761 | -123.967
2088.7188 | 123.9029 | -61.3403 | 62.4298 | -0.29121 | 0.016238 | 0.017259 | 0.013815 | 0.065161 | 0.00094847 | 0.081826 | -58.6121 | 62.4115 | -61.5692 | -61.4777 | 53.302 | 16.1499 | 2.2888 | 2.1423 | 62.4252 | -61.5692 | -0.22888 | -0.018311 | 2.7283 | -0.13733 | -9.1278 | -0.22888 | -0.004578 | 2.9572 | 63.6291 | 63.4827 | 114.6423 | 123.7518 | 2.7283 | 123.7656 | 77.4902 | -0.22888 | 123.7518 | 2.7283 | 77.4902 | 114.6423 | 123.7656 | -123.999 | -123.999
2089.7188 | 123.9029 | -61.2991 | 62.4252 | -0.0012969 | 0.01581 | 0.021317 | 0.013815 | 0.065589 | 9.4068e-05 | 0.082894 | -58.7082 | 62.4298 | -61.5326 | -61.5051 | 53.2791 | 16.1865 | 2.211 | 2.1561 | 62.4023 | -61.5921 | -0.23346 | 0.004578 | 2.5909 | -0.20599 | -9.1461 | -0.29297 | -0.022888 | 2.8244 | 63.5101 | 63.4552 | 114.5782 | 123.7289 | 2.5909 | 123.7015 | 77.4857 | -0.29297 | 123.7289 | 2.5909 | 77.4857 | 114.5782 | 123.7015 | -123.9578 | -124.0173
2090.7188 | 123.9349 | -61.2762 | 62.4252 | -0.077591 | 0.015597 | 0.020463 | 0.012106 | 0.067084 | 0.00073487 | 0.081185 | -58.6166 | 62.4207 | -61.5326 | -61.4594 | 53.3615 | 16.2552 | 2.2064 | 2.1378 | 62.4023 | -61.5555 | -0.25635 | -0.004578 | 2.6596 | -0.18311 | -9.0637 | -0.27924 | -0.022888 | 2.916 | 63.4827 | 63.414 | 114.6378 | 123.6969 | 2.6596 | 123.6786 | 77.5314 | -0.27924 | 123.6969 | 2.6596 | 77.5314 | 114.6378 | 123.6786 | -123.9578 | -123.9807
2091.7188 | 123.9075 | -61.3037 | 62.4481 | -0.16151 | 0.017947 | 0.017472 | 0.013174 | 0.064307 | 0.0028711 | 0.081826 | -58.6121 | 62.4115 | -61.5601 | -61.5005 | 53.3478 | 16.0538 | 2.2751 | 2.1332 | 62.4481 | -61.5738 | -0.25635 | -0.036621 | 2.6917 | -0.19684 | -9.1003 | -0.27008 | 0 | 2.948 | 63.5788 | 63.4369 | 114.6515 | 123.7152 | 2.6917 | 123.7518 | 77.3575 | -0.27008 | 123.7152 | 2.6917 | 77.3575 | 114.6515 | 123.7518 | -124.0082 | -124.0219
2092.7188 | 123.912 | -61.29 | 62.4573 | -0.19966 | 0.016024 | 0.018113 | 0.012106 | 0.065802 | 0.0020167 | 0.082681 | -58.493 | 62.4207 | -61.5692 | -61.5097 | 53.5034 | 16.04 | 2.1835 | 2.1881 | 62.4344 | -61.5646 | -0.27924 | -0.036621 | 2.7969 | -0.21973 | -8.9539 | -0.27466 | -0.022888 | 3.0762 | 63.4735 | 63.4781 | 114.7934 | 123.7106 | 2.7969 | 123.7244 | 77.33 | -0.27466 | 123.7106 | 2.7969 | 77.33 | 114.7934 | 123.7244 | -124.0265 | -124.0219
2093.7188 | 123.9716 | -61.3083 | 62.3611 | 0.22758 | 0.016238 | 0.020463 | 0.011679 | 0.06623 | 0.0041529 | 0.083749 | -58.5159 | 62.352 | -61.5738 | -61.4914 | 53.5034 | 16.3788 | 2.0004 | 2.2156 | 62.3703 | -61.5875 | -0.2655 | -0.009155 | 2.7924 | -0.1831 | -8.8577 | -0.27923 | 0.009155 | 3.0579 | 63.3087 | 63.5239 | 114.8117 | 123.6603 | 2.7924 | 123.6786 | 77.6871 | -0.27923 | 123.6603 | 2.7924 | 77.6871 | 114.8117 | 123.6786 | -123.9349 | -123.9487
2094.7188 | 123.8617 | -61.3083 | 62.4527 | -0.20729 | 0.016878 | 0.016618 | 0.0084744 | 0.064093 | 0.0024439 | 0.07969 | -58.6487 | 62.3932 | -61.5555 | -61.5234 | 53.3844 | 16.2094 | 2.3254 | 2.2476 | 62.4252 | -61.5875 | -0.24719 | -0.05951 | 2.6596 | -0.21515 | -9.0683 | -0.27923 | -0.027466 | 2.9068 | 63.6337 | 63.5559 | 114.6927 | 123.7015 | 2.6596 | 123.7335 | 77.5177 | -0.27923 | 123.7015 | 2.6596 | 77.5177 | 114.6927 | 123.7335 | -124.0082 | -124.0402
2095.7188 | 123.9212 | -61.2991 | 62.4069 | -0.14626 | 0.018374 | 0.013413 | 0.013388 | 0.065375 | 0.0018031 | 0.081613 | -58.5938 | 62.3886 | -61.5601 | -61.4731 | 53.5172 | 16.5207 | 2.2018 | 2.2568 | 62.3474 | -61.5646 | -0.26093 | -0.01831 | 2.7054 | -0.17395 | -8.8898 | -0.2655 | -0.059509 | 2.9663 | 63.501 | 63.5559 | 114.8163 | 123.6877 | 2.7054 | 123.6465 | 77.8198 | -0.2655 | 123.6877 | 2.7054 | 77.8198 | 114.8163 | 123.6465 | -123.967 | -123.9716
2096.7188 | 123.8663 | -61.3037 | 62.4344 | -0.65742 | 0.015169 | 0.012559 | 0.0099698 | 0.065161 | 0.0018031 | 0.080972 | -58.6349 | 62.4115 | -61.5601 | -61.496 | 53.3432 | 16.4108 | 2.3438 | 2.2614 | 62.4252 | -61.5463 | -0.25635 | -0.022888 | 2.6688 | -0.19226 | -9.0912 | -0.24262 | -0.009155 | 2.9251 | 63.6475 | 63.5651 | 114.6469 | 123.7152 | 2.6688 | 123.7289 | 77.7145 | -0.24262 | 123.7152 | 2.6688 | 77.7145 | 114.6469 | 123.7289 | -123.9944 | -123.9807
2097.7188 | 123.8846 | -61.2946 | 62.4207 | -0.039444 | 0.021792 | 0.016618 | 0.013388 | 0.06687 | 0.00052127 | 0.079476 | -58.6395 | 62.3932 | -61.6013 | -61.4731 | 53.5446 | 16.4703 | 2.1652 | 2.2064 | 62.384 | -61.5601 | -0.3067 | -0.027466 | 2.655 | -0.17853 | -8.876 | -0.2655 | -0.036621 | 2.9617 | 63.4598 | 63.501 | 114.8392 | 123.6877 | 2.655 | 123.6786 | 77.7649 | -0.2655 | 123.6877 | 2.655 | 77.7649 | 114.8392 | 123.6786 | -124.0219 | -123.9807
2098.7344 | 123.9075 | -61.3266 | 62.3749 | 0.15129 | 0.016878 | 0.017259 | 0.01232 | 0.064521 | 0.00073487 | 0.08204 | -58.6258 | 62.352 | -61.5875 | -61.528 | 53.4851 | 16.4291 | 2.2156 | 2.211 | 62.3932 | -61.5829 | -0.26093 | -0.022888 | 2.7008 | -0.20142 | -8.8898 | -0.25635 | 0.01831 | 2.9617 | 63.5422 | 63.5376 | 114.8117 | 123.6786 | 2.7008 | 123.7198 | 77.7557 | -0.25635 | 123.6786 | 2.7008 | 77.7557 | 114.8117 | 123.7198 | -123.9624 | -123.9578
2099.7188 | 123.8983 | -61.3129 | 62.4481 | -0.24544 | 0.015383 | 0.017686 | 0.010183 | 0.064948 | 0.0026575 | 0.081399 | -58.5159 | 62.3795 | -61.5646 | -61.528 | 53.2928 | 16.2689 | 2.3071 | 2.2018 | 62.4298 | -61.5738 | -0.25177 | -0.068664 | 2.7969 | -0.21515 | -9.1553 | -0.26093 | -0.01831 | 3.0487 | 63.62 | 63.5147 | 114.6057 | 123.6923 | 2.7969 | 123.7427 | 77.5818 | -0.26093 | 123.6923 | 2.7969 | 77.5818 | 114.6057 | 123.7427 | -124.0128 | -124.0219
2100.7188 | 123.9029 | -61.2946 | 62.4161 | -0.047073 | 0.016878 | 0.018327 | 0.01296 | 0.06388 | 0.0043665 | 0.081826 | -58.5434 | 62.4161 | -61.5692 | -61.4731 | 53.4119 | 16.3834 | 2.3071 | 2.2705 | 62.3978 | -61.5829 | -0.27466 | 0 | 2.7512 | -0.17853 | -9.0042 | -0.28839 | -0.018311 | 3.0258 | 63.6017 | 63.5651 | 114.7064 | 123.7106 | 2.7512 | 123.6923 | 77.6779 | -0.28839 | 123.7106 | 2.7512 | 77.6779 | 114.7064 | 123.6923 | -123.9853 | -123.999
2101.7188 | 123.8983 | -61.3129 | 62.4252 | -0.20729 | 0.016451 | 0.017045 | 0.013601 | 0.063239 | 0.0015893 | 0.080758 | -58.6441 | 62.4207 | -61.5601 | -61.5051 | 53.3478 | 16.2918 | 2.33 | 2.1927 | 62.4527 | -61.5784 | -0.24719 | -0.004578 | 2.6688 | -0.19226 | -9.0775 | -0.2655 | 0.027466 | 2.916 | 63.6429 | 63.5056 | 114.6606 | 123.7335 | 2.6688 | 123.7656 | 77.6047 | -0.2655 | 123.7335 | 2.6688 | 77.6047 | 114.6606 | 123.7656 | -123.9853 | -124.0036
2102.7188 | 123.9258 | -61.2854 | 62.4435 | -0.23781 | 0.015383 | 0.016191 | 0.0078336 | 0.062171 | 0.0030847 | 0.08439 | -58.6487 | 62.384 | -61.5829 | -61.5189 | 53.4302 | 16.452 | 2.3483 | 2.2202 | 62.439 | -61.5646 | -0.29755 | -0.059509 | 2.6367 | -0.23346 | -9.0134 | -0.27924 | -0.004577 | 2.9343 | 63.6337 | 63.5056 | 114.7156 | 123.6694 | 2.6367 | 123.7244 | 77.7374 | -0.27924 | 123.6694 | 2.6367 | 77.7374 | 114.7156 | 123.7244 | -124.0265 | -124.0082
2103.7188 | 123.8068 | -61.3266 | 62.384 | -0.08522 | 0.016451 | 0.017045 | 0.015097 | 0.064948 | 0.0011621 | 0.082894 | -58.6212 | 62.4161 | -61.5601 | -61.4685 | 53.4622 | 16.539 | 2.243 | 2.2568 | 62.4023 | -61.5875 | -0.23346 | 0.032044 | 2.7054 | -0.14191 | -8.9218 | -0.26093 | 0.018311 | 2.9388 | 63.5696 | 63.5834 | 114.7888 | 123.7427 | 2.7054 | 123.7289 | 77.8656 | -0.26093 | 123.7427 | 2.7054 | 77.8656 | 114.7888 | 123.7289 | -123.9441 | -123.9716
2104.7188 | 123.8754 | -61.3266 | 62.4115 | 1.1584 | 0.018374 | 0.014482 | 0.011038 | 0.064948 | 0.0024439 | 0.082253 | -58.5892 | 62.3978 | -61.5967 | -61.5005 | 53.4439 | 16.452 | 2.3666 | 2.2705 | 62.4207 | -61.5829 | -0.27008 | -0.013733 | 2.7374 | -0.17395 | -8.9676 | -0.25635 | 0.009155 | 3.0075 | 63.6932 | 63.5971 | 114.7705 | 123.7244 | 2.7374 | 123.7473 | 77.7786 | -0.25635 | 123.7244 | 2.7374 | 77.7786 | 114.7705 | 123.7473 | -124.0082 | -123.9944
2105.7188 | 123.8846 | -61.322 | 62.4481 | 0.029221 | 0.01581 | 0.019395 | 0.014029 | 0.065375 | 0.0018031 | 0.080331 | -58.5754 | 62.3886 | -61.5738 | -61.5005 | 53.3478 | 16.301 | 2.2247 | 2.1606 | 62.4115 | -61.6013 | -0.25177 | -0.059509 | 2.7466 | -0.17853 | -9.1003 | -0.27924 | -0.036621 | 2.9984 | 63.5468 | 63.4827 | 114.6698 | 123.7106 | 2.7466 | 123.7335 | 77.623 | -0.27924 | 123.7106 | 2.7466 | 77.623 | 114.6698 | 123.7335 | -124.0219 | -124.0494
2106.7188 | 123.912 | -61.3083 | 62.4298 | -0.26833 | 0.015383 | 0.013627 | 0.0056972 | 0.064307 | -0.0016149 | 0.083535 | -58.6578 | 62.352 | -61.5326 | -61.4914 | 53.4393 | 16.5207 | 2.1973 | 2.2522 | 62.4252 | -61.5555 | -0.2243 | -0.07782 | 2.6505 | -0.1831 | -8.9905 | -0.24719 | -0.004578 | 2.8748 | 63.5056 | 63.5605 | 114.7476 | 123.6603 | 2.6505 | 123.7335 | 77.829 | -0.24719 | 123.6603 | 2.6505 | 77.829 | 114.7476 | 123.7335 | -123.9624 | -123.9853
2107.7188 | 123.8754 | -61.3174 | 62.439 | -0.19966 | 0.014315 | 0.015122 | 0.014029 | 0.062171 | 0.0024439 | 0.082894 | -58.6395 | 62.4069 | -61.5738 | -61.5097 | 53.4668 | 16.6443 | 2.243 | 2.2476 | 62.4115 | -61.5875 | -0.25635 | -0.032044 | 2.6779 | -0.19226 | -8.9722 | -0.27008 | -0.027466 | 2.9343 | 63.5605 | 63.5651 | 114.7842 | 123.7244 | 2.6779 | 123.7289 | 77.9617 | -0.27008 | 123.7244 | 2.6779 | 77.9617 | 114.7842 | 123.7289 | -124.0128 | -124.0265
2108.7188 | 123.9487 | -61.3037 | 62.4207 | -0.031814 | 0.018587 | 0.014268 | 0.015097 | 0.064521 | 0.0020167 | 0.082894 | -58.5983 | 62.4023 | -61.5189 | -61.4685 | 53.3432 | 16.507 | 2.1423 | 2.2293 | 62.3886 | -61.5967 | -0.21515 | -0.01831 | 2.7054 | -0.16479 | -9.0775 | -0.29297 | -0.032043 | 2.9205 | 63.446 | 63.533 | 114.6469 | 123.7061 | 2.7054 | 123.6923 | 77.8107 | -0.29297 | 123.7061 | 2.7054 | 77.8107 | 114.6469 | 123.6923 | -123.9395 | -124.0173
2109.7188 | 123.912 | -61.2946 | 62.4115 | -0.15388 | 0.018374 | 0.017259 | 0.010824 | 0.064307 | 0.0032983 | 0.079904 | -58.6258 | 62.3932 | -61.5463 | -61.4822 | 53.4485 | 16.4017 | 2.1286 | 2.2202 | 62.4252 | -61.5601 | -0.25177 | -0.018311 | 2.6688 | -0.18768 | -8.963 | -0.2655 | 0.013733 | 2.9205 | 63.4232 | 63.5147 | 114.743 | 123.6877 | 2.6688 | 123.7198 | 77.6962 | -0.2655 | 123.6877 | 2.6688 | 77.6962 | 114.743 | 123.7198 | -123.9578 | -123.9716
2110.7188 | 123.8846 | -61.3312 | 62.4435 | -0.22255 | 0.014529 | 0.015977 | 0.0074062 | 0.063452 | 0.00052127 | 0.081399 | -58.5938 | 62.3657 | -61.5646 | -61.496 | 53.5263 | 16.571 | 2.243 | 2.2751 | 62.4161 | -61.5601 | -0.23346 | -0.077819 | 2.7374 | -0.1648 | -8.9172 | -0.22888 | -0.027465 | 2.9709 | 63.5742 | 63.6063 | 114.8575 | 123.6969 | 2.7374 | 123.7473 | 77.9022 | -0.22888 | 123.6969 | 2.7374 | 77.9022 | 114.8575 | 123.7473 | -124.0082 | -124.0036
2111.7188 | 123.8525 | -61.3358 | 62.4344 | -0.2607 | 0.016024 | 0.017259 | 0.011679 | 0.065375 | -0.00011953 | 0.080117 | -58.6166 | 62.3886 | -61.5646 | -61.5051 | 53.3203 | 16.4062 | 2.2842 | 2.1149 | 62.439 | -61.5875 | -0.22888 | -0.045776 | 2.7191 | -0.16937 | -9.1141 | -0.25177 | 0.004578 | 2.948 | 63.62 | 63.4506 | 114.6561 | 123.7244 | 2.7191 | 123.7747 | 77.742 | -0.25177 | 123.7244 | 2.7191 | 77.742 | 114.6561 | 123.7747 | -123.999 | -124.0219
2112.7188 | 123.9029 | -61.3129 | 62.4207 | -0.23018 | 0.014529 | 0.017472 | 0.0095424 | 0.061316 | 0.0022303 | 0.07969 | -58.4061 | 62.3474 | -61.5692 | -61.4868 | 53.4393 | 16.7633 | 2.1927 | 2.1469 | 62.4069 | -61.5463 | -0.25635 | -0.073242 | 2.9068 | -0.17395 | -8.9813 | -0.23346 | -0.013733 | 3.1631 | 63.5056 | 63.4598 | 114.7522 | 123.6603 | 2.9068 | 123.7198 | 78.0762 | -0.23346 | 123.6603 | 2.9068 | 78.0762 | 114.7522 | 123.7198 | -123.9899 | -123.967
2113.7188 | 123.8983 | -61.3266 | 62.3795 | 0.1284 | 0.017092 | 0.014909 | 0.017019 | 0.063239 | 0.0032983 | 0.082467 | -58.5114 | 62.384 | -61.5738 | -61.5372 | 53.5034 | 16.6351 | 2.1103 | 2.1011 | 62.352 | -61.6241 | -0.24719 | 0.004577 | 2.8152 | -0.21057 | -8.876 | -0.29755 | -0.027466 | 3.0624 | 63.4369 | 63.4277 | 114.83 | 123.7106 | 2.8152 | 123.6786 | 77.9617 | -0.29755 | 123.7106 | 2.8152 | 77.9617 | 114.83 | 123.6786 | -123.9532 | -124.0036
2114.7188 | 123.9029 | -61.2946 | 62.4115 | -0.14626 | 0.016451 | 0.020463 | 0.01531 | 0.063666 | 0.0013757 | 0.082894 | -58.4518 | 62.439 | -61.5646 | -61.4685 | 53.5446 | 16.7679 | 2.0645 | 2.1606 | 62.4115 | -61.5692 | -0.27008 | 0.027466 | 2.8427 | -0.17395 | -8.8669 | -0.27466 | 0 | 3.1128 | 63.3591 | 63.4552 | 114.8392 | 123.7335 | 2.8427 | 123.7061 | 78.0624 | -0.27466 | 123.7335 | 2.8427 | 78.0624 | 114.8392 | 123.7061 | -123.9761 | -123.9807
2115.7188 | 123.8937 | -61.3266 | 62.4298 | -0.21492 | 0.016024 | 0.020036 | 0.012106 | 0.064521 | -0.00054693 | 0.081185 | -58.4564 | 62.4069 | -61.5875 | -61.4822 | 53.5904 | 16.8686 | 2.1286 | 2.2705 | 62.4252 | -61.5738 | -0.26093 | -0.022889 | 2.8702 | -0.15564 | -8.8394 | -0.24719 | -0.004578 | 3.1311 | 63.4552 | 63.5971 | 114.917 | 123.7335 | 2.8702 | 123.7518 | 78.1952 | -0.24719 | 123.7335 | 2.8702 | 78.1952 | 114.917 | 123.7518 | -124.0173 | -124.0036
2116.7188 | 123.8525 | -61.3312 | 62.4023 | -0.24544 | 0.014956 | 0.015977 | 0.0080472 | 0.064948 | -0.00076053 | 0.081826 | -58.5434 | 62.3749 | -61.5738 | -61.5189 | 53.5309 | 16.8869 | 2.1698 | 2.2247 | 62.4161 | -61.5646 | -0.24262 | -0.027466 | 2.7878 | -0.18768 | -8.8715 | -0.23346 | 0.013733 | 3.0304 | 63.501 | 63.5559 | 114.8621 | 123.7061 | 2.7878 | 123.7473 | 78.2181 | -0.23346 | 123.7061 | 2.7878 | 78.2181 | 114.8621 | 123.7473 | -123.9761 | -123.967
2117.7188 | 123.8525 | -61.3174 | 62.4344 | -0.60402 | 0.015169 | 0.015336 | 0.011038 | 0.063452 | 0.0011621 | 0.081399 | -58.6029 | 62.4115 | -61.5784 | -61.5143 | 53.6499 | 16.8365 | 2.0966 | 2.1332 | 62.4161 | -61.5646 | -0.26093 | -0.022888 | 2.7145 | -0.19684 | -8.7845 | -0.24719 | -0.01831 | 2.9755 | 63.414 | 63.4506 | 114.9673 | 123.7289 | 2.7145 | 123.7335 | 78.154 | -0.24719 | 123.7289 | 2.7145 | 78.154 | 114.9673 | 123.7335 | -124.0128 | -123.999
2118.7188 | 123.9075 | -61.3037 | 62.3932 | -0.10048 | 0.017306 | 0.019181 | 0.014883 | 0.064521 | 0.0022303 | 0.082253 | -58.4061 | 62.4115 | -61.5417 | -61.4777 | 53.6682 | 16.951 | 2.0004 | 2.1286 | 62.4023 | -61.5738 | -0.23804 | 0.018311 | 2.8976 | -0.17395 | -8.725 | -0.27008 | 0.009156 | 3.1357 | 63.3041 | 63.4323 | 114.9719 | 123.7152 | 2.8976 | 123.7061 | 78.2547 | -0.27008 | 123.7152 | 2.8976 | 78.2547 | 114.9719 | 123.7061 | -123.9349 | -123.967
2119.7188 | 123.8525 | -61.3083 | 62.439 | 1.7992 | 0.014742 | 0.017472 | 0.0091152 | 0.062171 | 0.0013757 | 0.081826 | -58.6533 | 62.3703 | -61.5921 | -61.5051 | 53.595 | 17.0059 | 1.9913 | 1.9272 | 62.4298 | -61.5509 | -0.28381 | -0.068665 | 2.655 | -0.19684 | -8.844 | -0.24261 | -0.009155 | 2.9388 | 63.2996 | 63.2355 | 114.9033 | 123.6786 | 2.655 | 123.7381 | 78.3142 | -0.24261 | 123.6786 | 2.655 | 78.3142 | 114.9033 | 123.7381 | -124.0311 | -123.9899
2120.7344 | 123.9853 | -61.3037 | 62.3749 | 0.18181 | 0.016665 | 0.012986 | 0.011679 | 0.064948 | 0.00030767 | 0.082467 | -58.5022 | 62.3428 | -61.5509 | -61.4868 | 53.6957 | 17.0883 | 1.8677 | 1.9409 | 62.3474 | -61.5921 | -0.24719 | -0.032044 | 2.8015 | -0.1831 | -8.6792 | -0.28839 | -0.027466 | 3.0487 | 63.1714 | 63.2446 | 114.9994 | 123.6465 | 2.8015 | 123.6511 | 78.392 | -0.28839 | 123.6465 | 2.8015 | 78.392 | 114.9994 | 123.6511 | -123.9258 | -123.967
2121.7188 | 123.88 | -61.3449 | 62.4115 | 1.2881 | 0.017519 | 0.016618 | 0.010183 | 0.065589 | 0.0020167 | 0.081826 | -58.5663 | 62.4069 | -61.5738 | -61.5143 | 53.7186 | 16.9373 | 2.0004 | 1.8951 | 62.4207 | -61.5967 | -0.22888 | -0.004578 | 2.7786 | -0.16937 | -8.6929 | -0.25177 | 0.009155 | 3.0075 | 63.3453 | 63.2401 | 115.0635 | 123.7518 | 2.7786 | 123.7656 | 78.2822 | -0.25177 | 123.7518 | 2.7786 | 78.2822 | 115.0635 | 123.7656 | -123.9853 | -124.0082
2122.7188 | 123.9166 | -61.3312 | 62.4115 | -0.131 | 0.016878 | 0.014909 | 0.013388 | 0.064093 | 0.0032983 | 0.080544 | -58.4976 | 62.4207 | -61.5829 | -61.4685 | 53.7003 | 17.0517 | 1.9867 | 1.9226 | 62.4115 | -61.5875 | -0.25177 | 0.009155 | 2.8336 | -0.13733 | -8.7112 | -0.25635 | 0 | 3.0853 | 63.3179 | 63.2538 | 115.0314 | 123.7518 | 2.8336 | 123.7427 | 78.3829 | -0.25635 | 123.7518 | 2.8336 | 78.3829 | 115.0314 | 123.7427 | -123.9944 | -123.999
2123.7188 | 123.9029 | -61.2946 | 62.384 | -0.047073 | 0.017519 | 0.017472 | 0.014456 | 0.064948 | 0.00052127 | 0.080117 | -58.4381 | 62.4298 | -61.5463 | -61.4914 | 53.6087 | 16.9464 | 1.918 | 1.9272 | 62.3932 | -61.5875 | -0.25177 | 0.045777 | 2.8564 | -0.19684 | -8.7753 | -0.29297 | 0.009155 | 3.1082 | 63.2126 | 63.2217 | 114.9033 | 123.7244 | 2.8564 | 123.6877 | 78.241 | -0.29297 | 123.7244 | 2.8564 | 78.241 | 114.9033 | 123.6877 | -123.9304 | -123.9716
2124.7188 | 123.8892 | -61.3037 | 62.439 | -1.7637 | 0.017306 | 0.021531 | 0.011465 | 0.064948 | -0.00011953 | 0.082681 | -58.6716 | 62.4298 | -61.5692 | -61.5234 | 53.4714 | 16.8777 | 1.973 | 1.8631 | 62.4573 | -61.5875 | -0.2655 | -0.009155 | 2.6321 | -0.21973 | -8.9676 | -0.28381 | 0.01831 | 2.8976 | 63.2767 | 63.1668 | 114.7751 | 123.7335 | 2.6321 | 123.761 | 78.1815 | -0.28381 | 123.7335 | 2.6321 | 78.1815 | 114.7751 | 123.761 | -124.0082 | -124.0265
2125.7344 | 123.9532 | -61.2991 | 62.3337 | 0.13603 | 0.013888 | 0.012559 | 0.0065518 | 0.065375 | 0.00052127 | 0.082681 | -58.5297 | 62.2925 | -61.5463 | -61.4777 | 53.7415 | 17.2485 | 1.8173 | 2.0096 | 62.3245 | -61.5784 | -0.24719 | -0.041199 | 2.7695 | -0.17853 | -8.5922 | -0.27924 | -0.009155 | 3.0167 | 63.1165 | 63.3087 | 115.0406 | 123.5916 | 2.7695 | 123.6237 | 78.5477 | -0.27924 | 123.5916 | 2.7695 | 78.5477 | 115.0406 | 123.6237 | -123.88 | -123.912
2126.7188 | 123.848 | -61.322 | 62.4344 | -0.24544 | 0.017947 | 0.016191 | 0.010824 | 0.062812 | 0.0022303 | 0.081185 | -58.6853 | 62.4115 | -61.5463 | -61.5738 | 53.6819 | 17.1341 | 1.9867 | 1.973 | 62.3795 | -61.6104 | -0.22431 | -0.022888 | 2.6367 | -0.25177 | -8.7524 | -0.28839 | -0.054931 | 2.861 | 63.3087 | 63.295 | 115.004 | 123.7335 | 2.6367 | 123.7015 | 78.4561 | -0.28839 | 123.7335 | 2.6367 | 78.4561 | 115.004 | 123.7015 | -123.9807 | -124.0448
2127.7188 | 123.9029 | -61.3266 | 62.4115 | -0.15388 | 0.017306 | 0.01555 | 0.011892 | 0.064307 | 0.0030847 | 0.081185 | -58.5068 | 62.4344 | -61.5692 | -61.496 | 53.8422 | 17.2302 | 2.0645 | 2.0142 | 62.4069 | -61.5921 | -0.24262 | 0.022888 | 2.8198 | -0.16937 | -8.5693 | -0.2655 | -0.004578 | 3.0624 | 63.3911 | 63.3408 | 115.1688 | 123.761 | 2.8198 | 123.7335 | 78.5568 | -0.2655 | 123.761 | 2.8198 | 78.5568 | 115.1688 | 123.7335 | -123.9807 | -124.0036
2128.7188 | 123.8342 | -61.3495 | 62.3978 | 0.10551 | 0.016878 | 0.016191 | 0.015524 | 0.066016 | -0.00054693 | 0.079904 | -58.6716 | 62.4069 | -61.615 | -61.5784 | 53.7918 | 17.1844 | 1.9363 | 1.8402 | 62.3795 | -61.6333 | -0.2655 | 0.009155 | 2.6779 | -0.22888 | -8.606 | -0.28381 | -0.01831 | 2.9434 | 63.2858 | 63.1897 | 115.1413 | 123.7564 | 2.6779 | 123.7289 | 78.5339 | -0.28381 | 123.7564 | 2.6779 | 78.5339 | 115.1413 | 123.7289 | -124.0128 | -124.0311
2129.7188 | 123.9029 | -61.3129 | 62.4344 | -0.1844 | 0.015383 | 0.019822 | 0.010824 | 0.06388 | 0.0022303 | 0.080544 | -58.5938 | 62.4252 | -61.5921 | -61.5097 | 53.92 | 17.1295 | 1.9547 | 2.0416 | 62.4527 | -61.6013 | -0.27924 | -0.009155 | 2.7191 | -0.19684 | -8.5144 | -0.28839 | 0.018311 | 2.9984 | 63.2675 | 63.3545 | 115.2328 | 123.7381 | 2.7191 | 123.7656 | 78.4424 | -0.28839 | 123.7381 | 2.7191 | 78.4424 | 115.2328 | 123.7656 | -124.0265 | -124.0356
2130.7344 | 123.9624 | -61.2991 | 62.3886 | -0.016556 | 0.013247 | 0.016618 | 0.0061246 | 0.061957 | 0.0013757 | 0.082467 | -58.6304 | 62.2879 | -61.5738 | -61.4914 | 53.8605 | 17.1021 | 1.9821 | 2.0645 | 62.3749 | -61.5463 | -0.27466 | -0.10071 | 2.6688 | -0.19226 | -8.5281 | -0.24719 | -0.013733 | 2.9434 | 63.2812 | 63.3636 | 115.1596 | 123.587 | 2.6688 | 123.674 | 78.4012 | -0.24719 | 123.587 | 2.6688 | 78.4012 | 115.1596 | 123.674 | -123.9624 | -123.9349
2131.7188 | 123.9029 | -61.2991 | 62.439 | -0.2607 | 0.016878 | 0.018113 | 0.014456 | 0.063239 | 0.0013757 | 0.081399 | -58.7082 | 62.4207 | -61.5738 | -61.5097 | 53.7643 | 17.1158 | 1.9226 | 1.9455 | 62.3978 | -61.6196 | -0.27466 | -0.018311 | 2.5909 | -0.21057 | -8.6746 | -0.32044 | -0.041199 | 2.8656 | 63.2217 | 63.2446 | 115.0635 | 123.7198 | 2.5909 | 123.6969 | 78.4149 | -0.32044 | 123.7198 | 2.5909 | 78.4149 | 115.0635 | 123.6969 | -124.0128 | -124.0585
2132.7188 | 123.8754 | -61.3129 | 62.4252 | -0.14626 | 0.015597 | 0.01854 | 0.011679 | 0.062598 | 0.00094847 | 0.083535 | -58.6853 | 62.3886 | -61.5921 | -61.5051 | 53.7506 | 17.07 | 2.0096 | 1.9638 | 62.4115 | -61.5921 | -0.27924 | -0.036621 | 2.6276 | -0.19226 | -8.6746 | -0.27924 | -0.013733 | 2.9068 | 63.3224 | 63.2767 | 115.0635 | 123.7015 | 2.6276 | 123.7244 | 78.3829 | -0.27924 | 123.7015 | 2.6276 | 78.3829 | 115.0635 | 123.7244 | -124.0173 | -124.0173
2133.7188 | 123.9258 | -61.3037 | 62.439 | -0.12337 | 0.015597 | 0.018968 | 0.013815 | 0.063452 | 0.0015893 | 0.082681 | -58.5663 | 62.3886 | -61.5784 | -61.4685 | 53.7872 | 17.0425 | 2.0325 | 2.0462 | 62.4252 | -61.5692 | -0.27466 | -0.050354 | 2.7374 | -0.16479 | -8.6517 | -0.2655 | -0.013733 | 3.0121 | 63.3362 | 63.3499 | 115.0909 | 123.6923 | 2.7374 | 123.7289 | 78.3463 | -0.2655 | 123.6923 | 2.7374 | 78.3463 | 115.0909 | 123.7289 | -124.0173 | -124.0082
2134.7188 | 123.8434 | -61.3312 | 62.4435 | -0.23018 | 0.015169 | 0.0132 | 0.010397 | 0.064521 | 9.4068e-05 | 0.080117 | -58.5526 | 62.4115 | -61.5692 | -61.5372 | 53.7323 | 17.0609 | 1.9592 | 1.9913 | 62.4069 | -61.5601 | -0.23804 | -0.032043 | 2.7786 | -0.20599 | -8.7112 | -0.22888 | -0.036621 | 3.0167 | 63.2904 | 63.3224 | 115.0635 | 123.7427 | 2.7786 | 123.7381 | 78.392 | -0.22888 | 123.7427 | 2.7786 | 78.392 | 115.0635 | 123.7381 | -124.0128 | -124.0036
2135.7344 | 123.9075 | -61.3037 | 62.3749 | 0.04448 | 0.014315 | 0.017259 | 0.004202 | 0.062598 | -0.00054693 | 0.082467 | -58.6349 | 62.3062 | -61.5692 | -61.5143 | 53.8971 | 17.189 | 1.8036 | 2.092 | 62.3795 | -61.5463 | -0.2655 | -0.068665 | 2.6688 | -0.21057 | -8.4778 | -0.24262 | 0.004578 | 2.9343 | 63.1073 | 63.3957 | 115.2008 | 123.6099 | 2.6688 | 123.6832 | 78.4927 | -0.24262 | 123.6099 | 2.6688 | 78.4927 | 115.2008 | 123.6832 | -123.9441 | -123.9212
2136.7188 | 123.8571 | -61.3174 | 62.4344 | -0.21492 | 0.015383 | 0.018754 | 0.011679 | 0.061957 | 0.0026575 | 0.080117 | -58.6487 | 62.3749 | -61.5555 | -61.5051 | 53.7964 | 17.0334 | 1.8356 | 1.9592 | 62.4115 | -61.5921 | -0.23804 | -0.059509 | 2.6688 | -0.18768 | -8.638 | -0.27466 | -0.022888 | 2.9068 | 63.1531 | 63.2767 | 115.1138 | 123.6923 | 2.6688 | 123.7289 | 78.3508 | -0.27466 | 123.6923 | 2.6688 | 78.3508 | 115.1138 | 123.7289 | -123.9899 | -124.0265
2137.7188 | 123.8983 | -61.3129 | 62.4207 | -0.16914 | 0.016238 | 0.014482 | 0.01232 | 0.061743 | 0.00094847 | 0.081185 | -58.6578 | 62.3978 | -61.5555 | -61.4731 | 53.8467 | 17.2577 | 1.8265 | 1.9638 | 62.4069 | -61.6104 | -0.24262 | -0.022888 | 2.655 | -0.16022 | -8.5739 | -0.29755 | -0.013733 | 2.8976 | 63.1393 | 63.2767 | 115.1596 | 123.7106 | 2.655 | 123.7198 | 78.5706 | -0.29755 | 123.7106 | 2.655 | 78.5706 | 115.1596 | 123.7198 | -123.9761 | -124.0311
2138.7188 | 123.9029 | -61.3266 | 62.3978 | 0.63957 | 0.017092 | 0.01854 | 0.015738 | 0.064734 | 0.0018031 | 0.081826 | -58.5571 | 62.4023 | -61.5692 | -61.4639 | 54.007 | 17.3172 | 1.7715 | 1.918 | 62.4069 | -61.5784 | -0.24262 | 0.004578 | 2.7695 | -0.13733 | -8.3908 | -0.25177 | 0.009155 | 3.0121 | 63.0981 | 63.2446 | 115.3336 | 123.7289 | 2.7695 | 123.7335 | 78.6438 | -0.25177 | 123.7289 | 2.7695 | 78.6438 | 115.3336 | 123.7335 | -123.967 | -123.9761
2139.7188 | 123.8892 | -61.3083 | 62.4481 | -0.26833 | 0.016665 | 0.012345 | 0.0093288 | 0.063239 | 0.00030767 | 0.083322 | -58.6121 | 62.3886 | -61.5875 | -61.5097 | 53.9154 | 17.2256 | 1.8311 | 1.9043 | 62.4252 | -61.5555 | -0.27923 | -0.059509 | 2.6962 | -0.20142 | -8.5327 | -0.24719 | -0.022888 | 2.9755 | 63.1393 | 63.2126 | 115.2237 | 123.6969 | 2.6962 | 123.7335 | 78.5339 | -0.24719 | 123.6969 | 2.6962 | 78.5339 | 115.2237 | 123.7335 | -124.0356 | -124.0036
2140.7188 | 123.848 | -61.3083 | 62.4161 | -0.36751 | 0.016878 | 0.015336 | 0.010824 | 0.06388 | 0.00073487 | 0.082681 | -58.7128 | 62.3886 | -61.5784 | -61.5189 | 53.8971 | 17.2852 | 1.886 | 1.9135 | 62.4023 | -61.5738 | -0.27008 | -0.027466 | 2.5955 | -0.21057 | -8.519 | -0.2655 | -0.013733 | 2.8656 | 63.1943 | 63.2217 | 115.2054 | 123.6969 | 2.5955 | 123.7106 | 78.5934 | -0.2655 | 123.6969 | 2.5955 | 78.5934 | 115.2054 | 123.7106 | -123.9944 | -123.9899
2141.7188 | 123.8937 | -61.3358 | 62.4115 | -0.1844 | 0.017519 | 0.014054 | 0.010611 | 0.064948 | 0.0011621 | 0.083535 | -58.6166 | 62.4115 | -61.5829 | -61.4914 | 53.8788 | 17.3584 | 1.7349 | 1.8402 | 62.3886 | -61.5784 | -0.24719 | 0 | 2.7191 | -0.15564 | -8.5327 | -0.24262 | -0.022888 | 2.9663 | 63.0707 | 63.176 | 115.2145 | 123.7473 | 2.7191 | 123.7244 | 78.6942 | -0.24262 | 123.7473 | 2.7191 | 78.6942 | 115.2145 | 123.7244 | -123.9944 | -123.9899
2142.7188 | 123.8892 | -61.322 | 62.4344 | -0.26833 | 0.013674 | 0.019395 | 0.011465 | 0.063452 | 0.0018031 | 0.08204 | -58.5526 | 62.4069 | -61.5417 | -61.3358 | 53.8284 | 17.0334 | 1.8768 | 1.9547 | 62.4298 | -61.615 | -0.21973 | -0.027466 | 2.7695 | -0.013733 | -8.606 | -0.29297 | -0.004577 | 2.9892 | 63.1989 | 63.2767 | 115.1505 | 123.7289 | 2.7695 | 123.7518 | 78.3554 | -0.29297 | 123.7289 | 2.7695 | 78.3554 | 115.1505 | 123.7518 | -123.9761 | -124.0494
2143.7344 | 123.8617 | -61.3266 | 62.4023 | 0.04448 | 0.017092 | 0.019608 | 0.014669 | 0.062384 | 0.0013757 | 0.080972 | -58.6304 | 62.4161 | -61.5692 | -61.528 | 53.8971 | 17.2394 | 1.8173 | 1.8768 | 62.3978 | -61.615 | -0.24262 | 0.013733 | 2.6962 | -0.20142 | -8.5052 | -0.28839 | -0.004578 | 2.9388 | 63.1439 | 63.2034 | 115.2237 | 123.7427 | 2.6962 | 123.7244 | 78.566 | -0.28839 | 123.7427 | 2.6962 | 78.566 | 115.2237 | 123.7244 | -123.9716 | -124.0173
2144.7188 | 123.8754 | -61.3083 | 62.4298 | -0.20729 | 0.014956 | 0.015977 | 0.0099698 | 0.062171 | 0.0011621 | 0.080758 | -58.6075 | 62.3749 | -61.5555 | -61.5189 | 53.9703 | 17.2852 | 1.8173 | 1.886 | 62.4207 | -61.5784 | -0.24719 | -0.054932 | 2.7008 | -0.21057 | -8.4595 | -0.27008 | -0.009156 | 2.948 | 63.1256 | 63.1943 | 115.2786 | 123.6832 | 2.7008 | 123.7289 | 78.5934 | -0.27008 | 123.6832 | 2.7008 | 78.5934 | 115.2786 | 123.7289 | -123.9853 | -124.0082
2145.7188 | 123.8754 | -61.3129 | 62.384 | -0.031814 | 0.017306 | 0.017899 | 0.012747 | 0.065161 | 0.00052127 | 0.081185 | -58.7769 | 62.3566 | -61.5784 | -61.5372 | 53.9108 | 17.3676 | 1.7807 | 1.8997 | 62.3611 | -61.6104 | -0.2655 | -0.027466 | 2.536 | -0.2243 | -8.4732 | -0.29755 | -0.022888 | 2.8015 | 63.0936 | 63.2126 | 115.2237 | 123.6694 | 2.536 | 123.674 | 78.6804 | -0.29755 | 123.6694 | 2.536 | 78.6804 | 115.2237 | 123.674 | -123.9624 | -123.9944
2146.7188 | 123.8846 | -61.3174 | 62.4252 | -0.23018 | 0.016024 | 0.017045 | 0.01232 | 0.063239 | 0.0045801 | 0.081399 | -58.7173 | 62.3749 | -61.5372 | -61.5189 | 53.9291 | 17.276 | 1.9089 | 2.005 | 62.4023 | -61.5921 | -0.21973 | -0.050354 | 2.6001 | -0.20142 | -8.4961 | -0.27466 | -0.022888 | 2.8198 | 63.2263 | 63.3224 | 115.2466 | 123.6923 | 2.6001 | 123.7198 | 78.5934 | -0.27466 | 123.6923 | 2.6001 | 78.5934 | 115.2466 | 123.7198 | -123.9624 | -124.0173
2147.7188 | 123.9212 | -61.2808 | 62.4115 | -0.23018 | 0.013674 | 0.014695 | 0.008688 | 0.061316 | 0.0024439 | 0.081613 | -58.5938 | 62.3291 | -61.5372 | -61.4365 | 53.9017 | 17.3767 | 1.9272 | 2.124 | 62.3749 | -61.528 | -0.25635 | -0.082397 | 2.6871 | -0.15564 | -8.5098 | -0.24719 | -0.036621 | 2.9434 | 63.208 | 63.4048 | 115.1825 | 123.6099 | 2.6871 | 123.6557 | 78.6575 | -0.24719 | 123.6099 | 2.6871 | 78.6575 | 115.1825 | 123.6557 | -123.9487 | -123.9395
2148.7188 | 123.967 | -61.2625 | 62.3978 | -0.22255 | 0.016451 | 0.013841 | 0.0093288 | 0.061743 | 0.00052127 | 0.082253 | -58.548 | 62.3108 | -61.5646 | -61.4319 | 53.9658 | 17.363 | 1.8951 | 2.1286 | 62.3795 | -61.5463 | -0.30212 | -0.086975 | 2.7145 | -0.16937 | -8.432 | -0.28381 | -0.01831 | 3.0167 | 63.1577 | 63.3911 | 115.2283 | 123.5733 | 2.7145 | 123.642 | 78.6255 | -0.28381 | 123.5733 | 2.7145 | 78.6255 | 115.2283 | 123.642 | -123.9624 | -123.9441
2149.7188 | 123.9807 | -61.2717 | 62.4115 | -0.2607 | 0.014529 | 0.012345 | 0.010183 | 0.061103 | 0.0013757 | 0.080758 | -58.5617 | 62.3337 | -61.528 | -61.4227 | 53.952 | 17.3264 | 1.9272 | 2.1332 | 62.3657 | -61.5326 | -0.25635 | -0.07782 | 2.71 | -0.15106 | -8.4595 | -0.26093 | -0.045776 | 2.9663 | 63.1989 | 63.4048 | 115.2237 | 123.6053 | 2.71 | 123.6374 | 78.598 | -0.26093 | 123.6053 | 2.71 | 78.598 | 115.2237 | 123.6374 | -123.9395 | -123.9441
2150.7188 | 124.0082 | -61.2854 | 62.3474 | 0.23521 | 0.013888 | 0.015763 | 0.011679 | 0.061743 | 0.0020167 | 0.083108 | -58.5938 | 62.2787 | -61.5555 | -61.4685 | 53.9429 | 17.2577 | 1.6617 | 2.1011 | 62.3245 | -61.5646 | -0.27008 | -0.068664 | 2.6917 | -0.18311 | -8.4045 | -0.27924 | -0.022888 | 2.9617 | 62.9471 | 63.3865 | 115.2283 | 123.5641 | 2.6917 | 123.6099 | 78.5431 | -0.27924 | 123.5641 | 2.6917 | 78.5431 | 115.2283 | 123.6099 | -123.9029 | -123.912
2151.7188 | 123.8617 | -61.3266 | 62.4252 | -0.29884 | 0.017306 | 0.0132 | 0.011251 | 0.063025 | 0.0026575 | 0.081826 | -58.5892 | 62.3749 | -61.5646 | -61.5143 | 53.6957 | 17.1204 | 1.918 | 1.8951 | 62.3932 | -61.5829 | -0.23804 | -0.050354 | 2.7374 | -0.18768 | -8.7296 | -0.25635 | -0.032044 | 2.9755 | 63.2446 | 63.2217 | 115.0223 | 123.7015 | 2.7374 | 123.7198 | 78.447 | -0.25635 | 123.7015 | 2.7374 | 78.447 | 115.0223 | 123.7198 | -123.9899 | -124.0082
2152.7188 | 123.9716 | -61.2762 | 62.4069 | -0.16151 | 0.013674 | 0.014482 | 0.010183 | 0.06153 | 0.00030767 | 0.079263 | -58.5663 | 62.3062 | -61.5326 | -61.4182 | 53.8788 | 17.189 | 1.7303 | 2.0004 | 62.3703 | -61.5417 | -0.25635 | -0.10071 | 2.71 | -0.14191 | -8.5281 | -0.2655 | -0.036621 | 2.9663 | 63.0066 | 63.2767 | 115.155 | 123.5825 | 2.71 | 123.6465 | 78.4653 | -0.2655 | 123.5825 | 2.71 | 78.4653 | 115.155 | 123.6465 | -123.9395 | -123.9487
2153.7344 | 123.8297 | -61.3449 | 62.4252 | 0.04448 | 0.014956 | 0.012559 | 0.017874 | 0.064734 | 0.0022303 | 0.08204 | -58.6258 | 62.3703 | -61.5875 | -61.5463 | 53.8101 | 17.07 | 1.8082 | 1.7441 | 62.3703 | -61.6196 | -0.24261 | -0.054932 | 2.7191 | -0.20142 | -8.6151 | -0.27466 | -0.054932 | 2.9617 | 63.1531 | 63.089 | 115.155 | 123.7152 | 2.7191 | 123.7152 | 78.4149 | -0.27466 | 123.7152 | 2.7191 | 78.4149 | 115.155 | 123.7152 | -124.0128 | -124.0448
2154.7188 | 123.8068 | -61.2991 | 62.4115 | -0.2607 | 0.016451 | 0.016191 | 0.0097562 | 0.063239 | 0.0020167 | 0.079049 | -58.6212 | 62.3657 | -61.5646 | -61.5005 | 53.7827 | 17.0059 | 1.8768 | 1.9455 | 62.4207 | -61.5601 | -0.2655 | -0.045776 | 2.6779 | -0.20142 | -8.6288 | -0.26093 | 0.009155 | 2.9434 | 63.176 | 63.2446 | 115.0818 | 123.6649 | 2.6779 | 123.7198 | 78.3051 | -0.26093 | 123.6649 | 2.6779 | 78.3051 | 115.0818 | 123.7198 | -123.9761 | -123.9716
2155.7188 | 123.8571 | -61.2991 | 62.4435 | -0.23018 | 0.015383 | 0.01555 | 0.01296 | 0.061743 | 0.0013757 | 0.081613 | -58.699 | 62.3611 | -61.5692 | -61.496 | 53.8055 | 17.1204 | 1.8356 | 1.8311 | 62.4115 | -61.5601 | -0.27008 | -0.082397 | 2.6001 | -0.19684 | -8.638 | -0.26093 | -0.032043 | 2.8702 | 63.1348 | 63.1302 | 115.1047 | 123.6603 | 2.6001 | 123.7106 | 78.4195 | -0.26093 | 123.6603 | 2.6001 | 78.4195 | 115.1047 | 123.7106 | -124.0128 | -124.0036
2156.7188 | 123.9853 | -61.2762 | 62.3932 | -0.17677 | 0.014529 | 0.018113 | 0.011251 | 0.062598 | 0.0013757 | 0.085031 | -58.7219 | 62.3245 | -61.5005 | -61.4914 | 53.8605 | 17.07 | 1.5976 | 1.9684 | 62.3428 | -61.5372 | -0.2243 | -0.068664 | 2.5543 | -0.21515 | -8.5327 | -0.26093 | -0.050354 | 2.7786 | 62.8738 | 63.2446 | 115.1367 | 123.6008 | 2.5543 | 123.6191 | 78.3463 | -0.26093 | 123.6008 | 2.5543 | 78.3463 | 115.1367 | 123.6191 | -123.8937 | -123.9304
2157.7188 | 123.8617 | -61.322 | 62.4207 | -0.23018 | 0.014101 | 0.01555 | 0.0089016 | 0.059821 | -0.00011953 | 0.08204 | -58.5983 | 62.3383 | -61.5509 | -61.4822 | 53.7415 | 17.07 | 1.8311 | 1.9638 | 62.3932 | -61.5463 | -0.22888 | -0.082397 | 2.7237 | -0.16022 | -8.6792 | -0.22431 | -0.027466 | 2.9526 | 63.1531 | 63.2858 | 115.0635 | 123.6603 | 2.7237 | 123.7152 | 78.392 | -0.22431 | 123.6603 | 2.7237 | 78.392 | 115.0635 | 123.7152 | -123.9716 | -123.967
2158.7188 | 123.8846 | -61.3129 | 62.4344 | -0.17677 | 0.017306 | 0.014695 | 0.012106 | 0.063452 | 0.0015893 | 0.08204 | -58.7265 | 62.4023 | -61.5555 | -61.5005 | 53.7003 | 16.7679 | 2.1881 | 1.9592 | 62.4344 | -61.5463 | -0.24262 | -0.032043 | 2.5864 | -0.18768 | -8.7341 | -0.23346 | 0 | 2.829 | 63.501 | 63.2721 | 115.0131 | 123.7152 | 2.5864 | 123.7473 | 78.0807 | -0.23346 | 123.7152 | 2.5864 | 78.0807 | 115.0131 | 123.7473 | -123.9899 | -123.9807
2159.7188 | 123.9532 | -61.2625 | 62.3795 | -1.1533 | 0.011965 | 0.016191 | 0.011679 | 0.061957 | 0.00094847 | 0.083322 | -58.6945 | 62.2971 | -61.5555 | -61.3998 | 53.8605 | 17.0929 | 1.7303 | 2.124 | 62.3474 | -61.5005 | -0.29297 | -0.082398 | 2.5681 | -0.13733 | -8.519 | -0.23804 | -0.032044 | 2.861 | 62.9929 | 63.3865 | 115.123 | 123.5596 | 2.5681 | 123.6099 | 78.3554 | -0.23804 | 123.5596 | 2.5681 | 78.3554 | 115.123 | 123.6099 | -123.9349 | -123.88
2160.7188 | 123.9487 | -61.2946 | 62.4207 | -0.19966 | 0.011965 | 0.015122 | 0.008688 | 0.063666 | 9.4068e-05 | 0.081826 | -58.6441 | 62.2833 | -61.5463 | -61.4182 | 53.8879 | 16.9876 | 1.8631 | 2.1973 | 62.3703 | -61.5234 | -0.25177 | -0.13733 | 2.6505 | -0.1236 | -8.5327 | -0.22888 | -0.050354 | 2.9022 | 63.1577 | 63.4918 | 115.1825 | 123.5779 | 2.6505 | 123.6649 | 78.2822 | -0.22888 | 123.5779 | 2.6505 | 78.2822 | 115.1825 | 123.6649 | -123.967 | -123.9441
2161.7188 | 123.8937 | -61.2991 | 62.439 | -0.22255 | 0.014315 | 0.01555 | 0.011679 | 0.060675 | 0.0013757 | 0.083322 | -58.6853 | 62.3245 | -61.5555 | -61.4777 | 53.8422 | 17.0975 | 2.0966 | 2.2064 | 62.3749 | -61.5509 | -0.25635 | -0.11444 | 2.6138 | -0.17853 | -8.5968 | -0.25177 | -0.064087 | 2.8702 | 63.3957 | 63.5056 | 115.1413 | 123.6237 | 2.6138 | 123.674 | 78.3966 | -0.25177 | 123.6237 | 2.6138 | 78.3966 | 115.1413 | 123.674 | -123.9944 | -123.9899
2162.7188 | 123.8892 | -61.2717 | 62.4161 | -0.2607 | 0.014101 | 0.015763 | 0.0091152 | 0.060034 | -0.00033333 | 0.082894 | -58.6121 | 62.3154 | -61.5326 | -61.4731 | 53.8834 | 16.9693 | 2.0599 | 2.3438 | 62.384 | -61.5417 | -0.26093 | -0.10071 | 2.6596 | -0.20142 | -8.5327 | -0.27008 | -0.032044 | 2.9205 | 63.3316 | 63.6154 | 115.155 | 123.587 | 2.6596 | 123.6557 | 78.241 | -0.27008 | 123.587 | 2.6596 | 78.241 | 115.155 | 123.6557 | -123.9487 | -123.9578
2163.7344 | 123.8617 | -61.322 | 62.4069 | -0.0089264 | 0.017306 | 0.021531 | 0.016165 | 0.061316 | -0.00011953 | 0.08204 | -58.6487 | 62.3932 | -61.5692 | -61.4777 | 53.801 | 17.0425 | 1.9089 | 2.1378 | 62.3749 | -61.5738 | -0.24719 | -0.013733 | 2.6733 | -0.15564 | -8.606 | -0.25177 | -0.032043 | 2.9205 | 63.2309 | 63.4598 | 115.123 | 123.7152 | 2.6733 | 123.6969 | 78.3646 | -0.25177 | 123.7152 | 2.6733 | 78.3646 | 115.123 | 123.6969 | -123.9761 | -123.9807
2164.7188 | 123.9807 | -61.2762 | 62.3749 | -0.19966 | 0.014101 | 0.017472 | 0.00527 | 0.062384 | 0.00052127 | 0.082253 | -58.5754 | 62.2879 | -61.5509 | -61.5189 | 53.8971 | 17.0425 | 1.8402 | 2.33 | 62.3428 | -61.5051 | -0.27466 | -0.086975 | 2.7008 | -0.24261 | -8.4778 | -0.22888 | -0.032044 | 2.9755 | 63.1165 | 63.6063 | 115.1733 | 123.5641 | 2.7008 | 123.6191 | 78.3188 | -0.22888 | 123.5641 | 2.7008 | 78.3188 | 115.1733 | 123.6191 | -123.9258 | -123.88
2165.7188 | 123.8617 | -61.3174 | 62.4023 | 0.04448 | 0.018374 | 0.022172 | 0.015738 | 0.063666 | -0.00033333 | 0.082894 | -58.7723 | 62.3611 | -61.6013 | -61.5417 | 53.5721 | 16.7953 | 2.005 | 2.0782 | 62.384 | -61.5509 | -0.28381 | -0.041199 | 2.5452 | -0.2243 | -8.8303 | -0.23346 | -0.018311 | 2.829 | 63.3224 | 63.3957 | 114.8895 | 123.6786 | 2.5452 | 123.7015 | 78.1128 | -0.23346 | 123.6786 | 2.5452 | 78.1128 | 114.8895 | 123.7015 | -124.0036 | -123.9532
2166.7188 | 123.9807 | -61.2442 | 62.3795 | 0.2581 | 0.014315 | 0.012345 | 0.0071926 | 0.063452 | -0.0016149 | 0.081613 | -58.5709 | 62.2787 | -61.5417 | -61.3953 | 53.8742 | 17.0517 | 1.9501 | 2.2385 | 62.3611 | -61.5189 | -0.29755 | -0.10071 | 2.6733 | -0.15106 | -8.5052 | -0.27466 | -0.018311 | 2.9709 | 63.1943 | 63.4827 | 115.1184 | 123.523 | 2.6733 | 123.6053 | 78.2959 | -0.27466 | 123.523 | 2.6733 | 78.2959 | 115.1184 | 123.6053 | -123.9212 | -123.8983
2167.7188 | 123.9899 | -61.2488 | 62.4023 | -3.3048 | 0.013247 | 0.020677 | 0.0089016 | 0.06153 | 0.00073487 | 0.08204 | -58.7402 | 62.3199 | -61.5555 | -61.4227 | 53.9429 | 17.1844 | 2.0554 | 2.3438 | 62.3383 | -61.5234 | -0.3067 | -0.082398 | 2.5085 | -0.17395 | -8.4595 | -0.27466 | -0.064087 | 2.8152 | 63.3041 | 63.5925 | 115.1916 | 123.5687 | 2.5085 | 123.587 | 78.4332 | -0.27466 | 123.5687 | 2.5085 | 78.4332 | 115.1916 | 123.587 | -123.9578 | -123.9258
2168.7188 | 123.8709 | -61.3129 | 62.4664 | -0.23018 | 0.01346 | 0.011918 | 0.01296 | 0.060248 | -0.00054693 | 0.082467 | -58.5205 | 62.4069 | -61.5372 | -61.4914 | 53.8284 | 16.9693 | 2.179 | 2.2202 | 62.3886 | -61.5829 | -0.2243 | -0.05951 | 2.7924 | -0.17853 | -8.638 | -0.27008 | -0.07782 | 3.0167 | 63.4918 | 63.533 | 115.1413 | 123.7198 | 2.7924 | 123.7015 | 78.2822 | -0.27008 | 123.7198 | 2.7924 | 78.2822 | 115.1413 | 123.7015 | -124.0036 | -124.0494
2169.7188 | 123.912 | -61.3129 | 62.4435 | -0.24544 | 0.013674 | 0.016191 | 0.01232 | 0.063025 | -0.0016149 | 0.08204 | -58.6578 | 62.3016 | -61.5692 | -61.4639 | 53.7643 | 17.038 | 2.1194 | 2.3254 | 62.3703 | -61.5555 | -0.25635 | -0.14191 | 2.655 | -0.15106 | -8.6792 | -0.24262 | -0.073242 | 2.9114 | 63.4323 | 63.6383 | 115.0772 | 123.6145 | 2.655 | 123.6832 | 78.3508 | -0.24262 | 123.6145 | 2.655 | 78.3508 | 115.0772 | 123.6832 | -124.0128 | -123.999
2170.7188 | 123.8617 | -61.3083 | 62.4481 | -0.19966 | 0.014101 | 0.015336 | 0.011892 | 0.061103 | 9.4068e-05 | 0.079049 | -58.699 | 62.3291 | -61.5601 | -61.5005 | 53.8239 | 17.0471 | 2.2888 | 2.3392 | 62.3932 | -61.5646 | -0.25177 | -0.11902 | 2.6093 | -0.19226 | -8.6243 | -0.25635 | -0.054932 | 2.861 | 63.5971 | 63.6475 | 115.1321 | 123.6374 | 2.6093 | 123.7015 | 78.3554 | -0.25635 | 123.6374 | 2.6093 | 78.3554 | 115.1321 | 123.7015 | -124.0082 | -124.0128
2171.7188 | 123.8525 | -61.3037 | 62.4527 | -0.26833 | 0.015597 | 0.016618 | 0.012747 | 0.060034 | 9.4068e-05 | 0.080331 | -58.699 | 62.3611 | -61.5784 | -61.5234 | 53.714 | 17.0151 | 2.1973 | 2.3209 | 62.3978 | -61.5555 | -0.27466 | -0.091553 | 2.6047 | -0.21973 | -8.7387 | -0.25177 | -0.054932 | 2.8793 | 63.501 | 63.6246 | 115.0177 | 123.6649 | 2.6047 | 123.7015 | 78.3188 | -0.25177 | 123.6649 | 2.6047 | 78.3188 | 115.0177 | 123.7015 | -124.0311 | -124.0082
2172.7188 | 123.999 | -61.2534 | 62.3932 | -0.09285 | 0.012179 | 0.013627 | 0.0091152 | 0.060675 | -0.00011953 | 0.081185 | -58.6029 | 62.2925 | -61.5417 | -61.4319 | 53.8467 | 17.038 | 2.0462 | 2.4948 | 62.3199 | -61.5189 | -0.28839 | -0.10071 | 2.6505 | -0.17853 | -8.5464 | -0.2655 | -0.073242 | 2.9388 | 63.2996 | 63.7482 | 115.1001 | 123.5458 | 2.6505 | 123.5733 | 78.2913 | -0.2655 | 123.5458 | 2.6505 | 78.2913 | 115.1001 | 123.5733 | -123.9349 | -123.912
2173.7188 | 123.8617 | -61.3266 | 62.4115 | -0.062332 | 0.014315 | 0.012773 | 0.016592 | 0.061743 | -0.00033333 | 0.081826 | -58.6029 | 62.3566 | -61.5692 | -61.4868 | 53.8742 | 17.1112 | 2.092 | 2.33 | 62.3566 | -61.5829 | -0.24262 | -0.054932 | 2.7237 | -0.16022 | -8.5373 | -0.25635 | -0.054932 | 2.9663 | 63.4186 | 63.6566 | 115.2008 | 123.6832 | 2.7237 | 123.6832 | 78.4378 | -0.25635 | 123.6832 | 2.7237 | 78.4378 | 115.2008 | 123.6832 | -123.9807 | -123.9944
2174.7188 | 124.0082 | -61.2762 | 62.3749 | -0.15388 | 0.013674 | 0.016618 | 0.0091152 | 0.062384 | -0.00011953 | 0.083108 | -58.5617 | 62.2787 | -61.5555 | -61.3861 | 53.9886 | 17.3584 | 1.9226 | 2.4445 | 62.3383 | -61.5143 | -0.27924 | -0.09613 | 2.7145 | -0.10986 | -8.3862 | -0.23804 | -0.036621 | 2.9938 | 63.1989 | 63.7207 | 115.2649 | 123.555 | 2.7145 | 123.6145 | 78.6346 | -0.23804 | 123.555 | 2.7145 | 78.6346 | 115.2649 | 123.6145 | -123.9304 | -123.8892
2175.7188 | 123.999 | -61.2625 | 62.352 | -0.10811 | 0.014956 | 0.015763 | 0.0082608 | 0.060675 | 0.00073487 | 0.081185 | -58.548 | 62.265 | -61.5509 | -61.4182 | 53.9841 | 17.2211 | 1.9089 | 2.3987 | 62.3154 | -61.5417 | -0.28839 | -0.086975 | 2.7145 | -0.15564 | -8.3679 | -0.27924 | -0.036621 | 3.0029 | 63.1714 | 63.6612 | 115.2466 | 123.5275 | 2.7145 | 123.5779 | 78.4836 | -0.27924 | 123.5275 | 2.7145 | 78.4836 | 115.2466 | 123.5779 | -123.9029 | -123.8937
2176.7188 | 123.9716 | -61.3083 | 62.3749 | -0.0089264 | 0.015169 | 0.0132 | 0.0082608 | 0.059394 | 0.0015893 | 0.080544 | -58.7082 | 62.2742 | -61.5829 | -61.4685 | 53.9795 | 17.2989 | 1.8402 | 2.2705 | 62.3291 | -61.5463 | -0.27466 | -0.10071 | 2.6001 | -0.16022 | -8.3954 | -0.23804 | -0.045776 | 2.8748 | 63.1485 | 63.5788 | 115.2878 | 123.5825 | 2.6001 | 123.6374 | 78.6072 | -0.23804 | 123.5825 | 2.6001 | 78.6072 | 115.2878 | 123.6374 | -123.9578 | -123.9212
2177.7188 | 123.9899 | -61.2671 | 62.3749 | -0.08522 | 0.011538 | 0.017045 | 0.0080472 | 0.061743 | 0.0022303 | 0.080544 | -58.6578 | 62.2696 | -61.5829 | -61.4319 | 54.0344 | 17.5003 | 1.9043 | 2.4628 | 62.3199 | -61.5509 | -0.31586 | -0.10529 | 2.6093 | -0.16479 | -8.3405 | -0.28381 | -0.054932 | 2.9251 | 63.1714 | 63.7299 | 115.3015 | 123.5367 | 2.6093 | 123.587 | 78.7674 | -0.28381 | 123.5367 | 2.6093 | 78.7674 | 115.3015 | 123.587 | -123.9578 | -123.9258
2178.7188 | 123.7885 | -61.3083 | 62.4527 | -0.16151 | 0.016024 | 0.013413 | 0.013174 | 0.060889 | 0.00073487 | 0.079904 | -58.6349 | 62.384 | -61.5601 | -61.5005 | 53.952 | 17.3538 | 2.0828 | 2.1744 | 62.3749 | -61.5738 | -0.25177 | -0.068665 | 2.6733 | -0.19226 | -8.5007 | -0.2655 | -0.07782 | 2.9251 | 63.3911 | 63.4827 | 115.2603 | 123.6923 | 2.6733 | 123.6832 | 78.6621 | -0.2655 | 123.6923 | 2.6733 | 78.6621 | 115.2603 | 123.6832 | -124.0128 | -124.0265
2179.7188 | 123.9212 | -61.2946 | 62.3932 | -0.23781 | 0.01346 | 0.0132 | 0.0095424 | 0.061316 | 0.0026575 | 0.082467 | -58.6121 | 62.2879 | -61.5601 | -61.4365 | 53.9337 | 17.5049 | 1.9775 | 2.3849 | 62.3428 | -61.528 | -0.2655 | -0.10529 | 2.6825 | -0.14191 | -8.4595 | -0.23346 | -0.050354 | 2.948 | 63.2721 | 63.6795 | 115.2283 | 123.5825 | 2.6825 | 123.6374 | 78.7994 | -0.23346 | 123.5825 | 2.6825 | 78.7994 | 115.2283 | 123.6374 | -123.9532 | -123.9212
2180.7188 | 123.9716 | -61.2946 | 62.3932 | -0.16914 | 0.013888 | 0.014268 | 0.0095424 | 0.060675 | 0.0020167 | 0.08204 | -58.6395 | 62.265 | -61.5692 | -61.0977 | 54.1763 | 17.4316 | 1.9135 | 2.3987 | 62.3199 | -61.5234 | -0.27466 | -0.12817 | 2.655 | 0.19684 | -8.2169 | -0.22888 | -0.073242 | 2.9297 | 63.208 | 63.6932 | 115.4709 | 123.5596 | 2.655 | 123.6145 | 78.7262 | -0.22888 | 123.5596 | 2.655 | 78.7262 | 115.4709 | 123.6145 | -123.9624 | -123.9166
2181.7188 | 123.999 | -61.2579 | 62.4207 | -0.16151 | 0.013674 | 0.014482 | 0.013174 | 0.058325 | -0.00033333 | 0.082894 | -58.6121 | 62.2604 | -61.5417 | -61.3724 | 53.9978 | 17.5873 | 1.9226 | 2.3621 | 62.3199 | -61.5143 | -0.28381 | -0.16022 | 2.6459 | -0.11444 | -8.4229 | -0.25635 | -0.10071 | 2.9297 | 63.1805 | 63.62 | 115.2557 | 123.5184 | 2.6459 | 123.5779 | 78.8452 | -0.25635 | 123.5184 | 2.6459 | 78.8452 | 115.2557 | 123.5779 | -123.9624 | -123.9349
2182.7188 | 123.9807 | -61.2717 | 62.3886 | -0.10811 | 0.01581 | 0.012132 | 0.0095424 | 0.058539 | -0.00054693 | 0.081826 | -58.7173 | 62.2742 | -61.5463 | -61.4319 | 53.9246 | 17.5919 | 1.8494 | 2.298 | 62.3154 | -61.5463 | -0.27466 | -0.11444 | 2.5543 | -0.16022 | -8.4641 | -0.27466 | -0.073242 | 2.829 | 63.121 | 63.5696 | 115.1962 | 123.5458 | 2.5543 | 123.587 | 78.8635 | -0.27466 | 123.5458 | 2.5543 | 78.8635 | 115.1962 | 123.587 | -123.9349 | -123.9349
2183.7344 | 123.9349 | -61.3083 | 62.3611 | -0.13863 | 0.016878 | 0.018327 | 0.01766 | 0.060462 | 0.0020167 | 0.081399 | -58.6578 | 62.3932 | -61.5692 | -61.4365 | 53.9474 | 17.5323 | 2.005 | 2.3071 | 62.3703 | -61.6013 | -0.26093 | 0.032043 | 2.6505 | -0.12817 | -8.4137 | -0.29297 | 0.009155 | 2.9114 | 63.3133 | 63.6154 | 115.2557 | 123.7015 | 2.6505 | 123.6786 | 78.8406 | -0.29297 | 123.7015 | 2.6505 | 78.8406 | 115.2557 | 123.6786 | -123.9304 | -123.9624
2184.7188 | 123.9304 | -61.3083 | 62.3749 | 0.029221 | 0.015169 | 0.014695 | 0.0089016 | 0.062384 | 0.0035121 | 0.080972 | -58.7082 | 62.2742 | -61.5692 | -61.4914 | 54.039 | 17.6468 | 2.0874 | 2.5177 | 62.3657 | -61.5005 | -0.26093 | -0.10071 | 2.6001 | -0.1831 | -8.3359 | -0.19226 | -0.009155 | 2.861 | 63.3957 | 63.826 | 115.3473 | 123.5825 | 2.6001 | 123.674 | 78.9551 | -0.19226 | 123.5825 | 2.6001 | 78.9551 | 115.3473 | 123.674 | -123.9441 | -123.8754
2185.7188 | 123.9304 | -61.3129 | 62.3749 | -0.0012969 | 0.01346 | 0.014054 | 0.0097562 | 0.060034 | 0.0022303 | 0.081185 | -58.7128 | 62.2833 | -61.5784 | -61.4822 | 54.1626 | 17.7017 | 1.9867 | 2.4353 | 62.3108 | -61.5417 | -0.2655 | -0.091553 | 2.6001 | -0.16937 | -8.2123 | -0.22888 | -0.064087 | 2.8656 | 63.2996 | 63.7482 | 115.4755 | 123.5962 | 2.6001 | 123.6237 | 79.0146 | -0.22888 | 123.5962 | 2.6001 | 79.0146 | 115.4755 | 123.6237 | -123.9532 | -123.9166
2186.7188 | 123.9532 | -61.3083 | 62.3611 | -0.20729 | 0.014742 | 0.013413 | 0.0091152 | 0.058539 | 0.00094847 | 0.084603 | -58.7219 | 62.2787 | -61.5646 | -61.4777 | 53.9978 | 17.6468 | 2.1011 | 2.4216 | 62.3245 | -61.5417 | -0.25635 | -0.082397 | 2.5864 | -0.16937 | -8.3633 | -0.23346 | -0.036621 | 2.8427 | 63.4094 | 63.7299 | 115.3061 | 123.587 | 2.5864 | 123.6328 | 78.9551 | -0.23346 | 123.587 | 2.5864 | 78.9551 | 115.3061 | 123.6328 | -123.9258 | -123.9029
2187.7188 | 123.9578 | -61.2854 | 62.3886 | -0.27596 | 0.011324 | 0.014482 | 0.0082608 | 0.059821 | 0.0020167 | 0.082894 | -58.7402 | 62.2925 | -61.5555 | -61.4731 | 54.0482 | 17.5919 | 1.9592 | 2.449 | 62.2971 | -61.5646 | -0.27008 | -0.096131 | 2.5452 | -0.18768 | -8.3405 | -0.27924 | -0.091553 | 2.8152 | 63.2446 | 63.7344 | 115.3336 | 123.5779 | 2.5452 | 123.5825 | 78.8773 | -0.27924 | 123.5779 | 2.5452 | 78.8773 | 115.3336 | 123.5825 | -123.9441 | -123.9532
2188.7188 | 123.967 | -61.2991 | 62.3749 | -2.7174 | 0.014742 | 0.021104 | 0.011038 | 0.060248 | -0.00076053 | 0.07969 | -58.9508 | 62.3062 | -61.5646 | -61.4456 | 54.0665 | 17.9169 | 1.9318 | 2.4628 | 62.3291 | -61.5463 | -0.2655 | -0.068665 | 2.3483 | -0.14649 | -8.3084 | -0.24719 | -0.045776 | 2.6138 | 63.2309 | 63.7619 | 115.3656 | 123.6053 | 2.3483 | 123.6282 | 79.216 | -0.24719 | 123.6053 | 2.3483 | 79.216 | 115.3656 | 123.6282 | -123.9395 | -123.9212
2189.7188 | 123.8525 | -61.2854 | 62.3657 | -0.047073 | 0.013674 | 0.012559 | 0.0097562 | 0.058325 | 0.0022303 | 0.080758 | -58.8089 | 62.265 | -61.5555 | -61.4777 | 54.0939 | 17.7246 | 1.9135 | 2.5085 | 62.3199 | -61.5463 | -0.27008 | -0.10071 | 2.4765 | -0.19226 | -8.2718 | -0.26093 | -0.045777 | 2.7466 | 63.1989 | 63.7939 | 115.3793 | 123.5504 | 2.4765 | 123.6053 | 79.01 | -0.26093 | 123.5504 | 2.4765 | 79.01 | 115.3793 | 123.6053 | -123.9212 | -123.912
2190.7188 | 123.9944 | -61.2625 | 62.3749 | -0.047073 | 0.012606 | 0.014695 | 0.0074062 | 0.061316 | 0.0011621 | 0.081399 | -58.7448 | 62.265 | -61.5555 | -61.4182 | 54.0848 | 17.6743 | 2.0004 | 2.5681 | 62.3062 | -61.5326 | -0.29297 | -0.10986 | 2.5177 | -0.15564 | -8.2901 | -0.27008 | -0.068665 | 2.8107 | 63.2629 | 63.8306 | 115.3473 | 123.5275 | 2.5177 | 123.5687 | 78.9368 | -0.27008 | 123.5275 | 2.5177 | 78.9368 | 115.3473 | 123.5687 | -123.9304 | -123.9075
2191.7188 | 123.9258 | -61.2946 | 62.3749 | 0.12077 | 0.012606 | 0.013413 | 0.010611 | 0.060034 | 0.0013757 | 0.081826 | -58.7677 | 62.2833 | -61.5784 | -61.4868 | 53.9017 | 17.5735 | 1.9089 | 2.3483 | 62.3016 | -61.5372 | -0.28381 | -0.091553 | 2.5269 | -0.19226 | -8.4732 | -0.24261 | -0.073242 | 2.8107 | 63.2034 | 63.6429 | 115.1962 | 123.5779 | 2.5269 | 123.5962 | 78.8681 | -0.24261 | 123.5779 | 2.5269 | 78.8681 | 115.1962 | 123.5962 | -123.9532 | -123.912
2192.7188 | 123.9487 | -61.2946 | 62.3749 | 1.372 | 0.016878 | 0.012773 | 0.008688 | 0.062384 | 0.0018031 | 0.081826 | -58.6807 | 62.2696 | -61.5601 | -61.4868 | 53.9474 | 17.6971 | 1.8585 | 2.3712 | 62.3062 | -61.5509 | -0.2655 | -0.10529 | 2.6138 | -0.19226 | -8.4274 | -0.25635 | -0.068665 | 2.8793 | 63.1531 | 63.6658 | 115.242 | 123.5641 | 2.6138 | 123.6008 | 78.9917 | -0.25635 | 123.5641 | 2.6138 | 78.9917 | 115.242 | 123.6008 | -123.9349 | -123.9258
2193.7188 | 123.9761 | -61.2717 | 62.384 | -0.039444 | 0.012179 | 0.011277 | 0.0091152 | 0.060462 | 0.0022303 | 0.07969 | -58.7402 | 62.2971 | -61.5463 | -61.4273 | 53.9612 | 17.5415 | 1.9226 | 2.4948 | 62.3062 | -61.5326 | -0.27466 | -0.086975 | 2.5314 | -0.15564 | -8.4229 | -0.26093 | -0.07782 | 2.8061 | 63.1943 | 63.7665 | 115.2328 | 123.5687 | 2.5314 | 123.5779 | 78.8132 | -0.26093 | 123.5687 | 2.5314 | 78.8132 | 115.2328 | 123.5779 | -123.9304 | -123.9166
2194.7188 | 123.9624 | -61.2991 | 62.3611 | 0.11314 | 0.014742 | 0.015336 | 0.0061246 | 0.058325 | 0.0030847 | 0.081185 | -58.7357 | 62.2742 | -61.5646 | -61.5784 | 53.8193 | 17.5186 | 1.8723 | 2.3712 | 62.2787 | -61.5784 | -0.2655 | -0.086975 | 2.5635 | -0.27924 | -8.5419 | -0.27924 | -0.082397 | 2.829 | 63.1714 | 63.6703 | 115.1184 | 123.5733 | 2.5635 | 123.5779 | 78.8177 | -0.27924 | 123.5733 | 2.5635 | 78.8177 | 115.1184 | 123.5779 | -123.9258 | -123.9395
2195.7188 | 123.8937 | -61.3083 | 62.4115 | -0.17677 | 0.016665 | 0.016831 | 0.013601 | 0.062812 | -0.0011877 | 0.079263 | -58.6945 | 62.3383 | -61.5829 | -61.4502 | 53.9474 | 17.569 | 2.1378 | 2.3804 | 62.3657 | -61.5509 | -0.27466 | -0.073242 | 2.6138 | -0.14191 | -8.4641 | -0.24261 | -0.045776 | 2.8885 | 63.446 | 63.6887 | 115.2557 | 123.6465 | 2.6138 | 123.674 | 78.8773 | -0.24261 | 123.6465 | 2.6138 | 78.8773 | 115.2557 | 123.674 | -123.9944 | -123.9624
2196.7188 | 123.9441 | -61.2991 | 62.3657 | 0.0063326 | 0.014101 | 0.013627 | 0.00527 | 0.06153 | 0.0011621 | 0.082681 | -58.7723 | 62.2604 | -61.5417 | -61.4731 | 54.0527 | 17.7017 | 1.9592 | 2.3849 | 62.3428 | -61.5005 | -0.24262 | -0.10529 | 2.5269 | -0.17395 | -8.313 | -0.20142 | -0.022889 | 2.7695 | 63.2584 | 63.6841 | 115.3519 | 123.5596 | 2.5269 | 123.642 | 79.0009 | -0.20142 | 123.5596 | 2.5269 | 79.0009 | 115.3519 | 123.642 | -123.9075 | -123.8663
2197.7188 | 123.9716 | -61.2671 | 62.3703 | -0.22255 | 0.010683 | 0.015122 | 0.0054836 | 0.058539 | 0.0013757 | 0.082894 | -58.6533 | 62.2833 | -61.5463 | -61.6608 | 54.0756 | 17.7887 | 1.7578 | 2.4124 | 62.2833 | -61.5326 | -0.27924 | -0.086975 | 2.6138 | -0.39368 | -8.2947 | -0.2655 | -0.086975 | 2.8931 | 63.0249 | 63.6795 | 115.3427 | 123.5504 | 2.6138 | 123.5504 | 79.0558 | -0.2655 | 123.5504 | 2.6138 | 79.0558 | 115.3427 | 123.5504 | -123.9166 | -123.9029
2198.7188 | 123.9532 | -61.2854 | 62.4023 | -0.19203 | 0.015169 | 0.013413 | 0.010183 | 0.061957 | 0.00094847 | 0.080117 | -58.5846 | 62.3108 | -61.5143 | -61.3953 | 54.1077 | 17.6147 | 1.8127 | 2.33 | 62.3108 | -61.5372 | -0.22888 | -0.091553 | 2.7008 | -0.10986 | -8.2947 | -0.25177 | -0.091553 | 2.9297 | 63.0981 | 63.6154 | 115.3931 | 123.5962 | 2.7008 | 123.5962 | 78.9001 | -0.25177 | 123.5962 | 2.7008 | 78.9001 | 115.3931 | 123.5962 | -123.9166 | -123.9395
2199.7188 | 123.999 | -61.2762 | 62.3978 | -0.19966 | 0.013247 | 0.012773 | 0.011038 | 0.061103 | -0.00033333 | 0.077981 | -58.5663 | 62.2696 | -61.5601 | -61.171 | 53.9841 | 17.5003 | 1.8768 | 2.3712 | 62.3016 | -61.5189 | -0.28381 | -0.12817 | 2.71 | 0.10529 | -8.4137 | -0.24261 | -0.09613 | 2.9938 | 63.1531 | 63.6475 | 115.2603 | 123.5458 | 2.71 | 123.5779 | 78.7766 | -0.24261 | 123.5458 | 2.71 | 78.7766 | 115.2603 | 123.5779 | -123.9578 | -123.9166
2200.7188 | 123.9441 | -61.3037 | 62.3932 | -0.016556 | 0.014956 | 0.015122 | 0.0089016 | 0.060462 | 0.0015893 | 0.080972 | -58.6258 | 62.265 | -61.5555 | -61.4594 | 54.0253 | 17.6331 | 1.767 | 2.4078 | 62.3016 | -61.5417 | -0.25177 | -0.12817 | 2.6779 | -0.15564 | -8.3679 | -0.23804 | -0.091552 | 2.9297 | 63.0707 | 63.7115 | 115.329 | 123.5687 | 2.6779 | 123.6053 | 78.9368 | -0.23804 | 123.5687 | 2.6779 | 78.9368 | 115.329 | 123.6053 | -123.9487 | -123.9349
2201.7344 | 123.8709 | -61.322 | 62.3886 | -0.23781 | 0.015383 | 0.018327 | 0.018728 | 0.062598 | -0.00054693 | 0.07969 | -58.5434 | 62.4115 | -61.5509 | -61.4548 | 54.0482 | 17.7383 | 1.8677 | 2.2522 | 62.352 | -61.5784 | -0.22888 | 0.022888 | 2.7786 | -0.13275 | -8.3405 | -0.25635 | -0.036621 | 3.0075 | 63.1897 | 63.5742 | 115.3702 | 123.7335 | 2.7786 | 123.674 | 79.0604 | -0.25635 | 123.7335 | 2.7786 | 79.0604 | 115.3702 | 123.674 | -123.9395 | -123.967
2202.7188 | 123.9487 | -61.3037 | 62.3749 | 0.021591 | 0.014315 | 0.015763 | 0.005911 | 0.062812 | -0.00011953 | 0.082253 | -58.6441 | 62.3062 | -61.5875 | -61.4639 | 54.0573 | 17.6514 | 1.8494 | 2.3483 | 62.3245 | -61.5555 | -0.28381 | -0.068665 | 2.6596 | -0.16022 | -8.3176 | -0.25177 | -0.050354 | 2.9434 | 63.1531 | 63.652 | 115.361 | 123.6099 | 2.6596 | 123.6282 | 78.9551 | -0.25177 | 123.6099 | 2.6596 | 78.9551 | 115.361 | 123.6282 | -123.9624 | -123.9304
2203.7188 | 123.9395 | -61.2854 | 62.3795 | -0.19203 | 0.014742 | 0.01555 | 0.010611 | 0.061316 | 9.4068e-05 | 0.080117 | -58.5938 | 62.2787 | -61.5509 | -61.4044 | 54.1306 | 17.7887 | 1.8906 | 2.4353 | 62.3337 | -61.5509 | -0.2655 | -0.10071 | 2.6917 | -0.11902 | -8.2489 | -0.2655 | -0.045777 | 2.9572 | 63.176 | 63.7207 | 115.416 | 123.5641 | 2.6917 | 123.6191 | 79.0741 | -0.2655 | 123.5641 | 2.6917 | 79.0741 | 115.416 | 123.6191 | -123.9304 | -123.9304
2204.7188 | 123.9578 | -61.3037 | 62.384 | -0.069961 | 0.014315 | 0.014482 | 0.0074062 | 0.060462 | -0.0014013 | 0.083749 | -58.7219 | 62.2787 | -61.6013 | -61.4594 | 54.0802 | 17.7155 | 2.0096 | 2.4948 | 62.3154 | -61.5417 | -0.29755 | -0.10529 | 2.5818 | -0.15564 | -8.3038 | -0.23804 | -0.068664 | 2.8793 | 63.3133 | 63.7985 | 115.3839 | 123.5825 | 2.5818 | 123.6191 | 79.0192 | -0.23804 | 123.5825 | 2.5818 | 79.0192 | 115.3839 | 123.6191 | -123.9853 | -123.9258
2205.7188 | 123.9716 | -61.3037 | 62.3795 | -0.031814 | 0.013247 | 0.014268 | 0.0071926 | 0.058966 | 0.0011621 | 0.081185 | -58.6578 | 62.2421 | -61.5692 | -61.4502 | 54.0298 | 17.7704 | 1.918 | 2.4399 | 62.2971 | -61.5463 | -0.2655 | -0.13733 | 2.6459 | -0.14648 | -8.3496 | -0.24262 | -0.082398 | 2.9114 | 63.2217 | 63.7436 | 115.3336 | 123.5458 | 2.6459 | 123.6008 | 79.0741 | -0.24262 | 123.5458 | 2.6459 | 79.0741 | 115.3336 | 123.6008 | -123.9487 | -123.9258
2206.7344 | 123.9075 | -61.3266 | 62.4115 | -0.21492 | 0.017306 | 0.016404 | 0.016806 | 0.062598 | 9.4068e-05 | 0.078195 | -58.6212 | 62.3703 | -61.5417 | -61.4502 | 54.0436 | 17.807 | 2.1011 | 2.4628 | 62.3245 | -61.5967 | -0.21515 | -0.041199 | 2.7054 | -0.1236 | -8.3679 | -0.27008 | -0.086975 | 2.9205 | 63.4277 | 63.7894 | 115.3702 | 123.6969 | 2.7054 | 123.6511 | 79.1336 | -0.27008 | 123.6969 | 2.7054 | 79.1336 | 115.3702 | 123.6511 | -123.9532 | -124.0082
2207.7188 | 123.9853 | -61.2854 | 62.3749 | -0.12337 | 0.01047 | 0.014054 | 0.008688 | 0.062812 | -0.00033333 | 0.082681 | -58.6166 | 62.2513 | -61.5784 | -61.4044 | 54.1214 | 18.0222 | 2.0599 | 2.6093 | 62.3337 | -61.5189 | -0.29297 | -0.1236 | 2.6688 | -0.11902 | -8.2535 | -0.23346 | -0.041199 | 2.9617 | 63.3453 | 63.8947 | 115.4068 | 123.5367 | 2.6688 | 123.6191 | 79.3076 | -0.23346 | 123.5367 | 2.6688 | 79.3076 | 115.4068 | 123.6191 | -123.9532 | -123.8937
2208.7188 | 123.8434 | -61.2946 | 62.4115 | -0.29884 | 0.016878 | 0.015336 | 0.013174 | 0.060889 | -0.0016149 | 0.07969 | -58.6853 | 62.3474 | -61.5784 | -61.4914 | 53.9566 | 17.6239 | 2.5085 | 2.5681 | 62.3657 | -61.5738 | -0.28381 | -0.064087 | 2.6093 | -0.19684 | -8.4549 | -0.27924 | -0.045776 | 2.8931 | 63.8031 | 63.8626 | 115.2512 | 123.642 | 2.6093 | 123.6603 | 78.9185 | -0.27924 | 123.642 | 2.6093 | 78.9185 | 115.2512 | 123.6603 | -123.9899 | -123.9853
2209.7188 | 124.0265 | -61.2946 | 62.3749 | -0.13863 | 0.01282 | 0.012345 | 0.0082608 | 0.061743 | 0.0020167 | 0.07969 | -58.5434 | 62.2742 | -61.5784 | -61.3815 | 54.0619 | 17.7979 | 2.0691 | 2.5818 | 62.3016 | -61.5097 | -0.28381 | -0.10071 | 2.7512 | -0.086975 | -8.313 | -0.21515 | -0.073242 | 3.035 | 63.3636 | 63.8763 | 115.3564 | 123.5687 | 2.7512 | 123.5962 | 79.0924 | -0.21515 | 123.5687 | 2.7512 | 79.0924 | 115.3564 | 123.5962 | -123.9532 | -123.8846
2210.7188 | 124.0265 | -61.2488 | 62.4023 | -0.131 | 0.01282 | 0.011704 | 0.0078336 | 0.060675 | -0.00011953 | 0.081826 | -58.5983 | 62.2696 | -61.5326 | -61.3678 | 53.9246 | 17.7521 | 2.1469 | 2.5452 | 62.3199 | -61.5097 | -0.28381 | -0.13275 | 2.6505 | -0.11902 | -8.4778 | -0.26093 | -0.082398 | 2.9343 | 63.3957 | 63.7939 | 115.1733 | 123.5184 | 2.6505 | 123.5687 | 79.0009 | -0.26093 | 123.5184 | 2.6505 | 79.0009 | 115.1733 | 123.5687 | -123.9349 | -123.912
2211.7344 | 123.8754 | -61.3358 | 62.3886 | 0.029221 | 0.016878 | 0.02089 | 0.018301 | 0.063239 | -0.00033333 | 0.081613 | -58.7173 | 62.3566 | -61.5646 | -61.4914 | 53.952 | 17.7017 | 2.3438 | 2.4261 | 62.3611 | -61.5875 | -0.22888 | -0.032044 | 2.6184 | -0.15564 | -8.4366 | -0.25177 | -0.027466 | 2.8473 | 63.6795 | 63.7619 | 115.2878 | 123.6923 | 2.6184 | 123.6969 | 79.0375 | -0.25177 | 123.6923 | 2.6184 | 79.0375 | 115.2878 | 123.6969 | -123.9532 | -123.9761
2212.7188 | 124.0265 | -61.2717 | 62.3566 | -0.1844 | 0.016024 | 0.011918 | 0.010183 | 0.062171 | -0.00076053 | 0.081185 | -58.5297 | 62.2879 | -61.5509 | -61.3998 | 54.1077 | 17.8299 | 2.7512 | 2.7237 | 62.4023 | -61.4777 | -0.27924 | -0.068664 | 2.742 | -0.12817 | -8.2489 | -0.20599 | 0.045777 | 3.0212 | 64.0228 | 63.9954 | 115.3793 | 123.5596 | 2.742 | 123.674 | 79.1016 | -0.20599 | 123.5596 | 2.742 | 79.1016 | 115.3793 | 123.674 | -123.9075 | -123.8342
2213.7188 | 123.9716 | -61.2854 | 62.384 | -0.14626 | 0.01581 | 0.016191 | 0.010824 | 0.062598 | -0.00054693 | 0.082467 | -58.6075 | 62.2925 | -61.5555 | -61.4182 | 53.9429 | 17.9489 | 2.2751 | 2.4536 | 62.3154 | -61.5372 | -0.27008 | -0.091553 | 2.6779 | -0.13275 | -8.4412 | -0.25177 | -0.068664 | 2.948 | 63.5605 | 63.739 | 115.2283 | 123.5779 | 2.6779 | 123.6008 | 79.2343 | -0.25177 | 123.5779 | 2.6779 | 79.2343 | 115.2283 | 123.6008 | -123.9395 | -123.9212
2214.7188 | 123.9441 | -61.29 | 62.3978 | -0.17677 | 0.015597 | 0.013413 | 0.0099698 | 0.061103 | 9.4068e-05 | 0.081185 | -58.5571 | 62.2833 | -61.5601 | -61.409 | 53.9612 | 17.8253 | 2.1011 | 2.4719 | 62.3383 | -61.5005 | -0.27008 | -0.11444 | 2.7328 | -0.11902 | -8.4366 | -0.21057 | -0.059509 | 3.0029 | 63.3911 | 63.7619 | 115.2512 | 123.5733 | 2.7328 | 123.6282 | 79.1153 | -0.21057 | 123.5733 | 2.7328 | 79.1153 | 115.2512 | 123.6282 | -123.9578 | -123.8983
2215.7188 | 123.9212 | -61.3083 | 62.4207 | -0.20729 | 0.016024 | 0.014054 | 0.011679 | 0.062171 | -0.00033333 | 0.081613 | -58.6441 | 62.2833 | -61.5509 | -61.4319 | 54.0482 | 18.0038 | 2.092 | 2.3026 | 62.3474 | -61.5601 | -0.24261 | -0.13733 | 2.6642 | -0.1236 | -8.3725 | -0.25177 | -0.073242 | 2.9068 | 63.4003 | 63.6108 | 115.3564 | 123.5916 | 2.6642 | 123.6557 | 79.3121 | -0.25177 | 123.5916 | 2.6642 | 79.3121 | 115.3564 | 123.6557 | -123.9716 | -123.9807
2216.7188 | 123.967 | -61.2946 | 62.4207 | -0.19966 | 0.016238 | 0.014482 | 0.012533 | 0.062812 | 0.0015893 | 0.07969 | -58.6395 | 62.2879 | -61.5601 | -61.4273 | 54.0573 | 17.9718 | 2.1927 | 2.3895 | 62.3337 | -61.5234 | -0.2655 | -0.13275 | 2.655 | -0.13275 | -8.3633 | -0.22888 | -0.086975 | 2.9205 | 63.4872 | 63.6841 | 115.3519 | 123.5825 | 2.655 | 123.6282 | 79.2664 | -0.22888 | 123.5825 | 2.655 | 79.2664 | 115.3519 | 123.6282 | -123.9807 | -123.9441
2217.7188 | 123.9304 | -61.2991 | 62.3932 | -0.19966 | 0.015597 | 0.014054 | 0.0097562 | 0.06153 | 0.00030767 | 0.079904 | -58.5571 | 62.2971 | -61.5509 | -61.4273 | 54.1351 | 18.0862 | 2.1332 | 2.3254 | 62.3337 | -61.5189 | -0.25177 | -0.09613 | 2.742 | -0.12817 | -8.2581 | -0.21973 | -0.059509 | 2.9938 | 63.4323 | 63.6246 | 115.4343 | 123.5962 | 2.742 | 123.6328 | 79.3854 | -0.21973 | 123.5962 | 2.742 | 79.3854 | 115.4343 | 123.6328 | -123.9441 | -123.912
2218.7188 | 123.9075 | -61.3174 | 62.3932 | -0.14626 | 0.018374 | 0.014695 | 0.016592 | 0.061316 | -0.0016149 | 0.080331 | -58.5846 | 62.3657 | -61.5784 | -61.4594 | 54.039 | 18.1229 | 2.2659 | 2.4078 | 62.3749 | -61.5921 | -0.26093 | -0.027465 | 2.7328 | -0.14191 | -8.3542 | -0.27466 | -0.01831 | 2.9938 | 63.5834 | 63.7253 | 115.3564 | 123.6832 | 2.7328 | 123.6923 | 79.4403 | -0.27466 | 123.6832 | 2.7328 | 79.4403 | 115.3564 | 123.6923 | -123.9716 | -123.9853
2219.7188 | 123.9075 | -61.2808 | 62.3886 | -0.29121 | 0.015169 | 0.013413 | 0.010183 | 0.063452 | -0.00097413 | 0.082681 | -58.5983 | 62.3062 | -61.5555 | -61.4548 | 54.007 | 18.0542 | 2.3117 | 2.5085 | 62.3566 | -61.528 | -0.27466 | -0.082398 | 2.6825 | -0.17395 | -8.3817 | -0.24719 | -0.032044 | 2.9572 | 63.5925 | 63.7894 | 115.2878 | 123.587 | 2.6825 | 123.6374 | 79.335 | -0.24719 | 123.587 | 2.6825 | 79.335 | 115.2878 | 123.6374 | -123.9441 | -123.9166
2220.7188 | 123.8983 | -61.3358 | 62.3886 | -0.22255 | 0.015597 | 0.01854 | 0.016378 | 0.062812 | -0.0018285 | 0.081826 | -58.6533 | 62.3932 | -61.5738 | -61.4685 | 53.952 | 17.9489 | 2.5131 | 2.5406 | 62.3611 | -61.5738 | -0.23804 | 0.004577 | 2.6825 | -0.13275 | -8.4366 | -0.23804 | -0.027466 | 2.9205 | 63.8489 | 63.8763 | 115.2878 | 123.7289 | 2.6825 | 123.6969 | 79.2847 | -0.23804 | 123.7289 | 2.6825 | 79.2847 | 115.2878 | 123.6969 | -123.9624 | -123.9624
2221.7188 | 123.88 | -61.3129 | 62.3886 | -0.14626 | 0.014742 | 0.014482 | 0.011465 | 0.065802 | 0.00030767 | 0.08204 | -58.6395 | 62.352 | -61.5921 | -61.5189 | 54.0482 | 17.9764 | 2.4765 | 2.417 | 62.3795 | -61.5601 | -0.27924 | -0.036621 | 2.6733 | -0.20599 | -8.3405 | -0.24719 | -0.009155 | 2.9526 | 63.7894 | 63.7299 | 115.361 | 123.6649 | 2.6733 | 123.6923 | 79.2892 | -0.24719 | 123.6649 | 2.6733 | 79.2892 | 115.361 | 123.6923 | -123.9807 | -123.9487
2222.7188 | 123.848 | -61.3266 | 62.4023 | -0.24544 | 0.014529 | 0.014695 | 0.01296 | 0.063239 | 0.00052127 | 0.082467 | -58.6761 | 62.3428 | -61.5967 | -61.5234 | 54.0665 | 17.8802 | 2.4902 | 2.4536 | 62.3383 | -61.5875 | -0.27008 | -0.05951 | 2.6505 | -0.19684 | -8.3359 | -0.26093 | -0.064087 | 2.9205 | 63.8168 | 63.7802 | 115.3931 | 123.6694 | 2.6505 | 123.6649 | 79.2068 | -0.26093 | 123.6694 | 2.6505 | 79.2068 | 115.3931 | 123.6649 | -123.999 | -123.9899
2223.7188 | 123.8663 | -61.3083 | 62.4115 | -0.24544 | 0.015169 | 0.018327 | 0.012106 | 0.061103 | 9.4068e-05 | 0.080544 | -58.6807 | 62.3337 | -61.5921 | -61.5097 | 54.071 | 17.8665 | 2.4628 | 2.4445 | 62.3657 | -61.5738 | -0.28381 | -0.07782 | 2.6276 | -0.20142 | -8.3405 | -0.2655 | -0.045776 | 2.9114 | 63.7711 | 63.7527 | 115.3793 | 123.642 | 2.6276 | 123.674 | 79.1748 | -0.2655 | 123.642 | 2.6276 | 79.1748 | 115.3793 | 123.674 | -124.0036 | -123.9853
2224.7188 | 123.8617 | -61.3129 | 62.3978 | -0.25307 | 0.015169 | 0.011277 | 0.0089016 | 0.063025 | -0.00011953 | 0.080758 | -58.6029 | 62.3657 | -61.5784 | -61.5326 | 54.0482 | 17.9535 | 2.504 | 2.4902 | 62.384 | -61.5692 | -0.2655 | -0.032043 | 2.71 | -0.21973 | -8.3496 | -0.25635 | -0.013733 | 2.9755 | 63.8168 | 63.8031 | 115.361 | 123.6786 | 2.71 | 123.6969 | 79.2664 | -0.25635 | 123.6786 | 2.71 | 79.2664 | 115.361 | 123.6969 | -123.9761 | -123.967
2225.7188 | 123.8846 | -61.3358 | 62.4207 | -0.23781 | 0.015169 | 0.013841 | 0.010611 | 0.062598 | 0.00094847 | 0.082467 | -58.6304 | 62.3703 | -61.5646 | -61.528 | 54.039 | 17.9077 | 2.4628 | 2.4536 | 62.3886 | -61.5784 | -0.22888 | -0.050354 | 2.7054 | -0.19226 | -8.3817 | -0.24262 | -0.032043 | 2.9343 | 63.7985 | 63.7894 | 115.3748 | 123.7061 | 2.7054 | 123.7244 | 79.2435 | -0.24262 | 123.7061 | 2.7054 | 79.2435 | 115.3748 | 123.7244 | -123.9853 | -123.999
2226.7188 | 123.8297 | -61.3312 | 62.4069 | -0.24544 | 0.015597 | 0.015122 | 0.011892 | 0.062384 | -0.00054693 | 0.080758 | -58.6166 | 62.3474 | -61.5829 | -61.5189 | 54.1031 | 18.1229 | 2.5543 | 2.6138 | 62.3703 | -61.5875 | -0.25177 | -0.059509 | 2.7145 | -0.18768 | -8.3038 | -0.25635 | -0.036621 | 2.9663 | 63.8855 | 63.945 | 115.4343 | 123.6786 | 2.7145 | 123.7015 | 79.454 | -0.25635 | 123.6786 | 2.7145 | 79.454 | 115.4343 | 123.7015 | -123.9899 | -123.9944
2227.7188 | 123.8571 | -61.322 | 62.4069 | -0.26833 | 0.016024 | 0.011277 | 0.011679 | 0.060462 | -0.0020421 | 0.081185 | -58.5754 | 62.4023 | -61.5784 | -61.5417 | 54.0756 | 17.9077 | 2.4765 | 2.5497 | 62.4023 | -61.5921 | -0.25635 | -0.004577 | 2.7466 | -0.21973 | -8.3313 | -0.27008 | -0.004577 | 3.0029 | 63.7985 | 63.8718 | 115.3976 | 123.7244 | 2.7466 | 123.7244 | 79.2297 | -0.27008 | 123.7244 | 2.7466 | 79.2297 | 115.3976 | 123.7244 | -123.9853 | -123.999
2228.7188 | 123.8388 | -61.377 | 62.3566 | 0.067368 | 0.018587 | 0.018327 | 0.015738 | 0.064307 | 0.0018031 | 0.082681 | -58.6807 | 62.3611 | -61.5921 | -61.5875 | 54.0115 | 17.9626 | 2.4307 | 2.5543 | 62.352 | -61.6287 | -0.21515 | 0.004578 | 2.6962 | -0.21057 | -8.345 | -0.25177 | -0.004577 | 2.9114 | 63.8077 | 63.9313 | 115.3885 | 123.7381 | 2.6962 | 123.7289 | 79.3396 | -0.25177 | 123.7381 | 2.6962 | 79.3396 | 115.3885 | 123.7289 | -123.9487 | -123.9853
2229.7188 | 123.8388 | -61.3266 | 62.3932 | -0.22255 | 0.016665 | 0.019181 | 0.011038 | 0.060248 | -0.00033333 | 0.081826 | -58.6166 | 62.3611 | -61.6058 | -61.6791 | 54.0253 | 17.9169 | 2.3666 | 2.4765 | 62.3978 | -61.5692 | -0.27924 | -0.032043 | 2.71 | -0.35248 | -8.3679 | -0.24262 | 0.004578 | 2.9892 | 63.6932 | 63.8031 | 115.3519 | 123.6877 | 2.71 | 123.7244 | 79.2435 | -0.24262 | 123.6877 | 2.71 | 79.2435 | 115.3519 | 123.7244 | -123.999 | -123.9624
2230.7188 | 123.8434 | -61.3403 | 62.4023 | -0.1844 | 0.015597 | 0.014695 | 0.010397 | 0.063025 | 0.00073487 | 0.081613 | -58.6258 | 62.3886 | -61.5875 | -61.5646 | 54.1901 | 17.9398 | 2.1835 | 2.4673 | 62.3886 | -61.5875 | -0.24719 | -0.013733 | 2.7145 | -0.2243 | -8.2123 | -0.24719 | -0.013733 | 2.9617 | 63.5239 | 63.8077 | 115.5304 | 123.7289 | 2.7145 | 123.7289 | 79.2801 | -0.24719 | 123.7289 | 2.7145 | 79.2801 | 115.5304 | 123.7289 | -123.9899 | -123.9899
2231.7188 | 123.7701 | -61.3174 | 62.3749 | -0.2607 | 0.016878 | 0.016404 | 0.011038 | 0.061957 | 0.00030767 | 0.082253 | -58.6121 | 62.352 | -61.6058 | -61.5372 | 54.1031 | 17.8024 | 2.4811 | 2.742 | 62.4069 | -61.5509 | -0.28839 | -0.022888 | 2.7054 | -0.21973 | -8.2718 | -0.23346 | 0.032043 | 2.9938 | 63.7985 | 64.0594 | 115.4205 | 123.6694 | 2.7054 | 123.7244 | 79.1199 | -0.23346 | 123.6694 | 2.7054 | 79.1199 | 115.4205 | 123.7244 | -123.9807 | -123.9258
2232.7188 | 123.9349 | -61.322 | 62.4207 | -0.22255 | 0.016238 | 0.019822 | 0.010824 | 0.063239 | 0.0011621 | 0.081399 | -58.5983 | 62.3886 | -61.5738 | -61.5326 | 54.0665 | 17.8665 | 2.5589 | 2.6367 | 62.3886 | -61.5921 | -0.25177 | -0.032043 | 2.7237 | -0.21057 | -8.3542 | -0.27008 | -0.032043 | 2.9755 | 63.8809 | 63.9587 | 115.3885 | 123.7106 | 2.7237 | 123.7106 | 79.1885 | -0.27008 | 123.7106 | 2.7237 | 79.1885 | 115.3885 | 123.7106 | -123.9944 | -124.0128
2233.7188 | 123.8983 | -61.3358 | 62.3978 | -0.031814 | 0.017092 | 0.018754 | 0.014669 | 0.065802 | -0.00033333 | 0.080972 | -58.5571 | 62.3795 | -61.5921 | -61.4868 | 53.9841 | 17.8116 | 2.4216 | 2.5177 | 62.3611 | -61.6013 | -0.25635 | -0.01831 | 2.7786 | -0.15106 | -8.4137 | -0.2655 | -0.036621 | 3.035 | 63.7573 | 63.8535 | 115.3198 | 123.7152 | 2.7786 | 123.6969 | 79.1473 | -0.2655 | 123.7152 | 2.7786 | 79.1473 | 115.3198 | 123.6969 | -123.9899 | -123.999
2234.7188 | 123.8709 | -61.3312 | 62.4069 | -0.36751 | 0.016238 | 0.017686 | 0.011892 | 0.065589 | 0.0028711 | 0.080758 | -58.5846 | 62.384 | -61.6013 | -61.5189 | 54.1397 | 17.8436 | 2.4216 | 2.4765 | 62.3657 | -61.6058 | -0.27008 | -0.022888 | 2.7466 | -0.18768 | -8.2672 | -0.27466 | -0.041198 | 3.0167 | 63.7527 | 63.8077 | 115.4709 | 123.7152 | 2.7466 | 123.6969 | 79.1748 | -0.27466 | 123.7152 | 2.7466 | 79.1748 | 115.4709 | 123.6969 | -124.0082 | -124.0128
2235.7188 | 123.8388 | -61.3358 | 62.4069 | -0.5201 | 0.015169 | 0.017899 | 0.012747 | 0.062812 | 0.0015893 | 0.081399 | -58.6853 | 62.3886 | -61.6013 | -61.5463 | 54.1489 | 17.9031 | 2.4902 | 2.4628 | 62.3886 | -61.5921 | -0.2655 | -0.01831 | 2.6505 | -0.21057 | -8.2581 | -0.25635 | -0.01831 | 2.916 | 63.826 | 63.7985 | 115.4846 | 123.7244 | 2.6505 | 123.7244 | 79.2389 | -0.25635 | 123.7244 | 2.6505 | 79.2389 | 115.4846 | 123.7244 | -124.0082 | -123.999
2236.7188 | 123.8846 | -61.322 | 62.3932 | 1.7687 | 0.016665 | 0.013627 | 0.012747 | 0.064734 | 0.00052127 | 0.081399 | -58.5983 | 62.352 | -61.6013 | -61.5326 | 54.0802 | 17.8207 | 2.5131 | 2.4857 | 62.4115 | -61.5921 | -0.27924 | -0.041198 | 2.7237 | -0.21057 | -8.313 | -0.27008 | 0.018311 | 3.0029 | 63.8351 | 63.8077 | 115.4022 | 123.674 | 2.7237 | 123.7335 | 79.1428 | -0.27008 | 123.674 | 2.7237 | 79.1428 | 115.4022 | 123.7335 | -123.9944 | -123.9853
2237.7188 | 123.8434 | -61.3174 | 62.4069 | -0.22255 | 0.014956 | 0.019181 | 0.012747 | 0.065375 | 0.00073487 | 0.083108 | -58.7769 | 62.3657 | -61.5829 | -61.5921 | 54.1443 | 17.9077 | 2.4765 | 2.4124 | 62.3932 | -61.5829 | -0.2655 | -0.041198 | 2.5406 | -0.27466 | -8.2626 | -0.2655 | -0.013733 | 2.8061 | 63.7939 | 63.7299 | 115.4617 | 123.6832 | 2.5406 | 123.7106 | 79.2252 | -0.2655 | 123.6832 | 2.5406 | 79.2252 | 115.4617 | 123.7106 | -123.9899 | -123.9899
2238.7188 | 123.9212 | -61.322 | 62.3703 | -0.069961 | 0.015383 | 0.019395 | 0.014456 | 0.066016 | -0.00011953 | 0.080758 | -58.461 | 62.3108 | -61.5875 | -61.4914 | 54.1397 | 17.9306 | 2.3621 | 2.4628 | 62.3657 | -61.5921 | -0.2655 | -0.059509 | 2.861 | -0.16937 | -8.2306 | -0.27008 | -0.004577 | 3.1265 | 63.6841 | 63.7848 | 115.4617 | 123.6328 | 2.861 | 123.6877 | 79.2526 | -0.27008 | 123.6328 | 2.861 | 79.2526 | 115.4617 | 123.6877 | -123.9578 | -123.9624
2239.7188 | 123.8709 | -61.3174 | 62.4664 | -0.17677 | 0.016024 | 0.015336 | 0.0097562 | 0.06388 | -0.00011953 | 0.080331 | -58.6395 | 62.3795 | -61.5967 | -61.528 | 54.1306 | 17.8711 | 2.4261 | 2.3758 | 62.3978 | -61.5875 | -0.27924 | -0.086975 | 2.6779 | -0.21057 | -8.3359 | -0.27008 | -0.068665 | 2.9572 | 63.7436 | 63.6932 | 115.448 | 123.6969 | 2.6779 | 123.7152 | 79.1885 | -0.27008 | 123.6969 | 2.6779 | 79.1885 | 115.448 | 123.7152 | -124.0631 | -124.054
2240.7188 | 123.848 | -61.3358 | 62.3932 | -0.24544 | 0.017733 | 0.015763 | 0.0095424 | 0.062598 | 0.00094847 | 0.081613 | -58.6121 | 62.3795 | -61.5738 | -61.5326 | 54.1077 | 17.8757 | 2.5085 | 2.4948 | 62.3932 | -61.5829 | -0.23804 | -0.013732 | 2.7237 | -0.19684 | -8.2855 | -0.24719 | 0 | 2.9617 | 63.8443 | 63.8306 | 115.4434 | 123.7152 | 2.7237 | 123.7289 | 79.2114 | -0.24719 | 123.7152 | 2.7237 | 79.2114 | 115.4434 | 123.7289 | -123.967 | -123.9761
2241.7188 | 123.8663 | -61.3403 | 62.4161 | 0.34203 | 0.016665 | 0.014268 | 0.010183 | 0.062812 | -0.0016149 | 0.079263 | -58.5663 | 62.3383 | -61.6013 | -61.5097 | 54.1397 | 18.0038 | 2.5589 | 2.5406 | 62.3795 | -61.5875 | -0.26093 | -0.07782 | 2.774 | -0.16937 | -8.2764 | -0.24719 | -0.036621 | 3.035 | 63.8992 | 63.8809 | 115.48 | 123.6786 | 2.774 | 123.7198 | 79.3442 | -0.24719 | 123.6786 | 2.774 | 79.3442 | 115.48 | 123.7198 | -124.0173 | -124.0036
2242.7188 | 123.8846 | -61.3449 | 62.4023 | -0.24544 | 0.01346 | 0.016831 | 0.011465 | 0.065589 | 0.0013757 | 0.078835 | -58.6121 | 62.3657 | -61.5875 | -61.5051 | 54.0436 | 17.8986 | 2.6184 | 2.4536 | 62.4161 | -61.5829 | -0.24261 | -0.036621 | 2.7328 | -0.16022 | -8.3588 | -0.23804 | 0.013733 | 2.9755 | 63.9633 | 63.7985 | 115.3885 | 123.7106 | 2.7328 | 123.761 | 79.2435 | -0.23804 | 123.7106 | 2.7328 | 79.2435 | 115.3885 | 123.761 | -123.9899 | -123.9853
2243.7188 | 123.9029 | -61.3312 | 62.3611 | -0.062332 | 0.01581 | 0.019395 | 0.014456 | 0.068793 | -0.00054693 | 0.080972 | -58.4427 | 62.3886 | -61.6013 | -61.4731 | 54.071 | 17.9535 | 2.5131 | 2.6276 | 62.352 | -61.5921 | -0.27008 | 0.027466 | 2.8885 | -0.14191 | -8.2901 | -0.26093 | -0.009155 | 3.1586 | 63.8443 | 63.9587 | 115.4022 | 123.7198 | 2.8885 | 123.6832 | 79.2847 | -0.26093 | 123.7198 | 2.8885 | 79.2847 | 115.4022 | 123.6832 | -123.9624 | -123.9532
2244.7188 | 123.7564 | -61.3266 | 62.4252 | -0.25307 | 0.016024 | 0.01555 | 0.0067654 | 0.065375 | 0.0028711 | 0.080544 | -58.5983 | 62.3291 | -61.6058 | -61.5372 | 54.1031 | 18.0313 | 2.7191 | 2.6184 | 62.4207 | -61.5875 | -0.27924 | -0.09613 | 2.7283 | -0.21057 | -8.3221 | -0.26093 | -0.004578 | 3.0075 | 64.0457 | 63.945 | 115.4297 | 123.6557 | 2.7283 | 123.7473 | 79.3579 | -0.26093 | 123.6557 | 2.7283 | 79.3579 | 115.4297 | 123.7473 | -124.0311 | -124.0128
2245.7188 | 123.8709 | -61.3266 | 62.4023 | -0.11574 | 0.016665 | 0.018968 | 0.0082608 | 0.06388 | -0.00011953 | 0.080331 | -58.6395 | 62.3428 | -61.5875 | -61.5326 | 54.1122 | 18.0222 | 2.5681 | 2.504 | 62.3886 | -61.5784 | -0.26093 | -0.05951 | 2.6871 | -0.20599 | -8.2901 | -0.25177 | -0.013733 | 2.948 | 63.8947 | 63.8306 | 115.4388 | 123.6694 | 2.6871 | 123.7152 | 79.3488 | -0.25177 | 123.6694 | 2.6871 | 79.3488 | 115.4388 | 123.7152 | -123.9899 | -123.9807
2246.7188 | 123.8434 | -61.3083 | 62.3886 | -0.21492 | 0.015597 | 0.013841 | 0.0093288 | 0.063239 | 0.0011621 | 0.081613 | -58.58 | 62.352 | -61.5875 | -61.5097 | 54.0985 | 17.8757 | 2.5452 | 2.5177 | 62.4069 | -61.5738 | -0.27923 | -0.036621 | 2.7283 | -0.20142 | -8.2901 | -0.2655 | 0.01831 | 3.0075 | 63.8535 | 63.826 | 115.4068 | 123.6603 | 2.7283 | 123.7152 | 79.184 | -0.2655 | 123.6603 | 2.7283 | 79.184 | 115.4068 | 123.7152 | -123.9761 | -123.9624
2247.7188 | 123.8663 | -61.3129 | 62.384 | -0.2607 | 0.014742 | 0.020036 | 0.0097562 | 0.062171 | 0.0011621 | 0.081185 | -58.58 | 62.3199 | -61.5967 | -61.5143 | 54.158 | 18.1595 | 2.5314 | 2.5452 | 62.3749 | -61.5738 | -0.28381 | -0.064087 | 2.7328 | -0.20142 | -8.226 | -0.26093 | -0.009155 | 3.0167 | 63.8443 | 63.858 | 115.4709 | 123.6328 | 2.7328 | 123.6877 | 79.4724 | -0.26093 | 123.6328 | 2.7328 | 79.4724 | 115.4709 | 123.6877 | -123.9807 | -123.9578
2248.7188 | 123.8434 | -61.3266 | 62.3703 | -0.20729 | 0.015169 | 0.012345 | 0.014883 | 0.064734 | -0.0014013 | 0.081185 | -58.5297 | 62.384 | -61.5829 | -61.4685 | 54.2221 | 18.1366 | 2.536 | 2.5497 | 62.3657 | -61.5875 | -0.25635 | 0.013733 | 2.7969 | -0.14191 | -8.1482 | -0.26093 | -0.004577 | 3.0533 | 63.8626 | 63.8763 | 115.5487 | 123.7106 | 2.7969 | 123.6923 | 79.4632 | -0.26093 | 123.7106 | 2.7969 | 79.4632 | 115.5487 | 123.6923 | -123.9532 | -123.9578
2249.7188 | 123.8937 | -61.2991 | 62.4527 | -0.27596 | 0.016024 | 0.014054 | 0.010183 | 0.064734 | 0.0015893 | 0.08204 | -58.6075 | 62.3383 | -61.5921 | -61.5417 | 54.158 | 18.0817 | 2.6733 | 2.4902 | 62.4115 | -61.6058 | -0.29297 | -0.11444 | 2.6916 | -0.24262 | -8.2947 | -0.3067 | -0.041199 | 2.9846 | 63.9725 | 63.7894 | 115.4572 | 123.6374 | 2.6916 | 123.7106 | 79.3808 | -0.3067 | 123.6374 | 2.6916 | 79.3808 | 115.4572 | 123.7106 | -124.0448 | -124.0585
2250.7188 | 123.8342 | -61.3586 | 62.4023 | -0.1844 | 0.013888 | 0.01085 | 0.008688 | 0.063452 | 0.0028711 | 0.07969 | -58.6395 | 62.3337 | -61.5692 | -61.5372 | 54.2679 | 18.1549 | 2.6276 | 2.4353 | 62.3932 | -61.5921 | -0.21057 | -0.068665 | 2.7191 | -0.17853 | -8.1345 | -0.23346 | -0.009156 | 2.9297 | 63.9862 | 63.7939 | 115.6265 | 123.6923 | 2.7191 | 123.7518 | 79.5136 | -0.23346 | 123.6923 | 2.7191 | 79.5136 | 115.6265 | 123.7518 | -123.9716 | -123.9944
2251.7188 | 123.8297 | -61.3174 | 62.4161 | -0.10811 | 0.013033 | 0.014268 | 0.0093288 | 0.064734 | -0.00011953 | 0.082681 | -58.5938 | 62.3154 | -61.5784 | -61.5189 | 54.3961 | 18.2465 | 2.7283 | 2.4811 | 62.3749 | -61.5967 | -0.26093 | -0.10071 | 2.7237 | -0.20142 | -8.02 | -0.27924 | -0.041199 | 2.9846 | 64.0457 | 63.7985 | 115.7135 | 123.6328 | 2.7237 | 123.6923 | 79.5639 | -0.27924 | 123.6328 | 2.7237 | 79.5639 | 115.7135 | 123.6923 | -123.9944 | -124.0128
2252.7188 | 123.8617 | -61.3312 | 62.3932 | -0.27596 | 0.015169 | 0.015336 | 0.0099698 | 0.061743 | 0.00052127 | 0.081613 | -58.6349 | 62.3199 | -61.5829 | -61.5143 | 54.245 | 18.1458 | 2.6733 | 2.5635 | 62.3749 | -61.5738 | -0.25177 | -0.073242 | 2.6962 | -0.18311 | -8.1482 | -0.24262 | -0.01831 | 2.948 | 64.0045 | 63.8947 | 115.5762 | 123.6511 | 2.6962 | 123.7061 | 79.4769 | -0.24262 | 123.6511 | 2.6962 | 79.4769 | 115.5762 | 123.7061 | -123.9761 | -123.967
2253.7188 | 123.8846 | -61.3724 | 62.3657 | 0.16655 | 0.019656 | 0.017472 | 0.013174 | 0.064521 | 0.0024439 | 0.081399 | -58.6487 | 62.3383 | -61.6104 | -61.5509 | 54.2267 | 18.1641 | 2.4399 | 2.4948 | 62.3383 | -61.6333 | -0.23804 | -0.027466 | 2.7237 | -0.17853 | -8.139 | -0.26093 | -0.027466 | 2.9617 | 63.8123 | 63.8672 | 115.5991 | 123.7106 | 2.7237 | 123.7106 | 79.5364 | -0.26093 | 123.7106 | 2.7237 | 79.5364 | 115.5991 | 123.7106 | -123.9761 | -123.999
2254.7188 | 123.8983 | -61.3174 | 62.3932 | -0.23018 | 0.013888 | 0.0132 | 0.0099698 | 0.062812 | 0.00094847 | 0.080972 | -58.5617 | 62.3108 | -61.5921 | -61.4868 | 54.3182 | 18.2281 | 2.5909 | 2.6276 | 62.3245 | -61.5921 | -0.27466 | -0.082397 | 2.7557 | -0.16937 | -8.075 | -0.27466 | -0.068664 | 3.0304 | 63.9084 | 63.945 | 115.6357 | 123.6282 | 2.7557 | 123.642 | 79.5456 | -0.27466 | 123.6282 | 2.7557 | 79.5456 | 115.6357 | 123.642 | -123.9853 | -123.9853
2255.7188 | 123.8251 | -61.3266 | 62.4023 | -0.16151 | 0.017306 | 0.0132 | 0.010824 | 0.062812 | 0.00052127 | 0.082253 | -58.6533 | 62.3199 | -61.5692 | -61.5372 | 54.1214 | 18.2922 | 2.7008 | 2.6093 | 62.3703 | -61.5921 | -0.24262 | -0.082398 | 2.6733 | -0.21057 | -8.2809 | -0.2655 | -0.032044 | 2.916 | 64.0274 | 63.9359 | 115.448 | 123.6465 | 2.6733 | 123.6969 | 79.6188 | -0.2655 | 123.6465 | 2.6733 | 79.6188 | 115.448 | 123.6969 | -123.9716 | -123.9944
2256.7188 | 123.8571 | -61.3449 | 62.3886 | -0.1844 | 0.016024 | 0.011277 | 0.011465 | 0.063239 | 0.0022303 | 0.081826 | -58.6075 | 62.3428 | -61.6013 | -61.528 | 54.1763 | 18.3792 | 2.6367 | 2.6367 | 62.3978 | -61.5738 | -0.25635 | -0.045777 | 2.7374 | -0.18311 | -8.2123 | -0.22888 | 0.009155 | 2.9938 | 63.9816 | 63.9816 | 115.5212 | 123.6877 | 2.7374 | 123.7427 | 79.7241 | -0.22888 | 123.6877 | 2.7374 | 79.7241 | 115.5212 | 123.7427 | -123.9899 | -123.9624
2257.7188 | 123.8754 | -61.3403 | 62.3886 | -0.26833 | 0.015383 | 0.015122 | 0.010183 | 0.061103 | -0.00076053 | 0.081399 | -58.6258 | 62.3245 | -61.5829 | -61.5189 | 54.213 | 18.2007 | 2.7237 | 2.6321 | 62.3886 | -61.6013 | -0.24262 | -0.064087 | 2.7145 | -0.17853 | -8.1757 | -0.26093 | 0 | 2.9572 | 64.064 | 63.9725 | 115.5533 | 123.6649 | 2.7145 | 123.7289 | 79.541 | -0.26093 | 123.6649 | 2.7145 | 79.541 | 115.5533 | 123.7289 | -123.9716 | -123.9899
2258.7188 | 123.912 | -61.322 | 62.3749 | -0.069961 | 0.017733 | 0.014482 | 0.016378 | 0.063666 | -0.00033333 | 0.079049 | -58.4885 | 62.3657 | -61.5784 | -61.4685 | 54.2587 | 18.3334 | 2.5497 | 2.6413 | 62.352 | -61.5829 | -0.25635 | -0.009155 | 2.8336 | -0.14648 | -8.1162 | -0.26093 | -0.022888 | 3.0899 | 63.8718 | 63.9633 | 115.5807 | 123.6877 | 2.8336 | 123.674 | 79.6555 | -0.26093 | 123.6877 | 2.8336 | 79.6555 | 115.5807 | 123.674 | -123.9532 | -123.9578
2259.7188 | 123.848 | -61.3449 | 62.3749 | -0.20729 | 0.014529 | 0.019822 | 0.0080472 | 0.063025 | 0.00030767 | 0.080758 | -58.58 | 62.3245 | -61.5784 | -61.5005 | 54.3182 | 18.4158 | 2.7786 | 2.6596 | 62.3657 | -61.5784 | -0.23346 | -0.050354 | 2.7649 | -0.15564 | -8.0566 | -0.23346 | -0.009155 | 2.9984 | 64.1235 | 64.0045 | 115.6631 | 123.6694 | 2.7649 | 123.7106 | 79.7607 | -0.23346 | 123.6694 | 2.7649 | 79.7607 | 115.6631 | 123.7106 | -123.9532 | -123.9532
2260.7188 | 123.8937 | -61.322 | 62.3886 | -0.26833 | 0.015169 | 0.017899 | 0.010183 | 0.064093 | 0.00052127 | 0.081399 | -58.5983 | 62.3337 | -61.5875 | -61.5051 | 54.245 | 18.4799 | 2.7466 | 2.6642 | 62.3474 | -61.6013 | -0.2655 | -0.054932 | 2.7237 | -0.18311 | -8.1436 | -0.27924 | -0.041199 | 2.9892 | 64.0686 | 63.9862 | 115.567 | 123.6557 | 2.7237 | 123.6694 | 79.8019 | -0.27924 | 123.6557 | 2.7237 | 79.8019 | 115.567 | 123.6694 | -123.9761 | -123.9899
2261.7188 | 123.8892 | -61.3312 | 62.3749 | -0.23781 | 0.015597 | 0.015122 | 0.0099698 | 0.060889 | -0.00011953 | 0.082467 | -58.58 | 62.3428 | -61.5875 | -61.4914 | 54.1489 | 18.4525 | 2.6962 | 2.6917 | 62.3657 | -61.5829 | -0.25635 | -0.032044 | 2.7512 | -0.16022 | -8.226 | -0.25177 | -0.009155 | 3.0075 | 64.0274 | 64.0228 | 115.48 | 123.674 | 2.7512 | 123.6969 | 79.7836 | -0.25177 | 123.674 | 2.7512 | 79.7836 | 115.48 | 123.6969 | -123.9624 | -123.9578
2262.7188 | 123.8617 | -61.3358 | 62.4023 | -0.23018 | 0.015383 | 0.015977 | 0.011251 | 0.060462 | 0.0013757 | 0.081613 | -58.6121 | 62.3428 | -61.6013 | -61.5326 | 54.0848 | 18.3426 | 2.7328 | 2.6413 | 62.3886 | -61.5875 | -0.2655 | -0.05951 | 2.7237 | -0.19684 | -8.3176 | -0.25177 | -0.013733 | 2.9892 | 64.0686 | 63.977 | 115.4205 | 123.6786 | 2.7237 | 123.7244 | 79.6783 | -0.25177 | 123.6786 | 2.7237 | 79.6783 | 115.4205 | 123.7244 | -124.0036 | -123.9899
2263.7188 | 123.9853 | -61.3449 | 62.3474 | -0.031814 | 0.016238 | 0.015122 | 0.017447 | 0.063025 | 0.00030767 | 0.080544 | -58.5068 | 62.3611 | -61.5829 | -61.4777 | 54.1397 | 18.3884 | 2.6459 | 2.71 | 62.3566 | -61.6104 | -0.23804 | 0.013733 | 2.8381 | -0.13275 | -8.2077 | -0.2655 | 0.009155 | 3.0762 | 63.9908 | 64.0549 | 115.4846 | 123.7061 | 2.8381 | 123.7015 | 79.7333 | -0.2655 | 123.7061 | 2.8381 | 79.7333 | 115.4846 | 123.7015 | -123.9304 | -123.9578
2264.7188 | 123.8525 | -61.3403 | 62.3886 | -0.22255 | 0.014742 | 0.013841 | 0.0084744 | 0.063025 | 0.00030767 | 0.083749 | -58.5754 | 62.3108 | -61.5829 | -61.5326 | 54.0115 | 18.3289 | 2.8702 | 2.7557 | 62.3566 | -61.6058 | -0.24262 | -0.07782 | 2.7649 | -0.19226 | -8.3771 | -0.2655 | -0.032044 | 3.0075 | 64.2105 | 64.0961 | 115.3519 | 123.6511 | 2.7649 | 123.6969 | 79.6692 | -0.2655 | 123.6511 | 2.7649 | 79.6692 | 115.3519 | 123.6969 | -123.9716 | -123.9944
2265.7188 | 123.8617 | -61.3312 | 62.384 | -0.23781 | 0.017092 | 0.015763 | 0.0089016 | 0.062598 | 0.00052127 | 0.080758 | -58.5983 | 62.3245 | -61.5738 | -61.5051 | 54.1763 | 18.4433 | 2.8107 | 2.7054 | 62.3795 | -61.5967 | -0.24262 | -0.059509 | 2.7328 | -0.17395 | -8.2077 | -0.2655 | -0.004577 | 2.9755 | 64.1418 | 64.0366 | 115.5075 | 123.6557 | 2.7328 | 123.7106 | 79.7745 | -0.2655 | 123.6557 | 2.7328 | 79.7745 | 115.5075 | 123.7106 | -123.9578 | -123.9807
2266.7188 | 123.8342 | -61.3449 | 62.3703 | -0.19966 | 0.014529 | 0.011704 | 0.011679 | 0.06153 | -0.00011953 | 0.08204 | -58.6075 | 62.3428 | -61.5829 | -61.5646 | 54.2816 | 18.6676 | 2.6321 | 2.5818 | 62.3749 | -61.6241 | -0.23804 | -0.027466 | 2.7374 | -0.21973 | -8.0887 | -0.27924 | 0.004578 | 2.9755 | 63.9771 | 63.9267 | 115.6265 | 123.6877 | 2.7374 | 123.7198 | 80.0125 | -0.27924 | 123.6877 | 2.7374 | 80.0125 | 115.6265 | 123.7198 | -123.9532 | -123.9944
2267.7188 | 123.912 | -61.2991 | 62.4069 | -0.26833 | 0.015383 | 0.0089274 | 0.0095424 | 0.061743 | -0.00054693 | 0.081185 | -58.5892 | 62.3199 | -61.5738 | -61.4548 | 54.158 | 18.512 | 2.861 | 2.7832 | 62.3566 | -61.5875 | -0.27466 | -0.086975 | 2.71 | -0.15564 | -8.2489 | -0.28839 | -0.050354 | 2.9846 | 64.1602 | 64.0823 | 115.4572 | 123.6191 | 2.71 | 123.6557 | 79.8111 | -0.28839 | 123.6191 | 2.71 | 79.8111 | 115.4572 | 123.6557 | -123.9807 | -123.9944
2268.7188 | 123.88 | -61.3541 | 62.3703 | -0.131 | 0.015597 | 0.016191 | 0.015951 | 0.063239 | -0.0011877 | 0.079476 | -58.5617 | 62.3474 | -61.5784 | -61.4868 | 54.1718 | 18.5394 | 2.8839 | 2.8107 | 62.3474 | -61.6516 | -0.2243 | -0.022888 | 2.7924 | -0.13275 | -8.1985 | -0.29755 | -0.022888 | 3.0167 | 64.238 | 64.1647 | 115.5258 | 123.7015 | 2.7924 | 123.7015 | 79.8935 | -0.29755 | 123.7015 | 2.7924 | 79.8935 | 115.5258 | 123.7015 | -123.9487 | -124.0219
2269.7188 | 123.8709 | -61.3174 | 62.3886 | -0.29884 | 0.01346 | 0.015763 | 0.010397 | 0.062384 | -0.00033333 | 0.084817 | -58.6258 | 62.3383 | -61.5784 | -61.528 | 54.1626 | 18.4753 | 2.861 | 2.7649 | 62.352 | -61.6058 | -0.26093 | -0.050354 | 2.6917 | -0.21057 | -8.226 | -0.28839 | -0.036621 | 2.9526 | 64.1785 | 64.0823 | 115.48 | 123.6557 | 2.6917 | 123.6694 | 79.7928 | -0.28839 | 123.6557 | 2.6917 | 79.7928 | 115.48 | 123.6694 | -123.967 | -123.9944
2270.7188 | 123.8571 | -61.3495 | 62.3978 | -0.24544 | 0.013888 | 0.019822 | 0.0091152 | 0.062598 | -0.00011953 | 0.082681 | -58.5068 | 62.3154 | -61.6058 | -61.5234 | 54.1168 | 18.5165 | 3.0075 | 2.8336 | 62.3657 | -61.5646 | -0.25635 | -0.082397 | 2.8427 | -0.17395 | -8.2809 | -0.21515 | -0.032043 | 3.0991 | 64.357 | 64.183 | 115.4663 | 123.6649 | 2.8427 | 123.7152 | 79.866 | -0.21515 | 123.6649 | 2.8427 | 79.866 | 115.4663 | 123.7152 | -124.0036 | -123.9624
2271.7188 | 123.9075 | -61.3403 | 62.3795 | -0.21492 | 0.014101 | 0.013413 | 0.01232 | 0.062598 | 0.00030767 | 0.07969 | -58.5892 | 62.3291 | -61.615 | -61.5051 | 54.2358 | 18.6035 | 2.9526 | 2.8015 | 62.384 | -61.5692 | -0.27466 | -0.050354 | 2.7512 | -0.1648 | -8.1436 | -0.22888 | 0.004577 | 3.0258 | 64.2929 | 64.1418 | 115.5762 | 123.6694 | 2.7512 | 123.7244 | 79.9438 | -0.22888 | 123.6694 | 2.7512 | 79.9438 | 115.5762 | 123.7244 | -123.9944 | -123.9487
2272.7188 | 123.8937 | -61.3174 | 62.384 | -0.30647 | 0.015169 | 0.011918 | 0.0093288 | 0.062598 | -0.00033333 | 0.080544 | -58.5205 | 62.2742 | -61.5829 | -61.4731 | 54.1672 | 18.4937 | 2.8427 | 2.829 | 62.3657 | -61.5921 | -0.2655 | -0.10986 | 2.7969 | -0.15564 | -8.2169 | -0.27466 | -0.01831 | 3.0624 | 64.1602 | 64.1464 | 115.4846 | 123.5916 | 2.7969 | 123.6832 | 79.8111 | -0.27466 | 123.5916 | 2.7969 | 79.8111 | 115.4846 | 123.6832 | -123.967 | -123.9761
2273.7188 | 123.88 | -61.3495 | 62.384 | -0.054703 | 0.017947 | 0.016404 | 0.017019 | 0.064521 | 0.00073487 | 0.081826 | -58.5846 | 62.3474 | -61.5601 | -61.496 | 54.0802 | 18.4479 | 2.8702 | 2.6779 | 62.3428 | -61.5921 | -0.21057 | -0.036621 | 2.7649 | -0.14648 | -8.3038 | -0.24261 | -0.041199 | 2.9755 | 64.2197 | 64.0274 | 115.4297 | 123.6969 | 2.7649 | 123.6923 | 79.7974 | -0.24261 | 123.6969 | 2.7649 | 79.7974 | 115.4297 | 123.6923 | -123.9441 | -123.9761
2274.7188 | 123.9487 | -61.3174 | 62.384 | -0.21492 | 0.012179 | 0.017045 | 0.0084744 | 0.062812 | -0.00054693 | 0.082467 | -58.5571 | 62.2787 | -61.5875 | -61.4456 | 54.2679 | 18.5349 | 2.742 | 2.7969 | 62.3428 | -61.5692 | -0.27008 | -0.10529 | 2.7603 | -0.12817 | -8.1162 | -0.25177 | -0.041199 | 3.0304 | 64.0594 | 64.1144 | 115.5853 | 123.5962 | 2.7603 | 123.6603 | 79.8523 | -0.25177 | 123.5962 | 2.7603 | 79.8523 | 115.5853 | 123.6603 | -123.9716 | -123.9532
2275.7188 | 123.9441 | -61.2946 | 62.3749 | -0.15388 | 0.01282 | 0.012773 | 0.0076198 | 0.061743 | 9.4068e-05 | 0.081399 | -58.493 | 62.3016 | -61.5417 | -61.4319 | 54.126 | 18.5349 | 2.6917 | 2.7924 | 62.3428 | -61.5463 | -0.24719 | -0.073242 | 2.8015 | -0.13733 | -8.2489 | -0.25177 | -0.032044 | 3.0487 | 63.9862 | 64.0869 | 115.4205 | 123.5962 | 2.8015 | 123.6374 | 79.8294 | -0.25177 | 123.5962 | 2.8015 | 79.8294 | 115.4205 | 123.6374 | -123.9166 | -123.9212
2276.7188 | 123.8937 | -61.3312 | 62.384 | -0.25307 | 0.014529 | 0.0132 | 0.011038 | 0.061103 | -0.00097413 | 0.080758 | -58.5434 | 62.2742 | -61.5646 | -61.4685 | 54.1122 | 18.512 | 2.8015 | 2.8061 | 62.3566 | -61.5509 | -0.23346 | -0.10986 | 2.7878 | -0.13733 | -8.2718 | -0.21973 | -0.027466 | 3.0212 | 64.1327 | 64.1373 | 115.4434 | 123.6053 | 2.7878 | 123.6877 | 79.8431 | -0.21973 | 123.6053 | 2.7878 | 79.8431 | 115.4434 | 123.6877 | -123.9487 | -123.9349
2277.7188 | 123.9349 | -61.3083 | 62.3795 | -0.23018 | 0.015597 | 0.014268 | 0.0074062 | 0.063452 | -0.0024695 | 0.083322 | -58.5022 | 62.2696 | -61.5921 | -61.4456 | 54.1809 | 18.6356 | 2.774 | 2.8107 | 62.3291 | -61.5555 | -0.28381 | -0.10986 | 2.8061 | -0.13733 | -8.1985 | -0.24719 | -0.050354 | 3.0899 | 64.0823 | 64.119 | 115.4892 | 123.5779 | 2.8061 | 123.6374 | 79.9438 | -0.24719 | 123.5779 | 2.8061 | 79.9438 | 115.4892 | 123.6374 | -123.9716 | -123.9349
2278.7344 | 123.8434 | -61.377 | 62.3795 | -0.0012969 | 0.019228 | 0.017899 | 0.017874 | 0.066657 | 0.00030767 | 0.081185 | -58.5159 | 62.352 | -61.6104 | -61.5463 | 54.0894 | 18.3105 | 2.829 | 2.6733 | 62.3566 | -61.6196 | -0.23346 | -0.027466 | 2.861 | -0.16937 | -8.2901 | -0.24262 | -0.022889 | 3.0945 | 64.2059 | 64.0503 | 115.4663 | 123.7289 | 2.861 | 123.7335 | 79.6875 | -0.24262 | 123.7289 | 2.861 | 79.6875 | 115.4663 | 123.7335 | -123.9899 | -123.999
2279.7188 | 123.9807 | -61.3083 | 62.3703 | -0.20729 | 0.015383 | 0.017259 | 0.0093288 | 0.064521 | -0.00011953 | 0.081399 | -58.5754 | 62.2787 | -61.5921 | -61.441 | 54.1306 | 18.5165 | 2.8564 | 2.8976 | 62.3245 | -61.5555 | -0.28381 | -0.091552 | 2.7328 | -0.13275 | -8.2397 | -0.24719 | -0.045776 | 3.0167 | 64.1647 | 64.2059 | 115.4388 | 123.587 | 2.7328 | 123.6328 | 79.8248 | -0.24719 | 123.587 | 2.7328 | 79.8248 | 115.4388 | 123.6328 | -123.9624 | -123.9258
2280.7188 | 123.8754 | -61.3174 | 62.3886 | -0.2607 | 0.015169 | 0.01854 | 0.010824 | 0.064093 | 0.00073487 | 0.081613 | -58.5709 | 62.3062 | -61.5646 | -61.4731 | 54.1351 | 18.4113 | 2.948 | 2.7924 | 62.3749 | -61.5784 | -0.24719 | -0.082398 | 2.7466 | -0.15564 | -8.2535 | -0.26093 | -0.013733 | 2.9938 | 64.2654 | 64.1098 | 115.4526 | 123.6237 | 2.7466 | 123.6923 | 79.7287 | -0.26093 | 123.6237 | 2.7466 | 79.7287 | 115.4526 | 123.6923 | -123.9532 | -123.967
2281.7188 | 123.9807 | -61.2946 | 62.352 | -0.32173 | 0.01282 | 0.014268 | 0.010611 | 0.063025 | -0.00076053 | 0.080758 | -58.4839 | 62.2421 | -61.5601 | -61.4365 | 54.1946 | 18.3975 | 2.8748 | 2.8748 | 62.3154 | -61.5417 | -0.2655 | -0.10986 | 2.8107 | -0.14191 | -8.1573 | -0.24719 | -0.036621 | 3.0762 | 64.1693 | 64.1693 | 115.4892 | 123.5367 | 2.8107 | 123.6099 | 79.6921 | -0.24719 | 123.5367 | 2.8107 | 79.6921 | 115.4892 | 123.6099 | -123.912 | -123.8937
2282.7188 | 123.9761 | -61.2946 | 62.3337 | -1.4356 | 0.01581 | 0.017259 | 0.0091152 | 0.06153 | 9.4068e-05 | 0.079476 | -58.7952 | 62.2604 | -61.5784 | -61.4731 | 54.1122 | 18.5028 | 2.8427 | 2.9388 | 62.3062 | -61.5646 | -0.28381 | -0.073242 | 2.4994 | -0.17853 | -8.2214 | -0.27008 | -0.027466 | 2.7832 | 64.1373 | 64.2334 | 115.4068 | 123.555 | 2.4994 | 123.6008 | 79.7974 | -0.27008 | 123.555 | 2.4994 | 79.7974 | 115.4068 | 123.6008 | -123.912 | -123.8983
2283.7188 | 123.8617 | -61.3312 | 62.3932 | 1.4712 | 0.016878 | 0.014482 | 0.014456 | 0.060889 | 0.0015893 | 0.080758 | -58.548 | 62.3428 | -61.5875 | -61.5143 | 54.0253 | 18.2739 | 2.9251 | 2.7924 | 62.384 | -61.6196 | -0.25635 | -0.050354 | 2.7832 | -0.18311 | -8.3679 | -0.28839 | -0.009155 | 3.0395 | 64.2563 | 64.1235 | 115.3564 | 123.674 | 2.7832 | 123.7152 | 79.6051 | -0.28839 | 123.674 | 2.7832 | 79.6051 | 115.3564 | 123.7152 | -123.9807 | -124.0128
2284.7188 | 123.9716 | -61.322 | 62.3795 | -0.15388 | 0.013247 | 0.016618 | 0.010611 | 0.063025 | -0.00097413 | 0.080117 | -58.5388 | 62.2421 | -61.5601 | -61.4227 | 54.1534 | 18.3746 | 2.8427 | 2.916 | 62.3337 | -61.5601 | -0.23804 | -0.13733 | 2.7832 | -0.10071 | -8.226 | -0.23804 | -0.045777 | 3.0212 | 64.1647 | 64.238 | 115.4755 | 123.5641 | 2.7832 | 123.6557 | 79.6967 | -0.23804 | 123.5641 | 2.7832 | 79.6967 | 115.4755 | 123.6557 | -123.9395 | -123.9395
2285.7188 | 123.9487 | -61.2808 | 62.3795 | -0.20729 | 0.016878 | 0.012132 | 0.0099698 | 0.062171 | -0.0014013 | 0.080544 | -58.5434 | 62.2787 | -61.5784 | -61.4319 | 54.1443 | 18.3792 | 2.6642 | 2.829 | 62.3062 | -61.5555 | -0.29755 | -0.10071 | 2.7374 | -0.15106 | -8.2352 | -0.27466 | -0.073243 | 3.035 | 63.945 | 64.1098 | 115.4251 | 123.5596 | 2.7374 | 123.587 | 79.66 | -0.27466 | 123.5596 | 2.7374 | 79.66 | 115.4251 | 123.587 | -123.9578 | -123.9349
2286.7188 | 123.9624 | -61.3083 | 62.3657 | -0.40565 | 0.011751 | 0.012132 | 0.010611 | 0.061316 | -0.00097413 | 0.080331 | -58.5434 | 62.2604 | -61.5829 | -61.4319 | 54.0894 | 18.5028 | 2.774 | 2.9022 | 62.3016 | -61.5509 | -0.27466 | -0.10529 | 2.7649 | -0.1236 | -8.2764 | -0.24261 | -0.064087 | 3.0396 | 64.0823 | 64.2105 | 115.3976 | 123.5687 | 2.7649 | 123.6099 | 79.8111 | -0.24261 | 123.5687 | 2.7649 | 79.8111 | 115.3976 | 123.6099 | -123.9487 | -123.9166
2287.7188 | 123.7152 | -61.3907 | 62.3016 | 0.10551 | 0.017306 | 0.018754 | 0.018728 | 0.062812 | -0.00033333 | 0.082253 | -58.6212 | 62.3749 | -61.6013 | -61.5646 | 53.8742 | 18.1412 | 2.8152 | 2.742 | 62.3566 | -61.6562 | -0.21057 | 0.073242 | 2.7695 | -0.17395 | -8.4274 | -0.2655 | 0.054931 | 2.98 | 64.2059 | 64.1327 | 115.2649 | 123.7656 | 2.7695 | 123.7473 | 79.5319 | -0.2655 | 123.7656 | 2.7695 | 79.5319 | 115.2649 | 123.7473 | -123.9029 | -123.9578
2288.7188 | 123.9029 | -61.3541 | 62.3611 | -0.054703 | 0.014529 | 0.015977 | 0.01531 | 0.06388 | 0.0011621 | 0.081399 | -58.5846 | 62.3703 | -61.5967 | -61.4777 | 53.9154 | 18.1137 | 2.7649 | 2.7969 | 62.3428 | -61.5967 | -0.24262 | 0.009155 | 2.7695 | -0.1236 | -8.4457 | -0.24262 | -0.018311 | 3.0121 | 64.119 | 64.151 | 115.2695 | 123.7244 | 2.7695 | 123.6969 | 79.4678 | -0.24262 | 123.7244 | 2.7695 | 79.4678 | 115.2695 | 123.6969 | -123.9578 | -123.9578
2289.7188 | 123.9944 | -61.2946 | 62.3474 | -0.17677 | 0.011965 | 0.017045 | 0.013174 | 0.064307 | 9.4068e-05 | 0.083322 | -58.6945 | 62.2742 | -61.5601 | -61.5143 | 54.0894 | 18.3884 | 2.6688 | 2.8976 | 62.3337 | -61.5509 | -0.2655 | -0.073242 | 2.6001 | -0.21973 | -8.2581 | -0.25635 | -0.013733 | 2.8656 | 63.9633 | 64.1922 | 115.3839 | 123.5687 | 2.6001 | 123.6282 | 79.6829 | -0.25635 | 123.5687 | 2.6001 | 79.6829 | 115.3839 | 123.6282 | -123.9075 | -123.8983
2290.7188 | 123.9441 | -61.29 | 62.3749 | -0.21492 | 0.014742 | 0.014268 | 0.011251 | 0.062598 | -0.00033333 | 0.080331 | -58.5617 | 62.2879 | -61.5738 | -61.4319 | 54.0619 | 18.3014 | 2.7374 | 2.9343 | 62.3337 | -61.5509 | -0.28381 | -0.086975 | 2.7283 | -0.14191 | -8.313 | -0.26093 | -0.041199 | 3.0121 | 64.0274 | 64.2242 | 115.3519 | 123.5779 | 2.7283 | 123.6237 | 79.5914 | -0.26093 | 123.5779 | 2.7283 | 79.5914 | 115.3519 | 123.6237 | -123.9487 | -123.9258
2291.7188 | 123.9761 | -61.3083 | 62.3932 | -0.1844 | 0.01346 | 0.01555 | 0.0095424 | 0.061957 | 0.0015893 | 0.080972 | -58.5617 | 62.2467 | -61.5738 | -61.4273 | 54.1672 | 18.306 | 2.7054 | 2.9434 | 62.3108 | -61.5555 | -0.2655 | -0.14648 | 2.7466 | -0.11902 | -8.226 | -0.24719 | -0.082397 | 3.0121 | 64.0137 | 64.2517 | 115.4755 | 123.555 | 2.7466 | 123.6191 | 79.6143 | -0.24719 | 123.555 | 2.7466 | 79.6143 | 115.4755 | 123.6191 | -123.967 | -123.9487
2292.7344 | 123.8617 | -61.3358 | 62.4023 | 0.021591 | 0.018374 | 0.016618 | 0.017019 | 0.06388 | 0.00094847 | 0.079049 | -58.58 | 62.3657 | -61.5967 | -61.5234 | 54.0848 | 18.2419 | 2.7466 | 2.774 | 62.3703 | -61.6058 | -0.26093 | -0.036621 | 2.7557 | -0.18768 | -8.3176 | -0.27008 | -0.032044 | 3.0167 | 64.0823 | 64.1098 | 115.4205 | 123.7015 | 2.7557 | 123.7061 | 79.5776 | -0.27008 | 123.7015 | 2.7557 | 79.5776 | 115.4205 | 123.7061 | -123.999 | -124.0082
2293.7188 | 123.8892 | -61.322 | 62.3703 | -0.2607 | 0.015169 | 0.01854 | 0.014456 | 0.063239 | 0.00030767 | 0.079476 | -58.5754 | 62.384 | -61.5784 | -61.4685 | 54.0573 | 18.2693 | 2.7695 | 2.8748 | 62.384 | -61.6013 | -0.25635 | 0.013733 | 2.7466 | -0.14648 | -8.313 | -0.27924 | 0.013733 | 3.0029 | 64.0915 | 64.1968 | 115.3793 | 123.7061 | 2.7466 | 123.7061 | 79.5914 | -0.27924 | 123.7061 | 2.7466 | 79.5914 | 115.3793 | 123.7061 | -123.9487 | -123.9716
2294.7188 | 123.88 | -61.2991 | 62.3703 | -0.21492 | 0.013674 | 0.014695 | 0.0089016 | 0.062384 | -0.00054693 | 0.081185 | -58.5846 | 62.3154 | -61.5646 | -61.4777 | 54.1718 | 18.3929 | 2.774 | 2.8702 | 62.3566 | -61.5417 | -0.2655 | -0.054931 | 2.7145 | -0.17853 | -8.1985 | -0.24262 | -0.013733 | 2.98 | 64.0732 | 64.1693 | 115.4709 | 123.6145 | 2.7145 | 123.6557 | 79.6921 | -0.24262 | 123.6145 | 2.7145 | 79.6921 | 115.4709 | 123.6557 | -123.9349 | -123.912
2295.7188 | 123.967 | -61.2854 | 62.3657 | 0.63194 | 0.015383 | 0.018327 | 0.0097562 | 0.062384 | 0.00030767 | 0.081399 | -58.5114 | 62.2833 | -61.5692 | -61.4319 | 54.1489 | 18.3517 | 2.742 | 2.9617 | 62.2925 | -61.5601 | -0.28381 | -0.082398 | 2.774 | -0.14648 | -8.2169 | -0.27466 | -0.073243 | 3.0579 | 64.0274 | 64.2471 | 115.4343 | 123.5687 | 2.774 | 123.5779 | 79.6371 | -0.27466 | 123.5687 | 2.774 | 79.6371 | 115.4343 | 123.5779 | -123.9349 | -123.9258
2296.7188 | 123.9258 | -61.2854 | 62.3932 | -0.23781 | 0.014315 | 0.012345 | 0.0076198 | 0.062384 | 0.0015893 | 0.081826 | -58.5663 | 62.265 | -61.5692 | -61.4502 | 54.1351 | 18.425 | 2.7924 | 2.9205 | 62.352 | -61.5417 | -0.28381 | -0.12817 | 2.7191 | -0.16479 | -8.2581 | -0.25635 | -0.041198 | 3.0029 | 64.0778 | 64.2059 | 115.4205 | 123.5504 | 2.7191 | 123.6374 | 79.7104 | -0.25635 | 123.5504 | 2.7191 | 79.7104 | 115.4205 | 123.6374 | -123.9624 | -123.9349
2297.7344 | 123.8434 | -61.3724 | 62.3749 | 0.059738 | 0.018587 | 0.011704 | 0.017233 | 0.063239 | 0.00073487 | 0.080972 | -58.6304 | 62.3886 | -61.6104 | -61.5417 | 54.0344 | 18.2693 | 2.829 | 2.7374 | 62.3795 | -61.615 | -0.23804 | 0.013733 | 2.742 | -0.16937 | -8.3405 | -0.24262 | 0.004578 | 2.98 | 64.2014 | 64.1098 | 115.4068 | 123.761 | 2.742 | 123.7518 | 79.6417 | -0.24262 | 123.761 | 2.742 | 79.6417 | 115.4068 | 123.7518 | -123.9853 | -123.9899
2298.7188 | 123.8617 | -61.3541 | 62.3795 | -0.039444 | 0.018587 | 0.016618 | 0.015738 | 0.063239 | 0.0011621 | 0.080758 | -58.5571 | 62.3703 | -61.5875 | -61.4822 | 53.9612 | 18.2968 | 2.829 | 2.8839 | 62.3383 | -61.6287 | -0.23346 | -0.009156 | 2.7969 | -0.12817 | -8.4183 | -0.27466 | -0.041199 | 3.0304 | 64.183 | 64.238 | 115.3152 | 123.7244 | 2.7969 | 123.6923 | 79.6509 | -0.27466 | 123.7244 | 2.7969 | 79.6509 | 115.3152 | 123.6923 | -123.967 | -124.0082
2299.7188 | 123.9532 | -61.2991 | 62.3611 | -0.17677 | 0.01346 | 0.017045 | 0.008688 | 0.062598 | -0.0018285 | 0.081613 | -58.548 | 62.2971 | -61.6013 | -61.4365 | 54.1077 | 18.4204 | 2.7054 | 2.9343 | 62.3428 | -61.5463 | -0.30212 | -0.064087 | 2.7512 | -0.13733 | -8.2535 | -0.24719 | -0.018311 | 3.0533 | 64.0045 | 64.2334 | 115.4068 | 123.5962 | 2.7512 | 123.642 | 79.7195 | -0.24719 | 123.5962 | 2.7512 | 79.7195 | 115.4068 | 123.642 | -123.9624 | -123.9075
2300.7188 | 123.9258 | -61.3083 | 62.3428 | -0.13863 | 0.015169 | 0.017472 | 0.0099698 | 0.062171 | -0.0011877 | 0.081185 | -58.5434 | 62.2696 | -61.5601 | -61.4273 | 54.1397 | 18.6264 | 2.6962 | 3.0075 | 62.352 | -61.5417 | -0.25177 | -0.073242 | 2.7649 | -0.11902 | -8.2031 | -0.23346 | 0.009156 | 3.0167 | 64.0045 | 64.3158 | 115.448 | 123.5779 | 2.7649 | 123.6603 | 79.9347 | -0.23346 | 123.5779 | 2.7649 | 79.9347 | 115.448 | 123.6603 | -123.9029 | -123.8846
2301.7188 | 123.9441 | -61.2854 | 62.3383 | -0.1844 | 0.013674 | 0.012559 | 0.0093288 | 0.06388 | 0.00030767 | 0.079263 | -58.4885 | 62.3154 | -61.5555 | -61.4365 | 54.1718 | 18.4891 | 2.7191 | 3.0304 | 62.3016 | -61.5692 | -0.27008 | -0.022888 | 2.7969 | -0.15106 | -8.1665 | -0.28381 | -0.036621 | 3.067 | 64.0045 | 64.3158 | 115.4572 | 123.6008 | 2.7969 | 123.587 | 79.7745 | -0.28381 | 123.6008 | 2.7969 | 79.7745 | 115.4572 | 123.587 | -123.8937 | -123.9075
2302.7344 | 123.88 | -61.3724 | 62.352 | 0.14366 | 0.01581 | 0.019822 | 0.016165 | 0.063025 | -0.00076053 | 0.081399 | -58.5938 | 62.3291 | -61.615 | -61.5417 | 54.0207 | 18.4387 | 2.7466 | 2.9572 | 62.2971 | -61.6241 | -0.24262 | -0.022888 | 2.7786 | -0.16937 | -8.3313 | -0.25177 | -0.054932 | 3.0212 | 64.119 | 64.3295 | 115.3931 | 123.7015 | 2.7786 | 123.6694 | 79.8111 | -0.25177 | 123.7015 | 2.7786 | 79.8111 | 115.3931 | 123.6694 | -123.967 | -123.9761
2303.7344 | 123.88 | -61.3358 | 62.3611 | -0.054703 | 0.017947 | 0.016618 | 0.015097 | 0.061957 | 0.0024439 | 0.08204 | -58.5434 | 62.3611 | -61.5784 | -61.5097 | 54.0756 | 18.4753 | 2.7603 | 2.8793 | 62.3291 | -61.6287 | -0.24262 | 0 | 2.7924 | -0.17395 | -8.2855 | -0.29297 | -0.032043 | 3.035 | 64.0961 | 64.2151 | 115.4114 | 123.6969 | 2.7924 | 123.6649 | 79.8111 | -0.29297 | 123.6969 | 2.7924 | 79.8111 | 115.4114 | 123.6649 | -123.9395 | -123.9899
2304.7188 | 123.912 | -61.3129 | 62.3703 | -0.20729 | 0.013888 | 0.015763 | 0.0061246 | 0.062598 | 0.0015893 | 0.08204 | -58.5617 | 62.2925 | -61.5829 | -61.4731 | 54.0939 | 18.3746 | 2.7969 | 3.0121 | 62.3291 | -61.5738 | -0.27008 | -0.07782 | 2.7512 | -0.16022 | -8.2764 | -0.26093 | -0.041198 | 3.0212 | 64.1098 | 64.325 | 115.4068 | 123.6053 | 2.7512 | 123.642 | 79.6875 | -0.26093 | 123.6053 | 2.7512 | 79.6875 | 115.4068 | 123.642 | -123.9532 | -123.9441
2305.7188 | 123.8983 | -61.3129 | 62.3428 | -0.21492 | 0.010683 | 0.0132 | 0.011038 | 0.061316 | 0.00073487 | 0.079476 | -58.4793 | 62.2879 | -61.5875 | -61.4685 | 54.1992 | 18.6218 | 2.7878 | 3.0304 | 62.3566 | -61.5509 | -0.27466 | -0.054931 | 2.8336 | -0.15564 | -8.1436 | -0.23804 | 0.013733 | 3.1082 | 64.1006 | 64.3433 | 115.5121 | 123.6008 | 2.8336 | 123.6694 | 79.9347 | -0.23804 | 123.6008 | 2.8336 | 79.9347 | 115.5121 | 123.6694 | -123.9304 | -123.8937
2306.7188 | 123.9258 | -61.2808 | 62.3566 | -0.19203 | 0.015383 | 0.014909 | 0.0089016 | 0.060675 | 0.0018031 | 0.080972 | -58.5709 | 62.2833 | -61.5738 | -61.4502 | 54.1489 | 18.3563 | 2.8152 | 3.0808 | 62.3199 | -61.5326 | -0.29297 | -0.073242 | 2.71 | -0.16937 | -8.2077 | -0.25177 | -0.036621 | 3.0029 | 64.0961 | 64.3616 | 115.4297 | 123.5641 | 2.71 | 123.6008 | 79.6371 | -0.25177 | 123.5641 | 2.71 | 79.6371 | 115.4297 | 123.6008 | -123.9304 | -123.8892
2307.7188 | 123.8892 | -61.322 | 62.3978 | -0.19966 | 0.016451 | 0.015336 | 0.014456 | 0.063666 | -0.00076053 | 0.081185 | -58.5617 | 62.3291 | -61.5921 | -61.496 | 53.9932 | 18.2831 | 2.8152 | 2.9388 | 62.3611 | -61.5829 | -0.27008 | -0.068664 | 2.7603 | -0.17395 | -8.4045 | -0.26093 | -0.036621 | 3.0304 | 64.1373 | 64.2609 | 115.3152 | 123.6511 | 2.7603 | 123.6832 | 79.6051 | -0.26093 | 123.6511 | 2.7603 | 79.6051 | 115.3152 | 123.6832 | -123.9899 | -123.9807
2308.7188 | 123.8663 | -61.3449 | 62.3703 | -0.5201 | 0.018374 | 0.017899 | 0.017233 | 0.064734 | -0.0018285 | 0.080758 | -58.5297 | 62.3383 | -61.5829 | -61.4777 | 54.0848 | 18.306 | 2.7145 | 2.861 | 62.3611 | -61.6196 | -0.23804 | -0.032043 | 2.8152 | -0.13275 | -8.2855 | -0.27466 | -0.009155 | 3.0533 | 64.0594 | 64.2059 | 115.4297 | 123.6832 | 2.8152 | 123.7061 | 79.6509 | -0.27466 | 123.6832 | 2.8152 | 79.6509 | 115.4297 | 123.7061 | -123.9532 | -123.9899
2309.7188 | 123.9578 | -61.2991 | 62.3657 | -0.16151 | 0.015383 | 0.015977 | 0.0084744 | 0.063239 | -0.00011953 | 0.080972 | -58.5297 | 62.265 | -61.5692 | -61.4456 | 54.1077 | 18.3517 | 2.6825 | 3.0167 | 62.3291 | -61.5646 | -0.27008 | -0.10071 | 2.7695 | -0.14649 | -8.2581 | -0.2655 | -0.036621 | 3.0396 | 63.9816 | 64.3158 | 115.4068 | 123.5641 | 2.7695 | 123.6282 | 79.6509 | -0.2655 | 123.5641 | 2.7695 | 79.6509 | 115.4068 | 123.6282 | -123.9349 | -123.9304
2310.7188 | 123.8663 | -61.3266 | 62.3703 | -0.19966 | 0.014101 | 0.012559 | 0.011038 | 0.06388 | -0.00011953 | 0.080544 | -58.5571 | 62.2971 | -61.5646 | -61.5005 | 54.0939 | 18.3701 | 2.9297 | 2.9846 | 62.3611 | -61.5829 | -0.23804 | -0.073242 | 2.7695 | -0.17395 | -8.2764 | -0.25635 | -0.009155 | 3.0075 | 64.2563 | 64.3112 | 115.4205 | 123.6237 | 2.7695 | 123.6877 | 79.6967 | -0.25635 | 123.6237 | 2.7695 | 79.6967 | 115.4205 | 123.6877 | -123.9349 | -123.9532
2311.7188 | 123.8983 | -61.3403 | 62.384 | -0.28358 | 0.017519 | 0.015122 | 0.012106 | 0.062812 | 0.00052127 | 0.081399 | -58.5114 | 62.2925 | -61.5829 | -61.4868 | 54.126 | 18.4113 | 3.0533 | 3.0624 | 62.352 | -61.5601 | -0.24262 | -0.091553 | 2.829 | -0.14648 | -8.2581 | -0.21973 | -0.032043 | 3.0716 | 64.3936 | 64.4028 | 115.4663 | 123.6328 | 2.829 | 123.6923 | 79.7516 | -0.21973 | 123.6328 | 2.829 | 79.7516 | 115.4663 | 123.6923 | -123.967 | -123.9441
2312.7188 | 123.8525 | -61.322 | 62.3749 | -0.29884 | 0.014742 | 0.019181 | 0.0099698 | 0.06153 | 9.4068e-05 | 0.079049 | -58.5342 | 62.3154 | -61.5829 | -61.4822 | 54.1443 | 18.4204 | 2.9938 | 2.9984 | 62.352 | -61.5829 | -0.26093 | -0.059509 | 2.7878 | -0.16022 | -8.2306 | -0.26093 | -0.022888 | 3.0487 | 64.3158 | 64.3204 | 115.4663 | 123.6374 | 2.7878 | 123.674 | 79.7424 | -0.26093 | 123.6374 | 2.7878 | 79.7424 | 115.4663 | 123.674 | -123.9578 | -123.9578
2313.7344 | 123.8205 | -61.3449 | 62.3611 | 0.059738 | 0.016878 | 0.015763 | 0.017874 | 0.066016 | 9.4068e-05 | 0.081185 | -58.5434 | 62.3566 | -61.5967 | -61.5692 | 54.0894 | 18.3426 | 2.9938 | 2.9205 | 62.3428 | -61.6287 | -0.25177 | -0.004578 | 2.8015 | -0.2243 | -8.2718 | -0.28381 | -0.018311 | 3.0533 | 64.3387 | 64.2654 | 115.4343 | 123.7015 | 2.8015 | 123.6877 | 79.6875 | -0.28381 | 123.7015 | 2.8015 | 79.6875 | 115.4343 | 123.6877 | -123.9578 | -123.9899
2314.7188 | 123.8983 | -61.3174 | 62.3795 | -0.23781 | 0.01346 | 0.011918 | 0.011251 | 0.062812 | 9.4068e-05 | 0.082467 | -58.5388 | 62.3108 | -61.5875 | -61.4868 | 54.1718 | 18.5577 | 2.9205 | 3.0075 | 62.3428 | -61.5738 | -0.27008 | -0.068665 | 2.7786 | -0.16937 | -8.2077 | -0.25635 | -0.036622 | 3.0487 | 64.238 | 64.325 | 115.4892 | 123.6282 | 2.7786 | 123.6603 | 79.8752 | -0.25635 | 123.6282 | 2.7786 | 79.8752 | 115.4892 | 123.6603 | -123.967 | -123.9532
2315.7188 | 123.8892 | -61.3083 | 62.3795 | -0.24544 | 0.015383 | 0.01555 | 0.010397 | 0.062598 | -0.0018285 | 0.081826 | -58.8455 | 62.3108 | -61.5784 | -61.4685 | 54.1397 | 18.6264 | 3.1082 | 3.0853 | 62.3245 | -61.6013 | -0.27008 | -0.068665 | 2.4628 | -0.16022 | -8.2397 | -0.29297 | -0.054932 | 2.7328 | 64.4165 | 64.3936 | 115.448 | 123.6191 | 2.4628 | 123.6328 | 79.9347 | -0.29297 | 123.6191 | 2.4628 | 79.9347 | 115.448 | 123.6328 | -123.9578 | -123.9807
2316.7188 | 123.9029 | -61.3037 | 62.352 | -0.25307 | 0.015597 | 0.014482 | 0.011038 | 0.062384 | -0.0018285 | 0.081613 | -58.58 | 62.3108 | -61.5829 | -61.4777 | 54.1763 | 18.7454 | 3.0396 | 3.0853 | 62.3383 | -61.5921 | -0.27924 | -0.041199 | 2.7237 | -0.17395 | -8.1757 | -0.28839 | -0.013733 | 3.0029 | 64.3433 | 64.389 | 115.48 | 123.6145 | 2.7237 | 123.642 | 80.0491 | -0.28839 | 123.6145 | 2.7237 | 80.0491 | 115.48 | 123.642 | -123.9349 | -123.9441
2317.7188 | 123.8571 | -61.3358 | 62.384 | -0.22255 | 0.014529 | 0.012773 | 0.011038 | 0.059607 | 0.00030767 | 0.082467 | -58.7219 | 62.3108 | -61.5921 | -61.5372 | 54.0665 | 18.75 | 3.1036 | 2.9938 | 62.3566 | -61.6058 | -0.25635 | -0.073242 | 2.6138 | -0.20142 | -8.3176 | -0.27008 | -0.027466 | 2.8702 | 64.4394 | 64.3295 | 115.4022 | 123.6465 | 2.6138 | 123.6923 | 80.0858 | -0.27008 | 123.6465 | 2.6138 | 80.0858 | 115.4022 | 123.6923 | -123.9761 | -123.9899
2318.7188 | 123.8709 | -61.3312 | 62.3703 | -0.22255 | 0.017947 | 0.016404 | 0.014242 | 0.065161 | 0.00073487 | 0.082253 | -58.5205 | 62.3795 | -61.6058 | -61.4822 | 54.0253 | 18.6813 | 3.0533 | 3.0899 | 62.3474 | -61.6058 | -0.27466 | 0.009156 | 2.8107 | -0.15106 | -8.345 | -0.27466 | -0.022888 | 3.0853 | 64.3845 | 64.4211 | 115.3564 | 123.7106 | 2.8107 | 123.6786 | 80.0125 | -0.27466 | 123.7106 | 2.8107 | 80.0125 | 115.3564 | 123.6786 | -123.9761 | -123.9761
2319.7188 | 123.8434 | -61.3266 | 62.384 | -0.25307 | 0.015597 | 0.0082864 | 0.010397 | 0.06388 | 0.00030767 | 0.07969 | -58.6533 | 62.3383 | -61.6013 | -61.5372 | 53.9978 | 18.6859 | 3.154 | 3.067 | 62.3657 | -61.5921 | -0.27466 | -0.045776 | 2.6733 | -0.21057 | -8.3862 | -0.2655 | -0.01831 | 2.948 | 64.4806 | 64.3936 | 115.3244 | 123.6649 | 2.6733 | 123.6923 | 80.0125 | -0.2655 | 123.6649 | 2.6733 | 80.0125 | 115.3244 | 123.6923 | -123.9853 | -123.9761
2320.7188 | 123.8663 | -61.3586 | 62.3703 | -0.26833 | 0.015169 | 0.013627 | 0.0091152 | 0.061316 | 0.00052127 | 0.083749 | -58.6075 | 62.3474 | -61.6058 | -61.5143 | 54.0436 | 18.6218 | 3.3234 | 3.0853 | 62.3795 | -61.5921 | -0.24719 | -0.022888 | 2.7512 | -0.15564 | -8.3267 | -0.23346 | 0.009156 | 2.9984 | 64.682 | 64.444 | 115.4022 | 123.7061 | 2.7512 | 123.7381 | 79.9805 | -0.23346 | 123.7061 | 2.7512 | 79.9805 | 115.4022 | 123.7381 | -123.9761 | -123.9624
2321.7188 | 123.8297 | -61.3358 | 62.3795 | -0.26833 | 0.015597 | 0.015336 | 0.010183 | 0.06153 | -0.00097413 | 0.080972 | -58.6441 | 62.3337 | -61.6241 | -61.5417 | 54.1214 | 18.6584 | 3.2776 | 3.0853 | 62.3749 | -61.5829 | -0.28839 | -0.045777 | 2.6917 | -0.20599 | -8.2581 | -0.24719 | -0.004578 | 2.98 | 64.6133 | 64.4211 | 115.4572 | 123.6694 | 2.6917 | 123.7106 | 79.9942 | -0.24719 | 123.6694 | 2.6917 | 79.9942 | 115.4572 | 123.7106 | -124.0036 | -123.9624
2322.7188 | 123.848 | -61.377 | 62.3886 | -0.16151 | 0.013674 | 0.014054 | 0.011679 | 0.062812 | 0.0011621 | 0.08204 | -58.5709 | 62.352 | -61.6013 | -61.528 | 54.1672 | 18.6905 | 3.3005 | 3.1448 | 62.3703 | -61.5967 | -0.2243 | -0.036621 | 2.8061 | -0.15106 | -8.2214 | -0.21973 | -0.018311 | 3.0304 | 64.6774 | 64.5218 | 115.5441 | 123.7289 | 2.8061 | 123.7473 | 80.0674 | -0.21973 | 123.7289 | 2.8061 | 80.0674 | 115.5441 | 123.7473 | -123.9899 | -123.9853
2323.7188 | 123.8617 | -61.3678 | 62.3337 | 0.013962 | 0.017092 | 0.02089 | 0.01531 | 0.06388 | 0.00030767 | 0.079263 | -58.5754 | 62.3337 | -61.6058 | -61.5463 | 54.1351 | 18.7408 | 3.2089 | 3.0075 | 62.3703 | -61.6287 | -0.23804 | 0 | 2.7924 | -0.17853 | -8.1985 | -0.26093 | 0.036621 | 3.0304 | 64.5767 | 64.3753 | 115.5029 | 123.7015 | 2.7924 | 123.7381 | 80.1086 | -0.26093 | 123.7015 | 2.7924 | 80.1086 | 115.5029 | 123.7381 | -123.9395 | -123.9624
2324.7188 | 123.848 | -61.3358 | 62.3749 | -0.2607 | 0.017733 | 0.015977 | 0.012533 | 0.063666 | 0.0020167 | 0.081826 | -58.6487 | 62.3428 | -61.615 | -61.5326 | 54.1946 | 18.7225 | 3.2913 | 3.0487 | 62.3657 | -61.6196 | -0.27924 | -0.032044 | 2.6871 | -0.19684 | -8.1802 | -0.28381 | -0.009155 | 2.9663 | 64.6271 | 64.3845 | 115.5304 | 123.6786 | 2.6871 | 123.7015 | 80.0583 | -0.28381 | 123.6786 | 2.6871 | 80.0583 | 115.5304 | 123.7015 | -123.9899 | -123.9944
2325.7188 | 123.8709 | -61.3312 | 62.3657 | -0.40565 | 0.015169 | 0.015763 | 0.01296 | 0.063666 | -0.0014013 | 0.081185 | -58.6121 | 62.3474 | -61.6058 | -61.528 | 54.1077 | 18.6218 | 3.241 | 3.0487 | 62.3566 | -61.6196 | -0.27466 | -0.018311 | 2.7191 | -0.19684 | -8.2581 | -0.28839 | -0.009156 | 2.9938 | 64.5721 | 64.3799 | 115.4388 | 123.6786 | 2.7191 | 123.6877 | 79.953 | -0.28839 | 123.6786 | 2.7191 | 79.953 | 115.4388 | 123.6877 | -123.9716 | -123.9853
2326.7188 | 123.8342 | -61.3449 | 62.3795 | -0.93208 | 0.015597 | 0.017472 | 0.01296 | 0.06388 | -0.00054693 | 0.081185 | -58.754 | 62.3383 | -61.6196 | -61.5646 | 54.1306 | 18.6584 | 3.2318 | 3.0304 | 62.3932 | -61.5921 | -0.27466 | -0.041199 | 2.5909 | -0.21973 | -8.2489 | -0.24719 | 0.013732 | 2.8656 | 64.5767 | 64.3753 | 115.4755 | 123.6832 | 2.5909 | 123.7381 | 80.0034 | -0.24719 | 123.6832 | 2.5909 | 80.0034 | 115.4755 | 123.7381 | -123.999 | -123.9716
2327.7188 | 123.8434 | -61.3678 | 62.3795 | -0.22255 | 0.016451 | 0.011064 | 0.011679 | 0.062812 | 0.0030847 | 0.080544 | -58.3923 | 62.3657 | -61.5921 | -61.5097 | 54.3182 | 18.6905 | 3.3966 | 3.1586 | 62.3474 | -61.6058 | -0.2243 | -0.013733 | 2.9755 | -0.14191 | -8.0612 | -0.23804 | -0.032044 | 3.1998 | 64.7644 | 64.5264 | 115.686 | 123.7335 | 2.9755 | 123.7152 | 80.0583 | -0.23804 | 123.7335 | 2.9755 | 80.0583 | 115.686 | 123.7152 | -123.9716 | -123.9853
2328.7188 | 123.8525 | -61.3495 | 62.3795 | 0.029221 | 0.020296 | 0.019181 | 0.014456 | 0.064521 | 0.00073487 | 0.081826 | -58.6029 | 62.3566 | -61.615 | -61.5463 | 54.0115 | 18.5577 | 3.2959 | 3.1128 | 62.3199 | -61.6287 | -0.2655 | -0.022889 | 2.7466 | -0.19684 | -8.3679 | -0.27924 | -0.05951 | 3.0121 | 64.6454 | 64.4623 | 115.361 | 123.7061 | 2.7466 | 123.6694 | 79.9072 | -0.27924 | 123.7061 | 2.7466 | 79.9072 | 115.361 | 123.6694 | -123.9944 | -124.0082
2329.7188 | 123.8113 | -61.3815 | 62.3795 | -0.19203 | 0.01581 | 0.015336 | 0.0056972 | 0.064521 | 0.0037257 | 0.081613 | -58.58 | 62.3566 | -61.6013 | -61.6058 | 54.1489 | 18.5898 | 3.2135 | 3.0808 | 62.3657 | -61.6196 | -0.21973 | -0.022889 | 2.8015 | -0.2243 | -8.2306 | -0.23804 | -0.013733 | 3.0212 | 64.595 | 64.4623 | 115.5304 | 123.7381 | 2.8015 | 123.7473 | 79.9713 | -0.23804 | 123.7381 | 2.8015 | 79.9713 | 115.5304 | 123.7473 | -123.9807 | -123.999
2330.7188 | 123.848 | -61.3541 | 62.3611 | -0.29121 | 0.016024 | 0.016831 | 0.0099698 | 0.061957 | 0.0013757 | 0.081399 | -58.6441 | 62.3611 | -61.6196 | -61.6699 | 54.1077 | 18.6081 | 3.241 | 3.0487 | 62.3657 | -61.615 | -0.2655 | 0 | 2.71 | -0.31586 | -8.2535 | -0.26093 | 0.004578 | 2.9755 | 64.595 | 64.4028 | 115.4617 | 123.7152 | 2.71 | 123.7198 | 79.9622 | -0.26093 | 123.7152 | 2.71 | 79.9622 | 115.4617 | 123.7198 | -123.9807 | -123.9761
2331.7188 | 123.8617 | -61.3495 | 62.3886 | -0.23018 | 0.016024 | 0.018754 | 0.013601 | 0.062598 | 0.0018031 | 0.080117 | -58.6075 | 62.3474 | -61.6013 | -61.5326 | 54.126 | 18.6859 | 3.3554 | 3.0945 | 62.384 | -61.5921 | -0.25177 | -0.041199 | 2.742 | -0.18311 | -8.2626 | -0.24261 | -0.004578 | 2.9938 | 64.7049 | 64.444 | 115.4755 | 123.6969 | 2.742 | 123.7335 | 80.0354 | -0.24261 | 123.6969 | 2.742 | 80.0354 | 115.4755 | 123.7335 | -123.9899 | -123.9807
2332.7188 | 123.8709 | -61.3312 | 62.384 | -0.23018 | 0.017519 | 0.015977 | 0.008688 | 0.064093 | 0.0015893 | 0.082253 | -58.5983 | 62.3611 | -61.6287 | -61.5417 | 54.1718 | 18.6356 | 3.3188 | 3.0716 | 62.3703 | -61.5829 | -0.29755 | -0.022888 | 2.7328 | -0.21057 | -8.2123 | -0.25177 | -0.013733 | 3.0304 | 64.65 | 64.4028 | 115.5029 | 123.6923 | 2.7328 | 123.7015 | 79.9667 | -0.25177 | 123.6923 | 2.7328 | 79.9667 | 115.5029 | 123.7015 | -124.0128 | -123.967
2333.7344 | 123.9029 | -61.3449 | 62.3291 | 0.18944 | 0.019228 | 0.016404 | 0.01232 | 0.067298 | 0.0020167 | 0.081185 | -58.6395 | 62.3108 | -61.6287 | -61.5509 | 54.0894 | 18.6035 | 3.0579 | 2.9022 | 62.3062 | -61.6196 | -0.28381 | -0.018311 | 2.7054 | -0.20599 | -8.2397 | -0.27466 | -0.022889 | 2.9892 | 64.4028 | 64.2471 | 115.4343 | 123.6557 | 2.7054 | 123.6511 | 79.9484 | -0.27466 | 123.6557 | 2.7054 | 79.9484 | 115.4343 | 123.6511 | -123.9578 | -123.9487
2334.7188 | 123.8571 | -61.3403 | 62.3474 | -0.19203 | 0.017306 | 0.020463 | 0.011465 | 0.064307 | 0.0018031 | 0.08204 | -58.6121 | 62.352 | -61.6058 | -61.5143 | 54.0436 | 18.6676 | 3.3279 | 2.9892 | 62.3657 | -61.6287 | -0.2655 | 0.004578 | 2.7283 | -0.17395 | -8.3038 | -0.28839 | 0.018311 | 2.9938 | 64.6683 | 64.3295 | 115.3839 | 123.6923 | 2.7283 | 123.7061 | 80.0079 | -0.28839 | 123.6923 | 2.7283 | 80.0079 | 115.3839 | 123.7061 | -123.9532 | -123.9761
2335.7188 | 123.9029 | -61.3586 | 62.352 | -0.19203 | 0.015597 | 0.017686 | 0.014883 | 0.062812 | 9.4068e-05 | 0.081613 | -58.5983 | 62.3795 | -61.6196 | -61.496 | 54.0253 | 18.6447 | 3.2776 | 3.0167 | 62.352 | -61.6287 | -0.26093 | 0.027466 | 2.7603 | -0.13733 | -8.3267 | -0.27008 | 0 | 3.0212 | 64.6362 | 64.3753 | 115.3839 | 123.7381 | 2.7603 | 123.7106 | 80.0034 | -0.27008 | 123.7381 | 2.7603 | 80.0034 | 115.3839 | 123.7106 | -123.9716 | -123.9807
2336.7188 | 123.8571 | -61.3312 | 62.3749 | -0.19203 | 0.016238 | 0.018113 | 0.010183 | 0.063452 | 0.0020167 | 0.079049 | -58.6304 | 62.3566 | -61.6013 | -61.5463 | 54.007 | 18.5852 | 3.2455 | 2.8748 | 62.3932 | -61.6013 | -0.27008 | -0.018311 | 2.7008 | -0.21515 | -8.3679 | -0.27008 | 0.01831 | 2.9709 | 64.5767 | 64.2059 | 115.3381 | 123.6877 | 2.7008 | 123.7244 | 79.9164 | -0.27008 | 123.6877 | 2.7008 | 79.9164 | 115.3381 | 123.7244 | -123.9761 | -123.9761
2337.7188 | 123.8617 | -61.3312 | 62.384 | -0.21492 | 0.016238 | 0.01555 | 0.013601 | 0.065802 | 0.00094847 | 0.081826 | -58.5983 | 62.3474 | -61.5921 | -61.5463 | 54.1077 | 18.718 | 3.3051 | 2.9343 | 62.3749 | -61.5967 | -0.26093 | -0.036621 | 2.7328 | -0.21515 | -8.2764 | -0.2655 | -0.009155 | 2.9938 | 64.6362 | 64.2654 | 115.4388 | 123.6786 | 2.7328 | 123.7061 | 80.0491 | -0.2655 | 123.6786 | 2.7328 | 80.0491 | 115.4388 | 123.7061 | -123.9761 | -123.9807
2338.7188 | 123.8205 | -61.3495 | 62.3337 | 0.04448 | 0.017092 | 0.015336 | 0.014456 | 0.065375 | -0.00076053 | 0.080758 | -58.6121 | 62.3795 | -61.6241 | -61.5784 | 54.0436 | 18.7088 | 3.2776 | 2.9251 | 62.352 | -61.647 | -0.27466 | 0.045777 | 2.7374 | -0.22888 | -8.2901 | -0.29755 | 0.018311 | 3.0121 | 64.6271 | 64.2746 | 115.3931 | 123.7289 | 2.7374 | 123.7015 | 80.0583 | -0.29755 | 123.7289 | 2.7374 | 80.0583 | 115.3931 | 123.7015 | -123.9578 | -123.9807
2339.7188 | 123.9029 | -61.3495 | 62.3611 | -0.131 | 0.016878 | 0.01854 | 0.011892 | 0.06623 | -0.00011953 | 0.08204 | -58.5709 | 62.3749 | -61.6058 | -61.4868 | 54.0985 | 18.8004 | 3.1036 | 2.9251 | 62.3474 | -61.6241 | -0.25635 | 0.013733 | 2.7786 | -0.13733 | -8.2626 | -0.27466 | -0.013733 | 3.035 | 64.4531 | 64.2746 | 115.448 | 123.7244 | 2.7786 | 123.6969 | 80.1498 | -0.27466 | 123.7244 | 2.7786 | 80.1498 | 115.448 | 123.6969 | -123.967 | -123.9853
2340.7188 | 123.912 | -61.3403 | 62.384 | -0.10048 | 0.016451 | 0.019608 | 0.011679 | 0.068152 | 0.0032983 | 0.083322 | -58.58 | 62.3932 | -61.5875 | -61.4914 | 54.0344 | 18.7637 | 3.1769 | 2.9755 | 62.3749 | -61.6196 | -0.24719 | 0.009155 | 2.7603 | -0.15106 | -8.3496 | -0.27924 | -0.009155 | 3.0075 | 64.5172 | 64.3158 | 115.3748 | 123.7335 | 2.7603 | 123.7152 | 80.1041 | -0.27924 | 123.7335 | 2.7603 | 80.1041 | 115.3748 | 123.7152 | -123.9716 | -124.0036
2341.7188 | 123.88 | -61.3174 | 62.3428 | -0.23781 | 0.016878 | 0.014268 | 0.011892 | 0.064521 | -0.00033333 | 0.081613 | -58.5297 | 62.3749 | -61.5829 | -61.5097 | 54.0527 | 18.837 | 3.2043 | 2.9526 | 62.3978 | -61.615 | -0.2655 | 0.032044 | 2.7878 | -0.19226 | -8.2901 | -0.29755 | 0.054932 | 3.0533 | 64.5218 | 64.27 | 115.3702 | 123.6923 | 2.7878 | 123.7152 | 80.1544 | -0.29755 | 123.6923 | 2.7878 | 80.1544 | 115.3702 | 123.7152 | -123.9258 | -123.9578
2342.7188 | 123.8159 | -61.3678 | 62.3474 | -0.039444 | 0.016665 | 0.018754 | 0.014456 | 0.065802 | 0.0013757 | 0.081613 | -58.5159 | 62.3611 | -61.6104 | -61.4914 | 54.0115 | 18.7134 | 3.1494 | 2.948 | 62.3566 | -61.6241 | -0.24262 | 0.013733 | 2.8519 | -0.1236 | -8.3359 | -0.25635 | 0.009155 | 3.0945 | 64.5172 | 64.3158 | 115.3793 | 123.7289 | 2.8519 | 123.7244 | 80.0812 | -0.25635 | 123.7289 | 2.8519 | 80.0812 | 115.3793 | 123.7244 | -123.9578 | -123.9716
2343.7188 | 123.8937 | -61.3449 | 62.3016 | 0.12077 | 0.016451 | 0.018754 | 0.0099698 | 0.06623 | 0.0028711 | 0.080972 | -58.5571 | 62.3383 | -61.6333 | -61.5784 | 54.1214 | 18.7363 | 3.0762 | 2.8885 | 62.3337 | -61.6379 | -0.28839 | 0.036621 | 2.7878 | -0.23346 | -8.1802 | -0.29297 | 0.032043 | 3.0762 | 64.4211 | 64.2334 | 115.4663 | 123.6832 | 2.7878 | 123.6786 | 80.0812 | -0.29297 | 123.6832 | 2.7878 | 80.0812 | 115.4663 | 123.6786 | -123.9349 | -123.9395
2344.7188 | 123.8754 | -61.3495 | 62.3566 | -0.25307 | 0.016878 | 0.017259 | 0.012747 | 0.066016 | 0.0018031 | 0.080758 | -58.5754 | 62.384 | -61.6287 | -61.528 | 54.0344 | 18.7546 | 3.1677 | 2.98 | 62.3657 | -61.6241 | -0.27924 | 0.027466 | 2.774 | -0.17853 | -8.3221 | -0.27466 | 0.009156 | 3.0533 | 64.5172 | 64.3295 | 115.3839 | 123.7335 | 2.774 | 123.7152 | 80.1041 | -0.27466 | 123.7335 | 2.774 | 80.1041 | 115.3839 | 123.7152 | -123.9853 | -123.9807
2345.7188 | 123.9029 | -61.3312 | 62.352 | -0.16151 | 0.017092 | 0.019395 | 0.013601 | 0.066016 | 0.00052127 | 0.081826 | -58.5983 | 62.3657 | -61.6058 | -61.5051 | 54.158 | 18.8644 | 3.1998 | 2.948 | 62.3566 | -61.6241 | -0.27466 | 0.013733 | 2.7328 | -0.17395 | -8.194 | -0.29297 | 0.004577 | 3.0075 | 64.5309 | 64.2792 | 115.4892 | 123.6969 | 2.7328 | 123.6877 | 80.1956 | -0.29297 | 123.6969 | 2.7328 | 80.1956 | 115.4892 | 123.6877 | -123.9578 | -123.9761
2346.7188 | 123.88 | -61.3632 | 62.3199 | -0.14626 | 0.017519 | 0.019608 | 0.013815 | 0.065802 | 0.0030847 | 0.080758 | -58.5114 | 62.3611 | -61.6013 | -61.5097 | 54.2542 | 19.0338 | 3.1723 | 2.98 | 62.3566 | -61.6104 | -0.23804 | 0.041199 | 2.8519 | -0.14648 | -8.0658 | -0.24719 | 0.036621 | 3.0899 | 64.5355 | 64.3433 | 115.6174 | 123.7244 | 2.8519 | 123.7198 | 80.397 | -0.24719 | 123.7244 | 2.8519 | 80.397 | 115.6174 | 123.7198 | -123.9212 | -123.9304
2347.7188 | 123.8892 | -61.3312 | 62.3566 | -0.12337 | 0.017306 | 0.016831 | 0.013388 | 0.066016 | -0.00076053 | 0.083108 | -58.493 | 62.3474 | -61.5967 | -61.5005 | 54.158 | 19.0521 | 3.1036 | 2.9205 | 62.3749 | -61.6379 | -0.2655 | -0.009155 | 2.8381 | -0.16937 | -8.1985 | -0.3067 | 0.018311 | 3.1036 | 64.4348 | 64.2517 | 115.4892 | 123.6786 | 2.8381 | 123.7061 | 80.3833 | -0.3067 | 123.6786 | 2.8381 | 80.3833 | 115.4892 | 123.7061 | -123.9532 | -123.9944
2348.7188 | 123.8525 | -61.3907 | 62.2879 | 0.082626 | 0.019442 | 0.016404 | 0.013174 | 0.068366 | 0.0024439 | 0.081185 | -58.5434 | 62.3474 | -61.6562 | -61.6379 | 54.0344 | 18.9148 | 3.3234 | 3.0441 | 62.352 | -61.647 | -0.2655 | 0.059509 | 2.8473 | -0.24719 | -8.2535 | -0.25635 | 0.064087 | 3.1128 | 64.7141 | 64.4348 | 115.4251 | 123.7381 | 2.8473 | 123.7427 | 80.3055 | -0.25635 | 123.7381 | 2.8473 | 80.3055 | 115.4251 | 123.7427 | -123.9441 | -123.9349
2349.7188 | 123.8937 | -61.3632 | 62.3383 | -0.20729 | 0.017733 | 0.015122 | 0.013388 | 0.067084 | -0.00011953 | 0.081826 | -58.4976 | 62.3749 | -61.6104 | -61.528 | 54.1397 | 18.9331 | 3.2272 | 3.0441 | 62.3474 | -61.6425 | -0.24719 | 0.036621 | 2.8656 | -0.1648 | -8.1985 | -0.27924 | 0.009155 | 3.1128 | 64.5905 | 64.4073 | 115.5029 | 123.7381 | 2.8656 | 123.7106 | 80.2963 | -0.27924 | 123.7381 | 2.8656 | 80.2963 | 115.5029 | 123.7106 | -123.9487 | -123.9807
2350.7188 | 123.8846 | -61.3541 | 62.3428 | -0.11574 | 0.017519 | 0.017899 | 0.011892 | 0.064948 | 0.0028711 | 0.081826 | -58.493 | 62.384 | -61.5829 | -61.5143 | 54.1397 | 18.869 | 3.2364 | 3.1174 | 62.3337 | -61.647 | -0.22888 | 0.041199 | 2.861 | -0.16022 | -8.2031 | -0.29297 | -0.009155 | 3.0899 | 64.5905 | 64.4714 | 115.4938 | 123.7381 | 2.861 | 123.6877 | 80.2231 | -0.29297 | 123.7381 | 2.861 | 80.2231 | 115.4938 | 123.6877 | -123.9258 | -123.9899
2351.7188 | 123.9029 | -61.3358 | 62.3337 | -0.11574 | 0.017947 | 0.018968 | 0.0095424 | 0.067511 | 0.0022303 | 0.081185 | -58.5434 | 62.3657 | -61.615 | -61.5189 | 54.0848 | 18.9194 | 3.4012 | 3.1036 | 62.3383 | -61.6333 | -0.27924 | 0.032044 | 2.7924 | -0.18311 | -8.2489 | -0.29755 | 0.004578 | 3.0716 | 64.7369 | 64.4394 | 115.4205 | 123.7015 | 2.7924 | 123.674 | 80.2551 | -0.29755 | 123.7015 | 2.7924 | 80.2551 | 115.4205 | 123.674 | -123.9487 | -123.967
2352.7188 | 123.8846 | -61.3449 | 62.3474 | 0.052109 | 0.017733 | 0.017472 | 0.012106 | 0.067298 | 0.0015893 | 0.080544 | -58.5617 | 62.3566 | -61.615 | -61.5189 | 54.0482 | 18.9011 | 3.3783 | 3.0991 | 62.3383 | -61.6058 | -0.27008 | 0.009155 | 2.7832 | -0.17395 | -8.2993 | -0.26093 | -0.009155 | 3.0533 | 64.7232 | 64.444 | 115.3931 | 123.7015 | 2.7832 | 123.6832 | 80.246 | -0.26093 | 123.7015 | 2.7832 | 80.246 | 115.3931 | 123.6832 | -123.9624 | -123.9532
2353.7188 | 123.8434 | -61.377 | 62.3291 | 0.090256 | 0.018374 | 0.0132 | 0.01232 | 0.065375 | 0.00030767 | 0.082894 | -58.6304 | 62.3611 | -61.6653 | -61.5921 | 53.9703 | 18.8736 | 3.3371 | 2.948 | 62.3428 | -61.6379 | -0.28839 | 0.032043 | 2.7466 | -0.21515 | -8.3588 | -0.26093 | 0.013732 | 3.035 | 64.7141 | 64.325 | 115.3473 | 123.7381 | 2.7466 | 123.7198 | 80.2505 | -0.26093 | 123.7381 | 2.7466 | 80.2505 | 115.3473 | 123.7198 | -123.9944 | -123.967
2354.7188 | 123.8892 | -61.3312 | 62.3154 | 0.0063326 | 0.01816 | 0.017045 | 0.014456 | 0.067084 | 0.00052127 | 0.083535 | -58.5297 | 62.3474 | -61.5921 | -61.528 | 54.0482 | 18.9331 | 3.3508 | 3.0441 | 62.3383 | -61.6379 | -0.26093 | 0.032043 | 2.8015 | -0.19684 | -8.2672 | -0.3067 | 0.022888 | 3.0624 | 64.682 | 64.3753 | 115.3793 | 123.6786 | 2.8015 | 123.6694 | 80.2643 | -0.3067 | 123.6786 | 2.8015 | 80.2643 | 115.3793 | 123.6694 | -123.9075 | -123.9532
2355.7188 | 123.88 | -61.3312 | 62.3291 | 0.0063326 | 0.01816 | 0.02089 | 0.013388 | 0.065802 | 0.00073487 | 0.082894 | -58.548 | 62.3657 | -61.6058 | -61.5509 | 53.9932 | 18.8873 | 3.2501 | 2.9709 | 62.3566 | -61.6196 | -0.27466 | 0.036621 | 2.7832 | -0.21973 | -8.3359 | -0.28839 | 0.027465 | 3.0579 | 64.5813 | 64.3021 | 115.3244 | 123.6969 | 2.7832 | 123.6877 | 80.2185 | -0.28839 | 123.6969 | 2.7832 | 80.2185 | 115.3244 | 123.6877 | -123.9349 | -123.9487
2356.7188 | 123.8434 | -61.3449 | 62.3337 | 0.03685 | 0.01816 | 0.015763 | 0.013388 | 0.066016 | 0.0018031 | 0.082467 | -58.5892 | 62.3749 | -61.6333 | -61.5692 | 53.952 | 18.8736 | 3.3234 | 2.9343 | 62.3245 | -61.6699 | -0.28839 | 0.041199 | 2.7557 | -0.2243 | -8.3817 | -0.32501 | -0.009155 | 3.0441 | 64.6683 | 64.2792 | 115.2969 | 123.7198 | 2.7557 | 123.6694 | 80.2185 | -0.32501 | 123.7198 | 2.7557 | 80.2185 | 115.2969 | 123.6694 | -123.967 | -124.0036
2357.7188 | 123.8617 | -61.3541 | 62.3428 | -0.062332 | 0.019869 | 0.02089 | 0.01232 | 0.067511 | 0.0011621 | 0.08204 | -58.4564 | 62.3657 | -61.6058 | -61.5326 | 53.9108 | 18.988 | 3.2959 | 2.98 | 62.3566 | -61.6425 | -0.25177 | 0.022889 | 2.8976 | -0.17853 | -8.432 | -0.28839 | 0.013733 | 3.1494 | 64.65 | 64.3341 | 115.2649 | 123.7198 | 2.8976 | 123.7106 | 80.3421 | -0.28839 | 123.7198 | 2.8976 | 80.3421 | 115.2649 | 123.7106 | -123.9487 | -123.9853
2358.7188 | 123.9212 | -61.3266 | 62.2787 | 0.19707 | 0.017947 | 0.016831 | 0.0078336 | 0.065589 | 0.00094847 | 0.083535 | -58.5022 | 62.2879 | -61.6333 | -61.5189 | 54.0848 | 19.0704 | 3.1219 | 3.0304 | 62.2971 | -61.6241 | -0.3067 | 0.009155 | 2.8244 | -0.19226 | -8.194 | -0.29755 | 0.01831 | 3.1311 | 64.4485 | 64.357 | 115.4114 | 123.6145 | 2.8244 | 123.6237 | 80.397 | -0.29755 | 123.6145 | 2.8244 | 80.397 | 115.4114 | 123.6237 | -123.912 | -123.9029
2359.7188 | 123.848 | -61.3724 | 62.3337 | 0.013962 | 0.018374 | 0.015763 | 0.014242 | 0.065375 | 9.4068e-05 | 0.082894 | -58.5297 | 62.3611 | -61.6013 | -61.5784 | 53.9932 | 18.9926 | 3.2181 | 2.9297 | 62.352 | -61.647 | -0.22888 | 0.027466 | 2.8427 | -0.20599 | -8.3405 | -0.27466 | 0.018311 | 3.0716 | 64.5905 | 64.3021 | 115.3656 | 123.7335 | 2.8427 | 123.7244 | 80.365 | -0.27466 | 123.7335 | 2.8427 | 80.365 | 115.3656 | 123.7244 | -123.9349 | -123.9807
2360.7188 | 123.8342 | -61.3724 | 62.3566 | 0.021591 | 0.017733 | 0.02089 | 0.01296 | 0.065802 | 0.0018031 | 0.082467 | -58.5571 | 62.3383 | -61.6241 | -61.5646 | 53.9429 | 18.9835 | 3.186 | 2.9114 | 62.3749 | -61.6379 | -0.25177 | -0.01831 | 2.8152 | -0.19226 | -8.4137 | -0.2655 | 0.018311 | 3.067 | 64.5584 | 64.2838 | 115.3152 | 123.7106 | 2.8152 | 123.7473 | 80.3558 | -0.2655 | 123.7106 | 2.8152 | 80.3558 | 115.3152 | 123.7473 | -123.9807 | -123.9944
2361.7188 | 123.8388 | -61.3541 | 62.3383 | 0.052109 | 0.017947 | 0.018968 | 0.013815 | 0.06623 | -0.00011953 | 0.082467 | -58.58 | 62.4023 | -61.6287 | -61.5646 | 53.9383 | 18.8919 | 3.2501 | 2.916 | 62.3428 | -61.6653 | -0.27466 | 0.064087 | 2.774 | -0.21057 | -8.4 | -0.31128 | 0.004577 | 3.0487 | 64.6042 | 64.27 | 115.2924 | 123.7564 | 2.774 | 123.6969 | 80.246 | -0.31128 | 123.7564 | 2.774 | 80.246 | 115.2924 | 123.6969 | -123.967 | -124.0036
2362.7188 | 123.8159 | -61.3632 | 62.3245 | 0.082626 | 0.016238 | 0.016404 | 0.014669 | 0.066016 | 0.0035121 | 0.078835 | -58.6166 | 62.3474 | -61.6196 | -61.5829 | 53.8879 | 18.8782 | 3.3737 | 2.9572 | 62.3428 | -61.6699 | -0.25635 | 0.022888 | 2.7466 | -0.21973 | -8.4366 | -0.3067 | 0.01831 | 3.0029 | 64.7369 | 64.3204 | 115.2512 | 123.7106 | 2.7466 | 123.7061 | 80.2414 | -0.3067 | 123.7106 | 2.7466 | 80.2414 | 115.2512 | 123.7061 | -123.9441 | -123.9944
2363.7188 | 123.8892 | -61.3495 | 62.3383 | 0.15129 | 0.017947 | 0.017899 | 0.01296 | 0.066016 | 0.0015893 | 0.080544 | -58.6258 | 62.3383 | -61.6333 | -61.5921 | 53.92 | 19.0155 | 3.1265 | 2.9572 | 62.3291 | -61.6745 | -0.28381 | 0 | 2.7237 | -0.24261 | -8.4183 | -0.32501 | -0.009155 | 3.0075 | 64.476 | 64.3066 | 115.2695 | 123.6877 | 2.7237 | 123.6786 | 80.365 | -0.32501 | 123.6877 | 2.7237 | 80.365 | 115.2695 | 123.6786 | -123.9716 | -124.0128
2364.7188 | 123.8434 | -61.3632 | 62.352 | 0.013962 | 0.017306 | 0.014268 | 0.014242 | 0.065802 | 0.00052127 | 0.082894 | -58.6212 | 62.4023 | -61.6058 | -61.5738 | 53.8834 | 18.8782 | 3.186 | 2.8976 | 62.3337 | -61.6608 | -0.24262 | 0.050354 | 2.742 | -0.21057 | -8.4686 | -0.29755 | -0.018311 | 2.9846 | 64.5493 | 64.2609 | 115.2466 | 123.7656 | 2.742 | 123.6969 | 80.2414 | -0.29755 | 123.7656 | 2.742 | 80.2414 | 115.2466 | 123.6969 | -123.9578 | -124.0128
2365.7188 | 123.8159 | -61.3541 | 62.3428 | 0.029221 | 0.02051 | 0.015122 | 0.011038 | 0.064948 | 0.0035121 | 0.080758 | -58.667 | 62.3886 | -61.647 | -61.5875 | 53.8788 | 18.9606 | 3.0991 | 2.8564 | 62.352 | -61.6608 | -0.29297 | 0.045777 | 2.6871 | -0.23346 | -8.4641 | -0.3067 | 0.009156 | 2.98 | 64.4531 | 64.2105 | 115.2328 | 123.7427 | 2.6871 | 123.7061 | 80.3146 | -0.3067 | 123.7427 | 2.6871 | 80.3146 | 115.2328 | 123.7061 | -123.9899 | -124.0036
2366.7188 | 123.8297 | -61.3815 | 62.3474 | 0.15129 | 0.017733 | 0.018113 | 0.011679 | 0.064521 | 0.0045801 | 0.083108 | -58.6075 | 62.384 | -61.6379 | -61.5692 | 54.2953 | 19.162 | 3.0533 | 3.0579 | 62.352 | -61.6928 | -0.25635 | 0.036621 | 2.774 | -0.18768 | -8.0521 | -0.31128 | 0.004578 | 3.0304 | 64.4348 | 64.4394 | 115.6769 | 123.7656 | 2.774 | 123.7335 | 80.5435 | -0.31128 | 123.7656 | 2.774 | 80.5435 | 115.6769 | 123.7335 | -123.9853 | -124.0402
2367.7188 | 123.848 | -61.3678 | 62.3383 | 0.12077 | 0.017306 | 0.020036 | 0.01232 | 0.064093 | -0.0016149 | 0.081613 | -58.6624 | 62.3611 | -61.6287 | -61.9171 | 53.6682 | 19.2215 | 3.3554 | 2.9892 | 62.3474 | -61.6379 | -0.26093 | 0.022888 | 2.7054 | -0.54932 | -8.67 | -0.27008 | 0.009155 | 2.9663 | 64.7232 | 64.357 | 115.036 | 123.7289 | 2.7054 | 123.7152 | 80.5893 | -0.27008 | 123.7289 | 2.7054 | 80.5893 | 115.036 | 123.7152 | -123.967 | -123.9761
2368.7188 | 123.9761 | -61.3358 | 62.2925 | 0.12077 | 0.016238 | 0.012986 | 0.0046292 | 0.067725 | 9.4068e-05 | 0.081185 | -58.4473 | 62.2467 | -61.6287 | -61.441 | 54.0848 | 19.281 | 3.0762 | 3.1952 | 62.3062 | -61.6058 | -0.29297 | -0.045776 | 2.8885 | -0.10529 | -8.2077 | -0.27008 | 0.013733 | 3.1815 | 64.4119 | 64.5309 | 115.4205 | 123.5825 | 2.8885 | 123.642 | 80.6168 | -0.27008 | 123.5825 | 2.8885 | 80.6168 | 115.4205 | 123.642 | -123.9212 | -123.8983
2369.7188 | 123.8434 | -61.3495 | 62.3291 | 0.14366 | 0.016878 | 0.016618 | 0.014669 | 0.064307 | 0.0018031 | 0.080972 | -58.6441 | 62.352 | -61.615 | -61.5967 | 53.9429 | 19.0201 | 3.067 | 2.9343 | 62.3062 | -61.6791 | -0.2655 | 0.022888 | 2.7054 | -0.24719 | -8.3862 | -0.32959 | -0.022889 | 2.9709 | 64.4165 | 64.2838 | 115.2924 | 123.7015 | 2.7054 | 123.6557 | 80.3696 | -0.32959 | 123.7015 | 2.7054 | 80.3696 | 115.2924 | 123.6557 | -123.9441 | -124.0082
2370.7188 | 123.848 | -61.3815 | 62.3245 | 0.13603 | 0.016878 | 0.02089 | 0.012106 | 0.064948 | 0.0018031 | 0.081399 | -58.6349 | 62.3566 | -61.6241 | -61.5784 | 53.92 | 19.0704 | 3.0945 | 3.0029 | 62.3199 | -61.6745 | -0.24262 | 0.032043 | 2.7466 | -0.19684 | -8.4045 | -0.29297 | -0.004578 | 2.9892 | 64.476 | 64.3845 | 115.3015 | 123.7381 | 2.7466 | 123.7015 | 80.452 | -0.29297 | 123.7381 | 2.7466 | 80.452 | 115.3015 | 123.7015 | -123.9487 | -123.999
2371.7188 | 123.7061 | -61.3953 | 62.265 | 0.059738 | 0.018374 | 0.022813 | 0.013388 | 0.062812 | 0.00094847 | 0.080117 | -58.7265 | 62.3978 | -61.6287 | -61.6287 | 54.0665 | 19.1345 | 3.154 | 2.9846 | 62.3199 | -61.702 | -0.23346 | 0.13275 | 2.6688 | -0.23346 | -8.1985 | -0.3067 | 0.054931 | 2.9022 | 64.5493 | 64.3799 | 115.4617 | 123.793 | 2.6688 | 123.7152 | 80.5298 | -0.3067 | 123.793 | 2.6688 | 80.5298 | 115.4617 | 123.7152 | -123.8937 | -123.967
2372.7188 | 123.8113 | -61.3586 | 62.3291 | 0.059738 | 0.017306 | 0.018754 | 0.013388 | 0.063239 | -0.00054693 | 0.082894 | -58.6441 | 62.3886 | -61.6333 | -61.615 | 53.9658 | 19.075 | 3.2776 | 3.0533 | 62.3383 | -61.6699 | -0.27466 | 0.059509 | 2.7145 | -0.25635 | -8.3633 | -0.31128 | 0.009155 | 2.9892 | 64.6362 | 64.4119 | 115.3244 | 123.7473 | 2.7145 | 123.6969 | 80.4337 | -0.31128 | 123.7473 | 2.7145 | 80.4337 | 115.3244 | 123.6969 | -123.9624 | -123.999
2373.7188 | 123.8892 | -61.3449 | 62.3108 | 0.1284 | 0.017306 | 0.011704 | 0.0039882 | 0.064307 | -0.00033333 | 0.080544 | -58.6121 | 62.2696 | -61.6058 | -61.5509 | 54.0665 | 19.075 | 3.0808 | 3.1723 | 62.2925 | -61.6241 | -0.26093 | -0.041199 | 2.7328 | -0.20599 | -8.2443 | -0.27924 | -0.018311 | 2.9938 | 64.4257 | 64.5172 | 115.4114 | 123.6145 | 2.7328 | 123.6374 | 80.4199 | -0.27924 | 123.6145 | 2.7328 | 80.4199 | 115.4114 | 123.6374 | -123.9166 | -123.9349
2374.7188 | 123.8663 | -61.3449 | 62.3566 | 1.5246 | 0.02051 | 0.015977 | 0.014669 | 0.065802 | 9.4068e-05 | 0.081185 | -58.5617 | 62.3703 | -61.6241 | -61.6013 | 53.9978 | 19.0979 | 3.2364 | 3.0762 | 62.3245 | -61.6791 | -0.27924 | 0.013733 | 2.7832 | -0.25635 | -8.3588 | -0.33417 | -0.032043 | 3.0624 | 64.5813 | 64.4211 | 115.3427 | 123.7152 | 2.7832 | 123.6694 | 80.4428 | -0.33417 | 123.7152 | 2.7832 | 80.4428 | 115.3427 | 123.6694 | -123.9807 | -124.0356
2375.7188 | 123.8297 | -61.3678 | 62.3474 | 0.14366 | 0.022646 | 0.019395 | 0.01531 | 0.06623 | 0.0020167 | 0.079904 | -58.8318 | 62.2742 | -61.6562 | -61.6104 | 54.0161 | 19.0979 | 3.1998 | 3.0304 | 62.3428 | -61.6562 | -0.28839 | -0.073242 | 2.536 | -0.24262 | -8.3313 | -0.28839 | -0.004578 | 2.8244 | 64.5676 | 64.3982 | 115.3839 | 123.642 | 2.536 | 123.7106 | 80.4657 | -0.28839 | 123.642 | 2.536 | 80.4657 | 115.3839 | 123.7106 | -124.0036 | -124.0036
2376.7188 | 123.8709 | -61.3815 | 62.3291 | 0.15892 | 0.01816 | 0.020463 | 0.012747 | 0.065589 | 0.00030767 | 0.077554 | -58.6533 | 62.384 | -61.6379 | -61.3403 | 54.2679 | 19.162 | 3.2455 | 3.1219 | 62.3291 | -61.6791 | -0.25635 | 0.054931 | 2.7283 | 0.041199 | -8.0612 | -0.29755 | 0 | 2.9846 | 64.6271 | 64.5035 | 115.6494 | 123.7656 | 2.7283 | 123.7106 | 80.5435 | -0.29755 | 123.7656 | 2.7283 | 80.5435 | 115.6494 | 123.7106 | -123.967 | -124.0082
2377.7188 | 123.8663 | -61.3495 | 62.3291 | 0.082626 | 0.019869 | 0.018968 | 0.013388 | 0.064093 | 0.00094847 | 0.080972 | -58.5983 | 62.3199 | -61.6104 | -61.5829 | 54.0207 | 18.5806 | 3.2135 | 3.0716 | 62.3245 | -61.6379 | -0.26093 | -0.009156 | 2.7512 | -0.23346 | -8.3084 | -0.28839 | -0.004578 | 3.0121 | 64.563 | 64.4211 | 115.3702 | 123.6694 | 2.7512 | 123.674 | 79.9301 | -0.28839 | 123.6694 | 2.7512 | 79.9301 | 115.3702 | 123.674 | -123.9395 | -123.967
2378.7188 | 124.0356 | -61.3541 | 62.2787 | 0.25047 | 0.015383 | 0.018754 | 0.0084744 | 0.065589 | 0.0018031 | 0.082253 | -58.5159 | 62.2421 | -61.6287 | -61.5005 | 54.126 | 18.663 | 3.273 | 3.1036 | 62.2559 | -61.6287 | -0.27466 | -0.036622 | 2.8381 | -0.14648 | -8.1528 | -0.27466 | -0.022889 | 3.1128 | 64.6271 | 64.4577 | 115.48 | 123.5962 | 2.8381 | 123.6099 | 80.0171 | -0.27466 | 123.5962 | 2.8381 | 80.0171 | 115.48 | 123.6099 | -123.9075 | -123.9075
2379.7188 | 123.7885 | -61.3815 | 62.3245 | 0.19707 | 0.017733 | 0.01854 | 0.014242 | 0.064948 | 0.0015893 | 0.080758 | -58.5663 | 62.3337 | -61.6379 | -61.5829 | 53.9566 | 18.5898 | 3.4287 | 3.1036 | 62.3566 | -61.6974 | -0.25635 | 0.009155 | 2.8152 | -0.20142 | -8.3679 | -0.31586 | 0.032043 | 3.0716 | 64.8102 | 64.4852 | 115.3381 | 123.7152 | 2.8152 | 123.7381 | 79.9713 | -0.31586 | 123.7152 | 2.8152 | 79.9713 | 115.3381 | 123.7381 | -123.9624 | -124.0219
2380.7188 | 123.8297 | -61.3907 | 62.3383 | 0.15129 | 0.017733 | 0.018968 | 0.014242 | 0.066443 | -0.0016149 | 0.080331 | -58.9096 | 62.2833 | -61.6516 | -61.6287 | 53.9795 | 18.6813 | 3.3737 | 3.0899 | 62.3108 | -61.6653 | -0.26093 | -0.054932 | 2.4811 | -0.23804 | -8.3588 | -0.27466 | -0.027466 | 2.742 | 64.7644 | 64.4806 | 115.3702 | 123.674 | 2.4811 | 123.7015 | 80.072 | -0.27466 | 123.674 | 2.4811 | 80.072 | 115.3702 | 123.7015 | -123.9899 | -124.0036
2381.7188 | 123.8434 | -61.3541 | 62.3428 | 0.14366 | 0.018801 | 0.020463 | 0.012747 | 0.064734 | 0.0018031 | 0.084817 | -58.6212 | 62.3611 | -61.6241 | -61.8896 | 53.7186 | 18.7546 | 3.4744 | 3.0304 | 62.3566 | -61.6562 | -0.27008 | 0.018311 | 2.7328 | -0.53558 | -8.6243 | -0.30212 | 0.013733 | 3.0029 | 64.8285 | 64.3845 | 115.0726 | 123.7152 | 2.7328 | 123.7106 | 80.1086 | -0.30212 | 123.7152 | 2.7328 | 80.1086 | 115.0726 | 123.7106 | -123.967 | -123.999
2382.7188 | 123.6923 | -61.4044 | 62.2833 | 0.11314 | 0.017733 | 0.018968 | 0.011465 | 0.064521 | 0.0028711 | 0.082894 | -58.6716 | 62.3886 | -61.615 | -61.5784 | 54.0207 | 18.631 | 3.3051 | 3.0853 | 62.3154 | -61.6653 | -0.21057 | 0.10529 | 2.7328 | -0.17395 | -8.2626 | -0.26093 | 0.032044 | 2.9434 | 64.7095 | 64.4897 | 115.4251 | 123.793 | 2.7328 | 123.7198 | 80.0354 | -0.26093 | 123.793 | 2.7328 | 80.0354 | 115.4251 | 123.7198 | -123.8983 | -123.9487
2383.7344 | 123.912 | -61.3266 | 62.3611 | -0.22255 | 0.016238 | 0.019395 | 0.012533 | 0.064734 | 0.0015893 | 0.081826 | -58.5526 | 62.3886 | -61.6058 | -61.5051 | 54.0573 | 18.6905 | 3.3737 | 3.1403 | 62.3657 | -61.6425 | -0.27924 | 0.027466 | 2.774 | -0.17853 | -8.3038 | -0.31586 | 0.004578 | 3.0533 | 64.7003 | 64.4669 | 115.3839 | 123.7152 | 2.774 | 123.6923 | 80.0171 | -0.31586 | 123.7152 | 2.774 | 80.0171 | 115.3839 | 123.6923 | -123.967 | -124.0036
2384.7188 | 123.8388 | -61.3541 | 62.3383 | 1.4712 | 0.016665 | 0.014695 | 0.012747 | 0.064307 | 0.00030767 | 0.083108 | -58.5571 | 62.3566 | -61.6287 | -61.5829 | 53.9246 | 18.4525 | 3.4012 | 3.0396 | 62.3245 | -61.6608 | -0.27466 | 0.01831 | 2.7969 | -0.22888 | -8.4137 | -0.3067 | -0.013733 | 3.0716 | 64.7552 | 64.3936 | 115.2786 | 123.7106 | 2.7969 | 123.6786 | 79.8065 | -0.3067 | 123.7106 | 2.7969 | 79.8065 | 115.2786 | 123.6786 | -123.967 | -123.999
2385.7188 | 123.8388 | -61.3907 | 62.3474 | 0.029221 | 0.019015 | 0.017472 | 0.012747 | 0.06687 | 0.00094847 | 0.081826 | -58.6121 | 62.3795 | -61.615 | -61.5829 | 53.952 | 18.544 | 3.5248 | 3.1265 | 62.3611 | -61.6516 | -0.2243 | 0.032044 | 2.7786 | -0.19226 | -8.3954 | -0.26093 | 0.013733 | 3.0029 | 64.9155 | 64.5172 | 115.3427 | 123.7701 | 2.7786 | 123.7518 | 79.9347 | -0.26093 | 123.7701 | 2.7786 | 79.9347 | 115.3427 | 123.7518 | -123.9624 | -123.999
2386.7188 | 123.8068 | -61.3632 | 62.3291 | 0.15892 | 0.020724 | 0.019608 | 0.015097 | 0.064948 | 0.0035121 | 0.079904 | -58.6349 | 62.3428 | -61.6241 | -61.6562 | 54.1992 | 18.9148 | 3.3325 | 3.1586 | 62.3383 | -61.6516 | -0.26093 | 0.013732 | 2.7283 | -0.29297 | -8.1299 | -0.28839 | 0.009155 | 2.9892 | 64.6957 | 64.5218 | 115.5624 | 123.7061 | 2.7283 | 123.7015 | 80.278 | -0.28839 | 123.7061 | 2.7283 | 80.278 | 115.5624 | 123.7015 | -123.9532 | -123.9807
2387.7188 | 123.9304 | -61.3541 | 62.3383 | 0.082626 | 0.017733 | 0.018113 | 0.01296 | 0.065375 | -0.00054693 | 0.083108 | -58.6395 | 62.3749 | -61.6333 | -61.5967 | 53.8605 | 18.7729 | 3.2547 | 2.7695 | 62.2513 | -61.7157 | -0.27924 | 0.036621 | 2.7145 | -0.24262 | -8.4778 | -0.36163 | -0.086975 | 2.9938 | 64.6088 | 64.1235 | 115.2145 | 123.7289 | 2.7145 | 123.6053 | 80.127 | -0.36163 | 123.7289 | 2.7145 | 80.127 | 115.2145 | 123.6053 | -123.9716 | -124.054
2388.7344 | 123.9075 | -61.2946 | 62.3657 | -0.23781 | 0.015597 | 0.016191 | 0.0046292 | 0.064307 | -0.00054693 | 0.081185 | -58.5434 | 62.3016 | -61.5875 | -61.5051 | 53.9795 | 18.7683 | 3.4103 | 3.2089 | 62.3428 | -61.6013 | -0.29297 | -0.064087 | 2.7512 | -0.21057 | -8.3862 | -0.3067 | -0.022889 | 3.0441 | 64.7049 | 64.5035 | 115.274 | 123.5962 | 2.7512 | 123.6374 | 80.0629 | -0.3067 | 123.5962 | 2.7512 | 80.0629 | 115.274 | 123.6374 | -123.9532 | -123.967
2389.7188 | 123.7976 | -61.377 | 62.3474 | 0.03685 | 0.018801 | 0.017259 | 0.015524 | 0.067298 | -0.00076053 | 0.082467 | -58.6395 | 62.3657 | -61.6058 | -61.615 | 53.801 | 18.6401 | 3.4744 | 3.0808 | 62.3245 | -61.6653 | -0.22888 | 0.018311 | 2.7374 | -0.23804 | -8.5464 | -0.28839 | -0.022888 | 2.9663 | 64.8514 | 64.4577 | 115.1779 | 123.7427 | 2.7374 | 123.7015 | 80.0171 | -0.28839 | 123.7427 | 2.7374 | 80.0171 | 115.1779 | 123.7015 | -123.9532 | -124.0128
2390.7188 | 123.8251 | -61.3678 | 62.3611 | 0.082626 | 0.016451 | 0.019181 | 0.014242 | 0.064521 | 0.0013757 | 0.080758 | -58.6212 | 62.3749 | -61.6104 | -61.5967 | 53.801 | 18.631 | 3.511 | 3.1082 | 62.3291 | -61.702 | -0.24262 | 0.013733 | 2.7466 | -0.22888 | -8.5602 | -0.33417 | -0.032043 | 2.9892 | 64.8788 | 64.476 | 115.1688 | 123.7427 | 2.7466 | 123.6969 | 79.9988 | -0.33417 | 123.7427 | 2.7466 | 79.9988 | 115.1688 | 123.6969 | -123.9716 | -124.0631
2391.7188 | 123.8571 | -61.3586 | 62.3428 | 0.14366 | 0.01816 | 0.021745 | 0.015951 | 0.065375 | -0.00011953 | 0.082894 | -58.8593 | 62.3016 | -61.6745 | -61.615 | 53.8879 | 18.7729 | 3.4515 | 3.067 | 62.352 | -61.6791 | -0.31586 | -0.041198 | 2.4994 | -0.25635 | -8.4549 | -0.32043 | 0.009156 | 2.8152 | 64.8102 | 64.4257 | 115.2466 | 123.6603 | 2.4994 | 123.7106 | 80.1315 | -0.32043 | 123.6603 | 2.4994 | 80.1315 | 115.2466 | 123.7106 | -124.0173 | -124.0219
2392.7188 | 123.8342 | -61.3403 | 62.3337 | 0.029221 | 0.017306 | 0.020036 | 0.014029 | 0.066657 | 0.00094847 | 0.080972 | -58.6075 | 62.3703 | -61.615 | -61.5738 | 53.6957 | 18.3884 | 3.3508 | 3.0716 | 62.3566 | -61.6699 | -0.27466 | 0.036621 | 2.7328 | -0.23346 | -8.638 | -0.32959 | 0.022888 | 3.0075 | 64.6912 | 64.4119 | 115.036 | 123.7106 | 2.7328 | 123.6969 | 79.7287 | -0.32959 | 123.7106 | 2.7328 | 79.7287 | 115.036 | 123.6969 | -123.9487 | -124.0036
2393.7344 | 123.9441 | -61.2946 | 62.3428 | -0.35988 | 0.014529 | 0.016618 | 0.00527 | 0.064521 | -0.0014013 | 0.081399 | -58.5938 | 62.2971 | -61.5829 | -61.441 | 53.8605 | 18.6172 | 3.3096 | 3.2455 | 62.3291 | -61.5875 | -0.28839 | -0.045776 | 2.7008 | -0.14648 | -8.4824 | -0.29297 | -0.013732 | 2.9892 | 64.6042 | 64.5401 | 115.155 | 123.5916 | 2.7008 | 123.6237 | 79.9118 | -0.29297 | 123.5916 | 2.7008 | 79.9118 | 115.155 | 123.6237 | -123.9258 | -123.9304
2394.7188 | 123.7976 | -61.3449 | 62.3383 | 0.11314 | 0.017733 | 0.015122 | 0.01531 | 0.065375 | 0.0013757 | 0.083962 | -58.6304 | 62.3703 | -61.615 | -61.6287 | 53.7186 | 18.6493 | 3.4424 | 3.0533 | 62.3383 | -61.6699 | -0.27008 | 0.032043 | 2.7145 | -0.28381 | -8.6197 | -0.32501 | 0 | 2.9846 | 64.7873 | 64.3982 | 115.0635 | 123.7152 | 2.7145 | 123.6832 | 79.9942 | -0.32501 | 123.7152 | 2.7145 | 79.9942 | 115.0635 | 123.6832 | -123.9532 | -124.0082
2395.7188 | 123.8251 | -61.3678 | 62.3154 | 0.18181 | 0.017519 | 0.014695 | 0.012533 | 0.064093 | 0.00073487 | 0.082253 | -58.5617 | 62.384 | -61.6287 | -61.5967 | 53.7781 | 18.8782 | 3.5294 | 3.1219 | 62.3474 | -61.6928 | -0.26093 | 0.068664 | 2.8061 | -0.22888 | -8.5373 | -0.32501 | 0.032043 | 3.067 | 64.8972 | 64.4897 | 115.1459 | 123.7518 | 2.8061 | 123.7152 | 80.246 | -0.32501 | 123.7518 | 2.8061 | 80.246 | 115.1459 | 123.7152 | -123.9441 | -124.0082
2396.7188 | 123.8525 | -61.3678 | 62.3611 | 0.04448 | 0.019015 | 0.01854 | 0.014456 | 0.066657 | 0.0030847 | 0.082253 | -58.5571 | 62.3337 | -61.6241 | -61.5829 | 53.6865 | 18.8004 | 3.5431 | 3.1128 | 62.3657 | -61.6516 | -0.25635 | -0.027466 | 2.8107 | -0.21515 | -8.6746 | -0.28381 | 0.004578 | 3.067 | 64.9109 | 64.4806 | 115.0543 | 123.7015 | 2.8107 | 123.7335 | 80.1682 | -0.28381 | 123.7015 | 2.8107 | 80.1682 | 115.0543 | 123.7335 | -123.9853 | -124.0128
2397.7188 | 123.8113 | -61.3541 | 62.3245 | 0.17418 | 0.018374 | 0.015336 | 0.01296 | 0.066657 | -0.00011953 | 0.083535 | -58.5983 | 62.352 | -61.6745 | -61.7706 | 54.007 | 19.0613 | 3.3737 | 3.1357 | 62.3657 | -61.6608 | -0.32044 | 0.027466 | 2.7557 | -0.41656 | -8.3176 | -0.3067 | 0.041199 | 3.0762 | 64.7278 | 64.4897 | 115.361 | 123.7061 | 2.7557 | 123.7198 | 80.4153 | -0.3067 | 123.7061 | 2.7557 | 80.4153 | 115.361 | 123.7198 | -123.999 | -123.9853
2398.7344 | 123.8937 | -61.2991 | 62.3383 | -0.21492 | 0.014742 | 0.015977 | 0.0078336 | 0.06623 | 0.0015893 | 0.083535 | -58.5663 | 62.2925 | -61.5967 | -61.4731 | 53.8147 | 18.9606 | 3.479 | 3.2181 | 62.352 | -61.6241 | -0.29755 | -0.045777 | 2.7328 | -0.17395 | -8.5236 | -0.32501 | 0.013733 | 3.0304 | 64.7781 | 64.5172 | 115.1138 | 123.5916 | 2.7328 | 123.6511 | 80.2597 | -0.32501 | 123.5916 | 2.7328 | 80.2597 | 115.1138 | 123.6511 | -123.9349 | -123.9624
2399.7188 | 123.8434 | -61.3312 | 62.3245 | 0.04448 | 0.016024 | 0.018113 | 0.014242 | 0.065802 | 0.00052127 | 0.083535 | -58.5297 | 62.352 | -61.615 | -61.5646 | 53.7827 | 19.1574 | 3.4378 | 3.0762 | 62.3154 | -61.6562 | -0.28381 | 0.027466 | 2.8015 | -0.23346 | -8.5419 | -0.32501 | -0.009155 | 3.0853 | 64.769 | 64.4073 | 115.1138 | 123.6832 | 2.8015 | 123.6465 | 80.4886 | -0.32501 | 123.6832 | 2.8015 | 80.4886 | 115.1138 | 123.6465 | -123.9395 | -123.9807
2400.7188 | 123.8342 | -61.3678 | 62.3566 | 0.15892 | 0.01816 | 0.017686 | 0.013174 | 0.067511 | 0.00030767 | 0.080972 | -58.5983 | 62.3566 | -61.6241 | -61.6013 | 53.6545 | 19.0247 | 3.5797 | 3.0853 | 62.3383 | -61.6745 | -0.25635 | 0 | 2.7695 | -0.23346 | -8.7021 | -0.3067 | -0.01831 | 3.0258 | 64.9475 | 64.4531 | 115.0223 | 123.7244 | 2.7695 | 123.7061 | 80.3925 | -0.3067 | 123.7244 | 2.7695 | 80.3925 | 115.0223 | 123.7061 | -123.9807 | -124.0311
2401.7188 | 123.8297 | -61.3861 | 62.3566 | 0.029221 | 0.016878 | 0.020463 | 0.013388 | 0.066443 | 0.0013757 | 0.081185 | -58.5526 | 62.384 | -61.6287 | -61.5784 | 53.6819 | 19.2444 | 3.598 | 3.1128 | 62.3566 | -61.6653 | -0.24262 | 0.027466 | 2.8336 | -0.19226 | -8.6746 | -0.27924 | 0 | 3.0762 | 64.9841 | 64.4989 | 115.0681 | 123.7701 | 2.8336 | 123.7427 | 80.6305 | -0.27924 | 123.7701 | 2.8336 | 80.6305 | 115.0681 | 123.7427 | -123.9853 | -124.0219
2402.7188 | 123.7976 | -61.3861 | 62.3245 | 0.04448 | 0.016451 | 0.019395 | 0.013815 | 0.067725 | 0.0020167 | 0.081185 | -58.5709 | 62.3795 | -61.615 | -61.5829 | 53.833 | 19.2352 | 3.4561 | 3.1586 | 62.3245 | -61.6516 | -0.22888 | 0.054932 | 2.8152 | -0.19684 | -8.4915 | -0.2655 | 0 | 3.0441 | 64.8422 | 64.5447 | 115.2191 | 123.7656 | 2.8152 | 123.7106 | 80.6213 | -0.2655 | 123.7656 | 2.8152 | 80.6213 | 115.2191 | 123.7106 | -123.9395 | -123.9761
2403.7188 | 123.9487 | -61.3266 | 62.3062 | 0.18944 | 0.016878 | 0.014482 | 0.0099698 | 0.067084 | 0.00052127 | 0.082467 | -58.58 | 62.3062 | -61.6608 | -61.5143 | 53.7964 | 19.2307 | 3.4103 | 3.2043 | 62.2833 | -61.6379 | -0.33417 | 0 | 2.7466 | -0.18768 | -8.5098 | -0.31128 | -0.022888 | 3.0808 | 64.7369 | 64.5309 | 115.123 | 123.6328 | 2.7466 | 123.6099 | 80.5573 | -0.31128 | 123.6328 | 2.7466 | 80.5573 | 115.123 | 123.6099 | -123.967 | -123.9441
2404.7188 | 123.848 | -61.3678 | 62.352 | 0.067368 | 0.018801 | 0.021531 | 0.01531 | 0.066443 | -0.00076053 | 0.082681 | -58.5297 | 62.3657 | -61.6196 | -61.5555 | 53.6728 | 19.0842 | 3.5706 | 3.1723 | 62.3566 | -61.6562 | -0.25177 | 0.013733 | 2.8381 | -0.18768 | -8.6792 | -0.28839 | 0.004577 | 3.0899 | 64.9384 | 64.5401 | 115.0406 | 123.7335 | 2.8381 | 123.7244 | 80.452 | -0.28839 | 123.7335 | 2.8381 | 80.452 | 115.0406 | 123.7244 | -123.9716 | -124.0082
2405.7188 | 123.8342 | -61.3586 | 62.3611 | -0.039444 | 0.017519 | 0.019181 | 0.014669 | 0.065589 | 0.0039393 | 0.081613 | -58.5342 | 62.3428 | -61.6287 | -61.5555 | 53.5858 | 19.0887 | 3.5751 | 3.1631 | 62.3566 | -61.6562 | -0.27008 | -0.018311 | 2.8244 | -0.19684 | -8.7753 | -0.29755 | -0.004578 | 3.0945 | 64.9338 | 64.5218 | 114.9445 | 123.7015 | 2.8244 | 123.7152 | 80.4474 | -0.29755 | 123.7015 | 2.8244 | 80.4474 | 114.9445 | 123.7152 | -123.9899 | -124.0173
2406.7188 | 123.8434 | -61.322 | 62.3474 | -0.054703 | 0.018374 | 0.018327 | 0.013388 | 0.06687 | 0.00094847 | 0.082681 | -58.5114 | 62.352 | -61.6241 | -61.5509 | 53.746 | 18.9194 | 3.5797 | 3.1631 | 62.3566 | -61.6333 | -0.30213 | 0.004578 | 2.8107 | -0.22888 | -8.6014 | -0.31128 | 0.009155 | 3.1128 | 64.9017 | 64.4852 | 115.0681 | 123.674 | 2.8107 | 123.6786 | 80.2414 | -0.31128 | 123.674 | 2.8107 | 80.2414 | 115.0681 | 123.6786 | -123.9716 | -123.9807
2407.7188 | 123.8068 | -61.3861 | 62.3657 | 0.021591 | 0.017733 | 0.020677 | 0.012747 | 0.065589 | 0.0013757 | 0.08204 | -58.5754 | 62.352 | -61.6196 | -61.5692 | 53.7643 | 18.8919 | 3.6484 | 3.1082 | 62.3474 | -61.6333 | -0.23346 | -0.013733 | 2.8107 | -0.18311 | -8.6014 | -0.24719 | -0.018311 | 3.0441 | 65.0345 | 64.4943 | 115.1505 | 123.7381 | 2.8107 | 123.7335 | 80.278 | -0.24719 | 123.7381 | 2.8107 | 80.278 | 115.1505 | 123.7335 | -123.9853 | -123.999
2408.7188 | 123.9532 | -61.322 | 62.2971 | 0.21996 | 0.013674 | 0.017899 | 0.0089016 | 0.064521 | -0.00054693 | 0.080758 | -58.5388 | 62.2742 | -61.6287 | -61.7157 | 53.7048 | 19.0887 | 3.5156 | 3.1631 | 62.2925 | -61.5738 | -0.3067 | -0.022888 | 2.7832 | -0.39368 | -8.5922 | -0.25177 | -0.004578 | 3.0899 | 64.8376 | 64.4852 | 115.0269 | 123.5962 | 2.7832 | 123.6145 | 80.4108 | -0.25177 | 123.5962 | 2.7832 | 80.4108 | 115.0269 | 123.6145 | -123.9258 | -123.8708
2409.7188 | 123.8663 | -61.3541 | 62.3428 | 0.04448 | 0.020083 | 0.017045 | 0.012747 | 0.064521 | 9.4068e-05 | 0.082253 | -58.5846 | 62.3749 | -61.6058 | -61.5509 | 53.7231 | 18.8599 | 3.5477 | 3.0808 | 62.3337 | -61.6791 | -0.25177 | 0.032044 | 2.7695 | -0.19684 | -8.6197 | -0.32501 | -0.009155 | 3.0212 | 64.9017 | 64.4348 | 115.0772 | 123.7289 | 2.7695 | 123.6877 | 80.2139 | -0.32501 | 123.7289 | 2.7695 | 80.2139 | 115.0772 | 123.6877 | -123.9487 | -124.0219
2410.7188 | 123.848 | -61.3495 | 62.3566 | -0.054703 | 0.019228 | 0.015977 | 0.014029 | 0.066016 | 9.4068e-05 | 0.080331 | -58.5022 | 62.3474 | -61.6013 | -61.5646 | 53.7643 | 18.8965 | 3.5614 | 3.0945 | 62.3566 | -61.6516 | -0.25177 | -0.009155 | 2.8473 | -0.21515 | -8.5922 | -0.30212 | 0 | 3.0991 | 64.9109 | 64.444 | 115.1138 | 123.6969 | 2.8473 | 123.7061 | 80.246 | -0.30212 | 123.6969 | 2.8473 | 80.246 | 115.1138 | 123.7061 | -123.9578 | -124.0082
2411.7188 | 123.8754 | -61.3449 | 62.3566 | -0.054703 | 0.016665 | 0.020677 | 0.011251 | 0.067084 | 0.0013757 | 0.081826 | -58.5251 | 62.352 | -61.6104 | -61.528 | 53.714 | 18.8141 | 3.6255 | 3.0991 | 62.352 | -61.6562 | -0.2655 | -0.004577 | 2.8198 | -0.18311 | -8.6426 | -0.31128 | -0.004577 | 3.0853 | 64.9704 | 64.444 | 115.0589 | 123.6969 | 2.8198 | 123.6969 | 80.159 | -0.31128 | 123.6969 | 2.8198 | 80.159 | 115.0589 | 123.6969 | -123.967 | -124.0128
2412.7188 | 123.848 | -61.3403 | 62.3474 | -0.024185 | 0.019228 | 0.016831 | 0.01296 | 0.06623 | 0.00030767 | 0.082467 | -58.5159 | 62.3611 | -61.6058 | -61.5417 | 53.7598 | 18.9789 | 3.6484 | 3.1265 | 62.3611 | -61.6196 | -0.2655 | 0.013733 | 2.8244 | -0.20142 | -8.5876 | -0.27924 | 0.013733 | 3.0899 | 64.9887 | 64.4669 | 115.1001 | 123.7015 | 2.8244 | 123.7015 | 80.3192 | -0.27924 | 123.7015 | 2.8244 | 80.3192 | 115.1001 | 123.7015 | -123.9532 | -123.967
2413.7188 | 123.9212 | -61.3403 | 62.3016 | 0.23521 | 0.01581 | 0.014909 | 0.010397 | 0.06687 | 0.0024439 | 0.083322 | -58.6075 | 62.3016 | -61.6333 | -61.5372 | 53.7964 | 19.0063 | 3.4882 | 3.1265 | 62.3016 | -61.6104 | -0.29297 | 0 | 2.7328 | -0.19684 | -8.5052 | -0.27008 | 0 | 3.0258 | 64.8285 | 64.4669 | 115.1367 | 123.642 | 2.7328 | 123.642 | 80.3467 | -0.27008 | 123.642 | 2.7328 | 80.3467 | 115.1367 | 123.642 | -123.9349 | -123.912
2414.7188 | 123.8342 | -61.3495 | 62.3474 | 0.0063326 | 0.02051 | 0.016404 | 0.014242 | 0.064734 | 0.0024439 | 0.085031 | -58.5526 | 62.384 | -61.5967 | -61.5601 | 53.7506 | 19.0247 | 3.6667 | 3.1311 | 62.3428 | -61.6653 | -0.24719 | 0.036621 | 2.7969 | -0.21057 | -8.5968 | -0.31586 | -0.004578 | 3.0441 | 65.0162 | 64.4806 | 115.1001 | 123.7335 | 2.7969 | 123.6923 | 80.3741 | -0.31586 | 123.7335 | 2.7969 | 80.3741 | 115.1001 | 123.6923 | -123.9441 | -124.0128
2415.7188 | 123.88 | -61.3495 | 62.3657 | -0.0012969 | 0.017306 | 0.016831 | 0.013388 | 0.065802 | 0.0024439 | 0.082467 | -58.5297 | 62.3566 | -61.6058 | -61.5463 | 53.6499 | 18.9697 | 3.6118 | 3.1219 | 62.352 | -61.6562 | -0.25635 | -0.009156 | 2.8198 | -0.19684 | -8.7158 | -0.3067 | -0.013733 | 3.0762 | 64.9612 | 64.4714 | 114.9994 | 123.7061 | 2.8198 | 123.7015 | 80.3192 | -0.3067 | 123.7061 | 2.8198 | 80.3192 | 114.9994 | 123.7015 | -123.9716 | -124.0219
2416.7188 | 123.8754 | -61.3678 | 62.3611 | -0.039444 | 0.020083 | 0.017259 | 0.012106 | 0.06623 | 9.4068e-05 | 0.083108 | -58.5114 | 62.3611 | -61.6058 | -61.528 | 53.8193 | 19.0063 | 3.6346 | 3.1769 | 62.3337 | -61.6608 | -0.23804 | 0 | 2.8564 | -0.16022 | -8.5419 | -0.29297 | -0.027466 | 3.0945 | 65.0024 | 64.5447 | 115.1871 | 123.7289 | 2.8564 | 123.7015 | 80.3741 | -0.29297 | 123.7289 | 2.8564 | 80.3741 | 115.1871 | 123.7015 | -123.967 | -124.0219
2417.7188 | 123.8754 | -61.3678 | 62.3474 | -0.054703 | 0.017947 | 0.017045 | 0.012106 | 0.067298 | 0.0018031 | 0.082467 | -58.5342 | 62.352 | -61.6104 | -61.528 | 53.6911 | 18.924 | 3.7079 | 3.1998 | 62.3199 | -61.6333 | -0.24262 | 0.004578 | 2.8336 | -0.16022 | -8.6563 | -0.2655 | -0.027466 | 3.0762 | 65.0757 | 64.5676 | 115.0589 | 123.7198 | 2.8336 | 123.6877 | 80.2917 | -0.2655 | 123.7198 | 2.8336 | 80.2917 | 115.0589 | 123.6877 | -123.9578 | -123.9807
2418.7188 | 123.8846 | -61.3541 | 62.3016 | 0.23521 | 0.01816 | 0.015977 | 0.01296 | 0.068579 | 0.00052127 | 0.083535 | -58.6029 | 62.3016 | -61.6287 | -61.5692 | 53.7689 | 19.1849 | 3.5431 | 3.1998 | 62.3062 | -61.6425 | -0.27466 | 0 | 2.7512 | -0.21515 | -8.5327 | -0.28839 | 0.004577 | 3.0258 | 64.8972 | 64.5538 | 115.123 | 123.6557 | 2.7512 | 123.6603 | 80.5389 | -0.28839 | 123.6557 | 2.7512 | 80.5389 | 115.123 | 123.6603 | -123.9304 | -123.9441
2419.7188 | 123.8525 | -61.3495 | 62.352 | -0.16914 | 0.019015 | 0.021317 | 0.012747 | 0.067511 | 0.0013757 | 0.087808 | -58.5297 | 62.3749 | -61.6241 | -61.6562 | 53.5583 | 18.988 | 3.5477 | 3.0945 | 62.3428 | -61.6516 | -0.27466 | 0.022888 | 2.8198 | -0.3067 | -8.7936 | -0.30212 | -0.009156 | 3.0945 | 64.8972 | 64.444 | 114.9078 | 123.7244 | 2.8198 | 123.6923 | 80.3375 | -0.30212 | 123.7244 | 2.8198 | 80.3375 | 114.9078 | 123.6923 | -123.9761 | -124.0036
2420.7188 | 123.8846 | -61.3541 | 62.3337 | -0.069961 | 0.016878 | 0.017686 | 0.015524 | 0.064734 | 0.0024439 | 0.081399 | -58.4839 | 62.3611 | -61.6104 | -61.5143 | 53.8513 | 19.1803 | 3.6026 | 3.1952 | 62.352 | -61.647 | -0.25635 | 0.027466 | 2.8702 | -0.16022 | -8.4824 | -0.29297 | 0.018311 | 3.1265 | 64.9567 | 64.5493 | 115.2054 | 123.7152 | 2.8702 | 123.7061 | 80.5344 | -0.29297 | 123.7152 | 2.8702 | 80.5344 | 115.2054 | 123.7061 | -123.9441 | -123.9807
2421.7188 | 123.8663 | -61.3403 | 62.3428 | 0.082626 | 0.019228 | 0.015977 | 0.012533 | 0.064948 | -0.00076053 | 0.079263 | -58.4518 | 62.3611 | -61.6104 | -61.5189 | 53.7964 | 19.1208 | 3.5706 | 3.1219 | 62.3428 | -61.6379 | -0.27008 | 0.018311 | 2.8885 | -0.17853 | -8.5464 | -0.29755 | 0 | 3.1586 | 64.9109 | 64.4623 | 115.1367 | 123.7015 | 2.8885 | 123.6832 | 80.4611 | -0.29755 | 123.7015 | 2.8885 | 80.4611 | 115.1367 | 123.6832 | -123.9532 | -123.9807
2422.7188 | 123.8983 | -61.3403 | 62.3474 | -0.024185 | 0.02051 | 0.020036 | 0.011679 | 0.06623 | 0.00052127 | 0.082253 | -58.4656 | 62.3199 | -61.6241 | -61.5143 | 53.833 | 19.1803 | 3.6255 | 3.1586 | 62.3428 | -61.6241 | -0.28381 | -0.027466 | 2.8748 | -0.17395 | -8.5144 | -0.28381 | -0.004578 | 3.1586 | 64.9658 | 64.4989 | 115.1733 | 123.6603 | 2.8748 | 123.6832 | 80.5206 | -0.28381 | 123.6603 | 2.8748 | 80.5206 | 115.1733 | 123.6832 | -123.9716 | -123.9716
2423.7188 | 123.8068 | -61.3632 | 62.3245 | 0.03685 | 0.017092 | 0.022599 | 0.01531 | 0.06623 | 0.0024439 | 0.082253 | -58.58 | 62.3383 | -61.6379 | -61.6013 | 53.6591 | 19.3222 | 3.6804 | 3.0624 | 62.3474 | -61.647 | -0.27466 | 0.013733 | 2.7832 | -0.23804 | -8.6655 | -0.28381 | 0.022888 | 3.0579 | 65.0436 | 64.4257 | 115.0223 | 123.7015 | 2.7832 | 123.7106 | 80.6854 | -0.28381 | 123.7015 | 2.7832 | 80.6854 | 115.0223 | 123.7106 | -123.9624 | -123.9716
2424.7188 | 123.8754 | -61.3403 | 62.3474 | -0.047073 | 0.015169 | 0.018113 | 0.012747 | 0.066443 | -0.00097413 | 0.082894 | -58.5205 | 62.3428 | -61.6104 | -61.5143 | 53.7781 | 19.5236 | 3.6118 | 3.154 | 62.3611 | -61.6379 | -0.27008 | -0.004578 | 2.8198 | -0.17395 | -8.5693 | -0.29755 | 0.013733 | 3.0899 | 64.9521 | 64.4943 | 115.1184 | 123.6832 | 2.8198 | 123.7015 | 80.864 | -0.29755 | 123.6832 | 2.8198 | 80.864 | 115.1184 | 123.7015 | -123.9578 | -123.9853
2425.7188 | 123.8754 | -61.3403 | 62.3474 | 0.62431 | 0.017092 | 0.018754 | 0.013388 | 0.066443 | 0.0024439 | 0.08439 | -58.4656 | 62.3428 | -61.6379 | -61.528 | 53.8284 | 19.4092 | 3.6118 | 3.186 | 62.3337 | -61.6287 | -0.29755 | -0.004578 | 2.8748 | -0.18768 | -8.519 | -0.28839 | -0.013733 | 3.1723 | 64.9521 | 64.5264 | 115.1688 | 123.6832 | 2.8748 | 123.674 | 80.7495 | -0.28839 | 123.6832 | 2.8748 | 80.7495 | 115.1688 | 123.674 | -123.9853 | -123.9761
2426.7188 | 123.8754 | -61.3586 | 62.3383 | -0.23018 | 0.015383 | 0.017472 | 0.01232 | 0.065161 | 0.00030767 | 0.08439 | -58.5251 | 62.352 | -61.6058 | -61.5189 | 53.9291 | 19.5282 | 3.7033 | 3.2318 | 62.3657 | -61.6333 | -0.24719 | 0.013733 | 2.8336 | -0.16022 | -8.4091 | -0.27466 | 0.027466 | 3.0808 | 65.062 | 64.5905 | 115.2878 | 123.7106 | 2.8336 | 123.7244 | 80.8868 | -0.27466 | 123.7106 | 2.8336 | 80.8868 | 115.2878 | 123.7244 | -123.9441 | -123.9716
2427.7188 | 123.9075 | -61.3312 | 62.3611 | -0.14626 | 0.017306 | 0.015977 | 0.014029 | 0.06623 | 0.0013757 | 0.083322 | -58.5297 | 62.3703 | -61.6333 | -61.5143 | 53.8925 | 19.5602 | 3.7125 | 3.2227 | 62.3474 | -61.6333 | -0.30212 | 0.009155 | 2.8015 | -0.18311 | -8.4686 | -0.30212 | -0.013733 | 3.1036 | 65.0436 | 64.5538 | 115.2237 | 123.7015 | 2.8015 | 123.6786 | 80.8914 | -0.30212 | 123.7015 | 2.8015 | 80.8914 | 115.2237 | 123.6786 | -123.9944 | -123.9944
2428.7188 | 123.8663 | -61.3449 | 62.3428 | -0.0012969 | 0.018374 | 0.019822 | 0.011038 | 0.065589 | 0.0013757 | 0.083322 | -58.5297 | 62.3566 | -61.6196 | -61.5372 | 53.9108 | 19.4778 | 3.6301 | 3.1586 | 62.3566 | -61.6516 | -0.27466 | 0.013733 | 2.8152 | -0.19226 | -8.432 | -0.3067 | 0.013733 | 3.0899 | 64.975 | 64.5035 | 115.2557 | 123.7015 | 2.8152 | 123.7015 | 80.8228 | -0.3067 | 123.7015 | 2.8152 | 80.8228 | 115.2557 | 123.7015 | -123.9624 | -123.9944
2429.7188 | 123.8663 | -61.322 | 62.3474 | -0.20729 | 0.018801 | 0.019822 | 0.012747 | 0.064521 | 0.00094847 | 0.081399 | -58.5434 | 62.3611 | -61.6333 | -61.5051 | 53.8788 | 19.4962 | 3.5889 | 3.1952 | 62.3657 | -61.6333 | -0.31128 | 0.013733 | 2.7786 | -0.18311 | -8.4686 | -0.31128 | 0.018311 | 3.0899 | 64.9109 | 64.5172 | 115.2008 | 123.6832 | 2.7786 | 123.6877 | 80.8182 | -0.31128 | 123.6832 | 2.7786 | 80.8182 | 115.2008 | 123.6877 | -123.9807 | -123.9807
2430.7188 | 123.912 | -61.3586 | 62.3428 | -0.13863 | 0.018587 | 0.014909 | 0.013174 | 0.06388 | 0.0013757 | 0.08439 | -58.5159 | 62.352 | -61.6241 | -61.5189 | 54.0161 | 19.5557 | 3.6438 | 3.4287 | 62.3611 | -61.6196 | -0.2655 | 0.009156 | 2.8427 | -0.16022 | -8.3267 | -0.26093 | 0.018311 | 3.1082 | 65.0024 | 64.7873 | 115.3748 | 123.7106 | 2.8427 | 123.7198 | 80.9143 | -0.26093 | 123.7106 | 2.8427 | 80.9143 | 115.3748 | 123.7198 | -123.967 | -123.9624
2431.7188 | 123.9075 | -61.322 | 62.3566 | -0.131 | 0.018374 | 0.016191 | 0.01296 | 0.066443 | -0.0016149 | 0.083108 | -58.5617 | 62.3474 | -61.5967 | -61.5189 | 53.9978 | 19.5648 | 3.5339 | 3.0716 | 62.3474 | -61.6241 | -0.27466 | -0.009155 | 2.7603 | -0.19684 | -8.3588 | -0.30213 | -0.009155 | 3.035 | 64.856 | 64.3936 | 115.3198 | 123.6694 | 2.7603 | 123.6694 | 80.8868 | -0.30213 | 123.6694 | 2.7603 | 80.8868 | 115.3198 | 123.6694 | -123.9532 | -123.9807
2432.7188 | 123.7701 | -61.3449 | 62.352 | -0.024185 | 0.016665 | 0.014482 | 0.014456 | 0.066657 | 9.4068e-05 | 0.081185 | -58.5388 | 62.352 | -61.615 | -61.528 | 53.8605 | 19.5602 | 3.5477 | 3.1128 | 62.3428 | -61.6241 | -0.27008 | 0 | 2.8061 | -0.18311 | -8.4915 | -0.27924 | -0.009156 | 3.0762 | 64.8926 | 64.4577 | 115.2054 | 123.6969 | 2.8061 | 123.6877 | 80.9052 | -0.27924 | 123.6969 | 2.8061 | 80.9052 | 115.2054 | 123.6877 | -123.967 | -123.9761
2433.7188 | 123.8525 | -61.3541 | 62.3062 | 0.21996 | 0.016878 | 0.020677 | 0.011892 | 0.065375 | 0.0030847 | 0.082894 | -58.6258 | 62.3154 | -61.6379 | -61.6104 | 53.8513 | 19.5419 | 3.5568 | 3.0716 | 62.3245 | -61.6562 | -0.28381 | 0.009156 | 2.7283 | -0.25635 | -8.4549 | -0.30212 | 0.018311 | 3.0121 | 64.9109 | 64.4257 | 115.2054 | 123.6694 | 2.7283 | 123.6786 | 80.896 | -0.30212 | 123.6694 | 2.7283 | 80.896 | 115.2054 | 123.6786 | -123.9441 | -123.9624
2434.7188 | 123.848 | -61.3541 | 62.3566 | -0.16151 | 0.017519 | 0.014695 | 0.011251 | 0.064521 | 0.0015893 | 0.081613 | -58.5938 | 62.3566 | -61.6196 | -61.5555 | 53.8696 | 19.5465 | 3.7262 | 3.36 | 62.3703 | -61.6379 | -0.2655 | 0 | 2.7603 | -0.20142 | -8.4869 | -0.28381 | 0.013733 | 3.0258 | 65.0803 | 64.7141 | 115.2237 | 123.7106 | 2.7603 | 123.7244 | 80.9006 | -0.28381 | 123.7106 | 2.7603 | 80.9006 | 115.2237 | 123.7244 | -123.9761 | -123.9944
2435.7188 | 123.9029 | -61.3541 | 62.3337 | -0.24544 | 0.01816 | 0.017259 | 0.011251 | 0.065589 | -0.0016149 | 0.083749 | -58.493 | 62.3749 | -61.6058 | -61.5234 | 53.9566 | 19.6976 | 3.5889 | 3.1906 | 62.3428 | -61.6516 | -0.25177 | 0.041199 | 2.861 | -0.16937 | -8.3771 | -0.29755 | 0.009155 | 3.1128 | 64.9429 | 64.5447 | 115.3107 | 123.7289 | 2.861 | 123.6969 | 81.0516 | -0.29755 | 123.7289 | 2.861 | 81.0516 | 115.3107 | 123.6969 | -123.9395 | -123.9853
2436.7188 | 123.88 | -61.3403 | 62.3474 | -0.19966 | 0.016238 | 0.020249 | 0.01296 | 0.065802 | 9.4068e-05 | 0.083322 | -58.5663 | 62.3474 | -61.6058 | -61.5143 | 53.8971 | 19.5969 | 3.6072 | 3.2043 | 62.352 | -61.6196 | -0.2655 | 0 | 2.774 | -0.17395 | -8.4503 | -0.27924 | 0.004578 | 3.0396 | 64.9475 | 64.5447 | 115.2374 | 123.6877 | 2.774 | 123.6923 | 80.9372 | -0.27924 | 123.6877 | 2.774 | 80.9372 | 115.2374 | 123.6923 | -123.9532 | -123.967
2437.7188 | 123.9304 | -61.322 | 62.3657 | -0.25307 | 0.01816 | 0.015763 | 0.013388 | 0.065802 | -0.00011953 | 0.081826 | -58.58 | 62.3428 | -61.6241 | -61.5234 | 53.8925 | 19.5831 | 3.5751 | 3.1815 | 62.384 | -61.615 | -0.30213 | -0.022889 | 2.742 | -0.20142 | -8.4732 | -0.29297 | 0.01831 | 3.0441 | 64.8972 | 64.5035 | 115.2145 | 123.6649 | 2.742 | 123.7061 | 80.9052 | -0.29297 | 123.6649 | 2.742 | 80.9052 | 115.2145 | 123.7061 | -123.9899 | -123.9807
2438.7188 | 123.8251 | -61.3541 | 62.3291 | -0.0089264 | 0.017947 | 0.020677 | 0.014456 | 0.06687 | -0.00076053 | 0.081826 | -58.5983 | 62.3428 | -61.6013 | -61.5829 | 53.8101 | 19.5831 | 3.598 | 3.2227 | 62.3383 | -61.6287 | -0.24719 | 0.013732 | 2.7557 | -0.22888 | -8.519 | -0.27466 | 0.009155 | 3.0029 | 64.9521 | 64.5767 | 115.1642 | 123.6969 | 2.7557 | 123.6923 | 80.9372 | -0.27466 | 123.6969 | 2.7557 | 80.9372 | 115.1642 | 123.6923 | -123.9304 | -123.9578
2439.7188 | 123.88 | -61.3541 | 62.3383 | -0.22255 | 0.015169 | 0.013627 | 0.012747 | 0.06687 | 9.4068e-05 | 0.081185 | -58.5571 | 62.3566 | -61.6104 | -61.5097 | 54.0024 | 19.606 | 3.5385 | 3.2455 | 62.3795 | -61.6333 | -0.25635 | 0.01831 | 2.7969 | -0.15564 | -8.3359 | -0.27924 | 0.041199 | 3.0533 | 64.8926 | 64.5996 | 115.3564 | 123.7106 | 2.7969 | 123.7335 | 80.9601 | -0.27924 | 123.7106 | 2.7969 | 80.9601 | 115.3564 | 123.7335 | -123.9487 | -123.9716
2440.7188 | 123.8617 | -61.377 | 62.3611 | -0.24544 | 0.016451 | 0.016404 | 0.011465 | 0.065161 | 0.0020167 | 0.081399 | -58.6166 | 62.352 | -61.6287 | -61.5601 | 53.833 | 19.4138 | 3.6667 | 3.3096 | 62.3749 | -61.6287 | -0.25177 | -0.009155 | 2.7603 | -0.18311 | -8.5281 | -0.25177 | 0.013733 | 3.0121 | 65.0436 | 64.6866 | 115.21 | 123.7289 | 2.7603 | 123.7518 | 80.7907 | -0.25177 | 123.7289 | 2.7603 | 80.7907 | 115.21 | 123.7518 | -123.9899 | -123.9899
2441.7188 | 123.8297 | -61.3495 | 62.384 | -0.19966 | 0.015169 | 0.016191 | 0.010397 | 0.064307 | 0.0024439 | 0.083322 | -58.6258 | 62.3749 | -61.6058 | -61.5417 | 53.7369 | 19.3634 | 3.7354 | 3.3051 | 62.3611 | -61.6287 | -0.25635 | -0.009155 | 2.7237 | -0.19226 | -8.6472 | -0.27924 | -0.022888 | 2.98 | 65.0848 | 64.6545 | 115.0864 | 123.7244 | 2.7237 | 123.7106 | 80.7129 | -0.27924 | 123.7244 | 2.7237 | 80.7129 | 115.0864 | 123.7106 | -123.9899 | -124.0128
2442.7188 | 123.88 | -61.3495 | 62.3657 | -0.26833 | 0.019228 | 0.016831 | 0.011465 | 0.065375 | 0.0013757 | 0.081613 | -58.58 | 62.3703 | -61.5967 | -61.5234 | 53.7415 | 19.4092 | 3.6209 | 3.3051 | 62.3795 | -61.6379 | -0.24719 | 0.004577 | 2.7695 | -0.17395 | -8.6243 | -0.28839 | 0.013733 | 3.0167 | 64.9704 | 64.6545 | 115.0909 | 123.7198 | 2.7695 | 123.7289 | 80.7587 | -0.28839 | 123.7198 | 2.7695 | 80.7587 | 115.0909 | 123.7289 | -123.9624 | -124.0036
2443.7188 | 123.8297 | -61.3541 | 62.3291 | 0.0063326 | 0.019015 | 0.018113 | 0.012747 | 0.065375 | -0.00033333 | 0.080972 | -58.5342 | 62.3474 | -61.6333 | -61.5738 | 53.7918 | 19.487 | 3.6621 | 3.5248 | 62.3337 | -61.6837 | -0.27924 | 0.01831 | 2.8198 | -0.21973 | -8.5373 | -0.32959 | 0.004577 | 3.0991 | 65.0162 | 64.8788 | 115.1459 | 123.7015 | 2.8198 | 123.6877 | 80.8411 | -0.32959 | 123.7015 | 2.8198 | 80.8411 | 115.1459 | 123.6877 | -123.9624 | -124.0128
2444.7188 | 123.8663 | -61.3632 | 62.3428 | -0.1844 | 0.017519 | 0.015763 | 0.010611 | 0.065589 | 0.00094847 | 0.079904 | -58.5617 | 62.3703 | -61.6241 | -61.5509 | 53.7964 | 19.5053 | 3.7033 | 3.3325 | 62.352 | -61.6287 | -0.26093 | 0.027466 | 2.8015 | -0.18768 | -8.5464 | -0.2655 | 0.009156 | 3.0624 | 65.0665 | 64.6957 | 115.1596 | 123.7335 | 2.8015 | 123.7152 | 80.8685 | -0.2655 | 123.7335 | 2.8015 | 80.8685 | 115.1596 | 123.7152 | -123.967 | -123.9716
2445.7188 | 123.8892 | -61.3586 | 62.384 | -0.19966 | 0.016024 | 0.018754 | 0.0097562 | 0.065375 | 0.00030767 | 0.082681 | -58.5663 | 62.3428 | -61.6333 | -61.5555 | 53.9886 | 19.5511 | 3.6621 | 3.2684 | 62.3703 | -61.647 | -0.27466 | -0.041199 | 2.7924 | -0.19684 | -8.3954 | -0.28839 | -0.013733 | 3.067 | 65.0208 | 64.6271 | 115.3473 | 123.7015 | 2.7924 | 123.7289 | 80.9097 | -0.28839 | 123.7015 | 2.7924 | 80.9097 | 115.3473 | 123.7289 | -124.0173 | -124.0311
2446.7188 | 123.8983 | -61.3449 | 62.384 | -0.1844 | 0.014742 | 0.015336 | 0.012533 | 0.066443 | 0.00094847 | 0.081826 | -58.5251 | 62.3383 | -61.6241 | -61.5326 | 53.9795 | 19.6106 | 3.7537 | 3.3646 | 62.3611 | -61.6333 | -0.27924 | -0.045776 | 2.8198 | -0.18768 | -8.4045 | -0.28839 | -0.022888 | 3.0991 | 65.0986 | 64.7095 | 115.3244 | 123.6832 | 2.8198 | 123.7061 | 80.9555 | -0.28839 | 123.6832 | 2.8198 | 80.9555 | 115.3244 | 123.7061 | -124.0082 | -124.0173
2447.7188 | 123.8297 | -61.3541 | 62.3749 | -1.0694 | 0.016024 | 0.016618 | 0.0093288 | 0.064521 | 0.0030847 | 0.080972 | -58.6212 | 62.3657 | -61.6196 | -61.5601 | 53.8788 | 19.4687 | 3.7262 | 3.2913 | 62.3657 | -61.647 | -0.2655 | -0.009155 | 2.7328 | -0.20599 | -8.4961 | -0.29297 | -0.009155 | 2.9984 | 65.0803 | 64.6454 | 115.2328 | 123.7198 | 2.7328 | 123.7198 | 80.8228 | -0.29297 | 123.7198 | 2.7328 | 80.8228 | 115.2328 | 123.7198 | -123.9944 | -124.0219
2448.7188 | 123.8617 | -61.3586 | 62.3474 | -0.61928 | 0.018374 | 0.018968 | 0.01531 | 0.066657 | 0.0024439 | 0.083322 | -58.4747 | 62.3245 | -61.6196 | -61.5097 | 53.6224 | 19.4366 | 3.717 | 3.4332 | 62.3337 | -61.647 | -0.26093 | -0.022888 | 2.8839 | -0.15106 | -8.725 | -0.28839 | -0.013733 | 3.1448 | 65.0757 | 64.7919 | 114.9811 | 123.6832 | 2.8839 | 123.6923 | 80.7953 | -0.28839 | 123.6832 | 2.8839 | 80.7953 | 114.9811 | 123.6923 | -123.967 | -123.9944
2449.7188 | 123.8617 | -61.3312 | 62.3566 | -0.1844 | 0.018374 | 0.015977 | 0.012106 | 0.06623 | 0.00094847 | 0.079263 | -58.5754 | 62.3474 | -61.6196 | -61.5555 | 53.5629 | 19.4321 | 3.7491 | 3.36 | 62.384 | -61.6287 | -0.28839 | -0.009155 | 2.7557 | -0.2243 | -8.7936 | -0.29755 | 0.027466 | 3.0441 | 65.0803 | 64.6912 | 114.8941 | 123.6786 | 2.7557 | 123.7152 | 80.7632 | -0.29755 | 123.6786 | 2.7557 | 80.7632 | 114.8941 | 123.7152 | -123.9761 | -123.9853
2450.7188 | 123.8571 | -61.3358 | 62.3474 | -0.1844 | 0.017092 | 0.019181 | 0.011038 | 0.065375 | 0.0013757 | 0.082894 | -58.5663 | 62.3383 | -61.6241 | -61.5417 | 53.7323 | 19.5328 | 3.7857 | 3.3783 | 62.3932 | -61.615 | -0.28839 | -0.009155 | 2.7695 | -0.20599 | -8.6151 | -0.27924 | 0.045776 | 3.0579 | 65.1215 | 64.7141 | 115.0681 | 123.674 | 2.7695 | 123.7289 | 80.8685 | -0.27924 | 123.674 | 2.7695 | 80.8685 | 115.0681 | 123.7289 | -123.9716 | -123.9624
2451.7188 | 123.8709 | -61.3495 | 62.3611 | -0.20729 | 0.018801 | 0.014482 | 0.0097562 | 0.063239 | 9.4068e-05 | 0.081185 | -58.5709 | 62.352 | -61.6104 | -61.5555 | 53.746 | 19.4733 | 3.6713 | 3.3463 | 62.3383 | -61.6333 | -0.26093 | -0.009155 | 2.7786 | -0.20599 | -8.6151 | -0.28381 | -0.022888 | 3.0396 | 65.0208 | 64.6957 | 115.0955 | 123.7015 | 2.7786 | 123.6877 | 80.8228 | -0.28381 | 123.7015 | 2.7786 | 80.8228 | 115.0955 | 123.6877 | -123.9716 | -123.9944
2452.7188 | 123.8434 | -61.3586 | 62.3749 | -0.024185 | 0.016451 | 0.015763 | 0.011251 | 0.064307 | 0.00030767 | 0.08204 | -58.5434 | 62.3291 | -61.615 | -61.5509 | 53.6728 | 19.3039 | 3.804 | 3.4332 | 62.3474 | -61.6287 | -0.25635 | -0.045776 | 2.8152 | -0.19226 | -8.7021 | -0.27008 | -0.027466 | 3.0716 | 65.1627 | 64.7919 | 115.0314 | 123.6877 | 2.8152 | 123.7061 | 80.6625 | -0.27008 | 123.6877 | 2.8152 | 80.6625 | 115.0314 | 123.7061 | -123.9899 | -124.0036
2453.7188 | 123.793 | -61.377 | 62.3383 | 0.12077 | 0.019656 | 0.015763 | 0.01232 | 0.06623 | 0.0015893 | 0.083108 | -58.6075 | 62.3337 | -61.6287 | -61.6013 | 53.5034 | 19.3085 | 3.1906 | 3.2455 | 62.2559 | -61.6791 | -0.25177 | -0.004578 | 2.7695 | -0.2243 | -8.8348 | -0.30212 | -0.082398 | 3.0212 | 64.5676 | 64.6225 | 114.8804 | 123.7106 | 2.7695 | 123.6328 | 80.6854 | -0.30212 | 123.7106 | 2.7695 | 80.6854 | 114.8804 | 123.6328 | -123.967 | -124.0173
2454.7188 | 123.8388 | -61.3495 | 62.3566 | -0.42854 | 0.017733 | 0.014268 | 0.0089016 | 0.061316 | -0.00011953 | 0.081185 | -58.7082 | 62.3428 | -61.6287 | -61.5692 | 53.6316 | 19.2627 | 3.717 | 3.4058 | 62.3795 | -61.647 | -0.27924 | -0.013733 | 2.6413 | -0.21973 | -8.725 | -0.29755 | 0.022889 | 2.9205 | 65.0665 | 64.7552 | 114.9811 | 123.6923 | 2.6413 | 123.7289 | 80.6122 | -0.29755 | 123.6923 | 2.6413 | 80.6122 | 114.9811 | 123.7289 | -123.9853 | -124.0036
2455.7188 | 123.8434 | -61.3449 | 62.3611 | -0.19966 | 0.015383 | 0.0078592 | 0.010611 | 0.064734 | 0.00030767 | 0.081185 | -58.5526 | 62.3428 | -61.5829 | -61.5967 | 53.6087 | 19.2764 | 3.6667 | 3.392 | 62.352 | -61.6379 | -0.23804 | -0.018311 | 2.7924 | -0.25177 | -8.7524 | -0.29297 | -0.009155 | 3.0304 | 65.0116 | 64.7369 | 114.9536 | 123.6877 | 2.7924 | 123.6969 | 80.6213 | -0.29297 | 123.6877 | 2.7924 | 80.6213 | 114.9536 | 123.6969 | -123.9441 | -123.999
2456.7188 | 123.8617 | -61.3403 | 62.3749 | -0.16151 | 0.013888 | 0.01555 | 0.014456 | 0.062812 | 0.0015893 | 0.080117 | -58.5434 | 62.352 | -61.6058 | -61.5463 | 53.6133 | 19.2947 | 3.8132 | 3.4836 | 62.3611 | -61.6333 | -0.2655 | -0.022888 | 2.7969 | -0.20599 | -8.7616 | -0.29297 | -0.013733 | 3.0624 | 65.1535 | 64.8239 | 114.9536 | 123.6923 | 2.7969 | 123.7015 | 80.6351 | -0.29297 | 123.6923 | 2.7969 | 80.6351 | 114.9536 | 123.7015 | -123.9807 | -124.0082
2457.7188 | 123.8434 | -61.3312 | 62.3611 | -0.21492 | 0.016238 | 0.018754 | 0.012533 | 0.064093 | 0.0018031 | 0.081613 | -58.5663 | 62.3428 | -61.5967 | -61.5463 | 53.6682 | 19.4778 | 3.8589 | 3.5156 | 62.352 | -61.6241 | -0.2655 | -0.018311 | 2.7649 | -0.21515 | -8.6929 | -0.29297 | -0.009155 | 3.0304 | 65.1901 | 64.8468 | 114.9994 | 123.674 | 2.7649 | 123.6832 | 80.809 | -0.29297 | 123.674 | 2.7649 | 80.809 | 114.9994 | 123.6832 | -123.9578 | -123.9853
2458.7188 | 123.8617 | -61.3724 | 62.352 | -0.19203 | 0.015597 | 0.020249 | 0.01296 | 0.065375 | -0.00011953 | 0.082253 | -58.5663 | 62.3474 | -61.6104 | -61.5555 | 53.7415 | 19.4916 | 4.1794 | 3.7125 | 62.352 | -61.6379 | -0.23804 | -0.004578 | 2.8061 | -0.18311 | -8.6105 | -0.2655 | 0 | 3.0441 | 65.5518 | 65.0848 | 115.1138 | 123.7198 | 2.8061 | 123.7244 | 80.864 | -0.2655 | 123.7198 | 2.8061 | 80.864 | 115.1138 | 123.7244 | -123.9624 | -123.9899
2459.7188 | 123.8571 | -61.3449 | 62.3932 | -0.19966 | 0.016878 | 0.014695 | 0.01531 | 0.06388 | -0.00033333 | 0.081613 | -58.5342 | 62.3474 | -61.6241 | -61.5417 | 53.5675 | 19.3726 | 4.1199 | 3.5934 | 62.3428 | -61.6287 | -0.27924 | -0.045776 | 2.8107 | -0.19684 | -8.8257 | -0.28381 | -0.050354 | 3.0899 | 65.4648 | 64.9384 | 114.9124 | 123.6923 | 2.8107 | 123.6877 | 80.7175 | -0.28381 | 123.6923 | 2.8107 | 80.7175 | 114.9124 | 123.6877 | -124.0173 | -124.0219
2460.7188 | 123.8846 | -61.3541 | 62.3566 | -0.19966 | 0.016451 | 0.017472 | 0.014669 | 0.065161 | 0.0022303 | 0.081826 | -58.5434 | 62.3566 | -61.6333 | -61.5005 | 53.5492 | 19.5236 | 4.1656 | 3.6484 | 62.3474 | -61.647 | -0.27924 | 0 | 2.8107 | -0.14648 | -8.8074 | -0.29297 | -0.009155 | 3.0899 | 65.5197 | 65.0024 | 114.9033 | 123.7106 | 2.8107 | 123.7015 | 80.8777 | -0.29297 | 123.7106 | 2.8107 | 80.8777 | 114.9033 | 123.7015 | -123.9899 | -124.0036
2461.7188 | 123.848 | -61.3403 | 62.3657 | -0.38277 | 0.016451 | 0.017899 | 0.010183 | 0.063025 | 0.0018031 | 0.080758 | -58.58 | 62.384 | -61.6241 | -61.5738 | 53.5538 | 19.4229 | 4.0878 | 3.5843 | 62.3337 | -61.6241 | -0.28381 | 0.01831 | 2.7603 | -0.23346 | -8.812 | -0.28381 | -0.032044 | 3.0441 | 65.4282 | 64.9246 | 114.8941 | 123.7244 | 2.7603 | 123.674 | 80.7632 | -0.28381 | 123.7244 | 2.7603 | 80.7632 | 114.8941 | 123.674 | -123.9899 | -123.9899
2462.7188 | 123.8342 | -61.3586 | 62.3932 | -0.38277 | 0.016451 | 0.019822 | 0.011892 | 0.063025 | 0.00073487 | 0.081185 | -58.5754 | 62.3703 | -61.6516 | -61.5555 | 53.6179 | 19.487 | 4.0833 | 3.5797 | 62.3474 | -61.6516 | -0.29297 | -0.022888 | 2.7832 | -0.19684 | -8.7753 | -0.29297 | -0.045776 | 3.0762 | 65.4419 | 64.9384 | 114.9765 | 123.7289 | 2.7832 | 123.7061 | 80.8456 | -0.29297 | 123.7289 | 2.7832 | 80.8456 | 114.9765 | 123.7061 | -124.0448 | -124.0448
2463.7188 | 123.8388 | -61.3861 | 62.3291 | 0.04448 | 0.016024 | 0.014909 | 0.014883 | 0.064521 | -0.00011953 | 0.083108 | -58.5297 | 62.3428 | -61.6241 | -61.5692 | 53.5675 | 19.3954 | 4.1382 | 3.5477 | 62.3245 | -61.6425 | -0.23804 | 0.013732 | 2.8564 | -0.18311 | -8.7616 | -0.25635 | -0.004578 | 3.0945 | 65.5243 | 64.9338 | 114.9536 | 123.7289 | 2.8564 | 123.7106 | 80.7816 | -0.25635 | 123.7289 | 2.8564 | 80.7816 | 114.9536 | 123.7106 | -123.9532 | -123.9716
2464.7188 | 123.8617 | -61.3449 | 62.3703 | -0.20729 | 0.017092 | 0.019181 | 0.013815 | 0.06687 | -0.00076053 | 0.08204 | -58.5617 | 62.3383 | -61.6241 | -61.528 | 53.5812 | 19.4458 | 4.0512 | 3.566 | 62.3703 | -61.6196 | -0.27924 | -0.032043 | 2.7832 | -0.18311 | -8.7891 | -0.27466 | 0 | 3.0624 | 65.3961 | 64.9109 | 114.9261 | 123.6832 | 2.7832 | 123.7152 | 80.7907 | -0.27466 | 123.6832 | 2.7832 | 80.7907 | 114.9261 | 123.7152 | -123.9944 | -123.9899
2465.7188 | 123.8571 | -61.3312 | 62.352 | -0.19203 | 0.017733 | 0.019181 | 0.012533 | 0.065589 | 0.00094847 | 0.080544 | -58.5709 | 62.3428 | -61.6241 | -61.5417 | 53.5538 | 19.3863 | 4.0649 | 3.4836 | 62.3566 | -61.6241 | -0.29297 | -0.009156 | 2.7603 | -0.21057 | -8.7982 | -0.29297 | 0.004577 | 3.0533 | 65.3961 | 64.8148 | 114.8849 | 123.674 | 2.7603 | 123.6877 | 80.7175 | -0.29297 | 123.674 | 2.7603 | 80.7175 | 114.8849 | 123.6877 | -123.9761 | -123.9761
2466.7188 | 123.8663 | -61.3449 | 62.3474 | -0.1844 | 0.017306 | 0.017472 | 0.013601 | 0.064948 | -0.00076053 | 0.080758 | -58.5297 | 62.3611 | -61.6104 | -61.5143 | 53.5217 | 19.455 | 4.1107 | 3.598 | 62.3199 | -61.6196 | -0.2655 | 0.013733 | 2.8152 | -0.16937 | -8.8257 | -0.27466 | -0.027466 | 3.0808 | 65.4556 | 64.9429 | 114.8666 | 123.7061 | 2.8152 | 123.6649 | 80.7999 | -0.27466 | 123.7061 | 2.8152 | 80.7999 | 114.8666 | 123.6649 | -123.9578 | -123.967
2467.7188 | 123.88 | -61.3541 | 62.3383 | -0.131 | 0.017092 | 0.012986 | 0.015524 | 0.06687 | 0.00094847 | 0.081185 | -58.4885 | 62.3383 | -61.6104 | -61.496 | 53.5767 | 19.455 | 4.0237 | 3.6667 | 62.3245 | -61.647 | -0.25635 | 0 | 2.8656 | -0.14191 | -8.7616 | -0.29297 | -0.013733 | 3.1219 | 65.3778 | 65.0208 | 114.9307 | 123.6923 | 2.8656 | 123.6786 | 80.809 | -0.29297 | 123.6923 | 2.8656 | 80.809 | 114.9307 | 123.6786 | -123.9487 | -123.9853
2468.7188 | 123.8342 | -61.4044 | 62.3199 | 0.04448 | 0.017519 | 0.015336 | 0.013815 | 0.065802 | 0.0015893 | 0.082467 | -58.5617 | 62.3428 | -61.6562 | -61.5921 | 53.833 | 19.3771 | 3.9551 | 3.5614 | 62.352 | -61.6562 | -0.25177 | 0.022888 | 2.8427 | -0.18768 | -8.4869 | -0.25177 | 0.032044 | 3.0945 | 65.3595 | 64.9658 | 115.2374 | 123.7473 | 2.8427 | 123.7564 | 80.7816 | -0.25177 | 123.7473 | 2.8427 | 80.7816 | 115.2374 | 123.7564 | -123.9761 | -123.9761
2469.7344 | 123.9532 | -61.3403 | 62.2925 | 0.21996 | 0.016665 | 0.016831 | 0.0099698 | 0.068152 | 0.00052127 | 0.083749 | -58.5342 | 62.2467 | -61.6287 | -61.5189 | 53.8193 | 19.5969 | 3.9734 | 3.7811 | 62.265 | -61.6104 | -0.28839 | -0.045776 | 2.8061 | -0.17853 | -8.4732 | -0.27008 | -0.027465 | 3.0945 | 65.3137 | 65.1215 | 115.1596 | 123.587 | 2.8061 | 123.6053 | 80.9372 | -0.27008 | 123.587 | 2.8061 | 80.9372 | 115.1596 | 123.6053 | -123.9212 | -123.9029
2470.7188 | 123.7656 | -61.3541 | 62.2971 | -0.10811 | 0.019656 | 0.01555 | 0.01296 | 0.065375 | 9.4068e-05 | 0.083108 | -58.5251 | 62.3108 | -61.5921 | -61.5143 | 53.8422 | 19.4916 | 4.0146 | 3.7216 | 62.3428 | -61.6699 | -0.23804 | 0.013733 | 2.829 | -0.16022 | -8.4549 | -0.31586 | 0.045776 | 3.067 | 65.3687 | 65.0757 | 115.1962 | 123.6649 | 2.829 | 123.6969 | 80.8456 | -0.31586 | 123.6649 | 2.829 | 80.8456 | 115.1962 | 123.6969 | -123.8892 | -123.967
2471.7188 | 123.8892 | -61.3495 | 62.3154 | -0.10811 | 0.018587 | 0.014268 | 0.011251 | 0.066657 | 0.0037257 | 0.082253 | -58.5068 | 62.3199 | -61.6379 | -61.5143 | 53.6682 | 19.4092 | 4.0375 | 3.7216 | 62.3108 | -61.6425 | -0.28839 | 0.004577 | 2.8427 | -0.16479 | -8.6472 | -0.29297 | -0.004578 | 3.1311 | 65.387 | 65.0711 | 115.0177 | 123.6694 | 2.8427 | 123.6603 | 80.7587 | -0.29297 | 123.6694 | 2.8427 | 80.7587 | 115.0177 | 123.6603 | -123.9532 | -123.9578
2472.7188 | 123.848 | -61.3358 | 62.3383 | -0.09285 | 0.01581 | 0.017472 | 0.012533 | 0.066443 | 9.4068e-05 | 0.084176 | -58.5251 | 62.3474 | -61.5967 | -61.5143 | 53.7506 | 19.4733 | 4.1199 | 3.7582 | 62.3108 | -61.647 | -0.26093 | 0.009155 | 2.8107 | -0.17853 | -8.5876 | -0.31128 | -0.027466 | 3.0716 | 65.4556 | 65.094 | 115.0864 | 123.6832 | 2.8107 | 123.6465 | 80.809 | -0.31128 | 123.6832 | 2.8107 | 80.809 | 115.0864 | 123.6465 | -123.9349 | -123.9853
2473.7188 | 123.848 | -61.3815 | 62.3337 | 0.0063326 | 0.016665 | 0.019822 | 0.014242 | 0.06623 | 0.00073487 | 0.081613 | -58.5754 | 62.3291 | -61.6425 | -61.5646 | 53.7048 | 19.5236 | 4.1656 | 3.7445 | 62.3337 | -61.6425 | -0.26093 | -0.004577 | 2.8061 | -0.1831 | -8.6288 | -0.26093 | 0 | 3.067 | 65.5472 | 65.126 | 115.0864 | 123.7106 | 2.8061 | 123.7152 | 80.9052 | -0.26093 | 123.7106 | 2.8061 | 80.9052 | 115.0864 | 123.7152 | -123.9761 | -123.9761
2474.7344 | 123.8846 | -61.3449 | 62.2879 | -0.062332 | 0.014101 | 0.01555 | 0.0031338 | 0.064734 | -0.00054693 | 0.082894 | -58.6121 | 62.233 | -61.6333 | -61.528 | 54.0482 | 19.7754 | 3.8361 | 3.8269 | 62.3154 | -61.5967 | -0.28839 | -0.054932 | 2.7328 | -0.18311 | -8.2397 | -0.25177 | 0.027466 | 3.0212 | 65.181 | 65.1718 | 115.3931 | 123.5779 | 2.7328 | 123.6603 | 81.1203 | -0.25177 | 123.5779 | 2.7328 | 81.1203 | 115.3931 | 123.6603 | -123.9212 | -123.8846
2475.7188 | 123.848 | -61.3724 | 62.3428 | -0.16151 | 0.017733 | 0.014054 | 0.014242 | 0.064307 | 0.00073487 | 0.083322 | -58.5617 | 62.3428 | -61.6241 | -61.5555 | 53.7094 | 19.4641 | 4.1199 | 3.6987 | 62.3245 | -61.647 | -0.25177 | 0 | 2.8107 | -0.18311 | -8.6334 | -0.27466 | -0.01831 | 3.0624 | 65.4922 | 65.0711 | 115.0818 | 123.7152 | 2.8107 | 123.6969 | 80.8365 | -0.27466 | 123.7152 | 2.8107 | 80.8365 | 115.0818 | 123.6969 | -123.967 | -123.9899
2476.7188 | 123.8388 | -61.3678 | 62.3474 | -0.14626 | 0.014956 | 0.016404 | 0.011892 | 0.06388 | -0.00011953 | 0.082467 | -58.58 | 62.3703 | -61.6013 | -61.5646 | 53.7094 | 19.5053 | 4.303 | 3.7765 | 62.3657 | -61.6241 | -0.23346 | 0.022888 | 2.7878 | -0.19684 | -8.638 | -0.25635 | 0.018311 | 3.0212 | 65.6708 | 65.1443 | 115.0772 | 123.7381 | 2.7878 | 123.7335 | 80.8731 | -0.25635 | 123.7381 | 2.7878 | 80.8731 | 115.0772 | 123.7335 | -123.9487 | -123.9716
2477.7188 | 123.8754 | -61.3632 | 62.3383 | -0.23781 | 0.018374 | 0.015763 | 0.013815 | 0.064521 | 0.0043665 | 0.079904 | -58.5251 | 62.3566 | -61.6196 | -61.5234 | 53.8239 | 19.5648 | 4.248 | 3.8589 | 62.3428 | -61.6608 | -0.25635 | 0.01831 | 2.8381 | -0.16022 | -8.5144 | -0.29755 | 0.004577 | 3.0945 | 65.6113 | 65.2222 | 115.1871 | 123.7198 | 2.8381 | 123.7061 | 80.928 | -0.29755 | 123.7198 | 2.8381 | 80.928 | 115.1871 | 123.7061 | -123.9578 | -123.999
2478.7188 | 123.8297 | -61.3541 | 62.352 | 0.14366 | 0.022005 | 0.019395 | 0.012106 | 0.062812 | 0.0018031 | 0.084603 | -58.5709 | 62.3291 | -61.6745 | -61.6241 | 53.7735 | 19.5145 | 4.0512 | 3.6942 | 62.3337 | -61.6562 | -0.32044 | -0.022888 | 2.7832 | -0.27008 | -8.5785 | -0.30212 | -0.018311 | 3.1036 | 65.4053 | 65.0482 | 115.1276 | 123.6832 | 2.7832 | 123.6877 | 80.8685 | -0.30212 | 123.6832 | 2.7832 | 80.8685 | 115.1276 | 123.6877 | -124.0265 | -124.0082
2479.7344 | 123.9716 | -61.3358 | 62.2559 | 0.2047 | 0.016024 | 0.017045 | 0.01232 | 0.064093 | 0.0020167 | 0.083322 | -58.5342 | 62.265 | -61.6333 | -61.528 | 53.7369 | 19.519 | 4.1473 | 3.891 | 62.2742 | -61.6196 | -0.29755 | 0.009156 | 2.8015 | -0.19226 | -8.519 | -0.28381 | 0.018311 | 3.0991 | 65.4831 | 65.2267 | 115.0726 | 123.6008 | 2.8015 | 123.6099 | 80.8548 | -0.28381 | 123.6008 | 2.8015 | 80.8548 | 115.0726 | 123.6099 | -123.8892 | -123.8754
2480.7188 | 123.8846 | -61.3586 | 62.3383 | -0.2607 | 0.016878 | 0.014695 | 0.01232 | 0.066016 | 0.00052127 | 0.081399 | -58.5571 | 62.3428 | -61.6425 | -61.528 | 53.7506 | 19.5374 | 4.3671 | 3.8956 | 62.3474 | -61.647 | -0.28381 | 0.004577 | 2.8015 | -0.16937 | -8.5876 | -0.28839 | 0.009155 | 3.0853 | 65.7257 | 65.2542 | 115.1093 | 123.7015 | 2.8015 | 123.7061 | 80.896 | -0.28839 | 123.7015 | 2.8015 | 80.896 | 115.1093 | 123.7061 | -123.9807 | -123.9853
2481.7188 | 123.8846 | -61.3541 | 62.3108 | -0.10048 | 0.017092 | 0.02089 | 0.013601 | 0.064521 | 0.0011621 | 0.080758 | -58.5022 | 62.3703 | -61.615 | -61.5189 | 53.7415 | 19.5923 | 4.3167 | 3.8589 | 62.3474 | -61.6516 | -0.26093 | 0.059509 | 2.8519 | -0.16479 | -8.5693 | -0.29755 | 0.036621 | 3.1128 | 65.6708 | 65.213 | 115.0955 | 123.7244 | 2.8519 | 123.7015 | 80.9463 | -0.29755 | 123.7244 | 2.8519 | 80.9463 | 115.0955 | 123.7015 | -123.9258 | -123.9624
2482.7188 | 123.8709 | -61.3586 | 62.3657 | -0.14626 | 0.016878 | 0.015977 | 0.013815 | 0.06388 | 0.0018031 | 0.080331 | -58.58 | 62.3611 | -61.6241 | -61.5509 | 53.6865 | 19.5099 | 4.4907 | 3.9001 | 62.3337 | -61.6287 | -0.2655 | -0.004578 | 2.7786 | -0.19226 | -8.6792 | -0.27008 | -0.032044 | 3.0441 | 65.8493 | 65.2588 | 115.0452 | 123.7198 | 2.7786 | 123.6923 | 80.8685 | -0.27008 | 123.7198 | 2.7786 | 80.8685 | 115.0452 | 123.6923 | -123.9899 | -123.9944
2483.7188 | 123.8113 | -61.3861 | 62.3383 | 0.082626 | 0.017092 | 0.02089 | 0.013815 | 0.06388 | 0.0024439 | 0.083108 | -58.6075 | 62.3291 | -61.6562 | -61.6058 | 53.5812 | 19.3771 | 4.3213 | 3.7628 | 62.3291 | -61.6699 | -0.27008 | -0.009155 | 2.7786 | -0.21973 | -8.757 | -0.28381 | -0.009155 | 3.0487 | 65.7074 | 65.1489 | 114.9673 | 123.7152 | 2.7786 | 123.7152 | 80.7632 | -0.28381 | 123.7152 | 2.7786 | 80.7632 | 114.9673 | 123.7152 | -123.9944 | -124.0082
2484.7188 | 123.88 | -61.3815 | 62.3016 | 0.13603 | 0.016665 | 0.016831 | 0.011465 | 0.064948 | 0.0013757 | 0.083322 | -58.6121 | 62.3016 | -61.6699 | -61.5875 | 53.3524 | 19.3588 | 4.3579 | 3.923 | 62.2879 | -61.647 | -0.28839 | 0 | 2.7695 | -0.20599 | -8.9493 | -0.2655 | -0.013733 | 3.0579 | 65.7394 | 65.3046 | 114.7339 | 123.6832 | 2.7695 | 123.6694 | 80.7404 | -0.2655 | 123.6832 | 2.7695 | 80.7404 | 114.7339 | 123.6694 | -123.9716 | -123.9487
2485.7188 | 123.8754 | -61.3724 | 62.3291 | -0.16914 | 0.01581 | 0.016404 | 0.012747 | 0.065589 | 0.0020167 | 0.082681 | -58.5709 | 62.3245 | -61.6196 | -61.5189 | 53.6453 | 19.4595 | 4.3671 | 3.9276 | 62.3428 | -61.6608 | -0.24719 | -0.004578 | 2.8015 | -0.14648 | -8.6838 | -0.28839 | 0.013732 | 3.0487 | 65.7394 | 65.3 | 115.0177 | 123.6969 | 2.8015 | 123.7152 | 80.8319 | -0.28839 | 123.6969 | 2.8015 | 80.8319 | 115.0177 | 123.7152 | -123.9487 | -123.9899
2486.7188 | 123.8663 | -61.3586 | 62.352 | -0.13863 | 0.016878 | 0.017899 | 0.011465 | 0.064521 | 0.0028711 | 0.083962 | -58.5526 | 62.3474 | -61.6241 | -61.5234 | 53.4576 | 19.5282 | 4.4998 | 3.9917 | 62.3566 | -61.6379 | -0.2655 | -0.004578 | 2.8061 | -0.16479 | -8.8943 | -0.27923 | 0.004577 | 3.0716 | 65.8585 | 65.3503 | 114.8163 | 123.7061 | 2.8061 | 123.7152 | 80.8868 | -0.27923 | 123.7061 | 2.8061 | 80.8868 | 114.8163 | 123.7152 | -123.9761 | -123.9899
2487.7188 | 123.8617 | -61.3632 | 62.3337 | -0.21492 | 0.017519 | 0.014695 | 0.013601 | 0.065375 | 0.00052127 | 0.081613 | -58.5297 | 62.3428 | -61.6058 | -61.528 | 53.4348 | 19.5282 | 4.3854 | 3.9047 | 62.3428 | -61.6013 | -0.24262 | 0.009155 | 2.8336 | -0.1648 | -8.8989 | -0.23804 | 0.009155 | 3.0762 | 65.7486 | 65.2679 | 114.798 | 123.7061 | 2.8336 | 123.7061 | 80.8914 | -0.23804 | 123.7061 | 2.8336 | 80.8914 | 114.798 | 123.7061 | -123.9395 | -123.9349
2488.7188 | 123.8113 | -61.3815 | 62.3291 | 0.10551 | 0.018374 | 0.019395 | 0.01531 | 0.066657 | 0.00094847 | 0.081826 | -58.5983 | 62.3657 | -61.6608 | -61.6287 | 53.4668 | 19.4733 | 4.4083 | 3.7949 | 62.3383 | -61.647 | -0.27924 | 0.036621 | 2.7832 | -0.24719 | -8.8623 | -0.2655 | 0.009155 | 3.0624 | 65.7898 | 65.1764 | 114.8483 | 123.7473 | 2.7832 | 123.7198 | 80.8548 | -0.2655 | 123.7473 | 2.7832 | 80.8548 | 114.8483 | 123.7198 | -123.9899 | -123.9761
2489.7188 | 123.8709 | -61.3586 | 62.3566 | -0.20729 | 0.017733 | 0.014909 | 0.010183 | 0.066016 | 0.00052127 | 0.083535 | -58.5663 | 62.3428 | -61.6241 | -61.5601 | 53.4393 | 19.4778 | 4.4769 | 3.9093 | 62.3657 | -61.6379 | -0.2655 | -0.013733 | 2.7924 | -0.20142 | -8.9172 | -0.27923 | 0.009156 | 3.0579 | 65.8356 | 65.2679 | 114.798 | 123.7015 | 2.7924 | 123.7244 | 80.8365 | -0.27923 | 123.7015 | 2.7924 | 80.8365 | 114.798 | 123.7244 | -123.9807 | -123.9944
2490.7188 | 123.848 | -61.3449 | 62.3611 | -0.22255 | 0.015597 | 0.016191 | 0.011679 | 0.065589 | 9.4068e-05 | 0.082681 | -58.5205 | 62.352 | -61.6241 | -61.5555 | 53.6636 | 19.5465 | 4.4449 | 3.9322 | 62.352 | -61.6608 | -0.27924 | -0.009155 | 2.8244 | -0.21057 | -8.6975 | -0.31586 | -0.009155 | 3.1036 | 65.7898 | 65.2771 | 115.0085 | 123.6969 | 2.8244 | 123.6969 | 80.8914 | -0.31586 | 123.6969 | 2.8244 | 80.8914 | 115.0085 | 123.6969 | -123.9853 | -124.0219
2491.7188 | 123.8709 | -61.3266 | 62.3428 | -0.13863 | 0.017733 | 0.01555 | 0.014669 | 0.064307 | 0.0015893 | 0.079476 | -58.5434 | 62.352 | -61.6241 | -61.5189 | 53.5904 | 19.4778 | 4.3625 | 3.8864 | 62.352 | -61.6608 | -0.29755 | 0.009156 | 2.7832 | -0.19226 | -8.7524 | -0.33417 | 0.009156 | 3.0808 | 65.6891 | 65.213 | 114.917 | 123.6786 | 2.7832 | 123.6786 | 80.8044 | -0.33417 | 123.6786 | 2.7832 | 80.8044 | 114.917 | 123.6786 | -123.967 | -124.0036
2492.7188 | 123.8754 | -61.3449 | 62.3474 | -0.13863 | 0.016024 | 0.014695 | 0.013174 | 0.06623 | 0.0020167 | 0.080544 | -58.3557 | 62.3566 | -61.6196 | -61.528 | 53.6224 | 19.5648 | 4.3076 | 3.8773 | 62.3428 | -61.6196 | -0.27466 | 0.009155 | 2.9892 | -0.18311 | -8.725 | -0.27466 | -0.004578 | 3.2639 | 65.6525 | 65.2222 | 114.9673 | 123.7015 | 2.9892 | 123.6877 | 80.9097 | -0.27466 | 123.7015 | 2.9892 | 80.9097 | 114.9673 | 123.6877 | -123.967 | -123.967
2493.7188 | 123.8937 | -61.3724 | 62.3199 | 0.1284 | 0.017733 | 0.017472 | 0.014456 | 0.066016 | 0.0026575 | 0.087808 | -58.6304 | 62.3291 | -61.6653 | -61.8347 | 53.2745 | 19.3771 | 4.5685 | 3.6804 | 62.3154 | -61.6653 | -0.29297 | 0.009156 | 2.742 | -0.46234 | -9.0454 | -0.29297 | -0.004577 | 3.035 | 65.9409 | 65.0528 | 114.6469 | 123.7015 | 2.742 | 123.6877 | 80.7495 | -0.29297 | 123.7015 | 2.742 | 80.7495 | 114.6469 | 123.6877 | -123.9853 | -123.9853
2494.7188 | 123.8754 | -61.3724 | 62.3199 | -0.047073 | 0.018801 | 0.016404 | 0.013174 | 0.066443 | 0.00030767 | 0.081399 | -58.5159 | 62.3245 | -61.6379 | -61.5234 | 53.8055 | 19.5831 | 4.2938 | 3.9047 | 62.3383 | -61.6562 | -0.2655 | 0.004578 | 2.8564 | -0.15106 | -8.5144 | -0.28381 | 0.018311 | 3.1219 | 65.6662 | 65.2771 | 115.1779 | 123.6969 | 2.8564 | 123.7106 | 80.9555 | -0.28381 | 123.6969 | 2.8564 | 80.9555 | 115.1779 | 123.7106 | -123.9578 | -123.9761
2495.7188 | 123.8388 | -61.3632 | 62.3016 | -0.131 | 0.018801 | 0.017686 | 0.015097 | 0.065161 | 0.0011621 | 0.082894 | -58.5205 | 62.3749 | -61.6287 | -61.528 | 53.9017 | 19.5786 | 4.2801 | 3.9047 | 62.3062 | -61.6699 | -0.2655 | 0.073242 | 2.8427 | -0.1648 | -8.4 | -0.3067 | 0.004577 | 3.1082 | 65.6433 | 65.2679 | 115.2649 | 123.7381 | 2.8427 | 123.6694 | 80.9418 | -0.3067 | 123.7381 | 2.8427 | 80.9418 | 115.2649 | 123.6694 | -123.9304 | -123.9716
2496.7188 | 123.8617 | -61.377 | 62.3657 | -0.17677 | 0.017306 | 0.014695 | 0.010183 | 0.06623 | 0.0015893 | 0.081613 | -58.4656 | 62.3428 | -61.6287 | -61.5463 | 53.8239 | 19.5694 | 4.3945 | 3.9413 | 62.3474 | -61.6699 | -0.25177 | -0.022889 | 2.9114 | -0.16937 | -8.5419 | -0.29297 | -0.018311 | 3.1631 | 65.7715 | 65.3183 | 115.2008 | 123.7198 | 2.9114 | 123.7244 | 80.9463 | -0.29297 | 123.7198 | 2.9114 | 80.9463 | 115.2008 | 123.7244 | -123.9944 | -124.0356
2497.7188 | 123.88 | -61.3495 | 62.3337 | -0.23018 | 0.016451 | 0.014909 | 0.01232 | 0.066443 | 0.0013757 | 0.082681 | -58.5159 | 62.3291 | -61.6608 | -61.528 | 53.8513 | 19.606 | 4.2664 | 3.8956 | 62.3245 | -61.6562 | -0.31128 | -0.004577 | 2.8336 | -0.17853 | -8.4824 | -0.3067 | -0.009155 | 3.1448 | 65.6158 | 65.2451 | 115.2008 | 123.6786 | 2.8336 | 123.674 | 80.9555 | -0.3067 | 123.6786 | 2.8336 | 80.9555 | 115.2008 | 123.674 | -123.9944 | -123.9899
2498.7188 | 123.8709 | -61.3632 | 62.3291 | -0.062332 | 0.017306 | 0.02089 | 0.015097 | 0.067725 | -0.0020421 | 0.080758 | -58.5068 | 62.3383 | -61.6196 | -61.409 | 53.3432 | 19.3405 | 4.3259 | 3.8864 | 62.352 | -61.6241 | -0.25635 | 0.009155 | 2.8564 | -0.045777 | -8.9859 | -0.26093 | 0.022888 | 3.1128 | 65.6891 | 65.2496 | 114.7064 | 123.7015 | 2.8564 | 123.7152 | 80.7037 | -0.26093 | 123.7015 | 2.8564 | 80.7037 | 114.7064 | 123.7152 | -123.9487 | -123.9532
2499.7188 | 123.8937 | -61.3541 | 62.3245 | -0.131 | 0.014956 | 0.020463 | 0.01232 | 0.06687 | 0.00052127 | 0.081613 | -58.5205 | 62.3245 | -61.6379 | -61.5417 | 53.9017 | 19.6518 | 4.4678 | 4.01 | 62.3337 | -61.6333 | -0.28381 | 0 | 2.8336 | -0.18768 | -8.4229 | -0.27924 | 0.009155 | 3.1174 | 65.8218 | 65.3641 | 115.2557 | 123.6786 | 2.8336 | 123.6877 | 81.0059 | -0.27924 | 123.6786 | 2.8336 | 81.0059 | 115.2557 | 123.6877 | -123.9624 | -123.9578
2500.7188 | 123.8663 | -61.3678 | 62.3108 | -0.131 | 0.017519 | 0.021531 | 0.011892 | 0.067084 | 0.00030767 | 0.083535 | -58.5251 | 62.352 | -61.6104 | -61.5417 | 53.801 | 19.6655 | 4.4907 | 4.0375 | 62.3474 | -61.6608 | -0.24262 | 0.041199 | 2.8427 | -0.17395 | -8.5098 | -0.29297 | 0.036621 | 3.0853 | 65.8585 | 65.4053 | 115.1688 | 123.7198 | 2.8427 | 123.7152 | 81.0333 | -0.29297 | 123.7198 | 2.8427 | 81.0333 | 115.1688 | 123.7152 | -123.9212 | -123.9716
2501.7188 | 123.8754 | -61.3632 | 62.3245 | -0.09285 | 0.016878 | 0.018327 | 0.012747 | 0.066016 | 9.4068e-05 | 0.082253 | -58.5022 | 62.3245 | -61.6333 | -61.5326 | 53.6774 | 19.5145 | 4.3259 | 4.0146 | 62.3383 | -61.647 | -0.27008 | 0 | 2.861 | -0.16937 | -8.6472 | -0.28381 | 0.013733 | 3.1311 | 65.6891 | 65.3778 | 115.0406 | 123.6877 | 2.861 | 123.7015 | 80.8777 | -0.28381 | 123.6877 | 2.861 | 80.8777 | 115.0406 | 123.7015 | -123.9578 | -123.9716
2502.7188 | 123.88 | -61.3724 | 62.3657 | -0.17677 | 0.015597 | 0.015763 | 0.011465 | 0.065589 | -0.0022559 | 0.080758 | -58.548 | 62.3703 | -61.615 | -61.5555 | 53.746 | 19.5648 | 4.3945 | 3.9917 | 62.3566 | -61.647 | -0.24262 | 0.004577 | 2.8244 | -0.18311 | -8.6197 | -0.27466 | -0.009156 | 3.067 | 65.7669 | 65.3641 | 115.1184 | 123.7427 | 2.8244 | 123.7289 | 80.9372 | -0.27466 | 123.7427 | 2.8244 | 80.9372 | 115.1184 | 123.7289 | -123.9807 | -124.0128
2503.7188 | 123.8754 | -61.377 | 62.3291 | -0.131 | 0.016024 | 0.017899 | 0.012747 | 0.064093 | 0.0024439 | 0.081185 | -58.5022 | 62.3657 | -61.6287 | -61.5189 | 53.6819 | 19.5145 | 4.4907 | 4.097 | 62.3337 | -61.6516 | -0.25177 | 0.036621 | 2.8748 | -0.14191 | -8.6472 | -0.27466 | 0.004577 | 3.1265 | 65.8676 | 65.4739 | 115.0589 | 123.7427 | 2.8748 | 123.7106 | 80.8914 | -0.27466 | 123.7427 | 2.8748 | 80.8914 | 115.0589 | 123.7106 | -123.9578 | -123.9807
2504.7188 | 123.88 | -61.3403 | 62.3337 | -0.13863 | 0.016451 | 0.018754 | 0.011465 | 0.065161 | 0.00052127 | 0.082467 | -58.5342 | 62.3474 | -61.6013 | -61.5143 | 53.7506 | 19.5374 | 4.5136 | 4.2023 | 62.3291 | -61.6379 | -0.26093 | 0.013733 | 2.8061 | -0.17395 | -8.5831 | -0.29755 | -0.004577 | 3.067 | 65.8539 | 65.5426 | 115.0909 | 123.6877 | 2.8061 | 123.6694 | 80.8777 | -0.29755 | 123.6877 | 2.8061 | 80.8777 | 115.0909 | 123.6694 | -123.9349 | -123.9716
2505.7188 | 123.8434 | -61.3678 | 62.352 | -0.23781 | 0.016665 | 0.013841 | 0.011892 | 0.064093 | 0.0013757 | 0.081613 | -58.58 | 62.3245 | -61.6287 | -61.5326 | 53.6453 | 19.4916 | 4.6646 | 4.2984 | 62.3154 | -61.6653 | -0.26093 | -0.027466 | 2.7878 | -0.16479 | -8.7067 | -0.29755 | -0.036621 | 3.0487 | 66.0324 | 65.6662 | 115.0131 | 123.6923 | 2.7878 | 123.6832 | 80.8594 | -0.29755 | 123.6923 | 2.7878 | 80.8594 | 115.0131 | 123.6832 | -123.9807 | -124.0173
2506.7188 | 123.8617 | -61.3815 | 62.3383 | -0.21492 | 0.017947 | 0.014909 | 0.01232 | 0.063666 | 0.0011621 | 0.081613 | -58.5342 | 62.3245 | -61.6058 | -61.5372 | 53.7415 | 19.6655 | 4.66 | 4.2206 | 62.3337 | -61.6516 | -0.2243 | -0.013733 | 2.8473 | -0.15564 | -8.5968 | -0.27008 | -0.004578 | 3.0716 | 66.0416 | 65.6021 | 115.123 | 123.7061 | 2.8473 | 123.7152 | 81.0471 | -0.27008 | 123.7061 | 2.8473 | 81.0471 | 115.123 | 123.7152 | -123.9441 | -123.9899
2507.7188 | 123.848 | -61.3495 | 62.3428 | -0.21492 | 0.017519 | 0.018113 | 0.011465 | 0.065802 | 0.0030847 | 0.08204 | -58.5434 | 62.3291 | -61.6379 | -61.5601 | 53.6636 | 19.5282 | 4.6875 | 4.1977 | 62.3657 | -61.6425 | -0.28839 | -0.013732 | 2.8061 | -0.21057 | -8.6792 | -0.29297 | 0.022889 | 3.0945 | 66.037 | 65.5472 | 115.0131 | 123.6786 | 2.8061 | 123.7152 | 80.8777 | -0.29297 | 123.6786 | 2.8061 | 80.8777 | 115.0131 | 123.7152 | -123.9807 | -123.9853
2508.7188 | 123.9395 | -61.3312 | 62.2559 | 0.18181 | 0.017519 | 0.014695 | 0.0091152 | 0.065375 | 0.0041529 | 0.083322 | -58.5114 | 62.2375 | -61.6196 | -61.5189 | 53.7186 | 19.5969 | 4.509 | 4.2709 | 62.2833 | -61.6241 | -0.28839 | -0.01831 | 2.8198 | -0.18768 | -8.5373 | -0.29297 | 0.027466 | 3.1082 | 65.8401 | 65.6021 | 115.0497 | 123.5687 | 2.8198 | 123.6145 | 80.928 | -0.29297 | 123.5687 | 2.8198 | 80.928 | 115.0497 | 123.6145 | -123.8754 | -123.88
2509.7188 | 123.8571 | -61.3586 | 62.3337 | -0.17677 | 0.014315 | 0.016618 | 0.012533 | 0.062171 | -0.00033333 | 0.080758 | -58.5571 | 62.3428 | -61.6425 | -61.5601 | 53.7186 | 19.4778 | 4.7379 | 4.1748 | 62.3291 | -61.6745 | -0.28381 | 0.009155 | 2.8015 | -0.20142 | -8.6151 | -0.31586 | -0.004577 | 3.0853 | 66.0965 | 65.5334 | 115.0772 | 123.7015 | 2.8015 | 123.6877 | 80.8365 | -0.31586 | 123.7015 | 2.8015 | 80.8365 | 115.0772 | 123.6877 | -123.9761 | -124.0082
2510.7188 | 123.8525 | -61.3586 | 62.3337 | -0.20729 | 0.017947 | 0.018327 | 0.011038 | 0.06388 | 0.0011621 | 0.080331 | -58.5571 | 62.3245 | -61.6104 | -61.5555 | 53.476 | 19.3954 | 4.7058 | 4.1885 | 62.3428 | -61.6699 | -0.25177 | -0.009155 | 2.8015 | -0.19684 | -8.8577 | -0.31128 | 0.009155 | 3.0533 | 66.0645 | 65.5472 | 114.8346 | 123.6832 | 2.8015 | 123.7015 | 80.7541 | -0.31128 | 123.6832 | 2.8015 | 80.7541 | 114.8346 | 123.7015 | -123.9441 | -124.0036
2511.7188 | 123.8709 | -61.3312 | 62.3108 | -0.16151 | 0.017306 | 0.015122 | 0.011679 | 0.062171 | 0.0018031 | 0.080758 | -58.548 | 62.3337 | -61.6425 | -61.528 | 53.6591 | 19.5236 | 4.5868 | 4.1931 | 62.3337 | -61.6287 | -0.31128 | 0.022888 | 2.7832 | -0.19684 | -8.6517 | -0.29755 | 0.022888 | 3.0945 | 65.918 | 65.5243 | 114.9902 | 123.6649 | 2.7832 | 123.6649 | 80.8548 | -0.29755 | 123.6649 | 2.7832 | 80.8548 | 114.9902 | 123.6649 | -123.9532 | -123.9395
2512.7188 | 123.8297 | -61.3495 | 62.3337 | -0.16914 | 0.017947 | 0.018113 | 0.012533 | 0.065161 | 0.00030767 | 0.079476 | -58.5068 | 62.352 | -61.6287 | -61.5509 | 53.5629 | 19.5282 | 4.6417 | 4.1611 | 62.3566 | -61.6425 | -0.27924 | 0.018311 | 2.8427 | -0.20142 | -8.7708 | -0.29297 | 0.022888 | 3.1219 | 65.9912 | 65.5106 | 114.9124 | 123.7015 | 2.8427 | 123.7061 | 80.8777 | -0.29297 | 123.7015 | 2.8427 | 80.8777 | 114.9124 | 123.7061 | -123.9624 | -123.9761
2513.7188 | 123.8159 | -61.3678 | 62.3199 | 0.04448 | 0.017947 | 0.01854 | 0.013174 | 0.065161 | 0.0013757 | 0.080758 | -58.5068 | 62.3383 | -61.647 | -61.5921 | 53.6591 | 19.487 | 4.6005 | 4.1245 | 62.3108 | -61.6745 | -0.27924 | 0.018311 | 2.861 | -0.2243 | -8.6609 | -0.3067 | -0.009155 | 3.1403 | 65.9683 | 65.4922 | 115.0269 | 123.7061 | 2.861 | 123.6786 | 80.8548 | -0.3067 | 123.7061 | 2.861 | 80.8548 | 115.0269 | 123.6786 | -123.967 | -123.9944
2514.7188 | 123.8663 | -61.3678 | 62.3199 | -0.19966 | 0.017947 | 0.015336 | 0.0097562 | 0.065589 | 0.00073487 | 0.082894 | -58.5434 | 62.352 | -61.6699 | -61.5509 | 53.6911 | 19.5282 | 4.8111 | 4.3259 | 62.3428 | -61.6516 | -0.30212 | 0.032044 | 2.8244 | -0.1831 | -8.6288 | -0.28381 | 0.022888 | 3.1265 | 66.1789 | 65.6937 | 115.0589 | 123.7198 | 2.8244 | 123.7106 | 80.896 | -0.28381 | 123.7198 | 2.8244 | 80.896 | 115.0589 | 123.7106 | -123.9899 | -123.9716
2515.7188 | 123.8525 | -61.3541 | 62.352 | -0.11574 | 0.016665 | 0.017686 | 0.012747 | 0.067725 | -0.0011877 | 0.081185 | -58.4839 | 62.3428 | -61.6287 | -61.5143 | 53.6362 | 19.5374 | 4.5822 | 4.1977 | 62.3199 | -61.6333 | -0.27466 | -0.009156 | 2.8702 | -0.16022 | -8.7158 | -0.27924 | -0.032044 | 3.1448 | 65.9363 | 65.5518 | 114.9902 | 123.6969 | 2.8702 | 123.674 | 80.8914 | -0.27924 | 123.6969 | 2.8702 | 80.8914 | 114.9902 | 123.674 | -123.9807 | -123.9853
2516.7188 | 123.8571 | -61.3632 | 62.3245 | -0.1844 | 0.015169 | 0.017899 | 0.010183 | 0.067084 | 0.0013757 | 0.083962 | -58.5388 | 62.352 | -61.6241 | -61.5784 | 53.6453 | 19.5328 | 4.7653 | 4.2068 | 62.352 | -61.647 | -0.26093 | 0.027466 | 2.8244 | -0.21515 | -8.6792 | -0.28381 | 0.027466 | 3.0853 | 66.1285 | 65.5701 | 115.0085 | 123.7152 | 2.8244 | 123.7152 | 80.896 | -0.28381 | 123.7152 | 2.8244 | 80.896 | 115.0085 | 123.7152 | -123.9487 | -123.9716
2517.7188 | 123.8251 | -61.3678 | 62.3428 | -0.21492 | 0.016665 | 0.016191 | 0.012747 | 0.064307 | 0.0020167 | 0.082681 | -58.5297 | 62.3199 | -61.6287 | -61.5784 | 53.627 | 19.5419 | 4.8752 | 4.2664 | 62.3611 | -61.6516 | -0.26093 | -0.022888 | 2.8381 | -0.21057 | -8.7158 | -0.28381 | 0.018311 | 3.0991 | 66.243 | 65.6342 | 114.9948 | 123.6877 | 2.8381 | 123.7289 | 80.9097 | -0.28381 | 123.6877 | 2.8381 | 80.9097 | 114.9948 | 123.7289 | -123.9716 | -123.9944
2518.7188 | 123.7976 | -61.3724 | 62.3154 | 0.03685 | 0.017947 | 0.01854 | 0.015951 | 0.065802 | 9.4068e-05 | 0.080972 | -58.5114 | 62.3016 | -61.6516 | -61.6013 | 53.5767 | 19.5236 | 4.7424 | 4.2023 | 62.2971 | -61.6653 | -0.27924 | -0.013733 | 2.861 | -0.22888 | -8.7387 | -0.29297 | -0.018311 | 3.1403 | 66.1148 | 65.5746 | 114.949 | 123.674 | 2.861 | 123.6694 | 80.896 | -0.29297 | 123.674 | 2.861 | 80.896 | 114.949 | 123.6694 | -123.967 | -123.9807
2519.7188 | 123.848 | -61.3449 | 62.3154 | -0.12337 | 0.016451 | 0.015977 | 0.010611 | 0.065589 | 0.0018031 | 0.08439 | -58.5114 | 62.3383 | -61.647 | -61.5463 | 53.8055 | 19.6381 | 4.7653 | 4.2343 | 62.3383 | -61.6425 | -0.30212 | 0.022888 | 2.8336 | -0.20142 | -8.5098 | -0.29755 | 0.022888 | 3.1357 | 66.1102 | 65.5792 | 115.1505 | 123.6832 | 2.8336 | 123.6832 | 80.983 | -0.29755 | 123.6832 | 2.8336 | 80.983 | 115.1505 | 123.6832 | -123.9624 | -123.9578
2520.7188 | 123.8754 | -61.3541 | 62.3199 | -0.17677 | 0.016451 | 0.01854 | 0.011679 | 0.064093 | -0.00033333 | 0.083322 | -58.5159 | 62.3154 | -61.6333 | -61.5692 | 53.6774 | 19.6152 | 4.6967 | 4.248 | 62.3337 | -61.6425 | -0.27924 | -0.004577 | 2.8381 | -0.21515 | -8.6426 | -0.28839 | 0.013733 | 3.1174 | 66.0507 | 65.6021 | 115.0314 | 123.6694 | 2.8381 | 123.6877 | 80.9692 | -0.28839 | 123.6694 | 2.8381 | 80.9692 | 115.0314 | 123.6877 | -123.9532 | -123.9624
2521.7188 | 123.8297 | -61.3724 | 62.3337 | -0.19203 | 0.01816 | 0.016618 | 0.011251 | 0.064093 | 0.0026575 | 0.081613 | -58.699 | 62.3383 | -61.6241 | -61.5601 | 53.7872 | 19.6564 | 4.715 | 4.2435 | 62.3154 | -61.6653 | -0.25177 | 0.004578 | 2.6733 | -0.18768 | -8.5464 | -0.29297 | -0.01831 | 2.9251 | 66.0873 | 65.6158 | 115.1596 | 123.7106 | 2.6733 | 123.6877 | 81.0287 | -0.29297 | 123.7106 | 2.6733 | 81.0287 | 115.1596 | 123.6877 | -123.9578 | -123.999
2522.7188 | 123.8892 | -61.3541 | 62.3291 | -0.15388 | 0.019228 | 0.014054 | 0.013601 | 0.06687 | -0.00033333 | 0.080544 | -58.4747 | 62.3291 | -61.6287 | -61.5234 | 53.7643 | 19.6472 | 4.6967 | 4.2984 | 62.3337 | -61.6425 | -0.27466 | 0 | 2.8793 | -0.16937 | -8.5648 | -0.28839 | 0.004577 | 3.154 | 66.0507 | 65.6525 | 115.1184 | 123.6832 | 2.8793 | 123.6877 | 81.0013 | -0.28839 | 123.6832 | 2.8793 | 81.0013 | 115.1184 | 123.6877 | -123.9578 | -123.9716
2523.7188 | 123.8159 | -61.3907 | 62.3154 | 0.17418 | 0.016665 | 0.017899 | 0.013174 | 0.06623 | 0.00030767 | 0.083962 | -58.5526 | 62.3062 | -61.6608 | -61.8484 | 53.8696 | 19.8486 | 4.5456 | 4.1977 | 62.3154 | -61.6562 | -0.27008 | -0.009156 | 2.8381 | -0.45776 | -8.4457 | -0.2655 | 0 | 3.1082 | 65.9363 | 65.5884 | 115.2603 | 123.6969 | 2.8381 | 123.7061 | 81.2393 | -0.2655 | 123.6969 | 2.8381 | 81.2393 | 115.2603 | 123.7061 | -123.9761 | -123.9716
2524.7188 | 123.8388 | -61.3907 | 62.3383 | 0.059738 | 0.017306 | 0.011918 | 0.011465 | 0.064307 | 0.00052127 | 0.079904 | -58.5022 | 62.3245 | -61.6562 | -61.5738 | 53.7506 | 19.5145 | 4.6463 | 4.2252 | 62.3611 | -61.6608 | -0.2655 | -0.013733 | 2.8885 | -0.18311 | -8.5876 | -0.27008 | 0.022888 | 3.154 | 66.037 | 65.6158 | 115.1413 | 123.7152 | 2.8885 | 123.7518 | 80.9052 | -0.27008 | 123.7152 | 2.8885 | 80.9052 | 115.1413 | 123.7518 | -123.9944 | -123.999
2525.7188 | 123.8617 | -61.3586 | 62.3245 | -0.13863 | 0.018374 | 0.015977 | 0.011251 | 0.063452 | 0.00030767 | 0.081826 | -58.4885 | 62.3383 | -61.6196 | -61.5372 | 53.6774 | 19.5602 | 4.7012 | 4.3213 | 62.3199 | -61.6241 | -0.26093 | 0.013733 | 2.8702 | -0.17853 | -8.6472 | -0.2655 | -0.004578 | 3.1311 | 66.0599 | 65.6799 | 115.036 | 123.6969 | 2.8702 | 123.6786 | 80.9189 | -0.2655 | 123.6969 | 2.8702 | 80.9189 | 115.036 | 123.6786 | -123.9441 | -123.9487
2526.7188 | 123.88 | -61.3495 | 62.352 | -0.17677 | 0.016878 | 0.014054 | 0.0095424 | 0.066443 | 0.00094847 | 0.080972 | -58.5251 | 62.3383 | -61.647 | -61.5601 | 53.508 | 19.4778 | 4.6371 | 4.2801 | 62.3199 | -61.6104 | -0.29755 | -0.013733 | 2.8244 | -0.21057 | -8.844 | -0.26093 | -0.032044 | 3.1219 | 65.9866 | 65.6296 | 114.8575 | 123.6877 | 2.8244 | 123.6694 | 80.8273 | -0.26093 | 123.6877 | 2.8244 | 80.8273 | 114.8575 | 123.6694 | -123.999 | -123.9624
2527.7188 | 123.8342 | -61.377 | 62.352 | -0.16914 | 0.018587 | 0.020036 | 0.01296 | 0.065161 | 0.0030847 | 0.082894 | -58.5571 | 62.3154 | -61.6425 | -61.5509 | 53.421 | 19.5465 | 4.6738 | 4.2709 | 62.3428 | -61.6516 | -0.2655 | -0.036621 | 2.8198 | -0.17395 | -8.931 | -0.27466 | -0.009156 | 3.0853 | 66.0507 | 65.6479 | 114.798 | 123.6923 | 2.8198 | 123.7198 | 80.9235 | -0.27466 | 123.6923 | 2.8198 | 80.9235 | 114.798 | 123.7198 | -123.9944 | -124.0036
2528.7188 | 123.8113 | -61.3861 | 62.3016 | 1.3796 | 0.017092 | 0.014054 | 0.011038 | 0.067298 | 0.0018031 | 0.082253 | -58.0719 | 62.3154 | -61.6699 | -61.6241 | 53.4988 | 19.574 | 4.4403 | 4.1107 | 62.3108 | -61.6653 | -0.28381 | 0.013733 | 3.3142 | -0.23804 | -8.8028 | -0.27924 | 0.009155 | 3.598 | 65.8264 | 65.4968 | 114.8849 | 123.7015 | 3.3142 | 123.6969 | 80.9601 | -0.27924 | 123.7015 | 3.3142 | 80.9601 | 114.8849 | 123.6969 | -123.9716 | -123.967
2529.7188 | 123.8297 | -61.3632 | 62.3428 | -0.1844 | 0.017306 | 0.017472 | 0.0099698 | 0.064948 | 0.0026575 | 0.080758 | -58.5205 | 62.3199 | -61.6333 | -61.5646 | 53.6362 | 19.5007 | 4.509 | 4.2297 | 62.3566 | -61.6379 | -0.27008 | -0.022888 | 2.8427 | -0.20142 | -8.7067 | -0.27466 | 0.013733 | 3.1128 | 65.8722 | 65.593 | 114.9994 | 123.6832 | 2.8427 | 123.7198 | 80.864 | -0.27466 | 123.6832 | 2.8427 | 80.864 | 114.9994 | 123.7198 | -123.9761 | -123.9807
2530.7188 | 123.8205 | -61.3632 | 62.3337 | -0.27596 | 0.017092 | 0.014482 | 0.010397 | 0.065161 | 0.0015893 | 0.080758 | -58.5205 | 62.3428 | -61.6241 | -61.5784 | 53.7415 | 19.5877 | 4.5136 | 4.216 | 62.3428 | -61.647 | -0.26093 | 0.009155 | 2.8427 | -0.21515 | -8.5922 | -0.28381 | 0.009155 | 3.1036 | 65.8768 | 65.5792 | 115.1047 | 123.7061 | 2.8427 | 123.7061 | 80.9509 | -0.28381 | 123.7061 | 2.8427 | 80.9509 | 115.1047 | 123.7061 | -123.9578 | -123.9807
2531.7188 | 123.8159 | -61.377 | 62.3291 | -0.32173 | 0.017306 | 0.018754 | 0.012106 | 0.063666 | 0.0022303 | 0.081185 | -58.4793 | 62.3245 | -61.6333 | -61.5692 | 53.7415 | 19.5419 | 4.4586 | 4.1977 | 62.3291 | -61.6608 | -0.25635 | -0.004578 | 2.8976 | -0.19226 | -8.5876 | -0.28381 | 0 | 3.154 | 65.8356 | 65.5746 | 115.1184 | 123.7015 | 2.8976 | 123.7061 | 80.9189 | -0.28381 | 123.7015 | 2.8976 | 80.9189 | 115.1184 | 123.7061 | -123.9624 | -123.9899
2532.7188 | 123.8709 | -61.3678 | 62.3291 | -0.131 | 0.016024 | 0.014054 | 0.011892 | 0.064307 | -0.0014013 | 0.079049 | -58.4381 | 62.3428 | -61.6379 | -61.5326 | 53.7048 | 19.5602 | 4.4312 | 4.2023 | 62.3291 | -61.6379 | -0.27008 | 0.013732 | 2.9297 | -0.16479 | -8.6243 | -0.27008 | 0 | 3.1998 | 65.799 | 65.5701 | 115.0726 | 123.7106 | 2.9297 | 123.6969 | 80.928 | -0.27008 | 123.7106 | 2.9297 | 80.928 | 115.0726 | 123.6969 | -123.967 | -123.967
2533.7188 | 123.8388 | -61.4182 | 62.3108 | 0.097885 | 0.01816 | 0.018113 | 0.015524 | 0.065375 | 0.0015893 | 0.081613 | -58.548 | 62.3291 | -61.6608 | -61.6196 | 53.6316 | 19.4824 | 4.3808 | 4.0833 | 62.3291 | -61.6608 | -0.24262 | 0.018311 | 2.8702 | -0.20142 | -8.6792 | -0.24262 | 0.018311 | 3.1128 | 65.799 | 65.5014 | 115.0497 | 123.7473 | 2.8702 | 123.7473 | 80.9006 | -0.24262 | 123.7473 | 2.8702 | 80.9006 | 115.0497 | 123.7473 | -123.9716 | -123.9716
2534.7188 | 123.8525 | -61.3724 | 62.3566 | -0.16914 | 0.017947 | 0.017686 | 0.012533 | 0.064521 | 0.0020167 | 0.081826 | -58.4152 | 62.3154 | -61.6425 | -61.5509 | 53.6407 | 19.574 | 4.4998 | 4.2114 | 62.3703 | -61.6379 | -0.27008 | -0.041198 | 2.9572 | -0.17853 | -8.7158 | -0.2655 | 0.013733 | 3.2272 | 65.8722 | 65.5838 | 115.0131 | 123.6877 | 2.9572 | 123.7427 | 80.9463 | -0.2655 | 123.6877 | 2.9572 | 80.9463 | 115.0131 | 123.7427 | -123.999 | -123.9944
2535.7188 | 123.8297 | -61.3449 | 62.3657 | -0.16151 | 0.016451 | 0.020249 | 0.010611 | 0.064734 | 0.0011621 | 0.082681 | -58.4702 | 62.3062 | -61.6196 | -61.5601 | 53.7643 | 19.693 | 4.4769 | 4.216 | 62.3383 | -61.6379 | -0.27466 | -0.05951 | 2.8748 | -0.21515 | -8.6014 | -0.29297 | -0.027466 | 3.1494 | 65.8218 | 65.5609 | 115.1093 | 123.6511 | 2.8748 | 123.6832 | 81.0379 | -0.29297 | 123.6511 | 2.8748 | 81.0379 | 115.1093 | 123.6832 | -123.9853 | -124.0036
2536.7188 | 123.8709 | -61.3586 | 62.3291 | -0.24544 | 0.017733 | 0.019608 | 0.013601 | 0.064307 | 0.00094847 | 0.081826 | -58.4152 | 62.3337 | -61.6425 | -61.5051 | 53.8055 | 19.6609 | 4.5547 | 4.3442 | 62.3245 | -61.647 | -0.28381 | 0.004577 | 2.9434 | -0.14648 | -8.5236 | -0.28839 | -0.004578 | 3.2272 | 65.9134 | 65.7028 | 115.1642 | 123.6923 | 2.9434 | 123.6832 | 81.0196 | -0.28839 | 123.6923 | 2.9434 | 81.0196 | 115.1642 | 123.6832 | -123.9716 | -123.9761
2537.7188 | 123.8571 | -61.377 | 62.3199 | -0.36751 | 0.018587 | 0.015336 | 0.0099698 | 0.065589 | -0.0011877 | 0.079263 | -58.4335 | 62.3474 | -61.6516 | -61.5646 | 53.746 | 19.5007 | 4.6738 | 4.3167 | 62.352 | -61.6379 | -0.27466 | 0.027466 | 2.9434 | -0.18768 | -8.5739 | -0.26093 | 0.032044 | 3.2181 | 66.0507 | 65.6937 | 115.123 | 123.7244 | 2.9434 | 123.7289 | 80.8777 | -0.26093 | 123.7244 | 2.9434 | 80.8777 | 115.123 | 123.7289 | -123.9716 | -123.9578
2538.7344 | 123.8388 | -61.3907 | 62.3108 | 0.15892 | 0.017092 | 0.016831 | 0.012747 | 0.066016 | 0.0024439 | 0.08204 | -58.5068 | 62.2833 | -61.6653 | -61.6013 | 53.7415 | 19.5694 | 4.4678 | 4.2068 | 62.2971 | -61.6562 | -0.27466 | -0.027466 | 2.8839 | -0.21057 | -8.5693 | -0.2655 | -0.013733 | 3.1586 | 65.8585 | 65.5975 | 115.1321 | 123.674 | 2.8839 | 123.6877 | 80.9601 | -0.2655 | 123.674 | 2.8839 | 80.9601 | 115.1321 | 123.6877 | -123.9761 | -123.967
2539.7188 | 123.8663 | -61.377 | 62.3428 | -0.14626 | 0.017519 | 0.017259 | 0.012747 | 0.062171 | 0.0015893 | 0.082894 | -58.429 | 62.3199 | -61.6425 | -61.5555 | 53.7643 | 19.6014 | 4.6509 | 4.3121 | 62.3611 | -61.647 | -0.2655 | -0.022888 | 2.948 | -0.17853 | -8.5785 | -0.27008 | 0.018311 | 3.2135 | 66.0278 | 65.6891 | 115.1413 | 123.6969 | 2.948 | 123.7381 | 80.9784 | -0.27008 | 123.6969 | 2.948 | 80.9784 | 115.1413 | 123.7381 | -123.9853 | -123.9899
2540.7188 | 123.8571 | -61.3678 | 62.3291 | -0.16151 | 0.014742 | 0.017899 | 0.012106 | 0.065589 | 0.00052127 | 0.079049 | -58.4793 | 62.3291 | -61.6333 | -61.5601 | 53.7735 | 19.6564 | 4.8157 | 4.3533 | 62.3337 | -61.6516 | -0.2655 | 0 | 2.8885 | -0.19226 | -8.5556 | -0.28381 | 0.004577 | 3.154 | 66.1835 | 65.7211 | 115.1413 | 123.6969 | 2.8885 | 123.7015 | 81.0242 | -0.28381 | 123.6969 | 2.8885 | 81.0242 | 115.1413 | 123.7015 | -123.9624 | -123.9807
2541.7188 | 123.8617 | -61.3678 | 62.3474 | -0.19203 | 0.017733 | 0.010636 | 0.011038 | 0.064093 | 0.0026575 | 0.07969 | -58.4976 | 62.3016 | -61.6425 | -61.5646 | 53.8239 | 19.5786 | 4.7791 | 4.2938 | 62.352 | -61.6699 | -0.27466 | -0.045776 | 2.8702 | -0.19684 | -8.5236 | -0.30212 | 0.004578 | 3.1448 | 66.1469 | 65.6616 | 115.1917 | 123.6694 | 2.8702 | 123.7198 | 80.9463 | -0.30212 | 123.6694 | 2.8702 | 80.9463 | 115.1917 | 123.7198 | -123.9899 | -124.0173
2542.7188 | 123.8388 | -61.3724 | 62.3566 | -0.35225 | 0.017947 | 0.015336 | 0.011038 | 0.064093 | 0.00094847 | 0.083962 | -58.4702 | 62.3474 | -61.6425 | -61.5784 | 53.7048 | 19.6335 | 4.7058 | 4.2252 | 62.3337 | -61.6562 | -0.27008 | -0.009155 | 2.9022 | -0.20599 | -8.6517 | -0.28381 | -0.022888 | 3.1723 | 66.0782 | 65.5975 | 115.0772 | 123.7198 | 2.9022 | 123.7061 | 81.0059 | -0.28381 | 123.7198 | 2.9022 | 81.0059 | 115.0772 | 123.7061 | -123.999 | -124.0128
2543.7188 | 123.88 | -61.3907 | 62.1964 | 0.1284 | 0.017092 | 0.014695 | 0.012747 | 0.06623 | 0.0024439 | 0.080972 | -58.3649 | 62.2421 | -61.6196 | -61.5326 | 53.8376 | 19.8532 | 4.5319 | 4.303 | 62.2696 | -61.6333 | -0.22888 | 0.045776 | 3.0258 | -0.14191 | -8.3588 | -0.24262 | 0.073242 | 3.2547 | 65.9225 | 65.6937 | 115.2283 | 123.6328 | 3.0258 | 123.6603 | 81.2439 | -0.24262 | 123.6328 | 3.0258 | 81.2439 | 115.2283 | 123.6603 | -123.8159 | -123.8297
2544.7188 | 123.8342 | -61.3861 | 62.3566 | -2.2367 | 0.017519 | 0.01555 | 0.011038 | 0.064521 | 0.0028711 | 0.083322 | -58.6075 | 62.3428 | -61.6287 | -61.5784 | 53.801 | 19.7388 | 4.6463 | 4.1382 | 62.3337 | -61.6425 | -0.24262 | -0.013733 | 2.7786 | -0.19226 | -8.5556 | -0.25635 | -0.022888 | 3.0212 | 66.0324 | 65.5243 | 115.1871 | 123.7289 | 2.7786 | 123.7198 | 81.1249 | -0.25635 | 123.7289 | 2.7786 | 81.1249 | 115.1871 | 123.7198 | -123.9853 | -123.999
2545.7188 | 123.8022 | -61.3815 | 62.3245 | -0.22255 | 0.017947 | 0.016191 | 0.0063382 | 0.063239 | 0.0028711 | 0.081826 | -58.493 | 62.3428 | -61.6333 | -61.6608 | 53.8147 | 19.725 | 4.5731 | 4.2114 | 62.3566 | -61.6882 | -0.25177 | 0.01831 | 2.8885 | -0.27924 | -8.5098 | -0.3067 | 0.032043 | 3.1403 | 65.9546 | 65.593 | 115.1962 | 123.7244 | 2.8885 | 123.7381 | 81.1066 | -0.3067 | 123.7244 | 2.8885 | 81.1066 | 115.1962 | 123.7381 | -123.9578 | -124.0128
2546.7188 | 123.8434 | -61.3586 | 62.352 | -0.19966 | 0.017092 | 0.010423 | 0.012747 | 0.064734 | 0.0022303 | 0.082681 | -58.4427 | 62.3245 | -61.6425 | -61.5463 | 53.8147 | 19.6793 | 4.5364 | 4.1382 | 62.3383 | -61.647 | -0.28381 | -0.027466 | 2.916 | -0.18768 | -8.5373 | -0.28839 | -0.013733 | 3.1998 | 65.8951 | 65.4968 | 115.1733 | 123.6832 | 2.916 | 123.6969 | 81.0379 | -0.28839 | 123.6832 | 2.916 | 81.0379 | 115.1733 | 123.6969 | -123.9944 | -123.999
2547.7188 | 123.8342 | -61.3678 | 62.3428 | -0.15388 | 0.01816 | 0.016618 | 0.012533 | 0.062171 | 0.0018031 | 0.082253 | -58.3649 | 62.3291 | -61.6379 | -61.5692 | 53.9017 | 19.6564 | 4.4037 | 4.097 | 62.352 | -61.6241 | -0.27008 | -0.013732 | 3.0029 | -0.20142 | -8.4412 | -0.25635 | 0.009156 | 3.273 | 65.7715 | 65.4648 | 115.2695 | 123.6969 | 3.0029 | 123.7198 | 81.0242 | -0.25635 | 123.6969 | 3.0029 | 81.0242 | 115.2695 | 123.7198 | -123.9807 | -123.967
2548.7188 | 123.8113 | -61.3953 | 62.3062 | 0.052109 | 0.01816 | 0.017472 | 0.014669 | 0.064521 | 0.0032983 | 0.082253 | -58.4564 | 62.3199 | -61.6608 | -61.5921 | 53.7964 | 19.7296 | 4.5914 | 4.1748 | 62.3108 | -61.6653 | -0.2655 | 0.013733 | 2.9388 | -0.19684 | -8.5098 | -0.27008 | 0.004578 | 3.2043 | 65.9866 | 65.5701 | 115.1917 | 123.7152 | 2.9388 | 123.7061 | 81.1249 | -0.27008 | 123.7152 | 2.9388 | 81.1249 | 115.1917 | 123.7061 | -123.967 | -123.9716
2549.7188 | 123.8251 | -61.377 | 62.3383 | -0.0089264 | 0.016878 | 0.011064 | 0.010611 | 0.063239 | 9.4068e-05 | 0.080972 | -58.4244 | 62.2879 | -61.6699 | -61.5326 | 53.8742 | 19.6518 | 4.5639 | 4.1565 | 62.3657 | -61.6379 | -0.29297 | -0.050354 | 2.9526 | -0.15564 | -8.4641 | -0.26093 | 0.027466 | 3.2455 | 65.9409 | 65.5334 | 115.2512 | 123.6649 | 2.9526 | 123.7427 | 81.0287 | -0.26093 | 123.6649 | 2.9526 | 81.0287 | 115.2512 | 123.7427 | -124.0082 | -123.9761
2550.7188 | 123.8617 | -61.3586 | 62.3337 | -0.13863 | 0.015383 | 0.019181 | 0.011679 | 0.06388 | 0.0030847 | 0.081399 | -58.493 | 62.3383 | -61.6608 | -61.5555 | 54.0115 | 19.6884 | 4.5227 | 4.1702 | 62.3383 | -61.6653 | -0.30212 | 0.004578 | 2.8656 | -0.19684 | -8.3221 | -0.3067 | 0.004578 | 3.1677 | 65.8813 | 65.5289 | 115.3702 | 123.6969 | 2.8656 | 123.6969 | 81.0471 | -0.3067 | 123.6969 | 2.8656 | 81.0471 | 115.3702 | 123.6969 | -123.9944 | -123.999
2551.7188 | 123.8251 | -61.377 | 62.3474 | -0.2607 | 0.015169 | 0.015122 | 0.010397 | 0.063452 | 0.00094847 | 0.08204 | -58.4518 | 62.3291 | -61.6379 | -61.4136 | 54.126 | 19.5877 | 4.4586 | 4.2297 | 62.3108 | -61.6653 | -0.26093 | -0.01831 | 2.9251 | -0.036621 | -8.2214 | -0.28839 | -0.036621 | 3.186 | 65.8356 | 65.6067 | 115.5029 | 123.7061 | 2.9251 | 123.6877 | 80.9647 | -0.28839 | 123.7061 | 2.9251 | 80.9647 | 115.5029 | 123.6877 | -123.9853 | -124.0128
2552.7188 | 123.7885 | -61.3495 | 62.3611 | -0.20729 | 0.016238 | 0.015763 | 0.008688 | 0.063239 | 0.00030767 | 0.081826 | -58.4839 | 62.3016 | -61.6425 | -61.5921 | 54.0161 | 19.7021 | 4.5639 | 4.1656 | 62.3428 | -61.6241 | -0.29297 | -0.059509 | 2.8656 | -0.24261 | -8.345 | -0.27466 | -0.018311 | 3.1586 | 65.9134 | 65.5151 | 115.3656 | 123.6511 | 2.8656 | 123.6923 | 81.0516 | -0.27466 | 123.6511 | 2.8656 | 81.0516 | 115.3656 | 123.6923 | -124.0036 | -123.9853
2553.7188 | 123.8342 | -61.3724 | 62.3016 | -0.024185 | 0.017519 | 0.017472 | 0.015738 | 0.065802 | 0.00094847 | 0.082894 | -58.4061 | 62.3337 | -61.6425 | -61.5555 | 53.8834 | 19.8166 | 4.4037 | 4.1519 | 62.3154 | -61.6745 | -0.27008 | 0.032043 | 2.9663 | -0.18311 | -8.4183 | -0.30213 | 0.013733 | 3.2364 | 65.7761 | 65.5243 | 115.2557 | 123.7061 | 2.9663 | 123.6877 | 81.189 | -0.30213 | 123.7061 | 2.9663 | 81.189 | 115.2557 | 123.6877 | -123.9441 | -123.9761
2554.7188 | 123.8297 | -61.3678 | 62.3337 | -0.23018 | 0.01581 | 0.014909 | 0.0099698 | 0.064093 | 0.0032983 | 0.081613 | -58.5022 | 62.3016 | -61.6608 | -61.5646 | 53.8101 | 19.7388 | 4.4678 | 4.097 | 62.3474 | -61.6653 | -0.29297 | -0.032043 | 2.8656 | -0.19684 | -8.5236 | -0.29755 | 0.013733 | 3.1586 | 65.8356 | 65.4648 | 115.1779 | 123.6694 | 2.8656 | 123.7152 | 81.1066 | -0.29755 | 123.6694 | 2.8656 | 81.1066 | 115.1779 | 123.7152 | -123.9944 | -123.999
2555.7188 | 123.8388 | -61.3586 | 62.3383 | -1.0465 | 0.017092 | 0.016618 | 0.01296 | 0.06388 | -0.00011953 | 0.080544 | -58.6121 | 62.3245 | -61.6333 | -61.6058 | 53.7231 | 19.6518 | 4.5502 | 4.1382 | 62.3428 | -61.6287 | -0.27466 | -0.013733 | 2.7466 | -0.24719 | -8.6151 | -0.27008 | 0.004577 | 3.0212 | 65.9088 | 65.4968 | 115.0818 | 123.6832 | 2.7466 | 123.7015 | 81.0104 | -0.27008 | 123.6832 | 2.7466 | 81.0104 | 115.0818 | 123.7015 | -123.9716 | -123.967
2556.7188 | 123.8205 | -61.377 | 62.3703 | -0.28358 | 0.015169 | 0.014054 | 0.0054836 | 0.061957 | 0.0018031 | 0.081185 | -58.5297 | 62.3108 | -61.6516 | -61.6608 | 53.8055 | 19.6747 | 4.4037 | 4.0924 | 62.3291 | -61.6241 | -0.27466 | -0.059509 | 2.8473 | -0.28381 | -8.5648 | -0.24719 | -0.041198 | 3.1219 | 65.7806 | 65.4694 | 115.1825 | 123.6877 | 2.8473 | 123.7061 | 81.0516 | -0.24719 | 123.6877 | 2.8473 | 81.0516 | 115.1825 | 123.7061 | -124.0219 | -123.9944
2557.7188 | 123.8434 | -61.3495 | 62.3291 | -0.19966 | 0.016878 | 0.020036 | 0.013388 | 0.063025 | 0.00030767 | 0.083108 | -58.4747 | 62.3108 | -61.615 | -61.5509 | 53.8788 | 19.6976 | 4.4083 | 4.0695 | 62.3245 | -61.6379 | -0.2655 | -0.018311 | 2.8748 | -0.20142 | -8.4503 | -0.28839 | -0.004578 | 3.1403 | 65.7578 | 65.419 | 115.2283 | 123.6603 | 2.8748 | 123.674 | 81.0471 | -0.28839 | 123.6603 | 2.8748 | 81.0471 | 115.2283 | 123.674 | -123.9441 | -123.967
2558.7188 | 123.8571 | -61.3632 | 62.2971 | -0.069961 | 0.017733 | 0.020249 | 0.015738 | 0.064734 | -0.0020421 | 0.081826 | -58.4061 | 62.3108 | -61.6196 | -61.6608 | 53.9017 | 19.9036 | 4.3808 | 4.1565 | 62.3108 | -61.6562 | -0.25635 | 0.013733 | 2.9572 | -0.29755 | -8.3954 | -0.29297 | 0.013733 | 3.2135 | 65.744 | 65.5197 | 115.2649 | 123.674 | 2.9572 | 123.674 | 81.2668 | -0.29297 | 123.674 | 2.9572 | 81.2668 | 115.2649 | 123.674 | -123.9166 | -123.9532
2559.7188 | 123.8342 | -61.3495 | 62.3383 | -0.25307 | 0.015597 | 0.016191 | 0.010183 | 0.064734 | 0.0018031 | 0.08204 | -58.5068 | 62.3199 | -61.6608 | -61.5692 | 53.7598 | 18.9514 | 4.5776 | 4.1107 | 62.3428 | -61.6333 | -0.31128 | -0.018311 | 2.8427 | -0.21973 | -8.5785 | -0.28381 | 0.004577 | 3.154 | 65.9271 | 65.4602 | 115.1093 | 123.6694 | 2.8427 | 123.6923 | 80.3009 | -0.28381 | 123.6694 | 2.8427 | 80.3009 | 115.1093 | 123.6923 | -123.999 | -123.9716
2560.7188 | 123.8388 | -61.3541 | 62.3337 | -0.10811 | 0.017092 | 0.021531 | 0.016592 | 0.064307 | 9.4068e-05 | 0.080117 | -58.4198 | 62.3337 | -61.6058 | -61.5234 | 53.7048 | 18.7225 | 4.4678 | 4.1565 | 62.3245 | -61.6699 | -0.25177 | 0 | 2.9343 | -0.16937 | -8.6288 | -0.31586 | -0.009155 | 3.186 | 65.8218 | 65.5106 | 115.0589 | 123.6877 | 2.9343 | 123.6786 | 80.0766 | -0.31586 | 123.6877 | 2.9343 | 80.0766 | 115.0589 | 123.6786 | -123.9395 | -124.0036
2561.7188 | 123.8342 | -61.3678 | 62.3428 | -0.46669 | 0.016024 | 0.01555 | 0.011038 | 0.06388 | -0.00033333 | 0.081613 | -58.4976 | 62.352 | -61.6333 | -61.5692 | 53.6911 | 18.4387 | 4.6097 | 4.1382 | 62.3291 | -61.6287 | -0.2655 | 0.009156 | 2.8702 | -0.20142 | -8.6517 | -0.26093 | -0.013732 | 3.1357 | 65.9775 | 65.506 | 115.0589 | 123.7198 | 2.8702 | 123.6969 | 79.8065 | -0.26093 | 123.7198 | 2.8702 | 79.8065 | 115.0589 | 123.6969 | -123.9761 | -123.9716
2562.7188 | 123.8205 | -61.3724 | 62.3383 | 0.097885 | 0.016665 | 0.012773 | 0.011892 | 0.063239 | 0.00052127 | 0.082253 | -58.4747 | 62.352 | -61.6287 | -61.5692 | 53.6957 | 18.0908 | 4.6188 | 4.1656 | 62.3657 | -61.6333 | -0.25635 | 0.013733 | 2.8976 | -0.19684 | -8.6426 | -0.26093 | 0.027466 | 3.154 | 65.9912 | 65.538 | 115.0681 | 123.7244 | 2.8976 | 123.7381 | 79.4632 | -0.26093 | 123.7244 | 2.8976 | 79.4632 | 115.0681 | 123.7381 | -123.967 | -123.9716
2563.7188 | 123.8113 | -61.3815 | 62.3245 | -0.0012969 | 0.017733 | 0.017899 | 0.014669 | 0.064307 | 9.4068e-05 | 0.081613 | -58.4427 | 62.352 | -61.6333 | -61.5692 | 53.6728 | 18.5028 | 4.4907 | 4.0558 | 62.3291 | -61.6699 | -0.25177 | 0.027466 | 2.9388 | -0.18768 | -8.6517 | -0.28839 | 0.004578 | 3.1906 | 65.8722 | 65.4373 | 115.0543 | 123.7335 | 2.9388 | 123.7106 | 79.8843 | -0.28839 | 123.7335 | 2.9388 | 79.8843 | 115.0543 | 123.7106 | -123.9578 | -123.9944
2564.7188 | 123.8388 | -61.3449 | 62.3428 | -0.10811 | 0.01581 | 0.018113 | 0.01232 | 0.064521 | 0.00052127 | 0.081399 | -58.429 | 62.3108 | -61.6196 | -61.5326 | 53.6957 | 18.7042 | 4.6463 | 4.1565 | 62.3291 | -61.6425 | -0.27466 | -0.032043 | 2.916 | -0.18768 | -8.6472 | -0.29755 | -0.013732 | 3.1906 | 65.9912 | 65.5014 | 115.0406 | 123.6557 | 2.916 | 123.674 | 80.0491 | -0.29755 | 123.6557 | 2.916 | 80.0491 | 115.0406 | 123.674 | -123.9624 | -123.9853
2565.7344 | 123.9166 | -61.3449 | 62.2696 | 0.16655 | 0.012179 | 0.017045 | 0.0056972 | 0.065375 | -0.00011953 | 0.083322 | -58.4244 | 62.2192 | -61.6241 | -61.5234 | 53.7323 | 18.8507 | 4.5731 | 4.2526 | 62.2696 | -61.6013 | -0.27924 | -0.050354 | 2.9205 | -0.17853 | -8.5373 | -0.25635 | 0 | 3.1998 | 65.918 | 65.5975 | 115.0772 | 123.5641 | 2.9205 | 123.6145 | 80.1956 | -0.25635 | 123.5641 | 2.9205 | 80.1956 | 115.0772 | 123.6145 | -123.8937 | -123.8708
2566.7188 | 123.8251 | -61.3678 | 62.3566 | -0.2607 | 0.016878 | 0.015122 | 0.01232 | 0.063025 | -0.00033333 | 0.082253 | -58.5663 | 62.3291 | -61.6196 | -61.6241 | 53.7643 | 19.0018 | 4.7241 | 4.1336 | 62.3291 | -61.6608 | -0.25177 | -0.027465 | 2.8015 | -0.25635 | -8.5922 | -0.29297 | -0.027465 | 3.0533 | 66.0919 | 65.5014 | 115.1321 | 123.6969 | 2.8015 | 123.6969 | 80.3696 | -0.29297 | 123.6969 | 2.8015 | 80.3696 | 115.1321 | 123.6969 | -123.9761 | -124.0173
2567.7188 | 123.8434 | -61.3724 | 62.3566 | -0.23018 | 0.017092 | 0.015336 | 0.013601 | 0.063025 | 0.0013757 | 0.080331 | -58.461 | 62.3383 | -61.6196 | -61.5326 | 53.6362 | 18.9011 | 4.5685 | 4.1016 | 62.3245 | -61.6425 | -0.24719 | -0.01831 | 2.9114 | -0.16022 | -8.7204 | -0.27008 | -0.032043 | 3.1586 | 65.9409 | 65.4739 | 115.0085 | 123.7106 | 2.9114 | 123.6969 | 80.2734 | -0.27008 | 123.7106 | 2.9114 | 80.2734 | 115.0085 | 123.6969 | -123.9761 | -123.999
2568.7188 | 123.8571 | -61.4044 | 62.3154 | 0.0063326 | 0.017519 | 0.017899 | 0.014029 | 0.063452 | 0.0022303 | 0.081613 | -58.4473 | 62.3199 | -61.6425 | -61.6196 | 53.7003 | 18.9514 | 4.5044 | 4.0512 | 62.3062 | -61.6562 | -0.23804 | 0.004577 | 2.9572 | -0.21515 | -8.6151 | -0.25177 | -0.009156 | 3.1952 | 65.9088 | 65.4556 | 115.1047 | 123.7244 | 2.9572 | 123.7106 | 80.3558 | -0.25177 | 123.7244 | 2.9572 | 80.3558 | 115.1047 | 123.7106 | -123.9578 | -123.9716
2569.7188 | 123.8434 | -61.3586 | 62.3337 | -0.21492 | 0.016238 | 0.018113 | 0.011465 | 0.066443 | 0.00073487 | 0.080972 | -58.4656 | 62.3383 | -61.647 | -61.5417 | 53.6865 | 19.0933 | 4.5593 | 4.1382 | 62.3428 | -61.6196 | -0.28839 | 0.004578 | 2.8931 | -0.1831 | -8.6472 | -0.26093 | 0.009155 | 3.1815 | 65.918 | 65.4968 | 115.0452 | 123.6969 | 2.8931 | 123.7015 | 80.452 | -0.26093 | 123.6969 | 2.8931 | 80.452 | 115.0452 | 123.7015 | -123.9807 | -123.9532
2570.7344 | 123.9258 | -61.3541 | 62.2742 | 0.17418 | 0.013033 | 0.017472 | 0.010824 | 0.064521 | 0.0011621 | 0.085031 | -58.4244 | 62.2421 | -61.615 | -61.5097 | 53.8193 | 19.3039 | 4.303 | 4.1153 | 62.2375 | -61.5921 | -0.26093 | -0.032044 | 2.9297 | -0.15564 | -8.4549 | -0.23804 | -0.036621 | 3.1906 | 65.657 | 65.4694 | 115.1733 | 123.5962 | 2.9297 | 123.5916 | 80.658 | -0.23804 | 123.5962 | 2.9297 | 80.658 | 115.1733 | 123.5916 | -123.8892 | -123.8663
2571.7188 | 123.848 | -61.3815 | 62.3337 | -0.19203 | 0.017306 | 0.014909 | 0.011892 | 0.063025 | 9.4068e-05 | 0.07969 | -58.4427 | 62.3199 | -61.615 | -61.5555 | 53.801 | 19.3085 | 4.6051 | 4.0558 | 62.3291 | -61.6516 | -0.23346 | -0.013733 | 2.9388 | -0.17395 | -8.5327 | -0.27008 | -0.004577 | 3.1723 | 65.9866 | 65.4373 | 115.1825 | 123.7015 | 2.9388 | 123.7106 | 80.69 | -0.27008 | 123.7015 | 2.9388 | 80.69 | 115.1825 | 123.7106 | -123.9487 | -123.9853
2572.7188 | 123.7335 | -61.3358 | 62.3245 | -0.25307 | 0.016878 | 0.015122 | 0.012106 | 0.06388 | 0.0022303 | 0.07969 | -58.4381 | 62.3383 | -61.6241 | -61.5738 | 53.7689 | 19.2856 | 4.6967 | 4.2938 | 62.352 | -61.6196 | -0.28839 | 0.013733 | 2.8976 | -0.23804 | -8.5556 | -0.28381 | 0.027466 | 3.186 | 66.0324 | 65.6296 | 115.1047 | 123.674 | 2.8976 | 123.6877 | 80.6213 | -0.28381 | 123.674 | 2.8976 | 80.6213 | 115.1047 | 123.6877 | -123.9487 | -123.9441
2573.7188 | 123.8709 | -61.3495 | 62.3291 | -0.12337 | 0.017947 | 0.012559 | 0.015951 | 0.063666 | 0.0041529 | 0.080331 | -58.3694 | 62.3245 | -61.615 | -61.6699 | 53.8696 | 19.4962 | 4.4174 | 4.1245 | 62.3108 | -61.6379 | -0.2655 | -0.004578 | 2.98 | -0.32043 | -8.4595 | -0.28839 | -0.018311 | 3.2455 | 65.7669 | 65.4739 | 115.2191 | 123.674 | 2.98 | 123.6603 | 80.8456 | -0.28839 | 123.674 | 2.98 | 80.8456 | 115.2191 | 123.6603 | -123.9441 | -123.967
2574.7188 | 123.8159 | -61.3632 | 62.3383 | -0.19966 | 0.019228 | 0.015336 | 0.012106 | 0.064521 | 0.0024439 | 0.081613 | -58.4381 | 62.3337 | -61.6287 | -61.5692 | 53.6911 | 19.1711 | 4.5227 | 4.0283 | 62.3428 | -61.6516 | -0.2655 | -0.004578 | 2.9251 | -0.20599 | -8.6472 | -0.28839 | 0.004577 | 3.1906 | 65.8859 | 65.3915 | 115.0543 | 123.6969 | 2.9251 | 123.7061 | 80.5344 | -0.28839 | 123.6969 | 2.9251 | 80.5344 | 115.0543 | 123.7061 | -123.967 | -123.9899
2575.7344 | 123.9349 | -61.3403 | 62.2696 | 0.10551 | 0.014742 | 0.019181 | 0.005911 | 0.063666 | -0.00011953 | 0.07969 | -58.4061 | 62.2238 | -61.615 | -61.5372 | 53.7689 | 19.4138 | 4.3533 | 4.1245 | 62.2421 | -61.6241 | -0.27466 | -0.045776 | 2.9343 | -0.19684 | -8.5007 | -0.28381 | -0.027466 | 3.2089 | 65.6937 | 65.4648 | 115.1093 | 123.5641 | 2.9343 | 123.5825 | 80.7541 | -0.28381 | 123.5641 | 2.9343 | 80.7541 | 115.1093 | 123.5825 | -123.8846 | -123.8937
2576.7188 | 123.8251 | -61.3449 | 62.3428 | -0.40565 | 0.014315 | 0.019395 | 0.014029 | 0.061316 | 0.0022303 | 0.081185 | -58.4747 | 62.3154 | -61.6425 | -61.5646 | 53.8193 | 19.4183 | 4.6051 | 4.1336 | 62.3291 | -61.6379 | -0.29755 | -0.027465 | 2.8702 | -0.21973 | -8.5236 | -0.29297 | -0.013732 | 3.1677 | 65.95 | 65.4785 | 115.1642 | 123.6603 | 2.8702 | 123.674 | 80.7632 | -0.29297 | 123.6603 | 2.8702 | 80.7632 | 115.1642 | 123.674 | -123.9853 | -123.9807
2577.7188 | 123.8617 | -61.377 | 62.3428 | -0.23781 | 0.014315 | 0.018113 | 0.014456 | 0.064307 | -0.00011953 | 0.080544 | -58.3878 | 62.3428 | -61.615 | -61.5234 | 53.8925 | 19.4366 | 4.628 | 4.216 | 62.3199 | -61.6562 | -0.23804 | 0 | 2.9892 | -0.14648 | -8.4503 | -0.27924 | -0.022888 | 3.2272 | 66.0049 | 65.593 | 115.2695 | 123.7198 | 2.9892 | 123.6969 | 80.8136 | -0.27924 | 123.7198 | 2.9892 | 80.8136 | 115.2695 | 123.6969 | -123.9578 | -123.999
2578.7188 | 123.8754 | -61.377 | 62.2879 | 0.16655 | 0.02051 | 0.018327 | 0.014242 | 0.065375 | 0.0015893 | 0.081399 | -58.4702 | 62.3199 | -61.6516 | -61.6058 | 53.7781 | 19.3909 | 4.6005 | 4.1565 | 62.2971 | -61.6562 | -0.27466 | 0.032043 | 2.9068 | -0.22888 | -8.5098 | -0.27924 | 0.009155 | 3.1815 | 65.9775 | 65.5334 | 115.155 | 123.6969 | 2.9068 | 123.674 | 80.7678 | -0.27924 | 123.6969 | 2.9068 | 80.7678 | 115.155 | 123.674 | -123.9395 | -123.9441
2579.7188 | 123.8159 | -61.3632 | 62.3428 | -0.25307 | 0.017092 | 0.016191 | 0.012747 | 0.064948 | 0.00094847 | 0.081826 | -58.5526 | 62.3337 | -61.6058 | -61.6196 | 53.7872 | 19.4092 | 4.8065 | 4.2572 | 62.3016 | -61.6379 | -0.24262 | -0.009155 | 2.8107 | -0.25635 | -8.5556 | -0.27466 | -0.041198 | 3.0533 | 66.1697 | 65.6204 | 115.1505 | 123.6969 | 2.8107 | 123.6649 | 80.7724 | -0.27466 | 123.6969 | 2.8107 | 80.7724 | 115.1505 | 123.6649 | -123.9487 | -123.9807
2580.7188 | 123.848 | -61.3586 | 62.3383 | -0.20729 | 0.016665 | 0.016404 | 0.014029 | 0.064093 | 0.00030767 | 0.081185 | -58.4061 | 62.3108 | -61.6379 | -61.5417 | 53.7415 | 18.7775 | 4.628 | 3.9963 | 62.3291 | -61.6287 | -0.27923 | -0.027466 | 2.9526 | -0.1831 | -8.5968 | -0.27008 | -0.009155 | 3.2318 | 65.9866 | 65.3549 | 115.1001 | 123.6694 | 2.9526 | 123.6877 | 80.1361 | -0.27008 | 123.6694 | 2.9526 | 80.1361 | 115.1001 | 123.6877 | -123.9761 | -123.967
2581.7188 | 123.8068 | -61.3541 | 62.3337 | -0.16151 | 0.017306 | 0.015977 | 0.011251 | 0.064734 | 0.0035121 | 0.081613 | -58.4198 | 62.3199 | -61.6241 | -61.5417 | 53.7643 | 18.7363 | 4.6234 | 3.9688 | 62.3199 | -61.6241 | -0.27008 | -0.013733 | 2.9343 | -0.18768 | -8.5693 | -0.27008 | -0.013733 | 3.2043 | 65.9775 | 65.3229 | 115.1184 | 123.674 | 2.9343 | 123.674 | 80.0903 | -0.27008 | 123.674 | 2.9343 | 80.0903 | 115.1184 | 123.674 | -123.9578 | -123.9578
2582.7188 | 123.8297 | -61.3632 | 62.3428 | -0.20729 | 0.016024 | 0.015336 | 0.011892 | 0.065375 | 0.00030767 | 0.081826 | -58.4015 | 62.3383 | -61.6379 | -61.5509 | 53.8239 | 18.9285 | 4.6875 | 4.0604 | 62.3337 | -61.6333 | -0.27466 | -0.004577 | 2.9617 | -0.18768 | -8.519 | -0.27008 | -0.009155 | 3.2364 | 66.0507 | 65.4236 | 115.1871 | 123.7015 | 2.9617 | 123.6969 | 80.2917 | -0.27008 | 123.7015 | 2.9617 | 80.2917 | 115.1871 | 123.6969 | -123.9807 | -123.9761
2583.7188 | 123.8434 | -61.3815 | 62.3199 | 0.14366 | 0.017947 | 0.019181 | 0.016806 | 0.066443 | 0.0035121 | 0.086312 | -58.5205 | 62.3245 | -61.6699 | -61.9171 | 53.6819 | 19.281 | 4.6692 | 3.9047 | 62.3291 | -61.6699 | -0.28839 | 0.004578 | 2.861 | -0.53558 | -8.638 | -0.28839 | 0.009156 | 3.1494 | 66.0507 | 65.2863 | 115.0635 | 123.7061 | 2.861 | 123.7106 | 80.6625 | -0.28839 | 123.7061 | 2.861 | 80.6625 | 115.0635 | 123.7106 | -123.9899 | -123.9899
2584.7188 | 123.8571 | -61.3403 | 62.3566 | -0.23781 | 0.019015 | 0.013841 | 0.01296 | 0.063239 | 0.0011621 | 0.08204 | -58.4152 | 62.3383 | -61.6196 | -61.5234 | 53.8422 | 19.1116 | 4.6692 | 4.0375 | 62.2833 | -61.6608 | -0.27924 | -0.01831 | 2.9251 | -0.18311 | -8.5144 | -0.32044 | -0.073242 | 3.2043 | 66.0095 | 65.3778 | 115.1825 | 123.6786 | 2.9251 | 123.6237 | 80.452 | -0.32044 | 123.6786 | 2.9251 | 80.452 | 115.1825 | 123.6237 | -123.9761 | -124.0173
2585.7188 | 123.8022 | -61.3358 | 62.3383 | -0.26833 | 0.018374 | 0.011918 | 0.0099698 | 0.065589 | 0.0022303 | 0.081399 | -58.223 | 62.3566 | -61.6196 | -61.5738 | 53.7827 | 19.1437 | 4.7241 | 4.1199 | 62.3291 | -61.6379 | -0.28381 | 0.01831 | 3.1128 | -0.23804 | -8.5556 | -0.30212 | -0.009155 | 3.3966 | 66.0599 | 65.4556 | 115.1184 | 123.6923 | 3.1128 | 123.6649 | 80.4794 | -0.30212 | 123.6923 | 3.1128 | 80.4794 | 115.1184 | 123.6649 | -123.9578 | -123.9761
2586.7188 | 123.8388 | -61.377 | 62.3337 | -0.23781 | 0.016878 | 0.017045 | 0.0089016 | 0.063452 | 0.00052127 | 0.081826 | -58.4152 | 62.352 | -61.6241 | -61.3632 | 53.7369 | 19.0475 | 4.7012 | 4.0329 | 62.3337 | -61.6928 | -0.24719 | 0.018311 | 2.9617 | 0.013733 | -8.5968 | -0.31586 | 0 | 3.2089 | 66.0782 | 65.4099 | 115.1138 | 123.7289 | 2.9617 | 123.7106 | 80.4245 | -0.31586 | 123.7289 | 2.9617 | 80.4245 | 115.1138 | 123.7106 | -123.9578 | -124.0265
2587.7188 | 123.8342 | -61.3632 | 62.3199 | -0.16914 | 0.017092 | 0.012345 | 0.011892 | 0.063025 | 0.00073487 | 0.082467 | -58.3969 | 62.3474 | -61.6379 | -61.5509 | 53.8284 | 19.2078 | 4.8065 | 4.1153 | 62.3199 | -61.6608 | -0.27466 | 0.027466 | 2.9663 | -0.18768 | -8.4915 | -0.29755 | 0 | 3.241 | 66.1697 | 65.4785 | 115.1916 | 123.7106 | 2.9663 | 123.6832 | 80.571 | -0.29755 | 123.7106 | 2.9663 | 80.571 | 115.1916 | 123.6832 | -123.9578 | -123.9807
2588.7188 | 123.8068 | -61.3678 | 62.3337 | 0.03685 | 0.017733 | 0.017686 | 0.015524 | 0.06623 | -0.00033333 | 0.081826 | -58.3786 | 62.3291 | -61.6287 | -61.5784 | 53.7598 | 19.2307 | 4.6417 | 4.0375 | 62.3199 | -61.6745 | -0.26093 | -0.004577 | 2.9892 | -0.21057 | -8.5739 | -0.3067 | -0.013733 | 3.2501 | 66.0095 | 65.4053 | 115.1276 | 123.6969 | 2.9892 | 123.6877 | 80.5984 | -0.3067 | 123.6969 | 2.9892 | 80.5984 | 115.1276 | 123.6877 | -123.9624 | -124.0082
2589.7188 | 123.848 | -61.3815 | 62.3611 | 1.3186 | 0.017092 | 0.017899 | 0.0089016 | 0.064948 | 0.0026575 | 0.081399 | -58.4518 | 62.3199 | -61.647 | -61.5738 | 53.7964 | 19.0933 | 4.747 | 4.1473 | 62.3428 | -61.6287 | -0.2655 | -0.041199 | 2.9297 | -0.19226 | -8.5648 | -0.24719 | -0.018311 | 3.1952 | 66.1285 | 65.5289 | 115.1779 | 123.7015 | 2.9297 | 123.7244 | 80.4749 | -0.24719 | 123.7015 | 2.9297 | 80.4749 | 115.1779 | 123.7244 | -124.0082 | -123.9899
2590.7188 | 123.8113 | -61.3724 | 62.3428 | -0.23018 | 0.014956 | 0.017259 | 0.010611 | 0.063666 | -0.00011953 | 0.082467 | -58.4061 | 62.3062 | -61.6562 | -61.5601 | 53.7964 | 19.075 | 4.6783 | 4.1382 | 62.3154 | -61.6516 | -0.28381 | -0.036621 | 2.9663 | -0.18768 | -8.5464 | -0.27924 | -0.027465 | 3.2501 | 66.0507 | 65.5106 | 115.1688 | 123.6786 | 2.9663 | 123.6877 | 80.4474 | -0.27924 | 123.6786 | 2.9663 | 80.4474 | 115.1688 | 123.6877 | -123.999 | -123.9944
2591.7188 | 123.8617 | -61.3815 | 62.3474 | -0.1844 | 0.01816 | 0.017045 | 0.013388 | 0.064948 | 0.00052127 | 0.08204 | -58.3786 | 62.3337 | -61.6516 | -61.5646 | 53.8147 | 19.2307 | 4.7058 | 4.1473 | 62.3383 | -61.6516 | -0.27008 | -0.013733 | 3.0029 | -0.1831 | -8.5327 | -0.27008 | -0.009155 | 3.273 | 66.0873 | 65.5289 | 115.1962 | 123.7152 | 3.0029 | 123.7198 | 80.6122 | -0.27008 | 123.7152 | 3.0029 | 80.6122 | 115.1962 | 123.7198 | -123.999 | -123.999
2592.7188 | 123.8205 | -61.3861 | 62.3428 | -0.25307 | 0.016451 | 0.014695 | 0.011038 | 0.06153 | 0.0028711 | 0.082467 | -58.3969 | 62.3154 | -61.6241 | -61.5784 | 53.9383 | 19.249 | 4.6829 | 4.1794 | 62.3337 | -61.6287 | -0.23804 | -0.027465 | 2.9892 | -0.19226 | -8.4045 | -0.24262 | -0.009155 | 3.2272 | 66.069 | 65.5655 | 115.3244 | 123.7015 | 2.9892 | 123.7198 | 80.6351 | -0.24262 | 123.7015 | 2.9892 | 80.6351 | 115.3244 | 123.7198 | -123.967 | -123.9716
2593.7188 | 123.8617 | -61.3724 | 62.3108 | -0.016556 | 0.019015 | 0.01555 | 0.013815 | 0.064093 | -0.00033333 | 0.084176 | -58.2733 | 62.3108 | -61.6287 | -61.528 | 53.8055 | 19.2947 | 4.5914 | 4.1565 | 62.2879 | -61.6653 | -0.25635 | 0 | 3.0991 | -0.15564 | -8.5052 | -0.29297 | -0.022888 | 3.3554 | 65.9637 | 65.5289 | 115.1779 | 123.6832 | 3.0991 | 123.6603 | 80.6671 | -0.29297 | 123.6832 | 3.0991 | 80.6671 | 115.1779 | 123.6603 | -123.9395 | -123.9761
2594.7188 | 123.8251 | -61.3678 | 62.3383 | -0.30647 | 0.017092 | 0.017259 | 0.0054836 | 0.061316 | 0.0011621 | 0.082894 | -58.4198 | 62.2971 | -61.6425 | -61.702 | 53.7552 | 19.3909 | 4.6967 | 4.1656 | 62.3337 | -61.6241 | -0.27466 | -0.041199 | 2.948 | -0.33417 | -8.5831 | -0.25635 | -0.004578 | 3.2227 | 66.0645 | 65.5334 | 115.123 | 123.6649 | 2.948 | 123.7015 | 80.7587 | -0.25635 | 123.6649 | 2.948 | 80.7587 | 115.123 | 123.7015 | -123.9807 | -123.9624
2595.7188 | 123.8983 | -61.3358 | 62.3703 | -0.23018 | 0.015169 | 0.012559 | 0.0084744 | 0.062384 | 0.0022303 | 0.081613 | -58.3923 | 62.3016 | -61.6516 | -61.5692 | 53.9017 | 19.4916 | 4.8065 | 4.3304 | 62.3337 | -61.6287 | -0.31586 | -0.068664 | 2.9434 | -0.23346 | -8.4686 | -0.29297 | -0.036621 | 3.2593 | 66.1423 | 65.6662 | 115.2374 | 123.6374 | 2.9434 | 123.6694 | 80.8273 | -0.29297 | 123.6374 | 2.9434 | 80.8273 | 115.2374 | 123.6694 | -124.0219 | -123.999
2596.7188 | 123.8251 | -61.3541 | 62.3199 | -0.37514 | 0.016024 | 0.016831 | 0.0099698 | 0.06388 | 0.0013757 | 0.08204 | -58.3786 | 62.3108 | -61.6287 | -61.5646 | 53.8284 | 19.2169 | 4.6921 | 4.0466 | 62.3291 | -61.6196 | -0.27466 | -0.009155 | 2.9755 | -0.21057 | -8.4915 | -0.2655 | 0.009156 | 3.2501 | 66.0461 | 65.4007 | 115.1825 | 123.6649 | 2.9755 | 123.6832 | 80.571 | -0.2655 | 123.6649 | 2.9755 | 80.571 | 115.1825 | 123.6832 | -123.9487 | -123.9395
2597.7188 | 123.8342 | -61.3586 | 62.3291 | -0.23018 | 0.014101 | 0.014054 | 0.0093288 | 0.06153 | -0.00076053 | 0.081185 | -58.2962 | 62.2696 | -61.6196 | -61.5509 | 53.9337 | 19.2123 | 4.9164 | 4.6234 | 62.3291 | -61.6287 | -0.26093 | -0.05951 | 3.0624 | -0.19226 | -8.3954 | -0.27008 | 0 | 3.3234 | 66.275 | 65.9821 | 115.2924 | 123.6282 | 3.0624 | 123.6877 | 80.571 | -0.27008 | 123.6282 | 3.0624 | 80.571 | 115.2924 | 123.6877 | -123.9487 | -123.9578
2598.7188 | 123.9349 | -61.3724 | 62.2833 | 0.18944 | 0.016665 | 0.01854 | 0.013815 | 0.063239 | 0.0018031 | 0.083108 | -58.2962 | 62.2421 | -61.6425 | -61.5463 | 53.9246 | 19.4916 | 4.8019 | 4.7241 | 62.2467 | -61.6745 | -0.27008 | -0.041199 | 3.0762 | -0.17395 | -8.3588 | -0.30213 | -0.036621 | 3.3463 | 66.1743 | 66.0965 | 115.2969 | 123.6145 | 3.0762 | 123.6191 | 80.864 | -0.30213 | 123.6145 | 3.0762 | 80.864 | 115.2969 | 123.6191 | -123.9258 | -123.9578
2599.7188 | 123.88 | -61.3495 | 62.3016 | -0.2607 | 0.014742 | 0.0132 | 0.010397 | 0.063452 | 0.0024439 | 0.083749 | -58.3282 | 62.2284 | -61.615 | -61.496 | 54.0207 | 19.5923 | 4.8752 | 4.7791 | 62.2971 | -61.6196 | -0.2655 | -0.073242 | 3.0212 | -0.14648 | -8.2809 | -0.27008 | -0.004578 | 3.2867 | 66.2247 | 66.1285 | 115.3702 | 123.5779 | 3.0212 | 123.6465 | 80.9418 | -0.27008 | 123.5779 | 3.0212 | 80.9418 | 115.3702 | 123.6465 | -123.9166 | -123.9212
2600.7188 | 123.9304 | -61.3541 | 62.3062 | -0.17677 | 0.012606 | 0.01555 | 0.0082608 | 0.061743 | 0.0011621 | 0.080972 | -58.2962 | 62.2192 | -61.6196 | -61.4868 | 53.9337 | 19.6243 | 4.9667 | 4.8294 | 62.265 | -61.615 | -0.2655 | -0.086975 | 3.0579 | -0.13275 | -8.3725 | -0.26093 | -0.041198 | 3.3234 | 66.3208 | 66.1835 | 115.2878 | 123.5733 | 3.0579 | 123.6191 | 80.9784 | -0.26093 | 123.5733 | 3.0579 | 80.9784 | 115.2878 | 123.6191 | -123.9258 | -123.9212
2601.7188 | 123.8525 | -61.3724 | 62.3383 | -0.27596 | 0.014101 | 0.015977 | 0.012533 | 0.061957 | -0.00033333 | 0.083322 | -58.3603 | 62.2559 | -61.6196 | -61.5326 | 54.0207 | 19.6243 | 4.9713 | 4.6967 | 62.2787 | -61.6196 | -0.24719 | -0.082398 | 3.0121 | -0.16022 | -8.3176 | -0.24719 | -0.059509 | 3.2593 | 66.3437 | 66.069 | 115.3931 | 123.6282 | 3.0121 | 123.6511 | 80.9967 | -0.24719 | 123.6282 | 3.0121 | 80.9967 | 115.3931 | 123.6511 | -123.9578 | -123.9578
2602.7188 | 123.8754 | -61.3495 | 62.3383 | -0.23781 | 0.016024 | 0.012773 | 0.010183 | 0.06153 | 0.0013757 | 0.080544 | -58.3557 | 62.2238 | -61.615 | -61.5189 | 54.0115 | 19.5831 | 4.9713 | 4.7699 | 62.2925 | -61.6379 | -0.2655 | -0.11444 | 2.9938 | -0.16937 | -8.3267 | -0.28839 | -0.045777 | 3.2593 | 66.3208 | 66.1194 | 115.361 | 123.5733 | 2.9938 | 123.642 | 80.9326 | -0.28839 | 123.5733 | 2.9938 | 80.9326 | 115.361 | 123.642 | -123.9532 | -123.9761
2603.7188 | 123.8525 | -61.3678 | 62.3199 | -0.031814 | 0.017947 | 0.016831 | 0.017233 | 0.063452 | 0.0018031 | 0.07969 | -58.5388 | 62.2971 | -61.6287 | -61.5326 | 53.8376 | 19.3909 | 5.0354 | 4.7516 | 62.2925 | -61.6745 | -0.26093 | -0.022888 | 2.829 | -0.16479 | -8.4824 | -0.3067 | -0.027466 | 3.0899 | 66.4032 | 66.1194 | 115.2054 | 123.6649 | 2.829 | 123.6603 | 80.7587 | -0.3067 | 123.6649 | 2.829 | 80.7587 | 115.2054 | 123.6603 | -123.9487 | -123.9944
2604.7188 | 123.8434 | -61.3678 | 62.3062 | -0.27596 | 0.017519 | 0.013627 | 0.012533 | 0.060889 | 0.0015893 | 0.080117 | -58.3008 | 62.2742 | -61.6562 | -61.5509 | 53.8925 | 19.4092 | 5.0034 | 4.6921 | 62.3245 | -61.6333 | -0.28839 | -0.032043 | 3.067 | -0.1831 | -8.4137 | -0.2655 | 0.018311 | 3.3554 | 66.3712 | 66.0599 | 115.2603 | 123.642 | 3.067 | 123.6923 | 80.777 | -0.2655 | 123.642 | 3.067 | 80.777 | 115.2603 | 123.6923 | -123.9624 | -123.9395
2605.7188 | 123.8434 | -61.3678 | 62.3291 | -0.25307 | 0.01581 | 0.014909 | 0.012533 | 0.064734 | 0.0011621 | 0.081613 | -58.3237 | 62.3062 | -61.6699 | -61.5463 | 53.801 | 19.4366 | 5.0995 | 4.6555 | 62.3154 | -61.6791 | -0.30212 | -0.022889 | 3.0441 | -0.17853 | -8.5281 | -0.31128 | -0.013733 | 3.3463 | 66.4673 | 66.0233 | 115.1688 | 123.674 | 3.0441 | 123.6832 | 80.8044 | -0.31128 | 123.674 | 3.0441 | 80.8044 | 115.1688 | 123.6832 | -123.999 | -124.0082
2606.7188 | 123.8388 | -61.3495 | 62.3062 | -0.27596 | 0.01581 | 0.016831 | 0.010824 | 0.063239 | -0.0011877 | 0.081613 | -58.2596 | 62.2696 | -61.6287 | -61.5372 | 53.8651 | 19.4275 | 4.9805 | 4.628 | 62.2971 | -61.6333 | -0.27924 | -0.036621 | 3.0899 | -0.18768 | -8.4412 | -0.28381 | -0.009155 | 3.3691 | 66.33 | 65.9775 | 115.2145 | 123.6191 | 3.0899 | 123.6465 | 80.777 | -0.28381 | 123.6191 | 3.0899 | 80.777 | 115.2145 | 123.6465 | -123.9349 | -123.9395
2607.7188 | 123.88 | -61.3632 | 62.3154 | -0.24544 | 0.015383 | 0.012132 | 0.0099698 | 0.061103 | -0.0018285 | 0.081185 | -58.3054 | 62.2604 | -61.615 | -61.5189 | 53.8879 | 19.5465 | 4.9255 | 4.7333 | 62.2742 | -61.6287 | -0.25177 | -0.054932 | 3.0579 | -0.15564 | -8.4274 | -0.2655 | -0.041199 | 3.3096 | 66.2888 | 66.0965 | 115.2512 | 123.6237 | 3.0579 | 123.6374 | 80.9097 | -0.2655 | 123.6237 | 3.0579 | 80.9097 | 115.2512 | 123.6374 | -123.9304 | -123.9441
2608.7188 | 123.8068 | -61.3678 | 62.3291 | -0.49721 | 0.016024 | 0.016404 | 0.011679 | 0.064093 | 0.00094847 | 0.081185 | -58.4473 | 62.2971 | -61.6608 | -61.5646 | 53.801 | 19.519 | 4.9759 | 4.5868 | 62.3016 | -61.6516 | -0.29297 | -0.032044 | 2.9205 | -0.19684 | -8.5281 | -0.28381 | -0.027466 | 3.2135 | 66.3437 | 65.9546 | 115.1688 | 123.6649 | 2.9205 | 123.6694 | 80.8868 | -0.28381 | 123.6649 | 2.9205 | 80.8868 | 115.1688 | 123.6694 | -123.9899 | -123.9807
2609.7188 | 123.8251 | -61.3815 | 62.3291 | -0.29121 | 0.01581 | 0.010423 | 0.013815 | 0.060034 | 0.00094847 | 0.080331 | -58.3969 | 62.2604 | -61.6379 | -61.5692 | 53.92 | 19.7754 | 4.9438 | 4.4312 | 62.3245 | -61.6241 | -0.25635 | -0.068665 | 2.9846 | -0.18768 | -8.4091 | -0.24262 | -0.004578 | 3.241 | 66.3254 | 65.8127 | 115.3015 | 123.642 | 2.9846 | 123.7061 | 81.1569 | -0.24262 | 123.642 | 2.9846 | 81.1569 | 115.3015 | 123.7061 | -123.967 | -123.9532
2610.7188 | 123.8571 | -61.3678 | 62.3383 | -0.29884 | 0.015597 | 0.02089 | 0.010611 | 0.065589 | -0.00097413 | 0.082467 | -58.3694 | 62.2604 | -61.6379 | -61.5463 | 53.8834 | 19.4641 | 5.0354 | 4.5914 | 62.3154 | -61.6425 | -0.27008 | -0.07782 | 2.9984 | -0.17853 | -8.4549 | -0.27466 | -0.022888 | 3.2684 | 66.4032 | 65.9592 | 115.2512 | 123.6282 | 2.9984 | 123.6832 | 80.8319 | -0.27466 | 123.6282 | 2.9984 | 80.8319 | 115.2512 | 123.6832 | -123.9761 | -123.9807
2611.7188 | 123.8251 | -61.3541 | 62.3337 | -0.25307 | 0.016024 | 0.016618 | 0.011465 | 0.059821 | -0.0011877 | 0.080544 | -58.3328 | 62.2467 | -61.6241 | -61.5234 | 53.9429 | 19.5099 | 5.0446 | 4.7241 | 62.3016 | -61.6196 | -0.27008 | -0.086975 | 3.0212 | -0.16937 | -8.3908 | -0.2655 | -0.032043 | 3.2913 | 66.3986 | 66.0782 | 115.2969 | 123.6008 | 3.0212 | 123.6557 | 80.864 | -0.2655 | 123.6008 | 3.0212 | 80.864 | 115.2969 | 123.6557 | -123.9578 | -123.9532
2612.7188 | 123.8113 | -61.3586 | 62.3337 | -0.16914 | 0.017306 | 0.014482 | 0.011892 | 0.062598 | -0.0011877 | 0.080117 | -58.4335 | 62.2879 | -61.6562 | -61.5646 | 53.8879 | 19.693 | 5.1544 | 4.7653 | 62.3291 | -61.6653 | -0.29755 | -0.045776 | 2.9251 | -0.20599 | -8.4457 | -0.3067 | -0.004577 | 3.2227 | 66.5131 | 66.124 | 115.2466 | 123.6465 | 2.9251 | 123.6877 | 81.0516 | -0.3067 | 123.6465 | 2.9251 | 81.0516 | 115.2466 | 123.6877 | -123.9899 | -123.999
2613.7188 | 123.8251 | -61.3953 | 62.2925 | -0.054703 | 0.016878 | 0.016831 | 0.017019 | 0.061957 | 0.00073487 | 0.081613 | -58.3511 | 62.3108 | -61.6425 | -61.5189 | 53.9795 | 19.812 | 4.9255 | 4.6371 | 62.2879 | -61.6516 | -0.24719 | 0.018311 | 3.0441 | -0.1236 | -8.313 | -0.25635 | -0.004577 | 3.2913 | 66.3208 | 66.0324 | 115.3748 | 123.7061 | 3.0441 | 123.6832 | 81.2073 | -0.25635 | 123.7061 | 3.0441 | 81.2073 | 115.3748 | 123.6832 | -123.9349 | -123.9441
2614.7188 | 123.9487 | -61.3495 | 62.2971 | -2.0841 | 0.012606 | 0.017899 | 0.0082608 | 0.064307 | -0.0018285 | 0.080117 | -58.3282 | 62.2696 | -61.6287 | -61.4594 | 53.9383 | 19.8486 | 4.9988 | 4.7607 | 62.2604 | -61.6104 | -0.27924 | -0.027466 | 3.0212 | -0.10986 | -8.3588 | -0.26093 | -0.036621 | 3.3005 | 66.3483 | 66.1102 | 115.2878 | 123.6191 | 3.0212 | 123.6099 | 81.1981 | -0.26093 | 123.6191 | 3.0212 | 81.1981 | 115.2878 | 123.6099 | -123.9258 | -123.9075
2615.7188 | 123.9258 | -61.3358 | 62.3154 | -0.19203 | 0.016024 | 0.019395 | 0.011679 | 0.060675 | 0.0030847 | 0.081185 | -58.287 | 62.2421 | -61.6196 | -61.4914 | 54.0161 | 19.8212 | 5.0308 | 4.7058 | 62.2604 | -61.6241 | -0.28381 | -0.073243 | 3.0487 | -0.15564 | -8.2993 | -0.28839 | -0.054932 | 3.3325 | 66.3666 | 66.0416 | 115.3519 | 123.5779 | 3.0487 | 123.5962 | 81.1569 | -0.28839 | 123.5779 | 3.0487 | 81.1569 | 115.3519 | 123.5962 | -123.9349 | -123.9395
2616.7188 | 123.9029 | -61.3403 | 62.3062 | -0.1844 | 0.01282 | 0.014909 | 0.011038 | 0.061316 | 0.00073487 | 0.081613 | -58.3237 | 62.2147 | -61.6333 | -61.4731 | 53.9108 | 19.5969 | 5.04 | 4.7058 | 62.2742 | -61.6104 | -0.29297 | -0.091552 | 3.0167 | -0.13275 | -8.3954 | -0.27008 | -0.032043 | 3.3096 | 66.3803 | 66.0461 | 115.2512 | 123.555 | 3.0167 | 123.6145 | 80.9372 | -0.27008 | 123.555 | 3.0167 | 80.9372 | 115.2512 | 123.6145 | -123.9395 | -123.9166
2617.7188 | 123.9029 | -61.3495 | 62.2971 | -0.19966 | 0.014529 | 0.012986 | 0.011251 | 0.060248 | 9.4068e-05 | 0.080972 | -58.3054 | 62.2147 | -61.615 | -61.4868 | 53.9383 | 19.6014 | 5.1819 | 4.8294 | 62.2513 | -61.5967 | -0.2655 | -0.082397 | 3.0441 | -0.13733 | -8.3588 | -0.24719 | -0.045776 | 3.3096 | 66.5314 | 66.1789 | 115.2878 | 123.5641 | 3.0441 | 123.6008 | 80.9509 | -0.24719 | 123.5641 | 3.0441 | 80.9509 | 115.2878 | 123.6008 | -123.912 | -123.8937
2618.7188 | 123.8571 | -61.377 | 62.3199 | -0.131 | 0.016024 | 0.017899 | 0.015951 | 0.060248 | -0.00076053 | 0.078622 | -58.3878 | 62.2971 | -61.6287 | -61.5372 | 53.8696 | 19.6701 | 5.0903 | 4.6234 | 62.2833 | -61.6425 | -0.25177 | -0.022888 | 2.9892 | -0.16022 | -8.4503 | -0.2655 | -0.036621 | 3.241 | 66.4673 | 66.0004 | 115.2466 | 123.674 | 2.9892 | 123.6603 | 81.0471 | -0.2655 | 123.674 | 2.9892 | 81.0471 | 115.2466 | 123.6603 | -123.9487 | -123.9624
2619.7188 | 123.8113 | -61.3815 | 62.3291 | -0.22255 | 0.016451 | 0.013841 | 0.012747 | 0.06388 | -0.00033333 | 0.077767 | -58.4015 | 62.2879 | -61.6379 | -61.5555 | 53.746 | 19.6793 | 5.127 | 4.6188 | 62.2925 | -61.6287 | -0.25635 | -0.041199 | 2.98 | -0.17395 | -8.5831 | -0.24719 | -0.036622 | 3.2364 | 66.5085 | 66.0004 | 115.1276 | 123.6694 | 2.98 | 123.674 | 81.0608 | -0.24719 | 123.6694 | 2.98 | 81.0608 | 115.1276 | 123.674 | -123.967 | -123.9578
2620.7188 | 123.8983 | -61.3266 | 62.3062 | -0.23781 | 0.013888 | 0.015977 | 0.010397 | 0.060889 | 0.00030767 | 0.083108 | -58.3511 | 62.2284 | -61.6104 | -61.4777 | 53.8101 | 19.6609 | 5.0858 | 4.7836 | 62.265 | -61.6058 | -0.28381 | -0.077819 | 2.9755 | -0.15106 | -8.4961 | -0.27924 | -0.041198 | 3.2593 | 66.4124 | 66.1102 | 115.1367 | 123.555 | 2.9755 | 123.5916 | 80.9875 | -0.27924 | 123.555 | 2.9755 | 80.9875 | 115.1367 | 123.5916 | -123.9166 | -123.912
2621.7188 | 123.8937 | -61.3541 | 62.3062 | -0.23781 | 0.015383 | 0.015763 | 0.011679 | 0.061957 | 0.0011621 | 0.079904 | -58.3557 | 62.2467 | -61.6333 | -61.5051 | 53.7552 | 19.78 | 5.1819 | 4.7928 | 62.2513 | -61.6104 | -0.27924 | -0.059509 | 2.9984 | -0.15106 | -8.551 | -0.25635 | -0.054931 | 3.2776 | 66.5359 | 66.1469 | 115.1093 | 123.6008 | 2.9984 | 123.6053 | 81.134 | -0.25635 | 123.6008 | 2.9984 | 81.134 | 115.1093 | 123.6053 | -123.9395 | -123.9166
2622.7188 | 123.8388 | -61.3907 | 62.3337 | -0.27596 | 0.015383 | 0.012132 | 0.012747 | 0.061103 | 0.00030767 | 0.079476 | -58.4061 | 62.2742 | -61.6333 | -61.5692 | 53.8559 | 19.9402 | 5.2917 | 4.6921 | 62.2833 | -61.6287 | -0.24262 | -0.059509 | 2.9846 | -0.17853 | -8.4778 | -0.23804 | -0.050354 | 3.2272 | 66.6824 | 66.0828 | 115.2466 | 123.6649 | 2.9846 | 123.674 | 81.3309 | -0.23804 | 123.6649 | 2.9846 | 81.3309 | 115.2466 | 123.674 | -123.967 | -123.9624
2623.7188 | 123.8251 | -61.409 | 62.3154 | -0.0089264 | 0.019656 | 0.021317 | 0.018728 | 0.063025 | 0.00030767 | 0.080758 | -58.3282 | 62.3016 | -61.6516 | -61.5372 | 53.7277 | 19.6838 | 5.1132 | 4.6692 | 62.2833 | -61.6699 | -0.24261 | -0.013733 | 3.0808 | -0.12817 | -8.5876 | -0.26093 | -0.032044 | 3.3234 | 66.5222 | 66.0782 | 115.1367 | 123.7106 | 3.0808 | 123.6923 | 81.0928 | -0.26093 | 123.7106 | 3.0808 | 81.0928 | 115.1367 | 123.6923 | -123.967 | -123.9853
2624.7188 | 123.8113 | -61.3358 | 62.3428 | -0.24544 | 0.01581 | 0.014482 | 0.012106 | 0.063452 | -0.00033333 | 0.083108 | -58.4061 | 62.3016 | -61.6425 | -61.5692 | 53.7735 | 19.6655 | 5.1773 | 4.6326 | 62.3108 | -61.6104 | -0.3067 | -0.041198 | 2.9297 | -0.23346 | -8.5693 | -0.27466 | -0.032043 | 3.2364 | 66.5131 | 65.9683 | 115.1093 | 123.6374 | 2.9297 | 123.6465 | 81.0013 | -0.27466 | 123.6374 | 2.9297 | 81.0013 | 115.1093 | 123.6465 | -123.9853 | -123.9532
2625.7188 | 123.8571 | -61.3724 | 62.3199 | -0.22255 | 0.01581 | 0.015122 | 0.016592 | 0.06388 | 0.0011621 | 0.081826 | -58.3511 | 62.2925 | -61.6333 | -61.5509 | 53.8467 | 19.5786 | 5.0858 | 4.66 | 62.3199 | -61.6104 | -0.26093 | -0.027466 | 3.0212 | -0.17853 | -8.4732 | -0.23804 | 0 | 3.2822 | 66.4581 | 66.0324 | 115.2191 | 123.6649 | 3.0212 | 123.6923 | 80.9509 | -0.23804 | 123.6649 | 3.0212 | 80.9509 | 115.2191 | 123.6923 | -123.9532 | -123.9304
2626.7188 | 123.8663 | -61.377 | 62.3062 | -0.1844 | 0.017306 | 0.013627 | 0.013601 | 0.063452 | -0.00011953 | 0.08204 | -58.3649 | 62.3108 | -61.6379 | -61.5646 | 53.6911 | 19.5328 | 5.04 | 4.6188 | 62.3199 | -61.6241 | -0.26093 | 0.004578 | 3.0121 | -0.18768 | -8.6151 | -0.24719 | 0.013733 | 3.273 | 66.4169 | 65.9958 | 115.0681 | 123.6877 | 3.0121 | 123.6969 | 80.9097 | -0.24719 | 123.6877 | 3.0121 | 80.9097 | 115.0681 | 123.6969 | -123.9441 | -123.9304
2627.7188 | 123.8388 | -61.3953 | 62.3199 | -0.23018 | 0.017519 | 0.014268 | 0.01296 | 0.064948 | 0.0022303 | 0.080972 | -58.3649 | 62.3108 | -61.6516 | -61.5463 | 53.6407 | 19.7388 | 5.0766 | 4.5639 | 62.3199 | -61.6516 | -0.25635 | -0.009155 | 3.0304 | -0.15106 | -8.6792 | -0.25635 | 0 | 3.2867 | 66.4719 | 65.9592 | 115.036 | 123.7061 | 3.0304 | 123.7152 | 81.134 | -0.25635 | 123.7061 | 3.0304 | 81.134 | 115.036 | 123.7152 | -123.9716 | -123.9716
2628.7188 | 123.8571 | -61.3724 | 62.3062 | -0.16914 | 0.016878 | 0.01854 | 0.013815 | 0.065161 | 0.00052127 | 0.083749 | -58.2733 | 62.3108 | -61.6562 | -61.528 | 53.6636 | 19.7433 | 4.9896 | 4.6509 | 62.2833 | -61.6699 | -0.28381 | 0.004578 | 3.0991 | -0.15564 | -8.6426 | -0.29755 | -0.022888 | 3.3829 | 66.362 | 66.0233 | 115.036 | 123.6832 | 3.0991 | 123.6557 | 81.1157 | -0.29755 | 123.6832 | 3.0991 | 81.1157 | 115.036 | 123.6557 | -123.9624 | -123.9761
2629.7188 | 123.8663 | -61.377 | 62.3154 | -0.19966 | 0.017092 | 0.014909 | 0.014456 | 0.065589 | -0.0011877 | 0.081185 | -58.429 | 62.3337 | -61.6699 | -61.5372 | 53.7048 | 19.693 | 5.0949 | 4.7012 | 62.3108 | -61.6425 | -0.29297 | 0.01831 | 2.948 | -0.16022 | -8.6105 | -0.2655 | -0.004578 | 3.241 | 66.4719 | 66.0782 | 115.0818 | 123.7106 | 2.948 | 123.6877 | 81.0699 | -0.2655 | 123.7106 | 2.948 | 81.0699 | 115.0818 | 123.6877 | -123.9853 | -123.9578
2630.7188 | 123.848 | -61.3403 | 62.3062 | -0.062332 | 0.01816 | 0.014268 | 0.015524 | 0.066016 | 0.00030767 | 0.079476 | -58.3008 | 62.3154 | -61.6333 | -61.5326 | 53.6636 | 19.8761 | 5.1041 | 4.7516 | 62.2879 | -61.6425 | -0.29297 | 0.009156 | 3.0396 | -0.19226 | -8.6426 | -0.30212 | -0.01831 | 3.3325 | 66.4444 | 66.0919 | 115.004 | 123.6557 | 3.0396 | 123.6282 | 81.2164 | -0.30212 | 123.6557 | 3.0396 | 81.2164 | 115.004 | 123.6282 | -123.9395 | -123.9487
2631.7188 | 123.8617 | -61.3953 | 62.3154 | -0.08522 | 0.017733 | 0.017045 | 0.014242 | 0.065802 | -0.00076053 | 0.081826 | -58.342 | 62.3291 | -61.6196 | -61.5097 | 53.627 | 19.5831 | 4.8614 | 4.1748 | 62.3062 | -61.647 | -0.2243 | 0.013733 | 3.0533 | -0.11444 | -8.6884 | -0.25177 | -0.009156 | 3.2776 | 66.2567 | 65.5701 | 115.0223 | 123.7244 | 3.0533 | 123.7015 | 80.9784 | -0.25177 | 123.7244 | 3.0533 | 80.9784 | 115.0223 | 123.7015 | -123.9349 | -123.9624
2632.7188 | 123.8113 | -61.3998 | 62.3154 | -0.16151 | 0.018587 | 0.017899 | 0.014242 | 0.066016 | -0.0016149 | 0.082894 | -58.2779 | 62.2971 | -61.6241 | -61.5326 | 53.746 | 19.7617 | 4.9805 | 4.2297 | 62.3154 | -61.6653 | -0.22431 | -0.018311 | 3.1219 | -0.13275 | -8.5693 | -0.2655 | 0 | 3.3463 | 66.3803 | 65.6296 | 115.1459 | 123.6969 | 3.1219 | 123.7152 | 81.1615 | -0.2655 | 123.6969 | 3.1219 | 81.1615 | 115.1459 | 123.7152 | -123.9395 | -123.9807
2633.7188 | 123.88 | -61.3449 | 62.2925 | 0.15129 | 0.017519 | 0.017686 | 0.0067654 | 0.063666 | 0.0024439 | 0.083749 | -58.3878 | 62.2055 | -61.6425 | -61.5875 | 53.6362 | 19.6289 | 4.8157 | 4.2618 | 62.2421 | -61.6287 | -0.29755 | -0.086975 | 2.9572 | -0.24261 | -8.6563 | -0.28381 | -0.050354 | 3.2547 | 66.1606 | 65.6067 | 114.9811 | 123.5504 | 2.9572 | 123.587 | 80.9738 | -0.28381 | 123.5504 | 2.9572 | 80.9738 | 114.9811 | 123.587 | -123.9349 | -123.9212
2634.7188 | 123.8846 | -61.3724 | 62.3154 | -0.19203 | 0.018374 | 0.018327 | 0.01531 | 0.065161 | 0.0015893 | 0.082253 | -58.2687 | 62.3337 | -61.6562 | -61.528 | 53.8696 | 19.5374 | 4.953 | 4.5502 | 62.2375 | -61.702 | -0.28381 | 0.01831 | 3.1036 | -0.15564 | -8.4457 | -0.32959 | -0.07782 | 3.3875 | 66.3254 | 65.9225 | 115.242 | 123.7061 | 3.1036 | 123.6099 | 80.9097 | -0.32959 | 123.7061 | 3.1036 | 80.9097 | 115.242 | 123.6099 | -123.9716 | -124.0173
2635.7188 | 123.8754 | -61.377 | 62.3108 | -0.14626 | 0.019442 | 0.015122 | 0.014669 | 0.066443 | 0.00073487 | 0.082253 | -58.2916 | 62.3291 | -61.6653 | -61.5372 | 53.6179 | 19.8761 | 5.1315 | 4.2664 | 62.2971 | -61.6791 | -0.28839 | 0.018311 | 3.0853 | -0.16022 | -8.6929 | -0.30212 | -0.013733 | 3.3737 | 66.5085 | 65.6433 | 114.9948 | 123.7061 | 3.0853 | 123.674 | 81.2531 | -0.30212 | 123.7061 | 3.0853 | 81.2531 | 114.9948 | 123.674 | -123.9761 | -123.9899
2636.7188 | 123.8434 | -61.3724 | 62.2971 | -0.054703 | 0.018801 | 0.014054 | 0.016165 | 0.064948 | 0.00052127 | 0.081613 | -58.3145 | 62.3154 | -61.6608 | -61.5555 | 53.6636 | 19.7891 | 5.0308 | 4.2297 | 62.2879 | -61.647 | -0.28839 | 0.018311 | 3.0579 | -0.18311 | -8.6334 | -0.27466 | -0.009155 | 3.3463 | 66.4032 | 65.6021 | 115.036 | 123.6877 | 3.0579 | 123.6603 | 81.1615 | -0.27466 | 123.6877 | 3.0579 | 81.1615 | 115.036 | 123.6603 | -123.9578 | -123.9441
2637.7188 | 123.8388 | -61.3724 | 62.2925 | -0.024185 | 0.01816 | 0.015122 | 0.015524 | 0.067298 | 0.0015893 | 0.08204 | -58.3191 | 62.3016 | -61.6562 | -61.5646 | 53.5675 | 19.7983 | 4.921 | 4.1885 | 62.3062 | -61.647 | -0.28381 | 0.009156 | 3.0533 | -0.19226 | -8.725 | -0.27466 | 0.013733 | 3.3371 | 66.2933 | 65.5609 | 114.9399 | 123.674 | 3.0533 | 123.6786 | 81.1707 | -0.27466 | 123.674 | 3.0533 | 81.1707 | 114.9399 | 123.6786 | -123.9487 | -123.9395
2638.7188 | 123.8297 | -61.3998 | 62.2787 | 0.18181 | 0.017733 | 0.013627 | 0.011892 | 0.068793 | 0.0030847 | 0.082467 | -58.429 | 62.2833 | -61.6699 | -61.6196 | 53.5309 | 19.7708 | 5.2094 | 4.8065 | 62.2787 | -61.6928 | -0.27008 | 0.004577 | 2.9709 | -0.21973 | -8.7479 | -0.29297 | 0 | 3.241 | 66.6092 | 66.2064 | 114.9307 | 123.6832 | 2.9709 | 123.6786 | 81.1707 | -0.29297 | 123.6832 | 2.9709 | 81.1707 | 114.9307 | 123.6786 | -123.9487 | -123.9716
2639.7188 | 123.8663 | -61.3861 | 62.2742 | -0.047073 | 0.018801 | 0.020463 | 0.016378 | 0.065802 | 0.0015893 | 0.080544 | -58.374 | 62.3108 | -61.6241 | -61.5463 | 53.6636 | 19.7891 | 5.127 | 4.4861 | 62.3016 | -61.6745 | -0.23804 | 0.036621 | 3.0121 | -0.16022 | -8.6105 | -0.28839 | 0.027466 | 3.2501 | 66.5131 | 65.8722 | 115.0497 | 123.6969 | 3.0121 | 123.6877 | 81.1752 | -0.28839 | 123.6969 | 3.0121 | 81.1752 | 115.0497 | 123.6877 | -123.8983 | -123.9487
2640.7188 | 123.8113 | -61.409 | 62.2925 | 0.059738 | 0.017306 | 0.017259 | 0.013388 | 0.068579 | -0.0011877 | 0.083108 | -58.3191 | 62.3337 | -61.6516 | -61.5967 | 53.5446 | 19.7113 | 5.1224 | 4.2755 | 62.3383 | -61.6791 | -0.24261 | 0.041199 | 3.0899 | -0.18768 | -8.7479 | -0.27008 | 0.045777 | 3.3325 | 66.5314 | 65.6845 | 114.9536 | 123.7427 | 3.0899 | 123.7473 | 81.1203 | -0.27008 | 123.7427 | 3.0899 | 81.1203 | 114.9536 | 123.7473 | -123.9441 | -123.9716
2641.7188 | 123.8159 | -61.377 | 62.2879 | -0.17677 | 0.019869 | 0.018113 | 0.014242 | 0.06623 | -0.00033333 | 0.081185 | -58.2825 | 62.3474 | -61.6333 | -61.5417 | 53.5446 | 19.4778 | 5.0812 | 4.4312 | 62.3062 | -61.6516 | -0.25635 | 0.059509 | 3.0945 | -0.16479 | -8.7433 | -0.27466 | 0.01831 | 3.3508 | 66.4581 | 65.8081 | 114.9216 | 123.7244 | 3.0945 | 123.6832 | 80.8548 | -0.27466 | 123.7244 | 3.0945 | 80.8548 | 114.9216 | 123.6832 | -123.9212 | -123.9395
2642.7188 | 123.8663 | -61.3541 | 62.2879 | -0.2607 | 0.018587 | 0.017686 | 0.014029 | 0.064948 | 0.0013757 | 0.082467 | -58.287 | 62.3337 | -61.6425 | -61.5326 | 53.5492 | 19.5236 | 5.1132 | 4.4083 | 62.3108 | -61.6516 | -0.28839 | 0.045776 | 3.067 | -0.17853 | -8.7387 | -0.29755 | 0.022888 | 3.3554 | 66.4673 | 65.7623 | 114.9033 | 123.6877 | 3.067 | 123.6649 | 80.8777 | -0.29755 | 123.6877 | 3.067 | 80.8777 | 114.9033 | 123.6649 | -123.9304 | -123.9395
2643.7188 | 123.7976 | -61.3861 | 62.2925 | 0.082626 | 0.020724 | 0.019608 | 0.012106 | 0.068366 | 0.00030767 | 0.082894 | -58.2916 | 62.3337 | -61.6562 | -61.6608 | 53.5263 | 19.4641 | 5.2185 | 4.3259 | 62.3062 | -61.6608 | -0.27008 | 0.041199 | 3.0945 | -0.27466 | -8.7662 | -0.27466 | 0.013733 | 3.3646 | 66.6046 | 65.712 | 114.9124 | 123.7198 | 3.0945 | 123.6923 | 80.8502 | -0.27466 | 123.7198 | 3.0945 | 80.8502 | 114.9124 | 123.6923 | -123.9487 | -123.9532
2644.7188 | 123.8663 | -61.3449 | 62.2787 | -0.047073 | 0.017306 | 0.023026 | 0.011679 | 0.065375 | 0.0018031 | 0.082894 | -58.3969 | 62.2925 | -61.647 | -61.5463 | 53.5538 | 19.8669 | 5.2277 | 4.8981 | 62.3016 | -61.6516 | -0.30212 | 0.013732 | 2.948 | -0.20142 | -8.725 | -0.3067 | 0.022888 | 3.2501 | 66.5726 | 66.243 | 114.8987 | 123.6374 | 2.948 | 123.6465 | 81.2119 | -0.3067 | 123.6374 | 2.948 | 81.2119 | 114.8987 | 123.6465 | -123.9258 | -123.9304
2645.7188 | 123.8571 | -61.377 | 62.3154 | -0.10811 | 0.016878 | 0.018113 | 0.013815 | 0.064521 | 0.0045801 | 0.081826 | -58.3099 | 62.3337 | -61.6333 | -61.615 | 53.7552 | 19.4 | 5.2505 | 4.7745 | 62.3154 | -61.6425 | -0.25635 | 0.01831 | 3.067 | -0.23804 | -8.5602 | -0.2655 | 0 | 3.3234 | 66.6275 | 66.1514 | 115.1321 | 123.7106 | 3.067 | 123.6923 | 80.777 | -0.2655 | 123.7106 | 3.067 | 80.777 | 115.1321 | 123.6923 | -123.9487 | -123.9578
2646.7344 | 123.9304 | -61.3403 | 62.2879 | 0.082626 | 0.016665 | 0.013627 | 0.00527 | 0.06388 | -0.00097413 | 0.083108 | -58.4152 | 62.1918 | -61.6425 | -61.5646 | 53.5767 | 19.6243 | 5.1315 | 4.8065 | 62.2971 | -61.615 | -0.30212 | -0.096131 | 2.9251 | -0.2243 | -8.7112 | -0.27466 | 0.009155 | 3.2272 | 66.4719 | 66.1469 | 114.917 | 123.5321 | 2.9251 | 123.6374 | 80.9647 | -0.27466 | 123.5321 | 2.9251 | 80.9647 | 114.917 | 123.6374 | -123.9304 | -123.9029
2647.7188 | 123.8571 | -61.3586 | 62.2971 | -0.047073 | 0.018587 | 0.020036 | 0.016378 | 0.063452 | 0.00094847 | 0.082467 | -58.2962 | 62.3108 | -61.6104 | -61.5463 | 53.5034 | 19.3542 | 5.3238 | 4.7928 | 62.2879 | -61.7065 | -0.25177 | 0.013733 | 3.0624 | -0.18768 | -8.7936 | -0.3479 | -0.009155 | 3.3142 | 66.6824 | 66.1514 | 114.8621 | 123.6694 | 3.0624 | 123.6465 | 80.7129 | -0.3479 | 123.6694 | 3.0624 | 80.7129 | 114.8621 | 123.6465 | -123.9075 | -124.0036
2648.7188 | 123.8113 | -61.3861 | 62.3199 | 0.059738 | 0.018374 | 0.018327 | 0.014883 | 0.064307 | 0.00030767 | 0.079904 | -58.3466 | 62.2925 | -61.6791 | -61.6379 | 53.4576 | 19.3085 | 5.1407 | 4.6143 | 62.2925 | -61.6791 | -0.29297 | -0.027466 | 3.0395 | -0.25177 | -8.8623 | -0.29297 | -0.027466 | 3.3325 | 66.5268 | 66.0004 | 114.8438 | 123.6786 | 3.0395 | 123.6786 | 80.6946 | -0.29297 | 123.6786 | 3.0395 | 80.6946 | 114.8438 | 123.6786 | -123.999 | -123.999
2649.7188 | 123.8571 | -61.3724 | 62.3016 | -0.19203 | 0.019656 | 0.013627 | 0.01296 | 0.064521 | 9.4068e-05 | 0.081399 | -58.2596 | 62.3337 | -61.6333 | -61.528 | 53.5217 | 19.3771 | 5.2414 | 4.7653 | 62.3245 | -61.6562 | -0.26093 | 0.032043 | 3.1128 | -0.15564 | -8.7799 | -0.28381 | 0.022888 | 3.3737 | 66.6138 | 66.1377 | 114.8941 | 123.7061 | 3.1128 | 123.6969 | 80.7495 | -0.28381 | 123.7061 | 3.1128 | 80.7495 | 114.8941 | 123.6969 | -123.9349 | -123.9578
2650.7188 | 123.8937 | -61.3586 | 62.2925 | -0.12337 | 0.018374 | 0.016191 | 0.013815 | 0.065589 | 9.4068e-05 | 0.085244 | -58.3328 | 62.3016 | -61.6425 | -61.6653 | 53.5263 | 19.5969 | 5.2551 | 4.7745 | 62.3016 | -61.6974 | -0.28381 | 0.009156 | 3.0258 | -0.3067 | -8.7662 | -0.33874 | 0.009156 | 3.3096 | 66.6138 | 66.1331 | 114.8849 | 123.6603 | 3.0258 | 123.6603 | 80.9555 | -0.33874 | 123.6603 | 3.0258 | 80.9555 | 114.8849 | 123.6603 | -123.9349 | -123.9899
2651.7188 | 123.9532 | -61.3312 | 62.2513 | 0.13603 | 0.014956 | 0.019181 | 0.0091152 | 0.063452 | 0.00094847 | 0.081826 | -58.4427 | 62.1964 | -61.6425 | -61.5234 | 53.6224 | 19.4458 | 4.953 | 4.5044 | 62.2284 | -61.6104 | -0.31128 | -0.054932 | 2.8885 | -0.19226 | -8.6288 | -0.27924 | -0.022888 | 3.1998 | 66.2842 | 65.8356 | 114.9536 | 123.5275 | 2.8885 | 123.5596 | 80.777 | -0.27924 | 123.5275 | 2.8885 | 80.777 | 114.9536 | 123.5596 | -123.8937 | -123.8617
2652.7188 | 123.8525 | -61.3861 | 62.2879 | -0.21492 | 0.01816 | 0.017472 | 0.014242 | 0.06388 | 0.0022303 | 0.083108 | -58.2092 | 62.3154 | -61.6287 | -61.5417 | 53.5858 | 19.4641 | 5.1453 | 4.4632 | 62.3062 | -61.6791 | -0.24262 | 0.027466 | 3.1769 | -0.15564 | -8.7021 | -0.29297 | 0.01831 | 3.4195 | 66.5314 | 65.8493 | 114.9719 | 123.7015 | 3.1769 | 123.6923 | 80.8502 | -0.29297 | 123.7015 | 3.1769 | 80.8502 | 114.9719 | 123.6923 | -123.9166 | -123.967
2653.7188 | 123.9578 | -61.3358 | 62.233 | 0.1284 | 0.016238 | 0.019395 | 0.010183 | 0.065589 | 0.0020167 | 0.081826 | -58.255 | 62.2147 | -61.647 | -61.528 | 53.5538 | 19.5694 | 4.9118 | 4.4495 | 62.2421 | -61.6425 | -0.31128 | -0.01831 | 3.0807 | -0.19226 | -8.6792 | -0.3067 | 0.009155 | 3.392 | 66.2476 | 65.7852 | 114.8895 | 123.5504 | 3.0807 | 123.5779 | 80.9052 | -0.3067 | 123.5504 | 3.0807 | 80.9052 | 114.8895 | 123.5779 | -123.88 | -123.8754
2654.7188 | 123.8617 | -61.3724 | 62.2925 | -0.062332 | 0.017306 | 0.014268 | 0.016378 | 0.065375 | 0.0015893 | 0.07969 | -58.2504 | 62.2925 | -61.6333 | -61.4136 | 53.7231 | 19.5694 | 5.1315 | 4.3945 | 62.2833 | -61.6791 | -0.26093 | 0 | 3.1219 | -0.041199 | -8.5693 | -0.3067 | -0.009155 | 3.3829 | 66.5039 | 65.7669 | 115.0955 | 123.6649 | 3.1219 | 123.6557 | 80.9418 | -0.3067 | 123.6649 | 3.1219 | 80.9418 | 115.0955 | 123.6557 | -123.9258 | -123.9716
2655.7188 | 123.8892 | -61.3586 | 62.3016 | -0.25307 | 0.015597 | 0.017472 | 0.012106 | 0.065161 | 0.00094847 | 0.081185 | -58.3282 | 62.3383 | -61.6562 | -61.5326 | 53.714 | 19.5877 | 5.1178 | 4.335 | 62.3062 | -61.6333 | -0.29755 | 0.036621 | 3.0304 | -0.17395 | -8.5876 | -0.27466 | 0.004577 | 3.3279 | 66.4764 | 65.6937 | 115.0726 | 123.6969 | 3.0304 | 123.6649 | 80.9464 | -0.27466 | 123.6969 | 3.0304 | 80.9464 | 115.0726 | 123.6649 | -123.9578 | -123.9349
2656.7344 | 123.9304 | -61.3403 | 62.2513 | 0.21233 | 0.017092 | 0.014482 | 0.010397 | 0.065802 | 0.0011621 | 0.080331 | -58.2779 | 62.2101 | -61.6425 | -61.734 | 53.6407 | 19.8624 | 5.0446 | 4.4449 | 62.2604 | -61.615 | -0.30212 | -0.041199 | 3.0624 | -0.39368 | -8.6105 | -0.27466 | 0.009155 | 3.3646 | 66.3849 | 65.7852 | 114.9811 | 123.5504 | 3.0624 | 123.6008 | 81.2027 | -0.27466 | 123.5504 | 3.0624 | 81.2027 | 114.9811 | 123.6008 | -123.8937 | -123.8663
2657.7188 | 123.8434 | -61.3632 | 62.2604 | -0.12337 | 0.019228 | 0.017045 | 0.015738 | 0.064521 | 0.0020167 | 0.082681 | -58.2504 | 62.3154 | -61.6425 | -61.5234 | 53.7231 | 19.5007 | 5.2231 | 4.5868 | 62.2925 | -61.6562 | -0.27924 | 0.054932 | 3.1128 | -0.16022 | -8.5373 | -0.29297 | 0.032043 | 3.392 | 66.5863 | 65.95 | 115.0864 | 123.6786 | 3.1128 | 123.6557 | 80.864 | -0.29297 | 123.6786 | 3.1128 | 80.864 | 115.0864 | 123.6557 | -123.9029 | -123.9166
2658.7188 | 123.8159 | -61.3998 | 62.2879 | 0.21233 | 0.017519 | 0.022386 | 0.014883 | 0.067084 | 0.0020167 | 0.080758 | -58.4106 | 62.265 | -61.7065 | -61.5601 | 53.7231 | 19.4 | 5.5206 | 4.8431 | 62.3062 | -61.6882 | -0.3067 | -0.022888 | 2.9892 | -0.16022 | -8.5648 | -0.28839 | 0.01831 | 3.2959 | 66.9205 | 66.243 | 115.123 | 123.6649 | 2.9892 | 123.7061 | 80.7999 | -0.28839 | 123.6649 | 2.9892 | 80.7999 | 115.123 | 123.7061 | -123.9944 | -123.9761
2659.7188 | 123.8525 | -61.3632 | 62.2925 | -0.22255 | 0.014529 | 0.016191 | 0.013601 | 0.06388 | 0.00030767 | 0.081185 | -58.2733 | 62.3108 | -61.6425 | -61.5417 | 53.6865 | 19.487 | 5.6122 | 4.985 | 62.3245 | -61.6562 | -0.27924 | 0.018311 | 3.0899 | -0.17853 | -8.606 | -0.29297 | 0.032044 | 3.3691 | 66.9754 | 66.3483 | 115.0497 | 123.674 | 3.0899 | 123.6877 | 80.8502 | -0.29297 | 123.674 | 3.0899 | 80.8502 | 115.0497 | 123.6877 | -123.9349 | -123.9487
2660.7188 | 123.8663 | -61.3724 | 62.3016 | -0.1844 | 0.017733 | 0.017899 | 0.012747 | 0.063666 | -0.0016149 | 0.080117 | -58.2275 | 62.3245 | -61.6241 | -61.5509 | 53.8605 | 19.5374 | 5.4565 | 4.8386 | 62.3154 | -61.6562 | -0.25177 | 0.022888 | 3.1448 | -0.17853 | -8.4412 | -0.28381 | 0.013733 | 3.3966 | 66.8289 | 66.2109 | 115.2328 | 123.6969 | 3.1448 | 123.6877 | 80.9097 | -0.28381 | 123.6969 | 3.1448 | 80.9097 | 115.2328 | 123.6877 | -123.9258 | -123.9578
2661.7188 | 123.88 | -61.3678 | 62.2879 | -0.19203 | 0.017519 | 0.01854 | 0.014456 | 0.064948 | -0.0011877 | 0.081185 | -58.2779 | 62.3154 | -61.6196 | -61.5509 | 53.8147 | 19.368 | 5.5161 | 4.9393 | 62.3245 | -61.6791 | -0.25177 | 0.027466 | 3.0899 | -0.1831 | -8.4732 | -0.31128 | 0.036621 | 3.3417 | 66.8838 | 66.3071 | 115.1825 | 123.6832 | 3.0899 | 123.6923 | 80.7358 | -0.31128 | 123.6832 | 3.0899 | 80.7358 | 115.1825 | 123.6923 | -123.9075 | -123.967
2662.7188 | 123.8342 | -61.3907 | 62.3108 | -0.14626 | 0.016024 | 0.013841 | 0.011038 | 0.064734 | 0.0028711 | 0.08204 | -58.3099 | 62.3199 | -61.6425 | -61.5875 | 53.7186 | 19.7937 | 5.5344 | 4.8752 | 62.3611 | -61.6745 | -0.25177 | 0.009155 | 3.0807 | -0.19684 | -8.5922 | -0.28381 | 0.050354 | 3.3325 | 66.925 | 66.2659 | 115.1093 | 123.7106 | 3.0807 | 123.7518 | 81.1844 | -0.28381 | 123.7106 | 3.0807 | 81.1844 | 115.1093 | 123.7518 | -123.9532 | -123.9853
2663.7188 | 123.8434 | -61.3724 | 62.2879 | -0.047073 | 0.016665 | 0.017899 | 0.013174 | 0.064948 | -0.0016149 | 0.082253 | -58.2504 | 62.3108 | -61.6516 | -61.5646 | 53.7643 | 19.6564 | 5.452 | 4.9438 | 62.2833 | -61.6699 | -0.27924 | 0.022888 | 3.1219 | -0.19226 | -8.5236 | -0.29755 | -0.004578 | 3.4012 | 66.8243 | 66.3162 | 115.1367 | 123.6832 | 3.1219 | 123.6557 | 81.0287 | -0.29755 | 123.6832 | 3.1219 | 81.0287 | 115.1367 | 123.6557 | -123.9395 | -123.9578
2664.7188 | 123.8525 | -61.3724 | 62.3291 | -0.11574 | 0.017092 | 0.020463 | 0.011465 | 0.064307 | 9.4068e-05 | 0.083322 | -58.2733 | 62.3108 | -61.6699 | -61.5784 | 53.7186 | 19.606 | 5.4749 | 4.8386 | 62.3383 | -61.6379 | -0.29755 | -0.018311 | 3.0991 | -0.20599 | -8.6105 | -0.2655 | 0.009155 | 3.3966 | 66.8472 | 66.2109 | 115.0909 | 123.6832 | 3.0991 | 123.7106 | 80.9784 | -0.2655 | 123.6832 | 3.0991 | 80.9784 | 115.0909 | 123.7106 | -123.999 | -123.967
2665.7188 | 123.848 | -61.3861 | 62.3108 | -0.22255 | 0.017947 | 0.015977 | 0.010611 | 0.062812 | 0.0013757 | 0.081399 | -58.223 | 62.2925 | -61.647 | -61.5784 | 53.7827 | 19.7662 | 5.4932 | 4.9118 | 62.3108 | -61.647 | -0.26093 | -0.018311 | 3.1631 | -0.19226 | -8.5281 | -0.26093 | 0 | 3.4241 | 66.8793 | 66.2979 | 115.1688 | 123.6786 | 3.1631 | 123.6969 | 81.1523 | -0.26093 | 123.6786 | 3.1631 | 81.1523 | 115.1688 | 123.6969 | -123.9578 | -123.9578
2666.7188 | 123.8159 | -61.3861 | 62.3154 | -0.16151 | 0.016451 | 0.017259 | 0.010611 | 0.064948 | 0.00052127 | 0.081399 | -58.2962 | 62.3154 | -61.6653 | -61.5875 | 53.7369 | 19.8257 | 5.4016 | 4.9347 | 62.3108 | -61.6653 | -0.27924 | 0 | 3.0899 | -0.20142 | -8.5785 | -0.27924 | -0.004578 | 3.3691 | 66.7877 | 66.3208 | 115.123 | 123.7015 | 3.0899 | 123.6969 | 81.2119 | -0.27924 | 123.7015 | 3.0899 | 81.2119 | 115.123 | 123.6969 | -123.9807 | -123.9807
2667.7188 | 123.8709 | -61.3815 | 62.3016 | -0.20729 | 0.017947 | 0.017686 | 0.011679 | 0.065589 | 0.00030767 | 0.083322 | -58.287 | 62.2925 | -61.6562 | -61.5509 | 53.7231 | 19.899 | 5.4794 | 4.9301 | 62.3108 | -61.6653 | -0.27466 | -0.009156 | 3.0945 | -0.16937 | -8.5785 | -0.28381 | 0.009155 | 3.3691 | 66.861 | 66.3116 | 115.1047 | 123.674 | 3.0945 | 123.6923 | 81.2805 | -0.28381 | 123.674 | 3.0945 | 81.2805 | 115.1047 | 123.6923 | -123.9578 | -123.967
2668.7188 | 123.848 | -61.3998 | 62.265 | 0.21233 | 0.01581 | 0.015336 | 0.013174 | 0.065589 | 0.0011621 | 0.081399 | -58.3191 | 62.2925 | -61.6882 | -61.615 | 53.7552 | 19.8166 | 5.3238 | 4.8111 | 62.2833 | -61.6928 | -0.28839 | 0.027465 | 3.0807 | -0.21515 | -8.5098 | -0.29297 | 0.01831 | 3.3691 | 66.7236 | 66.2109 | 115.155 | 123.6923 | 3.0807 | 123.6832 | 81.2164 | -0.29297 | 123.6923 | 3.0807 | 81.2164 | 115.155 | 123.6832 | -123.9532 | -123.9578
2669.7188 | 123.7747 | -61.3678 | 62.2925 | -0.28358 | 0.016238 | 0.016831 | 0.0099698 | 0.063025 | 0.0011621 | 0.079476 | -58.3649 | 62.2833 | -61.6562 | -61.5005 | 53.9841 | 19.931 | 5.3787 | 4.9942 | 62.3062 | -61.647 | -0.28839 | -0.009155 | 3.0029 | -0.13275 | -8.3084 | -0.27924 | 0.013733 | 3.2913 | 66.7465 | 66.362 | 115.3519 | 123.6511 | 3.0029 | 123.674 | 81.2988 | -0.27924 | 123.6511 | 3.0029 | 81.2988 | 115.3519 | 123.674 | -123.9487 | -123.9395
2670.7188 | 123.8251 | -61.3907 | 62.3291 | -0.16914 | 0.016665 | 0.0132 | 0.011679 | 0.064307 | -0.00033333 | 0.080331 | -58.3328 | 62.3154 | -61.647 | -61.5875 | 53.8147 | 20.018 | 5.5664 | 5.0079 | 62.2971 | -61.6928 | -0.25635 | -0.013733 | 3.0579 | -0.19684 | -8.5144 | -0.30212 | -0.032044 | 3.3142 | 66.9571 | 66.3986 | 115.2054 | 123.7061 | 3.0579 | 123.6877 | 81.4087 | -0.30212 | 123.7061 | 3.0579 | 81.4087 | 115.2054 | 123.6877 | -123.9761 | -124.0219
2671.7188 | 123.8617 | -61.3632 | 62.2833 | -0.09285 | 0.019015 | 0.017472 | 0.011892 | 0.063666 | 0.0018031 | 0.082253 | -58.2779 | 62.3108 | -61.647 | -61.5463 | 53.714 | 20.0317 | 5.4932 | 5.0034 | 62.3245 | -61.6562 | -0.28381 | 0.027466 | 3.0853 | -0.18311 | -8.5693 | -0.29297 | 0.041199 | 3.3691 | 66.8564 | 66.3666 | 115.0772 | 123.674 | 3.0853 | 123.6877 | 81.395 | -0.29297 | 123.674 | 3.0853 | 81.395 | 115.0772 | 123.6877 | -123.9304 | -123.9395
2672.7188 | 123.8571 | -61.3632 | 62.3154 | -0.17677 | 0.017306 | 0.012986 | 0.012106 | 0.064734 | 0.00052127 | 0.080331 | -58.3328 | 62.3016 | -61.6379 | -61.5509 | 53.7003 | 19.8441 | 5.3833 | 4.8981 | 62.3291 | -61.6653 | -0.27466 | -0.013733 | 3.0304 | -0.18768 | -8.6151 | -0.30212 | 0.013733 | 3.3051 | 66.7465 | 66.2613 | 115.0635 | 123.6649 | 3.0304 | 123.6923 | 81.2073 | -0.30212 | 123.6649 | 3.0304 | 81.2073 | 115.0635 | 123.6923 | -123.9532 | -123.9807
2673.7188 | 123.7885 | -61.3998 | 62.265 | 0.16655 | 0.018587 | 0.01555 | 0.014883 | 0.064734 | 0.00073487 | 0.080972 | -58.3649 | 62.3016 | -61.6745 | -61.647 | 53.5767 | 19.7067 | 5.3879 | 4.7974 | 62.3199 | -61.6974 | -0.27466 | 0.036621 | 3.035 | -0.24719 | -8.6884 | -0.29755 | 0.054931 | 3.3096 | 66.7877 | 66.1972 | 114.9765 | 123.7015 | 3.035 | 123.7198 | 81.1066 | -0.29755 | 123.7015 | 3.035 | 81.1066 | 114.9765 | 123.7198 | -123.9395 | -123.9624
2674.7188 | 123.8617 | -61.3541 | 62.3154 | -0.10048 | 0.017519 | 0.017472 | 0.013601 | 0.063452 | 0.0013757 | 0.080758 | -58.3054 | 62.3199 | -61.6241 | -61.528 | 53.7231 | 19.8898 | 5.3879 | 4.9347 | 62.3062 | -61.647 | -0.27008 | 0.004577 | 3.0487 | -0.17395 | -8.5922 | -0.29297 | -0.009156 | 3.3188 | 66.7419 | 66.2888 | 115.0772 | 123.674 | 3.0487 | 123.6603 | 81.2439 | -0.29297 | 123.674 | 3.0487 | 81.2439 | 115.0772 | 123.6603 | -123.9395 | -123.9624
2675.7188 | 123.8388 | -61.3724 | 62.2833 | -0.2607 | 0.017092 | 0.016191 | 0.012106 | 0.065802 | 0.0013757 | 0.080972 | -58.3145 | 62.3062 | -61.6333 | -61.5417 | 53.7689 | 19.9219 | 5.3833 | 4.9393 | 62.3062 | -61.6516 | -0.26093 | 0.022888 | 3.0579 | -0.16937 | -8.5144 | -0.27924 | 0.022888 | 3.3188 | 66.7557 | 66.3116 | 115.1413 | 123.6786 | 3.0579 | 123.6786 | 81.2943 | -0.27924 | 123.6786 | 3.0579 | 81.2943 | 115.1413 | 123.6786 | -123.9166 | -123.9349
2676.7188 | 123.8159 | -61.3953 | 62.3199 | 0.3878 | 0.018587 | 0.014909 | 0.0082608 | 0.063666 | 0.0013757 | 0.081826 | -58.2962 | 62.2971 | -61.6699 | -61.5601 | 53.7735 | 19.8624 | 5.4428 | 4.8614 | 62.3474 | -61.6882 | -0.27466 | -0.022888 | 3.0991 | -0.1648 | -8.5464 | -0.29297 | 0.027466 | 3.3737 | 66.8381 | 66.2567 | 115.1688 | 123.6923 | 3.0991 | 123.7427 | 81.2576 | -0.29297 | 123.6923 | 3.0991 | 81.2576 | 115.1688 | 123.7427 | -123.9899 | -124.0082
2677.7188 | 123.8297 | -61.3586 | 62.3016 | -0.17677 | 0.01581 | 0.017686 | 0.010611 | 0.064307 | -0.00033333 | 0.081826 | -58.3191 | 62.3108 | -61.6562 | -61.5784 | 53.7781 | 19.7296 | 5.4016 | 4.8981 | 62.2971 | -61.6699 | -0.29755 | 0.009155 | 3.0396 | -0.21973 | -8.5236 | -0.31128 | -0.004578 | 3.3371 | 66.7603 | 66.2567 | 115.1367 | 123.6694 | 3.0396 | 123.6557 | 81.0883 | -0.31128 | 123.6694 | 3.0396 | 81.0883 | 115.1367 | 123.6557 | -123.9578 | -123.9716
2678.7188 | 123.9075 | -61.3724 | 62.2696 | -0.10048 | 0.017092 | 0.018327 | 0.016378 | 0.06623 | 0.0035121 | 0.080758 | -58.2687 | 62.2925 | -61.6333 | -61.4136 | 53.7506 | 19.931 | 5.3421 | 4.9622 | 62.2879 | -61.6699 | -0.26093 | 0.022888 | 3.1036 | -0.041199 | -8.519 | -0.29755 | 0.018311 | 3.3646 | 66.7145 | 66.3345 | 115.123 | 123.6649 | 3.1036 | 123.6603 | 81.3034 | -0.29755 | 123.6649 | 3.1036 | 81.3034 | 115.123 | 123.6603 | -123.9029 | -123.9395
2679.7188 | 123.8342 | -61.3724 | 62.3291 | 0.013962 | 0.016665 | 0.010423 | 0.010183 | 0.065375 | -0.00011953 | 0.082253 | -58.3328 | 62.2971 | -61.6516 | -61.5829 | 53.6041 | 19.8212 | 5.3604 | 4.9164 | 62.3199 | -61.647 | -0.27924 | -0.032044 | 3.0395 | -0.21057 | -8.725 | -0.27466 | -0.009156 | 3.3188 | 66.7328 | 66.2888 | 114.9765 | 123.6694 | 3.0395 | 123.6923 | 81.1935 | -0.27466 | 123.6694 | 3.0395 | 81.1935 | 114.9765 | 123.6923 | -123.9807 | -123.9761
2680.7188 | 123.8159 | -61.3815 | 62.3337 | -0.23018 | 0.016024 | 0.014054 | 0.0074062 | 0.066016 | -0.00054693 | 0.081613 | -58.3374 | 62.265 | -61.6287 | -61.5692 | 53.6636 | 19.8074 | 5.2963 | 4.9393 | 62.3016 | -61.6196 | -0.24719 | -0.068664 | 3.0441 | -0.18768 | -8.67 | -0.23804 | -0.032043 | 3.2913 | 66.6779 | 66.3208 | 115.0452 | 123.6465 | 3.0441 | 123.6832 | 81.189 | -0.23804 | 123.6465 | 3.0441 | 81.189 | 115.0452 | 123.6832 | -123.9624 | -123.9532
2681.7188 | 123.8113 | -61.377 | 62.3199 | -0.2607 | 0.016024 | 0.015122 | 0.0095424 | 0.064521 | -0.00033333 | 0.079904 | -58.3969 | 62.2742 | -61.6425 | -61.3907 | 53.7506 | 19.487 | 5.3146 | 4.9667 | 62.2925 | -61.6745 | -0.2655 | -0.045776 | 2.98 | -0.013733 | -8.5693 | -0.29755 | -0.027466 | 3.2455 | 66.6916 | 66.3437 | 115.1276 | 123.6511 | 2.98 | 123.6694 | 80.864 | -0.29755 | 123.6511 | 2.98 | 80.864 | 115.1276 | 123.6694 | -123.9624 | -123.9944
2682.7188 | 123.7976 | -61.377 | 62.3108 | -0.20729 | 0.015383 | 0.014695 | 0.011038 | 0.06153 | 0.0011621 | 0.081613 | -58.3374 | 62.2833 | -61.6608 | -61.5692 | 53.5538 | 19.7205 | 5.4337 | 5.0034 | 62.3474 | -61.6608 | -0.28381 | -0.027466 | 3.0396 | -0.19226 | -8.757 | -0.28381 | 0.036621 | 3.3234 | 66.8106 | 66.3803 | 114.9307 | 123.6603 | 3.0396 | 123.7244 | 81.0974 | -0.28381 | 123.6603 | 3.0396 | 81.0974 | 114.9307 | 123.7244 | -123.9716 | -123.9716
2683.7188 | 123.8754 | -61.3586 | 62.3291 | -0.11574 | 0.017092 | 0.017045 | 0.017447 | 0.06388 | -0.00033333 | 0.081826 | -58.2779 | 62.3108 | -61.6608 | -61.5555 | 53.5858 | 19.3222 | 5.4382 | 5.0537 | 62.2925 | -61.6379 | -0.30212 | -0.018311 | 3.0808 | -0.19684 | -8.7433 | -0.27923 | -0.036622 | 3.3829 | 66.7969 | 66.4124 | 114.9445 | 123.6694 | 3.0808 | 123.6511 | 80.6808 | -0.27923 | 123.6694 | 3.0808 | 80.6808 | 114.9445 | 123.6511 | -123.9899 | -123.967
2684.7188 | 123.8434 | -61.3678 | 62.3291 | -0.27596 | 0.014529 | 0.017045 | 0.006979 | 0.06388 | 0.00094847 | 0.082253 | -58.287 | 62.2513 | -61.6241 | -61.5692 | 53.7094 | 19.8395 | 5.3192 | 4.9713 | 62.3108 | -61.6379 | -0.25635 | -0.07782 | 3.0808 | -0.20142 | -8.6197 | -0.27008 | -0.018311 | 3.3371 | 66.687 | 66.3391 | 115.0772 | 123.6191 | 3.0808 | 123.6786 | 81.2073 | -0.27008 | 123.6191 | 3.0808 | 81.2073 | 115.0772 | 123.6786 | -123.9532 | -123.967
2685.7188 | 123.8525 | -61.3495 | 62.3199 | -0.23018 | 0.016665 | 0.012132 | 0.0089016 | 0.062171 | 0.0011621 | 0.08204 | -58.2962 | 62.233 | -61.6104 | -61.5326 | 53.6819 | 19.7891 | 5.2917 | 5.0354 | 62.2833 | -61.6104 | -0.26093 | -0.086975 | 3.0533 | -0.18311 | -8.638 | -0.26093 | -0.036621 | 3.3142 | 66.6412 | 66.3849 | 115.0314 | 123.5825 | 3.0533 | 123.6328 | 81.1386 | -0.26093 | 123.5825 | 3.0533 | 81.1386 | 115.0314 | 123.6328 | -123.9304 | -123.9304
2686.7188 | 123.88 | -61.3449 | 62.3154 | -0.26833 | 0.015383 | 0.016618 | 0.0097562 | 0.060675 | -0.0011877 | 0.082253 | -58.3145 | 62.2421 | -61.6425 | -61.5097 | 53.7094 | 19.8944 | 5.3696 | 5.1361 | 62.2742 | -61.6425 | -0.29755 | -0.073243 | 3.0304 | -0.16479 | -8.606 | -0.29755 | -0.041199 | 3.3279 | 66.7145 | 66.481 | 115.0543 | 123.587 | 3.0304 | 123.6191 | 81.2393 | -0.29755 | 123.587 | 3.0304 | 81.2393 | 115.0543 | 123.6191 | -123.9578 | -123.9578
2687.7188 | 123.8937 | -61.3358 | 62.3108 | -0.23018 | 0.014101 | 0.018113 | 0.0078336 | 0.060248 | -0.00054693 | 0.081399 | -58.2733 | 62.2284 | -61.6287 | -61.496 | 53.6865 | 19.7937 | 5.246 | 4.9896 | 62.265 | -61.6013 | -0.29297 | -0.082397 | 3.0624 | -0.16022 | -8.6243 | -0.2655 | -0.045776 | 3.3554 | 66.5817 | 66.3254 | 115.0223 | 123.5641 | 3.0624 | 123.6008 | 81.1295 | -0.2655 | 123.5641 | 3.0624 | 81.1295 | 115.0223 | 123.6008 | -123.9395 | -123.912
2688.7188 | 123.8617 | -61.3632 | 62.2879 | 0.58617 | 0.018801 | 0.017259 | 0.015524 | 0.063025 | 0.00073487 | 0.081399 | -58.3008 | 62.2879 | -61.6379 | -61.528 | 53.6316 | 19.5786 | 5.2872 | 4.9622 | 62.2833 | -61.6745 | -0.27466 | 0 | 3.0624 | -0.1648 | -8.6563 | -0.31128 | -0.004578 | 3.3371 | 66.6504 | 66.3254 | 114.9948 | 123.6511 | 3.0624 | 123.6465 | 80.9418 | -0.31128 | 123.6511 | 3.0624 | 80.9418 | 114.9948 | 123.6465 | -123.9258 | -123.9624
2689.7188 | 123.8937 | -61.3449 | 62.2971 | -0.24544 | 0.015383 | 0.016191 | 0.011251 | 0.062812 | 9.4068e-05 | 0.080544 | -58.2504 | 62.1964 | -61.6104 | -61.4777 | 53.6728 | 19.8257 | 5.0949 | 4.9576 | 62.2742 | -61.5875 | -0.2655 | -0.10071 | 3.0945 | -0.13275 | -8.6243 | -0.24261 | -0.022888 | 3.36 | 66.4398 | 66.3025 | 115.0177 | 123.5413 | 3.0945 | 123.6191 | 81.1707 | -0.24261 | 123.5413 | 3.0945 | 81.1707 | 115.0177 | 123.6191 | -123.9075 | -123.8846
2690.7188 | 123.9395 | -61.3449 | 62.2833 | 0.74638 | 0.014956 | 0.014482 | 0.010611 | 0.060248 | 0.0018031 | 0.082253 | -58.2184 | 62.1964 | -61.6241 | -61.4685 | 53.7323 | 19.7754 | 5.0629 | 4.9438 | 62.2559 | -61.6196 | -0.27924 | -0.086975 | 3.1265 | -0.1236 | -8.551 | -0.27466 | -0.027466 | 3.4058 | 66.4078 | 66.2888 | 115.0772 | 123.5413 | 3.1265 | 123.6008 | 81.1203 | -0.27466 | 123.5413 | 3.1265 | 81.1203 | 115.0772 | 123.6008 | -123.9075 | -123.9029
2691.7188 | 123.8617 | -61.3586 | 62.3016 | -0.24544 | 0.013888 | 0.016618 | 0.0099698 | 0.058753 | 0.00073487 | 0.082894 | -58.2687 | 62.233 | -61.6241 | -61.496 | 53.6636 | 19.6426 | 5.3741 | 4.9347 | 62.265 | -61.6241 | -0.2655 | -0.068665 | 3.0899 | -0.13733 | -8.638 | -0.2655 | -0.036621 | 3.3554 | 66.7328 | 66.2933 | 115.0223 | 123.5916 | 3.0899 | 123.6237 | 81.0013 | -0.2655 | 123.5916 | 3.0899 | 81.0013 | 115.0223 | 123.6237 | -123.9258 | -123.9258
2692.7188 | 123.912 | -61.3449 | 62.2971 | -0.22255 | 0.013888 | 0.018327 | 0.011038 | 0.059394 | -0.00033333 | 0.081399 | -58.2458 | 62.2147 | -61.6013 | -61.4914 | 53.7827 | 19.6838 | 5.2094 | 4.9164 | 62.2604 | -61.6241 | -0.25635 | -0.082397 | 3.0991 | -0.14648 | -8.5144 | -0.27924 | -0.036621 | 3.3554 | 66.5543 | 66.2613 | 115.1276 | 123.5596 | 3.0991 | 123.6053 | 81.0287 | -0.27924 | 123.5596 | 3.0991 | 81.0287 | 115.1276 | 123.6053 | -123.8983 | -123.9212
2693.7188 | 123.8937 | -61.3403 | 62.2925 | -0.15388 | 0.013888 | 0.010209 | 0.0089016 | 0.060034 | -0.00097413 | 0.079476 | -58.2596 | 62.1872 | -61.6058 | -61.4777 | 53.6774 | 19.7479 | 5.2368 | 4.9988 | 62.2604 | -61.6013 | -0.2655 | -0.10528 | 3.0807 | -0.13733 | -8.6151 | -0.26093 | -0.032043 | 3.3463 | 66.5771 | 66.3391 | 115.0177 | 123.5275 | 3.0807 | 123.6008 | 81.0883 | -0.26093 | 123.5275 | 3.0807 | 81.0883 | 115.0177 | 123.6008 | -123.8983 | -123.8937
2694.7188 | 123.8388 | -61.3586 | 62.3337 | -0.27596 | 0.014742 | 0.013627 | 0.010611 | 0.059394 | 0.00094847 | 0.082253 | -58.3054 | 62.265 | -61.6379 | -61.5417 | 53.7552 | 19.8166 | 5.3284 | 4.8798 | 62.3199 | -61.6653 | -0.27923 | -0.068664 | 3.0533 | -0.1831 | -8.5785 | -0.3067 | -0.013733 | 3.3325 | 66.687 | 66.2384 | 115.1138 | 123.6237 | 3.0533 | 123.6786 | 81.1752 | -0.3067 | 123.6237 | 3.0533 | 81.1752 | 115.1138 | 123.6786 | -123.9716 | -123.999
2695.7188 | 123.8068 | -61.3541 | 62.3337 | -0.21492 | 0.017092 | 0.017686 | 0.012106 | 0.06153 | 0.0013757 | 0.081185 | -58.2413 | 62.2192 | -61.6333 | -61.5326 | 53.7552 | 19.6976 | 5.3329 | 4.9072 | 62.2833 | -61.6241 | -0.27924 | -0.11444 | 3.1128 | -0.17853 | -8.5785 | -0.27008 | -0.050354 | 3.392 | 66.687 | 66.2613 | 115.1093 | 123.5733 | 3.1128 | 123.6374 | 81.0516 | -0.27008 | 123.5733 | 3.1128 | 81.0516 | 115.1093 | 123.6374 | -123.967 | -123.9578
2696.7188 | 123.8388 | -61.377 | 62.3154 | -0.22255 | 0.014742 | 0.012986 | 0.011892 | 0.060034 | -0.00054693 | 0.080758 | -58.2916 | 62.2375 | -61.6379 | -61.5143 | 53.6865 | 19.6655 | 5.3284 | 4.8706 | 62.2742 | -61.615 | -0.26093 | -0.07782 | 3.0853 | -0.13733 | -8.6288 | -0.23804 | -0.041199 | 3.3463 | 66.7053 | 66.2476 | 115.0635 | 123.6145 | 3.0853 | 123.6511 | 81.0425 | -0.23804 | 123.6145 | 3.0853 | 81.0425 | 115.0635 | 123.6511 | -123.9532 | -123.9304
2697.7188 | 123.8297 | -61.3403 | 62.3383 | -0.25307 | 0.016665 | 0.014054 | 0.012533 | 0.059821 | -0.00011953 | 0.081826 | -58.2825 | 62.233 | -61.6104 | -61.5097 | 53.7918 | 19.6701 | 5.3421 | 4.9255 | 62.2559 | -61.6287 | -0.27008 | -0.10529 | 3.0579 | -0.16937 | -8.5464 | -0.28839 | -0.082398 | 3.3279 | 66.6824 | 66.2659 | 115.1321 | 123.5733 | 3.0579 | 123.5962 | 81.0104 | -0.28839 | 123.5733 | 3.0579 | 81.0104 | 115.1321 | 123.5962 | -123.9487 | -123.967
2698.7188 | 123.7976 | -61.3724 | 62.3199 | -0.23018 | 0.018374 | 0.016831 | 0.014883 | 0.060462 | -0.00011953 | 0.080544 | -58.3282 | 62.2742 | -61.6791 | -61.5555 | 53.6819 | 19.5786 | 5.3421 | 4.7974 | 62.3199 | -61.6425 | -0.3067 | -0.045776 | 3.0441 | -0.18311 | -8.638 | -0.27008 | 0 | 3.3508 | 66.7145 | 66.1697 | 115.0543 | 123.6465 | 3.0441 | 123.6923 | 80.9509 | -0.27008 | 123.6465 | 3.0441 | 80.9509 | 115.0543 | 123.6923 | -123.999 | -123.9624
2699.7188 | 123.8892 | -61.3312 | 62.3428 | -0.25307 | 0.017306 | 0.015336 | 0.011892 | 0.060462 | -0.00076053 | 0.081185 | -58.2687 | 62.2467 | -61.6287 | -61.5051 | 53.7689 | 20.0226 | 5.3009 | 4.9072 | 62.2696 | -61.6013 | -0.29755 | -0.09613 | 3.0624 | -0.17395 | -8.5739 | -0.27008 | -0.073242 | 3.36 | 66.6321 | 66.2384 | 115.1001 | 123.5779 | 3.0624 | 123.6008 | 81.3538 | -0.27008 | 123.5779 | 3.0624 | 81.3538 | 115.1001 | 123.6008 | -123.9716 | -123.9441
2700.7188 | 123.8617 | -61.3358 | 62.3154 | -0.2607 | 0.014101 | 0.0099954 | 0.010397 | 0.060462 | -0.0016149 | 0.080117 | -58.2458 | 62.2375 | -61.6287 | -61.4868 | 53.8193 | 19.9539 | 5.3329 | 4.8614 | 62.2559 | -61.6104 | -0.29297 | -0.07782 | 3.0899 | -0.15106 | -8.4961 | -0.27466 | -0.05951 | 3.3829 | 66.6687 | 66.1972 | 115.155 | 123.5733 | 3.0899 | 123.5916 | 81.2897 | -0.27466 | 123.5733 | 3.0899 | 81.2897 | 115.155 | 123.5916 | -123.9441 | -123.9258
2701.7188 | 123.9075 | -61.3449 | 62.3062 | -0.2607 | 0.013888 | 0.017472 | 0.008688 | 0.060889 | -0.00011953 | 0.080331 | -58.2779 | 62.2192 | -61.6104 | -61.4868 | 53.8101 | 19.9127 | 5.3146 | 4.8614 | 62.2604 | -61.6287 | -0.2655 | -0.086975 | 3.067 | -0.14191 | -8.4961 | -0.28381 | -0.045776 | 3.3325 | 66.6595 | 66.2064 | 115.155 | 123.5641 | 3.067 | 123.6053 | 81.2576 | -0.28381 | 123.5641 | 3.067 | 81.2576 | 115.155 | 123.6053 | -123.9166 | -123.9349
2702.7188 | 123.8251 | -61.3815 | 62.3291 | -0.22255 | 0.017306 | 0.013841 | 0.012747 | 0.060462 | -0.00097413 | 0.080331 | -58.3099 | 62.2513 | -61.6516 | -61.5463 | 53.6362 | 19.4916 | 5.4016 | 4.8065 | 62.2787 | -61.6333 | -0.27008 | -0.07782 | 3.0716 | -0.16479 | -8.6929 | -0.25177 | -0.050354 | 3.3417 | 66.7831 | 66.1881 | 115.0177 | 123.6328 | 3.0716 | 123.6603 | 80.8731 | -0.25177 | 123.6328 | 3.0716 | 80.8731 | 115.0177 | 123.6603 | -123.9807 | -123.9624
2703.7188 | 123.848 | -61.3678 | 62.3291 | -0.22255 | 0.019015 | 0.010636 | 0.014029 | 0.062812 | -0.00054693 | 0.080758 | -58.2458 | 62.2971 | -61.6104 | -61.5326 | 53.595 | 19.7342 | 5.4153 | 4.8111 | 62.3016 | -61.6653 | -0.24262 | -0.032044 | 3.1219 | -0.16479 | -8.7341 | -0.29755 | -0.027466 | 3.3646 | 66.7831 | 66.1789 | 114.9628 | 123.6649 | 3.1219 | 123.6694 | 81.102 | -0.29755 | 123.6649 | 3.1219 | 81.102 | 114.9628 | 123.6694 | -123.9395 | -123.9944
2704.7188 | 123.8754 | -61.3358 | 62.2971 | -0.15388 | 0.016665 | 0.016831 | 0.008688 | 0.061957 | -0.00076053 | 0.083322 | -58.2733 | 62.2147 | -61.6379 | -61.4777 | 53.7415 | 19.9081 | 5.2826 | 4.8752 | 62.2513 | -61.5921 | -0.30212 | -0.082397 | 3.0624 | -0.14191 | -8.5556 | -0.25635 | -0.045776 | 3.3646 | 66.6183 | 66.2109 | 115.0772 | 123.5504 | 3.0624 | 123.587 | 81.2439 | -0.25635 | 123.5504 | 3.0624 | 81.2439 | 115.0772 | 123.587 | -123.9349 | -123.8892
2705.7188 | 123.8159 | -61.3632 | 62.3245 | -0.23018 | 0.014742 | 0.012345 | 0.010824 | 0.060034 | 0.0011621 | 0.083108 | -58.2779 | 62.2375 | -61.6287 | -61.5372 | 53.6316 | 19.9997 | 5.3696 | 4.7928 | 62.2925 | -61.6241 | -0.2655 | -0.086975 | 3.0853 | -0.17395 | -8.6929 | -0.26093 | -0.032044 | 3.3508 | 66.7328 | 66.156 | 114.9948 | 123.6008 | 3.0853 | 123.6557 | 81.3629 | -0.26093 | 123.6008 | 3.0853 | 81.3629 | 114.9948 | 123.6557 | -123.9532 | -123.9487
2706.7188 | 123.8159 | -61.3632 | 62.3383 | -0.2607 | 0.015169 | 0.013841 | 0.0097562 | 0.060675 | 0.0018031 | 0.082467 | -58.2458 | 62.233 | -61.6379 | -61.5326 | 53.6453 | 19.7845 | 5.246 | 4.7516 | 62.2879 | -61.6241 | -0.27466 | -0.10529 | 3.1174 | -0.16937 | -8.6929 | -0.26093 | -0.050354 | 3.392 | 66.6092 | 66.1148 | 115.0085 | 123.5962 | 3.1174 | 123.6511 | 81.1478 | -0.26093 | 123.5962 | 3.1174 | 81.1478 | 115.0085 | 123.6511 | -123.9761 | -123.9624
2707.7188 | 123.8297 | -61.3541 | 62.3154 | -0.26833 | 0.015169 | 0.012986 | 0.0093288 | 0.062384 | -0.00054693 | 0.082467 | -58.255 | 62.2375 | -61.6058 | -61.5005 | 53.6545 | 19.4641 | 5.2826 | 4.7653 | 62.2559 | -61.6104 | -0.25177 | -0.07782 | 3.0991 | -0.14648 | -8.6609 | -0.25635 | -0.05951 | 3.3508 | 66.6367 | 66.1194 | 115.0085 | 123.5916 | 3.0991 | 123.6099 | 80.8182 | -0.25635 | 123.5916 | 3.0991 | 80.8182 | 115.0085 | 123.6099 | -123.9212 | -123.9258
2708.7188 | 123.8571 | -61.3861 | 62.3245 | -0.10811 | 0.016451 | 0.019395 | 0.016592 | 0.060675 | 9.4068e-05 | 0.083749 | -58.2733 | 62.3108 | -61.6379 | -61.6562 | 53.4027 | 19.487 | 5.3192 | 4.7241 | 62.2513 | -61.6882 | -0.25177 | -0.013733 | 3.1128 | -0.27008 | -8.9218 | -0.30212 | -0.073242 | 3.3646 | 66.7053 | 66.1102 | 114.7888 | 123.6969 | 3.1128 | 123.6374 | 80.8731 | -0.30212 | 123.6969 | 3.1128 | 80.8731 | 114.7888 | 123.6374 | -123.9624 | -124.0128
2709.7188 | 123.8159 | -61.3724 | 62.3291 | -0.28358 | 0.017306 | 0.013413 | 0.010824 | 0.062812 | 0.0026575 | 0.082467 | -58.3237 | 62.3062 | -61.6608 | -61.5555 | 53.5172 | 19.4366 | 5.3421 | 4.7745 | 62.3062 | -61.615 | -0.28839 | -0.022889 | 3.0487 | -0.18311 | -8.812 | -0.24262 | -0.022889 | 3.3371 | 66.7145 | 66.1469 | 114.8895 | 123.6786 | 3.0487 | 123.6786 | 80.809 | -0.24262 | 123.6786 | 3.0487 | 80.809 | 114.8895 | 123.6786 | -123.9899 | -123.9441
2710.7188 | 123.8937 | -61.3449 | 62.3016 | -0.24544 | 0.015383 | 0.01555 | 0.0091152 | 0.062384 | 0.00030767 | 0.080758 | -58.2642 | 62.2559 | -61.6104 | -61.496 | 53.5995 | 19.4641 | 5.2597 | 4.8843 | 62.2787 | -61.5967 | -0.2655 | -0.045777 | 3.0808 | -0.15106 | -8.7021 | -0.25177 | -0.022888 | 3.3463 | 66.6046 | 66.2292 | 114.9445 | 123.6008 | 3.0808 | 123.6237 | 80.809 | -0.25177 | 123.6008 | 3.0808 | 80.809 | 114.9445 | 123.6237 | -123.912 | -123.8983
2711.7188 | 123.8937 | -61.3449 | 62.2925 | -0.1844 | 0.016451 | 0.013841 | 0.010611 | 0.061316 | 9.4068e-05 | 0.080331 | -58.3054 | 62.233 | -61.5921 | -61.5005 | 53.6591 | 19.7205 | 5.2231 | 4.9118 | 62.2742 | -61.5967 | -0.24719 | -0.059509 | 3.0396 | -0.15564 | -8.6334 | -0.25177 | -0.01831 | 3.2867 | 66.568 | 66.2567 | 115.004 | 123.5779 | 3.0396 | 123.6191 | 81.0654 | -0.25177 | 123.5779 | 3.0396 | 81.0654 | 115.004 | 123.6191 | -123.8846 | -123.8892
2712.7188 | 123.8388 | -61.3724 | 62.3245 | -0.25307 | 0.014956 | 0.013841 | 0.01232 | 0.060675 | 0.0015893 | 0.080117 | -58.3374 | 62.2375 | -61.6333 | -61.5326 | 53.5629 | 19.5145 | 5.3238 | 4.8386 | 62.3062 | -61.647 | -0.26093 | -0.086975 | 3.035 | -0.16022 | -8.7616 | -0.27466 | -0.018311 | 3.2959 | 66.6962 | 66.2109 | 114.9353 | 123.6099 | 3.035 | 123.6786 | 80.8868 | -0.27466 | 123.6099 | 3.035 | 80.8868 | 114.9353 | 123.6786 | -123.9578 | -123.9716
2713.7188 | 123.8571 | -61.3541 | 62.3245 | -0.23018 | 0.01816 | 0.011064 | 0.01531 | 0.062598 | -0.00033333 | 0.082467 | -58.3374 | 62.3016 | -61.6516 | -61.5417 | 53.6133 | 19.6152 | 5.484 | 4.8798 | 62.2879 | -61.647 | -0.29755 | -0.022888 | 3.0167 | -0.18768 | -8.7112 | -0.29297 | -0.036621 | 3.3142 | 66.8381 | 66.2338 | 114.9673 | 123.6557 | 3.0167 | 123.642 | 80.9692 | -0.29297 | 123.6557 | 3.0167 | 80.9692 | 114.9673 | 123.642 | -123.9761 | -123.9716
2714.7188 | 123.848 | -61.3724 | 62.2925 | -0.2607 | 0.013033 | 0.01555 | 0.0089016 | 0.06153 | 0.0011621 | 0.082467 | -58.3328 | 62.2147 | -61.6241 | -61.4914 | 53.7048 | 19.8578 | 5.4428 | 4.9988 | 62.2742 | -61.615 | -0.25177 | -0.077819 | 3.0395 | -0.11902 | -8.5876 | -0.24262 | -0.01831 | 3.2913 | 66.8152 | 66.3712 | 115.0772 | 123.587 | 3.0395 | 123.6465 | 81.2302 | -0.24262 | 123.587 | 3.0395 | 81.2302 | 115.0772 | 123.6465 | -123.9166 | -123.9075
2715.7188 | 123.7885 | -61.3678 | 62.3108 | -0.15388 | 0.016665 | 0.01555 | 0.01296 | 0.062598 | 0.0018031 | 0.081399 | -58.3374 | 62.2787 | -61.615 | -61.5646 | 53.6591 | 19.4504 | 5.4886 | 4.9667 | 62.3016 | -61.615 | -0.24719 | -0.032043 | 3.0304 | -0.19684 | -8.6517 | -0.24719 | -0.009155 | 3.2776 | 66.8564 | 66.3345 | 115.0269 | 123.6465 | 3.0304 | 123.6694 | 80.8182 | -0.24719 | 123.6465 | 3.0304 | 80.8182 | 115.0269 | 123.6694 | -123.9258 | -123.9258
2716.7188 | 123.8297 | -61.3678 | 62.3154 | -0.26833 | 0.016451 | 0.014695 | 0.010183 | 0.059607 | -0.00033333 | 0.081185 | -58.3099 | 62.2833 | -61.6425 | -61.5692 | 53.6362 | 19.6426 | 5.4291 | 4.9118 | 62.2925 | -61.6333 | -0.27466 | -0.032044 | 3.0579 | -0.20142 | -8.6792 | -0.2655 | -0.022889 | 3.3325 | 66.7969 | 66.2796 | 115.004 | 123.6511 | 3.0579 | 123.6603 | 81.0104 | -0.2655 | 123.6511 | 3.0579 | 81.0104 | 115.004 | 123.6603 | -123.9578 | -123.9487
2717.7188 | 123.8113 | -61.3724 | 62.3245 | -0.27596 | 0.017092 | 0.014695 | 0.012106 | 0.059607 | 0.0015893 | 0.081185 | -58.2916 | 62.2696 | -61.6608 | -61.5417 | 53.5995 | 19.5511 | 5.4245 | 5.072 | 62.2879 | -61.6699 | -0.28839 | -0.054932 | 3.0807 | -0.16937 | -8.725 | -0.29755 | -0.036621 | 3.3691 | 66.7969 | 66.4444 | 114.9719 | 123.642 | 3.0807 | 123.6603 | 80.9235 | -0.29755 | 123.642 | 3.0807 | 80.9235 | 114.9719 | 123.6603 | -123.9853 | -123.9944
2718.7188 | 123.8754 | -61.3495 | 62.2833 | -0.10811 | 0.017519 | 0.014695 | 0.016806 | 0.064093 | 0.0013757 | 0.081826 | -58.2779 | 62.3154 | -61.615 | -61.4868 | 53.6636 | 19.4962 | 5.3329 | 4.9805 | 62.2833 | -61.6653 | -0.2655 | 0.032044 | 3.0716 | -0.13733 | -8.6197 | -0.31586 | 0 | 3.3371 | 66.6824 | 66.33 | 115.0131 | 123.6649 | 3.0716 | 123.6328 | 80.8456 | -0.31586 | 123.6649 | 3.0716 | 80.8456 | 115.0131 | 123.6328 | -123.8983 | -123.9487
2719.7188 | 123.7656 | -61.3724 | 62.3337 | -0.23781 | 0.014742 | 0.017045 | 0.011038 | 0.063666 | -0.0018285 | 0.081185 | -58.3191 | 62.2833 | -61.6699 | -61.5601 | 53.6774 | 19.4733 | 5.4932 | 4.9805 | 62.3016 | -61.6379 | -0.29755 | -0.050354 | 3.0533 | -0.18768 | -8.6563 | -0.2655 | -0.032043 | 3.3508 | 66.8655 | 66.3528 | 115.0497 | 123.6557 | 3.0533 | 123.674 | 80.8456 | -0.2655 | 123.6557 | 3.0533 | 80.8456 | 115.0497 | 123.674 | -124.0036 | -123.9716
2720.7188 | 123.8068 | -61.3632 | 62.3291 | -0.23018 | 0.015597 | 0.012986 | 0.014669 | 0.062598 | 0.0011621 | 0.080972 | -58.3282 | 62.2604 | -61.647 | -61.5784 | 53.7003 | 19.8807 | 5.5206 | 5.0491 | 62.2971 | -61.6516 | -0.28381 | -0.068665 | 3.035 | -0.21515 | -8.6288 | -0.28839 | -0.032044 | 3.3188 | 66.8838 | 66.4124 | 115.0635 | 123.6237 | 3.035 | 123.6603 | 81.2439 | -0.28839 | 123.6237 | 3.035 | 81.2439 | 115.0635 | 123.6603 | -123.9761 | -123.9807
2721.7188 | 123.8113 | -61.3953 | 62.3199 | -0.15388 | 0.016451 | 0.015977 | 0.0093288 | 0.062171 | 0.00094847 | 0.080117 | -58.287 | 62.2696 | -61.6562 | -61.5646 | 53.6911 | 19.5969 | 5.4932 | 4.9988 | 62.3016 | -61.6241 | -0.26093 | -0.050354 | 3.1082 | -0.16937 | -8.6288 | -0.22888 | -0.01831 | 3.3691 | 66.8884 | 66.394 | 115.0864 | 123.6649 | 3.1082 | 123.6969 | 80.9921 | -0.22888 | 123.6649 | 3.1082 | 80.9921 | 115.0864 | 123.6969 | -123.9761 | -123.9441
2722.7188 | 123.8068 | -61.3541 | 62.3245 | -0.21492 | 0.015597 | 0.015977 | 0.0097562 | 0.062384 | -0.00011953 | 0.081399 | -58.2962 | 62.233 | -61.647 | -61.5601 | 53.5812 | 19.5831 | 5.4886 | 5.0308 | 62.2833 | -61.6104 | -0.29297 | -0.091553 | 3.0579 | -0.20599 | -8.7433 | -0.25635 | -0.041199 | 3.3508 | 66.8427 | 66.3849 | 114.9353 | 123.587 | 3.0579 | 123.6374 | 80.9372 | -0.25635 | 123.587 | 3.0579 | 80.9372 | 114.9353 | 123.6374 | -123.9716 | -123.9349
2723.7344 | 123.848 | -61.3998 | 62.2787 | -0.0089264 | 0.016665 | 0.016191 | 0.017233 | 0.06153 | 0.0011621 | 0.082894 | -58.3099 | 62.2696 | -61.6608 | -61.6104 | 53.5355 | 19.6884 | 5.4932 | 4.9988 | 62.2559 | -61.6974 | -0.26093 | -0.009156 | 3.0899 | -0.21057 | -8.7433 | -0.29755 | -0.022889 | 3.3508 | 66.893 | 66.3986 | 114.9353 | 123.6694 | 3.0899 | 123.6557 | 81.0883 | -0.29755 | 123.6694 | 3.0899 | 81.0883 | 114.9353 | 123.6557 | -123.9395 | -123.9761
2724.7188 | 123.793 | -61.3632 | 62.3108 | -0.24544 | 0.015597 | 0.016404 | 0.0093288 | 0.06153 | 9.4068e-05 | 0.083322 | -58.3237 | 62.233 | -61.6241 | -61.5372 | 53.5721 | 19.6198 | 5.5847 | 5.2139 | 62.2742 | -61.6333 | -0.26093 | -0.07782 | 3.0396 | -0.17395 | -8.7387 | -0.27008 | -0.036621 | 3.3005 | 66.9479 | 66.5771 | 114.9353 | 123.5962 | 3.0396 | 123.6374 | 80.983 | -0.27008 | 123.5962 | 3.0396 | 80.983 | 114.9353 | 123.6374 | -123.9349 | -123.9441
2725.7188 | 123.8663 | -61.3449 | 62.2971 | -0.2607 | 0.014956 | 0.020249 | 0.0095424 | 0.060462 | -0.00033333 | 0.081399 | -58.2642 | 62.2147 | -61.6379 | -61.5326 | 53.5629 | 19.7342 | 5.5847 | 5.278 | 62.2787 | -61.6333 | -0.29297 | -0.082397 | 3.0808 | -0.18768 | -8.7341 | -0.28839 | -0.01831 | 3.3737 | 66.9296 | 66.6229 | 114.9078 | 123.5596 | 3.0808 | 123.6237 | 81.0791 | -0.28839 | 123.5596 | 3.0808 | 81.0791 | 114.9078 | 123.6237 | -123.9349 | -123.9304
2726.7188 | 123.8846 | -61.377 | 62.3566 | -0.16151 | 0.014742 | 0.015122 | 0.012747 | 0.059394 | 0.00030767 | 0.081613 | -58.2962 | 62.2787 | -61.6608 | -61.5784 | 53.6087 | 19.606 | 5.6076 | 5.2002 | 62.2879 | -61.6562 | -0.28381 | -0.077819 | 3.0807 | -0.20142 | -8.7479 | -0.27924 | -0.068664 | 3.3646 | 66.9846 | 66.5771 | 114.9857 | 123.6557 | 3.0807 | 123.6649 | 80.983 | -0.27924 | 123.6557 | 3.0807 | 80.983 | 114.9857 | 123.6649 | -124.0173 | -124.0128
2727.7188 | 123.8342 | -61.3586 | 62.3337 | -0.27596 | 0.015597 | 0.014054 | 0.012533 | 0.061957 | 0.0015893 | 0.080758 | -58.3008 | 62.265 | -61.6608 | -61.5784 | 53.6453 | 19.6609 | 5.658 | 5.2917 | 62.2696 | -61.6425 | -0.30212 | -0.068664 | 3.0579 | -0.21973 | -8.6884 | -0.28381 | -0.064087 | 3.36 | 67.0166 | 66.6504 | 115.004 | 123.6237 | 3.0579 | 123.6282 | 81.0196 | -0.28381 | 123.6237 | 3.0579 | 81.0196 | 115.004 | 123.6282 | -123.9944 | -123.9761
2728.7188 | 123.8434 | -61.377 | 62.3245 | -0.26833 | 0.017306 | 0.017686 | 0.014669 | 0.060889 | 0.00073487 | 0.080758 | -58.2596 | 62.2925 | -61.6241 | -61.5326 | 53.6041 | 19.5969 | 5.5618 | 5.3421 | 62.2925 | -61.6379 | -0.24719 | -0.032044 | 3.1174 | -0.15564 | -8.7204 | -0.26093 | -0.032044 | 3.3646 | 66.9388 | 66.7191 | 114.9811 | 123.6694 | 3.1174 | 123.6694 | 80.9738 | -0.26093 | 123.6694 | 3.1174 | 80.9738 | 114.9811 | 123.6694 | -123.9487 | -123.9624
2729.7188 | 123.8068 | -61.3907 | 62.3016 | -0.32936 | 0.015169 | 0.01555 | 0.010183 | 0.062812 | 0.00030767 | 0.081185 | -58.2962 | 62.2742 | -61.6653 | -61.5692 | 53.6682 | 19.6335 | 5.6992 | 5.3787 | 62.3154 | -61.647 | -0.27466 | -0.027466 | 3.0945 | -0.17853 | -8.6334 | -0.25635 | 0.013733 | 3.3691 | 67.0898 | 66.7694 | 115.0589 | 123.6649 | 3.0945 | 123.7061 | 81.0242 | -0.25635 | 123.6649 | 3.0945 | 81.0242 | 115.0589 | 123.7061 | -123.967 | -123.9487
2730.7188 | 123.8388 | -61.3449 | 62.2971 | -0.19203 | 0.01581 | 0.014268 | 0.0093288 | 0.062384 | 0.0020167 | 0.083322 | -58.2596 | 62.2467 | -61.6562 | -61.5601 | 53.5767 | 19.4412 | 5.6351 | 5.3192 | 62.2833 | -61.6196 | -0.31128 | -0.050354 | 3.0853 | -0.21515 | -8.7204 | -0.27466 | -0.013733 | 3.3966 | 66.98 | 66.6641 | 114.9216 | 123.5916 | 3.0853 | 123.6282 | 80.7861 | -0.27466 | 123.5916 | 3.0853 | 80.7861 | 114.9216 | 123.6282 | -123.9532 | -123.9166
2731.7188 | 123.8892 | -61.3449 | 62.2833 | -0.16914 | 0.016238 | 0.011918 | 0.011679 | 0.061316 | -0.0014013 | 0.079904 | -58.2138 | 62.2192 | -61.6379 | -61.5005 | 53.6636 | 19.6747 | 5.5664 | 5.5069 | 62.2604 | -61.6196 | -0.29297 | -0.064087 | 3.1311 | -0.15564 | -8.6197 | -0.27466 | -0.022888 | 3.4241 | 66.9113 | 66.8518 | 115.0085 | 123.5641 | 3.1311 | 123.6053 | 81.0196 | -0.27466 | 123.5641 | 3.1311 | 81.0196 | 115.0085 | 123.6053 | -123.9212 | -123.9029
2732.7344 | 123.8205 | -61.3998 | 62.2971 | -0.11574 | 0.017306 | 0.015336 | 0.017019 | 0.063239 | 0.0011621 | 0.081399 | -58.2367 | 62.2696 | -61.6608 | -61.6333 | 53.4164 | 19.2993 | 5.5847 | 5.3558 | 62.233 | -61.6837 | -0.26093 | -0.027466 | 3.1631 | -0.23346 | -8.8806 | -0.28381 | -0.064087 | 3.4241 | 66.9846 | 66.7557 | 114.8163 | 123.6694 | 3.1631 | 123.6328 | 80.6992 | -0.28381 | 123.6694 | 3.1631 | 80.6992 | 114.8163 | 123.6328 | -123.9578 | -123.9807
2733.7188 | 123.8663 | -61.3907 | 62.2879 | -0.13863 | 0.016238 | 0.017899 | 0.014883 | 0.063025 | 0.0018031 | 0.080117 | -58.4106 | 62.2421 | -61.6928 | -61.528 | 53.6179 | 19.8944 | 5.6076 | 5.4932 | 62.2742 | -61.6882 | -0.30212 | -0.045777 | 2.98 | -0.13733 | -8.67 | -0.29755 | -0.013733 | 3.2822 | 66.9983 | 66.8838 | 115.0085 | 123.6328 | 2.98 | 123.6649 | 81.2851 | -0.29755 | 123.6328 | 2.98 | 81.2851 | 115.0085 | 123.6649 | -123.9807 | -123.9761
2734.7188 | 123.848 | -61.377 | 62.3291 | -0.23781 | 0.016024 | 0.011918 | 0.0097562 | 0.061957 | 0.00073487 | 0.08204 | -58.1589 | 62.233 | -61.647 | -61.5234 | 53.5767 | 19.6426 | 5.6671 | 5.4977 | 62.2833 | -61.6058 | -0.27008 | -0.096131 | 3.2181 | -0.14648 | -8.7524 | -0.22888 | -0.045777 | 3.4882 | 67.0441 | 66.8747 | 114.9536 | 123.6099 | 3.2181 | 123.6603 | 81.0196 | -0.22888 | 123.6099 | 3.2181 | 81.0196 | 114.9536 | 123.6603 | -123.9761 | -123.9349
2735.7188 | 123.848 | -61.3449 | 62.2833 | -0.21492 | 0.016665 | 0.015763 | 0.0089016 | 0.063239 | 0.00052127 | 0.083108 | -58.2321 | 62.2375 | -61.6425 | -61.5143 | 53.5767 | 19.6198 | 5.7129 | 5.5984 | 62.2696 | -61.6058 | -0.29755 | -0.045776 | 3.1128 | -0.16937 | -8.7067 | -0.26093 | -0.013733 | 3.4103 | 67.0578 | 66.9434 | 114.9216 | 123.5825 | 3.1128 | 123.6145 | 80.9647 | -0.26093 | 123.5825 | 3.1128 | 80.9647 | 114.9216 | 123.6145 | -123.9258 | -123.8892
2736.7188 | 123.8068 | -61.3907 | 62.3062 | -0.054703 | 0.015597 | 0.014482 | 0.011038 | 0.061316 | 0.0018031 | 0.081826 | -58.2458 | 62.265 | -61.647 | -61.5738 | 53.5034 | 19.4824 | 5.777 | 5.5115 | 62.2833 | -61.6241 | -0.25635 | -0.041198 | 3.1448 | -0.18311 | -8.8028 | -0.23346 | -0.022888 | 3.4012 | 67.1677 | 66.9022 | 114.8941 | 123.6557 | 3.1448 | 123.674 | 80.8731 | -0.23346 | 123.6557 | 3.1448 | 80.8731 | 114.8941 | 123.674 | -123.9532 | -123.9304
2737.7344 | 123.9349 | -61.3586 | 62.2467 | 0.26573 | 0.020296 | 0.019608 | 0.014456 | 0.064734 | 0.0022303 | 0.079904 | -58.1314 | 62.178 | -61.6516 | -61.496 | 53.7872 | 19.7479 | 5.5252 | 5.6992 | 62.2055 | -61.6379 | -0.29297 | -0.068664 | 3.2272 | -0.13733 | -8.4595 | -0.27923 | -0.041199 | 3.5202 | 66.8839 | 67.0578 | 115.1459 | 123.5367 | 3.2272 | 123.5641 | 81.1066 | -0.27923 | 123.5367 | 3.2272 | 81.1066 | 115.1459 | 123.5641 | -123.8983 | -123.8846
2738.7188 | 123.8388 | -61.3861 | 62.2696 | -0.5735 | 0.015383 | 0.014268 | 0.014883 | 0.064307 | 0.00094847 | 0.080331 | -58.1589 | 62.2971 | -61.6287 | -61.5509 | 53.595 | 19.8303 | 5.6351 | 5.4611 | 62.2604 | -61.6837 | -0.24262 | 0.027466 | 3.2272 | -0.16479 | -8.6746 | -0.29755 | -0.009155 | 3.4698 | 67.0212 | 66.8472 | 114.9811 | 123.6832 | 3.2272 | 123.6465 | 81.2164 | -0.29755 | 123.6832 | 3.2272 | 81.2164 | 114.9811 | 123.6465 | -123.8983 | -123.9532
2739.7188 | 123.9212 | -61.3449 | 62.2696 | -0.22255 | 0.016451 | 0.016404 | 0.0091152 | 0.062384 | -0.00011953 | 0.081826 | -58.1955 | 62.2192 | -61.6104 | -61.4914 | 53.7231 | 19.9219 | 5.6442 | 5.6305 | 62.2284 | -61.6058 | -0.2655 | -0.050354 | 3.1494 | -0.14648 | -8.5464 | -0.26093 | -0.041198 | 3.4149 | 66.9891 | 66.9754 | 115.0681 | 123.5641 | 3.1494 | 123.5733 | 81.2668 | -0.26093 | 123.5641 | 3.1494 | 81.2668 | 115.0681 | 123.5733 | -123.88 | -123.8754
2740.7188 | 123.8663 | -61.3586 | 62.3016 | -0.23018 | 0.016451 | 0.011491 | 0.010183 | 0.060034 | -0.00076053 | 0.083322 | -58.2138 | 62.2238 | -61.647 | -61.5326 | 53.6728 | 19.9219 | 5.8319 | 5.571 | 62.2513 | -61.6425 | -0.28839 | -0.07782 | 3.1448 | -0.17395 | -8.6288 | -0.28381 | -0.050354 | 3.4332 | 67.1906 | 66.9296 | 115.0314 | 123.5825 | 3.1448 | 123.6099 | 81.2805 | -0.28381 | 123.5825 | 3.1448 | 81.2805 | 115.0314 | 123.6099 | -123.9487 | -123.9441
2741.7188 | 123.8434 | -61.377 | 62.2833 | -0.26833 | 0.01581 | 0.017259 | 0.0099698 | 0.060889 | -0.00011953 | 0.080331 | -58.2184 | 62.2192 | -61.6196 | -61.5189 | 53.7506 | 19.7937 | 5.7953 | 5.571 | 62.265 | -61.6287 | -0.24262 | -0.064087 | 3.1586 | -0.14191 | -8.5327 | -0.25177 | -0.01831 | 3.4012 | 67.1722 | 66.9479 | 115.1276 | 123.5962 | 3.1586 | 123.642 | 81.1707 | -0.25177 | 123.5962 | 3.1586 | 81.1707 | 115.1276 | 123.642 | -123.9029 | -123.912
2742.7188 | 123.8068 | -61.4182 | 62.2925 | 0.021591 | 0.018587 | 0.019395 | 0.017874 | 0.062171 | -0.0020421 | 0.080117 | -58.255 | 62.2971 | -61.6608 | -61.6013 | 53.595 | 19.7845 | 5.7037 | 5.3604 | 62.2559 | -61.6837 | -0.24262 | 0.004578 | 3.1631 | -0.1831 | -8.6975 | -0.2655 | -0.036621 | 3.4058 | 67.1219 | 66.7786 | 115.0131 | 123.7152 | 3.1631 | 123.674 | 81.2027 | -0.2655 | 123.7152 | 3.1631 | 81.2027 | 115.0131 | 123.674 | -123.9532 | -123.9761
2743.7188 | 123.7885 | -61.4182 | 62.265 | -0.054703 | 0.017519 | 0.020677 | 0.014242 | 0.062171 | -0.0014013 | 0.079049 | -58.2001 | 62.2879 | -61.6516 | -61.5234 | 53.5721 | 19.9036 | 5.6488 | 5.4108 | 62.2971 | -61.6745 | -0.23346 | 0.022888 | 3.2181 | -0.10529 | -8.6929 | -0.25635 | 0.032043 | 3.4515 | 67.067 | 66.8289 | 114.9902 | 123.7061 | 3.2181 | 123.7152 | 81.3217 | -0.25635 | 123.7061 | 3.2181 | 81.3217 | 114.9902 | 123.7152 | -123.9166 | -123.9395
2744.7188 | 123.8205 | -61.3632 | 62.3062 | -0.10048 | 0.016878 | 0.012345 | 0.012533 | 0.062384 | 0.0013757 | 0.080544 | -58.2825 | 62.2513 | -61.6562 | -61.5875 | 53.627 | 19.5648 | 5.7587 | 5.4245 | 62.2971 | -61.6241 | -0.29297 | -0.054931 | 3.0807 | -0.2243 | -8.6792 | -0.26093 | -0.009155 | 3.3737 | 67.1219 | 66.7877 | 114.9902 | 123.6145 | 3.0807 | 123.6603 | 80.928 | -0.26093 | 123.6145 | 3.0807 | 80.928 | 114.9902 | 123.6603 | -123.9624 | -123.9304
2745.7188 | 123.8846 | -61.3586 | 62.2879 | -0.2607 | 0.017092 | 0.017472 | 0.010824 | 0.063239 | 0.00030767 | 0.080758 | -58.2596 | 62.2101 | -61.6196 | -61.5143 | 53.6545 | 19.4 | 5.7312 | 5.603 | 62.2696 | -61.6287 | -0.26093 | -0.07782 | 3.0991 | -0.15564 | -8.6334 | -0.27008 | -0.018311 | 3.36 | 67.0898 | 66.9617 | 115.0131 | 123.5687 | 3.0991 | 123.6282 | 80.7587 | -0.27008 | 123.5687 | 3.0991 | 80.7587 | 115.0131 | 123.6282 | -123.9075 | -123.9166
2746.7188 | 123.88 | -61.3449 | 62.2833 | -0.21492 | 0.013888 | 0.015336 | 0.0093288 | 0.061743 | 0.00052127 | 0.079904 | -58.255 | 62.2101 | -61.6333 | -61.4868 | 53.7186 | 19.5007 | 5.7083 | 5.5573 | 62.265 | -61.6241 | -0.28839 | -0.073242 | 3.0899 | -0.14191 | -8.5648 | -0.27924 | -0.01831 | 3.3783 | 67.0532 | 66.9022 | 115.0635 | 123.555 | 3.0899 | 123.6099 | 80.8456 | -0.27924 | 123.555 | 3.0899 | 80.8456 | 115.0635 | 123.6099 | -123.9166 | -123.9075
2747.7344 | 123.9029 | -61.3678 | 62.233 | 0.21996 | 0.017519 | 0.017045 | 0.013388 | 0.064093 | -0.00097413 | 0.082894 | -58.3328 | 62.2147 | -61.6882 | -61.5555 | 53.5995 | 19.7617 | 5.5344 | 5.4565 | 62.2101 | -61.6562 | -0.32043 | -0.01831 | 3.035 | -0.18768 | -8.6334 | -0.28839 | -0.022888 | 3.3554 | 66.9022 | 66.8243 | 114.9673 | 123.5825 | 3.035 | 123.5779 | 81.1295 | -0.28839 | 123.5825 | 3.035 | 81.1295 | 114.9673 | 123.5779 | -123.9212 | -123.8892
2748.7188 | 123.8022 | -61.4182 | 62.2696 | 0.013962 | 0.017092 | 0.01854 | 0.016378 | 0.063452 | -0.0016149 | 0.080544 | -58.2504 | 62.2742 | -61.6699 | -61.6013 | 53.5217 | 19.7571 | 5.7175 | 5.4291 | 62.2604 | -61.702 | -0.25177 | 0.004578 | 3.1677 | -0.1831 | -8.7479 | -0.28381 | -0.009155 | 3.4195 | 67.1356 | 66.8472 | 114.9399 | 123.6923 | 3.1677 | 123.6786 | 81.1752 | -0.28381 | 123.6923 | 3.1677 | 81.1752 | 114.9399 | 123.6786 | -123.9395 | -123.9716
2749.7188 | 123.8205 | -61.409 | 62.2879 | -0.23018 | 0.015383 | 0.0132 | 0.0084744 | 0.063666 | 0.00094847 | 0.082467 | -58.2504 | 62.2284 | -61.6837 | -61.5738 | 53.4348 | 19.8349 | 5.7541 | 5.484 | 62.3016 | -61.6516 | -0.27466 | -0.059509 | 3.1586 | -0.16479 | -8.8531 | -0.24261 | 0.013733 | 3.4332 | 67.1631 | 66.893 | 114.8438 | 123.6374 | 3.1586 | 123.7106 | 81.2439 | -0.24261 | 123.6374 | 3.1586 | 81.2439 | 114.8438 | 123.7106 | -123.9716 | -123.9395
2750.7188 | 123.8068 | -61.3861 | 62.3291 | -0.3904 | 0.016451 | 0.013841 | 0.014029 | 0.06153 | -0.00011953 | 0.081399 | -58.2779 | 62.3245 | -61.6562 | -61.5829 | 53.5721 | 19.7433 | 5.7999 | 5.4565 | 62.3016 | -61.6608 | -0.27008 | -0.004578 | 3.1082 | -0.19684 | -8.757 | -0.27466 | -0.027466 | 3.3783 | 67.186 | 66.8427 | 114.9582 | 123.7106 | 3.1082 | 123.6877 | 81.1295 | -0.27466 | 123.7106 | 3.1082 | 81.1295 | 114.9582 | 123.6877 | -123.9853 | -123.9899
2751.7188 | 123.8251 | -61.3861 | 62.3108 | -0.35988 | 0.017733 | 0.015122 | 0.012106 | 0.062384 | -0.00054693 | 0.082894 | -58.3054 | 62.2879 | -61.647 | -61.5921 | 53.5767 | 19.8624 | 5.983 | 5.5527 | 62.3062 | -61.6562 | -0.26093 | -0.022888 | 3.0807 | -0.20599 | -8.7341 | -0.27008 | -0.004578 | 3.3417 | 67.3691 | 66.9388 | 114.9628 | 123.674 | 3.0807 | 123.6923 | 81.2485 | -0.27008 | 123.674 | 3.0807 | 81.2485 | 114.9628 | 123.6923 | -123.9578 | -123.967
2752.7188 | 123.8251 | -61.3586 | 62.3383 | -0.1844 | 0.017306 | 0.0132 | 0.010183 | 0.064093 | 0.0013757 | 0.079049 | -58.2916 | 62.2742 | -61.647 | -61.5829 | 53.5904 | 19.7067 | 5.8136 | 5.4886 | 62.3016 | -61.6516 | -0.28839 | -0.064087 | 3.067 | -0.2243 | -8.7479 | -0.29297 | -0.036621 | 3.3554 | 67.1722 | 66.8472 | 114.949 | 123.6328 | 3.067 | 123.6603 | 81.0654 | -0.29297 | 123.6328 | 3.067 | 81.0654 | 114.949 | 123.6603 | -123.9853 | -123.9899
2753.7188 | 123.8342 | -61.3953 | 62.2833 | -0.039444 | 0.02051 | 0.017045 | 0.015097 | 0.064093 | -0.00097413 | 0.08204 | -58.2138 | 62.2925 | -61.6562 | -61.5555 | 53.5583 | 19.9722 | 5.7037 | 5.4657 | 62.2742 | -61.7065 | -0.26093 | 0.009155 | 3.1815 | -0.16022 | -8.725 | -0.31128 | -0.009155 | 3.4424 | 67.099 | 66.861 | 114.9536 | 123.6877 | 3.1815 | 123.6694 | 81.3675 | -0.31128 | 123.6877 | 3.1815 | 81.3675 | 114.9536 | 123.6694 | -123.9395 | -123.9899
2754.7188 | 123.8205 | -61.3953 | 62.3016 | -0.11574 | 0.01816 | 0.012345 | 0.011892 | 0.06388 | 0.0026575 | 0.081185 | -58.2962 | 62.2879 | -61.6791 | -61.5875 | 53.5675 | 20.018 | 5.7632 | 5.4565 | 62.2925 | -61.6425 | -0.28381 | -0.013733 | 3.0991 | -0.19226 | -8.7341 | -0.24719 | -0.009156 | 3.3829 | 67.1585 | 66.8518 | 114.9628 | 123.6832 | 3.0991 | 123.6877 | 81.4133 | -0.24719 | 123.6832 | 3.0991 | 81.4133 | 114.9628 | 123.6877 | -123.9807 | -123.9441
2755.7188 | 123.8251 | -61.3815 | 62.3108 | -0.054703 | 0.015597 | 0.017259 | 0.013174 | 0.063452 | 0.00030767 | 0.080972 | -58.3282 | 62.2925 | -61.6653 | -61.5875 | 53.5721 | 19.9722 | 5.7632 | 5.4565 | 62.3108 | -61.6608 | -0.28381 | -0.018311 | 3.0533 | -0.20599 | -8.7387 | -0.27924 | 0 | 3.3371 | 67.1448 | 66.8381 | 114.9536 | 123.674 | 3.0533 | 123.6923 | 81.3538 | -0.27924 | 123.674 | 3.0533 | 81.3538 | 114.9536 | 123.6923 | -123.9761 | -123.9716
2756.7188 | 123.8022 | -61.3953 | 62.3062 | 0.029221 | 0.018587 | 0.015977 | 0.012106 | 0.063452 | 0.00094847 | 0.080972 | -58.2367 | 62.2833 | -61.6837 | -61.5875 | 53.6133 | 20.0592 | 5.7724 | 5.4382 | 62.3108 | -61.6425 | -0.28839 | -0.022888 | 3.1586 | -0.19226 | -8.6929 | -0.24719 | 0.004578 | 3.447 | 67.1677 | 66.8335 | 115.0085 | 123.6786 | 3.1586 | 123.7061 | 81.4545 | -0.24719 | 123.6786 | 3.1586 | 81.4545 | 115.0085 | 123.7061 | -123.9899 | -123.9487
2757.7188 | 123.8434 | -61.377 | 62.2925 | -0.19966 | 0.017947 | 0.021317 | 0.014669 | 0.064948 | 0.0013757 | 0.080758 | -58.2504 | 62.3108 | -61.6699 | -61.5463 | 53.6453 | 20.0455 | 5.6305 | 5.4108 | 62.2879 | -61.6745 | -0.29297 | 0.018311 | 3.1265 | -0.16937 | -8.6472 | -0.29755 | -0.004577 | 3.4195 | 67.0074 | 66.7877 | 115.0223 | 123.6877 | 3.1265 | 123.6649 | 81.4224 | -0.29755 | 123.6877 | 3.1265 | 81.4224 | 115.0223 | 123.6649 | -123.9624 | -123.967
2758.7188 | 123.7518 | -61.3998 | 62.2742 | 0.14366 | 0.017519 | 0.013841 | 0.015097 | 0.070288 | 0.0015893 | 0.081399 | -58.3603 | 62.2879 | -61.6974 | -61.5189 | 53.8834 | 20.0912 | 5.6808 | 5.4703 | 62.2696 | -61.6974 | -0.29755 | 0.013733 | 3.0396 | -0.11902 | -8.3908 | -0.29755 | -0.004578 | 3.3371 | 67.0807 | 66.8701 | 115.2832 | 123.6877 | 3.0396 | 123.6694 | 81.4911 | -0.29755 | 123.6877 | 3.0396 | 81.4911 | 115.2832 | 123.6694 | -123.9716 | -123.9716
2759.7188 | 123.8525 | -61.4182 | 62.2787 | -0.1844 | 0.018587 | 0.024095 | 0.012747 | 0.063452 | -0.00033333 | 0.081185 | -58.2779 | 62.3154 | -61.6653 | -61.5463 | 53.627 | 20.192 | 5.7724 | 5.5481 | 62.2879 | -61.6791 | -0.24719 | 0.036621 | 3.1403 | -0.12817 | -8.6517 | -0.26093 | 0.009155 | 3.3875 | 67.1906 | 66.9662 | 115.0452 | 123.7335 | 3.1403 | 123.7061 | 81.6101 | -0.26093 | 123.7335 | 3.1403 | 81.6101 | 115.0452 | 123.7061 | -123.9441 | -123.9578
2760.7188 | 123.9349 | -61.3861 | 62.2604 | -0.069961 | 0.019442 | 0.015977 | 0.014029 | 0.065375 | 9.4068e-05 | 0.081399 | -58.2458 | 62.3245 | -61.6425 | -61.5555 | 53.6774 | 20.1324 | 5.6992 | 5.397 | 62.2696 | -61.6653 | -0.25635 | 0.064087 | 3.1403 | -0.16937 | -8.5831 | -0.27924 | 0.009155 | 3.3966 | 67.0853 | 66.7831 | 115.0635 | 123.7106 | 3.1403 | 123.6557 | 81.5186 | -0.27924 | 123.7106 | 3.1403 | 81.5186 | 115.0635 | 123.6557 | -123.9029 | -123.9258
2761.7188 | 123.9258 | -61.409 | 62.2696 | -0.069961 | 0.019228 | 0.014482 | 0.014242 | 0.065375 | 0.0020167 | 0.081613 | -58.2596 | 62.2696 | -61.6516 | -61.5463 | 53.5217 | 20.0775 | 5.7175 | 5.3055 | 62.2604 | -61.6882 | -0.24261 | 0 | 3.1494 | -0.13733 | -8.7479 | -0.27923 | -0.009155 | 3.392 | 67.1265 | 66.7145 | 114.9307 | 123.6786 | 3.1494 | 123.6694 | 81.4865 | -0.27923 | 123.6786 | 3.1494 | 81.4865 | 114.9307 | 123.6694 | -123.9212 | -123.9578
2762.7188 | 123.8342 | -61.409 | 62.2787 | -0.12337 | 0.017306 | 0.018327 | 0.014456 | 0.067298 | -0.00033333 | 0.080972 | -58.1955 | 62.2833 | -61.6608 | -61.5555 | 53.476 | 20.1828 | 5.6625 | 5.2414 | 62.2559 | -61.6882 | -0.25177 | 0.004577 | 3.2135 | -0.14648 | -8.8028 | -0.27923 | -0.022889 | 3.4653 | 67.0715 | 66.6504 | 114.8849 | 123.6923 | 3.2135 | 123.6649 | 81.5918 | -0.27923 | 123.6923 | 3.2135 | 81.5918 | 114.8849 | 123.6649 | -123.9395 | -123.967
2763.7188 | 123.8251 | -61.3953 | 62.2238 | 0.17418 | 0.017519 | 0.020463 | 0.012533 | 0.064521 | 0.0013757 | 0.083108 | -58.4152 | 62.2696 | -61.6928 | -61.615 | 53.5309 | 20.0867 | 5.69 | 5.4703 | 62.2513 | -61.7065 | -0.29755 | 0.045776 | 2.98 | -0.21973 | -8.6929 | -0.31128 | 0.027466 | 3.2776 | 67.0853 | 66.8655 | 114.9261 | 123.6649 | 2.98 | 123.6465 | 81.4819 | -0.31128 | 123.6649 | 2.98 | 81.4819 | 114.9261 | 123.6465 | -123.9166 | -123.9304
2764.7188 | 123.8342 | -61.3907 | 62.2787 | -0.054703 | 0.017947 | 0.016831 | 0.013815 | 0.064307 | -0.00011953 | 0.080117 | -58.2825 | 62.3062 | -61.6653 | -61.5738 | 53.54 | 20.0272 | 5.722 | 5.4382 | 62.2787 | -61.6837 | -0.27466 | 0.027465 | 3.1082 | -0.18311 | -8.7387 | -0.29297 | 0 | 3.3829 | 67.1127 | 66.8289 | 114.9307 | 123.6969 | 3.1082 | 123.6694 | 81.4178 | -0.29297 | 123.6969 | 3.1082 | 81.4178 | 114.9307 | 123.6694 | -123.9441 | -123.9624
2765.7188 | 123.848 | -61.3907 | 62.2696 | -0.054703 | 0.017519 | 0.018968 | 0.014456 | 0.065589 | -0.0020421 | 0.082681 | -58.2733 | 62.2925 | -61.6516 | -61.5875 | 53.4027 | 20.0317 | 5.7724 | 5.5069 | 62.2742 | -61.7065 | -0.26093 | 0.022888 | 3.1174 | -0.19684 | -8.8669 | -0.31586 | 0.004578 | 3.3783 | 67.1631 | 66.8976 | 114.7934 | 123.6832 | 3.1174 | 123.6649 | 81.4224 | -0.31586 | 123.6832 | 3.1174 | 81.4224 | 114.7934 | 123.6649 | -123.9212 | -123.9761
2766.7188 | 123.88 | -61.3861 | 62.2742 | 0.013962 | 0.019869 | 0.017045 | 0.011679 | 0.06623 | -0.0041785 | 0.081613 | -58.3099 | 62.3016 | -61.6653 | -61.6791 | 53.5446 | 20.0638 | 5.6717 | 5.5344 | 62.3016 | -61.6837 | -0.27924 | 0.027466 | 3.0762 | -0.29297 | -8.7296 | -0.29755 | 0.027466 | 3.3554 | 67.0578 | 66.9205 | 114.9307 | 123.6877 | 3.0762 | 123.6877 | 81.4499 | -0.29755 | 123.6877 | 3.0762 | 81.4499 | 114.9307 | 123.6877 | -123.9395 | -123.9578
2767.7188 | 123.8525 | -61.3815 | 62.265 | -0.069961 | 0.018801 | 0.019395 | 0.014669 | 0.067939 | -0.00076053 | 0.078835 | -58.2184 | 62.3154 | -61.6379 | -61.5234 | 53.2516 | 19.9402 | 5.7129 | 5.5069 | 62.2787 | -61.6745 | -0.25635 | 0.050354 | 3.1631 | -0.14191 | -9.0134 | -0.29297 | 0.013733 | 3.4195 | 67.0944 | 66.8884 | 114.6332 | 123.6969 | 3.1631 | 123.6603 | 81.3217 | -0.29297 | 123.6969 | 3.1631 | 81.3217 | 114.6332 | 123.6603 | -123.9029 | -123.9395
2768.7188 | 123.7839 | -61.4136 | 62.2833 | 0.090256 | 0.017306 | 0.014482 | 0.014242 | 0.06623 | 0.0020167 | 0.082894 | -58.3557 | 62.3154 | -61.6699 | -61.6287 | 53.3524 | 19.8349 | 5.7175 | 5.4108 | 62.2742 | -61.7203 | -0.25635 | 0.032044 | 3.0579 | -0.21515 | -8.931 | -0.3067 | -0.009155 | 3.3142 | 67.131 | 66.8243 | 114.7659 | 123.7289 | 3.0579 | 123.6877 | 81.2485 | -0.3067 | 123.7289 | 3.0579 | 81.2485 | 114.7659 | 123.6877 | -123.9532 | -124.0036
2769.7188 | 123.8434 | -61.3586 | 62.2787 | -0.08522 | 0.017092 | 0.021531 | 0.0099698 | 0.065161 | 0.00052127 | 0.080117 | -58.3099 | 62.2925 | -61.6882 | -61.5189 | 53.4943 | 19.9585 | 5.6763 | 5.5298 | 62.2742 | -61.6928 | -0.32959 | 0.013732 | 3.0487 | -0.16022 | -8.7845 | -0.33417 | -0.004578 | 3.3783 | 67.0349 | 66.8884 | 114.8529 | 123.6511 | 3.0487 | 123.6328 | 81.3171 | -0.33417 | 123.6511 | 3.0487 | 81.3171 | 114.8529 | 123.6328 | -123.967 | -123.9716
2770.7188 | 123.8251 | -61.377 | 62.2742 | -0.054703 | 0.017947 | 0.01854 | 0.011465 | 0.068366 | 0.0015893 | 0.083535 | -58.4839 | 62.2467 | -61.6974 | -61.5463 | 53.4393 | 20.0912 | 5.7678 | 5.5984 | 62.2742 | -61.6791 | -0.32043 | -0.027466 | 2.8931 | -0.16937 | -8.8348 | -0.30212 | 0 | 3.2135 | 67.1448 | 66.9754 | 114.8163 | 123.6237 | 2.8931 | 123.6511 | 81.4682 | -0.30212 | 123.6237 | 2.8931 | 81.4682 | 114.8163 | 123.6511 | -123.9716 | -123.9532
2771.7188 | 123.8022 | -61.3907 | 62.2787 | -0.031814 | 0.019656 | 0.015977 | 0.016378 | 0.068152 | 0.0013757 | 0.082253 | -58.0536 | 62.2925 | -61.6379 | -61.5921 | 53.3386 | 19.7525 | 5.7129 | 5.484 | 62.2971 | -61.6882 | -0.24719 | 0.013732 | 3.3371 | -0.20142 | -8.9401 | -0.29755 | 0.01831 | 3.5843 | 67.1036 | 66.8747 | 114.7293 | 123.6832 | 3.3371 | 123.6877 | 81.1432 | -0.29755 | 123.6832 | 3.3371 | 81.1432 | 114.7293 | 123.6877 | -123.9166 | -123.967
2772.7188 | 123.8205 | -61.3998 | 62.2604 | -0.016556 | 0.017733 | 0.019181 | 0.011679 | 0.067084 | 0.0018031 | 0.083535 | -58.2779 | 62.2604 | -61.6745 | -61.6104 | 53.3661 | 20.0272 | 5.7541 | 5.4657 | 62.2742 | -61.6791 | -0.27466 | 0 | 3.1219 | -0.21057 | -8.8943 | -0.27924 | 0.013733 | 3.3966 | 67.1539 | 66.8655 | 114.7659 | 123.6603 | 3.1219 | 123.674 | 81.427 | -0.27924 | 123.6603 | 3.1219 | 81.427 | 114.7659 | 123.674 | -123.9349 | -123.9395
2773.7188 | 123.793 | -61.3998 | 62.2787 | 0.013962 | 0.019442 | 0.019181 | 0.013601 | 0.067298 | 0.00073487 | 0.081826 | -58.3099 | 62.2879 | -61.6837 | -61.6425 | 53.3386 | 20.0363 | 5.7816 | 5.4291 | 62.2742 | -61.7065 | -0.28381 | 0.009155 | 3.0899 | -0.24262 | -8.9401 | -0.3067 | -0.004578 | 3.3737 | 67.1814 | 66.8289 | 114.7385 | 123.6877 | 3.0899 | 123.674 | 81.4362 | -0.3067 | 123.6877 | 3.0899 | 81.4362 | 114.7385 | 123.674 | -123.9624 | -123.9853
2774.7188 | 123.8251 | -61.3998 | 62.2833 | 0.03685 | 0.017733 | 0.017686 | 0.013815 | 0.063666 | 0.0020167 | 0.08204 | -58.2138 | 62.2925 | -61.6653 | -61.6058 | 53.4164 | 20.1004 | 5.7632 | 5.4886 | 62.2742 | -61.6745 | -0.2655 | 0.009155 | 3.186 | -0.20599 | -8.8669 | -0.27466 | -0.009155 | 3.4515 | 67.1631 | 66.8884 | 114.8163 | 123.6923 | 3.186 | 123.674 | 81.5002 | -0.27466 | 123.6923 | 3.186 | 81.5002 | 114.8163 | 123.674 | -123.9487 | -123.9578
2775.7188 | 123.8205 | -61.377 | 62.265 | -0.0089264 | 0.019869 | 0.020249 | 0.011892 | 0.067725 | 0.00094847 | 0.08204 | -58.2779 | 62.2925 | -61.647 | -61.6058 | 53.3981 | 20.0363 | 5.6946 | 5.4382 | 62.2971 | -61.6882 | -0.27008 | 0.027465 | 3.0991 | -0.22888 | -8.8669 | -0.31128 | 0.032043 | 3.3691 | 67.0715 | 66.8152 | 114.7751 | 123.6694 | 3.0991 | 123.674 | 81.4133 | -0.31128 | 123.6694 | 3.0991 | 81.4133 | 114.7751 | 123.674 | -123.912 | -123.9532
2776.7188 | 123.8297 | -61.3815 | 62.2696 | 0.029221 | 0.018374 | 0.020036 | 0.01296 | 0.06623 | 0.00073487 | 0.080972 | -58.2458 | 62.3199 | -61.6745 | -61.5875 | 53.3936 | 19.9219 | 5.658 | 5.3787 | 62.3062 | -61.6882 | -0.29297 | 0.050354 | 3.1357 | -0.20599 | -8.876 | -0.3067 | 0.036621 | 3.4287 | 67.0395 | 66.7603 | 114.7751 | 123.7015 | 3.1357 | 123.6877 | 81.3034 | -0.3067 | 123.7015 | 3.1357 | 81.3034 | 114.7751 | 123.6877 | -123.9441 | -123.9578
2777.7188 | 123.8022 | -61.4044 | 62.2833 | -0.031814 | 0.018587 | 0.020036 | 0.013174 | 0.065375 | 0.00094847 | 0.08204 | -58.2779 | 62.2925 | -61.6562 | -61.6058 | 53.4256 | 19.9219 | 5.6946 | 5.4016 | 62.2879 | -61.702 | -0.25177 | 0.009155 | 3.1265 | -0.20142 | -8.8577 | -0.29755 | 0.004578 | 3.3783 | 67.099 | 66.806 | 114.83 | 123.6969 | 3.1265 | 123.6923 | 81.3263 | -0.29755 | 123.6969 | 3.1265 | 81.3263 | 114.83 | 123.6923 | -123.9395 | -123.9853
2778.7188 | 123.912 | -61.3541 | 62.2192 | -0.062332 | 0.014956 | 0.014695 | 0.0071926 | 0.067725 | 0.0015893 | 0.082681 | -58.2413 | 62.1826 | -61.6653 | -61.5417 | 53.5446 | 20.2011 | 5.4932 | 5.5435 | 62.2375 | -61.647 | -0.31128 | -0.036621 | 3.1128 | -0.18768 | -8.6746 | -0.29297 | 0.018311 | 3.4241 | 66.8472 | 66.8976 | 114.8987 | 123.5367 | 3.1128 | 123.5916 | 81.5552 | -0.29297 | 123.5367 | 3.1128 | 81.5552 | 114.8987 | 123.5916 | -123.8846 | -123.8663
2779.7188 | 123.8342 | -61.3861 | 62.2833 | -0.0012969 | 0.017733 | 0.016191 | 0.015524 | 0.062384 | 0.0013757 | 0.083322 | -58.2367 | 62.3245 | -61.6608 | -61.5784 | 53.4256 | 20.1645 | 5.7266 | 5.4291 | 62.2696 | -61.7065 | -0.27466 | 0.041199 | 3.1494 | -0.19226 | -8.8577 | -0.32044 | -0.013733 | 3.4241 | 67.1127 | 66.8152 | 114.8117 | 123.7106 | 3.1494 | 123.6557 | 81.5506 | -0.32044 | 123.7106 | 3.1494 | 81.5506 | 114.8117 | 123.6557 | -123.9441 | -123.9899
2780.7188 | 123.8342 | -61.4136 | 62.265 | -0.016556 | 0.018587 | 0.016404 | 0.01531 | 0.06687 | 0.0022303 | 0.083322 | -58.2687 | 62.3016 | -61.647 | -61.5738 | 53.4851 | 19.9677 | 5.7175 | 5.4291 | 62.3016 | -61.6928 | -0.23346 | 0.036621 | 3.1448 | -0.16022 | -8.7799 | -0.27924 | 0.036621 | 3.3783 | 67.131 | 66.8427 | 114.8987 | 123.7152 | 3.1448 | 123.7152 | 81.3812 | -0.27924 | 123.7152 | 3.1448 | 81.3812 | 114.8987 | 123.7152 | -123.912 | -123.9578
2781.7188 | 123.7839 | -61.3998 | 62.2742 | 0.052109 | 0.017306 | 0.016831 | 0.013601 | 0.066657 | 0.0015893 | 0.081613 | -58.2687 | 62.2879 | -61.6745 | -61.615 | 53.5355 | 20.1279 | 5.8502 | 5.452 | 62.2787 | -61.7294 | -0.27466 | 0.013733 | 3.1311 | -0.21515 | -8.7387 | -0.32959 | 0.004578 | 3.4058 | 67.2501 | 66.8518 | 114.9353 | 123.6877 | 3.1311 | 123.6786 | 81.5277 | -0.32959 | 123.6877 | 3.1311 | 81.5277 | 114.9353 | 123.6786 | -123.9487 | -124.0036
2782.7188 | 123.793 | -61.409 | 62.2742 | 0.0063326 | 0.017733 | 0.022172 | 0.015097 | 0.066016 | 9.4068e-05 | 0.083962 | -58.2733 | 62.2879 | -61.6699 | -61.615 | 53.5172 | 20.05 | 5.8502 | 5.452 | 62.3062 | -61.6974 | -0.26093 | 0.013733 | 3.1357 | -0.20599 | -8.757 | -0.28839 | 0.032043 | 3.3966 | 67.2592 | 66.861 | 114.9261 | 123.6969 | 3.1357 | 123.7152 | 81.459 | -0.28839 | 123.6969 | 3.1357 | 81.459 | 114.9261 | 123.7152 | -123.9441 | -123.9716
2783.7188 | 123.8068 | -61.3998 | 62.2879 | 0.0063326 | 0.021364 | 0.018754 | 0.014029 | 0.066443 | 0.0011621 | 0.080972 | -58.223 | 62.3016 | -61.6882 | -61.615 | 53.5812 | 20.1004 | 5.7999 | 5.484 | 62.2879 | -61.6882 | -0.28839 | 0.013733 | 3.1769 | -0.21515 | -8.7067 | -0.28839 | 0 | 3.4653 | 67.1997 | 66.8838 | 114.9811 | 123.7015 | 3.1769 | 123.6877 | 81.5002 | -0.28839 | 123.7015 | 3.1769 | 81.5002 | 114.9811 | 123.6877 | -123.9761 | -123.9761
2784.7188 | 123.7656 | -61.4227 | 62.2787 | 0.097885 | 0.016451 | 0.020036 | 0.014242 | 0.066657 | 9.4068e-05 | 0.082467 | -58.2916 | 62.3016 | -61.6791 | -61.6608 | 53.5126 | 20.0317 | 5.8044 | 5.3879 | 62.2925 | -61.7203 | -0.25635 | 0.022888 | 3.1311 | -0.23804 | -8.7662 | -0.29755 | 0.013732 | 3.3875 | 67.2272 | 66.8106 | 114.9353 | 123.7244 | 3.1311 | 123.7152 | 81.4545 | -0.29755 | 123.7244 | 3.1311 | 81.4545 | 114.9353 | 123.7152 | -123.9578 | -123.999
2785.7188 | 123.793 | -61.4273 | 62.265 | 0.082626 | 0.017519 | 0.019608 | 0.014029 | 0.064948 | 0.00052127 | 0.080117 | -58.2733 | 62.2833 | -61.6699 | -61.6425 | 53.5629 | 20.0729 | 5.7999 | 5.3879 | 62.2925 | -61.734 | -0.24262 | 0.01831 | 3.154 | -0.21515 | -8.7021 | -0.3067 | 0.027465 | 3.3966 | 67.2272 | 66.8152 | 114.9902 | 123.7106 | 3.154 | 123.7198 | 81.5002 | -0.3067 | 123.7106 | 3.154 | 81.5002 | 114.9902 | 123.7198 | -123.9349 | -123.999
2786.7188 | 123.8022 | -61.409 | 62.2696 | -0.024185 | 0.018374 | 0.018754 | 0.014456 | 0.06687 | 0.00030767 | 0.081399 | -58.2321 | 62.2925 | -61.647 | -61.5784 | 53.6041 | 20.2423 | 5.7266 | 5.4153 | 62.3016 | -61.7294 | -0.23804 | 0.022888 | 3.1769 | -0.16937 | -8.6655 | -0.32043 | 0.032044 | 3.4149 | 67.1356 | 66.8243 | 115.0131 | 123.7015 | 3.1769 | 123.7106 | 81.6513 | -0.32043 | 123.7015 | 3.1769 | 81.6513 | 115.0131 | 123.7106 | -123.9166 | -123.999
2787.7188 | 123.848 | -61.3907 | 62.2696 | -0.031814 | 0.01816 | 0.016191 | 0.01296 | 0.066443 | 0.00052127 | 0.084603 | -58.2367 | 62.3016 | -61.6516 | -61.5601 | 53.5583 | 19.9814 | 5.7816 | 5.4886 | 62.2971 | -61.6745 | -0.26093 | 0.032044 | 3.154 | -0.16937 | -8.7112 | -0.28381 | 0.027466 | 3.4149 | 67.1722 | 66.8793 | 114.949 | 123.6923 | 3.154 | 123.6877 | 81.3721 | -0.28381 | 123.6923 | 3.154 | 81.3721 | 114.949 | 123.6877 | -123.9212 | -123.9441
2788.7188 | 123.9166 | -61.3861 | 62.2375 | 0.21233 | 0.017947 | 0.013413 | 0.0099698 | 0.065161 | 0.00030767 | 0.083322 | -58.3008 | 62.2101 | -61.6882 | -61.5646 | 53.6499 | 20.0409 | 5.6488 | 5.5389 | 62.233 | -61.6745 | -0.30212 | -0.027466 | 3.0853 | -0.17853 | -8.5876 | -0.28839 | -0.004578 | 3.3875 | 67.0349 | 66.925 | 115.036 | 123.5962 | 3.0853 | 123.6191 | 81.427 | -0.28839 | 123.5962 | 3.0853 | 81.427 | 115.036 | 123.6191 | -123.9258 | -123.912
2789.7188 | 123.8342 | -61.4136 | 62.2696 | 0.021591 | 0.018587 | 0.018754 | 0.013388 | 0.064734 | 0.0013757 | 0.081826 | -58.2825 | 62.2971 | -61.6837 | -61.6104 | 53.5583 | 20.05 | 5.8823 | 5.4932 | 62.2787 | -61.7157 | -0.27008 | 0.027466 | 3.1311 | -0.19684 | -8.7112 | -0.30212 | 0.009156 | 3.4012 | 67.2958 | 66.9067 | 114.9719 | 123.7106 | 3.1311 | 123.6923 | 81.4636 | -0.30212 | 123.7106 | 3.1311 | 81.4636 | 114.9719 | 123.6923 | -123.9532 | -123.9853
2790.7188 | 123.8022 | -61.3907 | 62.2787 | 0.021591 | 0.017947 | 0.014695 | 0.014669 | 0.067084 | -0.0018285 | 0.083535 | -58.3054 | 62.265 | -61.6699 | -61.615 | 53.5492 | 20.0409 | 5.8456 | 5.4977 | 62.2833 | -61.702 | -0.27924 | -0.013733 | 3.0853 | -0.2243 | -8.7296 | -0.31128 | 0.004577 | 3.3646 | 67.2363 | 66.8884 | 114.9399 | 123.6557 | 3.0853 | 123.674 | 81.4316 | -0.31128 | 123.6557 | 3.0853 | 81.4316 | 114.9399 | 123.674 | -123.9487 | -123.9807
2791.7188 | 123.8022 | -61.4136 | 62.2696 | 0.082626 | 0.021151 | 0.020677 | 0.01296 | 0.06623 | 0.0011621 | 0.083108 | -58.2687 | 62.2925 | -61.6882 | -61.6333 | 53.5812 | 20.1736 | 5.7678 | 5.3375 | 62.2696 | -61.7065 | -0.27466 | 0.022888 | 3.1448 | -0.21973 | -8.6884 | -0.29297 | 0 | 3.4195 | 67.1814 | 66.7511 | 114.9948 | 123.7061 | 3.1448 | 123.6832 | 81.5872 | -0.29297 | 123.7061 | 3.1448 | 81.5872 | 114.9948 | 123.6832 | -123.9578 | -123.9761
2792.7188 | 123.7701 | -61.4182 | 62.2604 | 0.04448 | 0.019228 | 0.019181 | 0.014456 | 0.065375 | -0.00033333 | 0.080758 | -58.3649 | 62.3062 | -61.6608 | -61.6287 | 53.5126 | 20.0409 | 5.7175 | 5.3421 | 62.2879 | -61.7111 | -0.24262 | 0.045776 | 3.0533 | -0.21057 | -8.7479 | -0.29297 | 0.027466 | 3.2959 | 67.1356 | 66.7603 | 114.9307 | 123.7244 | 3.0533 | 123.7061 | 81.459 | -0.29297 | 123.7244 | 3.0533 | 81.459 | 114.9307 | 123.7061 | -123.9212 | -123.9716
2793.7188 | 123.7976 | -61.3907 | 62.2604 | -0.069961 | 0.016238 | 0.017045 | 0.013601 | 0.066443 | 0.0022303 | 0.080117 | -58.2596 | 62.2559 | -61.6745 | -61.5829 | 53.5904 | 19.899 | 5.7449 | 5.4657 | 62.2879 | -61.7065 | -0.28381 | -0.004578 | 3.1311 | -0.19226 | -8.67 | -0.31586 | 0.027466 | 3.4149 | 67.1356 | 66.8564 | 114.9811 | 123.6465 | 3.1311 | 123.6786 | 81.2897 | -0.31586 | 123.6465 | 3.1311 | 81.2897 | 114.9811 | 123.6786 | -123.9349 | -123.967
2794.7188 | 123.8388 | -61.3861 | 62.265 | -0.09285 | 0.018374 | 0.018327 | 0.014029 | 0.067298 | 0.0015893 | 0.081613 | -58.2687 | 62.3062 | -61.6608 | -61.5738 | 53.5034 | 20.0546 | 5.7953 | 5.452 | 62.3108 | -61.6837 | -0.27466 | 0.041198 | 3.1174 | -0.18768 | -8.7616 | -0.29755 | 0.045776 | 3.392 | 67.1814 | 66.8381 | 114.8895 | 123.6923 | 3.1174 | 123.6969 | 81.4407 | -0.29755 | 123.6923 | 3.1174 | 81.4407 | 114.8895 | 123.6969 | -123.9258 | -123.9487
2795.7188 | 123.7839 | -61.409 | 62.2421 | 0.029221 | 0.02051 | 0.01854 | 0.013388 | 0.066016 | 0.00094847 | 0.081826 | -58.2642 | 62.2971 | -61.6745 | -61.6241 | 53.5309 | 20.1004 | 5.8868 | 5.4886 | 62.2971 | -61.7065 | -0.2655 | 0.054932 | 3.1448 | -0.21515 | -8.7112 | -0.29755 | 0.054932 | 3.4103 | 67.2958 | 66.8976 | 114.9399 | 123.7061 | 3.1448 | 123.7061 | 81.5094 | -0.29755 | 123.7061 | 3.1448 | 81.5094 | 114.9399 | 123.7061 | -123.9166 | -123.9487
2796.7188 | 123.6923 | -61.4273 | 62.1964 | 0.15892 | 0.020724 | 0.01854 | 0.013388 | 0.065375 | 0.0015893 | 0.082894 | -58.3145 | 62.2925 | -61.6791 | -61.6425 | 53.5858 | 20.1233 | 5.722 | 5.3558 | 62.2925 | -61.7065 | -0.25177 | 0.09613 | 3.1128 | -0.21515 | -8.6105 | -0.27924 | 0.09613 | 3.3646 | 67.1494 | 66.7831 | 115.0131 | 123.7198 | 3.1128 | 123.7198 | 81.5506 | -0.27924 | 123.7198 | 3.1128 | 81.5506 | 115.0131 | 123.7198 | -123.8754 | -123.9029
2797.7188 | 123.7747 | -61.409 | 62.233 | 0.059738 | 0.017947 | 0.018327 | 0.013388 | 0.064521 | 0.0018031 | 0.080972 | -58.3191 | 62.3062 | -61.6882 | -61.6699 | 53.6407 | 20.1141 | 5.7861 | 5.3421 | 62.2696 | -61.7249 | -0.27923 | 0.073242 | 3.0899 | -0.26093 | -8.5922 | -0.31586 | 0.036621 | 3.3691 | 67.1951 | 66.7511 | 115.0497 | 123.7152 | 3.0899 | 123.6786 | 81.5231 | -0.31586 | 123.7152 | 3.0899 | 81.5231 | 115.0497 | 123.6786 | -123.9212 | -123.9578
2798.7188 | 124.0173 | -61.3861 | 62.2055 | 0.13603 | 0.017092 | 0.013841 | 0.0099698 | 0.066443 | -0.00076053 | 0.081185 | -58.2413 | 62.2009 | -61.6745 | -61.5463 | 53.6362 | 20.2377 | 5.5801 | 5.4382 | 62.2467 | -61.6745 | -0.28839 | -0.004577 | 3.1448 | -0.16022 | -8.5693 | -0.28839 | 0.041199 | 3.4332 | 66.9662 | 66.8243 | 115.0223 | 123.587 | 3.1448 | 123.6328 | 81.6238 | -0.28839 | 123.587 | 3.1448 | 81.6238 | 115.0223 | 123.6328 | -123.88 | -123.88
2799.7188 | 123.8159 | -61.4227 | 62.2559 | 0.41832 | 0.019015 | 0.016404 | 0.013601 | 0.061316 | 0.0015893 | 0.083108 | -58.287 | 62.3108 | -61.6882 | -61.6379 | 53.5355 | 20.0867 | 5.7541 | 5.3741 | 62.2925 | -61.7203 | -0.2655 | 0.054932 | 3.1357 | -0.21515 | -8.7204 | -0.29755 | 0.036621 | 3.4012 | 67.1768 | 66.7969 | 114.9582 | 123.7335 | 3.1357 | 123.7152 | 81.5094 | -0.29755 | 123.7335 | 3.1357 | 81.5094 | 114.9582 | 123.7152 | -123.9441 | -123.9761
2800.7188 | 123.7747 | -61.3907 | 62.2696 | 0.11314 | 0.016024 | 0.022172 | 0.014242 | 0.066016 | 0.00073487 | 0.081613 | -58.3099 | 62.2604 | -61.6699 | -61.647 | 53.5034 | 20.0775 | 5.7632 | 5.3238 | 62.2925 | -61.7294 | -0.27924 | -0.009155 | 3.0807 | -0.25635 | -8.7662 | -0.33874 | 0.022888 | 3.36 | 67.1539 | 66.7145 | 114.8941 | 123.6511 | 3.0807 | 123.6832 | 81.4682 | -0.33874 | 123.6511 | 3.0807 | 81.4682 | 114.8941 | 123.6832 | -123.9395 | -123.999
2801.7188 | 123.7747 | -61.4227 | 62.2421 | 0.03685 | 0.021792 | 0.015763 | 0.014242 | 0.064734 | 0.00052127 | 0.083108 | -58.3145 | 62.2971 | -61.6699 | -61.647 | 53.4988 | 20.0775 | 5.6946 | 5.3146 | 62.2787 | -61.734 | -0.24719 | 0.054932 | 3.1082 | -0.22431 | -8.7433 | -0.31128 | 0.036622 | 3.3554 | 67.1173 | 66.7374 | 114.9216 | 123.7198 | 3.1082 | 123.7015 | 81.5002 | -0.31128 | 123.7198 | 3.1082 | 81.5002 | 114.9216 | 123.7015 | -123.912 | -123.9761
2802.7188 | 123.7976 | -61.409 | 62.233 | 0.18181 | 0.020296 | 0.019608 | 0.013388 | 0.06687 | 0.0020167 | 0.083962 | -58.5526 | 62.2238 | -61.7249 | -61.6699 | 53.4073 | 20.0226 | 5.722 | 5.3329 | 62.3154 | -61.7111 | -0.31586 | -0.009155 | 2.8564 | -0.26093 | -8.8257 | -0.30212 | 0.082398 | 3.1723 | 67.131 | 66.7419 | 114.8163 | 123.6328 | 2.8564 | 123.7244 | 81.4316 | -0.30212 | 123.6328 | 2.8564 | 81.4316 | 114.8163 | 123.7244 | -123.9578 | -123.9441
2803.7188 | 123.9532 | -61.3678 | 62.2101 | 0.2047 | 0.017519 | 0.017472 | 0.011465 | 0.065375 | 0.00052127 | 0.083535 | -58.2458 | 62.2284 | -61.6745 | -61.5463 | 53.6591 | 20.2423 | 5.5756 | 5.4611 | 62.2467 | -61.6791 | -0.3067 | 0.018311 | 3.1219 | -0.17853 | -8.551 | -0.31128 | 0.036621 | 3.4287 | 66.9434 | 66.8289 | 115.0269 | 123.5962 | 3.1219 | 123.6145 | 81.6101 | -0.31128 | 123.5962 | 3.1219 | 81.6101 | 115.0269 | 123.6145 | -123.8846 | -123.8892
2804.7188 | 123.8525 | -61.3953 | 62.2742 | 0.1284 | 0.018374 | 0.020249 | 0.013601 | 0.064521 | 0.0041529 | 0.080972 | -58.3054 | 62.2925 | -61.6974 | -61.8393 | 53.1006 | 19.7205 | 6.1386 | 5.3741 | 62.3199 | -61.7111 | -0.30212 | 0.01831 | 3.0899 | -0.44403 | -9.1736 | -0.31586 | 0.045776 | 3.392 | 67.5339 | 66.7694 | 114.4958 | 123.6877 | 3.0899 | 123.7152 | 81.1157 | -0.31586 | 123.6877 | 3.0899 | 81.1157 | 114.4958 | 123.7152 | -123.9716 | -123.9853
2805.7188 | 123.8434 | -61.3861 | 62.2375 | 0.15892 | 0.020724 | 0.01555 | 0.013388 | 0.066443 | 0.0022303 | 0.08204 | -58.2596 | 62.2833 | -61.6837 | -61.6425 | 53.5217 | 20.1508 | 5.7449 | 5.4062 | 62.2513 | -61.7249 | -0.29755 | 0.045776 | 3.1265 | -0.25635 | -8.7158 | -0.33875 | 0.013733 | 3.4241 | 67.131 | 66.7923 | 114.9078 | 123.6694 | 3.1265 | 123.6374 | 81.5369 | -0.33875 | 123.6694 | 3.1265 | 81.5369 | 114.9078 | 123.6374 | -123.9212 | -123.9624
2806.7188 | 123.8434 | -61.409 | 62.233 | 0.10551 | 0.019656 | 0.019822 | 0.013174 | 0.064093 | 0.00094847 | 0.080758 | -58.2413 | 62.2787 | -61.6837 | -61.6287 | 53.5721 | 20.2515 | 5.7495 | 5.4062 | 62.2833 | -61.7203 | -0.27466 | 0.045777 | 3.1677 | -0.21973 | -8.6609 | -0.31128 | 0.050354 | 3.4424 | 67.1585 | 66.8152 | 114.9811 | 123.6877 | 3.1677 | 123.6923 | 81.6605 | -0.31128 | 123.6877 | 3.1677 | 81.6605 | 114.9811 | 123.6923 | -123.9166 | -123.9532
2807.7188 | 123.8022 | -61.3907 | 62.2238 | 0.021591 | 0.017733 | 0.018968 | 0.015097 | 0.065161 | 0.0024439 | 0.080331 | -58.2413 | 62.3108 | -61.6837 | -61.5967 | 53.5858 | 20.3247 | 5.864 | 5.4611 | 62.265 | -61.702 | -0.29297 | 0.086975 | 3.1494 | -0.20599 | -8.638 | -0.31128 | 0.041199 | 3.4424 | 67.2546 | 66.8518 | 114.9765 | 123.7015 | 3.1494 | 123.6557 | 81.7154 | -0.31128 | 123.7015 | 3.1494 | 81.7154 | 114.9765 | 123.6557 | -123.9075 | -123.9258
2808.7188 | 123.88 | -61.4044 | 62.2284 | 0.2047 | 0.017519 | 0.015977 | 0.010824 | 0.065802 | 0.0015893 | 0.082253 | -58.342 | 62.265 | -61.6928 | -61.6013 | 53.476 | 20.2652 | 5.8136 | 5.5298 | 62.233 | -61.6745 | -0.28839 | 0.036621 | 3.0624 | -0.19684 | -8.7524 | -0.27008 | 0.004577 | 3.3508 | 67.218 | 66.9342 | 114.8804 | 123.6694 | 3.0624 | 123.6374 | 81.6696 | -0.27008 | 123.6694 | 3.0624 | 81.6696 | 114.8804 | 123.6374 | -123.9212 | -123.9029
2809.7188 | 123.8068 | -61.4136 | 62.2467 | 0.074997 | 0.017733 | 0.020036 | 0.014456 | 0.066016 | 9.4068e-05 | 0.080331 | -58.3878 | 62.2833 | -61.6837 | -61.6379 | 53.4393 | 20.2377 | 5.8868 | 5.452 | 62.2787 | -61.7294 | -0.27008 | 0.036621 | 3.0258 | -0.2243 | -8.8074 | -0.31586 | 0.032044 | 3.2959 | 67.3004 | 66.8655 | 114.8529 | 123.6969 | 3.0258 | 123.6923 | 81.6513 | -0.31586 | 123.6969 | 3.0258 | 81.6513 | 114.8529 | 123.6923 | -123.9304 | -123.9761
2810.7188 | 123.7839 | -61.3998 | 62.2696 | 0.074997 | 0.017947 | 0.014268 | 0.018301 | 0.064521 | 0.00030767 | 0.081826 | -58.2275 | 62.2833 | -61.6516 | -61.6058 | 53.5263 | 20.2652 | 5.8365 | 5.4016 | 62.2696 | -61.702 | -0.25177 | 0.013733 | 3.1723 | -0.20599 | -8.7433 | -0.30212 | 0 | 3.4241 | 67.2363 | 66.8015 | 114.9261 | 123.6832 | 3.1723 | 123.6694 | 81.665 | -0.30212 | 123.6832 | 3.1723 | 81.665 | 114.9261 | 123.6694 | -123.9212 | -123.9716
2811.7188 | 123.8205 | -61.377 | 62.2879 | 0.013962 | 0.019869 | 0.020463 | 0.013388 | 0.064734 | 0.0011621 | 0.082894 | -58.2184 | 62.2787 | -61.6699 | -61.6241 | 53.6499 | 20.1965 | 5.9235 | 5.4611 | 62.2879 | -61.7065 | -0.29297 | -0.009155 | 3.1586 | -0.24719 | -8.638 | -0.32959 | 0 | 3.4515 | 67.3004 | 66.8381 | 115.0269 | 123.6557 | 3.1586 | 123.6649 | 81.5735 | -0.32959 | 123.6557 | 3.1586 | 81.5735 | 115.0269 | 123.6649 | -123.9578 | -123.9944
2812.7188 | 123.7701 | -61.4548 | 62.2467 | 0.090256 | 0.018587 | 0.019395 | 0.013174 | 0.066443 | -0.00011953 | 0.08204 | -58.3099 | 62.2696 | -61.702 | -61.6562 | 53.4805 | 20.1096 | 5.8868 | 5.4657 | 62.2604 | -61.7249 | -0.24719 | 0.022888 | 3.1448 | -0.20142 | -8.7662 | -0.27008 | 0.013733 | 3.392 | 67.3416 | 66.9205 | 114.9353 | 123.7244 | 3.1448 | 123.7152 | 81.5643 | -0.27008 | 123.7244 | 3.1448 | 81.5643 | 114.9353 | 123.7152 | -123.9487 | -123.9716
2813.7188 | 123.8663 | -61.377 | 62.2238 | 0.052109 | 0.015383 | 0.014909 | 0.0054836 | 0.06388 | 0.0015893 | 0.082253 | -58.2779 | 62.1689 | -61.702 | -61.6013 | 53.5995 | 20.3247 | 5.8548 | 5.6076 | 62.233 | -61.6425 | -0.32501 | -0.054932 | 3.0991 | -0.2243 | -8.6243 | -0.2655 | 0.009155 | 3.4241 | 67.2318 | 66.9846 | 114.9765 | 123.5458 | 3.0991 | 123.6099 | 81.7017 | -0.2655 | 123.5458 | 3.0991 | 81.7017 | 114.9765 | 123.6099 | -123.9258 | -123.8663
2814.7188 | 123.7885 | -61.3815 | 62.2971 | 0.04448 | 0.019442 | 0.020036 | 0.015097 | 0.064734 | 0.0018031 | 0.081399 | -58.2321 | 62.2971 | -61.6699 | -61.6104 | 53.4805 | 20.1416 | 5.9509 | 5.5664 | 62.2604 | -61.7203 | -0.28839 | 0 | 3.1494 | -0.22888 | -8.8165 | -0.33874 | -0.036621 | 3.4378 | 67.3325 | 66.9479 | 114.8621 | 123.6786 | 3.1494 | 123.642 | 81.5231 | -0.33874 | 123.6786 | 3.1494 | 81.5231 | 114.8621 | 123.642 | -123.967 | -124.0173
2815.7188 | 123.8113 | -61.4182 | 62.2879 | 0.021591 | 0.019869 | 0.015763 | 0.013174 | 0.06623 | -0.00011953 | 0.080117 | -58.2092 | 62.265 | -61.6837 | -61.6058 | 53.595 | 20.0363 | 5.9738 | 5.5847 | 62.2833 | -61.702 | -0.2655 | -0.022888 | 3.2089 | -0.18768 | -8.6929 | -0.28381 | -0.004578 | 3.4744 | 67.392 | 67.0029 | 115.0131 | 123.6832 | 3.2089 | 123.7015 | 81.4545 | -0.28381 | 123.6832 | 3.2089 | 81.4545 | 115.0131 | 123.7015 | -123.9716 | -123.9899
2816.7188 | 123.8022 | -61.4044 | 62.265 | 0.11314 | 0.017733 | 0.01555 | 0.014242 | 0.067084 | 0.00073487 | 0.080758 | -58.2687 | 62.2833 | -61.6608 | -61.6425 | 53.6316 | 20.0409 | 6.0059 | 5.5252 | 62.2742 | -61.7294 | -0.25635 | 0.01831 | 3.1357 | -0.23804 | -8.6334 | -0.32501 | 0.009155 | 3.392 | 67.4103 | 66.9296 | 115.036 | 123.6877 | 3.1357 | 123.6786 | 81.4453 | -0.32501 | 123.6877 | 3.1357 | 81.4453 | 115.036 | 123.6786 | -123.9258 | -123.9944
2817.7188 | 123.7656 | -61.3907 | 62.2742 | 0.15129 | 0.017519 | 0.015977 | 0.013388 | 0.065802 | 0.0022303 | 0.081826 | -58.2779 | 62.2833 | -61.6745 | -61.6516 | 53.5904 | 19.9402 | 5.9921 | 5.5069 | 62.2513 | -61.734 | -0.28381 | 0.009155 | 3.1128 | -0.26093 | -8.6838 | -0.34332 | -0.022888 | 3.3966 | 67.3828 | 66.8976 | 114.9811 | 123.674 | 3.1128 | 123.642 | 81.3309 | -0.34332 | 123.674 | 3.1128 | 81.3309 | 114.9811 | 123.642 | -123.9487 | -124.0082
2818.7344 | 123.8159 | -61.3907 | 62.2879 | -0.20729 | 0.014956 | 0.015763 | 0.005911 | 0.06623 | 0.00073487 | 0.083108 | -58.2458 | 62.2925 | -61.6699 | -61.5967 | 53.6728 | 19.931 | 6.0516 | 5.6396 | 62.3154 | -61.6699 | -0.27924 | 0.004577 | 3.1448 | -0.20599 | -8.6151 | -0.27924 | 0.027466 | 3.4241 | 67.4423 | 67.0303 | 115.0635 | 123.6832 | 3.1448 | 123.7061 | 81.3217 | -0.27924 | 123.6832 | 3.1448 | 81.3217 | 115.0635 | 123.7061 | -123.9578 | -123.9578
2819.7188 | 123.8022 | -61.4136 | 62.265 | -0.1844 | 0.018374 | 0.015763 | 0.014242 | 0.065161 | 0.0022303 | 0.083108 | -58.3786 | 62.2787 | -61.6699 | -61.6379 | 53.5721 | 20.1553 | 5.9052 | 5.5069 | 62.265 | -61.702 | -0.25635 | 0.013733 | 3.035 | -0.2243 | -8.6929 | -0.28839 | 0 | 3.2913 | 67.3187 | 66.9205 | 114.9857 | 123.6923 | 3.035 | 123.6786 | 81.5689 | -0.28839 | 123.6923 | 3.035 | 81.5689 | 114.9857 | 123.6786 | -123.9349 | -123.967
2820.7188 | 123.8159 | -61.4136 | 62.2604 | -0.21492 | 0.018374 | 0.02089 | 0.014883 | 0.064734 | 0.0011621 | 0.082894 | -58.2275 | 62.2696 | -61.6791 | -61.647 | 53.6041 | 20.192 | 5.928 | 5.4703 | 62.2696 | -61.7294 | -0.2655 | 0.009155 | 3.186 | -0.23346 | -8.6563 | -0.31586 | 0.009155 | 3.4515 | 67.3416 | 66.8838 | 115.0177 | 123.6832 | 3.186 | 123.6832 | 81.6055 | -0.31586 | 123.6832 | 3.186 | 81.6055 | 115.0177 | 123.6832 | -123.9395 | -123.9899
2821.7188 | 123.793 | -61.4182 | 62.2421 | 0.021591 | 0.017092 | 0.019181 | 0.011679 | 0.064521 | 0.00030767 | 0.081826 | -58.2367 | 62.2742 | -61.6653 | -61.6653 | 53.7003 | 20.1004 | 5.8594 | 5.4245 | 62.2604 | -61.7249 | -0.24719 | 0.032044 | 3.1815 | -0.24719 | -8.5419 | -0.3067 | 0.018311 | 3.4286 | 67.2775 | 66.8427 | 115.1184 | 123.6923 | 3.1815 | 123.6786 | 81.5186 | -0.3067 | 123.6923 | 3.1815 | 81.5186 | 115.1184 | 123.6786 | -123.9075 | -123.967
2822.7188 | 123.7885 | -61.4227 | 62.265 | 0.04448 | 0.020296 | 0.022386 | 0.014242 | 0.067298 | -0.00076053 | 0.080758 | -58.2092 | 62.2879 | -61.6653 | -61.6562 | 53.6316 | 20.0134 | 5.8502 | 5.4565 | 62.2971 | -61.7157 | -0.24262 | 0.022888 | 3.2135 | -0.23346 | -8.6334 | -0.29297 | 0.032043 | 3.4561 | 67.2729 | 66.8793 | 115.0543 | 123.7106 | 3.2135 | 123.7198 | 81.4362 | -0.29297 | 123.7106 | 3.2135 | 81.4362 | 115.0543 | 123.7198 | -123.9304 | -123.9807
2823.7344 | 123.9487 | -61.3312 | 62.2513 | -0.16914 | 0.015383 | 0.011277 | 0.0054836 | 0.061743 | 0.00073487 | 0.083749 | -58.2184 | 62.2055 | -61.6562 | -61.496 | 53.7003 | 20.4895 | 5.7724 | 5.7312 | 62.2147 | -61.6379 | -0.32501 | -0.045777 | 3.1128 | -0.1648 | -8.551 | -0.3067 | -0.036621 | 3.4378 | 67.1036 | 67.0624 | 115.0314 | 123.5367 | 3.1128 | 123.5458 | 81.8207 | -0.3067 | 123.5367 | 3.1128 | 81.8207 | 115.0314 | 123.5458 | -123.9075 | -123.8892
2824.7188 | 123.7793 | -61.4044 | 62.2696 | -0.33699 | 0.019015 | 0.017899 | 0.013601 | 0.064521 | 0.0013757 | 0.082253 | -58.2962 | 62.2513 | -61.6653 | -61.6379 | 53.4668 | 20.1874 | 5.8044 | 5.4657 | 62.2604 | -61.7111 | -0.26093 | -0.01831 | 3.1082 | -0.23346 | -8.8028 | -0.3067 | -0.009155 | 3.3691 | 67.2089 | 66.8701 | 114.8712 | 123.6557 | 3.1082 | 123.6649 | 81.5918 | -0.3067 | 123.6557 | 3.1082 | 81.5918 | 114.8712 | 123.6649 | -123.9349 | -123.9807
2825.7188 | 123.8205 | -61.409 | 62.2696 | -0.66505 | 0.019869 | 0.016191 | 0.015097 | 0.065375 | 0.00030767 | 0.082681 | -58.3054 | 62.2879 | -61.6974 | -61.6241 | 53.4576 | 20.2927 | 5.928 | 5.5023 | 62.2559 | -61.7203 | -0.28839 | 0.018311 | 3.1036 | -0.21515 | -8.812 | -0.31128 | -0.013733 | 3.392 | 67.337 | 66.9113 | 114.8666 | 123.6969 | 3.1036 | 123.6649 | 81.7017 | -0.31128 | 123.6969 | 3.1036 | 81.7017 | 114.8666 | 123.6649 | -123.967 | -123.9899
2826.7188 | 123.8434 | -61.3953 | 62.2238 | 0.2047 | 0.018374 | 0.018968 | 0.012533 | 0.061957 | 0.00030767 | 0.08204 | -58.2916 | 62.2696 | -61.7111 | -61.6013 | 53.5263 | 20.3339 | 5.8228 | 5.5206 | 62.2742 | -61.7111 | -0.31586 | 0.045776 | 3.1036 | -0.20599 | -8.6975 | -0.31586 | 0.050354 | 3.4195 | 67.218 | 66.9159 | 114.9216 | 123.6649 | 3.1036 | 123.6694 | 81.7291 | -0.31586 | 123.6649 | 3.1036 | 81.7291 | 114.9216 | 123.6694 | -123.9349 | -123.9349
2827.7188 | 123.8754 | -61.3953 | 62.2375 | 0.18181 | 0.017733 | 0.015763 | 0.011038 | 0.063452 | 0.0026575 | 0.082253 | -58.287 | 62.2513 | -61.7065 | -61.5967 | 53.4622 | 20.2332 | 5.8365 | 5.5115 | 62.2513 | -61.7065 | -0.31128 | 0.013733 | 3.1082 | -0.20142 | -8.7753 | -0.31128 | 0.013733 | 3.4195 | 67.2318 | 66.9067 | 114.8575 | 123.6465 | 3.1082 | 123.6465 | 81.6284 | -0.31128 | 123.6465 | 3.1082 | 81.6284 | 114.8575 | 123.6465 | -123.9441 | -123.9441
2828.7344 | 123.8388 | -61.3907 | 62.2971 | -0.21492 | 0.016451 | 0.015763 | 0.010611 | 0.064948 | -0.00011953 | 0.08204 | -58.2367 | 62.2787 | -61.6516 | -61.5875 | 53.54 | 20.224 | 5.9967 | 5.5115 | 62.3016 | -61.6882 | -0.26093 | -0.01831 | 3.154 | -0.19684 | -8.757 | -0.29755 | 0.004578 | 3.4149 | 67.3874 | 66.9022 | 114.9307 | 123.6694 | 3.154 | 123.6923 | 81.6147 | -0.29755 | 123.6694 | 3.154 | 81.6147 | 114.9307 | 123.6923 | -123.9487 | -123.9853
2829.7188 | 123.8251 | -61.3953 | 62.2742 | 0.1284 | 0.018801 | 0.01555 | 0.014242 | 0.063666 | -0.00076053 | 0.080972 | -58.3237 | 62.2467 | -61.6882 | -61.5326 | 53.2974 | 20.0546 | 6.1569 | 5.6122 | 62.233 | -61.6974 | -0.29297 | -0.027466 | 3.0716 | -0.13733 | -8.9767 | -0.30212 | -0.041199 | 3.3646 | 67.5522 | 67.0074 | 114.6927 | 123.642 | 3.0716 | 123.6282 | 81.4499 | -0.30212 | 123.642 | 3.0716 | 81.4499 | 114.6927 | 123.6282 | -123.9624 | -123.9716
2830.7188 | 123.8297 | -61.4044 | 62.2467 | 0.18181 | 0.019228 | 0.019822 | 0.012747 | 0.066443 | 0.00052127 | 0.082467 | -58.287 | 62.2559 | -61.6928 | -61.6333 | 53.6636 | 20.3796 | 5.7816 | 5.3925 | 62.2604 | -61.7203 | -0.28839 | 0.009155 | 3.1174 | -0.22888 | -8.5831 | -0.31586 | 0.013733 | 3.4058 | 67.186 | 66.7969 | 115.0681 | 123.6603 | 3.1174 | 123.6649 | 81.7841 | -0.31586 | 123.6603 | 3.1174 | 81.7841 | 115.0681 | 123.6649 | -123.9395 | -123.967
2831.7188 | 123.8113 | -61.3953 | 62.2421 | 0.14366 | 0.017947 | 0.017472 | 0.010824 | 0.064307 | 0.0013757 | 0.080972 | -58.2825 | 62.2604 | -61.6791 | -61.6241 | 53.6453 | 20.2423 | 5.8548 | 5.4245 | 62.2467 | -61.7157 | -0.28381 | 0.018311 | 3.1128 | -0.22888 | -8.5968 | -0.32043 | 0.004578 | 3.3966 | 67.2501 | 66.8198 | 115.0406 | 123.6557 | 3.1128 | 123.642 | 81.6376 | -0.32043 | 123.6557 | 3.1128 | 81.6376 | 115.0406 | 123.642 | -123.9212 | -123.9578
2832.7188 | 123.8205 | -61.3998 | 62.233 | -0.60402 | 0.018587 | 0.015336 | 0.014456 | 0.064948 | 9.4068e-05 | 0.083108 | -58.287 | 62.2879 | -61.7065 | -61.6104 | 53.6179 | 20.2972 | 5.7953 | 5.3467 | 62.2467 | -61.7065 | -0.3067 | 0.054932 | 3.1128 | -0.21057 | -8.6151 | -0.3067 | 0.013733 | 3.4195 | 67.1951 | 66.7465 | 115.0177 | 123.6877 | 3.1128 | 123.6465 | 81.6971 | -0.3067 | 123.6877 | 3.1128 | 81.6971 | 115.0177 | 123.6465 | -123.9395 | -123.9395
2833.7188 | 123.8663 | -61.3358 | 62.3337 | -0.26833 | 0.017947 | 0.015122 | 0.0091152 | 0.063666 | -0.00011953 | 0.083108 | -58.2825 | 62.2513 | -61.6791 | -61.6013 | 53.7094 | 20.192 | 6.0333 | 5.5252 | 62.2971 | -61.6745 | -0.34332 | -0.082397 | 3.0533 | -0.2655 | -8.6243 | -0.33875 | -0.036621 | 3.3966 | 67.3691 | 66.861 | 115.0452 | 123.587 | 3.0533 | 123.6328 | 81.5277 | -0.33875 | 123.587 | 3.0533 | 81.5277 | 115.0452 | 123.6328 | -124.0128 | -124.0082
2834.7188 | 123.848 | -61.3998 | 62.2467 | 0.16655 | 0.017733 | 0.016404 | 0.013815 | 0.064521 | 0.0015893 | 0.081185 | -58.2916 | 62.2513 | -61.6974 | -61.615 | 53.6224 | 20.4712 | 5.809 | 5.452 | 62.2421 | -61.7157 | -0.29755 | 0.004578 | 3.1082 | -0.21515 | -8.6243 | -0.31586 | -0.004578 | 3.4058 | 67.2089 | 66.8518 | 115.0223 | 123.6511 | 3.1082 | 123.642 | 81.871 | -0.31586 | 123.6511 | 3.1082 | 81.871 | 115.0223 | 123.642 | -123.9441 | -123.9624
2835.7188 | 123.6969 | -61.441 | 62.1597 | 0.10551 | 0.018587 | 0.016191 | 0.013815 | 0.06388 | 0.0015893 | 0.083322 | -58.287 | 62.2833 | -61.6882 | -61.6379 | 53.6591 | 20.3247 | 5.928 | 5.4245 | 62.265 | -61.7294 | -0.24719 | 0.1236 | 3.154 | -0.19684 | -8.5007 | -0.28839 | 0.10529 | 3.4012 | 67.3691 | 66.8655 | 115.1001 | 123.7244 | 3.154 | 123.7061 | 81.7657 | -0.28839 | 123.7244 | 3.154 | 81.7657 | 115.1001 | 123.7061 | -123.848 | -123.8892
2836.7188 | 123.7747 | -61.4182 | 62.2421 | 0.097885 | 0.018587 | 0.019822 | 0.014456 | 0.06388 | 9.4068e-05 | 0.08204 | -58.2687 | 62.2696 | -61.6882 | -61.6425 | 53.6591 | 20.3247 | 6.015 | 5.4337 | 62.2696 | -61.7249 | -0.27008 | 0.027466 | 3.1494 | -0.2243 | -8.5831 | -0.3067 | 0.027466 | 3.4195 | 67.4332 | 66.8518 | 115.0772 | 123.6877 | 3.1494 | 123.6877 | 81.7429 | -0.3067 | 123.6877 | 3.1494 | 81.7429 | 115.0772 | 123.6877 | -123.9304 | -123.967
2837.7188 | 123.793 | -61.4182 | 62.233 | 2.6461 | 0.016451 | 0.014482 | 0.011251 | 0.066443 | 0.0028711 | 0.082253 | -57.9712 | 62.2604 | -61.6974 | -61.6013 | 53.7277 | 20.3842 | 6.0059 | 5.5252 | 62.2696 | -61.7249 | -0.27924 | 0.027466 | 3.447 | -0.1831 | -8.5052 | -0.3067 | 0.036621 | 3.7262 | 67.424 | 66.9434 | 115.1459 | 123.6786 | 3.447 | 123.6877 | 81.8024 | -0.3067 | 123.6786 | 3.447 | 81.8024 | 115.1459 | 123.6877 | -123.9304 | -123.9578
2838.7188 | 123.8846 | -61.377 | 62.2192 | 0.16655 | 0.017092 | 0.021104 | 0.0071926 | 0.065802 | 0.0013757 | 0.079049 | -58.2596 | 62.1414 | -61.647 | -61.5692 | 53.7827 | 20.4208 | 5.7312 | 5.5573 | 62.2101 | -61.6516 | -0.27008 | -0.07782 | 3.1174 | -0.19226 | -8.4366 | -0.27466 | -0.009155 | 3.3875 | 67.1082 | 66.9342 | 115.1596 | 123.5184 | 3.1174 | 123.587 | 81.7978 | -0.27466 | 123.5184 | 3.1174 | 81.7978 | 115.1596 | 123.587 | -123.8663 | -123.8708
2839.7188 | 123.761 | -61.409 | 62.2238 | 0.074997 | 0.020296 | 0.017472 | 0.014883 | 0.064948 | 9.4068e-05 | 0.081826 | -58.2687 | 62.2787 | -61.6974 | -61.6653 | 53.6865 | 20.3979 | 5.896 | 5.4657 | 62.2742 | -61.7157 | -0.28839 | 0.054932 | 3.1403 | -0.25635 | -8.5373 | -0.3067 | 0.050354 | 3.4286 | 67.305 | 66.8747 | 115.0955 | 123.6877 | 3.1403 | 123.6832 | 81.8069 | -0.3067 | 123.6877 | 3.1403 | 81.8069 | 115.0955 | 123.6832 | -123.9212 | -123.9395
2840.7188 | 123.8022 | -61.4136 | 62.2696 | 0.15129 | 0.017306 | 0.017045 | 0.012747 | 0.065375 | 0.00094847 | 0.081185 | -58.168 | 62.2787 | -61.7111 | -61.615 | 53.7369 | 20.343 | 5.9601 | 5.5069 | 62.2421 | -61.7065 | -0.29755 | 0.009156 | 3.2455 | -0.20142 | -8.5327 | -0.29297 | -0.027466 | 3.5431 | 67.3737 | 66.9205 | 115.1505 | 123.6923 | 3.2455 | 123.6557 | 81.7566 | -0.29297 | 123.6923 | 3.2455 | 81.7566 | 115.1505 | 123.6557 | -123.9807 | -123.9761
2841.7188 | 123.8342 | -61.4182 | 62.2513 | 0.14366 | 0.018801 | 0.019822 | 0.015097 | 0.064948 | -0.0020421 | 0.081185 | -58.2779 | 62.2742 | -61.7157 | -61.6516 | 53.6957 | 20.4712 | 6.0379 | 5.4565 | 62.2604 | -61.702 | -0.29755 | 0.022888 | 3.1403 | -0.23346 | -8.5556 | -0.28381 | 0.009155 | 3.4378 | 67.4561 | 66.8747 | 115.1138 | 123.6923 | 3.1403 | 123.6786 | 81.8893 | -0.28381 | 123.6923 | 3.1403 | 81.8893 | 115.1138 | 123.6786 | -123.967 | -123.9532
2842.7188 | 123.8113 | -61.3998 | 62.2604 | 0.059738 | 0.016238 | 0.015336 | 0.015951 | 0.064093 | -0.00011953 | 0.079904 | -58.2367 | 62.2467 | -61.6791 | -61.6058 | 53.8559 | 20.4712 | 6.0745 | 5.5298 | 62.2787 | -61.7249 | -0.27924 | -0.013733 | 3.1631 | -0.20599 | -8.4045 | -0.32501 | 0.018311 | 3.4424 | 67.4744 | 66.9296 | 115.2557 | 123.6465 | 3.1631 | 123.6786 | 81.871 | -0.32501 | 123.6465 | 3.1631 | 81.871 | 115.2557 | 123.6786 | -123.9395 | -123.9853
2843.7188 | 123.8068 | -61.4319 | 62.2513 | -0.6498 | 0.017092 | 0.017686 | 0.013601 | 0.066016 | 0.0015893 | 0.08204 | -58.3603 | 62.265 | -61.6745 | -61.6333 | 53.8101 | 20.3613 | 6.0104 | 5.5069 | 62.2604 | -61.6882 | -0.24262 | 0.013733 | 3.0716 | -0.20142 | -8.4412 | -0.25635 | 0.009155 | 3.3142 | 67.4423 | 66.9388 | 115.242 | 123.6969 | 3.0716 | 123.6923 | 81.7932 | -0.25635 | 123.6969 | 3.0716 | 81.7932 | 115.242 | 123.6923 | -123.9258 | -123.9395
2844.7188 | 123.7885 | -61.4365 | 62.2696 | 0.03685 | 0.01816 | 0.015763 | 0.014883 | 0.063239 | 0.00030767 | 0.080758 | -58.3237 | 62.2925 | -61.6699 | -61.6196 | 53.8422 | 20.2789 | 6.0059 | 5.4977 | 62.265 | -61.7294 | -0.23346 | 0.022888 | 3.1128 | -0.18311 | -8.4274 | -0.29297 | -0.004577 | 3.3463 | 67.4423 | 66.9342 | 115.2786 | 123.7289 | 3.1128 | 123.7015 | 81.7154 | -0.29297 | 123.7289 | 3.1128 | 81.7154 | 115.2786 | 123.7015 | -123.9395 | -123.999
2845.7188 | 123.8022 | -61.3998 | 62.2559 | 0.03685 | 0.019656 | 0.015336 | 0.013174 | 0.063452 | 0.0011621 | 0.081185 | -58.2962 | 62.3062 | -61.6882 | -61.6196 | 53.8193 | 20.3156 | 5.9052 | 5.4565 | 62.2696 | -61.7294 | -0.28839 | 0.050354 | 3.1036 | -0.21973 | -8.4366 | -0.32959 | 0.013733 | 3.392 | 67.305 | 66.8564 | 115.2191 | 123.7061 | 3.1036 | 123.6694 | 81.7154 | -0.32959 | 123.7061 | 3.1036 | 81.7154 | 115.2191 | 123.6694 | -123.9441 | -123.9853
2846.7188 | 123.7976 | -61.3998 | 62.2604 | -0.0089264 | 0.017092 | 0.020249 | 0.013815 | 0.064093 | 0.0020167 | 0.082894 | -58.2916 | 62.2833 | -61.6608 | -61.6013 | 53.8193 | 20.3522 | 6.015 | 5.5115 | 62.2467 | -61.7065 | -0.26093 | 0.022888 | 3.1082 | -0.20142 | -8.4412 | -0.3067 | -0.013733 | 3.3691 | 67.4149 | 66.9113 | 115.2191 | 123.6832 | 3.1082 | 123.6465 | 81.752 | -0.3067 | 123.6832 | 3.1082 | 81.752 | 115.2191 | 123.6465 | -123.9212 | -123.967
2847.7188 | 123.7656 | -61.4136 | 62.2696 | -0.0012969 | 0.020296 | 0.018754 | 0.012533 | 0.06687 | 0.00073487 | 0.080972 | -58.2733 | 62.265 | -61.6699 | -61.6287 | 53.8239 | 20.4666 | 6.0928 | 5.5344 | 62.2742 | -61.7065 | -0.25635 | -0.004577 | 3.1403 | -0.21515 | -8.4457 | -0.29297 | 0.004578 | 3.3966 | 67.5064 | 66.9479 | 115.2374 | 123.6786 | 3.1403 | 123.6877 | 81.8802 | -0.29297 | 123.6786 | 3.1403 | 81.8802 | 115.2374 | 123.6877 | -123.9395 | -123.9761
2848.7188 | 123.9761 | -61.3678 | 62.2192 | 0.18944 | 0.016238 | 0.017899 | 0.0078336 | 0.065375 | 0.00094847 | 0.084817 | -58.3008 | 62.1506 | -61.6837 | -61.6379 | 53.6911 | 20.5902 | 6.0791 | 5.6854 | 62.2192 | -61.6653 | -0.31586 | -0.068664 | 3.067 | -0.27008 | -8.5281 | -0.29755 | 0 | 3.3829 | 67.4469 | 67.0532 | 115.0589 | 123.5184 | 3.067 | 123.587 | 81.958 | -0.29755 | 123.5184 | 3.067 | 81.958 | 115.0589 | 123.587 | -123.9029 | -123.8846
2849.7188 | 123.8388 | -61.3861 | 62.265 | -0.09285 | 0.017519 | 0.016618 | 0.014242 | 0.063025 | -0.00033333 | 0.081185 | -58.2413 | 62.2696 | -61.6928 | -61.5417 | 53.8055 | 20.4803 | 6.1432 | 5.6717 | 62.2375 | -61.7157 | -0.3067 | 0.004577 | 3.1448 | -0.15564 | -8.4595 | -0.32959 | -0.027466 | 3.4515 | 67.5293 | 67.0578 | 115.1917 | 123.6557 | 3.1448 | 123.6237 | 81.8665 | -0.32959 | 123.6557 | 3.1448 | 81.8665 | 115.1917 | 123.6237 | -123.9578 | -123.9807
2850.7188 | 123.8388 | -61.4136 | 62.2696 | -0.031814 | 0.018587 | 0.017259 | 0.01232 | 0.065802 | 0.0030847 | 0.080758 | -58.2596 | 62.2971 | -61.6562 | -61.5555 | 53.9886 | 20.4575 | 6.0974 | 5.658 | 62.265 | -61.7065 | -0.24262 | 0.027466 | 3.154 | -0.14191 | -8.2809 | -0.29297 | -0.004577 | 3.3966 | 67.511 | 67.0715 | 115.4022 | 123.7106 | 3.154 | 123.6786 | 81.871 | -0.29297 | 123.7106 | 3.154 | 81.871 | 115.4022 | 123.6786 | -123.9258 | -123.9761
2851.7188 | 123.793 | -61.3998 | 62.2604 | 0.059738 | 0.018587 | 0.01854 | 0.012533 | 0.065589 | 0.00030767 | 0.081613 | -58.2596 | 62.2742 | -61.6882 | -61.615 | 53.8559 | 20.2377 | 6.0333 | 5.5618 | 62.2787 | -61.702 | -0.28839 | 0.013733 | 3.1403 | -0.21515 | -8.4045 | -0.30212 | 0.018311 | 3.4286 | 67.4332 | 66.9617 | 115.2557 | 123.674 | 3.1403 | 123.6786 | 81.6376 | -0.30212 | 123.674 | 3.1403 | 81.6376 | 115.2557 | 123.6786 | -123.9487 | -123.9624
2852.7188 | 123.8297 | -61.3907 | 62.2559 | -0.016556 | 0.020724 | 0.017045 | 0.014456 | 0.067298 | 0.00030767 | 0.081826 | -58.2642 | 62.2696 | -61.6974 | -61.6058 | 53.7643 | 20.2469 | 6.0287 | 5.603 | 62.2696 | -61.6837 | -0.3067 | 0.013733 | 3.1265 | -0.21515 | -8.4915 | -0.29297 | 0.013733 | 3.4332 | 67.4194 | 66.9937 | 115.155 | 123.6603 | 3.1265 | 123.6603 | 81.6376 | -0.29297 | 123.6603 | 3.1265 | 81.6376 | 115.155 | 123.6603 | -123.9532 | -123.9395
2853.7188 | 123.9304 | -61.3907 | 62.2101 | 0.24284 | 0.019228 | 0.017045 | 0.0099698 | 0.067939 | 0.0028711 | 0.082894 | -58.2962 | 62.2192 | -61.6882 | -61.5875 | 53.8605 | 20.3476 | 5.9326 | 5.7358 | 62.2192 | -61.6562 | -0.29755 | 0.009155 | 3.0945 | -0.19684 | -8.3496 | -0.2655 | 0.009155 | 3.392 | 67.3233 | 67.1265 | 115.2512 | 123.6099 | 3.0945 | 123.6099 | 81.7383 | -0.2655 | 123.6099 | 3.0945 | 81.7383 | 115.2512 | 123.6099 | -123.8983 | -123.8663
2854.7188 | 123.8251 | -61.377 | 62.265 | -0.0012969 | 0.018374 | 0.015763 | 0.014029 | 0.064948 | -0.0018285 | 0.080117 | -58.2458 | 62.2833 | -61.6653 | -61.5738 | 53.8147 | 20.1324 | 6.1066 | 5.722 | 62.2604 | -61.7111 | -0.28839 | 0.01831 | 3.1311 | -0.19684 | -8.4503 | -0.33417 | -0.004578 | 3.4195 | 67.4835 | 67.099 | 115.1917 | 123.6603 | 3.1311 | 123.6374 | 81.5094 | -0.33417 | 123.6603 | 3.1311 | 81.5094 | 115.1917 | 123.6374 | -123.9304 | -123.9761
2855.7188 | 123.8205 | -61.3861 | 62.265 | -0.047073 | 0.017306 | 0.020249 | 0.01232 | 0.064734 | 9.4068e-05 | 0.079904 | -58.2321 | 62.2787 | -61.6562 | -61.6013 | 53.8559 | 20.3293 | 6.0333 | 5.5939 | 62.265 | -61.7065 | -0.27008 | 0.013733 | 3.154 | -0.21515 | -8.4091 | -0.32044 | 0 | 3.4241 | 67.4194 | 66.98 | 115.242 | 123.6649 | 3.154 | 123.6511 | 81.7154 | -0.32044 | 123.6649 | 3.154 | 81.7154 | 115.242 | 123.6511 | -123.9212 | -123.9716
2856.7188 | 123.8434 | -61.3953 | 62.2513 | -0.2607 | 0.018374 | 0.015336 | 0.011679 | 0.065802 | 9.4068e-05 | 0.078195 | -58.3603 | 62.2879 | -61.6608 | -61.5646 | 53.8376 | 20.3568 | 6.1615 | 5.6808 | 62.3108 | -61.6699 | -0.2655 | 0.036621 | 3.035 | -0.16937 | -8.4137 | -0.27466 | 0.059509 | 3.3005 | 67.5568 | 67.0761 | 115.2328 | 123.6832 | 3.035 | 123.7061 | 81.752 | -0.27466 | 123.6832 | 3.035 | 81.752 | 115.2328 | 123.7061 | -123.912 | -123.9212
2857.7188 | 123.8571 | -61.377 | 62.2696 | -0.16151 | 0.017947 | 0.019822 | 0.010824 | 0.063666 | 0.0020167 | 0.083322 | -58.2138 | 62.2971 | -61.6745 | -61.5601 | 53.8696 | 20.3613 | 6.102 | 5.6854 | 62.2971 | -61.6653 | -0.29755 | 0.027466 | 3.1631 | -0.18311 | -8.4 | -0.28839 | 0.027466 | 3.4607 | 67.4789 | 67.0624 | 115.2466 | 123.674 | 3.1631 | 123.674 | 81.7383 | -0.28839 | 123.674 | 3.1631 | 81.7383 | 115.2466 | 123.674 | -123.9441 | -123.9349
2858.7188 | 123.7747 | -61.4182 | 62.265 | 0.04448 | 0.016878 | 0.015977 | 0.01531 | 0.06623 | 0.0011621 | 0.081826 | -58.3191 | 62.2696 | -61.6974 | -61.6562 | 53.8101 | 20.3018 | 6.0928 | 5.5206 | 62.2742 | -61.7294 | -0.27924 | 0.004577 | 3.0991 | -0.23804 | -8.4549 | -0.31128 | 0.009155 | 3.3783 | 67.511 | 66.9388 | 115.2283 | 123.6877 | 3.0991 | 123.6923 | 81.72 | -0.31128 | 123.6877 | 3.0991 | 81.72 | 115.2283 | 123.6923 | -123.9624 | -123.9944
2859.7188 | 123.8159 | -61.3907 | 62.2696 | -0.13863 | 0.019656 | 0.014695 | 0.01296 | 0.068366 | 0.0013757 | 0.081826 | -58.255 | 62.2971 | -61.647 | -61.5463 | 53.8834 | 20.43 | 6.0379 | 5.6351 | 62.2925 | -61.6837 | -0.25635 | 0.027466 | 3.1357 | -0.15564 | -8.3862 | -0.29297 | 0.022888 | 3.392 | 67.4286 | 67.0258 | 115.274 | 123.6877 | 3.1357 | 123.6832 | 81.8207 | -0.29297 | 123.6877 | 3.1357 | 81.8207 | 115.274 | 123.6832 | -123.9166 | -123.9532
2860.7188 | 123.9166 | -61.4136 | 62.2513 | -0.016556 | 0.016878 | 0.016618 | 0.012106 | 0.066657 | 0.00073487 | 0.082253 | -58.3145 | 62.2879 | -61.6562 | -61.5601 | 53.8193 | 20.4254 | 6.0837 | 5.6168 | 62.2742 | -61.6699 | -0.24262 | 0.036621 | 3.0991 | -0.14649 | -8.432 | -0.25635 | 0.022888 | 3.3417 | 67.4973 | 67.0303 | 115.2328 | 123.7015 | 3.0991 | 123.6877 | 81.839 | -0.25635 | 123.7015 | 3.0991 | 81.839 | 115.2328 | 123.6877 | -123.9075 | -123.9212
2861.7188 | 123.8251 | -61.3632 | 62.2421 | -0.10048 | 0.01816 | 0.021958 | 0.013601 | 0.066443 | 9.4068e-05 | 0.083322 | -58.2184 | 62.3154 | -61.6562 | -61.5646 | 53.8284 | 20.3384 | 6.134 | 5.6625 | 62.2879 | -61.6791 | -0.29297 | 0.073243 | 3.1448 | -0.20142 | -8.4137 | -0.31586 | 0.045777 | 3.4378 | 67.4973 | 67.0258 | 115.1916 | 123.6786 | 3.1448 | 123.6511 | 81.7017 | -0.31586 | 123.6786 | 3.1448 | 81.7017 | 115.1916 | 123.6511 | -123.8983 | -123.9212
2862.7188 | 123.8434 | -61.3998 | 62.265 | -0.16914 | 0.020724 | 0.01555 | 0.013174 | 0.06623 | 0.00094847 | 0.080117 | -58.2367 | 62.3108 | -61.6608 | -61.5784 | 53.8788 | 20.3934 | 6.3217 | 5.7312 | 62.2833 | -61.6837 | -0.26093 | 0.045776 | 3.1631 | -0.17853 | -8.3862 | -0.28381 | 0.01831 | 3.4241 | 67.7216 | 67.131 | 115.2786 | 123.7106 | 3.1631 | 123.6832 | 81.7932 | -0.28381 | 123.7106 | 3.1631 | 81.7932 | 115.2786 | 123.6832 | -123.9258 | -123.9487
2863.7188 | 123.8342 | -61.3998 | 62.2833 | -0.12337 | 0.016665 | 0.015122 | 0.011465 | 0.064734 | 0.00052127 | 0.07969 | -58.223 | 62.2879 | -61.6745 | -61.6104 | 54.0436 | 20.5032 | 6.2256 | 5.7175 | 62.2879 | -61.6882 | -0.27466 | 0.004578 | 3.1769 | -0.21057 | -8.2397 | -0.28839 | 0.004578 | 3.4515 | 67.6254 | 67.1173 | 115.4434 | 123.6877 | 3.1769 | 123.6877 | 81.9031 | -0.28839 | 123.6877 | 3.1769 | 81.9031 | 115.4434 | 123.6877 | -123.9578 | -123.9716
2864.7188 | 123.8205 | -61.3907 | 62.2696 | -0.12337 | 0.017519 | 0.016404 | 0.011892 | 0.064948 | 0.0020167 | 0.082681 | -58.2458 | 62.2604 | -61.6699 | -61.5509 | 53.8376 | 20.3979 | 6.2393 | 5.7495 | 62.2971 | -61.6974 | -0.27924 | -0.009155 | 3.1448 | -0.16022 | -8.432 | -0.3067 | 0.027466 | 3.4241 | 67.63 | 67.1402 | 115.2283 | 123.6511 | 3.1448 | 123.6877 | 81.7886 | -0.3067 | 123.6511 | 3.1448 | 81.7886 | 115.2283 | 123.6877 | -123.9395 | -123.967
2865.7188 | 123.8342 | -61.3907 | 62.2879 | -0.16914 | 0.016665 | 0.013841 | 0.010824 | 0.062384 | -0.00033333 | 0.07969 | -58.2001 | 62.2833 | -61.6745 | -61.5692 | 53.8651 | 20.3522 | 6.2714 | 5.7037 | 62.2742 | -61.647 | -0.28381 | -0.004578 | 3.1906 | -0.17853 | -8.4229 | -0.25635 | -0.013733 | 3.4744 | 67.662 | 67.0944 | 115.2557 | 123.674 | 3.1906 | 123.6649 | 81.7429 | -0.25635 | 123.674 | 3.1906 | 81.7429 | 115.2557 | 123.6649 | -123.9624 | -123.9349
2866.7188 | 123.8068 | -61.3815 | 62.2787 | -0.17677 | 0.016024 | 0.014482 | 0.010397 | 0.063025 | 9.4068e-05 | 0.081399 | -58.3054 | 62.3016 | -61.6882 | -61.6013 | 53.8834 | 20.4712 | 6.2714 | 5.6671 | 62.3016 | -61.6837 | -0.3067 | 0.022888 | 3.0762 | -0.21973 | -8.3954 | -0.30212 | 0.022888 | 3.3829 | 67.6529 | 67.0486 | 115.2649 | 123.6832 | 3.0762 | 123.6832 | 81.8527 | -0.30212 | 123.6832 | 3.0762 | 81.8527 | 115.2649 | 123.6832 | -123.967 | -123.9624
2867.7188 | 123.8571 | -61.409 | 62.2787 | -0.19203 | 0.019228 | 0.01555 | 0.012533 | 0.061316 | 0.00030767 | 0.081185 | -58.2504 | 62.2696 | -61.6653 | -61.5463 | 53.9337 | 20.4391 | 6.2668 | 5.6946 | 62.265 | -61.6928 | -0.25635 | -0.009156 | 3.1586 | -0.13733 | -8.345 | -0.28381 | -0.013733 | 3.4149 | 67.6758 | 67.1036 | 115.3427 | 123.6786 | 3.1586 | 123.674 | 81.8481 | -0.28381 | 123.6786 | 3.1586 | 81.8481 | 115.3427 | 123.674 | -123.9441 | -123.9716
2868.7188 | 123.8159 | -61.4136 | 62.2742 | 0.16655 | 0.020083 | 0.016618 | 0.021078 | 0.067511 | -0.0022559 | 0.079476 | -58.3099 | 62.2375 | -61.6974 | -61.4456 | 53.9246 | 20.2148 | 6.2668 | 5.5344 | 62.2879 | -61.6745 | -0.28381 | -0.036621 | 3.1036 | -0.032044 | -8.3496 | -0.26093 | 0.013733 | 3.3875 | 67.6804 | 66.9479 | 115.3381 | 123.6511 | 3.1036 | 123.7015 | 81.6284 | -0.26093 | 123.6511 | 3.1036 | 81.6284 | 115.3381 | 123.7015 | -123.9716 | -123.9487
2869.7188 | 123.8388 | -61.3907 | 62.2696 | -0.22255 | 0.019228 | 0.016831 | 0.013388 | 0.064734 | 0.00052127 | 0.08204 | -58.2458 | 62.2742 | -61.6745 | -61.5692 | 53.9932 | 20.4025 | 6.1798 | 5.6351 | 62.2787 | -61.6699 | -0.28381 | 0.004578 | 3.1448 | -0.17853 | -8.2764 | -0.27924 | 0.009156 | 3.4287 | 67.5705 | 67.0258 | 115.3839 | 123.6649 | 3.1448 | 123.6694 | 81.7932 | -0.27924 | 123.6649 | 3.1448 | 81.7932 | 115.3839 | 123.6694 | -123.9441 | -123.9395
2870.7188 | 123.7747 | -61.4044 | 62.2833 | -0.26833 | 0.017733 | 0.0097818 | 0.012747 | 0.06388 | 0.0032983 | 0.080758 | -58.1589 | 62.2971 | -61.6425 | -61.5921 | 53.8742 | 20.3064 | 6.1615 | 5.5893 | 62.3062 | -61.6791 | -0.23804 | 0.013733 | 3.2455 | -0.18768 | -8.4091 | -0.27466 | 0.022888 | 3.4836 | 67.5659 | 66.9937 | 115.2786 | 123.7015 | 3.2455 | 123.7106 | 81.7108 | -0.27466 | 123.7015 | 3.2455 | 81.7108 | 115.2786 | 123.7106 | -123.9258 | -123.9624
2871.7188 | 123.8388 | -61.3953 | 62.2833 | -0.19203 | 0.017733 | 0.01085 | 0.011892 | 0.063452 | 9.4068e-05 | 0.081399 | -58.3282 | 62.2833 | -61.6699 | -61.6013 | 53.9017 | 20.4895 | 6.2897 | 5.6854 | 62.3154 | -61.6974 | -0.27466 | 0 | 3.067 | -0.20599 | -8.3817 | -0.30212 | 0.032044 | 3.3417 | 67.6849 | 67.0807 | 115.2969 | 123.6786 | 3.067 | 123.7106 | 81.8848 | -0.30212 | 123.6786 | 3.067 | 81.8848 | 115.2969 | 123.7106 | -123.9532 | -123.9807
2872.7188 | 123.7793 | -61.3953 | 62.2925 | -0.24544 | 0.016451 | 0.017045 | 0.0095424 | 0.062812 | 0.0022303 | 0.081185 | -58.3282 | 62.2787 | -61.6791 | -61.5875 | 53.8513 | 20.4071 | 6.1523 | 5.5893 | 62.2971 | -61.6837 | -0.28381 | -0.013732 | 3.067 | -0.19226 | -8.4412 | -0.28839 | 0.004578 | 3.3508 | 67.5476 | 66.9846 | 115.2466 | 123.674 | 3.067 | 123.6923 | 81.8024 | -0.28839 | 123.674 | 3.067 | 81.8024 | 115.2466 | 123.6923 | -123.9716 | -123.9761
2873.7188 | 123.8022 | -61.3998 | 62.265 | 0.0063326 | 0.018587 | 0.016618 | 0.015097 | 0.064307 | 0.0013757 | 0.080758 | -58.2138 | 62.2971 | -61.6653 | -61.6058 | 53.801 | 20.1965 | 6.1066 | 5.484 | 62.2742 | -61.7203 | -0.2655 | 0.032043 | 3.186 | -0.20599 | -8.4641 | -0.32043 | 0.009155 | 3.4515 | 67.5064 | 66.8838 | 115.2008 | 123.6969 | 3.186 | 123.674 | 81.5964 | -0.32043 | 123.6969 | 3.186 | 81.5964 | 115.2008 | 123.674 | -123.9304 | -123.9853
2874.7188 | 123.8159 | -61.3953 | 62.265 | -0.15388 | 0.014101 | 0.018113 | 0.013388 | 0.065161 | 0.0032983 | 0.080544 | -58.2687 | 62.2833 | -61.6837 | -61.5875 | 53.9474 | 20.4117 | 6.2256 | 5.5344 | 62.3199 | -61.6791 | -0.28839 | 0.01831 | 3.1265 | -0.19226 | -8.3176 | -0.28381 | 0.054931 | 3.4149 | 67.6208 | 66.9296 | 115.3427 | 123.6786 | 3.1265 | 123.7152 | 81.8069 | -0.28381 | 123.6786 | 3.1265 | 81.8069 | 115.3427 | 123.7152 | -123.9487 | -123.9441
2875.7188 | 123.7976 | -61.4136 | 62.2971 | -0.22255 | 0.017306 | 0.017899 | 0.010824 | 0.064307 | 0.0015893 | 0.080758 | -58.3237 | 62.2696 | -61.6791 | -61.5875 | 53.8971 | 20.2835 | 6.2851 | 5.5801 | 62.2971 | -61.6928 | -0.2655 | -0.027466 | 3.0899 | -0.17395 | -8.4 | -0.27924 | 0 | 3.3554 | 67.6987 | 66.9937 | 115.3107 | 123.6832 | 3.0899 | 123.7106 | 81.6971 | -0.27924 | 123.6832 | 3.0899 | 81.6971 | 115.3107 | 123.7106 | -123.9761 | -123.9899
2876.7188 | 123.8022 | -61.3815 | 62.2833 | -0.25307 | 0.017306 | 0.014695 | 0.0078336 | 0.062598 | -0.0020421 | 0.081185 | -58.287 | 62.265 | -61.6608 | -61.5967 | 53.9841 | 20.4575 | 6.2805 | 5.603 | 62.3016 | -61.6882 | -0.27924 | -0.01831 | 3.0945 | -0.21515 | -8.2993 | -0.3067 | 0.018311 | 3.3737 | 67.662 | 66.9846 | 115.3656 | 123.6465 | 3.0945 | 123.6832 | 81.839 | -0.3067 | 123.6465 | 3.0945 | 81.839 | 115.3656 | 123.6832 | -123.9441 | -123.9716
2877.7188 | 123.8205 | -61.3861 | 62.2971 | -0.20729 | 0.014956 | 0.012345 | 0.010183 | 0.06153 | -0.00033333 | 0.083535 | -58.2138 | 62.2604 | -61.6608 | -61.5829 | 53.92 | 20.4437 | 6.2393 | 5.5664 | 62.2971 | -61.6699 | -0.27466 | -0.036621 | 3.1723 | -0.19684 | -8.3771 | -0.28381 | 0 | 3.447 | 67.6254 | 66.9525 | 115.3061 | 123.6465 | 3.1723 | 123.6832 | 81.8298 | -0.28381 | 123.6465 | 3.1723 | 81.8298 | 115.3061 | 123.6832 | -123.9578 | -123.967
2878.7188 | 123.8251 | -61.3953 | 62.2742 | -0.19966 | 0.01581 | 0.014695 | 0.011679 | 0.062171 | 0.0018031 | 0.080758 | -58.2413 | 62.2559 | -61.6837 | -61.5875 | 53.8376 | 20.4254 | 6.189 | 5.5252 | 62.3016 | -61.6745 | -0.28839 | -0.018311 | 3.154 | -0.19226 | -8.4366 | -0.27924 | 0.027466 | 3.4424 | 67.5842 | 66.9205 | 115.2328 | 123.6511 | 3.154 | 123.6969 | 81.8207 | -0.27924 | 123.6511 | 3.154 | 81.8207 | 115.2328 | 123.6969 | -123.9578 | -123.9487
2879.7188 | 123.8251 | -61.3907 | 62.2879 | -0.23781 | 0.016878 | 0.018327 | 0.0097562 | 0.062171 | 0.0018031 | 0.08204 | -58.3099 | 62.265 | -61.6699 | -61.5875 | 53.8788 | 20.4025 | 6.2073 | 5.5435 | 62.3016 | -61.6516 | -0.27924 | -0.022888 | 3.0807 | -0.19684 | -8.4091 | -0.26093 | 0.013733 | 3.36 | 67.598 | 66.9342 | 115.2695 | 123.6557 | 3.0807 | 123.6923 | 81.7932 | -0.26093 | 123.6557 | 3.0807 | 81.7932 | 115.2695 | 123.6923 | -123.9578 | -123.9395
2880.7188 | 123.8022 | -61.3953 | 62.3016 | -0.26833 | 0.016238 | 0.013627 | 0.010397 | 0.060248 | 0.0018031 | 0.080758 | -58.3374 | 62.233 | -61.6745 | -61.5784 | 53.7918 | 20.1782 | 6.2164 | 5.5756 | 62.2833 | -61.6653 | -0.27924 | -0.068665 | 3.0579 | -0.18311 | -8.5098 | -0.27008 | -0.018311 | 3.3371 | 67.6117 | 66.9708 | 115.1871 | 123.6282 | 3.0579 | 123.6786 | 81.5735 | -0.27008 | 123.6282 | 3.0579 | 81.5735 | 115.1871 | 123.6786 | -123.9761 | -123.967
2881.7188 | 123.8022 | -61.3907 | 62.2742 | -0.16914 | 0.016238 | 0.016191 | 0.01296 | 0.062171 | -0.0011877 | 0.081185 | -58.3054 | 62.2421 | -61.647 | -61.4548 | 53.9841 | 20.3018 | 6.0883 | 5.6671 | 62.2742 | -61.6928 | -0.25635 | -0.032044 | 3.0853 | -0.064087 | -8.2901 | -0.30212 | 0 | 3.3417 | 67.4789 | 67.0578 | 115.3748 | 123.6328 | 3.0853 | 123.6649 | 81.6925 | -0.30212 | 123.6328 | 3.0853 | 81.6925 | 115.3748 | 123.6649 | -123.9212 | -123.967
2882.7188 | 123.7793 | -61.4136 | 62.2971 | -0.17677 | 0.017306 | 0.015977 | 0.0095424 | 0.061957 | -0.00076053 | 0.079476 | -58.3282 | 62.265 | -61.6974 | -61.5829 | 53.833 | 20.4163 | 6.4133 | 5.8411 | 62.2696 | -61.647 | -0.28381 | -0.032043 | 3.0853 | -0.16937 | -8.4641 | -0.23346 | -0.027466 | 3.3691 | 67.8268 | 67.2546 | 115.2466 | 123.6786 | 3.0853 | 123.6832 | 81.8298 | -0.23346 | 123.6786 | 3.0853 | 81.8298 | 115.2466 | 123.6832 | -123.9944 | -123.9441
2883.7188 | 123.793 | -61.4136 | 62.2696 | -0.047073 | 0.016024 | 0.014054 | 0.014029 | 0.061743 | -0.0011877 | 0.081399 | -58.3374 | 62.2467 | -61.6791 | -61.5921 | 53.8879 | 20.4849 | 6.2988 | 5.777 | 62.265 | -61.7157 | -0.2655 | -0.022888 | 3.0762 | -0.17853 | -8.3817 | -0.30212 | -0.004577 | 3.3417 | 67.7124 | 67.1906 | 115.3015 | 123.6603 | 3.0762 | 123.6786 | 81.8985 | -0.30212 | 123.6603 | 3.0762 | 81.8985 | 115.3015 | 123.6786 | -123.9487 | -123.9853
2884.7188 | 123.9212 | -61.3724 | 62.2467 | -0.21492 | 0.016238 | 0.01555 | 0.0082608 | 0.060889 | -0.0011877 | 0.080117 | -58.3099 | 62.1689 | -61.6425 | -61.5097 | 53.9429 | 20.7642 | 6.1844 | 5.9509 | 62.2421 | -61.6241 | -0.27008 | -0.07782 | 3.0624 | -0.13733 | -8.3038 | -0.25177 | -0.004578 | 3.3325 | 67.5568 | 67.3233 | 115.3152 | 123.5413 | 3.0624 | 123.6145 | 82.1365 | -0.25177 | 123.5413 | 3.0624 | 82.1365 | 115.3152 | 123.6145 | -123.8892 | -123.8709
2885.7188 | 123.8251 | -61.3724 | 62.2879 | -0.30647 | 0.01581 | 0.015763 | 0.012747 | 0.062384 | 0.00052127 | 0.079904 | -58.2642 | 62.2101 | -61.6562 | -61.5601 | 53.9291 | 20.668 | 6.3354 | 5.9006 | 62.233 | -61.6562 | -0.28381 | -0.07782 | 3.1082 | -0.18768 | -8.3588 | -0.28381 | -0.054932 | 3.392 | 67.7078 | 67.2729 | 115.3015 | 123.5825 | 3.1082 | 123.6053 | 82.0404 | -0.28381 | 123.5825 | 3.1082 | 82.0404 | 115.3015 | 123.6053 | -123.9441 | -123.9441
2886.7188 | 123.8846 | -61.3724 | 62.2879 | -0.19966 | 0.015597 | 0.012345 | 0.0099698 | 0.058753 | -0.0022559 | 0.082467 | -58.2687 | 62.1964 | -61.6745 | -61.5143 | 54.0115 | 20.6177 | 6.34 | 5.9692 | 62.233 | -61.647 | -0.30213 | -0.091553 | 3.1036 | -0.14191 | -8.2764 | -0.27466 | -0.054932 | 3.4058 | 67.7124 | 67.3416 | 115.3839 | 123.5687 | 3.1036 | 123.6053 | 81.9901 | -0.27466 | 123.5687 | 3.1036 | 81.9901 | 115.3839 | 123.6053 | -123.9624 | -123.9349
2887.7188 | 123.8663 | -61.3403 | 62.2742 | -0.20729 | 0.015169 | 0.0095682 | 0.010611 | 0.060675 | 9.4068e-05 | 0.080117 | -58.2642 | 62.1597 | -61.6653 | -61.4914 | 53.9474 | 20.723 | 6.308 | 5.9463 | 62.2375 | -61.6379 | -0.32501 | -0.11444 | 3.0762 | -0.15106 | -8.3267 | -0.29755 | -0.036621 | 3.4012 | 67.6483 | 67.2867 | 115.2878 | 123.5001 | 3.0762 | 123.5779 | 82.0633 | -0.29755 | 123.5001 | 3.0762 | 82.0633 | 115.2878 | 123.5779 | -123.9395 | -123.912
2888.7188 | 123.8022 | -61.4044 | 62.265 | 1.5551 | 0.016238 | 0.01555 | 0.016806 | 0.061743 | 0.00030767 | 0.081826 | -58.1131 | 62.2696 | -61.6791 | -61.5372 | 53.8742 | 20.6635 | 6.2805 | 5.8548 | 62.2192 | -61.6928 | -0.27466 | 0.004577 | 3.2913 | -0.13275 | -8.3908 | -0.28839 | -0.045777 | 3.566 | 67.6849 | 67.2592 | 115.2786 | 123.674 | 3.2913 | 123.6237 | 82.0679 | -0.28839 | 123.674 | 3.2913 | 82.0679 | 115.2786 | 123.6237 | -123.9441 | -123.9578
2889.7188 | 123.848 | -61.377 | 62.2879 | -0.2607 | 0.013033 | 0.015122 | 0.0089016 | 0.061316 | -0.00011953 | 0.080544 | -58.2092 | 62.1964 | -61.6608 | -61.5463 | 53.8055 | 20.7092 | 6.4819 | 5.9647 | 62.2604 | -61.615 | -0.28381 | -0.091553 | 3.1677 | -0.16937 | -8.4824 | -0.23804 | -0.027466 | 3.4515 | 67.8589 | 67.3416 | 115.1825 | 123.5733 | 3.1677 | 123.6374 | 82.0862 | -0.23804 | 123.5733 | 3.1677 | 82.0862 | 115.1825 | 123.6374 | -123.9487 | -123.9029
2890.7188 | 123.9258 | -61.3449 | 62.2238 | -1.7561 | 0.01346 | 0.013413 | 0.0091152 | 0.063239 | 0.00094847 | 0.082681 | -58.1635 | 62.1735 | -61.6241 | -61.4731 | 53.8925 | 20.8008 | 6.2988 | 6.0013 | 62.178 | -61.6287 | -0.27924 | -0.050354 | 3.1815 | -0.12817 | -8.3313 | -0.28381 | -0.045776 | 3.4607 | 67.6437 | 67.3462 | 115.2374 | 123.5184 | 3.1815 | 123.523 | 82.1457 | -0.28381 | 123.5184 | 3.1815 | 82.1457 | 115.2374 | 123.523 | -123.848 | -123.8525
2891.7188 | 123.9258 | -61.3541 | 62.2375 | -0.19966 | 0.016024 | 0.0085 | 0.010824 | 0.058325 | -0.0014013 | 0.080758 | -58.1863 | 62.1872 | -61.6333 | -61.1618 | 54.0298 | 20.5215 | 6.1157 | 6.0654 | 62.1826 | -61.6379 | -0.27924 | -0.050354 | 3.1677 | 0.19226 | -8.2077 | -0.28381 | -0.054932 | 3.447 | 67.4698 | 67.4194 | 115.3839 | 123.5413 | 3.1677 | 123.5367 | 81.8756 | -0.28381 | 123.5413 | 3.1677 | 81.8756 | 115.3839 | 123.5367 | -123.8709 | -123.8754
2892.7188 | 123.9075 | -61.3541 | 62.2467 | -0.27596 | 0.016878 | 0.013627 | 0.014029 | 0.060675 | -0.00076053 | 0.079476 | -58.1772 | 62.1689 | -61.6379 | -61.5005 | 53.7918 | 20.6955 | 6.2668 | 5.9875 | 62.2192 | -61.6516 | -0.28381 | -0.07782 | 3.1769 | -0.14648 | -8.4549 | -0.29755 | -0.027466 | 3.4607 | 67.6209 | 67.3416 | 115.1459 | 123.5229 | 3.1769 | 123.5733 | 82.0496 | -0.29755 | 123.5229 | 3.1769 | 82.0496 | 115.1459 | 123.5733 | -123.8846 | -123.8983
2893.7188 | 123.848 | -61.3724 | 62.2833 | -0.11574 | 0.016665 | 0.014054 | 0.015524 | 0.061743 | 0.0018031 | 0.079476 | -58.2001 | 62.265 | -61.6791 | -61.5417 | 53.8925 | 20.7413 | 6.395 | 5.9097 | 62.2559 | -61.6928 | -0.3067 | -0.01831 | 3.1723 | -0.16937 | -8.3908 | -0.32044 | -0.027466 | 3.479 | 67.7673 | 67.2821 | 115.2649 | 123.6374 | 3.1723 | 123.6282 | 82.1136 | -0.32044 | 123.6374 | 3.1723 | 82.1136 | 115.2649 | 123.6282 | -123.9624 | -123.9761
2894.7188 | 123.9258 | -61.3678 | 62.233 | -3.9533 | 0.01282 | 0.015977 | 0.0091152 | 0.062384 | 9.4068e-05 | 0.081399 | -58.3145 | 62.1918 | -61.6516 | -61.496 | 53.8284 | 20.7962 | 6.3766 | 6.0425 | 62.2238 | -61.615 | -0.28381 | -0.041199 | 3.0533 | -0.12817 | -8.4045 | -0.24719 | -0.009155 | 3.3371 | 67.7444 | 67.4103 | 115.1962 | 123.5596 | 3.0533 | 123.5916 | 82.164 | -0.24719 | 123.5596 | 3.0533 | 82.164 | 115.1962 | 123.5916 | -123.8846 | -123.848
2895.7188 | 123.8754 | -61.3724 | 62.2513 | -0.1844 | 0.017519 | 0.013841 | 0.0095424 | 0.062171 | -0.0014013 | 0.081399 | -58.2047 | 62.1872 | -61.6562 | -61.5005 | 53.8239 | 20.8099 | 6.3446 | 5.9921 | 62.2101 | -61.6333 | -0.28381 | -0.064087 | 3.1677 | -0.12817 | -8.4274 | -0.26093 | -0.041199 | 3.4515 | 67.717 | 67.3645 | 115.1962 | 123.5596 | 3.1677 | 123.5825 | 82.1823 | -0.26093 | 123.5596 | 3.1677 | 82.1823 | 115.1962 | 123.5825 | -123.9075 | -123.8846
2896.7188 | 123.9029 | -61.3449 | 62.2513 | -0.131 | 0.015597 | 0.014268 | 0.01296 | 0.059821 | 0.0011621 | 0.082253 | -58.2184 | 62.1506 | -61.6653 | -61.5051 | 53.7781 | 20.8145 | 6.4362 | 6.0791 | 62.2375 | -61.6562 | -0.32043 | -0.10071 | 3.1265 | -0.16022 | -8.4732 | -0.31128 | -0.013733 | 3.447 | 67.7811 | 67.424 | 115.123 | 123.4955 | 3.1265 | 123.5825 | 82.1594 | -0.31128 | 123.4955 | 3.1265 | 82.1594 | 115.123 | 123.5825 | -123.9166 | -123.9075
2897.7188 | 123.9349 | -61.3495 | 62.265 | -0.15388 | 0.013247 | 0.018327 | 0.0084744 | 0.060248 | 0.00073487 | 0.081826 | -58.2413 | 62.1552 | -61.6516 | -61.4685 | 53.92 | 21.0251 | 6.308 | 6.0745 | 62.1964 | -61.6196 | -0.30212 | -0.10986 | 3.1082 | -0.11902 | -8.345 | -0.27008 | -0.068665 | 3.4103 | 67.6575 | 67.424 | 115.2695 | 123.5046 | 3.1082 | 123.5458 | 82.3746 | -0.27008 | 123.5046 | 3.1082 | 82.3746 | 115.2695 | 123.5458 | -123.9166 | -123.8846
2898.7188 | 123.8251 | -61.409 | 62.2787 | -0.15388 | 0.016878 | 0.0132 | 0.015738 | 0.061103 | 0.00030767 | 0.080544 | -58.2596 | 62.2375 | -61.6745 | -61.5646 | 53.8788 | 20.8191 | 6.4911 | 5.9235 | 62.2284 | -61.6882 | -0.2655 | -0.041199 | 3.1494 | -0.15564 | -8.4 | -0.27923 | -0.050354 | 3.4149 | 67.9001 | 67.3325 | 115.2878 | 123.6465 | 3.1494 | 123.6374 | 82.2281 | -0.27923 | 123.6465 | 3.1494 | 82.2281 | 115.2878 | 123.6374 | -123.9532 | -123.967
2899.7188 | 123.9166 | -61.3403 | 62.2559 | -0.024185 | 0.014315 | 0.012986 | 0.0095424 | 0.061103 | -0.00076053 | 0.08204 | -58.2596 | 62.1506 | -61.6653 | -61.4868 | 53.8696 | 20.8786 | 6.3263 | 6.0471 | 62.1964 | -61.6104 | -0.32501 | -0.10529 | 3.0807 | -0.14648 | -8.3862 | -0.27008 | -0.059509 | 3.4058 | 67.6666 | 67.3874 | 115.21 | 123.4909 | 3.0807 | 123.5367 | 82.2189 | -0.27008 | 123.4909 | 3.0807 | 82.2189 | 115.21 | 123.5367 | -123.9212 | -123.8663
2900.7188 | 123.9258 | -61.3495 | 62.2421 | -3.8541 | 0.017733 | 0.011491 | 0.012106 | 0.060248 | -0.00097413 | 0.081185 | -58.4335 | 62.1872 | -61.6516 | -61.496 | 53.8055 | 20.9244 | 6.3126 | 6.0104 | 62.1964 | -61.647 | -0.30212 | -0.054931 | 2.916 | -0.14648 | -8.4366 | -0.29755 | -0.045776 | 3.2181 | 67.662 | 67.3599 | 115.155 | 123.5367 | 2.916 | 123.5458 | 82.2739 | -0.29755 | 123.5367 | 2.916 | 82.2739 | 115.155 | 123.5458 | -123.8937 | -123.8892
2901.7188 | 123.9441 | -61.3495 | 62.2513 | -0.23018 | 0.015169 | 0.011277 | 0.0082608 | 0.064948 | 0.0022303 | 0.081399 | -58.1818 | 62.1414 | -61.6333 | -61.4227 | 53.9383 | 20.7962 | 6.2851 | 6.015 | 62.1918 | -61.6241 | -0.28381 | -0.10986 | 3.1677 | -0.073242 | -8.313 | -0.27466 | -0.05951 | 3.4515 | 67.6346 | 67.3645 | 115.2878 | 123.4909 | 3.1677 | 123.5413 | 82.1457 | -0.27466 | 123.4909 | 3.1677 | 82.1457 | 115.2878 | 123.5413 | -123.8846 | -123.8754
2902.7188 | 123.8754 | -61.3632 | 62.265 | -0.13863 | 0.016238 | 0.016191 | 0.011892 | 0.057685 | -0.0026831 | 0.081613 | -58.1863 | 62.1552 | -61.6608 | -61.4868 | 53.9383 | 20.8603 | 6.2897 | 6.0287 | 62.2055 | -61.615 | -0.29755 | -0.10986 | 3.1769 | -0.1236 | -8.3267 | -0.25177 | -0.05951 | 3.4744 | 67.6529 | 67.392 | 115.3015 | 123.5184 | 3.1769 | 123.5687 | 82.2235 | -0.25177 | 123.5184 | 3.1769 | 82.2235 | 115.3015 | 123.5687 | -123.9258 | -123.88
2903.7188 | 123.8205 | -61.3861 | 62.265 | -0.12337 | 0.017306 | 0.014695 | 0.019583 | 0.061316 | 0.0011621 | 0.080544 | -58.1955 | 62.2742 | -61.647 | -61.5234 | 53.8879 | 20.9015 | 6.3538 | 5.9647 | 62.2421 | -61.6791 | -0.26093 | 0.009155 | 3.1906 | -0.13733 | -8.3771 | -0.29297 | -0.022889 | 3.4515 | 67.7399 | 67.3508 | 115.274 | 123.6603 | 3.1906 | 123.6282 | 82.2876 | -0.29297 | 123.6603 | 3.1906 | 82.2876 | 115.274 | 123.6282 | -123.912 | -123.9441
2904.7344 | 123.7656 | -61.4136 | 62.2604 | 0.029221 | 0.020937 | 0.015763 | 0.016806 | 0.065589 | 0.00073487 | 0.078835 | -58.255 | 62.2513 | -61.702 | -61.6241 | 53.7781 | 20.755 | 6.3126 | 5.7632 | 62.2421 | -61.7157 | -0.28839 | -0.009155 | 3.1586 | -0.21057 | -8.4824 | -0.30212 | -0.018311 | 3.447 | 67.7261 | 67.1768 | 115.1916 | 123.6649 | 3.1586 | 123.6557 | 82.1686 | -0.30212 | 123.6649 | 3.1586 | 82.1686 | 115.1916 | 123.6557 | -123.9624 | -123.9761
2905.7188 | 123.9395 | -61.3724 | 62.2375 | -0.062332 | 0.01581 | 0.014695 | 0.0082608 | 0.059821 | -0.00054693 | 0.081399 | -58.255 | 62.146 | -61.6837 | -61.4914 | 53.92 | 20.9747 | 6.1386 | 6.0608 | 62.233 | -61.6058 | -0.31128 | -0.091553 | 3.1174 | -0.11902 | -8.3176 | -0.23346 | -0.004578 | 3.4287 | 67.511 | 67.4332 | 115.2924 | 123.5184 | 3.1174 | 123.6053 | 82.3471 | -0.23346 | 123.5184 | 3.1174 | 82.3471 | 115.2924 | 123.6053 | -123.9212 | -123.8434
2906.7188 | 123.912 | -61.3586 | 62.233 | -1.5653 | 0.016878 | 0.012132 | 0.0097562 | 0.060889 | -0.0016149 | 0.082894 | -58.3237 | 62.1414 | -61.6791 | -61.5005 | 53.9474 | 21.0938 | 6.1569 | 6.0059 | 62.2101 | -61.6425 | -0.32043 | -0.091553 | 3.035 | -0.14191 | -8.2855 | -0.28381 | -0.022888 | 3.3554 | 67.5156 | 67.3645 | 115.3061 | 123.5001 | 3.035 | 123.5687 | 82.4524 | -0.28381 | 123.5001 | 3.035 | 82.4524 | 115.3061 | 123.5687 | -123.912 | -123.8754
2907.7188 | 123.9075 | -61.3312 | 62.2559 | -1.634 | 0.013674 | 0.015977 | 0.0097562 | 0.062384 | -0.0011877 | 0.078622 | -58.1863 | 62.1918 | -61.6287 | -61.4868 | 53.9658 | 20.8969 | 6.1615 | 6.0104 | 62.2238 | -61.6333 | -0.29755 | -0.064087 | 3.1448 | -0.15564 | -8.2901 | -0.30212 | -0.032043 | 3.4424 | 67.4927 | 67.3416 | 115.2969 | 123.5229 | 3.1448 | 123.555 | 82.2281 | -0.30212 | 123.5229 | 3.1448 | 82.2281 | 115.2969 | 123.555 | -123.8846 | -123.8892
2908.7188 | 123.8434 | -61.3815 | 62.265 | -0.069961 | 0.018587 | 0.013841 | 0.019156 | 0.060462 | 0.0018031 | 0.080331 | -58.2321 | 62.2467 | -61.6608 | -61.5509 | 53.8422 | 20.9839 | 6.221 | 5.8868 | 62.2238 | -61.6837 | -0.27924 | -0.018311 | 3.1494 | -0.16937 | -8.4229 | -0.30212 | -0.041199 | 3.4286 | 67.6025 | 67.2684 | 115.2237 | 123.6282 | 3.1494 | 123.6053 | 82.3654 | -0.30212 | 123.6282 | 3.1494 | 82.3654 | 115.2237 | 123.6053 | -123.9258 | -123.9487
2909.7344 | 123.8159 | -61.4136 | 62.2375 | 0.059738 | 0.017092 | 0.021104 | 0.01531 | 0.063666 | 0.0013757 | 0.080758 | -58.3282 | 62.2421 | -61.6974 | -61.6104 | 53.8055 | 20.874 | 6.2714 | 5.8502 | 62.2421 | -61.6928 | -0.28381 | 0.004577 | 3.0853 | -0.19684 | -8.432 | -0.27924 | 0.004577 | 3.3691 | 67.6849 | 67.2638 | 115.2191 | 123.6557 | 3.0853 | 123.6557 | 82.2876 | -0.27924 | 123.6557 | 3.0853 | 82.2876 | 115.2191 | 123.6557 | -123.9349 | -123.9304
2910.7188 | 123.8663 | -61.3724 | 62.2375 | -0.19203 | 0.014101 | 0.014909 | 0.0091152 | 0.061743 | -0.00097413 | 0.081185 | -58.2458 | 62.1735 | -61.6516 | -61.5143 | 54.007 | 21.1212 | 6.2622 | 6.0928 | 62.2147 | -61.615 | -0.27924 | -0.064087 | 3.1265 | -0.14191 | -8.2306 | -0.24262 | -0.022888 | 3.4058 | 67.6346 | 67.4652 | 115.3793 | 123.5458 | 3.1265 | 123.587 | 82.4936 | -0.24262 | 123.5458 | 3.1265 | 82.4936 | 115.3793 | 123.587 | -123.8892 | -123.8525
2911.7188 | 123.9349 | -61.3312 | 62.2559 | -0.1844 | 0.013674 | 0.013413 | 0.0074062 | 0.061316 | -0.00076053 | 0.080331 | -58.2138 | 62.146 | -61.6425 | -61.4777 | 54.0527 | 21.2265 | 6.2256 | 6.102 | 62.178 | -61.6425 | -0.31128 | -0.10986 | 3.1174 | -0.14648 | -8.2031 | -0.31128 | -0.077819 | 3.4287 | 67.5568 | 67.4332 | 115.3839 | 123.4772 | 3.1174 | 123.5092 | 82.5577 | -0.31128 | 123.4772 | 3.1174 | 82.5577 | 115.3839 | 123.5092 | -123.8983 | -123.8983
2912.7188 | 123.9395 | -61.3358 | 62.2284 | -0.16151 | 0.013674 | 0.012559 | 0.010397 | 0.060675 | 9.4068e-05 | 0.082467 | -58.2275 | 62.1185 | -61.6287 | -61.4777 | 54.071 | 21.2082 | 6.221 | 6.102 | 62.2009 | -61.6333 | -0.29297 | -0.10986 | 3.1082 | -0.14191 | -8.1573 | -0.29755 | -0.027466 | 3.4012 | 67.5568 | 67.4377 | 115.4068 | 123.4543 | 3.1082 | 123.5367 | 82.5439 | -0.29755 | 123.4543 | 3.1082 | 82.5439 | 115.4068 | 123.5367 | -123.8571 | -123.8617
2913.7188 | 123.8434 | -61.409 | 62.2559 | -0.031814 | 0.018374 | 0.015336 | 0.020651 | 0.060889 | 0.0018031 | 0.07969 | -58.2642 | 62.2421 | -61.6745 | -61.5326 | 53.9246 | 20.8969 | 6.4774 | 6.015 | 62.2284 | -61.702 | -0.2655 | -0.013733 | 3.1448 | -0.1236 | -8.3313 | -0.29297 | -0.027465 | 3.4103 | 67.8864 | 67.424 | 115.3336 | 123.6511 | 3.1448 | 123.6374 | 82.3059 | -0.29297 | 123.6511 | 3.1448 | 82.3059 | 115.3336 | 123.6374 | -123.9304 | -123.9578
2914.7188 | 123.8388 | -61.3632 | 62.2559 | -0.27596 | 0.017519 | 0.016831 | 0.014669 | 0.062171 | -0.00054693 | 0.080972 | -58.2642 | 62.2742 | -61.6653 | -61.5372 | 53.9017 | 21.0892 | 6.3492 | 5.9509 | 62.2513 | -61.6791 | -0.30212 | 0.018311 | 3.0991 | -0.17395 | -8.3542 | -0.31586 | -0.004577 | 3.4012 | 67.7124 | 67.3141 | 115.2649 | 123.6374 | 3.0991 | 123.6145 | 82.4524 | -0.31586 | 123.6374 | 3.0991 | 82.4524 | 115.2649 | 123.6145 | -123.9212 | -123.9349
2915.7188 | 123.9029 | -61.3632 | 62.2421 | -0.3141 | 0.017947 | 0.01854 | 0.0074062 | 0.062812 | 0.00052127 | 0.082681 | -58.461 | 62.1552 | -61.6608 | -61.5372 | 54.0436 | 21.2082 | 6.2027 | 6.015 | 62.2147 | -61.615 | -0.29755 | -0.086975 | 2.9022 | -0.17395 | -8.1985 | -0.25177 | -0.027465 | 3.1998 | 67.5659 | 67.3782 | 115.4068 | 123.5184 | 2.9022 | 123.5779 | 82.5714 | -0.25177 | 123.5184 | 2.9022 | 82.5714 | 115.4068 | 123.5779 | -123.9029 | -123.8571
2916.7188 | 123.8709 | -61.377 | 62.2467 | -0.21492 | 0.017519 | 0.014482 | 0.010611 | 0.060034 | 0.00052127 | 0.082894 | -58.2779 | 62.1643 | -61.6562 | -61.5234 | 54.0482 | 21.199 | 6.3446 | 6.0379 | 62.2421 | -61.6379 | -0.27924 | -0.082397 | 3.0991 | -0.14648 | -8.1985 | -0.26093 | -0.004578 | 3.3783 | 67.7216 | 67.4149 | 115.4251 | 123.5413 | 3.0991 | 123.6191 | 82.576 | -0.26093 | 123.5413 | 3.0991 | 82.576 | 115.4251 | 123.6191 | -123.9029 | -123.8846
2917.7188 | 123.8434 | -61.3953 | 62.2696 | -0.13863 | 0.014742 | 0.020463 | 0.010397 | 0.061103 | 0.00073487 | 0.081185 | -58.2275 | 62.1735 | -61.6653 | -61.5372 | 54.0894 | 21.2448 | 6.34 | 6.0562 | 62.2009 | -61.615 | -0.27008 | -0.09613 | 3.1677 | -0.14191 | -8.1802 | -0.21973 | -0.068664 | 3.4378 | 67.7353 | 67.4515 | 115.4846 | 123.5687 | 3.1677 | 123.5962 | 82.6401 | -0.21973 | 123.5687 | 3.1677 | 82.6401 | 115.4846 | 123.5962 | -123.9349 | -123.8846
2918.7188 | 123.8571 | -61.3861 | 62.2696 | -0.1844 | 0.017947 | 0.018968 | 0.016806 | 0.062812 | -0.00011953 | 0.079476 | -58.2275 | 62.2787 | -61.6287 | -61.5509 | 53.9795 | 21.1578 | 6.4133 | 6.0562 | 62.233 | -61.7065 | -0.24262 | 0.009156 | 3.1586 | -0.16479 | -8.2901 | -0.32044 | -0.036621 | 3.4012 | 67.7994 | 67.4423 | 115.3656 | 123.6649 | 3.1586 | 123.6191 | 82.5439 | -0.32044 | 123.6649 | 3.1586 | 82.5439 | 115.3656 | 123.6191 | -123.8983 | -123.9761
2919.7188 | 123.848 | -61.3358 | 62.2009 | -0.1844 | 0.01346 | 0.0132 | 0.0091152 | 0.063666 | -0.00076053 | 0.080972 | -58.2275 | 62.1323 | -61.647 | -61.496 | 54.158 | 21.2723 | 6.4682 | 6.5048 | 62.2604 | -61.5875 | -0.31128 | -0.068665 | 3.1082 | -0.16022 | -8.0429 | -0.25177 | 0.059509 | 3.4195 | 67.804 | 67.8406 | 115.4938 | 123.468 | 3.1082 | 123.5962 | 82.608 | -0.25177 | 123.468 | 3.1082 | 82.608 | 115.4938 | 123.5962 | -123.848 | -123.7885
2920.7188 | 123.8754 | -61.3815 | 62.2238 | -0.21492 | 0.015169 | 0.012986 | 0.0099698 | 0.062171 | -0.0020421 | 0.081613 | -58.2184 | 62.1368 | -61.6653 | -61.5097 | 54.0619 | 21.3364 | 6.5277 | 6.1478 | 62.2284 | -61.6333 | -0.28381 | -0.086975 | 3.1631 | -0.12817 | -8.1619 | -0.25177 | 0.004578 | 3.447 | 67.9092 | 67.5293 | 115.4434 | 123.5184 | 3.1631 | 123.6099 | 82.7179 | -0.25177 | 123.5184 | 3.1631 | 82.7179 | 115.4434 | 123.6099 | -123.8892 | -123.8571
2921.7188 | 123.9075 | -61.3586 | 62.2421 | -0.2607 | 0.014956 | 0.0095682 | 0.011892 | 0.060034 | -0.0028967 | 0.080544 | -58.287 | 62.1506 | -61.6653 | -61.5143 | 54.0756 | 21.3364 | 6.459 | 6.0745 | 62.1872 | -61.647 | -0.3067 | -0.091552 | 3.0716 | -0.15564 | -8.1665 | -0.28839 | -0.054931 | 3.3783 | 67.8177 | 67.4332 | 115.4343 | 123.5092 | 3.0716 | 123.5458 | 82.695 | -0.28839 | 123.5092 | 3.0716 | 82.695 | 115.4343 | 123.5458 | -123.9075 | -123.8892
2922.7188 | 123.8342 | -61.3907 | 62.2513 | -0.23781 | 0.014101 | 0.014268 | 0.014029 | 0.060462 | -0.00054693 | 0.081826 | -58.3054 | 62.1826 | -61.6608 | -61.5601 | 54.1214 | 21.3455 | 6.5689 | 6.0608 | 62.2467 | -61.6562 | -0.27008 | -0.068665 | 3.0853 | -0.16937 | -8.1299 | -0.2655 | -0.004578 | 3.3554 | 67.9596 | 67.4515 | 115.5121 | 123.5733 | 3.0853 | 123.6374 | 82.7362 | -0.2655 | 123.5733 | 3.0853 | 82.7362 | 115.5121 | 123.6374 | -123.912 | -123.9075
2923.7188 | 123.8159 | -61.409 | 62.2604 | -0.08522 | 0.017306 | 0.017045 | 0.017447 | 0.060889 | 0.00052127 | 0.081185 | -58.3054 | 62.2604 | -61.6974 | -61.5509 | 54.1122 | 21.2219 | 6.4316 | 5.9189 | 62.2192 | -61.7157 | -0.28839 | 0 | 3.1036 | -0.14191 | -8.1482 | -0.3067 | -0.041199 | 3.392 | 67.8406 | 67.3279 | 115.5212 | 123.6694 | 3.1036 | 123.6282 | 82.6309 | -0.3067 | 123.6694 | 3.1036 | 82.6309 | 115.5212 | 123.6282 | -123.9578 | -123.9761
2924.7188 | 123.8617 | -61.3815 | 62.2375 | -0.23018 | 0.014742 | 0.014909 | 0.0099698 | 0.061743 | -0.00011953 | 0.082253 | -58.2642 | 62.1689 | -61.6653 | -61.528 | 54.1122 | 21.2952 | 6.4682 | 6.015 | 62.2192 | -61.6287 | -0.28381 | -0.068665 | 3.1174 | -0.14648 | -8.1253 | -0.24719 | -0.018311 | 3.4012 | 67.8497 | 67.3965 | 115.4938 | 123.5504 | 3.1174 | 123.6008 | 82.6767 | -0.24719 | 123.5504 | 3.1174 | 82.6767 | 115.4938 | 123.6008 | -123.9029 | -123.8663
2925.7188 | 123.912 | -61.3678 | 62.2101 | -0.1844 | 0.012392 | 0.012986 | 0.010397 | 0.055762 | -0.0037511 | 0.081399 | -58.2504 | 62.1689 | -61.6379 | -61.6882 | 53.8788 | 21.2631 | 6.3492 | 5.9189 | 62.1735 | -61.6104 | -0.27008 | -0.041199 | 3.1174 | -0.32043 | -8.3313 | -0.24262 | -0.036621 | 3.3875 | 67.717 | 67.2867 | 115.2466 | 123.5367 | 3.1174 | 123.5413 | 82.6309 | -0.24262 | 123.5367 | 3.1174 | 82.6309 | 115.2466 | 123.5413 | -123.848 | -123.8205
2926.7188 | 123.8846 | -61.3632 | 62.2238 | -0.17677 | 0.016238 | 0.016191 | 0.010824 | 0.059394 | -0.0014013 | 0.083749 | -58.2275 | 62.1552 | -61.6379 | -61.5005 | 54.1031 | 21.2494 | 6.8985 | 6.2805 | 62.2559 | -61.5875 | -0.27466 | -0.068665 | 3.1357 | -0.13733 | -8.1207 | -0.2243 | 0.032043 | 3.4103 | 68.2617 | 67.6437 | 115.4663 | 123.5184 | 3.1357 | 123.6191 | 82.6126 | -0.2243 | 123.5184 | 3.1357 | 82.6126 | 115.4663 | 123.6191 | -123.8617 | -123.8113
2927.7188 | 123.8937 | -61.3678 | 62.2467 | -0.23781 | 0.01346 | 0.016404 | 0.01232 | 0.05918 | -0.0016149 | 0.080544 | -58.2275 | 62.1872 | -61.647 | -61.4914 | 54.1214 | 21.2723 | 6.3629 | 6.0425 | 62.1872 | -61.6241 | -0.27924 | -0.059509 | 3.1403 | -0.1236 | -8.1253 | -0.25635 | -0.059509 | 3.4195 | 67.7307 | 67.4103 | 115.4892 | 123.555 | 3.1403 | 123.555 | 82.6401 | -0.25635 | 123.555 | 3.1403 | 82.6401 | 115.4892 | 123.555 | -123.8937 | -123.8709
2928.7188 | 123.8342 | -61.3907 | 62.2833 | -0.19966 | 0.017306 | 0.015763 | 0.017447 | 0.06153 | -0.0016149 | 0.079904 | -58.2642 | 62.2559 | -61.6745 | -61.5463 | 54.0527 | 21.1029 | 6.4911 | 5.9875 | 62.2375 | -61.6882 | -0.28381 | -0.027466 | 3.1265 | -0.15564 | -8.2306 | -0.29755 | -0.045776 | 3.4103 | 67.8818 | 67.3782 | 115.4434 | 123.6465 | 3.1265 | 123.6282 | 82.4936 | -0.29755 | 123.6465 | 3.1265 | 82.4936 | 115.4434 | 123.6282 | -123.9578 | -123.9716
2929.7188 | 123.848 | -61.3907 | 62.2513 | -0.25307 | 0.014956 | 0.012559 | 0.0097562 | 0.062171 | -0.0011877 | 0.079904 | -58.2001 | 62.1643 | -61.6516 | -61.5372 | 54.0939 | 21.2036 | 6.5002 | 5.9921 | 62.2192 | -61.6516 | -0.26093 | -0.086975 | 3.1906 | -0.14648 | -8.1573 | -0.26093 | -0.032044 | 3.4515 | 67.8909 | 67.3828 | 115.4846 | 123.555 | 3.1906 | 123.6099 | 82.5943 | -0.26093 | 123.555 | 3.1906 | 82.5943 | 115.4846 | 123.6099 | -123.9029 | -123.9029
2930.7188 | 123.8525 | -61.3953 | 62.2742 | -0.24544 | 0.014529 | 0.014695 | 0.0093288 | 0.061957 | 0.00030767 | 0.082467 | -58.2184 | 62.1735 | -61.647 | -61.5143 | 53.9886 | 21.1441 | 6.4682 | 6.0379 | 62.2147 | -61.6196 | -0.25177 | -0.10071 | 3.1769 | -0.11902 | -8.2855 | -0.2243 | -0.059509 | 3.4286 | 67.8635 | 67.4332 | 115.3839 | 123.5687 | 3.1769 | 123.6099 | 82.5394 | -0.2243 | 123.5687 | 3.1769 | 82.5394 | 115.3839 | 123.6099 | -123.9212 | -123.8937
2931.7188 | 123.8754 | -61.3907 | 62.2604 | -0.15388 | 0.015383 | 0.012345 | 0.0097562 | 0.061957 | 9.4068e-05 | 0.079476 | -58.2504 | 62.1506 | -61.6562 | -61.5097 | 53.9703 | 21.2173 | 6.4224 | 6.0196 | 62.1918 | -61.6287 | -0.2655 | -0.10986 | 3.1403 | -0.11902 | -8.2901 | -0.23804 | -0.068665 | 3.4058 | 67.8131 | 67.4103 | 115.361 | 123.5413 | 3.1403 | 123.5825 | 82.608 | -0.23804 | 123.5413 | 3.1403 | 82.608 | 115.361 | 123.5825 | -123.9166 | -123.8892
2932.7188 | 123.967 | -61.3403 | 62.2421 | -0.09285 | 0.013888 | 0.011064 | 0.010611 | 0.060889 | 0.0015893 | 0.07969 | -58.2184 | 62.1506 | -61.6379 | -61.4685 | 54.0482 | 21.3455 | 6.3217 | 6.0059 | 62.2055 | -61.6333 | -0.29755 | -0.091552 | 3.1219 | -0.12817 | -8.194 | -0.29297 | -0.036621 | 3.4195 | 67.662 | 67.3462 | 115.3885 | 123.4909 | 3.1219 | 123.5458 | 82.6859 | -0.29297 | 123.4909 | 3.1219 | 82.6859 | 115.3885 | 123.5458 | -123.88 | -123.8754
2933.7188 | 123.7885 | -61.4227 | 62.2787 | 0.04448 | 0.020937 | 0.017686 | 0.015738 | 0.058966 | -0.00054693 | 0.080331 | -58.2596 | 62.2742 | -61.6745 | -61.5784 | 53.9566 | 21.1075 | 6.5689 | 5.8685 | 62.2604 | -61.6882 | -0.25177 | -0.004578 | 3.1631 | -0.15564 | -8.3221 | -0.2655 | -0.018311 | 3.4149 | 67.9916 | 67.2913 | 115.3793 | 123.6969 | 3.1631 | 123.6832 | 82.5302 | -0.2655 | 123.6969 | 3.1631 | 82.5302 | 115.3793 | 123.6832 | -123.9532 | -123.967
2934.7188 | 123.9258 | -61.3586 | 62.2467 | -0.19966 | 0.014956 | 0.014482 | 0.0084744 | 0.062384 | 0.00030767 | 0.078622 | -58.2138 | 62.1414 | -61.6699 | -61.2396 | 54.1855 | 20.9793 | 6.4865 | 6.0425 | 62.1872 | -61.6287 | -0.31128 | -0.10529 | 3.1448 | 0.11902 | -8.0612 | -0.27008 | -0.059509 | 3.4561 | 67.8452 | 67.4011 | 115.5441 | 123.5001 | 3.1448 | 123.5458 | 82.338 | -0.27008 | 123.5001 | 3.1448 | 82.338 | 115.5441 | 123.5458 | -123.9166 | -123.8754
2935.7188 | 123.8709 | -61.3403 | 62.2513 | -0.13863 | 0.014742 | 0.014054 | 0.010611 | 0.061103 | 0.00030767 | 0.080331 | -58.2367 | 62.1689 | -61.6379 | -61.5051 | 54.1168 | 21.254 | 6.5323 | 6.0745 | 62.2238 | -61.6104 | -0.29755 | -0.082398 | 3.1036 | -0.1648 | -8.1345 | -0.27008 | -0.027466 | 3.4012 | 67.8726 | 67.4149 | 115.4572 | 123.5092 | 3.1036 | 123.5641 | 82.5943 | -0.27008 | 123.5092 | 3.1036 | 82.5943 | 115.4572 | 123.5641 | -123.8892 | -123.8617
2936.7188 | 123.9349 | -61.3632 | 62.2375 | -0.054703 | 0.01346 | 0.012132 | 0.0082608 | 0.058325 | 0.00073487 | 0.081399 | -58.2275 | 62.1414 | -61.6608 | -61.496 | 54.1397 | 21.3364 | 6.4453 | 6.0883 | 62.1735 | -61.6058 | -0.29755 | -0.096131 | 3.1357 | -0.13275 | -8.0978 | -0.24262 | -0.064087 | 3.4332 | 67.8085 | 67.4515 | 115.5029 | 123.5046 | 3.1357 | 123.5367 | 82.6996 | -0.24262 | 123.5046 | 3.1357 | 82.6996 | 115.5029 | 123.5367 | -123.8983 | -123.8434
2937.7188 | 123.9304 | -61.4136 | 62.1826 | -0.16914 | 0.016665 | 0.015122 | 0.010397 | 0.060034 | 0.00052127 | 0.079263 | -58.2184 | 62.146 | -61.6608 | -61.5005 | 54.1626 | 21.5378 | 6.8436 | 5.7495 | 62.2055 | -61.6058 | -0.24719 | -0.036621 | 3.1952 | -0.086975 | -8.02 | -0.19226 | 0.022888 | 3.4424 | 68.2571 | 67.1631 | 115.5762 | 123.5596 | 3.1952 | 123.6191 | 82.9514 | -0.19226 | 123.5596 | 3.1952 | 82.9514 | 115.5762 | 123.6191 | -123.8434 | -123.7885
2938.7188 | 123.8251 | -61.4044 | 62.2467 | -0.15388 | 0.017092 | 0.016404 | 0.017447 | 0.061743 | 0.00094847 | 0.080544 | -58.2321 | 62.2421 | -61.6745 | -61.5417 | 54.1397 | 21.3409 | 6.7657 | 6.0562 | 62.2284 | -61.6791 | -0.27008 | -0.004578 | 3.1723 | -0.13733 | -8.107 | -0.27466 | -0.01831 | 3.4424 | 68.1702 | 67.4606 | 115.5441 | 123.6465 | 3.1723 | 123.6328 | 82.7454 | -0.27466 | 123.6465 | 3.1723 | 82.7454 | 115.5441 | 123.6328 | -123.9212 | -123.9258
2939.7188 | 123.9075 | -61.377 | 62.2238 | -0.016556 | 0.01346 | 0.011277 | 0.008688 | 0.06153 | 0.00073487 | 0.080758 | -58.3466 | 62.1597 | -61.6882 | -61.5372 | 54.1077 | 21.2402 | 6.5735 | 6.0471 | 62.2101 | -61.6287 | -0.31128 | -0.064087 | 3.0304 | -0.16022 | -8.1161 | -0.25177 | -0.013733 | 3.3417 | 67.9504 | 67.424 | 115.4846 | 123.5367 | 3.0304 | 123.587 | 82.6172 | -0.25177 | 123.5367 | 3.0304 | 82.6172 | 115.4846 | 123.587 | -123.912 | -123.8525
2940.7188 | 123.912 | -61.3724 | 62.2147 | -0.069961 | 0.016238 | 0.012345 | 0.010611 | 0.058753 | -0.00033333 | 0.081399 | -58.3099 | 62.1185 | -61.6608 | -61.5097 | 54.1351 | 21.4188 | 6.4819 | 6.102 | 62.1643 | -61.6333 | -0.28839 | -0.096131 | 3.0624 | -0.13733 | -8.0795 | -0.26093 | -0.050354 | 3.3508 | 67.8543 | 67.4744 | 115.5075 | 123.4909 | 3.0624 | 123.5367 | 82.7911 | -0.26093 | 123.4909 | 3.0624 | 82.7911 | 115.5075 | 123.5367 | -123.8754 | -123.848
2941.7188 | 123.9029 | -61.3907 | 62.233 | -0.031814 | 0.012392 | 0.012345 | 0.010611 | 0.057257 | -0.00011953 | 0.080972 | -58.2916 | 62.1323 | -61.6699 | -61.5417 | 54.0939 | 21.3638 | 6.514 | 6.0745 | 62.1918 | -61.6745 | -0.27924 | -0.10071 | 3.0991 | -0.15106 | -8.139 | -0.28381 | -0.041199 | 3.3783 | 67.9047 | 67.4652 | 115.4846 | 123.5229 | 3.0991 | 123.5825 | 82.7545 | -0.28381 | 123.5229 | 3.0991 | 82.7545 | 115.4846 | 123.5825 | -123.9029 | -123.9075
2942.7188 | 123.912 | -61.3632 | 62.2101 | -0.08522 | 0.013674 | 0.015977 | 0.010397 | 0.058753 | 0.0013757 | 0.079904 | -58.2687 | 62.1414 | -61.6653 | -61.5143 | 54.1672 | 21.4096 | 6.3675 | 6.015 | 62.1689 | -61.6287 | -0.30212 | -0.068665 | 3.0945 | -0.15106 | -8.0429 | -0.2655 | -0.041199 | 3.3966 | 67.7307 | 67.3782 | 115.5304 | 123.5046 | 3.0945 | 123.5321 | 82.7728 | -0.2655 | 123.5046 | 3.0945 | 82.7728 | 115.5304 | 123.5321 | -123.8754 | -123.8388
2943.7188 | 123.9075 | -61.3403 | 62.2284 | -0.5735 | 0.016665 | 0.012559 | 0.011465 | 0.059394 | -0.00033333 | 0.079476 | -58.2367 | 62.1323 | -61.6562 | -61.496 | 54.1626 | 21.4645 | 6.3263 | 6.0104 | 62.1964 | -61.615 | -0.31586 | -0.096131 | 3.1036 | -0.15564 | -8.0658 | -0.27466 | -0.032044 | 3.4195 | 67.6666 | 67.3508 | 115.5029 | 123.4726 | 3.1036 | 123.5367 | 82.8049 | -0.27466 | 123.4726 | 3.1036 | 82.8049 | 115.5029 | 123.5367 | -123.8846 | -123.8434
2944.7188 | 123.9166 | -61.3724 | 62.2238 | -0.047073 | 0.015169 | 0.015336 | 0.008688 | 0.061103 | -0.00011953 | 0.082467 | -58.2413 | 62.146 | -61.647 | -61.4914 | 54.2267 | 21.4645 | 6.3034 | 6.0471 | 62.1552 | -61.6379 | -0.27466 | -0.07782 | 3.1311 | -0.11902 | -7.9971 | -0.2655 | -0.068665 | 3.4058 | 67.6758 | 67.4194 | 115.5991 | 123.5184 | 3.1311 | 123.5275 | 82.8369 | -0.2655 | 123.5184 | 3.1311 | 82.8369 | 115.5991 | 123.5275 | -123.8708 | -123.8617
2945.7188 | 123.9212 | -61.3586 | 62.2421 | -0.077591 | 0.01346 | 0.013627 | 0.0080472 | 0.058966 | 0.0015893 | 0.081399 | -58.2596 | 62.1277 | -61.6791 | -61.5189 | 54.1718 | 21.4142 | 6.3492 | 6.0379 | 62.1826 | -61.6241 | -0.32043 | -0.11444 | 3.0991 | -0.16022 | -8.0704 | -0.2655 | -0.059509 | 3.4195 | 67.7078 | 67.3965 | 115.5304 | 123.4863 | 3.0991 | 123.5413 | 82.7728 | -0.2655 | 123.4863 | 3.0991 | 82.7728 | 115.5304 | 123.5413 | -123.9212 | -123.8663
2946.7188 | 123.8617 | -61.4044 | 62.2192 | -0.016556 | 0.015597 | 0.013627 | 0.011892 | 0.058325 | 0.00094847 | 0.081826 | -58.3466 | 62.1231 | -61.6608 | -61.5875 | 54.071 | 21.3547 | 6.34 | 5.9738 | 62.1597 | -61.6516 | -0.25635 | -0.09613 | 3.0579 | -0.18311 | -8.1482 | -0.24719 | -0.059509 | 3.3142 | 67.7444 | 67.3782 | 115.4755 | 123.5275 | 3.0579 | 123.5641 | 82.7591 | -0.24719 | 123.5275 | 3.0579 | 82.7591 | 115.4755 | 123.5641 | -123.88 | -123.8708
2947.7188 | 123.9166 | -61.3907 | 62.2421 | 0.0063326 | 0.012392 | 0.016191 | 0.0084744 | 0.059607 | 0.00030767 | 0.078835 | -58.3145 | 62.1368 | -61.702 | -61.5692 | 54.0802 | 21.2952 | 6.3904 | 6.0425 | 62.1689 | -61.647 | -0.31128 | -0.10529 | 3.0762 | -0.17853 | -8.1619 | -0.25635 | -0.073242 | 3.3875 | 67.7811 | 67.4332 | 115.4709 | 123.5275 | 3.0762 | 123.5596 | 82.6859 | -0.25635 | 123.5275 | 3.0762 | 82.6859 | 115.4709 | 123.5596 | -123.9441 | -123.8892
2948.7188 | 123.8571 | -61.3815 | 62.2055 | 0.5175 | 0.014101 | 0.018113 | 0.0099698 | 0.060034 | -0.00011953 | 0.080331 | -58.2779 | 62.1231 | -61.6837 | -61.5555 | 54.1306 | 21.3593 | 6.3629 | 6.0242 | 62.1643 | -61.6653 | -0.30212 | -0.082397 | 3.1036 | -0.17395 | -8.075 | -0.28381 | -0.041198 | 3.4058 | 67.7444 | 67.4057 | 115.5121 | 123.5046 | 3.1036 | 123.5458 | 82.7408 | -0.28381 | 123.5046 | 3.1036 | 82.7408 | 115.5121 | 123.5458 | -123.8892 | -123.8708
2949.7188 | 123.848 | -61.3953 | 62.2147 | 0.067368 | 0.016238 | 0.015336 | 0.010183 | 0.054694 | 0.0013757 | 0.081185 | -58.2825 | 62.1323 | -61.6791 | -61.6882 | 54.2038 | 21.3776 | 6.2714 | 5.9784 | 62.1689 | -61.6653 | -0.28381 | -0.082398 | 3.1128 | -0.29297 | -8.0109 | -0.27008 | -0.045777 | 3.3966 | 67.6666 | 67.3737 | 115.5991 | 123.5275 | 3.1128 | 123.5641 | 82.7728 | -0.27008 | 123.5275 | 3.1128 | 82.7728 | 115.5991 | 123.5641 | -123.8937 | -123.88
2950.7188 | 123.9029 | -61.409 | 62.2101 | -0.024185 | 0.017519 | 0.012559 | 0.0082608 | 0.057257 | -0.0022559 | 0.080758 | -58.342 | 62.1323 | -61.6882 | -61.5509 | 54.1489 | 21.405 | 6.3629 | 5.9921 | 62.1506 | -61.6379 | -0.27923 | -0.07782 | 3.067 | -0.14191 | -8.0612 | -0.22888 | -0.059509 | 3.3463 | 67.7719 | 67.4011 | 115.5579 | 123.5413 | 3.067 | 123.5596 | 82.814 | -0.22888 | 123.5413 | 3.067 | 82.814 | 115.5579 | 123.5596 | -123.8983 | -123.848
2951.7188 | 123.8525 | -61.377 | 62.2284 | 1.372 | 0.016024 | 0.013841 | 0.0080472 | 0.05918 | 0.0018031 | 0.080117 | -58.2047 | 62.146 | -61.6608 | -61.5646 | 54.1214 | 21.3181 | 6.2759 | 5.9326 | 62.114 | -61.6425 | -0.28381 | -0.082398 | 3.1723 | -0.18768 | -8.107 | -0.2655 | -0.11444 | 3.4561 | 67.6529 | 67.3096 | 115.4984 | 123.5229 | 3.1723 | 123.4909 | 82.695 | -0.2655 | 123.5229 | 3.1723 | 82.695 | 115.4984 | 123.4909 | -123.8892 | -123.8709
2952.7188 | 123.8663 | -61.3953 | 62.2238 | 0.067368 | 0.014742 | 0.013841 | 0.0095424 | 0.058753 | -0.00076053 | 0.07969 | -58.2962 | 62.1277 | -61.6791 | -61.5372 | 54.332 | 21.4325 | 6.0242 | 5.9052 | 62.1597 | -61.6425 | -0.28381 | -0.09613 | 3.0991 | -0.14191 | -7.8918 | -0.24719 | -0.064087 | 3.3829 | 67.4194 | 67.3004 | 115.7272 | 123.5229 | 3.0991 | 123.555 | 82.8278 | -0.24719 | 123.5229 | 3.0991 | 82.8278 | 115.7272 | 123.555 | -123.9029 | -123.8663
2953.7188 | 123.8937 | -61.3815 | 62.1872 | 0.12077 | 0.017092 | 0.015336 | 0.010397 | 0.060462 | 0.0022303 | 0.080758 | -58.2458 | 62.1323 | -61.6745 | -61.5417 | 54.1901 | 21.3272 | 6.2027 | 5.9647 | 62.1414 | -61.6562 | -0.29297 | -0.054932 | 3.1357 | -0.16022 | -7.9971 | -0.27466 | -0.045777 | 3.4287 | 67.5842 | 67.3462 | 115.5716 | 123.5138 | 3.1357 | 123.5229 | 82.7087 | -0.27466 | 123.5138 | 3.1357 | 82.7087 | 115.5716 | 123.5229 | -123.8617 | -123.8434
2954.7188 | 123.9029 | -61.3724 | 62.1964 | 0.19707 | 0.015169 | 0.014054 | 0.0095424 | 0.060462 | 0.0028711 | 0.07969 | -58.2596 | 62.1185 | -61.6837 | -61.5326 | 54.2542 | 21.3043 | 6.221 | 5.9921 | 62.1552 | -61.6425 | -0.31128 | -0.07782 | 3.1128 | -0.16022 | -7.9422 | -0.27008 | -0.041199 | 3.4241 | 67.5934 | 67.3645 | 115.6265 | 123.4909 | 3.1128 | 123.5275 | 82.6767 | -0.27008 | 123.4909 | 3.1128 | 82.6767 | 115.6265 | 123.5275 | -123.88 | -123.8388
2955.7188 | 123.8663 | -61.3907 | 62.2009 | 0.17418 | 0.016024 | 0.014268 | 0.011038 | 0.060248 | 0.0022303 | 0.080117 | -58.2413 | 62.1277 | -61.6699 | -61.5738 | 54.1489 | 21.2585 | 6.2256 | 5.9601 | 62.1414 | -61.6745 | -0.27924 | -0.073242 | 3.1494 | -0.18311 | -8.0521 | -0.28381 | -0.05951 | 3.4286 | 67.6163 | 67.3508 | 115.5396 | 123.5184 | 3.1494 | 123.5321 | 82.6492 | -0.28381 | 123.5184 | 3.1494 | 82.6492 | 115.5396 | 123.5321 | -123.8708 | -123.8754
2956.7188 | 123.8754 | -61.377 | 62.2192 | -0.039444 | 0.014529 | 0.012773 | 0.0078336 | 0.058753 | 0.0013757 | 0.081185 | -58.3832 | 62.146 | -61.6882 | -61.5463 | 54.2313 | 21.3226 | 6.3538 | 6.015 | 62.1689 | -61.6379 | -0.31128 | -0.073242 | 2.9938 | -0.16937 | -7.988 | -0.26093 | -0.050354 | 3.3051 | 67.7307 | 67.392 | 115.6082 | 123.5229 | 2.9938 | 123.5458 | 82.6996 | -0.26093 | 123.5229 | 2.9938 | 82.6996 | 115.6082 | 123.5458 | -123.9075 | -123.8571
2957.7188 | 123.8937 | -61.3861 | 62.2101 | 0.090256 | 0.015383 | 0.010423 | 0.0097562 | 0.060889 | 0.0026575 | 0.081185 | -58.2687 | 62.1368 | -61.6608 | -61.6013 | 54.2084 | 21.3409 | 6.2942 | 5.9326 | 62.1323 | -61.6425 | -0.27466 | -0.073242 | 3.1174 | -0.21515 | -8.0017 | -0.25635 | -0.07782 | 3.392 | 67.6804 | 67.3187 | 115.5945 | 123.5229 | 3.1174 | 123.5184 | 82.727 | -0.25635 | 123.5229 | 3.1174 | 82.727 | 115.5945 | 123.5184 | -123.8708 | -123.8525
2958.7188 | 123.9349 | -61.3495 | 62.2192 | -0.10048 | 0.01346 | 0.011704 | 0.0067654 | 0.059394 | 0.00094847 | 0.079904 | -58.2825 | 62.1506 | -61.647 | -61.496 | 54.158 | 21.3776 | 6.3263 | 6.0699 | 62.1506 | -61.6608 | -0.29755 | -0.068664 | 3.067 | -0.14648 | -8.0612 | -0.31128 | -0.068664 | 3.3646 | 67.6758 | 67.4194 | 115.5075 | 123.5001 | 3.067 | 123.5001 | 82.7271 | -0.31128 | 123.5001 | 3.067 | 82.7271 | 115.5075 | 123.5001 | -123.8663 | -123.88
2959.7188 | 123.8983 | -61.3724 | 62.1872 | 0.1284 | 0.016878 | 0.011704 | 0.0091152 | 0.059821 | -0.00011953 | 0.081399 | -58.2916 | 62.1506 | -61.6791 | -61.5372 | 54.1168 | 21.3638 | 6.2347 | 5.9555 | 62.1414 | -61.6516 | -0.3067 | -0.036621 | 3.0807 | -0.1648 | -8.0704 | -0.27924 | -0.045777 | 3.3875 | 67.6071 | 67.3279 | 115.4892 | 123.5229 | 3.0807 | 123.5138 | 82.7362 | -0.27924 | 123.5229 | 3.0807 | 82.7362 | 115.4892 | 123.5138 | -123.8663 | -123.8388
2960.7188 | 123.9532 | -61.377 | 62.1964 | 0.16655 | 0.017092 | 0.014482 | 0.014883 | 0.059607 | 0.00073487 | 0.080758 | -58.2367 | 62.1414 | -61.6562 | -61.5143 | 54.0665 | 21.3318 | 6.0928 | 5.7953 | 62.1048 | -61.6791 | -0.27924 | -0.054932 | 3.1403 | -0.13733 | -8.1299 | -0.30212 | -0.091553 | 3.4195 | 67.4698 | 67.1722 | 115.4434 | 123.5184 | 3.1403 | 123.4818 | 82.7087 | -0.30212 | 123.5184 | 3.1403 | 82.7087 | 115.4434 | 123.4818 | -123.8525 | -123.8754
2961.7188 | 123.8434 | -61.3632 | 62.2147 | 0.18944 | 0.01581 | 0.013413 | 0.012106 | 0.060462 | -0.00076053 | 0.081399 | -58.223 | 62.1323 | -61.6699 | -61.5372 | 53.9932 | 21.2173 | 6.1935 | 5.8594 | 62.1368 | -61.647 | -0.3067 | -0.082398 | 3.1403 | -0.17395 | -8.2214 | -0.28381 | -0.07782 | 3.447 | 67.5568 | 67.2226 | 115.3564 | 123.4955 | 3.1403 | 123.5001 | 82.5806 | -0.28381 | 123.4955 | 3.1403 | 82.5806 | 115.3564 | 123.5001 | -123.8846 | -123.8617
2962.7188 | 123.9166 | -61.3861 | 62.2009 | 0.17418 | 0.01581 | 0.015336 | 0.014456 | 0.062384 | 9.4068e-05 | 0.080544 | -58.1955 | 62.178 | -61.6974 | -61.4868 | 54.0802 | 21.3593 | 6.2805 | 6.0745 | 62.1277 | -61.6562 | -0.31128 | -0.022888 | 3.1906 | -0.10071 | -8.1207 | -0.27008 | -0.073242 | 3.5019 | 67.6666 | 67.4606 | 115.4663 | 123.5641 | 3.1906 | 123.5138 | 82.7454 | -0.27008 | 123.5641 | 3.1906 | 82.7454 | 115.4663 | 123.5138 | -123.8983 | -123.8571
2963.7188 | 123.8617 | -61.3907 | 62.2101 | -0.062332 | 0.014101 | 0.013841 | 0.0054836 | 0.061743 | 0.00030767 | 0.078408 | -58.287 | 62.1368 | -61.6791 | -61.5372 | 54.0848 | 21.3409 | 6.3126 | 6.0242 | 62.1689 | -61.6287 | -0.28839 | -0.073242 | 3.1036 | -0.14648 | -8.1253 | -0.23804 | -0.041199 | 3.392 | 67.7032 | 67.4149 | 115.4755 | 123.5275 | 3.1036 | 123.5596 | 82.7316 | -0.23804 | 123.5275 | 3.1036 | 82.7316 | 115.4755 | 123.5596 | -123.8892 | -123.8388
2964.7188 | 123.912 | -61.3632 | 62.1872 | -0.08522 | 0.017733 | 0.018968 | 0.01232 | 0.060889 | 0.0015893 | 0.078835 | -58.2184 | 62.1597 | -61.6608 | -61.5097 | 54.0207 | 21.4005 | 6.2393 | 6.0333 | 62.1414 | -61.6608 | -0.29755 | -0.027466 | 3.1448 | -0.14648 | -8.1665 | -0.29755 | -0.045777 | 3.4424 | 67.6025 | 67.3965 | 115.3839 | 123.5229 | 3.1448 | 123.5046 | 82.7637 | -0.29755 | 123.5229 | 3.1448 | 82.7637 | 115.3839 | 123.5046 | -123.848 | -123.848
2965.7188 | 123.9029 | -61.377 | 62.1735 | 0.16655 | 0.020937 | 0.018327 | 0.012106 | 0.060034 | -0.0016149 | 0.081185 | -58.4747 | 62.1323 | -61.6928 | -61.5326 | 54.1168 | 21.4874 | 6.1981 | 6.0013 | 62.1414 | -61.647 | -0.31586 | -0.041199 | 2.9022 | -0.15564 | -8.0566 | -0.27008 | -0.032044 | 3.2181 | 67.5751 | 67.3782 | 115.4938 | 123.5092 | 2.9022 | 123.5184 | 82.8644 | -0.27008 | 123.5092 | 2.9022 | 82.8644 | 115.4938 | 123.5184 | -123.8663 | -123.8205
2966.7188 | 123.8754 | -61.3541 | 62.2375 | -0.16151 | 0.014529 | 0.014268 | 0.0099698 | 0.059821 | -0.00011953 | 0.07969 | -58.255 | 62.1735 | -61.6882 | -61.4914 | 54.1077 | 21.46 | 6.3766 | 6.0608 | 62.178 | -61.6241 | -0.33417 | -0.064087 | 3.0991 | -0.13733 | -8.1299 | -0.27008 | -0.059509 | 3.4332 | 67.7307 | 67.4149 | 115.4617 | 123.5275 | 3.0991 | 123.5321 | 82.814 | -0.27008 | 123.5275 | 3.0991 | 82.814 | 115.4617 | 123.5321 | -123.9258 | -123.8617
2967.7188 | 123.8342 | -61.409 | 62.2192 | 0.24284 | 0.017306 | 0.017686 | 0.015097 | 0.062598 | -0.00033333 | 0.082467 | -58.3466 | 62.2009 | -61.7111 | -61.5921 | 54.0573 | 21.46 | 6.3217 | 5.8914 | 62.1735 | -61.6837 | -0.30212 | -0.01831 | 3.0624 | -0.1831 | -8.1619 | -0.27466 | -0.045776 | 3.3646 | 67.7307 | 67.3004 | 115.4663 | 123.6099 | 3.0624 | 123.5825 | 82.869 | -0.27466 | 123.6099 | 3.0624 | 82.869 | 115.4663 | 123.5825 | -123.9304 | -123.9029
2968.7188 | 123.8663 | -61.409 | 62.2101 | 0.090256 | 0.015169 | 0.010209 | 0.0099698 | 0.060248 | 9.4068e-05 | 0.083108 | -58.3099 | 62.1368 | -61.6745 | -61.5738 | 54.0939 | 21.4416 | 6.2942 | 5.9418 | 62.1872 | -61.6516 | -0.2655 | -0.073242 | 3.0991 | -0.16479 | -8.1161 | -0.24261 | -0.022888 | 3.3646 | 67.7032 | 67.3508 | 115.5029 | 123.5458 | 3.0991 | 123.5962 | 82.8506 | -0.24261 | 123.5458 | 3.0991 | 82.8506 | 115.5029 | 123.5962 | -123.8846 | -123.8617
2969.7188 | 123.9075 | -61.3815 | 62.2192 | 0.21996 | 0.019656 | 0.015977 | 0.015738 | 0.063452 | -0.00011953 | 0.082681 | -58.2916 | 62.2009 | -61.6882 | -61.5463 | 53.9795 | 21.3959 | 6.2576 | 5.9189 | 62.1231 | -61.6974 | -0.3067 | -0.01831 | 3.0899 | -0.16479 | -8.2397 | -0.31586 | -0.09613 | 3.3966 | 67.6392 | 67.3004 | 115.361 | 123.5825 | 3.0899 | 123.5046 | 82.7774 | -0.31586 | 123.5825 | 3.0899 | 82.7774 | 115.361 | 123.5046 | -123.9075 | -123.9166
2970.7188 | 123.8937 | -61.3815 | 62.178 | 0.15129 | 0.016665 | 0.016404 | 0.014883 | 0.061957 | -0.00033333 | 0.081826 | -58.2916 | 62.1414 | -61.6837 | -61.5326 | 54.0619 | 21.4188 | 6.2073 | 6.0699 | 62.1552 | -61.6562 | -0.30212 | -0.036622 | 3.0899 | -0.15106 | -8.1162 | -0.27466 | -0.022889 | 3.392 | 67.5888 | 67.4515 | 115.4434 | 123.5229 | 3.0899 | 123.5367 | 82.8003 | -0.27466 | 123.5229 | 3.0899 | 82.8003 | 115.4434 | 123.5367 | -123.8617 | -123.8342
2971.7188 | 123.8937 | -61.3678 | 62.2192 | -0.016556 | 0.01581 | 0.015977 | 0.0093288 | 0.061316 | 0.00052127 | 0.082253 | -58.3099 | 62.1414 | -61.6791 | -61.5555 | 54.0298 | 21.3913 | 6.3217 | 6.1066 | 62.1506 | -61.6425 | -0.31128 | -0.07782 | 3.0579 | -0.18768 | -8.1894 | -0.27466 | -0.068664 | 3.3691 | 67.6895 | 67.4744 | 115.3976 | 123.5092 | 3.0579 | 123.5184 | 82.7591 | -0.27466 | 123.5092 | 3.0579 | 82.7591 | 115.3976 | 123.5184 | -123.8983 | -123.8617
2972.7188 | 123.8983 | -61.3724 | 62.1964 | 0.99052 | 0.016451 | 0.015763 | 0.014029 | 0.062598 | -0.00054693 | 0.082467 | -58.2138 | 62.1597 | -61.6516 | -61.5372 | 54.0436 | 21.4233 | 6.1935 | 6.102 | 62.1094 | -61.6653 | -0.27924 | -0.036621 | 3.1586 | -0.1648 | -8.1528 | -0.29297 | -0.086975 | 3.4378 | 67.5659 | 67.4744 | 115.416 | 123.5321 | 3.1586 | 123.4818 | 82.7957 | -0.29297 | 123.5321 | 3.1586 | 82.7957 | 115.416 | 123.4818 | -123.848 | -123.8617
2973.7188 | 123.8525 | -61.3815 | 62.1918 | -0.039444 | 0.014956 | 0.016618 | 0.0095424 | 0.059821 | -0.00033333 | 0.08204 | -58.3878 | 62.1323 | -61.6562 | -61.5829 | 54.0115 | 21.4371 | 6.3171 | 6.0654 | 62.1552 | -61.6241 | -0.27466 | -0.059509 | 2.9938 | -0.20142 | -8.1802 | -0.24262 | -0.036621 | 3.2684 | 67.6987 | 67.4469 | 115.3931 | 123.5138 | 2.9938 | 123.5367 | 82.8186 | -0.24262 | 123.5138 | 2.9938 | 82.8186 | 115.3931 | 123.5367 | -123.848 | -123.8159
2974.7188 | 123.7885 | -61.409 | 62.2192 | 0.1284 | 0.01816 | 0.017899 | 0.015951 | 0.060889 | -0.00033333 | 0.081399 | -58.342 | 62.233 | -61.7157 | -61.6333 | 53.9062 | 21.3226 | 6.4133 | 5.9784 | 62.1872 | -61.7111 | -0.3067 | 0.013733 | 3.067 | -0.2243 | -8.313 | -0.30212 | -0.032043 | 3.3737 | 67.8223 | 67.3874 | 115.3152 | 123.642 | 3.067 | 123.5962 | 82.7316 | -0.30212 | 123.642 | 3.067 | 82.7316 | 115.3152 | 123.5962 | -123.9349 | -123.9304
2975.7188 | 123.88 | -61.4136 | 62.2238 | 0.21233 | 0.017733 | 0.015763 | 0.013601 | 0.063666 | -0.00076053 | 0.080331 | -58.3145 | 62.2192 | -61.702 | -61.5967 | 53.9658 | 21.4325 | 6.3858 | 6.0516 | 62.1872 | -61.702 | -0.28839 | -0.004578 | 3.0991 | -0.18311 | -8.2581 | -0.28839 | -0.036621 | 3.3875 | 67.7994 | 67.4652 | 115.3793 | 123.6328 | 3.0991 | 123.6008 | 82.8461 | -0.28839 | 123.6328 | 3.0991 | 82.8461 | 115.3793 | 123.6008 | -123.9258 | -123.9258
2976.7344 | 123.8983 | -61.3632 | 62.1964 | 0.17418 | 0.015383 | 0.013627 | 0.011892 | 0.061957 | 0.0013757 | 0.08204 | -58.2275 | 62.1643 | -61.6882 | -61.5372 | 53.9383 | 21.4096 | 6.3446 | 6.1295 | 62.1506 | -61.6241 | -0.32501 | -0.032043 | 3.1357 | -0.17395 | -8.2581 | -0.26093 | -0.045776 | 3.4607 | 67.7078 | 67.4927 | 115.3015 | 123.5275 | 3.1357 | 123.5138 | 82.7728 | -0.26093 | 123.5275 | 3.1357 | 82.7728 | 115.3015 | 123.5138 | -123.8846 | -123.8205
2977.7188 | 123.848 | -61.4182 | 62.1964 | 0.17418 | 0.020296 | 0.017899 | 0.019156 | 0.061743 | 0.0015893 | 0.080544 | -58.2916 | 62.2284 | -61.702 | -61.6196 | 53.8513 | 21.3181 | 6.3812 | 5.9692 | 62.1964 | -61.7111 | -0.28381 | 0.032044 | 3.1265 | -0.20142 | -8.345 | -0.29297 | 0 | 3.4103 | 67.7994 | 67.3874 | 115.2695 | 123.6465 | 3.1265 | 123.6145 | 82.7362 | -0.29297 | 123.6465 | 3.1265 | 82.7362 | 115.2695 | 123.6145 | -123.8983 | -123.9075
2978.7344 | 123.9807 | -61.3586 | 62.2055 | -0.069961 | 0.013674 | 0.015122 | 0.0054836 | 0.060034 | -0.0020421 | 0.082253 | -58.2504 | 62.1506 | -61.6562 | -61.4594 | 54.0024 | 21.4554 | 6.3309 | 6.1478 | 62.1964 | -61.6196 | -0.29755 | -0.054931 | 3.1082 | -0.10071 | -8.2031 | -0.26093 | -0.009155 | 3.4058 | 67.6895 | 67.5064 | 115.361 | 123.5092 | 3.1082 | 123.555 | 82.814 | -0.26093 | 123.5092 | 3.1082 | 82.814 | 115.361 | 123.555 | -123.8617 | -123.8251
2979.7188 | 123.8937 | -61.3998 | 62.2147 | 0.16655 | 0.017733 | 0.012986 | 0.01531 | 0.062598 | 9.4068e-05 | 0.083322 | -58.3145 | 62.1964 | -61.6653 | -61.5692 | 53.8742 | 21.3043 | 6.3538 | 6.0471 | 62.146 | -61.702 | -0.2655 | -0.018311 | 3.0853 | -0.16937 | -8.3405 | -0.30212 | -0.068665 | 3.3508 | 67.7536 | 67.4469 | 115.274 | 123.5962 | 3.0853 | 123.5458 | 82.7042 | -0.30212 | 123.5962 | 3.0853 | 82.7042 | 115.274 | 123.5458 | -123.88 | -123.9166
2980.7188 | 123.9029 | -61.3907 | 62.1964 | 0.15892 | 0.017733 | 0.022813 | 0.01531 | 0.062812 | -0.00033333 | 0.081826 | -58.3237 | 62.2375 | -61.702 | -61.5829 | 53.801 | 21.3181 | 6.3354 | 5.9921 | 62.1597 | -61.7157 | -0.31128 | 0.041199 | 3.067 | -0.19226 | -8.3954 | -0.32501 | -0.036621 | 3.3783 | 67.7261 | 67.3828 | 115.1917 | 123.6282 | 3.067 | 123.5504 | 82.7087 | -0.32501 | 123.6282 | 3.067 | 82.7087 | 115.1917 | 123.5504 | -123.8983 | -123.912
2981.7344 | 123.848 | -61.3861 | 62.2467 | -0.23018 | 0.018801 | 0.014054 | 0.014669 | 0.063025 | -0.00076053 | 0.079049 | -58.3008 | 62.2742 | -61.6837 | -61.5555 | 53.9429 | 21.3455 | 6.5552 | 6.0471 | 62.2467 | -61.6608 | -0.29755 | 0.027466 | 3.0853 | -0.16937 | -8.3038 | -0.27466 | 0 | 3.3829 | 67.9413 | 67.4332 | 115.329 | 123.6603 | 3.0853 | 123.6328 | 82.7316 | -0.27466 | 123.6603 | 3.0853 | 82.7316 | 115.329 | 123.6328 | -123.9304 | -123.9075
2982.7188 | 123.8571 | -61.3998 | 62.1964 | 0.15892 | 0.01816 | 0.015977 | 0.014883 | 0.063239 | -0.00097413 | 0.083322 | -58.3649 | 62.2192 | -61.7065 | -61.5829 | 53.9612 | 21.46 | 6.4178 | 5.9601 | 62.2284 | -61.6882 | -0.3067 | 0.022888 | 3.035 | -0.18311 | -8.2352 | -0.28839 | 0.032044 | 3.3417 | 67.8177 | 67.3599 | 115.361 | 123.6191 | 3.035 | 123.6282 | 82.8598 | -0.28839 | 123.6191 | 3.035 | 82.8598 | 115.361 | 123.6282 | -123.9029 | -123.8846
2983.7188 | 123.9029 | -61.3815 | 62.2055 | 0.0063326 | 0.014956 | 0.014054 | 0.0061246 | 0.060248 | 0.0013757 | 0.082681 | -58.374 | 62.1735 | -61.6745 | -61.5601 | 54.0298 | 21.4828 | 6.4041 | 6.0791 | 62.2055 | -61.6562 | -0.29297 | -0.032043 | 3.0075 | -0.17853 | -8.1757 | -0.27466 | 0 | 3.3005 | 67.7856 | 67.4606 | 115.4114 | 123.555 | 3.0075 | 123.587 | 82.8644 | -0.27466 | 123.555 | 3.0075 | 82.8644 | 115.4114 | 123.587 | -123.88 | -123.8617
2984.7188 | 123.9075 | -61.4044 | 62.2101 | 0.19707 | 0.017947 | 0.014695 | 0.013815 | 0.063666 | 0.00030767 | 0.081185 | -58.287 | 62.1506 | -61.7065 | -61.5326 | 53.952 | 21.4691 | 6.3263 | 6.0928 | 62.146 | -61.6882 | -0.30212 | -0.059509 | 3.1174 | -0.12817 | -8.2581 | -0.28381 | -0.064087 | 3.4195 | 67.7307 | 67.4973 | 115.3564 | 123.555 | 3.1174 | 123.5504 | 82.8735 | -0.28381 | 123.555 | 3.1174 | 82.8735 | 115.3564 | 123.5504 | -123.9166 | -123.8983
2985.7344 | 123.9395 | -61.3678 | 62.2192 | -0.15388 | 0.01346 | 0.018113 | 0.010397 | 0.061743 | 9.4068e-05 | 0.07969 | -58.2733 | 62.1506 | -61.6608 | -61.496 | 53.9841 | 21.4508 | 6.3721 | 6.1661 | 62.2101 | -61.6425 | -0.29297 | -0.068664 | 3.0945 | -0.12817 | -8.2352 | -0.27466 | -0.009155 | 3.3875 | 67.7399 | 67.5339 | 115.3519 | 123.5184 | 3.0945 | 123.5779 | 82.8186 | -0.27466 | 123.5184 | 3.0945 | 82.8186 | 115.3519 | 123.5779 | -123.88 | -123.8617
2986.7344 | 123.9075 | -61.3541 | 62.2101 | 0.24284 | 0.017306 | 0.017686 | 0.013174 | 0.061316 | 0.00030767 | 0.081399 | -58.3191 | 62.1689 | -61.6745 | -61.5463 | 53.8834 | 21.3821 | 6.3126 | 6.1066 | 62.1552 | -61.6653 | -0.32044 | -0.041199 | 3.035 | -0.19226 | -8.3267 | -0.31128 | -0.054932 | 3.3554 | 67.6666 | 67.4606 | 115.2374 | 123.5229 | 3.035 | 123.5092 | 82.7362 | -0.31128 | 123.5229 | 3.035 | 82.7362 | 115.2374 | 123.5092 | -123.8846 | -123.8754
2987.7188 | 123.8709 | -61.3861 | 62.2192 | 0.14366 | 0.014529 | 0.015977 | 0.0082608 | 0.061316 | 0.0011621 | 0.081613 | -58.342 | 62.1185 | -61.6974 | -61.6013 | 53.8559 | 21.3409 | 6.2622 | 5.9784 | 62.1918 | -61.6562 | -0.31128 | -0.10071 | 3.0441 | -0.21515 | -8.3633 | -0.27008 | -0.027466 | 3.3554 | 67.6483 | 67.3645 | 115.242 | 123.5046 | 3.0441 | 123.5779 | 82.727 | -0.27008 | 123.5046 | 3.0441 | 82.727 | 115.242 | 123.5779 | -123.9166 | -123.8754
2988.7188 | 123.8709 | -61.3724 | 62.2147 | 0.11314 | 0.013033 | 0.015763 | 0.0099698 | 0.059607 | -0.0014013 | 0.080972 | -58.3374 | 62.1277 | -61.6928 | -61.5692 | 53.8879 | 21.3821 | 6.2851 | 6.0333 | 62.1414 | -61.6699 | -0.32044 | -0.086975 | 3.035 | -0.19684 | -8.3267 | -0.29755 | -0.073243 | 3.3554 | 67.6575 | 67.4057 | 115.2603 | 123.5001 | 3.035 | 123.5138 | 82.7545 | -0.29755 | 123.5001 | 3.035 | 82.7545 | 115.2603 | 123.5138 | -123.9075 | -123.8846
2989.7188 | 123.8525 | -61.4182 | 62.2009 | 0.2047 | 0.016665 | 0.015763 | 0.017447 | 0.058753 | 0.0013757 | 0.08204 | -58.3237 | 62.2009 | -61.7065 | -61.5738 | 53.7964 | 21.2814 | 6.3675 | 6.0471 | 62.1918 | -61.6974 | -0.28839 | 0 | 3.0945 | -0.15564 | -8.4045 | -0.27924 | -0.009156 | 3.3829 | 67.7856 | 67.4652 | 115.2145 | 123.6191 | 3.0945 | 123.6099 | 82.6996 | -0.27924 | 123.6191 | 3.0945 | 82.6996 | 115.2145 | 123.6099 | -123.9075 | -123.8983
2990.7344 | 123.9395 | -61.3632 | 62.2192 | -0.21492 | 0.015383 | 0.016404 | 0.010183 | 0.064307 | -0.00033333 | 0.07969 | -58.2779 | 62.1735 | -61.6516 | -61.4319 | 53.8513 | 21.2906 | 6.3995 | 6.1523 | 62.1735 | -61.647 | -0.28839 | -0.045776 | 3.0853 | -0.068665 | -8.3679 | -0.28381 | -0.045776 | 3.3737 | 67.7628 | 67.5156 | 115.2145 | 123.5367 | 3.0853 | 123.5367 | 82.6538 | -0.28381 | 123.5367 | 3.0853 | 82.6538 | 115.2145 | 123.5367 | -123.8708 | -123.8663
2991.7344 | 123.8113 | -61.3998 | 62.2192 | 0.067368 | 0.018374 | 0.015977 | 0.016378 | 0.061743 | -0.0014013 | 0.080972 | -58.3099 | 62.2284 | -61.7111 | -61.6196 | 53.7552 | 21.2585 | 6.4682 | 6.0333 | 62.2192 | -61.6974 | -0.31128 | 0.009156 | 3.0899 | -0.21973 | -8.4641 | -0.29755 | 0 | 3.4012 | 67.868 | 67.4332 | 115.155 | 123.6282 | 3.0899 | 123.6191 | 82.6584 | -0.29755 | 123.6282 | 3.0899 | 82.6584 | 115.155 | 123.6191 | -123.9304 | -123.9166
2992.7188 | 123.9258 | -61.3632 | 62.1918 | 0.19707 | 0.017519 | 0.012132 | 0.015738 | 0.062384 | -0.00011953 | 0.081826 | -58.2687 | 62.1872 | -61.6928 | -61.5417 | 53.9749 | 21.4279 | 6.2347 | 6.0837 | 62.1689 | -61.6928 | -0.32959 | -0.004577 | 3.0945 | -0.17853 | -8.2169 | -0.32959 | -0.022888 | 3.4241 | 67.598 | 67.4469 | 115.3381 | 123.5504 | 3.0945 | 123.5321 | 82.7911 | -0.32959 | 123.5504 | 3.0945 | 82.7911 | 115.3381 | 123.5321 | -123.8846 | -123.8846
2993.7188 | 123.8571 | -61.377 | 62.2101 | 0.18181 | 0.016665 | 0.015763 | 0.0089016 | 0.062384 | 0.00094847 | 0.080331 | -58.3237 | 62.1597 | -61.6837 | -61.5829 | 53.9703 | 21.4966 | 6.308 | 6.134 | 62.1964 | -61.647 | -0.3067 | -0.050354 | 3.0533 | -0.20599 | -8.2397 | -0.27008 | -0.013733 | 3.36 | 67.6849 | 67.511 | 115.3473 | 123.5367 | 3.0533 | 123.5733 | 82.8735 | -0.27008 | 123.5367 | 3.0533 | 82.8735 | 115.3473 | 123.5733 | -123.8937 | -123.8571
2994.7188 | 123.9395 | -61.3678 | 62.1826 | 0.34966 | 0.016024 | 0.013413 | 0.015524 | 0.063239 | -0.00054693 | 0.079049 | -58.2504 | 62.1368 | -61.6562 | -61.5326 | 54.0115 | 21.4828 | 6.2393 | 6.1432 | 62.1277 | -61.6791 | -0.28839 | -0.045776 | 3.1174 | -0.16479 | -8.1711 | -0.31128 | -0.054931 | 3.4058 | 67.6071 | 67.511 | 115.3793 | 123.5046 | 3.1174 | 123.4955 | 82.8506 | -0.31128 | 123.5046 | 3.1174 | 82.8506 | 115.3793 | 123.4955 | -123.8388 | -123.8617
2995.7344 | 123.7885 | -61.3998 | 62.2604 | -0.24544 | 0.017092 | 0.015122 | 0.015097 | 0.060675 | 0.00030767 | 0.080331 | -58.3557 | 62.233 | -61.6928 | -61.5784 | 53.8239 | 21.3913 | 6.6193 | 6.0425 | 62.2238 | -61.7065 | -0.29297 | -0.027466 | 3.0441 | -0.17853 | -8.4366 | -0.3067 | -0.036621 | 3.3371 | 68.0191 | 67.4423 | 115.2237 | 123.6328 | 3.0441 | 123.6237 | 82.7911 | -0.3067 | 123.6328 | 3.0441 | 82.7911 | 115.2237 | 123.6237 | -123.9532 | -123.967
2996.7344 | 123.7518 | -61.4594 | 62.2238 | 0.090256 | 0.02051 | 0.016831 | 0.018728 | 0.061743 | 0.0011621 | 0.080544 | -58.3557 | 62.2604 | -61.6974 | -61.6241 | 53.9246 | 21.4096 | 6.4636 | 5.9509 | 62.233 | -61.734 | -0.23804 | 0.036621 | 3.1036 | -0.1648 | -8.2993 | -0.27466 | 0.009155 | 3.3417 | 67.923 | 67.4103 | 115.3839 | 123.7198 | 3.1036 | 123.6923 | 82.869 | -0.27466 | 123.7198 | 3.1036 | 82.869 | 115.3839 | 123.6923 | -123.9212 | -123.9578
2997.7188 | 123.9212 | -61.4136 | 62.2238 | 0.18944 | 0.015383 | 0.01555 | 0.014029 | 0.066016 | 0.0013757 | 0.080117 | -58.2733 | 62.2055 | -61.6837 | -61.5417 | 54.039 | 21.5332 | 6.2439 | 6.0471 | 62.1735 | -61.6745 | -0.27008 | -0.018311 | 3.1403 | -0.12817 | -8.1848 | -0.26093 | -0.050354 | 3.4103 | 67.6575 | 67.4606 | 115.4526 | 123.6191 | 3.1403 | 123.587 | 82.9468 | -0.26093 | 123.6191 | 3.1403 | 82.9468 | 115.4526 | 123.587 | -123.9075 | -123.8983
2998.7344 | 123.7885 | -61.3861 | 62.2787 | -0.26833 | 0.017947 | 0.016618 | 0.011892 | 0.061103 | -0.00076053 | 0.080972 | -58.3054 | 62.1964 | -61.6882 | -61.5646 | 54.0207 | 21.5607 | 6.5002 | 6.1111 | 62.233 | -61.6653 | -0.30212 | -0.082398 | 3.0807 | -0.17853 | -8.2581 | -0.27924 | -0.045777 | 3.3829 | 67.8864 | 67.4973 | 115.4068 | 123.5825 | 3.0807 | 123.6191 | 82.9468 | -0.27924 | 123.5825 | 3.0807 | 82.9468 | 115.4068 | 123.6191 | -123.967 | -123.9441
2999.7188 | 123.8892 | -61.409 | 62.2284 | 0.03685 | 0.015383 | 0.011704 | 0.0089016 | 0.062384 | 0.00052127 | 0.081826 | -58.3282 | 62.1323 | -61.6699 | -61.5875 | 53.9658 | 21.698 | 6.3583 | 6.0379 | 62.178 | -61.647 | -0.26093 | -0.096131 | 3.0808 | -0.17853 | -8.2626 | -0.23804 | -0.050354 | 3.3417 | 67.7673 | 67.4469 | 115.3748 | 123.5413 | 3.0808 | 123.587 | 83.107 | -0.23804 | 123.5413 | 3.0808 | 83.107 | 115.3748 | 123.587 | -123.8983 | -123.8754
3000.7344 | 123.7518 | -61.3907 | 62.2696 | -0.2607 | 0.018587 | 0.017045 | 0.013815 | 0.060034 | 0.00094847 | 0.076486 | -58.3557 | 62.2284 | -61.6791 | -61.5143 | 54.2038 | 21.5652 | 6.3492 | 6.0425 | 62.2467 | -61.6974 | -0.28839 | -0.041198 | 3.035 | -0.1236 | -8.0658 | -0.3067 | -0.022888 | 3.3234 | 67.7399 | 67.4332 | 115.5945 | 123.6191 | 3.035 | 123.6374 | 82.9559 | -0.3067 | 123.6191 | 3.035 | 82.9559 | 115.5945 | 123.6374 | -123.9487 | -123.967
3001.7344 | 123.7885 | -61.4044 | 62.2375 | 1.517 | 0.019015 | 0.019181 | 0.016378 | 0.061957 | 0.0015893 | 0.080331 | -58.2001 | 62.2375 | -61.702 | -61.647 | 53.9749 | 21.4691 | 6.3995 | 5.9555 | 62.2284 | -61.7203 | -0.29755 | 0 | 3.2043 | -0.24262 | -8.2626 | -0.31586 | -0.009155 | 3.5019 | 67.804 | 67.3599 | 115.3793 | 123.642 | 3.2043 | 123.6328 | 82.8735 | -0.31586 | 123.642 | 3.2043 | 82.8735 | 115.3793 | 123.6328 | -123.9395 | -123.9578
3002.7188 | 123.8525 | -61.3861 | 62.2101 | -0.08522 | 0.014101 | 0.01854 | 0.0074062 | 0.061316 | -0.00033333 | 0.08204 | -58.3374 | 62.146 | -61.6974 | -61.5875 | 54.0802 | 21.5927 | 6.3492 | 6.1203 | 62.2055 | -61.6745 | -0.31128 | -0.064087 | 3.0487 | -0.20142 | -8.1299 | -0.28839 | -0.004578 | 3.36 | 67.7353 | 67.5064 | 115.4663 | 123.5321 | 3.0487 | 123.5916 | 82.9788 | -0.28839 | 123.5321 | 3.0487 | 82.9788 | 115.4663 | 123.5916 | -123.9075 | -123.8846
3003.7344 | 123.8205 | -61.3907 | 62.265 | -0.26833 | 0.016451 | 0.020677 | 0.0095424 | 0.059607 | -0.00054693 | 0.080331 | -58.2779 | 62.1964 | -61.6516 | -61.5417 | 54.0436 | 21.5607 | 6.3904 | 6.0379 | 62.2147 | -61.6562 | -0.26093 | -0.068665 | 3.1128 | -0.15106 | -8.2214 | -0.2655 | -0.050354 | 3.3737 | 67.7811 | 67.4286 | 115.4343 | 123.587 | 3.1128 | 123.6053 | 82.9514 | -0.2655 | 123.587 | 3.1128 | 82.9514 | 115.4343 | 123.6053 | -123.9166 | -123.9212
3004.7188 | 123.8892 | -61.3815 | 62.1872 | 0.15129 | 0.016665 | 0.013841 | 0.011038 | 0.060034 | -0.0014013 | 0.080758 | -58.2642 | 62.1643 | -61.6653 | -61.5509 | 54.0802 | 21.6293 | 6.1478 | 6.015 | 62.1414 | -61.6699 | -0.28381 | -0.022888 | 3.1174 | -0.16937 | -8.107 | -0.28839 | -0.045777 | 3.4012 | 67.5293 | 67.3965 | 115.4617 | 123.5458 | 3.1174 | 123.5229 | 83.0109 | -0.28839 | 123.5458 | 3.1174 | 83.0109 | 115.4617 | 123.5229 | -123.8525 | -123.8571
3005.7188 | 123.8525 | -61.4182 | 62.1597 | 0.16655 | 0.014742 | 0.017899 | 0.017233 | 0.06153 | -0.00097413 | 0.083749 | -58.2504 | 62.1414 | -61.6745 | -61.5509 | 54.0482 | 21.6019 | 6.0837 | 6.0013 | 62.1231 | -61.6837 | -0.25635 | -0.018311 | 3.1677 | -0.13275 | -8.1116 | -0.2655 | -0.036621 | 3.4241 | 67.5018 | 67.4194 | 115.4663 | 123.5596 | 3.1677 | 123.5413 | 83.02 | -0.2655 | 123.5596 | 3.1677 | 83.02 | 115.4663 | 123.5413 | -123.8342 | -123.8434
3006.7344 | 123.8022 | -61.3998 | 62.2696 | -0.26833 | 0.01581 | 0.015763 | 0.012747 | 0.059607 | -0.0018285 | 0.082467 | -58.2825 | 62.2147 | -61.6882 | -61.5921 | 53.9841 | 21.4554 | 6.3812 | 6.0242 | 62.2421 | -61.702 | -0.28839 | -0.054931 | 3.1174 | -0.19226 | -8.2855 | -0.30212 | -0.027466 | 3.4058 | 67.7811 | 67.424 | 115.3839 | 123.6145 | 3.1174 | 123.642 | 82.8552 | -0.30212 | 123.6145 | 3.1174 | 82.8552 | 115.3839 | 123.642 | -123.9578 | -123.9716
3007.7188 | 123.88 | -61.3953 | 62.1964 | 0.12077 | 0.018374 | 0.014909 | 0.010397 | 0.061743 | 9.4068e-05 | 0.081185 | -58.2367 | 62.1506 | -61.6882 | -61.5784 | 53.9291 | 21.4279 | 6.1386 | 6.0104 | 62.1689 | -61.6791 | -0.29297 | -0.045776 | 3.1586 | -0.18311 | -8.2672 | -0.28381 | -0.027466 | 3.4515 | 67.5339 | 67.4057 | 115.3244 | 123.5458 | 3.1586 | 123.5641 | 82.8232 | -0.28381 | 123.5458 | 3.1586 | 82.8232 | 115.3244 | 123.5641 | -123.8846 | -123.8754
3008.7188 | 123.8754 | -61.3632 | 62.233 | -0.19203 | 0.016451 | 0.014482 | 0.012747 | 0.06153 | -0.00076053 | 0.081185 | -58.2138 | 62.1964 | -61.6837 | -61.5005 | 54.0802 | 21.5332 | 6.3034 | 6.0974 | 62.2009 | -61.6562 | -0.32044 | -0.036621 | 3.1494 | -0.13733 | -8.1528 | -0.29297 | -0.032043 | 3.4698 | 67.6666 | 67.4606 | 115.4434 | 123.5596 | 3.1494 | 123.5641 | 82.8964 | -0.29297 | 123.5596 | 3.1494 | 82.8964 | 115.4434 | 123.5641 | -123.9166 | -123.8892
3009.7188 | 123.88 | -61.3953 | 62.2101 | 0.15129 | 0.01816 | 0.016618 | 0.016806 | 0.060675 | -0.0024695 | 0.080972 | -58.2733 | 62.1689 | -61.7111 | -61.5738 | 54.1168 | 21.6156 | 6.2027 | 5.9921 | 62.1689 | -61.6974 | -0.31586 | -0.041199 | 3.1219 | -0.17853 | -8.0933 | -0.30212 | -0.041199 | 3.4378 | 67.598 | 67.3874 | 115.5121 | 123.5641 | 3.1219 | 123.5641 | 83.0109 | -0.30212 | 123.5641 | 3.1219 | 83.0109 | 115.5121 | 123.5641 | -123.9212 | -123.9075
3010.7188 | 123.8617 | -61.377 | 62.2055 | 0.13603 | 0.013674 | 0.011704 | 0.0093288 | 0.062812 | 0.0013757 | 0.084603 | -58.3374 | 62.1552 | -61.6837 | -61.5875 | 53.9932 | 21.5332 | 6.2531 | 6.0104 | 62.1506 | -61.6653 | -0.3067 | -0.050354 | 3.0396 | -0.21057 | -8.2123 | -0.28839 | -0.054931 | 3.3463 | 67.63 | 67.3874 | 115.3702 | 123.5321 | 3.0396 | 123.5275 | 82.9102 | -0.28839 | 123.5321 | 3.0396 | 82.9102 | 115.3702 | 123.5275 | -123.8892 | -123.8708
3011.7344 | 123.7885 | -61.3907 | 62.2833 | -0.23018 | 0.014529 | 0.014909 | 0.013601 | 0.062171 | -0.0037511 | 0.081826 | -58.2825 | 62.1872 | -61.6699 | -61.5509 | 53.9612 | 21.5012 | 6.3995 | 6.0059 | 62.2421 | -61.6562 | -0.27924 | -0.09613 | 3.1082 | -0.16022 | -8.3221 | -0.2655 | -0.041199 | 3.3875 | 67.7902 | 67.3965 | 115.3519 | 123.5779 | 3.1082 | 123.6328 | 82.8918 | -0.2655 | 123.5779 | 3.1082 | 82.8918 | 115.3519 | 123.6328 | -123.9532 | -123.9395
3012.7188 | 123.8937 | -61.3724 | 62.2055 | 0.16655 | 0.018374 | 0.018327 | 0.016165 | 0.063239 | -0.0014013 | 0.080758 | -58.3008 | 62.1826 | -61.6791 | -61.5555 | 53.9154 | 21.5149 | 6.0791 | 5.9418 | 62.178 | -61.6837 | -0.3067 | -0.022888 | 3.0716 | -0.18311 | -8.2901 | -0.31128 | -0.027465 | 3.3783 | 67.4515 | 67.3141 | 115.2878 | 123.555 | 3.0716 | 123.5504 | 82.8873 | -0.31128 | 123.555 | 3.0716 | 82.8873 | 115.2878 | 123.5504 | -123.8846 | -123.8892
3013.7188 | 123.88 | -61.3998 | 62.1414 | 0.15129 | 0.01816 | 0.017259 | 0.016806 | 0.063025 | -0.00054693 | 0.081826 | -58.2825 | 62.1735 | -61.7065 | -61.5234 | 53.9886 | 21.6156 | 6.1249 | 5.9647 | 62.146 | -61.6653 | -0.3067 | 0.032044 | 3.1174 | -0.1236 | -8.1528 | -0.2655 | 0.004578 | 3.4241 | 67.5247 | 67.3645 | 115.3885 | 123.5733 | 3.1174 | 123.5458 | 83.0154 | -0.2655 | 123.5733 | 3.1174 | 83.0154 | 115.3885 | 123.5458 | -123.848 | -123.8068
3014.7188 | 123.8617 | -61.3953 | 62.1872 | 0.03685 | 0.017733 | 0.017045 | 0.0084744 | 0.060248 | -0.00076053 | 0.08204 | -58.3191 | 62.1506 | -61.6882 | -61.5875 | 53.9429 | 21.524 | 6.2942 | 5.9967 | 62.2009 | -61.6653 | -0.29297 | -0.036621 | 3.0762 | -0.19226 | -8.2443 | -0.27008 | 0.013733 | 3.3691 | 67.6895 | 67.392 | 115.3381 | 123.5458 | 3.0762 | 123.5962 | 82.9193 | -0.27008 | 123.5458 | 3.0762 | 82.9193 | 115.3381 | 123.5962 | -123.8754 | -123.8525
3015.7188 | 123.8571 | -61.3541 | 62.2055 | 0.12077 | 0.01581 | 0.016191 | 0.011251 | 0.058325 | 0.0020167 | 0.079476 | -58.2687 | 62.1506 | -61.6928 | -61.5417 | 53.9703 | 21.5149 | 6.2347 | 6.0287 | 62.1597 | -61.6653 | -0.33875 | -0.054931 | 3.0853 | -0.18768 | -8.2352 | -0.31128 | -0.045776 | 3.4241 | 67.5888 | 67.3828 | 115.3244 | 123.5046 | 3.0853 | 123.5138 | 82.869 | -0.31128 | 123.5046 | 3.0853 | 82.869 | 115.3244 | 123.5138 | -123.8983 | -123.8708
3016.7188 | 123.848 | -61.3586 | 62.2238 | 0.23521 | 0.017733 | 0.017045 | 0.017874 | 0.060248 | 0.00094847 | 0.081399 | -58.3282 | 62.2055 | -61.6928 | -61.5784 | 53.8925 | 21.4874 | 6.1661 | 5.8868 | 62.1735 | -61.7065 | -0.33417 | -0.018311 | 3.0304 | -0.21973 | -8.3313 | -0.3479 | -0.050354 | 3.3646 | 67.5247 | 67.2455 | 115.2512 | 123.5641 | 3.0304 | 123.5321 | 82.8461 | -0.3479 | 123.5641 | 3.0304 | 82.8461 | 115.2512 | 123.5321 | -123.9166 | -123.9304
3017.7188 | 123.848 | -61.3586 | 62.2147 | 0.082626 | 0.014315 | 0.013413 | 0.0095424 | 0.062598 | -0.00033333 | 0.081826 | -58.3282 | 62.1323 | -61.6745 | -61.5784 | 54.0024 | 21.5424 | 6.1981 | 5.9463 | 62.1872 | -61.6516 | -0.31586 | -0.082398 | 3.0304 | -0.21973 | -8.2123 | -0.29297 | -0.027466 | 3.3463 | 67.5568 | 67.305 | 115.361 | 123.4909 | 3.0304 | 123.5458 | 82.901 | -0.29297 | 123.4909 | 3.0304 | 82.901 | 115.361 | 123.5458 | -123.8892 | -123.8663
3018.7188 | 123.8937 | -61.3724 | 62.178 | 0.15892 | 0.015169 | 0.017472 | 0.019156 | 0.060034 | -0.0024695 | 0.081826 | -58.255 | 62.1552 | -61.6699 | -61.496 | 54.0253 | 21.5378 | 6.2988 | 6.0425 | 62.1597 | -61.6837 | -0.29755 | -0.022889 | 3.1174 | -0.1236 | -8.1528 | -0.31128 | -0.018311 | 3.4149 | 67.6712 | 67.4149 | 115.3976 | 123.5275 | 3.1174 | 123.5321 | 82.9102 | -0.31128 | 123.5275 | 3.1174 | 82.9102 | 115.3976 | 123.5321 | -123.848 | -123.8617
3019.7188 | 123.8937 | -61.3815 | 62.1231 | 0.18181 | 0.014315 | 0.018327 | 0.015951 | 0.060248 | 0.0020167 | 0.08204 | -58.2642 | 62.1506 | -61.6699 | -61.5234 | 54.1168 | 21.5378 | 6.134 | 5.9372 | 62.1552 | -61.702 | -0.28839 | 0.027466 | 3.1174 | -0.14191 | -8.0063 | -0.32043 | 0.032043 | 3.4058 | 67.5156 | 67.3187 | 115.4984 | 123.5321 | 3.1174 | 123.5367 | 82.9193 | -0.32043 | 123.5321 | 3.1174 | 82.9193 | 115.4984 | 123.5367 | -123.793 | -123.8251
3020.7344 | 123.8022 | -61.4136 | 62.2787 | -0.29121 | 0.017947 | 0.013627 | 0.014242 | 0.061957 | 0.0011621 | 0.081613 | -58.3145 | 62.265 | -61.6837 | -61.5738 | 53.9703 | 21.4096 | 6.4682 | 5.9143 | 62.2238 | -61.6974 | -0.27008 | -0.013733 | 3.0991 | -0.16022 | -8.3084 | -0.28381 | -0.054932 | 3.3691 | 67.8818 | 67.3279 | 115.3839 | 123.6786 | 3.0991 | 123.6374 | 82.8232 | -0.28381 | 123.6786 | 3.0991 | 82.8232 | 115.3839 | 123.6374 | -123.9624 | -123.9761
3021.7188 | 123.8251 | -61.409 | 62.1918 | 0.11314 | 0.019015 | 0.021531 | 0.016165 | 0.06153 | 0.00052127 | 0.082253 | -58.3374 | 62.2421 | -61.6974 | -61.6196 | 53.9337 | 21.4233 | 6.3354 | 5.9006 | 62.2009 | -61.7111 | -0.28839 | 0.050354 | 3.0716 | -0.21057 | -8.2581 | -0.30212 | 0.009156 | 3.36 | 67.7444 | 67.3096 | 115.3427 | 123.6511 | 3.0716 | 123.6099 | 82.8323 | -0.30212 | 123.6511 | 3.0716 | 82.8323 | 115.3427 | 123.6099 | -123.8892 | -123.9029
3022.7188 | 123.88 | -61.3815 | 62.1918 | 0.18181 | 0.018374 | 0.013841 | 0.01531 | 0.063239 | 0.0022303 | 0.082253 | -58.3054 | 62.2147 | -61.702 | -61.5509 | 53.952 | 21.4096 | 6.1661 | 5.928 | 62.1689 | -61.7065 | -0.32043 | 0.022889 | 3.0762 | -0.16937 | -8.2397 | -0.32501 | -0.022888 | 3.3966 | 67.5476 | 67.3096 | 115.3336 | 123.5962 | 3.0762 | 123.5504 | 82.7911 | -0.32501 | 123.5962 | 3.0762 | 82.7911 | 115.3336 | 123.5504 | -123.8937 | -123.8983
3023.7344 | 123.9212 | -61.4044 | 62.1689 | 0.18181 | 0.012392 | 0.02324 | 0.014669 | 0.062384 | 0.0011621 | 0.080758 | -58.2779 | 62.1826 | -61.6745 | -61.5326 | 54.0344 | 21.5332 | 6.1478 | 6.0516 | 62.1597 | -61.6882 | -0.27008 | 0.013733 | 3.1265 | -0.12817 | -8.1345 | -0.28381 | -0.009155 | 3.3966 | 67.5522 | 67.4561 | 115.4388 | 123.587 | 3.1265 | 123.5641 | 82.9376 | -0.28381 | 123.587 | 3.1265 | 82.9376 | 115.4388 | 123.5641 | -123.8434 | -123.8571
3024.7188 | 123.793 | -61.3998 | 62.2421 | 0.13603 | 0.018374 | 0.015763 | 0.016592 | 0.064948 | 0.0013757 | 0.080544 | -58.3374 | 62.2238 | -61.6882 | -61.647 | 53.8193 | 21.0846 | 6.4224 | 6.1707 | 62.2055 | -61.734 | -0.28839 | -0.01831 | 3.0624 | -0.24719 | -8.4229 | -0.33417 | -0.036621 | 3.3508 | 67.8223 | 67.5705 | 115.2191 | 123.6237 | 3.0624 | 123.6053 | 82.4844 | -0.33417 | 123.6237 | 3.0624 | 82.4844 | 115.2191 | 123.6053 | -123.9304 | -123.9761
3025.7188 | 123.7656 | -61.4502 | 62.233 | 0.029221 | 0.019656 | 0.017259 | 0.014883 | 0.064734 | -0.00033333 | 0.080117 | -58.255 | 62.2513 | -61.6928 | -61.6425 | 53.9108 | 21.3959 | 6.4499 | 5.896 | 62.2375 | -61.7477 | -0.24262 | 0.018311 | 3.1952 | -0.19226 | -8.3221 | -0.29755 | 0.004578 | 3.4378 | 67.9001 | 67.3462 | 115.361 | 123.7015 | 3.1952 | 123.6877 | 82.8461 | -0.29755 | 123.7015 | 3.1952 | 82.8461 | 115.361 | 123.6877 | -123.9258 | -123.9807
3026.7344 | 123.8617 | -61.4044 | 62.1872 | 0.11314 | 0.017306 | 0.012773 | 0.0076198 | 0.063666 | 0.00052127 | 0.080544 | -58.3099 | 62.1643 | -61.7294 | -61.5829 | 53.9932 | 21.5149 | 6.2576 | 5.9692 | 62.1918 | -61.6699 | -0.32501 | -0.022888 | 3.0945 | -0.17853 | -8.194 | -0.2655 | 0.004577 | 3.4195 | 67.662 | 67.3737 | 115.3976 | 123.5687 | 3.0945 | 123.5962 | 82.9193 | -0.2655 | 123.5687 | 3.0945 | 82.9193 | 115.3976 | 123.5962 | -123.9166 | -123.8571
3027.7188 | 123.8022 | -61.4136 | 62.1964 | 0.067368 | 0.019228 | 0.017899 | 0.018515 | 0.063025 | 0.0015893 | 0.082253 | -58.3191 | 62.2467 | -61.6974 | -61.6104 | 54.0573 | 21.4554 | 6.2393 | 5.8319 | 62.2009 | -61.7477 | -0.28381 | 0.050354 | 3.0945 | -0.19684 | -8.139 | -0.33417 | 0.004578 | 3.3783 | 67.6529 | 67.2455 | 115.4709 | 123.6603 | 3.0945 | 123.6145 | 82.869 | -0.33417 | 123.6603 | 3.0945 | 82.869 | 115.4709 | 123.6145 | -123.8937 | -123.9441
3028.7188 | 123.8663 | -61.3998 | 62.146 | 0.14366 | 0.014956 | 0.017259 | 0.013174 | 0.065375 | -0.00076053 | 0.080972 | -58.2825 | 62.1735 | -61.6791 | -61.5372 | 54.0939 | 21.5515 | 6.1752 | 5.9692 | 62.178 | -61.6837 | -0.27924 | 0.027466 | 3.1174 | -0.13733 | -8.0521 | -0.28381 | 0.032044 | 3.3966 | 67.5751 | 67.3691 | 115.4938 | 123.5733 | 3.1174 | 123.5779 | 82.9514 | -0.28381 | 123.5733 | 3.1174 | 82.9514 | 115.4938 | 123.5779 | -123.8251 | -123.8297
3029.7344 | 123.8892 | -61.3724 | 62.2055 | 0.11314 | 0.01581 | 0.012773 | 0.0076198 | 0.061957 | -0.00011953 | 0.080758 | -58.3328 | 62.146 | -61.6653 | -61.5875 | 54.0115 | 21.5332 | 6.2668 | 5.8868 | 62.1826 | -61.6608 | -0.29297 | -0.059509 | 3.0395 | -0.21515 | -8.194 | -0.28839 | -0.022888 | 3.3325 | 67.6392 | 67.2592 | 115.3839 | 123.5184 | 3.0395 | 123.555 | 82.9056 | -0.28839 | 123.5184 | 3.0395 | 82.9056 | 115.3839 | 123.555 | -123.8708 | -123.8663
3030.7188 | 123.7564 | -61.4273 | 62.233 | 0.052109 | 0.014742 | 0.017045 | 0.021078 | 0.062598 | 0.00030767 | 0.081613 | -58.2962 | 62.2559 | -61.6928 | -61.6241 | 54.0802 | 21.4966 | 6.3721 | 5.8411 | 62.2055 | -61.7432 | -0.2655 | 0.022888 | 3.1311 | -0.19684 | -8.1528 | -0.31586 | -0.027466 | 3.3966 | 67.7994 | 67.2684 | 115.5075 | 123.6832 | 3.1311 | 123.6328 | 82.9239 | -0.31586 | 123.6832 | 3.1311 | 82.9239 | 115.5075 | 123.6328 | -123.9258 | -123.9761
3031.7188 | 123.8251 | -61.4456 | 62.2284 | -0.08522 | 0.018374 | 0.017686 | 0.016165 | 0.064307 | -0.00097413 | 0.079904 | -58.3603 | 62.2421 | -61.6974 | -61.647 | 54.039 | 21.5195 | 6.3492 | 5.864 | 62.2421 | -61.7294 | -0.25177 | 0.013732 | 3.0853 | -0.20142 | -8.1894 | -0.28381 | 0.013732 | 3.3371 | 67.7948 | 67.3096 | 115.4846 | 123.6877 | 3.0853 | 123.6877 | 82.9651 | -0.28381 | 123.6877 | 3.0853 | 82.9651 | 115.4846 | 123.6877 | -123.9258 | -123.9578
3032.7344 | 123.8754 | -61.409 | 62.1964 | 0.021591 | 0.014956 | 0.017259 | 0.0071926 | 0.062598 | -0.00033333 | 0.082681 | -58.3466 | 62.146 | -61.6928 | -61.5738 | 54.213 | 21.6476 | 6.2942 | 5.983 | 62.2055 | -61.6425 | -0.28381 | -0.050354 | 3.0624 | -0.16479 | -7.9834 | -0.23346 | 0.009155 | 3.3463 | 67.7032 | 67.392 | 115.6219 | 123.555 | 3.0624 | 123.6145 | 83.0566 | -0.23346 | 123.555 | 3.0624 | 83.0566 | 115.6219 | 123.6145 | -123.8892 | -123.8388
3033.7188 | 123.7976 | -61.4136 | 62.2238 | 0.04448 | 0.018801 | 0.015977 | 0.016165 | 0.064093 | -0.0028967 | 0.082467 | -58.3191 | 62.2513 | -61.6837 | -61.6196 | 54.1992 | 21.5515 | 6.3904 | 5.8777 | 62.2101 | -61.734 | -0.27008 | 0.027466 | 3.0945 | -0.20599 | -8.0246 | -0.32044 | -0.013733 | 3.3646 | 67.804 | 67.2913 | 115.6128 | 123.6649 | 3.0945 | 123.6237 | 82.9651 | -0.32044 | 123.6649 | 3.0945 | 82.9651 | 115.6128 | 123.6237 | -123.9075 | -123.9578
3034.7188 | 123.7976 | -61.441 | 62.2238 | 0.067368 | 0.017733 | 0.01555 | 0.017233 | 0.064521 | 0.00030767 | 0.081613 | -58.3374 | 62.2604 | -61.6974 | -61.6516 | 54.1168 | 21.5195 | 6.4774 | 5.8777 | 62.2421 | -61.734 | -0.25635 | 0.036621 | 3.1036 | -0.21057 | -8.107 | -0.29297 | 0.01831 | 3.36 | 67.9184 | 67.3187 | 115.5579 | 123.7015 | 3.1036 | 123.6832 | 82.9605 | -0.29297 | 123.7015 | 3.1036 | 82.9605 | 115.5579 | 123.6832 | -123.9212 | -123.9578
3035.7344 | 123.8754 | -61.3998 | 62.178 | 0.11314 | 0.016665 | 0.013627 | 0.0078336 | 0.064948 | 0.0028711 | 0.080758 | -58.3191 | 62.1277 | -61.6974 | -61.5784 | 54.2587 | 21.6797 | 6.2119 | 5.9601 | 62.1689 | -61.647 | -0.29755 | -0.050354 | 3.0807 | -0.17853 | -7.9193 | -0.24719 | -0.009156 | 3.3783 | 67.6117 | 67.3599 | 115.6586 | 123.5275 | 3.0807 | 123.5687 | 83.0795 | -0.24719 | 123.5275 | 3.0807 | 83.0795 | 115.6586 | 123.5687 | -123.8754 | -123.8251
3036.7344 | 123.9075 | -61.3815 | 62.1964 | -0.054703 | 0.01346 | 0.012345 | 0.0056972 | 0.062812 | 0.00094847 | 0.080331 | -58.3969 | 62.146 | -61.6837 | -61.5372 | 54.1626 | 21.6476 | 6.3034 | 5.9967 | 62.1918 | -61.6425 | -0.30212 | -0.050354 | 2.9846 | -0.15564 | -8.0338 | -0.26093 | -0.004578 | 3.2867 | 67.6849 | 67.3782 | 115.5441 | 123.5275 | 2.9846 | 123.5733 | 83.0292 | -0.26093 | 123.5275 | 2.9846 | 83.0292 | 115.5441 | 123.5733 | -123.88 | -123.8388
3037.7188 | 123.8342 | -61.3907 | 62.265 | -0.16914 | 0.017519 | 0.014695 | 0.018515 | 0.061743 | -0.00097413 | 0.081399 | -58.2504 | 62.2742 | -61.6653 | -61.5463 | 54.126 | 21.7072 | 6.4041 | 5.9875 | 62.2375 | -61.7386 | -0.27466 | 0.009155 | 3.1403 | -0.15564 | -8.139 | -0.3479 | -0.027466 | 3.4149 | 67.7948 | 67.3782 | 115.5167 | 123.6649 | 3.1403 | 123.6282 | 83.0978 | -0.3479 | 123.6649 | 3.1403 | 83.0978 | 115.5167 | 123.6282 | -123.9304 | -124.0036
3038.7344 | 123.8892 | -61.3998 | 62.1826 | 0.25047 | 0.018374 | 0.016831 | 0.014242 | 0.064948 | -0.00054693 | 0.079263 | -58.3008 | 62.146 | -61.7157 | -61.5463 | 54.1351 | 21.7163 | 6.2347 | 5.9875 | 62.178 | -61.6608 | -0.31586 | -0.036621 | 3.0991 | -0.14648 | -8.0475 | -0.26093 | -0.004577 | 3.4149 | 67.6346 | 67.3874 | 115.535 | 123.5458 | 3.0991 | 123.5779 | 83.1162 | -0.26093 | 123.5458 | 3.0991 | 83.1162 | 115.535 | 123.5779 | -123.8983 | -123.8434
3039.7188 | 123.8205 | -61.3953 | 62.2467 | -0.0089264 | 0.019228 | 0.016404 | 0.016378 | 0.06153 | -0.00054693 | 0.081613 | -58.2962 | 62.2696 | -61.6699 | -61.5646 | 54.1351 | 21.6339 | 6.3904 | 5.983 | 62.2147 | -61.7065 | -0.27466 | 0.022888 | 3.0991 | -0.16937 | -8.1116 | -0.31128 | -0.032043 | 3.3737 | 67.7856 | 67.3782 | 115.5304 | 123.6649 | 3.0991 | 123.6099 | 83.0292 | -0.31128 | 123.6649 | 3.0991 | 83.0292 | 115.5304 | 123.6099 | -123.9166 | -123.9532
3040.7188 | 123.7793 | -61.409 | 62.2009 | -0.23018 | 0.017306 | 0.021104 | 0.015524 | 0.064521 | 0.00094847 | 0.080544 | -58.3466 | 62.2467 | -61.7065 | -61.6379 | 54.007 | 21.0663 | 6.4087 | 5.8868 | 62.2421 | -61.702 | -0.29755 | 0.045776 | 3.0624 | -0.22888 | -8.194 | -0.29297 | 0.041198 | 3.36 | 67.8177 | 67.2958 | 115.416 | 123.6557 | 3.0624 | 123.6511 | 82.4753 | -0.29297 | 123.6557 | 3.0624 | 82.4753 | 115.416 | 123.6511 | -123.9075 | -123.9029
3041.7188 | 123.8342 | -61.4044 | 62.2055 | 0.13603 | 0.01581 | 0.019395 | 0.014883 | 0.064521 | -0.0014013 | 0.082894 | -58.3466 | 62.2147 | -61.7065 | -61.615 | 54.1077 | 21.5652 | 6.3217 | 5.9097 | 62.2192 | -61.7065 | -0.30212 | 0.009156 | 3.0579 | -0.21057 | -8.0978 | -0.30212 | 0.013733 | 3.36 | 67.7261 | 67.3141 | 115.5121 | 123.6191 | 3.0579 | 123.6237 | 82.9697 | -0.30212 | 123.6191 | 3.0579 | 82.9697 | 115.5121 | 123.6237 | -123.912 | -123.912
3042.7188 | 123.8068 | -61.4182 | 62.233 | -0.039444 | 0.015597 | 0.019822 | 0.013174 | 0.064093 | -0.0018285 | 0.079476 | -58.3054 | 62.2787 | -61.6745 | -61.5738 | 54.0253 | 21.3409 | 6.3583 | 5.9463 | 62.2375 | -61.7065 | -0.25635 | 0.045777 | 3.1128 | -0.15564 | -8.2077 | -0.28839 | 0.004578 | 3.3691 | 67.7765 | 67.3645 | 115.4434 | 123.6969 | 3.1128 | 123.6557 | 82.7591 | -0.28839 | 123.6969 | 3.1128 | 82.7591 | 115.4434 | 123.6557 | -123.9075 | -123.9395
3043.7188 | 123.8205 | -61.4136 | 62.2696 | -0.15388 | 0.017306 | 0.017045 | 0.01296 | 0.064307 | 0.0018031 | 0.080331 | -58.3328 | 62.265 | -61.6974 | -61.5784 | 54.0848 | 21.4233 | 6.5231 | 5.9738 | 62.2467 | -61.702 | -0.28381 | -0.004577 | 3.0807 | -0.1648 | -8.1848 | -0.28839 | -0.022888 | 3.3646 | 67.9367 | 67.3874 | 115.4984 | 123.6786 | 3.0807 | 123.6603 | 82.8369 | -0.28839 | 123.6786 | 3.0807 | 82.8369 | 115.4984 | 123.6603 | -123.967 | -123.9716
3044.7188 | 123.8297 | -61.4319 | 62.2238 | 1.2728 | 0.015597 | 0.017899 | 0.013601 | 0.064734 | 0.0018031 | 0.080544 | -58.255 | 62.2513 | -61.7157 | -61.6516 | 53.952 | 21.2814 | 6.3904 | 5.8823 | 62.2421 | -61.7203 | -0.28381 | 0.027466 | 3.1769 | -0.21973 | -8.2718 | -0.28839 | 0.01831 | 3.4607 | 67.8223 | 67.3141 | 115.3839 | 123.6832 | 3.1769 | 123.674 | 82.7133 | -0.28839 | 123.6832 | 3.1769 | 82.7133 | 115.3839 | 123.674 | -123.9395 | -123.9441
3045.7188 | 123.8297 | -61.3953 | 62.2559 | -0.19966 | 0.016665 | 0.014909 | 0.011892 | 0.062812 | 9.4068e-05 | 0.080544 | -58.3008 | 62.2696 | -61.6653 | -61.5601 | 54.071 | 21.373 | 6.4636 | 6.102 | 62.2604 | -61.6791 | -0.27008 | 0.013733 | 3.0945 | -0.1648 | -8.1848 | -0.28381 | 0.004578 | 3.3646 | 67.8589 | 67.4973 | 115.4663 | 123.6649 | 3.0945 | 123.6557 | 82.7682 | -0.28381 | 123.6649 | 3.0945 | 82.7682 | 115.4663 | 123.6557 | -123.9212 | -123.9349
3046.7188 | 123.8159 | -61.3953 | 62.2147 | -0.10811 | 0.017733 | 0.015763 | 0.015738 | 0.064948 | -0.0011877 | 0.081399 | -58.2367 | 62.2513 | -61.6928 | -61.5738 | 54.0207 | 21.5927 | 6.395 | 5.9875 | 62.233 | -61.6974 | -0.29755 | 0.036621 | 3.1586 | -0.17853 | -8.194 | -0.30212 | 0.01831 | 3.4561 | 67.7902 | 67.3828 | 115.416 | 123.6465 | 3.1586 | 123.6282 | 82.988 | -0.30212 | 123.6465 | 3.1586 | 82.988 | 115.416 | 123.6282 | -123.9075 | -123.912
3047.7188 | 123.7656 | -61.4273 | 62.2375 | 0.029221 | 0.018374 | 0.020249 | 0.011679 | 0.06687 | 0.0011621 | 0.080972 | -58.374 | 62.265 | -61.7157 | -61.6745 | 53.9612 | 21.4508 | 6.4819 | 5.928 | 62.2375 | -61.7111 | -0.28839 | 0.027466 | 3.0533 | -0.24719 | -8.2764 | -0.28381 | 0 | 3.3417 | 67.9092 | 67.3553 | 115.3885 | 123.6923 | 3.0533 | 123.6649 | 82.8781 | -0.28381 | 123.6923 | 3.0533 | 82.8781 | 115.3885 | 123.6649 | -123.9532 | -123.9487
3048.7188 | 123.7656 | -61.441 | 62.2467 | 0.04448 | 0.016665 | 0.017259 | 0.013815 | 0.065161 | 9.4068e-05 | 0.080972 | -58.3054 | 62.2559 | -61.6928 | -61.6562 | 53.9932 | 21.4737 | 6.5414 | 6.0013 | 62.2421 | -61.7249 | -0.25177 | 0.009155 | 3.1357 | -0.21515 | -8.2535 | -0.28381 | -0.004578 | 3.3875 | 67.9825 | 67.4423 | 115.4343 | 123.6969 | 3.1357 | 123.6832 | 82.9147 | -0.28381 | 123.6969 | 3.1357 | 82.9147 | 115.4343 | 123.6832 | -123.9395 | -123.9716
3049.7188 | 123.8571 | -61.3861 | 62.2696 | -0.24544 | 0.016665 | 0.017045 | 0.01232 | 0.064734 | -0.00076053 | 0.081826 | -58.3008 | 62.2696 | -61.6745 | -61.5646 | 54.0344 | 21.5424 | 6.5231 | 6.0333 | 62.2696 | -61.6699 | -0.28839 | 0 | 3.0853 | -0.17853 | -8.2352 | -0.28381 | 0 | 3.3737 | 67.9092 | 67.4194 | 115.4205 | 123.6557 | 3.0853 | 123.6557 | 82.9285 | -0.28381 | 123.6557 | 3.0853 | 82.9285 | 115.4205 | 123.6557 | -123.9441 | -123.9395
3050.7344 | 123.8709 | -61.3907 | 62.1918 | 0.19707 | 0.014956 | 0.01854 | 0.012747 | 0.067939 | 0.00052127 | 0.081826 | -58.3649 | 62.2055 | -61.702 | -61.6058 | 54.1168 | 21.6797 | 6.3446 | 6.0471 | 62.1918 | -61.702 | -0.31128 | 0.013733 | 3.0258 | -0.21515 | -8.075 | -0.31128 | 0 | 3.3371 | 67.7353 | 67.4377 | 115.5075 | 123.5962 | 3.0258 | 123.5825 | 83.0704 | -0.31128 | 123.5962 | 3.0258 | 83.0704 | 115.5075 | 123.5825 | -123.8937 | -123.8937
3051.7188 | 123.8205 | -61.3998 | 62.233 | -0.20729 | 0.017092 | 0.012559 | 0.010611 | 0.064093 | 0.0018031 | 0.080544 | -58.3374 | 62.2696 | -61.7111 | -61.5875 | 54.0344 | 21.5881 | 6.5048 | 6.0654 | 62.2604 | -61.6928 | -0.31128 | 0.036621 | 3.0624 | -0.18768 | -8.1985 | -0.29297 | 0.027466 | 3.3737 | 67.9047 | 67.4652 | 115.4343 | 123.6694 | 3.0624 | 123.6603 | 82.988 | -0.29297 | 123.6694 | 3.0624 | 82.988 | 115.4343 | 123.6603 | -123.9441 | -123.9258
3052.7188 | 123.793 | -61.4182 | 62.2375 | -0.0089264 | 0.01816 | 0.021317 | 0.013815 | 0.067084 | 9.4068e-05 | 0.083535 | -58.3237 | 62.2696 | -61.6745 | -61.5921 | 54.0619 | 21.611 | 6.5231 | 6.0654 | 62.2192 | -61.6928 | -0.25635 | 0.032043 | 3.0945 | -0.17395 | -8.1757 | -0.27466 | -0.018311 | 3.3508 | 67.9413 | 67.4835 | 115.48 | 123.6877 | 3.0945 | 123.6374 | 83.0292 | -0.27466 | 123.6877 | 3.0945 | 83.0292 | 115.48 | 123.6374 | -123.912 | -123.9304
3053.7344 | 123.8159 | -61.4365 | 62.2192 | 0.11314 | 0.017092 | 0.019395 | 0.010183 | 0.065161 | 0.00030767 | 0.081185 | -58.3694 | 62.2375 | -61.7111 | -61.6516 | 53.9658 | 21.5515 | 6.4774 | 5.983 | 62.2375 | -61.734 | -0.27466 | 0.018311 | 3.067 | -0.21515 | -8.2535 | -0.29755 | 0.018311 | 3.3417 | 67.9138 | 67.4194 | 115.4022 | 123.674 | 3.067 | 123.674 | 82.988 | -0.29755 | 123.674 | 3.067 | 82.988 | 115.4022 | 123.674 | -123.9304 | -123.9532
3054.7188 | 123.8113 | -61.3861 | 62.2604 | -0.19203 | 0.01581 | 0.015336 | 0.01296 | 0.064307 | 0.00094847 | 0.082681 | -58.3237 | 62.2604 | -61.6974 | -61.6196 | 54.0894 | 21.5332 | 6.5002 | 6.0516 | 62.2833 | -61.6791 | -0.31128 | 0 | 3.0624 | -0.23346 | -8.1711 | -0.29297 | 0.022888 | 3.3737 | 67.8864 | 67.4377 | 115.4755 | 123.6465 | 3.0624 | 123.6694 | 82.9193 | -0.29297 | 123.6465 | 3.0624 | 82.9193 | 115.4755 | 123.6694 | -123.9578 | -123.9395
3055.7344 | 123.9029 | -61.377 | 62.2009 | 0.16655 | 0.016451 | 0.017259 | 0.0091152 | 0.06687 | 0.00030767 | 0.081613 | -58.3282 | 62.1735 | -61.6974 | -61.5601 | 54.1397 | 21.6385 | 6.2347 | 6.0379 | 62.1872 | -61.6837 | -0.32043 | -0.027466 | 3.0487 | -0.18311 | -8.0612 | -0.3067 | -0.013733 | 3.3691 | 67.6117 | 67.4149 | 115.5167 | 123.5504 | 3.0487 | 123.5641 | 83.0154 | -0.3067 | 123.5504 | 3.0487 | 83.0154 | 115.5167 | 123.5641 | -123.8983 | -123.8846
3056.7188 | 123.8297 | -61.4136 | 62.2192 | -0.23781 | 0.017519 | 0.019822 | 0.01296 | 0.064093 | 0.00073487 | 0.080117 | -58.2642 | 62.2421 | -61.6653 | -61.5601 | 54.1443 | 21.6522 | 6.3583 | 5.9921 | 62.2421 | -61.7203 | -0.25177 | 0.022888 | 3.1494 | -0.14649 | -8.075 | -0.3067 | 0.022888 | 3.4012 | 67.7719 | 67.4057 | 115.5579 | 123.6557 | 3.1494 | 123.6557 | 83.0658 | -0.3067 | 123.6557 | 3.1494 | 83.0658 | 115.5579 | 123.6557 | -123.8846 | -123.9395
3057.7188 | 123.8297 | -61.409 | 62.265 | -0.26833 | 0.017519 | 0.014482 | 0.0071926 | 0.064093 | -0.00076053 | 0.080117 | -58.3054 | 62.1964 | -61.6653 | -61.5692 | 54.1489 | 21.5973 | 6.4178 | 6.015 | 62.2559 | -61.6745 | -0.25635 | -0.068665 | 3.1036 | -0.16022 | -8.1161 | -0.2655 | -0.009156 | 3.36 | 67.8268 | 67.424 | 115.5579 | 123.6053 | 3.1036 | 123.6649 | 83.0063 | -0.2655 | 123.6053 | 3.1036 | 83.0063 | 115.5579 | 123.6649 | -123.9304 | -123.9395
3058.7188 | 123.8159 | -61.409 | 62.2238 | -0.054703 | 0.019015 | 0.019395 | 0.014669 | 0.064948 | 9.4068e-05 | 0.082681 | -58.2916 | 62.2467 | -61.6837 | -61.5921 | 54.1718 | 21.6797 | 6.3126 | 5.9509 | 62.2421 | -61.7065 | -0.27466 | 0.022888 | 3.1174 | -0.1831 | -8.0521 | -0.29755 | 0.01831 | 3.392 | 67.7216 | 67.3599 | 115.5807 | 123.6557 | 3.1174 | 123.6511 | 83.0887 | -0.29755 | 123.6557 | 3.1174 | 83.0887 | 115.5807 | 123.6511 | -123.9075 | -123.9304
3059.7188 | 123.7793 | -61.409 | 62.2467 | -0.25307 | 0.015383 | 0.011704 | 0.0089016 | 0.063666 | 0.0015893 | 0.081826 | -58.3374 | 62.1826 | -61.6974 | -61.6058 | 54.1901 | 21.6202 | 6.5552 | 6.0104 | 62.265 | -61.6608 | -0.28839 | -0.064087 | 3.0716 | -0.19684 | -8.0566 | -0.25177 | 0.018311 | 3.36 | 67.9642 | 67.4194 | 115.5991 | 123.5916 | 3.0716 | 123.674 | 83.0292 | -0.25177 | 123.5916 | 3.0716 | 83.0292 | 115.5991 | 123.674 | -123.9441 | -123.9075
3060.7344 | 123.8571 | -61.4044 | 62.1964 | 0.23521 | 0.017947 | 0.017045 | 0.014456 | 0.065375 | 0.0013757 | 0.082467 | -58.3466 | 62.178 | -61.7111 | -61.6058 | 54.245 | 21.7026 | 6.2942 | 5.9463 | 62.1872 | -61.702 | -0.3067 | -0.01831 | 3.0579 | -0.20142 | -7.9514 | -0.29755 | -0.009155 | 3.3646 | 67.6987 | 67.3508 | 115.6494 | 123.5825 | 3.0579 | 123.5916 | 83.107 | -0.29755 | 123.5825 | 3.0579 | 83.107 | 115.6494 | 123.5916 | -123.9075 | -123.8983
3061.7188 | 123.8251 | -61.4044 | 62.265 | -0.10811 | 0.01816 | 0.018754 | 0.014669 | 0.063025 | 0.0011621 | 0.080331 | -58.287 | 62.2604 | -61.6745 | -61.5646 | 54.1992 | 21.6431 | 6.5094 | 6.0242 | 62.265 | -61.6928 | -0.27008 | -0.004578 | 3.1174 | -0.16022 | -8.0658 | -0.28839 | 0 | 3.3875 | 67.9138 | 67.4286 | 115.6036 | 123.6649 | 3.1174 | 123.6694 | 83.0475 | -0.28839 | 123.6649 | 3.1174 | 83.0475 | 115.6036 | 123.6694 | -123.9395 | -123.9578
3062.7188 | 123.7885 | -61.4227 | 62.265 | -0.37514 | 0.015597 | 0.013627 | 0.013601 | 0.061957 | 0.0015893 | 0.082253 | -58.3557 | 62.2421 | -61.6882 | -61.6104 | 54.2175 | 21.6156 | 6.5231 | 5.9555 | 62.2604 | -61.6745 | -0.2655 | -0.022889 | 3.067 | -0.18768 | -8.0475 | -0.25177 | -0.004578 | 3.3325 | 67.9459 | 67.3782 | 115.6403 | 123.6649 | 3.067 | 123.6832 | 83.0383 | -0.25177 | 123.6649 | 3.067 | 83.0383 | 115.6403 | 123.6832 | -123.9532 | -123.9395
3063.7188 | 123.7885 | -61.4273 | 62.2284 | -0.131 | 0.018801 | 0.017045 | 0.013174 | 0.064307 | -0.0026831 | 0.081613 | -58.4106 | 62.2421 | -61.7157 | -61.6562 | 54.1031 | 21.5973 | 6.5231 | 5.9235 | 62.233 | -61.7249 | -0.28839 | 0.013732 | 3.0167 | -0.22888 | -8.1253 | -0.29755 | 0.004577 | 3.3051 | 67.9504 | 67.3508 | 115.5304 | 123.6694 | 3.0167 | 123.6603 | 83.0246 | -0.29755 | 123.6694 | 3.0167 | 83.0246 | 115.5304 | 123.6603 | -123.9441 | -123.9532
3064.7188 | 123.8251 | -61.4136 | 62.2147 | -0.23018 | 0.017947 | 0.014695 | 0.015097 | 0.065589 | -0.00076053 | 0.080331 | -58.2733 | 62.2559 | -61.6791 | -61.5738 | 54.2542 | 21.6568 | 6.4682 | 5.9692 | 62.2375 | -61.6745 | -0.2655 | 0.041198 | 3.1403 | -0.16022 | -7.9605 | -0.26093 | 0.022888 | 3.4058 | 67.8818 | 67.3828 | 115.6677 | 123.6694 | 3.1403 | 123.6511 | 83.0704 | -0.26093 | 123.6694 | 3.1403 | 83.0704 | 115.6677 | 123.6511 | -123.8937 | -123.8892
3065.7188 | 123.8068 | -61.4182 | 62.2421 | 0.60905 | 0.017733 | 0.0132 | 0.015097 | 0.067298 | -0.00054693 | 0.081399 | -58.2275 | 62.2513 | -61.6791 | -61.5784 | 54.2038 | 21.73 | 6.4636 | 5.9738 | 62.265 | -61.7065 | -0.26093 | 0.009156 | 3.1906 | -0.16022 | -8.0383 | -0.28839 | 0.022889 | 3.4515 | 67.8818 | 67.392 | 115.6219 | 123.6694 | 3.1906 | 123.6832 | 83.1482 | -0.28839 | 123.6694 | 3.1906 | 83.1482 | 115.6219 | 123.6832 | -123.9212 | -123.9487
3066.7188 | 123.793 | -61.4365 | 62.2604 | -0.23018 | 0.013888 | 0.012559 | 0.008688 | 0.063666 | 0.00094847 | 0.077981 | -58.3603 | 62.233 | -61.7111 | -61.409 | 54.3274 | 21.5836 | 6.4682 | 5.9738 | 62.2742 | -61.6974 | -0.27466 | -0.027466 | 3.0762 | 0.027465 | -7.933 | -0.26093 | 0.013733 | 3.3508 | 67.9047 | 67.4103 | 115.7639 | 123.6694 | 3.0762 | 123.7106 | 83.02 | -0.26093 | 123.6694 | 3.0762 | 83.02 | 115.7639 | 123.7106 | -123.9716 | -123.9578
3067.7188 | 123.8068 | -61.4044 | 62.265 | -0.27596 | 0.01581 | 0.014909 | 0.010183 | 0.063666 | -0.00011953 | 0.08204 | -58.3054 | 62.1918 | -61.6653 | -61.5692 | 54.1946 | 21.7209 | 6.5826 | 6.0654 | 62.265 | -61.6379 | -0.26093 | -0.073243 | 3.0991 | -0.1648 | -8.0704 | -0.23346 | 0 | 3.36 | 67.9871 | 67.4698 | 115.5991 | 123.5962 | 3.0991 | 123.6694 | 83.1253 | -0.23346 | 123.5962 | 3.0991 | 83.1253 | 115.5991 | 123.6694 | -123.9304 | -123.9029
3068.7344 | 123.7976 | -61.4273 | 62.233 | 0.15129 | 0.019015 | 0.018327 | 0.0071926 | 0.062812 | 0.0013757 | 0.079476 | -58.3374 | 62.233 | -61.702 | -61.6104 | 54.1992 | 21.6248 | 6.4957 | 5.9463 | 62.2375 | -61.7294 | -0.27466 | 0 | 3.0899 | -0.18311 | -8.0338 | -0.30212 | 0.004578 | 3.3646 | 67.923 | 67.3737 | 115.6265 | 123.6603 | 3.0899 | 123.6649 | 83.0521 | -0.30212 | 123.6603 | 3.0899 | 83.0521 | 115.6265 | 123.6649 | -123.9349 | -123.9624
3069.7188 | 123.8251 | -61.4044 | 62.2559 | -0.25307 | 0.016878 | 0.017259 | 0.013388 | 0.065161 | 0.0015893 | 0.080117 | -58.3054 | 62.233 | -61.6745 | -61.5509 | 54.1992 | 21.6339 | 6.5369 | 6.0333 | 62.2925 | -61.6791 | -0.27008 | -0.022888 | 3.0991 | -0.14648 | -8.0566 | -0.27466 | 0.036621 | 3.3691 | 67.9413 | 67.4377 | 115.6036 | 123.6374 | 3.0991 | 123.6969 | 83.0383 | -0.27466 | 123.6374 | 3.0991 | 83.0383 | 115.6036 | 123.6969 | -123.9304 | -123.9349
3070.7188 | 123.8388 | -61.409 | 62.233 | -0.062332 | 0.016451 | 0.019608 | 0.014029 | 0.064307 | -0.00054693 | 0.081185 | -58.3099 | 62.2375 | -61.6745 | -61.5784 | 54.1306 | 21.5881 | 6.6193 | 6.0883 | 62.2604 | -61.6928 | -0.2655 | 0.004578 | 3.0991 | -0.16937 | -8.1024 | -0.28381 | 0.027466 | 3.3646 | 68.0283 | 67.4973 | 115.5396 | 123.6465 | 3.0991 | 123.6694 | 82.9971 | -0.28381 | 123.6465 | 3.0991 | 82.9971 | 115.5396 | 123.6694 | -123.9075 | -123.9258
3071.7188 | 123.8434 | -61.3907 | 62.233 | -0.19966 | 0.013033 | 0.0132 | 0.0074062 | 0.062812 | -0.00011953 | 0.082467 | -58.287 | 62.1597 | -61.6653 | -61.5326 | 54.2587 | 21.6888 | 6.5552 | 6.1249 | 62.2513 | -61.6608 | -0.27466 | -0.073242 | 3.1036 | -0.14191 | -7.9742 | -0.27008 | 0.018311 | 3.3783 | 67.9459 | 67.5156 | 115.6494 | 123.5504 | 3.1036 | 123.642 | 83.0795 | -0.27008 | 123.5504 | 3.1036 | 83.0795 | 115.6494 | 123.642 | -123.8983 | -123.8937
3072.7188 | 123.8022 | -61.3953 | 62.2467 | -0.15388 | 0.016451 | 0.016404 | 0.012747 | 0.062171 | -0.00054693 | 0.080972 | -58.2962 | 62.2284 | -61.6699 | -61.5738 | 54.1168 | 21.6751 | 6.6284 | 6.0104 | 62.2467 | -61.7111 | -0.27466 | -0.01831 | 3.0991 | -0.17853 | -8.1299 | -0.31586 | 0 | 3.3737 | 68.0237 | 67.4057 | 115.5121 | 123.6237 | 3.0991 | 123.642 | 83.0704 | -0.31586 | 123.6237 | 3.0991 | 83.0704 | 115.5121 | 123.642 | -123.9166 | -123.9578
3073.7188 | 123.8388 | -61.409 | 62.2513 | -0.14626 | 0.019015 | 0.017472 | 0.015524 | 0.06388 | 0.0018031 | 0.079263 | -58.223 | 62.2421 | -61.6791 | -61.5646 | 54.1534 | 21.7163 | 6.5872 | 6.0471 | 62.2559 | -61.7157 | -0.27008 | -0.009156 | 3.186 | -0.15564 | -8.0978 | -0.3067 | 0.004577 | 3.4561 | 67.9962 | 67.4561 | 115.5624 | 123.6511 | 3.186 | 123.6649 | 83.1253 | -0.3067 | 123.6511 | 3.186 | 83.1253 | 115.5624 | 123.6649 | -123.9304 | -123.967
3074.7188 | 123.8205 | -61.3998 | 62.2604 | -0.23781 | 0.018587 | 0.012986 | 0.012106 | 0.064948 | 0.00052127 | 0.081613 | -58.3145 | 62.2696 | -61.6653 | -61.6013 | 54.0894 | 21.698 | 6.6925 | 6.0837 | 62.2696 | -61.6882 | -0.2655 | 0.009155 | 3.0853 | -0.20142 | -8.1711 | -0.28839 | 0.009155 | 3.3508 | 68.0923 | 67.4835 | 115.4892 | 123.6694 | 3.0853 | 123.6694 | 83.0978 | -0.28839 | 123.6694 | 3.0853 | 83.0978 | 115.4892 | 123.6694 | -123.9258 | -123.9487
3075.7188 | 123.8434 | -61.4136 | 62.2284 | -0.069961 | 0.017733 | 0.01555 | 0.018515 | 0.063239 | 0.0011621 | 0.081826 | -58.2596 | 62.2467 | -61.7157 | -61.5829 | 54.1443 | 21.7117 | 6.6467 | 6.1432 | 62.2192 | -61.6974 | -0.30212 | 0.01831 | 3.154 | -0.16937 | -8.0841 | -0.28381 | -0.009156 | 3.4561 | 68.0603 | 67.5568 | 115.5579 | 123.6603 | 3.154 | 123.6328 | 83.1253 | -0.28381 | 123.6603 | 3.154 | 83.1253 | 115.5579 | 123.6328 | -123.9441 | -123.9258
3076.7188 | 123.8159 | -61.3998 | 62.2375 | -0.11574 | 0.017947 | 0.01854 | 0.015951 | 0.065161 | 0.00052127 | 0.080117 | -58.255 | 62.265 | -61.6837 | -61.5326 | 53.9932 | 21.5652 | 6.8573 | 6.1752 | 62.2467 | -61.7157 | -0.28381 | 0.027466 | 3.1448 | -0.13275 | -8.2443 | -0.31586 | 0.009155 | 3.4287 | 68.2571 | 67.5751 | 115.3931 | 123.6649 | 3.1448 | 123.6465 | 82.9651 | -0.31586 | 123.6649 | 3.1448 | 82.9651 | 115.3931 | 123.6465 | -123.9212 | -123.9532
3077.7188 | 123.8113 | -61.4044 | 62.2513 | -0.27596 | 0.016665 | 0.014268 | 0.012106 | 0.06388 | 0.00030767 | 0.079049 | -58.3099 | 62.2421 | -61.6882 | -61.5738 | 54.2038 | 21.7163 | 6.6879 | 6.1478 | 62.2604 | -61.6791 | -0.28381 | -0.009156 | 3.0945 | -0.16937 | -8.0475 | -0.27466 | 0.009155 | 3.3783 | 68.0923 | 67.5522 | 115.6082 | 123.6465 | 3.0945 | 123.6649 | 83.1207 | -0.27466 | 123.6465 | 3.0945 | 83.1207 | 115.6082 | 123.6649 | -123.9395 | -123.9304
3078.7188 | 123.8068 | -61.4182 | 62.2375 | -0.10048 | 0.019228 | 0.01854 | 0.016165 | 0.064093 | 0.00094847 | 0.080972 | -58.2687 | 62.2467 | -61.6653 | -61.5921 | 54.0848 | 21.6476 | 6.633 | 6.1569 | 62.2421 | -61.6882 | -0.24719 | 0.009155 | 3.1494 | -0.17395 | -8.1528 | -0.27008 | 0.004577 | 3.3966 | 68.0511 | 67.5751 | 115.5029 | 123.6649 | 3.1494 | 123.6603 | 83.0658 | -0.27008 | 123.6649 | 3.1494 | 83.0658 | 115.5029 | 123.6603 | -123.9029 | -123.9258
3079.7188 | 123.7885 | -61.3998 | 62.2513 | -0.22255 | 0.016024 | 0.012773 | 0.0078336 | 0.062171 | 9.4068e-05 | 0.081185 | -58.1589 | 62.2971 | -61.6699 | -61.5921 | 54.0939 | 21.666 | 6.7245 | 6.1111 | 62.2971 | -61.7111 | -0.27008 | 0.045776 | 3.241 | -0.19226 | -8.1573 | -0.31128 | 0.045776 | 3.511 | 68.1244 | 67.511 | 115.4938 | 123.6969 | 3.241 | 123.6969 | 83.0658 | -0.31128 | 123.6969 | 3.241 | 83.0658 | 115.4938 | 123.6969 | -123.9212 | -123.9624
3080.7188 | 123.7747 | -61.4319 | 62.233 | -0.031814 | 0.017733 | 0.019395 | 0.013601 | 0.066657 | 0.0022303 | 0.080331 | -58.2825 | 62.2559 | -61.6653 | -61.6333 | 54.0573 | 21.666 | 6.7017 | 6.1203 | 62.2375 | -61.7203 | -0.23346 | 0.022888 | 3.1494 | -0.20142 | -8.1757 | -0.28839 | 0.004578 | 3.3829 | 68.1335 | 67.5522 | 115.4892 | 123.6877 | 3.1494 | 123.6694 | 83.0978 | -0.28839 | 123.6877 | 3.1494 | 83.0978 | 115.4892 | 123.6694 | -123.8983 | -123.9532
3081.7344 | 123.8892 | -61.409 | 62.1872 | -0.12337 | 0.017306 | 0.019822 | 0.008688 | 0.064093 | 0.0011621 | 0.080972 | -58.3008 | 62.114 | -61.7111 | -61.5555 | 54.1718 | 21.7575 | 6.4774 | 6.2119 | 62.1918 | -61.6791 | -0.30212 | -0.073242 | 3.1082 | -0.14648 | -8.0154 | -0.27008 | 0.004577 | 3.4103 | 67.8864 | 67.6209 | 115.5807 | 123.523 | 3.1082 | 123.6008 | 83.1665 | -0.27008 | 123.523 | 3.1082 | 83.1665 | 115.5807 | 123.6008 | -123.8983 | -123.8663
3082.7188 | 123.7747 | -61.3953 | 62.265 | -0.22255 | 0.017947 | 0.014268 | 0.0084744 | 0.060889 | 0.0018031 | 0.081826 | -58.3328 | 62.2421 | -61.6928 | -61.6058 | 54.1306 | 21.7163 | 6.8344 | 6.1935 | 62.2742 | -61.7065 | -0.29755 | -0.022889 | 3.0624 | -0.21057 | -8.1345 | -0.31128 | 0.009155 | 3.36 | 68.2297 | 67.5888 | 115.5258 | 123.6374 | 3.0624 | 123.6694 | 83.1116 | -0.31128 | 123.6374 | 3.0624 | 83.1116 | 115.5258 | 123.6694 | -123.9578 | -123.9716
3083.7188 | 123.8022 | -61.4365 | 62.2284 | 0.067368 | 0.016238 | 0.018968 | 0.015524 | 0.062384 | 0.0018031 | 0.081399 | -58.3557 | 62.233 | -61.7111 | -61.6562 | 54.0665 | 21.7667 | 6.665 | 6.1203 | 62.2055 | -61.7111 | -0.27466 | 0.004577 | 3.0807 | -0.21973 | -8.1619 | -0.27466 | -0.022889 | 3.3554 | 68.1015 | 67.5568 | 115.5029 | 123.6694 | 3.0807 | 123.642 | 83.2031 | -0.27466 | 123.6694 | 3.0807 | 83.2031 | 115.5029 | 123.642 | -123.9395 | -123.9395
3084.7188 | 123.8113 | -61.409 | 62.233 | -0.21492 | 0.017092 | 0.014482 | 0.010611 | 0.062171 | 0.00030767 | 0.080117 | -58.3328 | 62.2238 | -61.7065 | -61.5875 | 54.1443 | 21.7896 | 6.7749 | 6.1935 | 62.2559 | -61.7111 | -0.29755 | -0.009155 | 3.0762 | -0.17853 | -8.0887 | -0.30212 | 0.022888 | 3.3737 | 68.1839 | 67.6025 | 115.5533 | 123.6328 | 3.0762 | 123.6649 | 83.1985 | -0.30212 | 123.6328 | 3.0762 | 83.1985 | 115.5533 | 123.6649 | -123.9395 | -123.9441
3085.7188 | 123.8388 | -61.4227 | 62.233 | 0.12077 | 0.019656 | 0.014909 | 0.013174 | 0.064093 | -0.0014013 | 0.081826 | -58.2779 | 62.2375 | -61.6882 | -61.5738 | 54.1718 | 21.8491 | 6.6925 | 6.1844 | 62.2421 | -61.7111 | -0.2655 | 0.004578 | 3.1448 | -0.15106 | -8.0612 | -0.28839 | 0.009155 | 3.4103 | 68.1152 | 67.6071 | 115.5945 | 123.6603 | 3.1448 | 123.6649 | 83.2718 | -0.28839 | 123.6603 | 3.1448 | 83.2718 | 115.5945 | 123.6649 | -123.9212 | -123.9441
3086.7188 | 123.8159 | -61.4273 | 62.2192 | -1.2754 | 0.016878 | 0.013413 | 0.014456 | 0.064093 | 0.0011621 | 0.081185 | -58.3282 | 62.2513 | -61.6928 | -61.5601 | 54.2633 | 21.936 | 6.665 | 6.134 | 62.2559 | -61.7157 | -0.2655 | 0.032044 | 3.0991 | -0.13275 | -7.9559 | -0.28839 | 0.036621 | 3.3646 | 68.0923 | 67.5613 | 115.6906 | 123.6786 | 3.0991 | 123.6832 | 83.3633 | -0.28839 | 123.6786 | 3.0991 | 83.3633 | 115.6906 | 123.6832 | -123.912 | -123.9349
3087.7188 | 123.8297 | -61.4273 | 62.2192 | -0.23781 | 0.016878 | 0.011277 | 0.0063382 | 0.06388 | -0.00097413 | 0.082894 | -58.3282 | 62.2101 | -61.6791 | -61.5829 | 54.1534 | 21.7712 | 6.7749 | 6.1798 | 62.2467 | -61.6745 | -0.25177 | -0.009155 | 3.0991 | -0.15564 | -8.0658 | -0.24719 | 0.027466 | 3.3508 | 68.2022 | 67.6071 | 115.5807 | 123.6374 | 3.0991 | 123.674 | 83.1985 | -0.24719 | 123.6374 | 3.0991 | 83.1985 | 115.5807 | 123.674 | -123.8983 | -123.8937
3088.7188 | 123.8159 | -61.4548 | 62.233 | -0.19203 | 0.016451 | 0.01555 | 0.014029 | 0.063666 | -0.00097413 | 0.080758 | -58.3099 | 62.2513 | -61.6882 | -61.5738 | 54.2679 | 21.9177 | 6.7429 | 6.1798 | 62.2375 | -61.6882 | -0.23346 | 0.018311 | 3.1448 | -0.11902 | -7.9651 | -0.23346 | 0.004578 | 3.3783 | 68.1976 | 67.6346 | 115.7227 | 123.7061 | 3.1448 | 123.6923 | 83.3725 | -0.23346 | 123.7061 | 3.1448 | 83.3725 | 115.7227 | 123.6923 | -123.9212 | -123.9212
3089.7188 | 123.8068 | -61.409 | 62.2513 | -0.20729 | 0.019015 | 0.014695 | 0.01232 | 0.064948 | 0.00030767 | 0.08204 | -58.374 | 62.2238 | -61.6928 | -61.5967 | 54.1946 | 21.7804 | 6.7429 | 6.102 | 62.2742 | -61.7249 | -0.28381 | -0.027466 | 3.035 | -0.18768 | -8.0566 | -0.31586 | 0.022888 | 3.3188 | 68.1519 | 67.511 | 115.6036 | 123.6328 | 3.035 | 123.6832 | 83.1894 | -0.31586 | 123.6328 | 3.035 | 83.1894 | 115.6036 | 123.6832 | -123.9441 | -123.9761
3090.7188 | 123.8297 | -61.4044 | 62.2421 | -0.26833 | 0.016665 | 0.015763 | 0.012533 | 0.06388 | 0.0011621 | 0.081185 | -58.3191 | 62.2467 | -61.6882 | -61.5875 | 54.332 | 21.8491 | 6.7429 | 6.1935 | 62.2742 | -61.6745 | -0.28381 | 0.004578 | 3.0853 | -0.18311 | -7.9102 | -0.27008 | 0.032044 | 3.3691 | 68.1473 | 67.598 | 115.7364 | 123.6511 | 3.0853 | 123.6786 | 83.2535 | -0.27008 | 123.6511 | 3.0853 | 83.2535 | 115.7364 | 123.6786 | -123.9304 | -123.9166
3091.7344 | 123.7381 | -61.4594 | 62.2513 | 0.14366 | 0.014315 | 0.017259 | 0.014669 | 0.066016 | 0.0011621 | 0.082467 | -58.3786 | 62.233 | -61.7294 | -61.6699 | 54.4601 | 21.6522 | 6.4041 | 6.459 | 62.1872 | -61.7386 | -0.27008 | -0.018311 | 3.0807 | -0.21057 | -7.7911 | -0.27923 | -0.064087 | 3.3508 | 67.8635 | 67.9184 | 115.9195 | 123.6923 | 3.0807 | 123.6465 | 83.1116 | -0.27923 | 123.6923 | 3.0807 | 83.1116 | 115.9195 | 123.6465 | -123.9807 | -123.9899
3092.7188 | 123.8983 | -61.3998 | 62.233 | -0.19203 | 0.014529 | 0.014695 | 0.008688 | 0.063666 | 0.00094847 | 0.07969 | -58.3054 | 62.1826 | -61.6699 | -61.5234 | 54.3274 | 21.4462 | 6.7154 | 6.2942 | 62.2192 | -61.6425 | -0.27008 | -0.050354 | 3.0945 | -0.1236 | -7.9056 | -0.24262 | -0.013733 | 3.3646 | 68.1152 | 67.6941 | 115.7272 | 123.5825 | 3.0945 | 123.6191 | 82.8461 | -0.24262 | 123.5825 | 3.0945 | 82.8461 | 115.7272 | 123.6191 | -123.9029 | -123.8754
3093.7188 | 123.8159 | -61.4227 | 62.2513 | -0.12337 | 0.017947 | 0.012986 | 0.01531 | 0.062384 | -0.00033333 | 0.081613 | -58.3694 | 62.2513 | -61.6653 | -61.6058 | 54.245 | 20.4849 | 6.8481 | 6.2256 | 62.2696 | -61.6882 | -0.24262 | 0 | 3.0533 | -0.18311 | -8.0063 | -0.2655 | 0.01831 | 3.2959 | 68.2709 | 67.6483 | 115.6677 | 123.674 | 3.0533 | 123.6923 | 81.9077 | -0.2655 | 123.674 | 3.0533 | 81.9077 | 115.6677 | 123.6923 | -123.9166 | -123.9395
3094.7188 | 123.7839 | -61.3953 | 62.2559 | -0.17677 | 0.014742 | 0.013841 | 0.011251 | 0.06388 | -0.00076053 | 0.081826 | -58.3878 | 62.2559 | -61.6837 | -61.6287 | 54.3457 | 20.9518 | 6.6147 | 5.9875 | 62.2742 | -61.702 | -0.28839 | 0 | 3.0075 | -0.23346 | -7.9102 | -0.3067 | 0.018311 | 3.2959 | 68.0099 | 67.3828 | 115.741 | 123.6511 | 3.0075 | 123.6694 | 82.3471 | -0.3067 | 123.6511 | 3.0075 | 82.3471 | 115.741 | 123.6694 | -123.9395 | -123.9578
3095.7188 | 123.7747 | -61.3907 | 62.2742 | -0.27596 | 0.017947 | 0.013627 | 0.013388 | 0.062171 | 0.0013757 | 0.079904 | -58.3832 | 62.2375 | -61.6882 | -61.6013 | 54.2404 | 20.8969 | 6.7932 | 6.1569 | 62.2375 | -61.6791 | -0.29755 | -0.036621 | 3.0075 | -0.21057 | -8.0338 | -0.28839 | -0.036621 | 3.3051 | 68.1839 | 67.5476 | 115.6311 | 123.6282 | 3.0075 | 123.6282 | 82.2876 | -0.28839 | 123.6282 | 3.0075 | 82.2876 | 115.6311 | 123.6282 | -123.9624 | -123.9532
3096.7344 | 123.8434 | -61.377 | 62.2055 | -0.131 | 0.015383 | 0.012132 | 0.0065518 | 0.061957 | 0.00094847 | 0.080972 | -58.3282 | 62.1689 | -61.6516 | -61.5921 | 54.2999 | 21.2173 | 6.6742 | 6.2119 | 62.2147 | -61.6974 | -0.27466 | -0.036621 | 3.0487 | -0.21515 | -7.9056 | -0.32043 | 0.009156 | 3.3234 | 68.0511 | 67.5888 | 115.6769 | 123.5458 | 3.0487 | 123.5916 | 82.5943 | -0.32043 | 123.5458 | 3.0487 | 82.5943 | 115.6769 | 123.5916 | -123.8571 | -123.9029
3097.7188 | 123.7976 | -61.4319 | 62.2742 | 0.19707 | 0.017519 | 0.015977 | 0.013815 | 0.062812 | -0.00033333 | 0.080331 | -58.3374 | 62.233 | -61.7065 | -61.5875 | 54.2038 | 21.1487 | 6.7749 | 6.1661 | 62.265 | -61.7157 | -0.27466 | -0.041199 | 3.0945 | -0.15564 | -8.0704 | -0.28381 | -0.009155 | 3.3691 | 68.2068 | 67.598 | 115.6357 | 123.6649 | 3.0945 | 123.6969 | 82.5806 | -0.28381 | 123.6649 | 3.0945 | 82.5806 | 115.6357 | 123.6969 | -123.9807 | -123.9899
3098.7344 | 123.7793 | -61.4273 | 62.2284 | 0.074997 | 0.016451 | 0.019395 | 0.014669 | 0.062812 | 0.00094847 | 0.08204 | -58.3694 | 62.2467 | -61.7157 | -61.6562 | 54.1214 | 20.9747 | 6.7703 | 6.1295 | 62.233 | -61.7294 | -0.28839 | 0.01831 | 3.0579 | -0.22888 | -8.107 | -0.30212 | 0.004577 | 3.3463 | 68.1976 | 67.5568 | 115.5487 | 123.674 | 3.0579 | 123.6603 | 82.402 | -0.30212 | 123.674 | 3.0579 | 82.402 | 115.5487 | 123.6603 | -123.9441 | -123.9578
3099.7188 | 123.8892 | -61.377 | 62.2375 | -0.23018 | 0.01346 | 0.013413 | 0.0078336 | 0.062598 | 0.00073487 | 0.081185 | -58.2642 | 62.1597 | -61.6653 | -61.528 | 54.3365 | 21.2402 | 6.7291 | 6.3492 | 62.2009 | -61.6562 | -0.28839 | -0.07782 | 3.1128 | -0.15106 | -7.901 | -0.27924 | -0.036621 | 3.4012 | 68.1061 | 67.7261 | 115.7135 | 123.5367 | 3.1128 | 123.5779 | 82.6172 | -0.27924 | 123.5367 | 3.1128 | 82.6172 | 115.7135 | 123.5779 | -123.9029 | -123.8937
3100.7188 | 123.8434 | -61.4273 | 62.2559 | -0.09285 | 0.01816 | 0.022172 | 0.017874 | 0.063666 | 0.0039393 | 0.080544 | -58.2733 | 62.2467 | -61.6745 | -61.5692 | 54.2816 | 21.0892 | 6.7932 | 6.1752 | 62.2284 | -61.7157 | -0.24719 | -0.009155 | 3.154 | -0.14191 | -7.9742 | -0.28839 | -0.027465 | 3.4012 | 68.2205 | 67.6025 | 115.7089 | 123.674 | 3.154 | 123.6557 | 82.5165 | -0.28839 | 123.674 | 3.154 | 82.5165 | 115.7089 | 123.6557 | -123.9304 | -123.9716
3101.7188 | 123.7793 | -61.4044 | 62.2421 | -0.27596 | 0.016878 | 0.014482 | 0.0091152 | 0.061957 | 0.0011621 | 0.081185 | -58.3466 | 62.233 | -61.6928 | -61.5875 | 54.2313 | 20.9976 | 6.8573 | 6.2119 | 62.2787 | -61.6791 | -0.28839 | -0.009155 | 3.0579 | -0.18311 | -8.0109 | -0.27466 | 0.036622 | 3.3463 | 68.2617 | 67.6163 | 115.6357 | 123.6374 | 3.0579 | 123.6832 | 82.402 | -0.27466 | 123.6374 | 3.0579 | 82.402 | 115.6357 | 123.6832 | -123.9349 | -123.9212
3102.7188 | 123.848 | -61.3678 | 62.2101 | -0.20729 | 0.014101 | 0.014482 | 0.010824 | 0.061103 | -0.00076053 | 0.078195 | -58.2916 | 62.1552 | -61.6745 | -61.5234 | 54.2908 | 21.2265 | 6.7978 | 6.308 | 62.2192 | -61.6653 | -0.3067 | -0.054932 | 3.0762 | -0.15564 | -7.9193 | -0.29755 | 0.009155 | 3.3829 | 68.1656 | 67.6758 | 115.6586 | 123.5229 | 3.0762 | 123.587 | 82.5943 | -0.29755 | 123.5229 | 3.0762 | 82.5943 | 115.6586 | 123.587 | -123.8846 | -123.8754
3103.7188 | 123.8297 | -61.3998 | 62.2375 | -0.039444 | 0.019015 | 0.014268 | 0.017874 | 0.062384 | -0.00076053 | 0.080117 | -58.3008 | 62.2559 | -61.6791 | -61.5601 | 54.1946 | 21.1899 | 6.8573 | 6.308 | 62.2284 | -61.7065 | -0.27924 | 0.01831 | 3.0991 | -0.16022 | -8.0429 | -0.3067 | -0.009155 | 3.3783 | 68.2571 | 67.7078 | 115.5945 | 123.6557 | 3.0991 | 123.6282 | 82.5897 | -0.3067 | 123.6557 | 3.0991 | 82.5897 | 115.5945 | 123.6282 | -123.9166 | -123.9441
3104.7188 | 123.7656 | -61.4044 | 62.2879 | -0.30647 | 0.014101 | 0.012559 | 0.011251 | 0.062598 | 0.0020167 | 0.079049 | -58.3923 | 62.2421 | -61.6516 | -61.6333 | 54.1855 | 21.1121 | 6.8939 | 6.2851 | 62.2833 | -61.7203 | -0.24719 | -0.045777 | 3.0121 | -0.22888 | -8.1024 | -0.31586 | -0.004578 | 3.2593 | 68.2983 | 67.6895 | 115.5899 | 123.6465 | 3.0121 | 123.6877 | 82.5165 | -0.31586 | 123.6465 | 3.0121 | 82.5165 | 115.5899 | 123.6877 | -123.9395 | -124.0082
3105.7188 | 123.8205 | -61.409 | 62.233 | 1.6314 | 0.017519 | 0.014695 | 0.014669 | 0.064948 | 0.00030767 | 0.082467 | -58.1589 | 62.2055 | -61.7111 | -61.5646 | 54.2953 | 21.1121 | 6.8207 | 6.3309 | 62.2284 | -61.6882 | -0.30212 | -0.027466 | 3.2501 | -0.15564 | -7.9376 | -0.27923 | -0.004577 | 3.5522 | 68.2297 | 67.7399 | 115.7043 | 123.6145 | 3.2501 | 123.6374 | 82.5211 | -0.27923 | 123.6145 | 3.2501 | 82.5211 | 115.7043 | 123.6374 | -123.9441 | -123.9212
3106.7188 | 123.8892 | -61.3953 | 62.233 | -0.131 | 0.01282 | 0.016831 | 0.0065518 | 0.059821 | -0.00097413 | 0.081613 | -58.2916 | 62.1597 | -61.6608 | -61.4914 | 54.2679 | 21.2036 | 6.8069 | 6.4453 | 62.2238 | -61.647 | -0.2655 | -0.073242 | 3.1036 | -0.09613 | -7.9651 | -0.25177 | -0.009155 | 3.3691 | 68.2022 | 67.8406 | 115.6631 | 123.555 | 3.1036 | 123.6191 | 82.5989 | -0.25177 | 123.555 | 3.1036 | 82.5989 | 115.6631 | 123.6191 | -123.8937 | -123.88
3107.7188 | 123.8388 | -61.3953 | 62.2559 | -0.29121 | 0.01346 | 0.015763 | 0.0097562 | 0.061316 | -0.00076053 | 0.08204 | -58.3054 | 62.1826 | -61.6653 | -61.5555 | 54.3091 | 21.1761 | 6.839 | 6.3309 | 62.2604 | -61.6608 | -0.27008 | -0.073242 | 3.0899 | -0.16022 | -7.9468 | -0.2655 | 0.004578 | 3.36 | 68.2343 | 67.7261 | 115.7043 | 123.5779 | 3.0899 | 123.6557 | 82.5714 | -0.2655 | 123.5779 | 3.0899 | 82.5714 | 115.7043 | 123.6557 | -123.9212 | -123.9166
3108.7188 | 123.7701 | -61.409 | 62.2696 | -0.16914 | 0.01581 | 0.012986 | 0.012106 | 0.061316 | -0.0011877 | 0.081399 | -58.3832 | 62.2467 | -61.6745 | -61.5921 | 54.2038 | 21.0205 | 6.9351 | 6.3034 | 62.2604 | -61.6974 | -0.2655 | -0.022888 | 3.0258 | -0.1831 | -8.0658 | -0.28839 | -0.009155 | 3.2913 | 68.3441 | 67.7124 | 115.6128 | 123.6557 | 3.0258 | 123.6694 | 82.4295 | -0.28839 | 123.6557 | 3.0258 | 82.4295 | 115.6128 | 123.6694 | -123.9441 | -123.967
3109.7188 | 123.7839 | -61.4273 | 62.2787 | -0.19966 | 0.014529 | 0.011491 | 0.010183 | 0.061957 | 0.00030767 | 0.080758 | -58.3694 | 62.2238 | -61.6974 | -61.6058 | 54.2633 | 21.1945 | 6.9534 | 6.3171 | 62.2467 | -61.6745 | -0.27008 | -0.054932 | 3.0579 | -0.17853 | -8.0154 | -0.24719 | -0.032044 | 3.3279 | 68.3807 | 67.7444 | 115.6906 | 123.6511 | 3.0579 | 123.674 | 82.6218 | -0.24719 | 123.6511 | 3.0579 | 82.6218 | 115.6906 | 123.674 | -123.9761 | -123.9532
3110.7188 | 123.8022 | -61.409 | 62.2192 | 0.37254 | 0.017519 | 0.014482 | 0.01531 | 0.062171 | 0.00030767 | 0.080544 | -58.3328 | 62.233 | -61.7065 | -61.6516 | 54.1534 | 21.1945 | 6.9214 | 6.2668 | 62.2284 | -61.7386 | -0.29755 | 0.013733 | 3.0762 | -0.24261 | -8.0658 | -0.32959 | 0.009156 | 3.3737 | 68.3304 | 67.6758 | 115.5624 | 123.642 | 3.0762 | 123.6374 | 82.6035 | -0.32959 | 123.642 | 3.0762 | 82.6035 | 115.5624 | 123.6374 | -123.9258 | -123.9578
3111.7188 | 123.8068 | -61.4273 | 62.2513 | -0.24544 | 0.014956 | 0.018113 | 0.010824 | 0.062812 | -0.00076053 | 0.080758 | -58.342 | 62.2192 | -61.7157 | -61.5967 | 54.2221 | 21.254 | 6.9672 | 6.3309 | 62.2513 | -61.6837 | -0.28839 | -0.032044 | 3.0853 | -0.16937 | -8.0292 | -0.25635 | 0 | 3.3737 | 68.3945 | 67.7582 | 115.6494 | 123.6465 | 3.0853 | 123.6786 | 82.6813 | -0.25635 | 123.6465 | 3.0853 | 82.6813 | 115.6494 | 123.6786 | -123.967 | -123.9349
3112.7188 | 123.7656 | -61.4136 | 62.2421 | -0.23781 | 0.015169 | 0.011064 | 0.008688 | 0.061957 | -0.00097413 | 0.080331 | -58.3145 | 62.2055 | -61.6837 | -61.5829 | 54.2587 | 21.2997 | 6.926 | 6.3171 | 62.2742 | -61.6699 | -0.27008 | -0.036621 | 3.0991 | -0.16937 | -7.9834 | -0.25635 | 0.032044 | 3.3691 | 68.3395 | 67.7307 | 115.6723 | 123.6191 | 3.0991 | 123.6877 | 82.7133 | -0.25635 | 123.6191 | 3.0991 | 82.7133 | 115.6723 | 123.6877 | -123.9258 | -123.912
3113.7188 | 123.8113 | -61.4136 | 62.2238 | 1.1965 | 0.017092 | 0.017259 | 0.015951 | 0.06388 | 0.0011621 | 0.080544 | -58.3282 | 62.2238 | -61.6974 | -61.5509 | 54.245 | 21.3638 | 6.8207 | 6.2988 | 62.2192 | -61.6837 | -0.28381 | 0 | 3.0853 | -0.13733 | -7.9788 | -0.27008 | -0.004578 | 3.3691 | 68.2343 | 67.7124 | 115.6586 | 123.6374 | 3.0853 | 123.6328 | 82.7774 | -0.27008 | 123.6374 | 3.0853 | 82.7774 | 115.6586 | 123.6328 | -123.9212 | -123.9075
3114.7188 | 123.7564 | -61.409 | 62.2559 | -0.19203 | 0.01581 | 0.011064 | 0.012747 | 0.06388 | 0.0018031 | 0.080331 | -58.3328 | 62.233 | -61.7065 | -61.6013 | 54.1946 | 21.286 | 6.9901 | 6.5369 | 62.2879 | -61.6608 | -0.29755 | -0.022888 | 3.0762 | -0.19226 | -8.0612 | -0.25177 | 0.032044 | 3.3737 | 68.399 | 67.9459 | 115.6036 | 123.642 | 3.0762 | 123.6969 | 82.695 | -0.25177 | 123.642 | 3.0762 | 82.695 | 115.6036 | 123.6969 | -123.9624 | -123.9166
3115.7188 | 123.7885 | -61.3998 | 62.2559 | -0.2607 | 0.017092 | 0.016618 | 0.014029 | 0.063239 | -0.00054693 | 0.081399 | -58.3603 | 62.2513 | -61.6837 | -61.5921 | 54.1901 | 21.2402 | 6.8344 | 6.2439 | 62.2604 | -61.6791 | -0.28381 | -0.004577 | 3.0396 | -0.19226 | -8.0658 | -0.27924 | 0.004578 | 3.3234 | 68.2343 | 67.6437 | 115.5899 | 123.6511 | 3.0396 | 123.6603 | 82.6401 | -0.27924 | 123.6511 | 3.0396 | 82.6401 | 115.5899 | 123.6603 | -123.9395 | -123.9349
3116.7188 | 123.8022 | -61.3953 | 62.2513 | -0.16151 | 0.016024 | 0.019395 | 0.011465 | 0.064093 | -0.00033333 | 0.081399 | -58.3282 | 62.233 | -61.6974 | -61.6013 | 54.1855 | 21.3226 | 6.8756 | 6.2576 | 62.2742 | -61.7065 | -0.30212 | -0.018311 | 3.067 | -0.20599 | -8.0658 | -0.31128 | 0.022888 | 3.3691 | 68.2709 | 67.6529 | 115.5807 | 123.6282 | 3.067 | 123.6694 | 82.7179 | -0.31128 | 123.6282 | 3.067 | 82.7179 | 115.5807 | 123.6694 | -123.9487 | -123.9578
3117.7188 | 123.7976 | -61.409 | 62.233 | -0.32936 | 0.015169 | 0.01555 | 0.0091152 | 0.063025 | -0.00033333 | 0.080758 | -58.3511 | 62.2238 | -61.6791 | -61.6241 | 54.2221 | 21.3684 | 6.8893 | 6.3263 | 62.2513 | -61.6928 | -0.27008 | -0.009155 | 3.0579 | -0.21515 | -8.0109 | -0.28381 | 0.018311 | 3.3279 | 68.2983 | 67.7353 | 115.6311 | 123.6328 | 3.0579 | 123.6603 | 82.7774 | -0.28381 | 123.6328 | 3.0579 | 82.7774 | 115.6311 | 123.6603 | -123.912 | -123.9258
3118.7188 | 123.8113 | -61.4044 | 62.2238 | -0.24544 | 0.017519 | 0.021745 | 0.015738 | 0.062171 | -0.00097413 | 0.080544 | -58.3237 | 62.2513 | -61.6791 | -61.5509 | 54.2725 | 21.3364 | 6.8024 | 6.3583 | 62.2147 | -61.6928 | -0.27466 | 0.027466 | 3.0807 | -0.14648 | -7.9514 | -0.28839 | -0.009155 | 3.3554 | 68.2068 | 67.7628 | 115.6769 | 123.6557 | 3.0807 | 123.6191 | 82.7408 | -0.28839 | 123.6557 | 3.0807 | 82.7408 | 115.6769 | 123.6191 | -123.9029 | -123.9166
3119.7188 | 123.8892 | -61.3632 | 62.2375 | -0.20729 | 0.012392 | 0.012559 | 0.0078336 | 0.061957 | 9.4068e-05 | 0.080758 | -58.3008 | 62.1323 | -61.6379 | -61.5234 | 54.3594 | 21.5149 | 6.6467 | 6.4087 | 62.2147 | -61.6562 | -0.27466 | -0.10529 | 3.0624 | -0.16022 | -7.8781 | -0.29297 | -0.022888 | 3.3371 | 68.0099 | 67.7719 | 115.7227 | 123.4955 | 3.0624 | 123.5779 | 82.8781 | -0.29297 | 123.4955 | 3.0624 | 82.8781 | 115.7227 | 123.5779 | -123.8754 | -123.8937
3120.7344 | 123.7656 | -61.4365 | 62.2375 | 0.04448 | 0.019015 | 0.015763 | 0.018301 | 0.064521 | 0.00052127 | 0.081399 | -58.3511 | 62.2421 | -61.7157 | -61.6379 | 54.1946 | 21.2723 | 6.8253 | 6.2256 | 62.233 | -61.7249 | -0.27924 | 0.004577 | 3.0853 | -0.20142 | -8.0429 | -0.28839 | -0.004578 | 3.3646 | 68.2617 | 67.662 | 115.6311 | 123.6786 | 3.0853 | 123.6694 | 82.7087 | -0.28839 | 123.6786 | 3.0853 | 82.7087 | 115.6311 | 123.6694 | -123.9532 | -123.9624
3121.7188 | 123.7839 | -61.4227 | 62.2375 | -0.19966 | 0.015597 | 0.012132 | 0.0082608 | 0.060675 | -0.0022559 | 0.081826 | -58.3649 | 62.2147 | -61.6974 | -61.6013 | 54.2633 | 21.3501 | 6.9214 | 6.2714 | 62.2879 | -61.6745 | -0.27466 | -0.022888 | 3.0579 | -0.17853 | -7.9742 | -0.25177 | 0.050354 | 3.3325 | 68.3441 | 67.6941 | 115.686 | 123.6374 | 3.0579 | 123.7106 | 82.7728 | -0.25177 | 123.6374 | 3.0579 | 82.7728 | 115.686 | 123.7106 | -123.9349 | -123.912
3122.7188 | 123.848 | -61.3861 | 62.2604 | -0.19966 | 0.015169 | 0.014482 | 0.0078336 | 0.063025 | -0.0016149 | 0.082467 | -58.3328 | 62.1689 | -61.6699 | -61.528 | 54.3365 | 21.3821 | 6.8665 | 6.395 | 62.2421 | -61.647 | -0.28381 | -0.091553 | 3.0533 | -0.14191 | -7.9239 | -0.26093 | -0.018311 | 3.3371 | 68.2526 | 67.7811 | 115.7227 | 123.555 | 3.0533 | 123.6282 | 82.7682 | -0.26093 | 123.555 | 3.0533 | 82.7682 | 115.7227 | 123.6282 | -123.9304 | -123.9075
3123.7344 | 123.761 | -61.4136 | 62.1964 | 0.04448 | 0.018801 | 0.017045 | 0.015951 | 0.062171 | 0.00052127 | 0.080117 | -58.3969 | 62.2559 | -61.7386 | -61.6745 | 54.158 | 21.2402 | 6.8253 | 6.189 | 62.2009 | -61.7386 | -0.32501 | 0.059509 | 3.0167 | -0.26093 | -8.0383 | -0.32501 | 0.004578 | 3.3417 | 68.2388 | 67.6025 | 115.5716 | 123.6694 | 3.0167 | 123.6145 | 82.6538 | -0.32501 | 123.6694 | 3.0167 | 82.6538 | 115.5716 | 123.6145 | -123.9349 | -123.9349
3124.7188 | 123.8068 | -61.3815 | 62.2604 | -0.19966 | 0.016024 | 0.016831 | 0.014669 | 0.063239 | -0.00033333 | 0.080972 | -58.3328 | 62.2742 | -61.6974 | -61.5921 | 54.2542 | 21.2128 | 6.9122 | 6.2439 | 62.2467 | -61.6882 | -0.31586 | 0.013733 | 3.0487 | -0.21057 | -8.0063 | -0.3067 | -0.013733 | 3.3646 | 68.2938 | 67.6254 | 115.6357 | 123.6557 | 3.0487 | 123.6282 | 82.5943 | -0.3067 | 123.6557 | 3.0487 | 82.5943 | 115.6357 | 123.6282 | -123.9578 | -123.9487
3125.7188 | 123.7976 | -61.4227 | 62.2559 | -0.19203 | 0.015597 | 0.017045 | 0.013815 | 0.065589 | 9.4068e-05 | 0.078622 | -58.3603 | 62.2604 | -61.6974 | -61.5875 | 54.2953 | 21.2128 | 6.9443 | 6.2988 | 62.265 | -61.6837 | -0.27466 | 0.004578 | 3.0624 | -0.1648 | -7.9605 | -0.26093 | 0.009156 | 3.3371 | 68.367 | 67.7216 | 115.7181 | 123.6832 | 3.0624 | 123.6877 | 82.6355 | -0.26093 | 123.6832 | 3.0624 | 82.6355 | 115.7181 | 123.6877 | -123.9532 | -123.9395
3126.7188 | 123.8388 | -61.409 | 62.233 | -0.24544 | 0.01816 | 0.017472 | 0.014669 | 0.063239 | -0.00011953 | 0.079904 | -58.2916 | 62.2604 | -61.6882 | -61.5555 | 54.3182 | 21.2311 | 6.8756 | 6.3217 | 62.2421 | -61.6653 | -0.27923 | 0.027466 | 3.1174 | -0.14648 | -7.9147 | -0.25635 | 0.009155 | 3.3966 | 68.2846 | 67.7307 | 115.7272 | 123.6694 | 3.1174 | 123.6511 | 82.6401 | -0.25635 | 123.6694 | 3.1174 | 82.6401 | 115.7272 | 123.6511 | -123.9212 | -123.8983
3127.7188 | 123.9029 | -61.3861 | 62.2192 | -0.19203 | 0.013888 | 0.0095682 | 0.0074062 | 0.063239 | -0.0024695 | 0.080972 | -58.0078 | 62.2009 | -61.6287 | -61.4685 | 54.3594 | 21.373 | 6.6742 | 6.3583 | 62.1964 | -61.6241 | -0.24262 | -0.01831 | 3.3783 | -0.082398 | -7.8598 | -0.23804 | -0.022888 | 3.6209 | 68.0603 | 67.7444 | 115.7455 | 123.587 | 3.3783 | 123.5825 | 82.7591 | -0.23804 | 123.587 | 3.3783 | 82.7591 | 115.7455 | 123.5825 | -123.848 | -123.8434
3128.7188 | 123.8388 | -61.3815 | 62.233 | -0.10811 | 0.01816 | 0.015977 | 0.015524 | 0.063452 | 0.00052127 | 0.080758 | -58.3145 | 62.2467 | -61.6562 | -61.5646 | 54.2496 | 21.1578 | 6.7841 | 6.2119 | 62.2055 | -61.6974 | -0.27466 | 0.013733 | 3.067 | -0.1831 | -7.9834 | -0.31586 | -0.027466 | 3.3417 | 68.1656 | 67.5934 | 115.6311 | 123.6282 | 3.067 | 123.587 | 82.5394 | -0.31586 | 123.6282 | 3.067 | 82.5394 | 115.6311 | 123.587 | -123.8892 | -123.9304
3129.7188 | 123.7701 | -61.409 | 62.2559 | -0.2607 | 0.017306 | 0.013413 | 0.0097562 | 0.061316 | -0.00033333 | 0.080331 | -58.342 | 62.1964 | -61.6837 | -61.5784 | 54.1901 | 21.2036 | 6.871 | 6.2119 | 62.2604 | -61.6516 | -0.27466 | -0.059509 | 3.067 | -0.16937 | -8.0658 | -0.24261 | 0.004578 | 3.3417 | 68.28 | 67.6209 | 115.5991 | 123.6053 | 3.067 | 123.6694 | 82.6126 | -0.24261 | 123.6053 | 3.067 | 82.6126 | 115.5991 | 123.6694 | -123.9395 | -123.9075
3130.7344 | 123.7564 | -61.4365 | 62.2604 | 0.067368 | 0.017733 | 0.017472 | 0.016806 | 0.061957 | -0.0016149 | 0.07969 | -58.3786 | 62.2559 | -61.6974 | -61.6653 | 54.1992 | 21.1029 | 6.8436 | 6.1432 | 62.233 | -61.7477 | -0.26093 | -0.004578 | 3.0579 | -0.22888 | -8.0612 | -0.31128 | -0.027466 | 3.3188 | 68.28 | 67.5797 | 115.6357 | 123.6923 | 3.0579 | 123.6694 | 82.5394 | -0.31128 | 123.6923 | 3.0579 | 82.5394 | 115.6357 | 123.6694 | -123.9578 | -124.0082
3131.7188 | 123.793 | -61.3861 | 62.2467 | -0.21492 | 0.013247 | 0.0095682 | 0.0093288 | 0.061957 | -0.00054693 | 0.081826 | -58.3054 | 62.1689 | -61.702 | -61.5417 | 54.2862 | 21.2631 | 6.839 | 6.3034 | 62.2238 | -61.6745 | -0.31586 | -0.07782 | 3.0807 | -0.15564 | -7.9605 | -0.28839 | -0.022888 | 3.3966 | 68.2251 | 67.6895 | 115.6723 | 123.555 | 3.0807 | 123.6099 | 82.6492 | -0.28839 | 123.555 | 3.0807 | 82.6492 | 115.6723 | 123.6099 | -123.9487 | -123.9212
3132.7188 | 123.8068 | -61.4182 | 62.2467 | -0.33699 | 0.014315 | 0.012132 | 0.0091152 | 0.060248 | -0.00097413 | 0.07969 | -58.3511 | 62.2009 | -61.7111 | -61.6287 | 54.2816 | 21.2082 | 6.8802 | 6.2256 | 62.2421 | -61.6653 | -0.29297 | -0.045776 | 3.067 | -0.21057 | -7.9651 | -0.24719 | -0.004578 | 3.36 | 68.2983 | 67.6437 | 115.6998 | 123.6191 | 3.067 | 123.6603 | 82.6263 | -0.24719 | 123.6191 | 3.067 | 82.6263 | 115.6998 | 123.6603 | -123.9578 | -123.912
3133.7188 | 123.8571 | -61.4365 | 62.2375 | -0.21492 | 0.017519 | 0.0132 | 0.017233 | 0.063452 | -0.0022559 | 0.081399 | -58.2642 | 62.2421 | -61.6837 | -61.5646 | 54.3549 | 21.2402 | 6.7749 | 6.2576 | 62.2375 | -61.6837 | -0.24719 | 0.004577 | 3.1723 | -0.12817 | -7.8827 | -0.24719 | 0 | 3.4195 | 68.2114 | 67.6941 | 115.7913 | 123.6786 | 3.1723 | 123.674 | 82.6767 | -0.24719 | 123.6786 | 3.1723 | 82.6767 | 115.7913 | 123.674 | -123.9212 | -123.9212
3134.7188 | 123.7839 | -61.4182 | 62.2559 | -0.20729 | 0.014956 | 0.014909 | 0.010824 | 0.061743 | 0.00094847 | 0.080117 | -58.3557 | 62.233 | -61.6837 | -61.3815 | 54.2725 | 21.0297 | 6.8756 | 6.2439 | 62.233 | -61.7065 | -0.2655 | -0.022888 | 3.0624 | 0.036621 | -7.9834 | -0.28839 | -0.022888 | 3.3279 | 68.2938 | 67.662 | 115.6906 | 123.6511 | 3.0624 | 123.6511 | 82.4478 | -0.28839 | 123.6511 | 3.0624 | 82.4478 | 115.6906 | 123.6511 | -123.9395 | -123.9624
3135.7188 | 123.7335 | -61.409 | 62.2925 | -0.21492 | 0.01581 | 0.015336 | 0.0099698 | 0.061743 | -0.0011877 | 0.079904 | -58.3374 | 62.2467 | -61.6837 | -61.5967 | 54.2999 | 21.1624 | 6.8527 | 6.2668 | 62.265 | -61.6653 | -0.27466 | -0.045776 | 3.0716 | -0.18768 | -7.9926 | -0.25635 | -0.027465 | 3.3463 | 68.2617 | 67.6758 | 115.7089 | 123.6557 | 3.0716 | 123.674 | 82.5714 | -0.25635 | 123.6557 | 3.0716 | 82.5714 | 115.7089 | 123.674 | -123.9761 | -123.9578
3136.7188 | 123.761 | -61.3907 | 62.2604 | -0.16151 | 0.016451 | 0.011918 | 0.011038 | 0.061316 | -0.0033239 | 0.081185 | -58.3878 | 62.2284 | -61.6837 | -61.6013 | 54.2313 | 21.1258 | 6.8573 | 6.2439 | 62.2421 | -61.6653 | -0.29297 | -0.032043 | 3.0029 | -0.21057 | -8.0292 | -0.27466 | -0.018311 | 3.2959 | 68.248 | 67.6346 | 115.6219 | 123.6191 | 3.0029 | 123.6328 | 82.5165 | -0.27466 | 123.6191 | 3.0029 | 82.5165 | 115.6219 | 123.6328 | -123.9441 | -123.9258
3137.7188 | 123.8068 | -61.4273 | 62.2696 | -0.26833 | 0.017092 | 0.010209 | 0.0091152 | 0.060248 | 0.0013757 | 0.081399 | -58.3557 | 62.1918 | -61.6837 | -61.6058 | 54.2953 | 21.2769 | 6.9077 | 6.2622 | 62.2467 | -61.6562 | -0.25635 | -0.07782 | 3.0716 | -0.17853 | -7.9742 | -0.22888 | -0.022888 | 3.3279 | 68.335 | 67.6895 | 115.7227 | 123.6191 | 3.0716 | 123.674 | 82.7042 | -0.22888 | 123.6191 | 3.0716 | 82.7042 | 115.7227 | 123.674 | -123.9532 | -123.9258
3138.7188 | 123.8068 | -61.4136 | 62.2559 | -0.22255 | 0.019656 | 0.017259 | 0.014883 | 0.061103 | 0.00052127 | 0.080331 | -58.3511 | 62.2375 | -61.6837 | -61.5829 | 54.2221 | 21.1716 | 6.926 | 6.2805 | 62.2467 | -61.7065 | -0.27008 | -0.01831 | 3.0624 | -0.16937 | -8.0338 | -0.29297 | -0.009155 | 3.3325 | 68.3395 | 67.6941 | 115.6357 | 123.6511 | 3.0624 | 123.6603 | 82.5851 | -0.29297 | 123.6511 | 3.0624 | 82.5851 | 115.6357 | 123.6603 | -123.9395 | -123.9624
3139.7188 | 123.9166 | -61.3815 | 62.2284 | 0.18944 | 0.01581 | 0.014268 | 0.0097562 | 0.065375 | 0.00094847 | 0.080972 | -58.2687 | 62.1323 | -61.6791 | -61.5097 | 54.3228 | 21.3364 | 6.6925 | 6.3126 | 62.1964 | -61.6287 | -0.29755 | -0.096131 | 3.1128 | -0.12817 | -7.9056 | -0.24719 | -0.032044 | 3.4103 | 68.074 | 67.6941 | 115.7043 | 123.5138 | 3.1128 | 123.5779 | 82.7179 | -0.24719 | 123.5138 | 3.1128 | 82.7179 | 115.7043 | 123.5779 | -123.9075 | -123.8571
3140.7188 | 123.8068 | -61.3998 | 62.233 | -0.20729 | 0.016665 | 0.015977 | 0.015951 | 0.061957 | 0.00073487 | 0.080758 | -58.3328 | 62.2467 | -61.6653 | -61.5601 | 54.1946 | 21.1258 | 6.8665 | 6.2347 | 62.2238 | -61.6928 | -0.2655 | 0.013733 | 3.067 | -0.16022 | -8.0383 | -0.29297 | -0.009155 | 3.3325 | 68.2663 | 67.6346 | 115.5945 | 123.6465 | 3.067 | 123.6237 | 82.5256 | -0.29297 | 123.6465 | 3.067 | 82.5256 | 115.5945 | 123.6237 | -123.8983 | -123.9258
3141.7188 | 123.9304 | -61.3541 | 62.2284 | -0.069961 | 0.014315 | 0.0099954 | 0.005911 | 0.060462 | 0.00052127 | 0.079904 | -58.3282 | 62.1323 | -61.6837 | -61.5143 | 54.3594 | 21.3593 | 6.6879 | 6.2759 | 62.1826 | -61.6379 | -0.32959 | -0.096131 | 3.0258 | -0.16022 | -7.869 | -0.28381 | -0.045777 | 3.3554 | 68.042 | 67.63 | 115.7135 | 123.4863 | 3.0258 | 123.5367 | 82.7133 | -0.28381 | 123.4863 | 3.0258 | 82.7133 | 115.7135 | 123.5367 | -123.912 | -123.8663
3142.7188 | 123.793 | -61.4136 | 62.2421 | -0.29121 | 0.016878 | 0.010423 | 0.012747 | 0.061103 | 0.00030767 | 0.079263 | -58.374 | 62.2284 | -61.6791 | -61.6013 | 54.3091 | 21.2219 | 6.8527 | 6.1844 | 62.2284 | -61.6837 | -0.2655 | -0.013732 | 3.0396 | -0.18768 | -7.933 | -0.27008 | -0.013732 | 3.3051 | 68.2663 | 67.598 | 115.7227 | 123.642 | 3.0396 | 123.642 | 82.6355 | -0.27008 | 123.642 | 3.0396 | 82.6355 | 115.7227 | 123.642 | -123.9212 | -123.9258
3143.7188 | 123.793 | -61.4273 | 62.2787 | -0.19966 | 0.019015 | 0.015763 | 0.01296 | 0.062171 | -0.00033333 | 0.080117 | -58.3511 | 62.233 | -61.6837 | -61.5921 | 54.2908 | 21.3318 | 6.8756 | 6.2439 | 62.2284 | -61.6974 | -0.25635 | -0.045777 | 3.0762 | -0.16479 | -7.988 | -0.27008 | -0.050354 | 3.3325 | 68.3029 | 67.6712 | 115.7181 | 123.6603 | 3.0762 | 123.6557 | 82.7591 | -0.27008 | 123.6603 | 3.0762 | 82.7591 | 115.7181 | 123.6557 | -123.9624 | -123.9761
3144.7188 | 123.848 | -61.3632 | 62.265 | -0.28358 | 0.014956 | 0.016404 | 0.0084744 | 0.060462 | -0.0022559 | 0.078195 | -58.3237 | 62.1643 | -61.6791 | -61.5372 | 54.3823 | 21.4416 | 6.8436 | 6.3583 | 62.2192 | -61.6425 | -0.31586 | -0.10071 | 3.0396 | -0.17395 | -7.8827 | -0.27924 | -0.045777 | 3.3554 | 68.2068 | 67.7216 | 115.7455 | 123.5275 | 3.0396 | 123.5825 | 82.8049 | -0.27924 | 123.5275 | 3.0396 | 82.8049 | 115.7455 | 123.5825 | -123.9441 | -123.9075
3145.7188 | 123.7518 | -61.4136 | 62.2604 | -0.45143 | 0.018587 | 0.012132 | 0.012747 | 0.062171 | 0.00052127 | 0.079263 | -58.3969 | 62.2192 | -61.7157 | -61.5829 | 54.245 | 21.3593 | 7.0084 | 6.3034 | 62.2559 | -61.702 | -0.30212 | -0.041199 | 3.0167 | -0.16937 | -8.0154 | -0.28839 | -0.004578 | 3.3188 | 68.4219 | 67.717 | 115.6586 | 123.6328 | 3.0167 | 123.6694 | 82.7728 | -0.28839 | 123.6328 | 3.0167 | 82.7728 | 115.6586 | 123.6694 | -123.9761 | -123.9624
3146.7188 | 123.7793 | -61.4182 | 62.2696 | -0.22255 | 0.016878 | 0.01085 | 0.01531 | 0.063025 | 0.00052127 | 0.079904 | -58.4976 | 62.2055 | -61.6699 | -61.647 | 54.245 | 21.4371 | 6.9077 | 6.2164 | 62.2467 | -61.6745 | -0.25177 | -0.064087 | 2.9205 | -0.22888 | -8.0246 | -0.25635 | -0.022888 | 3.1723 | 68.3258 | 67.6346 | 115.6631 | 123.6237 | 2.9205 | 123.6649 | 82.8552 | -0.25635 | 123.6237 | 2.9205 | 82.8552 | 115.6631 | 123.6649 | -123.9395 | -123.9441
3147.7188 | 123.9166 | -61.3632 | 62.2055 | -0.077591 | 0.01346 | 0.01555 | 0.0067654 | 0.061316 | -0.0016149 | 0.080972 | -58.342 | 62.1506 | -61.6791 | -61.5463 | 54.3274 | 21.492 | 6.752 | 6.3583 | 62.2009 | -61.6333 | -0.31586 | -0.054931 | 3.0212 | -0.18311 | -7.8781 | -0.27008 | -0.004577 | 3.3371 | 68.1152 | 67.7216 | 115.6906 | 123.5138 | 3.0212 | 123.5641 | 82.8552 | -0.27008 | 123.5138 | 3.0212 | 82.8552 | 115.6906 | 123.5641 | -123.8846 | -123.8388
3148.7188 | 123.8068 | -61.4044 | 62.2742 | -0.16151 | 0.014529 | 0.017045 | 0.015524 | 0.060889 | 9.4068e-05 | 0.080544 | -58.3878 | 62.2559 | -61.6745 | -61.5967 | 54.2862 | 21.3684 | 6.9122 | 6.2302 | 62.2375 | -61.702 | -0.27008 | -0.018311 | 3.0167 | -0.19226 | -7.988 | -0.29755 | -0.036621 | 3.2867 | 68.3166 | 67.6346 | 115.6906 | 123.6603 | 3.0167 | 123.642 | 82.7728 | -0.29755 | 123.6603 | 3.0167 | 82.7728 | 115.6906 | 123.642 | -123.9487 | -123.9761
3149.7188 | 123.9075 | -61.3495 | 62.1918 | -0.11574 | 0.014315 | 0.011491 | 0.006979 | 0.060248 | -0.00033333 | 0.080544 | -58.3328 | 62.1323 | -61.6791 | -61.496 | 54.3777 | 21.5378 | 6.7291 | 6.3904 | 62.1918 | -61.6241 | -0.32959 | -0.059509 | 3.0167 | -0.14648 | -7.814 | -0.27466 | 0 | 3.3463 | 68.0786 | 67.7399 | 115.7272 | 123.4818 | 3.0167 | 123.5413 | 82.8873 | -0.27466 | 123.4818 | 3.0167 | 82.8873 | 115.7272 | 123.5413 | -123.8708 | -123.8159
3150.7188 | 123.8251 | -61.4136 | 62.2742 | -0.19203 | 0.016878 | 0.017259 | 0.014029 | 0.062384 | 0.0022303 | 0.080972 | -58.3649 | 62.2375 | -61.702 | -61.5784 | 54.2633 | 21.4462 | 6.8939 | 6.2714 | 62.2421 | -61.6882 | -0.28839 | -0.036621 | 3.0487 | -0.1648 | -8.0109 | -0.27466 | -0.032044 | 3.3371 | 68.3075 | 67.6849 | 115.6769 | 123.6511 | 3.0487 | 123.6557 | 82.8598 | -0.27466 | 123.6511 | 3.0487 | 82.8598 | 115.6769 | 123.6557 | -123.9761 | -123.9624
3151.7188 | 123.8297 | -61.3815 | 62.2559 | -0.20729 | 0.017947 | 0.016831 | 0.013174 | 0.061316 | 0.00094847 | 0.081185 | -58.3282 | 62.178 | -61.6837 | -61.5646 | 54.3045 | 21.5012 | 6.8939 | 6.3721 | 62.233 | -61.6653 | -0.30212 | -0.077819 | 3.0533 | -0.1831 | -7.9514 | -0.28381 | -0.022888 | 3.3554 | 68.2755 | 67.7536 | 115.686 | 123.5596 | 3.0533 | 123.6145 | 82.8827 | -0.28381 | 123.5596 | 3.0533 | 82.8827 | 115.686 | 123.6145 | -123.9395 | -123.9212
3152.7188 | 123.9258 | -61.3449 | 62.2147 | -0.077591 | 0.013888 | 0.0089274 | 0.0095424 | 0.057898 | -0.0011877 | 0.080972 | -58.3191 | 62.1094 | -61.6745 | -61.5189 | 54.3869 | 21.6019 | 6.8069 | 6.5002 | 62.1735 | -61.6333 | -0.32959 | -0.10529 | 3.0258 | -0.17395 | -7.8278 | -0.28839 | -0.041199 | 3.3554 | 68.1519 | 67.8452 | 115.7318 | 123.4543 | 3.0258 | 123.5184 | 82.9468 | -0.28839 | 123.4543 | 3.0258 | 82.9468 | 115.7318 | 123.5184 | -123.8892 | -123.848
3153.7188 | 123.8022 | -61.3998 | 62.2604 | -0.069961 | 0.014742 | 0.013627 | 0.016165 | 0.060248 | 0.00030767 | 0.081613 | -58.3786 | 62.2467 | -61.7111 | -61.5692 | 54.2313 | 21.4645 | 7.0129 | 6.3217 | 62.2238 | -61.6791 | -0.31128 | -0.013733 | 3.0212 | -0.16937 | -8.0292 | -0.27924 | -0.036621 | 3.3325 | 68.4128 | 67.7216 | 115.6311 | 123.6465 | 3.0212 | 123.6237 | 82.8644 | -0.27924 | 123.6465 | 3.0212 | 82.8644 | 115.6311 | 123.6237 | -123.9716 | -123.9395
3154.7188 | 123.9029 | -61.3632 | 62.1872 | -0.12337 | 0.01282 | 0.012773 | 0.0095424 | 0.062171 | -0.0011877 | 0.078408 | -58.3191 | 62.1231 | -61.6837 | -61.5372 | 54.3503 | 21.6751 | 6.8344 | 6.4682 | 62.178 | -61.647 | -0.32044 | -0.064087 | 3.0441 | -0.17395 | -7.8369 | -0.28381 | -0.009155 | 3.3646 | 68.1976 | 67.8314 | 115.7135 | 123.4863 | 3.0441 | 123.5413 | 83.0383 | -0.28381 | 123.4863 | 3.0441 | 83.0383 | 115.7135 | 123.5413 | -123.8709 | -123.8342
3155.7188 | 123.7701 | -61.4182 | 62.2421 | -0.031814 | 0.017306 | 0.014054 | 0.019156 | 0.061316 | -0.0011877 | 0.078835 | -58.3466 | 62.1735 | -61.702 | -61.5784 | 54.245 | 21.6385 | 6.958 | 6.3538 | 62.2101 | -61.6974 | -0.28381 | -0.068664 | 3.0716 | -0.16022 | -7.9971 | -0.27924 | -0.032043 | 3.3554 | 68.3762 | 67.7719 | 115.6631 | 123.5916 | 3.0716 | 123.6282 | 83.0566 | -0.27924 | 123.5916 | 3.0716 | 83.0566 | 115.6631 | 123.6282 | -123.9441 | -123.9395
3156.7344 | 123.7976 | -61.4136 | 62.233 | -0.039444 | 0.016451 | 0.015122 | 0.017019 | 0.061316 | 0.0013757 | 0.079049 | -58.2779 | 62.2238 | -61.6745 | -61.5875 | 54.2358 | 21.6843 | 6.9809 | 6.3492 | 62.2147 | -61.6928 | -0.26093 | -0.009155 | 3.1357 | -0.17395 | -7.9971 | -0.27924 | -0.01831 | 3.3966 | 68.3945 | 67.7628 | 115.6494 | 123.6374 | 3.1357 | 123.6282 | 83.0978 | -0.27924 | 123.6374 | 3.1357 | 83.0978 | 115.6494 | 123.6282 | -123.9075 | -123.9258
3157.7188 | 123.88 | -61.3541 | 62.2009 | -0.024185 | 0.016451 | 0.014909 | 0.0074062 | 0.062812 | 0.00030767 | 0.081826 | -58.3786 | 62.1277 | -61.6837 | -61.5646 | 54.2496 | 21.666 | 6.8161 | 6.3629 | 62.178 | -61.6287 | -0.32959 | -0.073242 | 2.9755 | -0.21057 | -7.9514 | -0.27466 | -0.022888 | 3.3051 | 68.1702 | 67.717 | 115.6036 | 123.4818 | 2.9755 | 123.5321 | 83.02 | -0.27466 | 123.4818 | 2.9755 | 83.02 | 115.6036 | 123.5321 | -123.8846 | -123.8297
3158.7344 | 123.8617 | -61.409 | 62.2284 | -0.22255 | 0.018801 | 0.014054 | 0.016378 | 0.061103 | -0.00076053 | 0.081185 | -58.2825 | 62.2375 | -61.6837 | -61.5463 | 54.3045 | 21.7117 | 6.9397 | 6.3904 | 62.2147 | -61.7249 | -0.27466 | 0.009155 | 3.1265 | -0.13733 | -7.9239 | -0.31586 | -0.013733 | 3.4012 | 68.3487 | 67.7994 | 115.7135 | 123.6465 | 3.1265 | 123.6237 | 83.1207 | -0.31586 | 123.6465 | 3.1265 | 83.1207 | 115.7135 | 123.6237 | -123.912 | -123.9532
3159.7188 | 123.8846 | -61.3632 | 62.2238 | -0.13863 | 0.013033 | 0.01555 | 0.0076198 | 0.060462 | -0.0014013 | 0.08204 | -58.2962 | 62.1552 | -61.6653 | -61.5051 | 54.3045 | 21.698 | 6.8253 | 6.4316 | 62.2238 | -61.6058 | -0.30212 | -0.068665 | 3.067 | -0.14191 | -7.9193 | -0.24262 | 0 | 3.3691 | 68.1885 | 67.7948 | 115.6677 | 123.5184 | 3.067 | 123.587 | 83.0612 | -0.24262 | 123.5184 | 3.067 | 83.0612 | 115.6677 | 123.587 | -123.8892 | -123.8297
3160.7188 | 123.7976 | -61.4044 | 62.2375 | -0.10811 | 0.014742 | 0.016831 | 0.014883 | 0.063452 | -0.00033333 | 0.078622 | -58.3054 | 62.2009 | -61.7065 | -61.5738 | 54.2953 | 21.6293 | 6.9168 | 6.3583 | 62.2055 | -61.6882 | -0.30212 | -0.036621 | 3.0991 | -0.16937 | -7.9422 | -0.28381 | -0.032044 | 3.4012 | 68.3212 | 67.7628 | 115.6998 | 123.6053 | 3.0991 | 123.6099 | 83.0338 | -0.28381 | 123.6053 | 3.0991 | 83.0338 | 115.6998 | 123.6099 | -123.9441 | -123.9258
3161.7188 | 123.8617 | -61.377 | 62.1918 | -0.069961 | 0.011965 | 0.0099954 | 0.006979 | 0.060889 | 0.00073487 | 0.079263 | -58.2733 | 62.1414 | -61.6928 | -61.4868 | 54.1626 | 21.5836 | 6.7978 | 6.3263 | 62.178 | -61.6608 | -0.31586 | -0.050354 | 3.1036 | -0.10986 | -8.0292 | -0.28381 | -0.013732 | 3.4195 | 68.1747 | 67.7032 | 115.5396 | 123.5184 | 3.1036 | 123.555 | 82.9605 | -0.28381 | 123.5184 | 3.1036 | 82.9605 | 115.5396 | 123.555 | -123.8846 | -123.8525
3162.7188 | 123.8709 | -61.3907 | 62.2467 | -0.19203 | 0.013033 | 0.012132 | 0.010183 | 0.06153 | -0.00011953 | 0.081826 | -58.3054 | 62.1506 | -61.647 | -61.5189 | 54.3365 | 21.7941 | 6.9214 | 6.459 | 62.1826 | -61.6608 | -0.25635 | -0.09613 | 3.0853 | -0.12817 | -7.9102 | -0.27008 | -0.064087 | 3.3417 | 68.3121 | 67.8497 | 115.7272 | 123.5413 | 3.0853 | 123.5733 | 83.1848 | -0.27008 | 123.5413 | 3.0853 | 83.1848 | 115.7272 | 123.5733 | -123.8937 | -123.9075
3163.7188 | 123.793 | -61.3907 | 62.2559 | -0.24544 | 0.013247 | 0.012132 | 0.010611 | 0.060462 | -0.0022559 | 0.079904 | -58.3511 | 62.1552 | -61.6608 | -61.5829 | 54.245 | 21.7209 | 7.0679 | 6.4453 | 62.2192 | -61.6745 | -0.27008 | -0.10071 | 3.0396 | -0.19226 | -8.0109 | -0.28381 | -0.036621 | 3.3096 | 68.4586 | 67.836 | 115.6357 | 123.5458 | 3.0396 | 123.6099 | 83.1116 | -0.28381 | 123.5458 | 3.0396 | 83.1116 | 115.6357 | 123.6099 | -123.9166 | -123.9304
3164.7188 | 123.9258 | -61.3495 | 62.1964 | -0.16914 | 0.013033 | 0.014054 | 0.010397 | 0.059821 | -0.0011877 | 0.081185 | -58.3054 | 62.1094 | -61.6882 | -61.496 | 54.3777 | 21.8674 | 6.9031 | 6.5323 | 62.1964 | -61.615 | -0.33874 | -0.086975 | 3.0441 | -0.14648 | -7.8186 | -0.2655 | 0 | 3.3829 | 68.2526 | 67.8818 | 115.7272 | 123.4589 | 3.0441 | 123.5458 | 83.2169 | -0.2655 | 123.4589 | 3.0441 | 83.2169 | 115.7272 | 123.5458 | -123.8846 | -123.8113
3165.7188 | 123.8205 | -61.377 | 62.2101 | -0.047073 | 0.01581 | 0.017045 | 0.015951 | 0.060889 | -0.0011877 | 0.081826 | -58.3282 | 62.1964 | -61.702 | -61.5601 | 54.3045 | 21.7392 | 6.9626 | 6.3812 | 62.1872 | -61.6745 | -0.32501 | -0.013733 | 3.0487 | -0.18311 | -7.9056 | -0.29755 | -0.022888 | 3.3737 | 68.3395 | 67.7582 | 115.6815 | 123.5733 | 3.0487 | 123.5641 | 83.1162 | -0.29755 | 123.5733 | 3.0487 | 83.1162 | 115.6815 | 123.5641 | -123.912 | -123.8846
3166.7188 | 123.8846 | -61.3678 | 62.233 | 0.66246 | 0.014315 | 0.016404 | 0.0080472 | 0.061743 | -0.0026831 | 0.080117 | -58.2596 | 62.1094 | -61.6837 | -61.5143 | 54.3732 | 21.904 | 6.8298 | 6.427 | 62.1918 | -61.6287 | -0.31586 | -0.1236 | 3.1082 | -0.14648 | -7.8598 | -0.26093 | -0.041199 | 3.4241 | 68.1976 | 67.7948 | 115.741 | 123.4772 | 3.1082 | 123.5596 | 83.2718 | -0.26093 | 123.4772 | 3.1082 | 83.2718 | 115.741 | 123.5596 | -123.9166 | -123.8617
3167.7188 | 123.9258 | -61.3632 | 62.2192 | -0.12337 | 0.013888 | 0.014695 | 0.012747 | 0.059607 | -0.0020421 | 0.080331 | -58.2962 | 62.114 | -61.6608 | -61.5097 | 54.4144 | 21.8628 | 6.7795 | 6.4316 | 62.1597 | -61.6013 | -0.29755 | -0.10528 | 3.067 | -0.14648 | -7.8049 | -0.23804 | -0.059509 | 3.3646 | 68.1427 | 67.7948 | 115.7776 | 123.4772 | 3.067 | 123.5229 | 83.226 | -0.23804 | 123.4772 | 3.067 | 83.226 | 115.7776 | 123.5229 | -123.88 | -123.8205
3168.7188 | 123.8342 | -61.3632 | 62.2513 | -0.26833 | 0.016451 | 0.013413 | 0.013388 | 0.058325 | -0.00011953 | 0.081185 | -58.3099 | 62.1689 | -61.6516 | -61.528 | 54.3182 | 21.7392 | 6.8756 | 6.4178 | 62.1964 | -61.6699 | -0.28839 | -0.082398 | 3.0533 | -0.1648 | -7.933 | -0.3067 | -0.054932 | 3.3417 | 68.2388 | 67.7811 | 115.6815 | 123.5321 | 3.0533 | 123.5596 | 83.1024 | -0.3067 | 123.5321 | 3.0533 | 83.1024 | 115.6815 | 123.5596 | -123.9029 | -123.9212
3169.7188 | 123.8937 | -61.3724 | 62.2192 | -0.024185 | 0.014101 | 0.0132 | 0.0099698 | 0.05918 | 0.0015893 | 0.078622 | -58.3694 | 62.1368 | -61.6974 | -61.5509 | 54.3274 | 21.817 | 6.8069 | 6.4087 | 62.1735 | -61.6608 | -0.32501 | -0.082397 | 3.0029 | -0.17853 | -7.8918 | -0.28839 | -0.045776 | 3.3279 | 68.1793 | 67.7811 | 115.6998 | 123.5092 | 3.0029 | 123.5458 | 83.1894 | -0.28839 | 123.5092 | 3.0029 | 83.1894 | 115.6998 | 123.5458 | -123.9166 | -123.88
3170.7188 | 123.7427 | -61.441 | 62.2513 | 0.03685 | 0.016665 | 0.015336 | 0.017447 | 0.061316 | -0.0016149 | 0.080544 | -58.4244 | 62.1689 | -61.7203 | -61.6425 | 54.2313 | 21.5927 | 6.8939 | 6.1981 | 62.178 | -61.6928 | -0.27924 | -0.082398 | 3.0167 | -0.20142 | -8.02 | -0.25177 | -0.073242 | 3.2959 | 68.335 | 67.6392 | 115.6723 | 123.6099 | 3.0167 | 123.6191 | 83.0338 | -0.25177 | 123.6099 | 3.0167 | 83.0338 | 115.6723 | 123.6191 | -123.9716 | -123.9441
3171.7188 | 123.8709 | -61.3953 | 62.2284 | -0.0089264 | 0.014315 | 0.01555 | 0.0061246 | 0.060248 | -0.00097413 | 0.080544 | -58.4061 | 62.1323 | -61.6699 | -61.5646 | 54.3503 | 21.7667 | 6.839 | 6.3766 | 62.1552 | -61.6608 | -0.27466 | -0.096131 | 2.9892 | -0.16937 | -7.8781 | -0.2655 | -0.073243 | 3.2639 | 68.2343 | 67.7719 | 115.7455 | 123.5275 | 2.9892 | 123.5504 | 83.1619 | -0.2655 | 123.5275 | 2.9892 | 83.1619 | 115.7455 | 123.5504 | -123.8983 | -123.8892
3172.7344 | 123.7701 | -61.4182 | 62.2284 | 0.090256 | 0.017733 | 0.016831 | 0.019369 | 0.061316 | 0.00052127 | 0.079263 | -58.3603 | 62.2284 | -61.6745 | -61.6241 | 54.2862 | 21.6751 | 6.8848 | 6.221 | 62.2009 | -61.7203 | -0.25635 | 0 | 3.0579 | -0.20599 | -7.9422 | -0.30212 | -0.027466 | 3.3142 | 68.3029 | 67.6392 | 115.7043 | 123.6465 | 3.0579 | 123.6191 | 83.0933 | -0.30212 | 123.6465 | 3.0579 | 83.0933 | 115.7043 | 123.6191 | -123.9029 | -123.9487
3173.7188 | 123.7976 | -61.409 | 62.2513 | -0.23018 | 0.014742 | 0.014054 | 0.010183 | 0.060675 | -0.0011877 | 0.080331 | -58.3466 | 62.1826 | -61.6928 | -61.5646 | 54.3411 | 21.7026 | 6.9305 | 6.3126 | 62.2375 | -61.6653 | -0.28381 | -0.068665 | 3.0624 | -0.15564 | -7.9102 | -0.25635 | -0.013733 | 3.3463 | 68.3395 | 67.7216 | 115.7501 | 123.5916 | 3.0624 | 123.6465 | 83.1116 | -0.25635 | 123.5916 | 3.0624 | 83.1116 | 115.7501 | 123.6465 | -123.9441 | -123.9166
3174.7188 | 123.8937 | -61.3449 | 62.2147 | -0.131 | 0.015383 | 0.011277 | 0.011251 | 0.060248 | -0.00097413 | 0.079476 | -58.3282 | 62.1414 | -61.6562 | -61.5143 | 54.3503 | 21.7484 | 6.8848 | 6.4316 | 62.1918 | -61.6287 | -0.31128 | -0.073243 | 3.0167 | -0.16937 | -7.8644 | -0.28381 | -0.022889 | 3.3279 | 68.2297 | 67.7765 | 115.6952 | 123.4863 | 3.0167 | 123.5367 | 83.0933 | -0.28381 | 123.4863 | 3.0167 | 83.0933 | 115.6952 | 123.5367 | -123.8708 | -123.8434
3175.7188 | 123.8205 | -61.4365 | 62.233 | 0.16655 | 0.015169 | 0.017259 | 0.015524 | 0.062171 | -0.0014013 | 0.081399 | -58.3923 | 62.1506 | -61.7477 | -61.6287 | 54.3182 | 21.6248 | 6.8115 | 6.2302 | 62.178 | -61.6653 | -0.31128 | -0.082397 | 3.0441 | -0.19226 | -7.9147 | -0.22888 | -0.054931 | 3.3554 | 68.248 | 67.6666 | 115.7547 | 123.587 | 3.0441 | 123.6145 | 83.0612 | -0.22888 | 123.587 | 3.0441 | 83.0612 | 115.7547 | 123.6145 | -123.9807 | -123.8983
3176.7188 | 123.8892 | -61.3586 | 62.1918 | -0.08522 | 0.012606 | 0.0132 | 0.0097562 | 0.060248 | 0.0026575 | 0.080758 | -58.342 | 62.1277 | -61.6653 | -61.5326 | 54.4281 | 21.7804 | 6.8253 | 6.395 | 62.1689 | -61.6562 | -0.3067 | -0.064086 | 3.0167 | -0.17395 | -7.7637 | -0.29755 | -0.022888 | 3.3234 | 68.1839 | 67.7536 | 115.7867 | 123.4863 | 3.0167 | 123.5275 | 83.139 | -0.29755 | 123.4863 | 3.0167 | 83.139 | 115.7867 | 123.5275 | -123.8571 | -123.848
3177.7344 | 123.8251 | -61.3998 | 62.2375 | -0.054703 | 0.016024 | 0.011064 | 0.016378 | 0.061743 | -0.0014013 | 0.079263 | -58.6761 | 62.2375 | -61.6745 | -61.5417 | 54.277 | 21.7529 | 6.8985 | 6.3354 | 62.2147 | -61.7111 | -0.27466 | 0 | 2.7237 | -0.14191 | -7.9605 | -0.31128 | -0.022888 | 2.9984 | 68.2983 | 67.7353 | 115.6769 | 123.6374 | 2.7237 | 123.6145 | 83.1528 | -0.31128 | 123.6374 | 2.7237 | 83.1528 | 115.6769 | 123.6145 | -123.912 | -123.9487
3178.7344 | 123.8388 | -61.4044 | 62.2238 | -0.039444 | 0.016451 | 0.013627 | 0.015951 | 0.066443 | -0.0018285 | 0.080972 | -58.3145 | 62.2101 | -61.702 | -61.5509 | 54.2313 | 21.7026 | 6.8893 | 6.2668 | 62.2009 | -61.6699 | -0.29755 | -0.013733 | 3.0899 | -0.14648 | -7.9926 | -0.2655 | -0.022888 | 3.3875 | 68.2938 | 67.6712 | 115.6357 | 123.6145 | 3.0899 | 123.6053 | 83.107 | -0.2655 | 123.6145 | 3.0899 | 83.107 | 115.6357 | 123.6053 | -123.9258 | -123.8937
3179.7188 | 123.8846 | -61.377 | 62.2101 | -0.42091 | 0.015597 | 0.012559 | 0.0082608 | 0.061743 | 0.00073487 | 0.081826 | -58.3099 | 62.1231 | -61.6516 | -61.496 | 54.4144 | 21.8491 | 6.8436 | 6.3812 | 62.2055 | -61.6379 | -0.27466 | -0.086975 | 3.067 | -0.11902 | -7.7957 | -0.26093 | -0.004578 | 3.3417 | 68.2205 | 67.7582 | 115.7913 | 123.5001 | 3.067 | 123.5825 | 83.226 | -0.26093 | 123.5001 | 3.067 | 83.226 | 115.7913 | 123.5825 | -123.8617 | -123.848
3180.7188 | 123.8113 | -61.4319 | 62.1872 | 0.090256 | 0.013888 | 0.017045 | 0.016165 | 0.063239 | -0.00054693 | 0.080758 | -58.4244 | 62.1826 | -61.7432 | -61.6791 | 54.158 | 21.6064 | 6.9351 | 6.1935 | 62.2101 | -61.6882 | -0.31128 | -0.004578 | 3.0075 | -0.24719 | -8.0292 | -0.25635 | 0.022888 | 3.3188 | 68.367 | 67.6254 | 115.5899 | 123.6145 | 3.0075 | 123.642 | 83.0383 | -0.25635 | 123.6145 | 3.0075 | 83.0383 | 115.5899 | 123.642 | -123.9304 | -123.8754
3181.7188 | 123.9075 | -61.3495 | 62.2055 | -0.11574 | 0.014529 | 0.010636 | 0.0084744 | 0.060889 | 0.00030767 | 0.080758 | -58.3191 | 62.1277 | -61.6653 | -61.5005 | 54.3549 | 21.7987 | 6.8069 | 6.395 | 62.1643 | -61.6196 | -0.31586 | -0.077819 | 3.0304 | -0.15106 | -7.8506 | -0.27008 | -0.041198 | 3.3463 | 68.1564 | 67.7444 | 115.7043 | 123.4772 | 3.0304 | 123.5138 | 83.1482 | -0.27008 | 123.4772 | 3.0304 | 83.1482 | 115.7043 | 123.5138 | -123.8708 | -123.8251
3182.7344 | 123.8068 | -61.3953 | 62.2375 | -0.21492 | 0.016451 | 0.01555 | 0.015738 | 0.061743 | 9.4068e-05 | 0.077767 | -58.3191 | 62.2284 | -61.6745 | -61.5646 | 54.2816 | 21.6751 | 6.9351 | 6.2256 | 62.2284 | -61.6882 | -0.27924 | -0.009155 | 3.0762 | -0.16937 | -7.9559 | -0.29297 | -0.009155 | 3.3554 | 68.3304 | 67.6208 | 115.6769 | 123.6237 | 3.0762 | 123.6237 | 83.0704 | -0.29297 | 123.6237 | 3.0762 | 83.0704 | 115.6769 | 123.6237 | -123.912 | -123.9258
3183.7188 | 123.8709 | -61.3678 | 62.2421 | -0.21492 | 0.015383 | 0.013413 | 0.0089016 | 0.062598 | -0.0011877 | 0.083535 | -58.3145 | 62.1643 | -61.6425 | -61.528 | 54.2999 | 21.7255 | 6.9031 | 6.3583 | 62.2192 | -61.647 | -0.27466 | -0.077819 | 3.0533 | -0.16022 | -7.9422 | -0.27924 | -0.022888 | 3.3279 | 68.2709 | 67.7261 | 115.6677 | 123.5321 | 3.0533 | 123.587 | 83.0933 | -0.27924 | 123.5321 | 3.0533 | 83.0933 | 115.6677 | 123.587 | -123.8846 | -123.8892
3184.7188 | 123.8617 | -61.3861 | 62.2513 | -0.21492 | 0.01581 | 0.011918 | 0.011892 | 0.061316 | 0.00094847 | 0.080758 | -58.3099 | 62.1506 | -61.6882 | -61.5189 | 54.3274 | 21.7896 | 6.8619 | 6.2622 | 62.2147 | -61.6196 | -0.30212 | -0.10071 | 3.0762 | -0.13275 | -7.9239 | -0.23346 | -0.036621 | 3.3783 | 68.248 | 67.6483 | 115.7135 | 123.5367 | 3.0762 | 123.6008 | 83.1757 | -0.23346 | 123.5367 | 3.0762 | 83.1757 | 115.7135 | 123.6008 | -123.9395 | -123.8709
3185.7188 | 123.8617 | -61.3678 | 62.2375 | -0.16151 | 0.016024 | 0.015336 | 0.0097562 | 0.060675 | 0.00052127 | 0.080758 | -58.3282 | 62.1552 | -61.6608 | -61.5097 | 54.3045 | 21.7392 | 6.8069 | 6.2805 | 62.2009 | -61.647 | -0.29297 | -0.082398 | 3.0396 | -0.14191 | -7.933 | -0.27924 | -0.036621 | 3.3325 | 68.1747 | 67.6483 | 115.6723 | 123.5229 | 3.0396 | 123.5687 | 83.107 | -0.27924 | 123.5229 | 3.0396 | 83.107 | 115.6723 | 123.5687 | -123.8983 | -123.8846
3186.7188 | 123.7747 | -61.4182 | 62.2787 | -0.28358 | 0.013247 | 0.0078592 | 0.013388 | 0.05918 | -0.0048193 | 0.079476 | -58.3649 | 62.1964 | -61.6974 | -61.5829 | 54.3457 | 21.7117 | 6.9626 | 6.2256 | 62.2101 | -61.6562 | -0.27924 | -0.082398 | 3.0533 | -0.16479 | -7.933 | -0.23804 | -0.068665 | 3.3325 | 68.3807 | 67.6437 | 115.7639 | 123.6145 | 3.0533 | 123.6282 | 83.1299 | -0.23804 | 123.6145 | 3.0533 | 83.1299 | 115.7639 | 123.6282 | -123.9761 | -123.9349
3187.7188 | 123.7793 | -61.4456 | 62.2238 | 2.2265 | 0.015169 | 0.01085 | 0.014669 | 0.06153 | -0.00097413 | 0.080972 | -58.1497 | 62.1826 | -61.7157 | -61.6196 | 54.1718 | 21.5057 | 6.8802 | 6.0928 | 62.2192 | -61.7157 | -0.27008 | -0.041199 | 3.2959 | -0.17395 | -8.0521 | -0.27008 | -0.004578 | 3.566 | 68.3258 | 67.5385 | 115.6174 | 123.6282 | 3.2959 | 123.6649 | 82.9514 | -0.27008 | 123.6282 | 3.2959 | 82.9514 | 115.6174 | 123.6649 | -123.9395 | -123.9395
3188.7188 | 123.7839 | -61.4044 | 62.2192 | -0.054703 | 0.017519 | 0.020036 | 0.01766 | 0.064948 | -0.00054693 | 0.080117 | -58.3328 | 62.1872 | -61.6837 | -61.5829 | 54.2404 | 21.5698 | 6.8985 | 6.189 | 62.2192 | -61.7111 | -0.27924 | -0.032043 | 3.0716 | -0.17853 | -7.9788 | -0.3067 | 0 | 3.3508 | 68.3029 | 67.5934 | 115.6448 | 123.5916 | 3.0716 | 123.6237 | 82.9742 | -0.3067 | 123.5916 | 3.0716 | 82.9742 | 115.6448 | 123.6237 | -123.9029 | -123.9304
3189.7188 | 123.9578 | -61.3861 | 62.1872 | -0.17677 | 0.014315 | 0.01085 | 0.0061246 | 0.061103 | -0.00011953 | 0.082467 | -58.2825 | 62.1506 | -61.6745 | -61.5051 | 54.3823 | 21.7255 | 7.2556 | 6.3812 | 62.2559 | -61.5875 | -0.28839 | -0.036621 | 3.1036 | -0.11902 | -7.8049 | -0.20142 | 0.068664 | 3.392 | 68.6417 | 67.7673 | 115.7684 | 123.5367 | 3.1036 | 123.642 | 83.1116 | -0.20142 | 123.5367 | 3.1036 | 83.1116 | 115.7684 | 123.642 | -123.8617 | -123.7747
3190.7188 | 123.8251 | -61.3998 | 62.2467 | -0.1844 | 0.016024 | 0.013627 | 0.014883 | 0.064521 | -0.0031103 | 0.081399 | -58.3832 | 62.1872 | -61.7111 | -61.5967 | 54.2908 | 21.6888 | 6.9901 | 6.2942 | 62.265 | -61.6653 | -0.31128 | -0.059509 | 3.0167 | -0.19684 | -7.9559 | -0.2655 | 0.018311 | 3.3279 | 68.3899 | 67.6941 | 115.6906 | 123.587 | 3.0167 | 123.6649 | 83.0887 | -0.2655 | 123.587 | 3.0167 | 83.0887 | 115.6906 | 123.6649 | -123.9578 | -123.912
3191.7188 | 123.88 | -61.3815 | 62.233 | -0.13863 | 0.01346 | 0.011277 | 0.0082608 | 0.060248 | -0.0014013 | 0.079904 | -58.3145 | 62.1368 | -61.6608 | -61.5234 | 54.3869 | 21.785 | 6.8527 | 6.3675 | 62.2238 | -61.6287 | -0.27924 | -0.09613 | 3.067 | -0.14191 | -7.8461 | -0.24719 | -0.009155 | 3.3463 | 68.2343 | 67.749 | 115.7684 | 123.5184 | 3.067 | 123.6053 | 83.1665 | -0.24719 | 123.5184 | 3.067 | 83.1665 | 115.7684 | 123.6053 | -123.8937 | -123.8617
3192.7188 | 123.7701 | -61.409 | 62.2742 | -0.19966 | 0.01346 | 0.013841 | 0.01296 | 0.060675 | -0.0011877 | 0.080972 | -58.342 | 62.1735 | -61.6791 | -61.5555 | 54.3137 | 21.8216 | 7.0175 | 6.2805 | 62.2238 | -61.6699 | -0.27008 | -0.10071 | 3.067 | -0.14648 | -7.9605 | -0.26093 | -0.050354 | 3.3371 | 68.4265 | 67.6895 | 115.7227 | 123.5825 | 3.067 | 123.6328 | 83.2306 | -0.26093 | 123.5825 | 3.067 | 83.2306 | 115.7227 | 123.6328 | -123.9532 | -123.9441
3193.7344 | 123.761 | -61.4182 | 62.2284 | 0.052109 | 0.018587 | 0.015336 | 0.01766 | 0.064307 | -0.0011877 | 0.080117 | -58.3923 | 62.2421 | -61.702 | -61.6699 | 54.1534 | 21.73 | 6.9626 | 6.221 | 62.2101 | -61.7294 | -0.28381 | 0.013732 | 3.0258 | -0.25177 | -8.075 | -0.31128 | -0.018311 | 3.3096 | 68.3807 | 67.6392 | 115.5716 | 123.6603 | 3.0258 | 123.6282 | 83.1482 | -0.31128 | 123.6603 | 3.0258 | 83.1482 | 115.5716 | 123.6282 | -123.9304 | -123.9578
3194.7188 | 123.7701 | -61.4044 | 62.2559 | -0.2607 | 0.015383 | 0.011491 | 0.012533 | 0.060462 | -0.0022559 | 0.080972 | -58.4061 | 62.1918 | -61.702 | -61.6058 | 54.2679 | 21.7621 | 7.0816 | 6.3675 | 62.2513 | -61.6608 | -0.29755 | -0.064087 | 2.9984 | -0.20142 | -7.988 | -0.25635 | -0.004577 | 3.2959 | 68.486 | 67.7719 | 115.6723 | 123.5962 | 2.9984 | 123.6557 | 83.1665 | -0.25635 | 123.5962 | 2.9984 | 83.1665 | 115.6723 | 123.6557 | -123.9578 | -123.9166
3195.7188 | 123.7656 | -61.4319 | 62.2467 | 0.059738 | 0.014742 | 0.014268 | 0.013174 | 0.064093 | -0.00011953 | 0.07969 | -58.3694 | 62.2009 | -61.7157 | -61.6058 | 54.2862 | 21.7484 | 7.1091 | 6.308 | 62.2513 | -61.6882 | -0.28381 | -0.045776 | 3.0624 | -0.17395 | -7.9605 | -0.25635 | 0.004578 | 3.3463 | 68.541 | 67.7399 | 115.7181 | 123.6328 | 3.0624 | 123.6832 | 83.1802 | -0.25635 | 123.6328 | 3.0624 | 83.1802 | 115.7181 | 123.6832 | -123.9624 | -123.9349
3196.7188 | 123.8342 | -61.3815 | 62.2284 | -0.22255 | 0.016024 | 0.014909 | 0.0097562 | 0.061743 | 0.00094847 | 0.078835 | -58.3145 | 62.1643 | -61.6608 | -61.5417 | 54.3411 | 21.817 | 6.958 | 6.3675 | 62.2375 | -61.6516 | -0.27924 | -0.064087 | 3.067 | -0.16022 | -7.8873 | -0.27008 | 0.009155 | 3.3463 | 68.3395 | 67.749 | 115.7227 | 123.5458 | 3.067 | 123.6191 | 83.1985 | -0.27008 | 123.5458 | 3.067 | 83.1985 | 115.7227 | 123.6191 | -123.8892 | -123.88
3197.7188 | 123.8342 | -61.3907 | 62.2513 | -0.22255 | 0.016238 | 0.016404 | 0.0093288 | 0.060034 | 0.0011621 | 0.080544 | -58.3191 | 62.1643 | -61.6699 | -61.5463 | 54.3045 | 21.8216 | 7.0038 | 6.3675 | 62.1964 | -61.6653 | -0.27924 | -0.086975 | 3.0716 | -0.15564 | -7.9468 | -0.27466 | -0.054932 | 3.3508 | 68.3945 | 67.7582 | 115.6952 | 123.555 | 3.0716 | 123.587 | 83.2123 | -0.27466 | 123.555 | 3.0716 | 83.2123 | 115.6952 | 123.587 | -123.9212 | -123.9166
3198.7188 | 123.8068 | -61.4227 | 62.2467 | -0.19966 | 0.016665 | 0.015122 | 0.015097 | 0.061316 | -0.0016149 | 0.079049 | -58.3603 | 62.2192 | -61.702 | -61.6013 | 54.1946 | 21.8124 | 7.0496 | 6.308 | 62.233 | -61.6745 | -0.27924 | -0.027466 | 3.0624 | -0.17853 | -8.0521 | -0.25177 | -0.013733 | 3.3417 | 68.4723 | 67.7307 | 115.6174 | 123.642 | 3.0624 | 123.6557 | 83.2352 | -0.25177 | 123.642 | 3.0624 | 83.2352 | 115.6174 | 123.6557 | -123.9487 | -123.9212
3199.7188 | 123.7839 | -61.4182 | 62.2421 | -0.24544 | 0.014529 | 0.017899 | 0.010824 | 0.059821 | -0.00011953 | 0.078835 | -58.3832 | 62.2238 | -61.6745 | -61.3998 | 54.451 | 21.7117 | 6.9946 | 6.2988 | 62.2467 | -61.6974 | -0.25635 | -0.01831 | 3.035 | 0.018311 | -7.7911 | -0.27924 | 0.004578 | 3.2913 | 68.4128 | 67.717 | 115.8691 | 123.642 | 3.035 | 123.6649 | 83.1299 | -0.27924 | 123.642 | 3.035 | 83.1299 | 115.8691 | 123.6649 | -123.9166 | -123.9395
3200.7188 | 123.7885 | -61.3998 | 62.2513 | -0.131 | 0.016878 | 0.012345 | 0.013815 | 0.063025 | -0.00097413 | 0.081613 | -58.3969 | 62.2284 | -61.6928 | -61.5921 | 54.2358 | 21.8033 | 7.0312 | 6.2897 | 62.2238 | -61.6974 | -0.29297 | -0.022888 | 3.0029 | -0.19226 | -8.0154 | -0.29755 | -0.027466 | 3.2959 | 68.4311 | 67.6895 | 115.6357 | 123.6282 | 3.0029 | 123.6237 | 83.2031 | -0.29755 | 123.6282 | 3.0029 | 83.2031 | 115.6357 | 123.6237 | -123.9441 | -123.9487
3201.7188 | 123.7885 | -61.4136 | 62.2238 | 1.4483 | 0.015597 | 0.013413 | 0.013174 | 0.061103 | -0.00033333 | 0.081185 | -58.4381 | 62.2192 | -61.702 | -61.6196 | 54.2633 | 21.8262 | 7.0633 | 6.3034 | 62.2604 | -61.6745 | -0.28839 | -0.004578 | 2.9755 | -0.20599 | -7.9605 | -0.26093 | 0.036621 | 3.2639 | 68.4769 | 67.717 | 115.6769 | 123.6328 | 2.9755 | 123.674 | 83.2397 | -0.26093 | 123.6328 | 2.9755 | 83.2397 | 115.6769 | 123.674 | -123.9258 | -123.8983
3202.7188 | 123.7976 | -61.4227 | 62.2604 | -0.30647 | 0.016665 | 0.0132 | 0.010397 | 0.064521 | 0.00073487 | 0.079904 | -58.374 | 62.2421 | -61.6928 | -61.6104 | 54.2038 | 21.7804 | 7.0404 | 6.2714 | 62.2604 | -61.6837 | -0.27008 | -0.018311 | 3.0487 | -0.18768 | -8.0566 | -0.26093 | 0 | 3.3188 | 68.4631 | 67.6941 | 115.6265 | 123.6649 | 3.0487 | 123.6832 | 83.2031 | -0.26093 | 123.6649 | 3.0487 | 83.2031 | 115.6265 | 123.6832 | -123.9532 | -123.9441
3203.7188 | 123.7839 | -61.441 | 62.2055 | -0.0012969 | 0.018374 | 0.021104 | 0.014883 | 0.065375 | -0.0011877 | 0.078835 | -58.3374 | 62.2421 | -61.6974 | -61.5784 | 54.2175 | 22.0825 | 7.0084 | 6.3217 | 62.2192 | -61.734 | -0.25635 | 0.036621 | 3.1036 | -0.13733 | -7.988 | -0.29297 | 0.013733 | 3.36 | 68.4494 | 67.7628 | 115.6586 | 123.6832 | 3.1036 | 123.6603 | 83.5236 | -0.29297 | 123.6832 | 3.1036 | 83.5236 | 115.6586 | 123.6603 | -123.9029 | -123.9395
3204.7188 | 123.7885 | -61.4182 | 62.2421 | -0.17677 | 0.016238 | 0.018754 | 0.01232 | 0.064521 | -0.00076053 | 0.079049 | -58.3694 | 62.2055 | -61.7249 | -61.5921 | 54.2679 | 21.9955 | 7.0862 | 6.34 | 62.2467 | -61.6974 | -0.3067 | -0.036621 | 3.0487 | -0.17395 | -7.9742 | -0.27924 | 0.004578 | 3.3554 | 68.5043 | 67.7582 | 115.686 | 123.6237 | 3.0487 | 123.6649 | 83.4137 | -0.27924 | 123.6237 | 3.0487 | 83.4137 | 115.686 | 123.6649 | -123.967 | -123.9395
3205.7188 | 123.8388 | -61.409 | 62.2467 | -0.20729 | 0.015383 | 0.012986 | 0.01531 | 0.063666 | -0.0011877 | 0.079476 | -58.3832 | 62.233 | -61.6974 | -61.5646 | 54.2542 | 21.9635 | 7.0175 | 6.3126 | 62.2421 | -61.6882 | -0.28839 | -0.013733 | 3.0258 | -0.15564 | -7.9926 | -0.27923 | -0.004578 | 3.3142 | 68.4265 | 67.7216 | 115.6631 | 123.642 | 3.0258 | 123.6511 | 83.3725 | -0.27923 | 123.642 | 3.0258 | 83.3725 | 115.6631 | 123.6511 | -123.9441 | -123.9349
3206.7188 | 123.8342 | -61.4182 | 62.2147 | -0.062332 | 0.017092 | 0.015122 | 0.017019 | 0.064307 | -0.00097413 | 0.07969 | -58.3191 | 62.233 | -61.7111 | -61.5829 | 54.2725 | 21.904 | 7.0084 | 6.3126 | 62.2284 | -61.6974 | -0.29297 | 0.01831 | 3.0991 | -0.16479 | -7.9422 | -0.27924 | 0.013733 | 3.392 | 68.4265 | 67.7307 | 115.6906 | 123.6511 | 3.0991 | 123.6465 | 83.3221 | -0.27924 | 123.6511 | 3.0991 | 83.3221 | 115.6906 | 123.6465 | -123.9258 | -123.912
3207.7188 | 123.8297 | -61.4044 | 62.2147 | -0.12337 | 0.019015 | 0.021104 | 0.015097 | 0.06388 | -0.0014013 | 0.07969 | -58.3099 | 62.233 | -61.702 | -61.5875 | 54.2862 | 21.9315 | 6.9809 | 6.3126 | 62.2421 | -61.7111 | -0.29755 | 0.01831 | 3.0945 | -0.18311 | -7.9285 | -0.3067 | 0.027465 | 3.392 | 68.3853 | 67.717 | 115.6906 | 123.6374 | 3.0945 | 123.6465 | 83.3359 | -0.3067 | 123.6374 | 3.0945 | 83.3359 | 115.6906 | 123.6465 | -123.9166 | -123.9258
3208.7188 | 123.7427 | -61.4319 | 62.2238 | 0.15129 | 0.018374 | 0.014909 | 0.013388 | 0.064521 | -0.00011953 | 0.080972 | -58.4518 | 62.233 | -61.6974 | -61.6562 | 54.0665 | 21.936 | 6.9809 | 6.1157 | 62.2147 | -61.7386 | -0.2655 | 0.009155 | 2.98 | -0.2243 | -8.1573 | -0.3067 | -0.009155 | 3.2455 | 68.4128 | 67.5476 | 115.4984 | 123.6649 | 2.98 | 123.6465 | 83.3679 | -0.3067 | 123.6649 | 2.98 | 83.3679 | 115.4984 | 123.6465 | -123.9212 | -123.9624
3209.7188 | 123.8205 | -61.4136 | 62.233 | -0.17677 | 0.017306 | 0.018754 | 0.014883 | 0.064521 | -0.00054693 | 0.080331 | -58.3603 | 62.2375 | -61.6882 | -61.5555 | 54.277 | 21.9406 | 6.958 | 6.2714 | 62.2375 | -61.6928 | -0.27466 | 0.004578 | 3.0533 | -0.14191 | -7.9559 | -0.27924 | 0.004578 | 3.3279 | 68.3716 | 67.6849 | 115.6906 | 123.6511 | 3.0533 | 123.6511 | 83.3542 | -0.27924 | 123.6511 | 3.0533 | 83.3542 | 115.6906 | 123.6511 | -123.9212 | -123.9258
3210.7188 | 123.8525 | -61.4273 | 62.2055 | 0.18944 | 0.018587 | 0.020463 | 0.01296 | 0.065589 | 9.4068e-05 | 0.080331 | -58.4244 | 62.2238 | -61.7157 | -61.6196 | 54.1855 | 21.9498 | 6.8619 | 6.2256 | 62.2055 | -61.7111 | -0.28839 | 0.018311 | 3.0029 | -0.19226 | -8.02 | -0.28381 | 0 | 3.2913 | 68.2892 | 67.6529 | 115.6128 | 123.6511 | 3.0029 | 123.6328 | 83.3771 | -0.28381 | 123.6511 | 3.0029 | 83.3771 | 115.6128 | 123.6328 | -123.9212 | -123.9166
3211.7188 | 123.7976 | -61.4227 | 62.2055 | -0.0089264 | 0.016878 | 0.020036 | 0.01531 | 0.064307 | 0.00094847 | 0.081613 | -58.3786 | 62.2513 | -61.7065 | -61.6241 | 54.1489 | 21.991 | 6.9534 | 6.2027 | 62.2147 | -61.7294 | -0.28381 | 0.045777 | 3.0441 | -0.20142 | -8.0566 | -0.3067 | 0.009156 | 3.3279 | 68.3762 | 67.6254 | 115.5716 | 123.674 | 3.0441 | 123.6374 | 83.4137 | -0.3067 | 123.674 | 3.0441 | 83.4137 | 115.5716 | 123.6374 | -123.912 | -123.9349
3212.7188 | 123.8434 | -61.3861 | 62.2101 | -0.16151 | 0.017733 | 0.017259 | 0.013388 | 0.064734 | -0.0018285 | 0.082253 | -58.342 | 62.2559 | -61.6928 | -61.5692 | 54.2587 | 22.0001 | 6.9397 | 6.2393 | 62.2375 | -61.702 | -0.3067 | 0.045776 | 3.0441 | -0.18311 | -7.9514 | -0.31586 | 0.027466 | 3.3508 | 68.3258 | 67.6254 | 115.6448 | 123.642 | 3.0441 | 123.6237 | 83.3862 | -0.31586 | 123.642 | 3.0441 | 83.3862 | 115.6448 | 123.6237 | -123.9029 | -123.912
3213.7188 | 123.7793 | -61.4319 | 62.1964 | 3.2259 | 0.016451 | 0.012345 | 0.012533 | 0.065802 | 0.0022303 | 0.079904 | -58.2916 | 62.2147 | -61.7157 | -61.647 | 54.2725 | 21.8948 | 6.8985 | 6.1615 | 62.2375 | -61.7249 | -0.28381 | 0.018311 | 3.1403 | -0.21515 | -7.9239 | -0.29297 | 0.041199 | 3.4241 | 68.3304 | 67.5934 | 115.7043 | 123.6465 | 3.1403 | 123.6694 | 83.3267 | -0.29297 | 123.6465 | 3.1403 | 83.3267 | 115.7043 | 123.6694 | -123.912 | -123.9212
3214.7188 | 123.8251 | -61.4044 | 62.1964 | -0.10048 | 0.017519 | 0.019181 | 0.016378 | 0.066657 | 0.00052127 | 0.080758 | -58.342 | 62.2513 | -61.6837 | -61.7294 | 54.1168 | 21.9269 | 6.9305 | 6.2302 | 62.2467 | -61.702 | -0.27924 | 0.054932 | 3.0624 | -0.32501 | -8.0795 | -0.29755 | 0.050354 | 3.3417 | 68.335 | 67.6346 | 115.5212 | 123.6557 | 3.0624 | 123.6511 | 83.3313 | -0.29755 | 123.6557 | 3.0624 | 83.3313 | 115.5212 | 123.6511 | -123.88 | -123.8983
3215.7188 | 123.8434 | -61.3998 | 62.2101 | -0.024185 | 0.017733 | 0.01854 | 0.014456 | 0.064734 | 0.00094847 | 0.079904 | -58.3054 | 62.2559 | -61.6928 | -61.5646 | 54.2038 | 21.8674 | 7.0908 | 6.2622 | 62.2284 | -61.7386 | -0.29297 | 0.045776 | 3.0945 | -0.16479 | -8.0063 | -0.33874 | 0.018311 | 3.3875 | 68.4906 | 67.662 | 115.6036 | 123.6557 | 3.0945 | 123.6282 | 83.2672 | -0.33874 | 123.6557 | 3.0945 | 83.2672 | 115.6036 | 123.6282 | -123.9029 | -123.9487
3216.7188 | 123.8159 | -61.3998 | 62.2147 | -0.13863 | 0.016665 | 0.019395 | 0.013601 | 0.064521 | 0.00073487 | 0.082467 | -58.342 | 62.2787 | -61.6699 | -61.5692 | 54.277 | 21.9589 | 6.9992 | 6.3309 | 62.2604 | -61.702 | -0.27008 | 0.064087 | 3.0579 | -0.16937 | -7.9376 | -0.30212 | 0.045776 | 3.3279 | 68.399 | 67.7307 | 115.6769 | 123.6786 | 3.0579 | 123.6603 | 83.3588 | -0.30212 | 123.6786 | 3.0579 | 83.3588 | 115.6769 | 123.6603 | -123.8846 | -123.9166
3217.7188 | 123.8068 | -61.3815 | 62.2559 | -0.22255 | 0.018587 | 0.019181 | 0.012106 | 0.064093 | 0.00030767 | 0.080972 | -58.3511 | 62.2513 | -61.6882 | -61.5829 | 54.2862 | 22.0047 | 6.9534 | 6.2942 | 62.2513 | -61.734 | -0.3067 | -0.004577 | 3.0304 | -0.20142 | -7.9697 | -0.35248 | -0.004577 | 3.3371 | 68.335 | 67.6758 | 115.6677 | 123.6328 | 3.0304 | 123.6328 | 83.3862 | -0.35248 | 123.6328 | 3.0304 | 83.3862 | 115.6677 | 123.6328 | -123.9441 | -123.9899
3218.7188 | 123.7701 | -61.4456 | 62.2238 | 0.14366 | 0.017092 | 0.016191 | 0.016806 | 0.071997 | -0.0022559 | 0.080972 | -58.429 | 62.2421 | -61.7249 | -61.5646 | 54.1901 | 22.0551 | 7.045 | 6.1478 | 62.2238 | -61.7477 | -0.27924 | 0.01831 | 3.0167 | -0.11902 | -8.0338 | -0.30212 | 0 | 3.2959 | 68.4906 | 67.5934 | 115.6357 | 123.6877 | 3.0167 | 123.6694 | 83.5007 | -0.30212 | 123.6877 | 3.0167 | 83.5007 | 115.6357 | 123.6694 | -123.9487 | -123.9716
3219.7188 | 123.8388 | -61.4502 | 62.2147 | 0.013962 | 0.015169 | 0.017686 | 0.012106 | 0.066016 | -0.00033333 | 0.080758 | -58.3511 | 62.2421 | -61.6837 | -61.5875 | 54.3045 | 22.0001 | 7.0129 | 6.2851 | 62.2192 | -61.7157 | -0.23346 | 0.027465 | 3.0991 | -0.13733 | -7.9102 | -0.2655 | 0.004577 | 3.3325 | 68.4631 | 67.7353 | 115.7547 | 123.6923 | 3.0991 | 123.6694 | 83.4503 | -0.2655 | 123.6923 | 3.0991 | 83.4503 | 115.7547 | 123.6694 | -123.8983 | -123.9304
3220.7188 | 123.8068 | -61.409 | 62.2192 | 0.021591 | 0.014315 | 0.017472 | 0.014456 | 0.067084 | 0.00052127 | 0.082253 | -58.3328 | 62.2787 | -61.6928 | -61.6013 | 54.3228 | 22.0917 | 6.958 | 6.2393 | 62.2421 | -61.7203 | -0.28381 | 0.05951 | 3.0762 | -0.19226 | -7.8964 | -0.31128 | 0.022888 | 3.36 | 68.367 | 67.6483 | 115.7318 | 123.6877 | 3.0762 | 123.6511 | 83.5007 | -0.31128 | 123.6877 | 3.0762 | 83.5007 | 115.7318 | 123.6511 | -123.912 | -123.9395
3221.7188 | 123.8297 | -61.3998 | 62.2238 | -0.024185 | 0.017092 | 0.01555 | 0.012106 | 0.064093 | 9.4068e-05 | 0.080117 | -58.3466 | 62.233 | -61.6837 | -61.5921 | 54.3045 | 22.0963 | 6.9397 | 6.2668 | 62.2284 | -61.7386 | -0.28381 | 0.009155 | 3.0533 | -0.19226 | -7.9193 | -0.33874 | 0.004578 | 3.3371 | 68.3395 | 67.6666 | 115.7043 | 123.6328 | 3.0533 | 123.6282 | 83.4961 | -0.33874 | 123.6328 | 3.0533 | 83.4961 | 115.7043 | 123.6282 | -123.9075 | -123.9624
3222.7188 | 123.8251 | -61.4227 | 62.2101 | -0.069961 | 0.019228 | 0.022599 | 0.012747 | 0.065375 | -0.00076053 | 0.081613 | -58.3191 | 62.2513 | -61.7065 | -61.5875 | 54.2725 | 22.0459 | 6.9168 | 6.2256 | 62.2238 | -61.7203 | -0.28381 | 0.041199 | 3.1036 | -0.1648 | -7.9376 | -0.29755 | 0.013733 | 3.3875 | 68.3395 | 67.6483 | 115.6952 | 123.674 | 3.1036 | 123.6465 | 83.4686 | -0.29755 | 123.674 | 3.1036 | 83.4686 | 115.6952 | 123.6465 | -123.9166 | -123.9304
3223.7188 | 123.7793 | -61.4227 | 62.2147 | 0.029221 | 0.016878 | 0.015336 | 0.01296 | 0.066016 | 9.4068e-05 | 0.082253 | -58.4061 | 62.2467 | -61.7111 | -61.6516 | 54.3182 | 22.0001 | 6.9672 | 6.2439 | 62.2284 | -61.7294 | -0.28839 | 0.032043 | 3.0167 | -0.22888 | -7.8964 | -0.3067 | 0.013733 | 3.3051 | 68.3899 | 67.6666 | 115.741 | 123.6694 | 3.0167 | 123.6511 | 83.4229 | -0.3067 | 123.6694 | 3.0167 | 83.4229 | 115.741 | 123.6511 | -123.9258 | -123.9441
3224.7188 | 123.8251 | -61.3998 | 62.2238 | -0.19966 | 0.017092 | 0.01555 | 0.013388 | 0.065375 | 0.00073487 | 0.080758 | -58.3832 | 62.2696 | -61.7065 | -61.5921 | 54.3777 | 22.2153 | 6.9855 | 6.3126 | 62.233 | -61.7065 | -0.3067 | 0.045776 | 3.0167 | -0.19226 | -7.8461 | -0.3067 | 0.009155 | 3.3234 | 68.3853 | 67.7124 | 115.7776 | 123.6694 | 3.0167 | 123.6328 | 83.6151 | -0.3067 | 123.6694 | 3.0167 | 83.6151 | 115.7776 | 123.6328 | -123.9304 | -123.9304
3225.7188 | 123.8113 | -61.4273 | 62.2009 | -0.10048 | 0.016665 | 0.013627 | 0.012533 | 0.063666 | -0.0016149 | 0.080758 | -58.3054 | 62.2192 | -61.7065 | -61.6058 | 54.3137 | 22.261 | 6.8848 | 6.221 | 62.2513 | -61.7203 | -0.27924 | 0.01831 | 3.1219 | -0.17853 | -7.8873 | -0.29297 | 0.050354 | 3.4012 | 68.3121 | 67.6483 | 115.741 | 123.6465 | 3.1219 | 123.6786 | 83.6884 | -0.29297 | 123.6465 | 3.1219 | 83.6884 | 115.741 | 123.6786 | -123.9075 | -123.9212
3226.7188 | 123.793 | -61.4273 | 62.2284 | -0.09285 | 0.01816 | 0.01555 | 0.013174 | 0.067084 | 0.00052127 | 0.085885 | -58.374 | 62.2559 | -61.6882 | -61.7294 | 54.1901 | 22.1787 | 6.9077 | 6.2302 | 62.233 | -61.7432 | -0.26093 | 0.027465 | 3.0533 | -0.30212 | -8.0383 | -0.31586 | 0.004577 | 3.3142 | 68.335 | 67.6575 | 115.6174 | 123.6832 | 3.0533 | 123.6603 | 83.606 | -0.31586 | 123.6832 | 3.0533 | 83.606 | 115.6174 | 123.6603 | -123.9166 | -123.9716
3227.7188 | 123.793 | -61.4136 | 62.1826 | -0.031814 | 0.01816 | 0.017686 | 0.014669 | 0.063666 | 0.00094847 | 0.081826 | -58.3603 | 62.2513 | -61.6974 | -61.5967 | 54.3777 | 22.316 | 6.9489 | 6.2531 | 62.2421 | -61.7477 | -0.28381 | 0.068665 | 3.0533 | -0.18311 | -7.8049 | -0.33417 | 0.059509 | 3.3371 | 68.3624 | 67.6666 | 115.7913 | 123.6649 | 3.0533 | 123.6557 | 83.7296 | -0.33417 | 123.6649 | 3.0533 | 83.7296 | 115.7913 | 123.6557 | -123.88 | -123.9304
3228.7188 | 123.8846 | -61.4136 | 62.1643 | 0.21233 | 0.017733 | 0.018327 | 0.010824 | 0.065589 | -0.00033333 | 0.081185 | -58.4061 | 62.2009 | -61.7065 | -61.6241 | 54.3137 | 22.2656 | 6.7886 | 6.2897 | 62.2009 | -61.7157 | -0.29297 | 0.036621 | 3.0075 | -0.21057 | -7.8506 | -0.30212 | 0.036621 | 3.3005 | 68.2022 | 67.7032 | 115.7272 | 123.6145 | 3.0075 | 123.6145 | 83.6792 | -0.30212 | 123.6145 | 3.0075 | 83.6792 | 115.7272 | 123.6145 | -123.8709 | -123.88
3229.7188 | 123.8297 | -61.4182 | 62.2101 | -0.79475 | 0.018374 | 0.014695 | 0.013601 | 0.063452 | -0.00076053 | 0.082894 | -58.3511 | 62.2467 | -61.7203 | -61.5875 | 54.3686 | 22.4075 | 6.9763 | 6.308 | 62.2284 | -61.7294 | -0.30212 | 0.036621 | 3.067 | -0.16937 | -7.8415 | -0.31128 | 0.018311 | 3.3691 | 68.3945 | 67.7261 | 115.7867 | 123.6649 | 3.067 | 123.6465 | 83.8257 | -0.31128 | 123.6649 | 3.067 | 83.8257 | 115.7867 | 123.6465 | -123.9304 | -123.9395
3230.7188 | 123.8251 | -61.3953 | 62.2055 | -0.19966 | 0.017947 | 0.015122 | 0.011679 | 0.066016 | -0.0020421 | 0.079476 | -58.3511 | 62.2513 | -61.6745 | -61.5875 | 54.3869 | 22.4167 | 7.0084 | 6.2805 | 62.2513 | -61.7065 | -0.27924 | 0.045777 | 3.0441 | -0.19226 | -7.8186 | -0.31128 | 0.045777 | 3.3234 | 68.4036 | 67.6758 | 115.7822 | 123.6465 | 3.0441 | 123.6465 | 83.812 | -0.31128 | 123.6465 | 3.0441 | 83.812 | 115.7822 | 123.6465 | -123.88 | -123.912
3231.7188 | 123.8113 | -61.4182 | 62.2238 | -0.19203 | 0.01816 | 0.016404 | 0.013388 | 0.064734 | -0.0014013 | 0.080331 | -58.3694 | 62.2604 | -61.7065 | -61.5921 | 54.4052 | 22.3984 | 7.0084 | 6.3126 | 62.2421 | -61.702 | -0.28839 | 0.036621 | 3.0487 | -0.17395 | -7.8186 | -0.28381 | 0.01831 | 3.3371 | 68.4265 | 67.7307 | 115.8234 | 123.6786 | 3.0487 | 123.6603 | 83.8165 | -0.28381 | 123.6786 | 3.0487 | 83.8165 | 115.8234 | 123.6603 | -123.9304 | -123.9258
3232.7188 | 123.88 | -61.4136 | 62.1964 | -0.09285 | 0.016024 | 0.016831 | 0.012533 | 0.064307 | -0.00033333 | 0.081399 | -58.3328 | 62.2375 | -61.702 | -61.5784 | 54.4556 | 22.3709 | 6.9534 | 6.2531 | 62.2238 | -61.7249 | -0.28839 | 0.041199 | 3.0807 | -0.1648 | -7.7408 | -0.31128 | 0.027466 | 3.3691 | 68.367 | 67.6666 | 115.8691 | 123.6511 | 3.0807 | 123.6374 | 83.7845 | -0.31128 | 123.6511 | 3.0807 | 83.7845 | 115.8691 | 123.6374 | -123.8983 | -123.9212
3233.7188 | 123.793 | -61.4365 | 62.2009 | 0.0063326 | 0.018374 | 0.015122 | 0.013174 | 0.065802 | 0.0011621 | 0.081185 | -58.3969 | 62.2421 | -61.7111 | -61.6516 | 54.3549 | 22.3251 | 7.0175 | 6.2302 | 62.2467 | -61.7249 | -0.27466 | 0.041198 | 3.0395 | -0.21515 | -7.8461 | -0.28839 | 0.045776 | 3.3142 | 68.454 | 67.6666 | 115.7913 | 123.6786 | 3.0395 | 123.6832 | 83.7616 | -0.28839 | 123.6786 | 3.0395 | 83.7616 | 115.7913 | 123.6832 | -123.912 | -123.9258
3234.7188 | 123.8113 | -61.409 | 62.2101 | -0.131 | 0.019869 | 0.016404 | 0.014242 | 0.064734 | -0.00097413 | 0.079904 | -58.3328 | 62.2375 | -61.6974 | -61.6058 | 54.4006 | 22.3572 | 6.9992 | 6.2897 | 62.2604 | -61.7477 | -0.28839 | 0.027466 | 3.0762 | -0.19684 | -7.8094 | -0.33875 | 0.050354 | 3.3646 | 68.4082 | 67.6987 | 115.8096 | 123.6465 | 3.0762 | 123.6694 | 83.7662 | -0.33875 | 123.6465 | 3.0762 | 83.7662 | 115.8096 | 123.6694 | -123.9075 | -123.9578
3235.7188 | 123.8068 | -61.4182 | 62.2192 | -0.17677 | 0.018374 | 0.017686 | 0.015524 | 0.066657 | 0.00030767 | 0.080758 | -58.3786 | 62.2467 | -61.6928 | -61.5829 | 54.4189 | 22.3846 | 6.9855 | 6.2714 | 62.2284 | -61.7477 | -0.27466 | 0.027466 | 3.0396 | -0.16479 | -7.8003 | -0.32959 | 0.009156 | 3.3142 | 68.4036 | 67.6895 | 115.8371 | 123.6649 | 3.0396 | 123.6465 | 83.8028 | -0.32959 | 123.6649 | 3.0396 | 83.8028 | 115.8371 | 123.6465 | -123.912 | -123.967
3236.7188 | 123.8297 | -61.3953 | 62.178 | -0.54298 | 0.017947 | 0.014909 | 0.014242 | 0.064093 | 0.00030767 | 0.081399 | -58.3557 | 62.2513 | -61.7477 | -61.5692 | 54.4098 | 22.3114 | 6.9901 | 6.2714 | 62.2238 | -61.7294 | -0.35248 | 0.073242 | 3.0396 | -0.17395 | -7.7683 | -0.33417 | 0.045776 | 3.392 | 68.3853 | 67.6666 | 115.8051 | 123.6465 | 3.0396 | 123.6191 | 83.7067 | -0.33417 | 123.6465 | 3.0396 | 83.7067 | 115.8051 | 123.6191 | -123.9258 | -123.9075
3237.7188 | 123.8113 | -61.4319 | 62.2009 | -0.22255 | 0.016238 | 0.020463 | 0.011251 | 0.064307 | 0.0013757 | 0.081613 | -58.374 | 62.265 | -61.7065 | -61.5784 | 54.4327 | 22.3938 | 7.0862 | 6.3492 | 62.2192 | -61.7386 | -0.27466 | 0.064087 | 3.0579 | -0.14648 | -7.7682 | -0.3067 | 0.01831 | 3.3325 | 68.5181 | 67.7811 | 115.8646 | 123.6969 | 3.0579 | 123.6511 | 83.8257 | -0.3067 | 123.6969 | 3.0579 | 83.8257 | 115.8646 | 123.6511 | -123.9075 | -123.9395
3238.7188 | 123.7839 | -61.4594 | 62.1964 | -0.46669 | 0.019869 | 0.018754 | 0.01296 | 0.065375 | -0.00011953 | 0.080331 | -58.4885 | 62.2375 | -61.7249 | -61.6882 | 54.3549 | 22.3434 | 7.0908 | 6.2714 | 62.2467 | -61.7661 | -0.2655 | 0.041199 | 2.9709 | -0.22888 | -7.8415 | -0.3067 | 0.050354 | 3.2364 | 68.5501 | 67.7307 | 115.8142 | 123.6969 | 2.9709 | 123.7061 | 83.8028 | -0.3067 | 123.6969 | 2.9709 | 83.8028 | 115.8142 | 123.7061 | -123.9212 | -123.9624
3239.7188 | 123.8068 | -61.4227 | 62.1872 | -0.09285 | 0.016238 | 0.017686 | 0.014029 | 0.062598 | -0.0026831 | 0.078835 | -58.3603 | 62.2421 | -61.7111 | -61.5005 | 54.4235 | 22.4808 | 7.0496 | 6.3538 | 62.2375 | -61.7157 | -0.28839 | 0.054931 | 3.0624 | -0.07782 | -7.7637 | -0.29297 | 0.050354 | 3.3508 | 68.4723 | 67.7765 | 115.8463 | 123.6649 | 3.0624 | 123.6603 | 83.9035 | -0.29297 | 123.6649 | 3.0624 | 83.9035 | 115.8463 | 123.6603 | -123.8983 | -123.9029
3240.7188 | 123.7793 | -61.4365 | 62.2147 | -0.062332 | 0.017733 | 0.015763 | 0.014883 | 0.065802 | 0.0011621 | 0.080972 | -58.3786 | 62.233 | -61.6974 | -61.6287 | 54.3503 | 22.3022 | 7.045 | 6.3171 | 62.2421 | -61.7386 | -0.26093 | 0.01831 | 3.0579 | -0.19226 | -7.8644 | -0.30212 | 0.027465 | 3.3188 | 68.4814 | 67.7536 | 115.7867 | 123.6694 | 3.0579 | 123.6786 | 83.7387 | -0.30212 | 123.6694 | 3.0579 | 83.7387 | 115.7867 | 123.6786 | -123.912 | -123.9532
3241.7188 | 123.8022 | -61.4456 | 62.1826 | -0.069961 | 0.02051 | 0.01854 | 0.013601 | 0.063239 | -0.0016149 | 0.081399 | -58.3557 | 62.2421 | -61.7111 | -61.615 | 54.3869 | 22.3801 | 7.0679 | 6.395 | 62.233 | -61.7249 | -0.2655 | 0.059509 | 3.0899 | -0.16937 | -7.7957 | -0.27924 | 0.050354 | 3.3554 | 68.5135 | 67.8406 | 115.8325 | 123.6877 | 3.0899 | 123.6786 | 83.8257 | -0.27924 | 123.6877 | 3.0899 | 83.8257 | 115.8325 | 123.6786 | -123.8937 | -123.9075
3242.7188 | 123.8205 | -61.4136 | 62.2238 | -0.054703 | 0.016238 | 0.012559 | 0.014029 | 0.065802 | -0.00076053 | 0.080117 | -58.342 | 62.2421 | -61.7294 | -61.615 | 54.3274 | 22.3206 | 6.9809 | 6.3583 | 62.2604 | -61.7386 | -0.31586 | 0.01831 | 3.0716 | -0.20142 | -7.8964 | -0.32501 | 0.036621 | 3.3875 | 68.3945 | 67.7719 | 115.741 | 123.6557 | 3.0716 | 123.674 | 83.7341 | -0.32501 | 123.6557 | 3.0716 | 83.7341 | 115.741 | 123.674 | -123.9532 | -123.9624
3243.7188 | 123.7747 | -61.4365 | 62.2055 | -0.0089264 | 0.018801 | 0.016831 | 0.012533 | 0.066016 | 0.0020167 | 0.080117 | -58.3969 | 62.2421 | -61.7294 | -61.6516 | 54.3594 | 22.2931 | 7.0404 | 6.3217 | 62.2467 | -61.7477 | -0.29297 | 0.036621 | 3.0395 | -0.21515 | -7.8461 | -0.31128 | 0.041199 | 3.3325 | 68.4769 | 67.7582 | 115.7959 | 123.6786 | 3.0395 | 123.6832 | 83.7296 | -0.31128 | 123.6786 | 3.0395 | 83.7296 | 115.7959 | 123.6832 | -123.9349 | -123.9532
3244.7188 | 123.8022 | -61.3998 | 62.2421 | -0.16151 | 0.020083 | 0.015763 | 0.011038 | 0.06623 | -0.00097413 | 0.079476 | -58.3328 | 62.265 | -61.6882 | -61.5967 | 54.2908 | 22.4579 | 6.7841 | 5.69 | 62.2513 | -61.7203 | -0.28839 | 0.022889 | 3.067 | -0.19684 | -7.9514 | -0.32043 | 0.009156 | 3.3554 | 68.1839 | 67.0898 | 115.6906 | 123.6649 | 3.067 | 123.6511 | 83.8577 | -0.32043 | 123.6649 | 3.067 | 83.8577 | 115.6906 | 123.6511 | -123.9304 | -123.9624
3245.7188 | 123.8205 | -61.4182 | 62.2009 | -0.08522 | 0.016665 | 0.019395 | 0.011892 | 0.06388 | 9.4068e-05 | 0.079476 | -58.3694 | 62.2559 | -61.6791 | -61.5829 | 54.3686 | 22.4579 | 7.1182 | 6.459 | 62.2467 | -61.7157 | -0.26093 | 0.054931 | 3.0487 | -0.16479 | -7.8323 | -0.29755 | 0.045776 | 3.3096 | 68.5364 | 67.8772 | 115.7867 | 123.674 | 3.0487 | 123.6649 | 83.876 | -0.29755 | 123.674 | 3.0487 | 83.876 | 115.7867 | 123.6649 | -123.88 | -123.9166
3246.7188 | 123.7747 | -61.4319 | 62.2101 | -0.077591 | 0.017519 | 0.013841 | 0.01531 | 0.065375 | 0.00073487 | 0.079904 | -58.3282 | 62.2513 | -61.6928 | -61.6013 | 54.3365 | 22.5769 | 6.8069 | 5.7495 | 62.2147 | -61.7157 | -0.26093 | 0.041199 | 3.1036 | -0.16937 | -7.8735 | -0.28381 | 0.004578 | 3.3646 | 68.2388 | 67.1814 | 115.7684 | 123.6832 | 3.1036 | 123.6465 | 84.0088 | -0.28381 | 123.6832 | 3.1036 | 84.0088 | 115.7684 | 123.6465 | -123.9029 | -123.9258
3247.7188 | 123.8022 | -61.4182 | 62.2101 | -0.039444 | 0.017733 | 0.017686 | 0.013601 | 0.064948 | -0.0018285 | 0.08204 | -58.342 | 62.2421 | -61.6974 | -61.6058 | 54.3137 | 22.4716 | 6.8481 | 5.7999 | 62.2147 | -61.7386 | -0.27924 | 0.032043 | 3.0762 | -0.18768 | -7.8964 | -0.32043 | 0.004578 | 3.3554 | 68.2663 | 67.218 | 115.7318 | 123.6603 | 3.0762 | 123.6328 | 83.8898 | -0.32043 | 123.6603 | 3.0762 | 83.8898 | 115.7318 | 123.6328 | -123.9075 | -123.9487
3248.7188 | 123.8892 | -61.4273 | 62.1368 | 0.2047 | 0.017306 | 0.016831 | 0.010611 | 0.067298 | -0.00011953 | 0.082894 | -58.3969 | 62.1872 | -61.7157 | -61.5875 | 54.3503 | 22.5403 | 6.8802 | 6.395 | 62.1735 | -61.7523 | -0.28839 | 0.050354 | 3.0304 | -0.16022 | -7.7866 | -0.32501 | 0.036621 | 3.3188 | 68.3075 | 67.8223 | 115.7776 | 123.6145 | 3.0304 | 123.6008 | 83.9676 | -0.32501 | 123.6145 | 3.0304 | 83.9676 | 115.7776 | 123.6008 | -123.8525 | -123.8892
3249.7188 | 123.7747 | -61.4136 | 62.2147 | -0.0012969 | 0.016665 | 0.013413 | 0.014242 | 0.065589 | 0.0015893 | 0.081613 | -58.429 | 62.2421 | -61.7111 | -61.6608 | 54.2587 | 22.403 | 7.0221 | 6.2851 | 62.2421 | -61.7615 | -0.29755 | 0.027465 | 2.9846 | -0.24719 | -7.9559 | -0.3479 | 0.027465 | 3.2822 | 68.4357 | 67.6987 | 115.6723 | 123.6557 | 2.9846 | 123.6557 | 83.8165 | -0.3479 | 123.6557 | 2.9846 | 83.8165 | 115.6723 | 123.6557 | -123.9258 | -123.9761
3250.7188 | 123.7747 | -61.4365 | 62.2192 | 0.03685 | 0.016665 | 0.019395 | 0.01531 | 0.065375 | 0.0022303 | 0.081185 | -58.3969 | 62.2559 | -61.6974 | -61.647 | 54.2725 | 22.3663 | 7.0084 | 6.2988 | 62.233 | -61.7569 | -0.26093 | 0.036621 | 3.0395 | -0.21057 | -7.9468 | -0.32044 | 0.013733 | 3.3005 | 68.4448 | 67.7353 | 115.7089 | 123.6923 | 3.0395 | 123.6694 | 83.8028 | -0.32044 | 123.6923 | 3.0395 | 83.8028 | 115.7089 | 123.6694 | -123.9166 | -123.9761
3251.7188 | 123.8205 | -61.4227 | 62.1918 | -0.047073 | 0.019656 | 0.014695 | 0.011251 | 0.065802 | -0.00054693 | 0.080758 | -58.4015 | 62.2375 | -61.6928 | -61.6058 | 54.3365 | 22.4167 | 7.0816 | 6.4178 | 62.2192 | -61.7523 | -0.27008 | 0.045777 | 3.0212 | -0.18311 | -7.8552 | -0.32959 | 0.027466 | 3.2913 | 68.5043 | 67.8406 | 115.7593 | 123.6603 | 3.0212 | 123.642 | 83.8394 | -0.32959 | 123.6603 | 3.0212 | 83.8394 | 115.7593 | 123.642 | -123.8846 | -123.9441
3252.7188 | 123.8205 | -61.4273 | 62.2101 | -0.039444 | 0.02051 | 0.016618 | 0.013388 | 0.063666 | 0.0011621 | 0.080331 | -58.3832 | 62.2421 | -61.6882 | -61.6013 | 54.3457 | 22.4258 | 7.0679 | 6.427 | 62.2375 | -61.734 | -0.26093 | 0.032043 | 3.0441 | -0.17395 | -7.8644 | -0.3067 | 0.027466 | 3.3051 | 68.4952 | 67.8543 | 115.773 | 123.6694 | 3.0441 | 123.6649 | 83.8531 | -0.3067 | 123.6694 | 3.0441 | 83.8531 | 115.773 | 123.6649 | -123.8983 | -123.9441
3253.7188 | 123.912 | -61.3907 | 62.1552 | 1.3567 | 0.014956 | 0.012773 | 0.0067654 | 0.064307 | 0.0020167 | 0.080758 | -58.255 | 62.1414 | -61.7065 | -61.5601 | 54.4098 | 22.5677 | 6.8253 | 6.3995 | 62.1872 | -61.7157 | -0.31586 | -0.013733 | 3.1357 | -0.16937 | -7.7454 | -0.32501 | 0.032044 | 3.4515 | 68.2159 | 67.7902 | 115.8005 | 123.5321 | 3.1357 | 123.5779 | 83.9584 | -0.32501 | 123.5321 | 3.1357 | 83.9584 | 115.8005 | 123.5779 | -123.8617 | -123.8708
3254.7188 | 123.7564 | -61.4136 | 62.2101 | 0.052109 | 0.017092 | 0.019181 | 0.014883 | 0.062598 | 0.0011621 | 0.081613 | -58.4106 | 62.2421 | -61.7203 | -61.6653 | 54.3411 | 22.4945 | 7.0633 | 6.2942 | 62.2009 | -61.7706 | -0.3067 | 0.032043 | 3.0029 | -0.25177 | -7.869 | -0.35706 | -0.009155 | 3.3096 | 68.4769 | 67.7078 | 115.7547 | 123.6557 | 3.0029 | 123.6145 | 83.9081 | -0.35706 | 123.6557 | 3.0029 | 83.9081 | 115.7547 | 123.6145 | -123.9304 | -123.9807
3255.7188 | 123.7885 | -61.4685 | 62.1918 | 0.14366 | 0.018801 | 0.013841 | 0.010397 | 0.064521 | -0.00033333 | 0.082681 | -58.255 | 62.1918 | -61.7752 | -61.6013 | 54.2358 | 22.4579 | 6.9946 | 6.3217 | 62.2375 | -61.7706 | -0.3067 | 0 | 3.2135 | -0.13275 | -7.9559 | -0.30212 | 0.045777 | 3.5202 | 68.4631 | 67.7902 | 115.7043 | 123.6603 | 3.2135 | 123.7061 | 83.9264 | -0.30212 | 123.6603 | 3.2135 | 83.9264 | 115.7043 | 123.7061 | -123.967 | -123.9624
3256.7188 | 123.7656 | -61.4502 | 62.1872 | 0.14366 | 0.019015 | 0.020677 | 0.014242 | 0.065375 | -0.00033333 | 0.079904 | -58.699 | 62.1826 | -61.7798 | -61.6608 | 54.1168 | 22.4121 | 7.1228 | 6.3675 | 62.1918 | -61.7752 | -0.32959 | -0.004578 | 2.7512 | -0.21057 | -8.0704 | -0.32501 | 0.004577 | 3.0807 | 68.573 | 67.8177 | 115.567 | 123.6328 | 2.7512 | 123.642 | 83.8623 | -0.32501 | 123.6328 | 2.7512 | 83.8623 | 115.567 | 123.642 | -123.967 | -123.9624
3257.7188 | 123.7885 | -61.4639 | 62.1964 | 0.18944 | 0.017947 | 0.014268 | 0.013601 | 0.065802 | -0.00033333 | 0.081399 | -58.5846 | 62.2101 | -61.7523 | -61.6287 | 54.2175 | 22.3892 | 7.1777 | 6.4453 | 62.2055 | -61.7615 | -0.28839 | 0.013733 | 2.8793 | -0.16479 | -7.9788 | -0.29755 | 0.009155 | 3.1677 | 68.6417 | 67.9092 | 115.6815 | 123.674 | 2.8793 | 123.6694 | 83.8531 | -0.29755 | 123.674 | 2.8793 | 83.8531 | 115.6815 | 123.6694 | -123.9487 | -123.9578
3258.7188 | 123.7839 | -61.4502 | 62.2101 | 0.18181 | 0.017519 | 0.017472 | 0.012747 | 0.06623 | 0.0018031 | 0.081399 | -58.7494 | 62.1643 | -61.7432 | -61.6791 | 54.1718 | 22.3892 | 7.1548 | 6.3858 | 62.2375 | -61.7569 | -0.29297 | -0.045776 | 2.7008 | -0.22888 | -8.0383 | -0.3067 | 0.027466 | 2.9938 | 68.605 | 67.836 | 115.6219 | 123.6145 | 2.7008 | 123.6877 | 83.8394 | -0.3067 | 123.6145 | 2.7008 | 83.8394 | 115.6219 | 123.6877 | -123.9532 | -123.967
3259.7188 | 123.7473 | -61.4548 | 62.2238 | 0.04448 | 0.017306 | 0.019181 | 0.01296 | 0.062812 | 0.0020167 | 0.080117 | -58.4473 | 62.233 | -61.7294 | -61.6745 | 54.2221 | 22.4396 | 7.1411 | 6.4224 | 62.2101 | -61.7752 | -0.27466 | 0.009155 | 3.0075 | -0.21973 | -8.0017 | -0.32043 | -0.013733 | 3.2822 | 68.5959 | 67.8772 | 115.6769 | 123.6877 | 3.0075 | 123.6649 | 83.8943 | -0.32043 | 123.6877 | 3.0075 | 83.8943 | 115.6769 | 123.6649 | -123.9532 | -123.999
3260.7188 | 123.7793 | -61.4639 | 62.1872 | 0.17418 | 0.017519 | 0.017045 | 0.014456 | 0.06687 | -0.00054693 | 0.082467 | -58.7173 | 62.1826 | -61.7386 | -61.6699 | 54.1992 | 22.4258 | 7.1365 | 6.3721 | 62.2513 | -61.7477 | -0.27466 | -0.004578 | 2.7466 | -0.20599 | -7.988 | -0.28381 | 0.064087 | 3.0212 | 68.6005 | 67.836 | 115.6631 | 123.6465 | 2.7466 | 123.7152 | 83.8898 | -0.28381 | 123.6465 | 2.7466 | 83.8898 | 115.6631 | 123.7152 | -123.9258 | -123.9349
3261.7188 | 123.7701 | -61.4502 | 62.2055 | 0.14366 | 0.020083 | 0.016191 | 0.012533 | 0.064948 | 0.00073487 | 0.080972 | -58.4198 | 62.2147 | -61.7615 | -61.5921 | 54.2313 | 22.3846 | 7.0908 | 6.427 | 62.2238 | -61.7798 | -0.31128 | 0.009156 | 3.0304 | -0.14191 | -7.9742 | -0.32959 | 0.018311 | 3.3417 | 68.541 | 67.8772 | 115.6815 | 123.6649 | 3.0304 | 123.674 | 83.8348 | -0.32959 | 123.6649 | 3.0304 | 83.8348 | 115.6815 | 123.674 | -123.967 | -123.9853
3262.7188 | 123.848 | -61.4136 | 62.1918 | 0.18181 | 0.014529 | 0.016191 | 0.011465 | 0.06388 | 0.0028711 | 0.080758 | -58.4564 | 62.2192 | -61.7203 | -61.6562 | 54.213 | 22.467 | 7.0038 | 6.4453 | 62.2009 | -61.7523 | -0.3067 | 0.027466 | 2.9572 | -0.24262 | -7.9788 | -0.33875 | 0.009156 | 3.2639 | 68.4174 | 67.8589 | 115.6265 | 123.6328 | 2.9572 | 123.6145 | 83.8806 | -0.33875 | 123.6328 | 2.9572 | 83.8806 | 115.6265 | 123.6145 | -123.912 | -123.9441
3263.7344 | 123.7976 | -61.4044 | 62.2513 | -0.20729 | 0.017092 | 0.013841 | 0.011892 | 0.061743 | 0.0011621 | 0.078408 | -58.4244 | 62.2787 | -61.7157 | -61.6104 | 54.2587 | 22.5082 | 6.8802 | 5.8136 | 62.2467 | -61.7294 | -0.31128 | 0.027466 | 2.98 | -0.20599 | -7.9926 | -0.32501 | -0.004578 | 3.2913 | 68.2846 | 67.218 | 115.6631 | 123.6832 | 2.98 | 123.6511 | 83.9127 | -0.32501 | 123.6832 | 2.98 | 83.9127 | 115.6631 | 123.6511 | -123.967 | -123.9807
3264.7188 | 123.7976 | -61.4227 | 62.2009 | 0.18944 | 0.01581 | 0.01555 | 0.012747 | 0.063452 | 0.0011621 | 0.081613 | -58.4473 | 62.2147 | -61.7386 | -61.6379 | 54.1946 | 22.4258 | 6.7795 | 5.7953 | 62.2238 | -61.7249 | -0.31586 | 0.013733 | 2.9755 | -0.21515 | -8.0063 | -0.30213 | 0.022888 | 3.2913 | 68.2022 | 67.218 | 115.6174 | 123.6374 | 2.9755 | 123.6465 | 83.8486 | -0.30213 | 123.6374 | 2.9755 | 83.8486 | 115.6174 | 123.6465 | -123.9395 | -123.9258
3265.7188 | 123.7289 | -61.4319 | 62.1872 | 0.15892 | 0.019228 | 0.013413 | 0.010183 | 0.061316 | -0.0011877 | 0.080758 | -58.4747 | 62.2421 | -61.7294 | -61.6608 | 54.3594 | 22.4991 | 7.0267 | 6.4224 | 62.2192 | -61.7432 | -0.29755 | 0.054931 | 2.9572 | -0.22888 | -7.8278 | -0.31128 | 0.032043 | 3.2547 | 68.4586 | 67.8543 | 115.7913 | 123.674 | 2.9572 | 123.6511 | 83.931 | -0.31128 | 123.674 | 2.9572 | 83.931 | 115.7913 | 123.6511 | -123.9166 | -123.9304
3266.7188 | 123.8022 | -61.409 | 62.1964 | 0.15892 | 0.01816 | 0.020463 | 0.011465 | 0.063666 | 0.0020167 | 0.080972 | -58.4244 | 62.2192 | -61.734 | -61.6287 | 54.3045 | 22.5266 | 6.72 | 5.6671 | 62.2101 | -61.7294 | -0.32501 | 0.022888 | 2.9846 | -0.21973 | -7.8918 | -0.32043 | 0.013733 | 3.3096 | 68.129 | 67.0761 | 115.7135 | 123.6282 | 2.9846 | 123.6191 | 83.9355 | -0.32043 | 123.6282 | 2.9846 | 83.9355 | 115.7135 | 123.6191 | -123.9304 | -123.9258
3267.7188 | 123.8113 | -61.4182 | 62.1826 | 0.16655 | 0.018801 | 0.013841 | 0.011679 | 0.063666 | 0.0011621 | 0.07969 | -58.4747 | 62.2147 | -61.7386 | -61.6379 | 54.2084 | 22.4808 | 7.0175 | 6.4087 | 62.1872 | -61.7477 | -0.32043 | 0.032044 | 2.9434 | -0.21973 | -7.9742 | -0.32959 | 0.004578 | 3.2639 | 68.4357 | 67.8268 | 115.6265 | 123.6328 | 2.9434 | 123.6053 | 83.8989 | -0.32959 | 123.6328 | 2.9434 | 83.8989 | 115.6265 | 123.6053 | -123.9212 | -123.9304
3268.7344 | 123.88 | -61.3632 | 62.1918 | -0.19203 | 0.011751 | 0.012986 | 0.0065518 | 0.062384 | 0.00073487 | 0.082467 | -58.374 | 62.1643 | -61.6974 | -61.5372 | 54.245 | 22.5723 | 7.0404 | 6.5506 | 62.2009 | -61.6974 | -0.33417 | -0.027465 | 2.9892 | -0.17395 | -7.9468 | -0.33417 | 0.009156 | 3.3234 | 68.4036 | 67.9138 | 115.6082 | 123.5275 | 2.9892 | 123.5641 | 83.9355 | -0.33417 | 123.5275 | 2.9892 | 83.9355 | 115.6082 | 123.5641 | -123.8892 | -123.8892
3269.7188 | 123.8754 | -61.4136 | 62.1735 | 0.30388 | 0.013674 | 0.014482 | 0.013815 | 0.064307 | 0.0020167 | 0.080117 | -58.4061 | 62.146 | -61.7065 | -61.5601 | 54.2175 | 22.5952 | 6.9946 | 6.5186 | 62.1552 | -61.6974 | -0.29297 | -0.027466 | 3.0075 | -0.14649 | -7.9559 | -0.28381 | -0.018311 | 3.3005 | 68.4082 | 67.9321 | 115.6311 | 123.5596 | 3.0075 | 123.5687 | 84.0088 | -0.28381 | 123.5596 | 3.0075 | 84.0088 | 115.6311 | 123.5687 | -123.88 | -123.8708
3270.7188 | 123.8846 | -61.3815 | 62.1826 | 0.36491 | 0.016238 | 0.014054 | 0.012747 | 0.063239 | 0.0011621 | 0.08204 | -58.3694 | 62.1735 | -61.6928 | -61.5509 | 54.2908 | 22.6273 | 6.6284 | 5.5435 | 62.1552 | -61.7157 | -0.31128 | -0.009155 | 3.0121 | -0.16937 | -7.8918 | -0.33417 | -0.027466 | 3.3234 | 68.0099 | 66.925 | 115.6723 | 123.555 | 3.0121 | 123.5367 | 84.0088 | -0.33417 | 123.555 | 3.0121 | 84.0088 | 115.6723 | 123.5367 | -123.8754 | -123.8983
3271.7188 | 123.8937 | -61.3953 | 62.178 | 0.21233 | 0.016665 | 0.016618 | 0.014242 | 0.062171 | 0.0018031 | 0.07969 | -58.3649 | 62.178 | -61.7111 | -61.5692 | 54.2633 | 22.6685 | 7.0084 | 6.5048 | 62.1323 | -61.702 | -0.31586 | 0 | 3.0304 | -0.17395 | -7.9147 | -0.3067 | -0.045777 | 3.3463 | 68.4036 | 67.9001 | 115.6586 | 123.5733 | 3.0304 | 123.5275 | 84.0637 | -0.3067 | 123.5733 | 3.0304 | 84.0637 | 115.6586 | 123.5275 | -123.8892 | -123.88
3272.7188 | 123.8388 | -61.4227 | 62.1826 | 0.21233 | 0.018587 | 0.014268 | 0.014883 | 0.062598 | 9.4068e-05 | 0.082253 | -58.4198 | 62.1964 | -61.7249 | -61.6333 | 54.2038 | 22.5266 | 7.0816 | 6.4041 | 62.1964 | -61.7386 | -0.30213 | 0.013733 | 3.0029 | -0.21057 | -7.9788 | -0.31586 | 0.013733 | 3.3051 | 68.5043 | 67.8268 | 115.6265 | 123.6191 | 3.0029 | 123.6191 | 83.9493 | -0.31586 | 123.6191 | 3.0029 | 83.9493 | 115.6265 | 123.6191 | -123.9075 | -123.9212
3273.7344 | 123.7701 | -61.3953 | 62.2467 | -0.26833 | 0.017519 | 0.014054 | 0.011465 | 0.061743 | 9.4068e-05 | 0.079476 | -58.3694 | 62.2101 | -61.6974 | -61.5875 | 54.2404 | 22.5723 | 6.9397 | 5.5573 | 62.2513 | -61.6974 | -0.30212 | -0.036621 | 3.0258 | -0.19226 | -8.0063 | -0.30212 | 0.004578 | 3.3279 | 68.335 | 66.9525 | 115.6357 | 123.6053 | 3.0258 | 123.6465 | 83.9676 | -0.30212 | 123.6053 | 3.0258 | 83.9676 | 115.6357 | 123.6465 | -123.9441 | -123.9441
3274.7188 | 123.8892 | -61.3907 | 62.1689 | 0.30388 | 0.014529 | 0.015763 | 0.011038 | 0.06388 | -0.00097413 | 0.080331 | -58.374 | 62.1185 | -61.6928 | -61.5646 | 54.2587 | 22.6273 | 6.7657 | 5.6351 | 62.1506 | -61.6699 | -0.30212 | -0.050354 | 3.0167 | -0.17395 | -7.9102 | -0.27924 | -0.01831 | 3.3188 | 68.1564 | 67.0258 | 115.6494 | 123.5092 | 3.0167 | 123.5413 | 84.0179 | -0.27924 | 123.5092 | 3.0167 | 84.0179 | 115.6494 | 123.5413 | -123.8617 | -123.8388
3275.7188 | 123.9029 | -61.3861 | 62.1552 | 0.79216 | 0.01581 | 0.014268 | 0.0080472 | 0.061743 | -0.00011953 | 0.081613 | -58.3511 | 62.1552 | -61.6745 | -61.5738 | 54.2358 | 22.6089 | 7.0541 | 6.546 | 62.1368 | -61.7111 | -0.28839 | 0 | 3.035 | -0.18768 | -7.9193 | -0.32501 | -0.01831 | 3.3234 | 68.4402 | 67.9321 | 115.6219 | 123.5413 | 3.035 | 123.5229 | 83.9951 | -0.32501 | 123.5413 | 3.035 | 83.9951 | 115.6219 | 123.5229 | -123.8297 | -123.8663
3276.7188 | 123.8846 | -61.3953 | 62.1918 | 0.28099 | 0.014529 | 0.013627 | 0.0097562 | 0.061103 | 0.00052127 | 0.080544 | -58.3832 | 62.1323 | -61.6745 | -61.5555 | 54.2725 | 22.6364 | 6.7429 | 5.6946 | 62.1368 | -61.6699 | -0.27924 | -0.059509 | 3.0121 | -0.16022 | -7.9193 | -0.27466 | -0.054931 | 3.2913 | 68.1381 | 67.0898 | 115.6677 | 123.5275 | 3.0121 | 123.5321 | 84.0317 | -0.27466 | 123.5275 | 3.0121 | 84.0317 | 115.6677 | 123.5321 | -123.8663 | -123.8617
3277.7188 | 123.8846 | -61.3953 | 62.1643 | -1.283 | 0.013674 | 0.013627 | 0.011251 | 0.063025 | 0.0015893 | 0.081613 | -58.3511 | 62.1506 | -61.6745 | -61.5509 | 54.277 | 22.5586 | 7.0908 | 6.514 | 62.1552 | -61.6791 | -0.27924 | -0.013733 | 3.0441 | -0.15564 | -7.8873 | -0.28381 | -0.009156 | 3.3234 | 68.486 | 67.9092 | 115.6723 | 123.5458 | 3.0441 | 123.5504 | 83.9539 | -0.28381 | 123.5458 | 3.0441 | 83.9539 | 115.6723 | 123.5504 | -123.8388 | -123.8434
3278.7188 | 123.9166 | -61.4044 | 62.1643 | 0.25047 | 0.017947 | 0.011704 | 0.013601 | 0.063452 | 0.00094847 | 0.079476 | -58.3923 | 62.1368 | -61.7157 | -61.5692 | 54.2175 | 22.5311 | 7.132 | 6.4865 | 62.1368 | -61.7111 | -0.31128 | -0.027466 | 3.0121 | -0.1648 | -7.9468 | -0.3067 | -0.027466 | 3.3234 | 68.5364 | 67.8909 | 115.6219 | 123.5413 | 3.0121 | 123.5413 | 83.9355 | -0.3067 | 123.5413 | 3.0121 | 83.9355 | 115.6219 | 123.5413 | -123.88 | -123.8754
3279.7188 | 123.8983 | -61.377 | 62.1735 | 0.24284 | 0.016238 | 0.014909 | 0.016165 | 0.064093 | 0.00030767 | 0.079904 | -58.3832 | 62.1689 | -61.7157 | -61.5646 | 54.277 | 22.5632 | 6.7886 | 5.7175 | 62.1643 | -61.6699 | -0.33875 | -0.004578 | 2.9938 | -0.18768 | -7.8964 | -0.29297 | -0.009155 | 3.3325 | 68.1656 | 67.0944 | 115.654 | 123.5458 | 2.9938 | 123.5413 | 83.9401 | -0.29297 | 123.5458 | 2.9938 | 83.9401 | 115.654 | 123.5413 | -123.8892 | -123.8434
3280.7188 | 123.8937 | -61.3861 | 62.1735 | 0.25047 | 0.016665 | 0.012132 | 0.013388 | 0.062384 | -0.00097413 | 0.080972 | -58.3694 | 62.1368 | -61.6608 | -61.5463 | 54.2862 | 22.6547 | 6.7657 | 5.7632 | 62.146 | -61.6882 | -0.27466 | -0.036621 | 3.0167 | -0.16022 | -7.8873 | -0.30212 | -0.027466 | 3.2913 | 68.1519 | 67.1494 | 115.6723 | 123.5229 | 3.0167 | 123.5321 | 84.0408 | -0.30212 | 123.5229 | 3.0167 | 84.0408 | 115.6723 | 123.5321 | -123.8342 | -123.8617
3281.7188 | 123.9166 | -61.3724 | 62.1643 | 0.28862 | 0.016451 | 0.015763 | 0.013815 | 0.065375 | -0.00076053 | 0.079263 | -58.3923 | 62.114 | -61.7203 | -61.3907 | 54.4052 | 22.6364 | 7.0267 | 6.601 | 62.1735 | -61.6837 | -0.3479 | -0.050354 | 2.98 | -0.018311 | -7.7591 | -0.31128 | 0.009155 | 3.3279 | 68.399 | 67.9733 | 115.7776 | 123.4863 | 2.98 | 123.5458 | 84.0088 | -0.31128 | 123.4863 | 2.98 | 84.0088 | 115.7776 | 123.5458 | -123.8846 | -123.848
3282.7188 | 123.848 | -61.3861 | 62.1964 | 0.15892 | 0.014101 | 0.016618 | 0.011038 | 0.06153 | -0.00054693 | 0.080331 | -58.4015 | 62.1231 | -61.702 | -61.5372 | 54.2908 | 22.6501 | 6.7245 | 5.7129 | 62.1506 | -61.6791 | -0.31586 | -0.073242 | 2.9846 | -0.15106 | -7.9056 | -0.29297 | -0.045776 | 3.3005 | 68.1107 | 67.099 | 115.6769 | 123.5092 | 2.9846 | 123.5367 | 84.0363 | -0.29297 | 123.5092 | 2.9846 | 84.0363 | 115.6769 | 123.5367 | -123.8983 | -123.8754
3283.7188 | 123.9212 | -61.3541 | 62.1689 | -0.069961 | 0.014529 | 0.0095682 | 0.0076198 | 0.058753 | -0.00054693 | 0.080544 | -58.3786 | 62.1094 | -61.6974 | -61.496 | 54.2816 | 22.6273 | 6.8573 | 5.8777 | 62.1689 | -61.6699 | -0.34332 | -0.059509 | 2.9755 | -0.14191 | -7.8873 | -0.31586 | 0 | 3.3188 | 68.2114 | 67.2318 | 115.6357 | 123.4634 | 2.9755 | 123.5229 | 83.9813 | -0.31586 | 123.4634 | 2.9755 | 83.9813 | 115.6357 | 123.5229 | -123.8663 | -123.8388
3284.7188 | 123.9212 | -61.3998 | 62.1689 | 0.21233 | 0.013674 | 0.015122 | 0.01531 | 0.06153 | -0.0018285 | 0.079476 | -58.3649 | 62.1185 | -61.6837 | -61.5463 | 54.3045 | 22.6135 | 6.9031 | 5.8502 | 62.1735 | -61.6837 | -0.28381 | -0.050354 | 3.035 | -0.14648 | -7.8644 | -0.28381 | 0.004578 | 3.3188 | 68.3029 | 67.2501 | 115.7043 | 123.5184 | 3.035 | 123.5733 | 84.0134 | -0.28381 | 123.5184 | 3.035 | 84.0134 | 115.7043 | 123.5733 | -123.8525 | -123.8525
3285.7188 | 123.9029 | -61.377 | 62.1872 | 0.21996 | 0.017306 | 0.014909 | 0.013815 | 0.061316 | 0.0011621 | 0.082894 | -58.3923 | 62.1506 | -61.6791 | -61.528 | 54.3228 | 22.5861 | 6.871 | 5.9647 | 62.1323 | -61.7111 | -0.30212 | -0.036621 | 2.9846 | -0.15106 | -7.8644 | -0.33417 | -0.054932 | 3.2867 | 68.248 | 67.3416 | 115.6998 | 123.5275 | 2.9846 | 123.5092 | 83.963 | -0.33417 | 123.5275 | 2.9846 | 83.963 | 115.6998 | 123.5092 | -123.8663 | -123.8983
3286.7188 | 123.8709 | -61.3907 | 62.1918 | 0.25047 | 0.015597 | 0.015977 | 0.014669 | 0.061957 | 0.00073487 | 0.08204 | -58.374 | 62.1277 | -61.6791 | -61.5463 | 54.3365 | 22.6364 | 6.8207 | 5.8411 | 62.1414 | -61.6974 | -0.28839 | -0.064086 | 3.0167 | -0.15564 | -7.8552 | -0.3067 | -0.050354 | 3.3051 | 68.2114 | 67.2318 | 115.7272 | 123.5184 | 3.0167 | 123.5321 | 84.0271 | -0.3067 | 123.5184 | 3.0167 | 84.0271 | 115.7272 | 123.5321 | -123.8708 | -123.8892
3287.7188 | 123.8846 | -61.377 | 62.1597 | -1.6492 | 0.016665 | 0.016618 | 0.011679 | 0.060248 | -0.00097413 | 0.078835 | -58.374 | 62.1277 | -61.6699 | -61.5509 | 54.3045 | 22.6822 | 6.8573 | 5.9052 | 62.1368 | -61.6791 | -0.29297 | -0.032043 | 3.0029 | -0.17395 | -7.8552 | -0.30212 | -0.022888 | 3.2959 | 68.2343 | 67.2821 | 115.6815 | 123.5046 | 3.0029 | 123.5138 | 84.0591 | -0.30212 | 123.5046 | 3.0029 | 84.0591 | 115.6815 | 123.5138 | -123.8297 | -123.8388
3288.7188 | 123.8754 | -61.3998 | 62.1597 | 0.19707 | 0.017306 | 0.017472 | 0.014456 | 0.063666 | 0.0015893 | 0.080972 | -58.5205 | 62.1094 | -61.7432 | -61.5326 | 54.2999 | 22.6135 | 7.0953 | 6.5323 | 62.1231 | -61.702 | -0.34332 | -0.050354 | 2.8793 | -0.13275 | -7.8598 | -0.30212 | -0.036621 | 3.2227 | 68.4952 | 67.9321 | 115.6998 | 123.5092 | 2.8793 | 123.5229 | 84.0134 | -0.30212 | 123.5092 | 2.8793 | 84.0134 | 115.6998 | 123.5229 | -123.9029 | -123.8617
3289.7188 | 123.8983 | -61.377 | 62.1735 | 0.13603 | 0.01581 | 0.013841 | 0.012747 | 0.060675 | 0.0011621 | 0.080972 | -58.4244 | 62.1094 | -61.7203 | -61.5463 | 54.3411 | 22.5906 | 6.9489 | 6.1432 | 62.1414 | -61.7203 | -0.34332 | -0.064087 | 2.9526 | -0.16937 | -7.8323 | -0.34332 | -0.032044 | 3.2959 | 68.3258 | 67.5201 | 115.7181 | 123.4863 | 2.9526 | 123.5184 | 83.9676 | -0.34332 | 123.4863 | 2.9526 | 83.9676 | 115.7181 | 123.5184 | -123.8937 | -123.8937
3290.7188 | 123.8892 | -61.3907 | 62.1597 | 0.17418 | 0.016238 | 0.013413 | 0.01232 | 0.061103 | -0.00076053 | 0.078408 | -58.3969 | 62.1185 | -61.702 | -61.5372 | 54.4006 | 22.6273 | 6.8756 | 5.9692 | 62.1277 | -61.702 | -0.31128 | -0.041199 | 2.9938 | -0.14648 | -7.7591 | -0.31128 | -0.032043 | 3.3051 | 68.2663 | 67.3599 | 115.7913 | 123.5092 | 2.9938 | 123.5184 | 84.0179 | -0.31128 | 123.5092 | 2.9938 | 84.0179 | 115.7913 | 123.5184 | -123.8617 | -123.8617
3291.7188 | 123.88 | -61.3907 | 62.146 | 0.2047 | 0.016451 | 0.01555 | 0.013388 | 0.059607 | -0.00097413 | 0.079476 | -58.3786 | 62.1277 | -61.6882 | -61.5463 | 54.4144 | 22.7234 | 6.871 | 6.1111 | 62.1231 | -61.702 | -0.29755 | -0.01831 | 3.0121 | -0.15564 | -7.7316 | -0.31128 | -0.022888 | 3.3096 | 68.2617 | 67.5018 | 115.8051 | 123.5184 | 3.0121 | 123.5138 | 84.1141 | -0.31128 | 123.5184 | 3.0121 | 84.1141 | 115.8051 | 123.5138 | -123.8342 | -123.848
3292.7188 | 123.88 | -61.3953 | 62.1826 | 0.13603 | 0.016238 | 0.013413 | 0.014669 | 0.061743 | -0.0016149 | 0.080331 | -58.4152 | 62.1506 | -61.7111 | -61.5372 | 54.3915 | 22.6913 | 6.9489 | 6.2347 | 62.1414 | -61.6974 | -0.31586 | -0.032043 | 2.98 | -0.14191 | -7.7911 | -0.30212 | -0.041199 | 3.2959 | 68.3441 | 67.63 | 115.7867 | 123.5458 | 2.98 | 123.5367 | 84.0866 | -0.30212 | 123.5458 | 2.98 | 84.0866 | 115.7867 | 123.5367 | -123.8937 | -123.88
3293.7188 | 123.8434 | -61.3998 | 62.2009 | 0.63194 | 0.014315 | 0.011064 | 0.0089016 | 0.058966 | 0.0026575 | 0.080544 | -58.4518 | 62.1277 | -61.6882 | -61.5967 | 54.364 | 22.6318 | 7.1045 | 6.3766 | 62.1506 | -61.702 | -0.28839 | -0.073242 | 2.948 | -0.19684 | -7.8369 | -0.30212 | -0.050354 | 3.2364 | 68.5043 | 67.7765 | 115.7639 | 123.5275 | 2.948 | 123.5504 | 84.0317 | -0.30212 | 123.5275 | 2.948 | 84.0317 | 115.7639 | 123.5504 | -123.8892 | -123.9029
3294.7188 | 123.8297 | -61.4136 | 62.1414 | 0.15892 | 0.017092 | 0.015336 | 0.014883 | 0.062812 | 0.00030767 | 0.079904 | -58.3832 | 62.1185 | -61.6837 | -61.5326 | 54.4052 | 22.6639 | 6.9626 | 6.34 | 62.1552 | -61.6791 | -0.27008 | -0.022888 | 3.0304 | -0.11902 | -7.7362 | -0.2655 | 0.013733 | 3.3005 | 68.3762 | 67.7536 | 115.8188 | 123.5321 | 3.0304 | 123.5687 | 84.0775 | -0.2655 | 123.5321 | 3.0304 | 84.0775 | 115.8188 | 123.5687 | -123.8251 | -123.8205
3295.7188 | 123.9029 | -61.4227 | 62.1414 | 0.32677 | 0.016024 | 0.015122 | 0.013388 | 0.061316 | 0.0013757 | 0.081826 | -58.3832 | 62.146 | -61.7294 | -61.528 | 54.3503 | 22.6593 | 7.0129 | 6.4865 | 62.1094 | -61.702 | -0.3067 | 0.004578 | 3.0395 | -0.10529 | -7.7911 | -0.27924 | -0.032043 | 3.3463 | 68.4357 | 67.9092 | 115.773 | 123.5687 | 3.0395 | 123.5321 | 84.082 | -0.27924 | 123.5687 | 3.0395 | 84.082 | 115.773 | 123.5321 | -123.8708 | -123.8434
3296.7188 | 123.8846 | -61.3907 | 62.1552 | 0.23521 | 0.014529 | 0.017045 | 0.010611 | 0.061103 | -0.0011877 | 0.081399 | -58.374 | 62.1094 | -61.7203 | -61.5372 | 54.3732 | 22.6273 | 6.9946 | 6.5781 | 62.1185 | -61.6928 | -0.32959 | -0.045776 | 3.0167 | -0.14648 | -7.782 | -0.30212 | -0.036621 | 3.3463 | 68.3853 | 67.9688 | 115.7639 | 123.5001 | 3.0167 | 123.5092 | 84.0179 | -0.30212 | 123.5001 | 3.0167 | 84.0179 | 115.7639 | 123.5092 | -123.8754 | -123.848
3297.7188 | 123.8709 | -61.4136 | 62.1002 | 0.18944 | 0.016024 | 0.021745 | 0.014456 | 0.062171 | -0.00054693 | 0.080117 | -58.3557 | 62.1231 | -61.702 | -61.5555 | 54.3915 | 22.6593 | 7.0312 | 6.5826 | 62.1231 | -61.702 | -0.28839 | 0.022888 | 3.0579 | -0.14191 | -7.7087 | -0.28839 | 0.022888 | 3.3463 | 68.4448 | 67.9962 | 115.8051 | 123.5367 | 3.0579 | 123.5367 | 84.0729 | -0.28839 | 123.5367 | 3.0579 | 84.0729 | 115.8051 | 123.5367 | -123.8022 | -123.8022
3298.7344 | 123.9853 | -61.3358 | 62.2284 | -0.16151 | 0.01581 | 0.0082864 | 0.0097562 | 0.060675 | -0.0018285 | 0.079904 | -58.3649 | 62.1048 | -61.6837 | -61.5005 | 54.4556 | 22.6364 | 7.164 | 6.72 | 62.1414 | -61.6608 | -0.3479 | -0.1236 | 2.9709 | -0.16479 | -7.7728 | -0.32501 | -0.086976 | 3.3188 | 68.4998 | 68.0557 | 115.7913 | 123.4406 | 2.9709 | 123.4772 | 83.9722 | -0.32501 | 123.4406 | 2.9709 | 83.9722 | 115.7913 | 123.4772 | -123.912 | -123.8892
3299.7188 | 123.8022 | -61.4227 | 62.1872 | 0.18181 | 0.016665 | 0.01555 | 0.016592 | 0.061743 | 0.00094847 | 0.07969 | -58.461 | 62.2009 | -61.702 | -61.6379 | 54.2908 | 22.4991 | 7.1823 | 6.4087 | 62.1643 | -61.7294 | -0.27924 | 0.013733 | 2.9617 | -0.21515 | -7.8964 | -0.3067 | -0.022888 | 3.241 | 68.605 | 67.8314 | 115.7135 | 123.6237 | 2.9617 | 123.587 | 83.9218 | -0.3067 | 123.6237 | 2.9617 | 83.9218 | 115.7135 | 123.587 | -123.8892 | -123.9166
3300.7188 | 123.7656 | -61.4365 | 62.1872 | -0.42854 | 0.018587 | 0.014268 | 0.016806 | 0.062812 | 0.0018031 | 0.081826 | -58.4015 | 62.2101 | -61.7294 | -61.6333 | 54.2175 | 22.4762 | 7.2327 | 6.4087 | 62.1735 | -61.7432 | -0.29297 | 0.022888 | 3.035 | -0.19684 | -7.9697 | -0.3067 | -0.013733 | 3.3279 | 68.6691 | 67.8452 | 115.654 | 123.6465 | 3.035 | 123.6099 | 83.9127 | -0.3067 | 123.6465 | 3.035 | 83.9127 | 115.654 | 123.6099 | -123.9166 | -123.9304
3301.7188 | 123.7976 | -61.4227 | 62.1826 | 0.13603 | 0.017733 | 0.02089 | 0.014883 | 0.06388 | 0.00094847 | 0.080544 | -58.4564 | 62.2101 | -61.7203 | -61.6379 | 54.2267 | 22.4899 | 7.1915 | 6.5094 | 62.1506 | -61.7523 | -0.29755 | 0.027466 | 2.9663 | -0.21515 | -7.9559 | -0.32959 | -0.032043 | 3.2639 | 68.6142 | 67.9321 | 115.6494 | 123.6328 | 2.9663 | 123.5733 | 83.9127 | -0.32959 | 123.6328 | 2.9663 | 83.9127 | 115.6494 | 123.5733 | -123.9029 | -123.9349
3302.7188 | 123.7747 | -61.4502 | 62.2055 | 0.074997 | 0.017733 | 0.016618 | 0.016592 | 0.064307 | 0.00052127 | 0.082467 | -58.4427 | 62.2238 | -61.7294 | -61.647 | 54.213 | 22.4991 | 7.2235 | 6.4453 | 62.1918 | -61.7294 | -0.27924 | 0.018311 | 3.0075 | -0.19684 | -7.9926 | -0.27924 | -0.013733 | 3.2867 | 68.6737 | 67.8955 | 115.6631 | 123.674 | 3.0075 | 123.642 | 83.9493 | -0.27924 | 123.674 | 3.0075 | 83.9493 | 115.6631 | 123.642 | -123.9349 | -123.9349
3303.7188 | 123.848 | -61.4136 | 62.1735 | 0.052109 | 0.014315 | 0.015336 | 0.0080472 | 0.060248 | 0.0011621 | 0.081185 | -58.4656 | 62.1231 | -61.6974 | -61.5921 | 54.2862 | 22.6639 | 7.1732 | 6.5323 | 62.1643 | -61.6791 | -0.28381 | -0.050354 | 2.948 | -0.17853 | -7.8873 | -0.2655 | -0.009155 | 3.2318 | 68.5867 | 67.9459 | 115.6998 | 123.5367 | 2.948 | 123.5779 | 84.0775 | -0.2655 | 123.5367 | 2.948 | 84.0775 | 115.6998 | 123.5779 | -123.8708 | -123.8525
3304.7188 | 123.8022 | -61.4319 | 62.1735 | 0.1284 | 0.019442 | 0.01555 | 0.015097 | 0.063452 | 0.0011621 | 0.080117 | -58.4564 | 62.2192 | -61.7249 | -61.647 | 54.2633 | 22.5815 | 7.2647 | 6.5094 | 62.1552 | -61.7523 | -0.29297 | 0.045776 | 2.9755 | -0.21515 | -7.9102 | -0.32043 | -0.018311 | 3.2684 | 68.6966 | 67.9413 | 115.6952 | 123.6511 | 2.9755 | 123.587 | 84.0134 | -0.32043 | 123.6511 | 2.9755 | 84.0134 | 115.6952 | 123.587 | -123.8983 | -123.9258
3305.7188 | 123.8068 | -61.4456 | 62.2009 | 0.18181 | 0.017092 | 0.017045 | 0.017233 | 0.063452 | 0.0020167 | 0.081613 | -58.4518 | 62.2284 | -61.7249 | -61.6333 | 54.2679 | 22.6135 | 7.2372 | 6.4774 | 62.2009 | -61.7386 | -0.27924 | 0.027466 | 2.9938 | -0.18768 | -7.933 | -0.29297 | 0 | 3.273 | 68.6829 | 67.923 | 115.7135 | 123.674 | 2.9938 | 123.6465 | 84.0591 | -0.29297 | 123.674 | 2.9938 | 84.0591 | 115.7135 | 123.6465 | -123.9258 | -123.9395
3306.7188 | 123.7381 | -61.4182 | 62.2009 | 0.059738 | 0.017947 | 0.017472 | 0.017019 | 0.064307 | 9.4068e-05 | 0.080972 | -58.4702 | 62.2101 | -61.7065 | -61.6745 | 54.277 | 22.4716 | 7.2327 | 6.5002 | 62.2101 | -61.7386 | -0.28839 | 0.009155 | 2.948 | -0.25635 | -7.9239 | -0.32043 | 0.009155 | 3.2364 | 68.6508 | 67.9184 | 115.6952 | 123.6282 | 2.948 | 123.6282 | 83.8898 | -0.32043 | 123.6282 | 2.948 | 83.8898 | 115.6952 | 123.6282 | -123.9075 | -123.9395
3307.7188 | 123.7747 | -61.4502 | 62.2101 | 0.029221 | 0.017733 | 0.018754 | 0.014883 | 0.06388 | -0.0016149 | 0.080117 | -58.4381 | 62.233 | -61.7249 | -61.647 | 54.3228 | 22.5449 | 7.2327 | 6.5186 | 62.2055 | -61.734 | -0.27466 | 0.022888 | 3.0121 | -0.19684 | -7.8873 | -0.28381 | -0.004578 | 3.2867 | 68.6829 | 67.9688 | 115.773 | 123.6832 | 3.0121 | 123.6557 | 83.9951 | -0.28381 | 123.6832 | 3.0121 | 83.9951 | 115.773 | 123.6557 | -123.9349 | -123.9441
3308.7188 | 123.8892 | -61.409 | 62.1506 | 0.16655 | 0.014315 | 0.014909 | 0.012106 | 0.066443 | -0.0014013 | 0.080544 | -58.3878 | 62.1323 | -61.6791 | -61.5829 | 54.3915 | 22.6639 | 6.7749 | 6.5002 | 62.1094 | -61.7203 | -0.27008 | -0.018311 | 3.0212 | -0.17395 | -7.7591 | -0.31128 | -0.041199 | 3.2913 | 68.1839 | 67.9092 | 115.8005 | 123.5413 | 3.0212 | 123.5184 | 84.0729 | -0.31128 | 123.5413 | 3.0212 | 84.0729 | 115.8005 | 123.5184 | -123.8297 | -123.8708
3309.7188 | 123.7473 | -61.4182 | 62.2101 | 0.029221 | 0.017306 | 0.018113 | 0.016592 | 0.06388 | -0.00076053 | 0.081399 | -58.4518 | 62.2192 | -61.6974 | -61.6791 | 54.2313 | 22.4304 | 7.2418 | 6.4865 | 62.2101 | -61.7615 | -0.27924 | 0.009155 | 2.9663 | -0.26093 | -7.9788 | -0.34332 | 0 | 3.2455 | 68.66 | 67.9047 | 115.6494 | 123.6374 | 2.9663 | 123.6282 | 83.8486 | -0.34332 | 123.6374 | 2.9663 | 83.8486 | 115.6494 | 123.6282 | -123.9075 | -123.9716
3310.7188 | 123.7793 | -61.4273 | 62.2009 | 0.1284 | 0.019228 | 0.018754 | 0.014883 | 0.069007 | 0.0020167 | 0.080331 | -58.5159 | 62.2467 | -61.7386 | -61.3815 | 54.3594 | 22.3892 | 7.3288 | 6.5735 | 62.2101 | -61.7249 | -0.31128 | 0.045776 | 2.9114 | 0.045776 | -7.8415 | -0.29755 | 0.009155 | 3.2227 | 68.7561 | 68.0008 | 115.7867 | 123.674 | 2.9114 | 123.6374 | 83.8165 | -0.29755 | 123.674 | 2.9114 | 83.8165 | 115.7867 | 123.6374 | -123.9395 | -123.9258
3311.7188 | 123.6237 | -61.4731 | 62.1277 | 0.052109 | 0.017519 | 0.020249 | 0.014883 | 0.063452 | -0.0011877 | 0.082894 | -58.493 | 62.2375 | -61.734 | -61.6837 | 54.2084 | 22.4213 | 7.2189 | 6.5323 | 62.1643 | -61.7935 | -0.26093 | 0.10986 | 2.98 | -0.21057 | -7.9193 | -0.32043 | 0.036621 | 3.241 | 68.692 | 68.0054 | 115.6815 | 123.7106 | 2.98 | 123.6374 | 83.8943 | -0.32043 | 123.7106 | 2.98 | 83.8943 | 115.6815 | 123.6374 | -123.8617 | -123.9212
3312.7188 | 123.7473 | -61.4319 | 62.1918 | -0.031814 | 0.018801 | 0.021104 | 0.013815 | 0.063025 | -0.0011877 | 0.080331 | -58.4885 | 62.233 | -61.7432 | -61.6974 | 54.2358 | 22.3892 | 7.2281 | 6.5323 | 62.2147 | -61.7661 | -0.31128 | 0.041199 | 2.9434 | -0.2655 | -7.9559 | -0.33417 | 0.022889 | 3.2547 | 68.66 | 67.9642 | 115.6677 | 123.6649 | 2.9434 | 123.6465 | 83.8211 | -0.33417 | 123.6649 | 2.9434 | 83.8211 | 115.6677 | 123.6465 | -123.9349 | -123.9578
3313.7188 | 123.761 | -61.4365 | 62.2192 | -0.0012969 | 0.015383 | 0.018113 | 0.014242 | 0.065802 | -0.00054693 | 0.079904 | -58.4518 | 62.2375 | -61.7432 | -61.6562 | 54.2175 | 22.4167 | 7.2784 | 6.5506 | 62.2009 | -61.7386 | -0.3067 | 0.018311 | 2.9846 | -0.21973 | -8.0017 | -0.30212 | -0.01831 | 3.2913 | 68.7149 | 67.9871 | 115.654 | 123.674 | 2.9846 | 123.6374 | 83.8531 | -0.30212 | 123.674 | 2.9846 | 83.8531 | 115.654 | 123.6374 | -123.9624 | -123.9578
3314.7188 | 123.793 | -61.4136 | 62.1964 | -0.024185 | 0.019442 | 0.01555 | 0.014029 | 0.065589 | -0.00011953 | 0.080758 | -58.3786 | 62.2421 | -61.6928 | -61.5967 | 54.2313 | 22.4533 | 7.1732 | 6.6376 | 62.233 | -61.7157 | -0.27924 | 0.045776 | 3.035 | -0.18311 | -7.9651 | -0.30212 | 0.036621 | 3.3142 | 68.5867 | 68.0511 | 115.6448 | 123.6557 | 3.035 | 123.6465 | 83.8669 | -0.30212 | 123.6557 | 3.035 | 83.8669 | 115.6448 | 123.6465 | -123.8892 | -123.912
3315.7188 | 123.7793 | -61.4502 | 62.1918 | 0.013962 | 0.020083 | 0.011704 | 0.01531 | 0.065375 | -0.00033333 | 0.081613 | -58.429 | 62.2375 | -61.7203 | -61.615 | 54.2084 | 22.4442 | 7.2235 | 6.5872 | 62.2101 | -61.7523 | -0.27008 | 0.045777 | 3.0212 | -0.16479 | -7.9834 | -0.30212 | 0.018311 | 3.2913 | 68.6737 | 68.0374 | 115.6586 | 123.6877 | 3.0212 | 123.6603 | 83.8943 | -0.30212 | 123.6877 | 3.0212 | 83.8943 | 115.6586 | 123.6603 | -123.912 | -123.9441
3316.7188 | 123.8205 | -61.4182 | 62.2055 | 0.0063326 | 0.018374 | 0.016404 | 0.013601 | 0.064948 | 0.00052127 | 0.080331 | -58.3832 | 62.2375 | -61.702 | -61.6333 | 54.1489 | 22.403 | 7.2189 | 6.5826 | 62.2009 | -61.7249 | -0.28381 | 0.032044 | 3.035 | -0.21515 | -8.0566 | -0.3067 | -0.004577 | 3.3188 | 68.6371 | 68.0008 | 115.567 | 123.6557 | 3.035 | 123.6191 | 83.8211 | -0.3067 | 123.6557 | 3.035 | 83.8211 | 115.567 | 123.6191 | -123.9075 | -123.9304
3317.7188 | 123.761 | -61.4319 | 62.2147 | 0.013962 | 0.017733 | 0.017686 | 0.014456 | 0.067511 | 0.00094847 | 0.080972 | -58.4564 | 62.2559 | -61.7249 | -61.6653 | 54.1763 | 22.4442 | 7.2647 | 6.5918 | 62.2192 | -61.7615 | -0.29297 | 0.041198 | 2.9755 | -0.23346 | -8.0383 | -0.32959 | 0.004577 | 3.2684 | 68.6966 | 68.0237 | 115.6082 | 123.6877 | 2.9755 | 123.6511 | 83.876 | -0.32959 | 123.6877 | 2.9755 | 83.876 | 115.6082 | 123.6511 | -123.9395 | -123.9761
3318.7188 | 123.8892 | -61.3953 | 62.1506 | 0.18944 | 0.013674 | 0.012773 | 0.013174 | 0.064307 | 0.00030767 | 0.081185 | -58.3878 | 62.1597 | -61.6745 | -61.5463 | 54.2313 | 22.5861 | 7.0129 | 6.6833 | 62.1506 | -61.6928 | -0.27924 | 0.009155 | 3.0075 | -0.15106 | -7.9193 | -0.29755 | 0 | 3.2867 | 68.4082 | 68.0786 | 115.6265 | 123.555 | 3.0075 | 123.5458 | 83.9813 | -0.29755 | 123.555 | 3.0075 | 83.9813 | 115.6265 | 123.5458 | -123.8251 | -123.8434
3319.7188 | 123.7747 | -61.4319 | 62.1872 | 0.013962 | 0.019015 | 0.016618 | 0.014242 | 0.064307 | 0.00052127 | 0.082894 | -58.4335 | 62.2559 | -61.7157 | -61.6425 | 54.2679 | 22.5677 | 7.2098 | 6.5964 | 62.2238 | -61.7569 | -0.28381 | 0.068664 | 2.9984 | -0.21057 | -7.9193 | -0.32501 | 0.036621 | 3.2822 | 68.6417 | 68.0283 | 115.6998 | 123.6877 | 2.9984 | 123.6557 | 83.9996 | -0.32501 | 123.6877 | 2.9984 | 83.9996 | 115.6998 | 123.6557 | -123.9029 | -123.9441
3320.7188 | 123.8205 | -61.4227 | 62.2238 | -0.069961 | 0.017306 | 0.016191 | 0.014029 | 0.065375 | 0.00030767 | 0.082681 | -58.3374 | 62.2238 | -61.7294 | -61.5967 | 54.2633 | 22.5998 | 7.1823 | 6.6467 | 62.2421 | -61.7249 | -0.3067 | 0 | 3.0853 | -0.17395 | -7.9605 | -0.30213 | 0.01831 | 3.392 | 68.605 | 68.0695 | 115.686 | 123.6465 | 3.0853 | 123.6649 | 84.0225 | -0.30213 | 123.6465 | 3.0853 | 84.0225 | 115.686 | 123.6649 | -123.9532 | -123.9487
3321.7188 | 123.8113 | -61.4044 | 62.1918 | -0.10048 | 0.017306 | 0.020249 | 0.013174 | 0.063666 | -0.00011953 | 0.083322 | -58.3923 | 62.2421 | -61.6928 | -61.5738 | 54.2679 | 22.5815 | 7.0496 | 6.6879 | 62.2009 | -61.734 | -0.28839 | 0.050354 | 3.0121 | -0.16937 | -7.9239 | -0.32959 | 0.009156 | 3.3005 | 68.454 | 68.0923 | 115.6723 | 123.6465 | 3.0121 | 123.6053 | 83.9859 | -0.32959 | 123.6465 | 3.0121 | 83.9859 | 115.6723 | 123.6053 | -123.8846 | -123.9258
3322.7188 | 123.7976 | -61.4273 | 62.1964 | -0.039444 | 0.019015 | 0.016191 | 0.015524 | 0.062598 | -0.0016149 | 0.080972 | -58.3878 | 62.233 | -61.6882 | -61.6196 | 54.2038 | 22.6135 | 7.3059 | 6.6925 | 62.2192 | -61.7432 | -0.26093 | 0.036621 | 3.0396 | -0.19226 | -7.9926 | -0.31586 | 0.022888 | 3.3005 | 68.7332 | 68.1198 | 115.6311 | 123.6603 | 3.0396 | 123.6465 | 84.0408 | -0.31586 | 123.6603 | 3.0396 | 84.0408 | 115.6311 | 123.6465 | -123.8846 | -123.9395
3323.7188 | 123.8617 | -61.4319 | 62.1643 | 0.22758 | 0.018587 | 0.013841 | 0.011465 | 0.064521 | 0.0026575 | 0.079904 | -58.461 | 62.1826 | -61.7065 | -61.6196 | 54.2587 | 22.5677 | 7.1045 | 6.72 | 62.2055 | -61.7294 | -0.27466 | 0.01831 | 2.9709 | -0.18768 | -7.9056 | -0.29755 | 0.041198 | 3.2455 | 68.5364 | 68.1519 | 115.6906 | 123.6145 | 2.9709 | 123.6374 | 83.9996 | -0.29755 | 123.6145 | 2.9709 | 83.9996 | 115.6906 | 123.6374 | -123.8709 | -123.8937
3324.7188 | 123.8022 | -61.4456 | 62.1964 | -0.039444 | 0.018374 | 0.016831 | 0.01531 | 0.064307 | -0.0016149 | 0.083749 | -58.4061 | 62.2238 | -61.7065 | -61.6196 | 54.213 | 22.5128 | 7.2235 | 6.6284 | 62.2147 | -61.7706 | -0.26093 | 0.027466 | 3.0396 | -0.17395 | -7.9834 | -0.32501 | 0.018311 | 3.3005 | 68.6691 | 68.074 | 115.6586 | 123.6694 | 3.0396 | 123.6603 | 83.9584 | -0.32501 | 123.6694 | 3.0396 | 83.9584 | 115.6586 | 123.6603 | -123.9029 | -123.967
3325.7188 | 123.793 | -61.4136 | 62.1689 | -0.062332 | 0.017092 | 0.015122 | 0.014456 | 0.065802 | 0.0024439 | 0.080972 | -58.4152 | 62.2513 | -61.6928 | -61.6013 | 54.2542 | 22.6868 | 7.1777 | 6.6467 | 62.2055 | -61.7477 | -0.27924 | 0.082398 | 2.9984 | -0.18768 | -7.9147 | -0.33417 | 0.036621 | 3.2776 | 68.5913 | 68.0603 | 115.6677 | 123.6649 | 2.9984 | 123.6191 | 84.1003 | -0.33417 | 123.6649 | 2.9984 | 84.1003 | 115.6677 | 123.6191 | -123.8617 | -123.9166
3326.7188 | 123.8159 | -61.441 | 62.2101 | -0.024185 | 0.014956 | 0.021958 | 0.014883 | 0.063452 | 0.00073487 | 0.080758 | -58.4244 | 62.2147 | -61.6928 | -61.6013 | 54.2862 | 22.5906 | 7.1869 | 6.6788 | 62.2238 | -61.7203 | -0.25177 | 0.004578 | 3.0167 | -0.16022 | -7.9239 | -0.27924 | 0.013733 | 3.2684 | 68.6279 | 68.1198 | 115.7272 | 123.6557 | 3.0167 | 123.6649 | 84.0317 | -0.27924 | 123.6557 | 3.0167 | 84.0317 | 115.7272 | 123.6649 | -123.9029 | -123.9304
3327.7188 | 123.8068 | -61.3998 | 62.2238 | -0.08522 | 0.016238 | 0.012559 | 0.013601 | 0.065589 | 9.4068e-05 | 0.080758 | -58.3923 | 62.2375 | -61.702 | -61.5921 | 54.3411 | 22.6364 | 7.2098 | 6.7337 | 62.2101 | -61.7065 | -0.30212 | 0.013733 | 3.0075 | -0.19226 | -7.8827 | -0.3067 | -0.013733 | 3.3096 | 68.6096 | 68.1335 | 115.741 | 123.6374 | 3.0075 | 123.6099 | 84.0363 | -0.3067 | 123.6374 | 3.0075 | 84.0363 | 115.741 | 123.6099 | -123.9258 | -123.9304
3328.7188 | 123.7518 | -61.4594 | 62.1872 | 2.5393 | 0.017092 | 0.011704 | 0.011465 | 0.063666 | 0.00094847 | 0.080972 | -58.4793 | 62.1964 | -61.7569 | -61.6745 | 54.245 | 22.5403 | 7.2189 | 6.633 | 62.2192 | -61.734 | -0.29755 | 0.009155 | 2.98 | -0.21515 | -7.9422 | -0.27466 | 0.032043 | 3.2776 | 68.6783 | 68.0923 | 115.7043 | 123.6557 | 2.98 | 123.6786 | 83.9996 | -0.27466 | 123.6557 | 2.98 | 83.9996 | 115.7043 | 123.6786 | -123.9441 | -123.9212
3329.7188 | 123.7839 | -61.4273 | 62.1735 | -0.054703 | 0.016238 | 0.017899 | 0.013601 | 0.065802 | -0.00054693 | 0.082467 | -58.4106 | 62.2559 | -61.6928 | -61.5921 | 54.2908 | 22.5906 | 7.283 | 6.7337 | 62.2284 | -61.734 | -0.2655 | 0.082397 | 3.0167 | -0.16479 | -7.8827 | -0.3067 | 0.054932 | 3.2822 | 68.7103 | 68.161 | 115.7181 | 123.6832 | 3.0167 | 123.6557 | 84.0179 | -0.3067 | 123.6832 | 3.0167 | 84.0179 | 115.7181 | 123.6557 | -123.8663 | -123.9075
3330.7188 | 123.8205 | -61.4365 | 62.2284 | -0.08522 | 0.016024 | 0.015763 | 0.01232 | 0.064521 | 0.00030767 | 0.082467 | -58.4061 | 62.2513 | -61.702 | -61.6058 | 54.3503 | 22.6547 | 7.2281 | 6.7383 | 62.2467 | -61.7294 | -0.2655 | 0.022888 | 3.0304 | -0.16937 | -7.8781 | -0.29297 | 0.01831 | 3.2959 | 68.6645 | 68.1747 | 115.7867 | 123.6877 | 3.0304 | 123.6832 | 84.0912 | -0.29297 | 123.6877 | 3.0304 | 84.0912 | 115.7867 | 123.6832 | -123.9304 | -123.9578
3331.7188 | 123.8434 | -61.409 | 62.2055 | -0.11574 | 0.019015 | 0.018113 | 0.015524 | 0.06388 | 0.0013757 | 0.078835 | -58.58 | 62.2101 | -61.7569 | -61.6058 | 54.3732 | 22.6685 | 7.2052 | 6.7062 | 62.2284 | -61.7157 | -0.3479 | 0.004578 | 2.829 | -0.19684 | -7.8323 | -0.3067 | 0.022889 | 3.1769 | 68.6142 | 68.1152 | 115.7822 | 123.6191 | 2.829 | 123.6374 | 84.0775 | -0.3067 | 123.6191 | 2.829 | 84.0775 | 115.7822 | 123.6374 | -123.9624 | -123.9212
3332.7188 | 123.7885 | -61.4227 | 62.2147 | -0.08522 | 0.017519 | 0.01854 | 0.014242 | 0.064521 | 0.0024439 | 0.080758 | -58.4335 | 62.2192 | -61.6974 | -61.6058 | 54.2816 | 22.6776 | 6.9763 | 6.6788 | 62.2055 | -61.7294 | -0.27466 | 0.004577 | 2.9892 | -0.18311 | -7.933 | -0.3067 | -0.009156 | 3.2639 | 68.399 | 68.1015 | 115.7043 | 123.642 | 2.9892 | 123.6282 | 84.1003 | -0.3067 | 123.642 | 2.9892 | 84.1003 | 115.7043 | 123.6282 | -123.912 | -123.9441
3333.7188 | 123.8709 | -61.4182 | 62.1506 | 0.16655 | 0.015383 | 0.016404 | 0.0074062 | 0.065589 | 0.00094847 | 0.079904 | -58.3923 | 62.1414 | -61.7065 | -61.5875 | 54.3823 | 22.728 | 7.0679 | 6.8436 | 62.1826 | -61.702 | -0.28839 | -0.009156 | 3.0258 | -0.16937 | -7.7683 | -0.28381 | 0.032043 | 3.3142 | 68.486 | 68.2617 | 115.8005 | 123.5596 | 3.0258 | 123.6008 | 84.1461 | -0.28381 | 123.5596 | 3.0258 | 84.1461 | 115.8005 | 123.6008 | -123.8571 | -123.8525
3334.7188 | 123.8113 | -61.4136 | 62.2559 | -0.15388 | 0.017306 | 0.018754 | 0.01232 | 0.062384 | -0.0016149 | 0.080972 | -58.4518 | 62.2467 | -61.6882 | -61.615 | 54.2953 | 22.6318 | 7.1411 | 6.1615 | 62.2421 | -61.7477 | -0.27466 | -0.009155 | 2.9617 | -0.20142 | -7.9605 | -0.33417 | -0.013733 | 3.2364 | 68.5547 | 67.5751 | 115.7089 | 123.6603 | 2.9617 | 123.6557 | 84.0454 | -0.33417 | 123.6603 | 2.9617 | 84.0454 | 115.7089 | 123.6557 | -123.9441 | -124.0036
3335.7188 | 123.793 | -61.4182 | 62.2421 | -0.1844 | 0.017733 | 0.016191 | 0.011465 | 0.06388 | -0.0014013 | 0.080972 | -58.4427 | 62.2559 | -61.702 | -61.6287 | 54.2908 | 22.5906 | 7.1091 | 6.1386 | 62.2604 | -61.7249 | -0.28381 | 0.013733 | 2.9755 | -0.21057 | -7.9514 | -0.3067 | 0.018311 | 3.2593 | 68.5272 | 67.5568 | 115.7089 | 123.674 | 2.9755 | 123.6786 | 84.0088 | -0.3067 | 123.674 | 2.9755 | 84.0088 | 115.7089 | 123.6786 | -123.9441 | -123.967
3336.7188 | 123.8297 | -61.409 | 62.2238 | -0.11574 | 0.018587 | 0.01854 | 0.012533 | 0.06388 | 0.0013757 | 0.082253 | -58.4518 | 62.2421 | -61.7157 | -61.5921 | 54.277 | 22.6044 | 7.0724 | 6.221 | 62.2559 | -61.7386 | -0.3067 | 0.01831 | 2.9572 | -0.1831 | -7.9468 | -0.32959 | 0.032043 | 3.2639 | 68.4814 | 67.63 | 115.686 | 123.6511 | 2.9572 | 123.6649 | 84.0134 | -0.32959 | 123.6511 | 2.9572 | 84.0134 | 115.686 | 123.6649 | -123.9395 | -123.9624
3337.7188 | 123.8297 | -61.4227 | 62.2375 | -0.22255 | 0.017092 | 0.011704 | 0.014669 | 0.063452 | -0.0011877 | 0.081826 | -58.4702 | 62.2284 | -61.6974 | -61.5967 | 54.3823 | 22.6456 | 7.1503 | 6.2393 | 62.2467 | -61.7157 | -0.27466 | -0.009155 | 2.9526 | -0.17395 | -7.8552 | -0.29297 | 0.009155 | 3.2272 | 68.573 | 67.662 | 115.8051 | 123.6511 | 2.9526 | 123.6694 | 84.0683 | -0.29297 | 123.6511 | 2.9526 | 84.0683 | 115.8051 | 123.6694 | -123.9349 | -123.9532
3338.7344 | 123.8251 | -61.4273 | 62.1643 | 0.22758 | 0.018374 | 0.015977 | 0.011038 | 0.065161 | 0.0030847 | 0.081399 | -58.4885 | 62.2009 | -61.7569 | -61.6333 | 54.332 | 22.6318 | 6.9992 | 6.2347 | 62.1918 | -61.7157 | -0.32959 | 0.036621 | 2.9388 | -0.20599 | -7.8323 | -0.28839 | 0.027465 | 3.2684 | 68.4265 | 67.662 | 115.7593 | 123.6282 | 2.9388 | 123.6191 | 84.0591 | -0.28839 | 123.6282 | 2.9388 | 84.0591 | 115.7593 | 123.6191 | -123.9212 | -123.88
3339.7188 | 123.8297 | -61.4227 | 62.2284 | -0.27596 | 0.014101 | 0.012132 | 0.014669 | 0.062598 | -0.0018285 | 0.079476 | -58.4518 | 62.233 | -61.7065 | -61.5921 | 54.3091 | 22.6364 | 7.3013 | 6.7612 | 62.2375 | -61.7523 | -0.28381 | 0.004577 | 2.9709 | -0.16937 | -7.9193 | -0.32959 | 0.009155 | 3.2547 | 68.7241 | 68.1839 | 115.7318 | 123.6557 | 2.9709 | 123.6603 | 84.0591 | -0.32959 | 123.6557 | 2.9709 | 84.0591 | 115.7318 | 123.6603 | -123.9349 | -123.9807
3340.7188 | 123.8159 | -61.4273 | 62.2238 | -0.15388 | 0.015383 | 0.012345 | 0.012747 | 0.062384 | 0.00030767 | 0.080331 | -58.461 | 62.2467 | -61.7157 | -61.5967 | 54.3549 | 22.7188 | 7.3105 | 6.7383 | 62.2467 | -61.7111 | -0.28839 | 0.022888 | 2.9663 | -0.16937 | -7.869 | -0.28381 | 0.022888 | 3.2547 | 68.7378 | 68.1656 | 115.7822 | 123.674 | 2.9663 | 123.674 | 84.1461 | -0.28381 | 123.674 | 2.9663 | 84.1461 | 115.7822 | 123.674 | -123.9395 | -123.9349
3341.7188 | 123.7701 | -61.4319 | 62.2192 | -0.28358 | 0.01581 | 0.014909 | 0.0074062 | 0.060462 | 0.0018031 | 0.080758 | -58.4702 | 62.2421 | -61.702 | -61.7706 | 54.213 | 22.6776 | 7.3288 | 6.6879 | 62.2559 | -61.7432 | -0.27008 | 0.022888 | 2.9617 | -0.33874 | -8.0063 | -0.31128 | 0.036621 | 3.2318 | 68.7607 | 68.1198 | 115.6448 | 123.674 | 2.9617 | 123.6877 | 84.1095 | -0.31128 | 123.674 | 2.9617 | 84.1095 | 115.6448 | 123.6877 | -123.9212 | -123.9624
3342.7188 | 123.7885 | -61.409 | 62.265 | -0.23018 | 0.014956 | 0.0132 | 0.0084744 | 0.063025 | 0.0018031 | 0.080117 | -58.4839 | 62.2421 | -61.7294 | -61.6196 | 54.2908 | 22.6547 | 7.3654 | 6.72 | 62.2559 | -61.7111 | -0.32043 | -0.022889 | 2.9251 | -0.21057 | -7.9742 | -0.30212 | -0.009156 | 3.2455 | 68.7744 | 68.129 | 115.6998 | 123.6511 | 2.9251 | 123.6649 | 84.0637 | -0.30212 | 123.6511 | 2.9251 | 84.0637 | 115.6998 | 123.6649 | -123.9944 | -123.9761
3343.7188 | 123.7793 | -61.409 | 62.2147 | -0.031814 | 0.017092 | 0.013413 | 0.016378 | 0.064521 | 0.00073487 | 0.079904 | -58.3923 | 62.2147 | -61.7157 | -61.5967 | 54.3228 | 22.5998 | 7.0999 | 6.2073 | 62.2284 | -61.7111 | -0.3067 | 0 | 3.0167 | -0.18768 | -7.8918 | -0.30212 | 0.013733 | 3.3234 | 68.5089 | 67.6163 | 115.7318 | 123.6237 | 3.0167 | 123.6374 | 84.0088 | -0.30212 | 123.6237 | 3.0167 | 84.0088 | 115.7318 | 123.6374 | -123.9304 | -123.9258
3344.7344 | 123.9624 | -61.4044 | 62.1735 | 0.19707 | 0.01346 | 0.016404 | 0.0099698 | 0.064521 | -0.00076053 | 0.081185 | -58.4244 | 62.146 | -61.6974 | -61.5738 | 54.3457 | 22.641 | 6.9031 | 6.0974 | 62.146 | -61.7157 | -0.29297 | -0.027466 | 2.98 | -0.16937 | -7.8278 | -0.31128 | -0.027466 | 3.273 | 68.3075 | 67.5018 | 115.7501 | 123.5504 | 2.98 | 123.5504 | 84.0454 | -0.31128 | 123.5504 | 2.98 | 84.0454 | 115.7501 | 123.5504 | -123.8708 | -123.8892
3345.7188 | 123.793 | -61.4136 | 62.2101 | -0.20729 | 0.017519 | 0.016618 | 0.014029 | 0.062598 | 0.0018031 | 0.080972 | -58.461 | 62.2284 | -61.7249 | -61.6058 | 54.3274 | 22.6639 | 7.2006 | 6.2942 | 62.2238 | -61.7249 | -0.31128 | 0.018311 | 2.9526 | -0.19226 | -7.8827 | -0.31128 | 0.013733 | 3.2639 | 68.6142 | 67.7078 | 115.741 | 123.642 | 2.9526 | 123.6374 | 84.0775 | -0.31128 | 123.642 | 2.9526 | 84.0775 | 115.741 | 123.6374 | -123.9349 | -123.9349
3346.7188 | 123.8205 | -61.4227 | 62.2147 | -0.23018 | 0.017092 | 0.013627 | 0.011038 | 0.061743 | 0.00030767 | 0.078408 | -58.4747 | 62.2375 | -61.7203 | -61.615 | 54.2679 | 22.641 | 7.3792 | 6.8207 | 62.2467 | -61.7157 | -0.29755 | 0.022888 | 2.948 | -0.19226 | -7.9468 | -0.29297 | 0.032043 | 3.2455 | 68.8019 | 68.2434 | 115.6906 | 123.6603 | 2.948 | 123.6694 | 84.0637 | -0.29297 | 123.6603 | 2.948 | 84.0637 | 115.6906 | 123.6694 | -123.9349 | -123.9304
3347.7188 | 123.793 | -61.4227 | 62.2009 | -0.0012969 | 0.016451 | 0.018327 | 0.011465 | 0.063025 | -0.00011953 | 0.076913 | -58.5342 | 62.2147 | -61.734 | -61.6333 | 54.2038 | 22.5815 | 7.3608 | 6.7337 | 62.265 | -61.7294 | -0.31128 | 0.013733 | 2.8885 | -0.21057 | -7.9971 | -0.3067 | 0.064087 | 3.1998 | 68.7836 | 68.1564 | 115.6265 | 123.6374 | 2.8885 | 123.6877 | 84.0042 | -0.3067 | 123.6374 | 2.8885 | 84.0042 | 115.6265 | 123.6877 | -123.9349 | -123.9304
3348.7188 | 123.8205 | -61.4365 | 62.2238 | -0.10048 | 0.017733 | 0.018754 | 0.015097 | 0.064948 | 9.4068e-05 | 0.079263 | -58.4015 | 62.2055 | -61.7157 | -61.5784 | 54.213 | 22.7463 | 7.2876 | 6.7795 | 62.2375 | -61.7111 | -0.27924 | -0.018311 | 3.035 | -0.14191 | -8.0109 | -0.27466 | 0.013733 | 3.3142 | 68.7241 | 68.2159 | 115.6494 | 123.642 | 3.035 | 123.674 | 84.1827 | -0.27466 | 123.642 | 3.035 | 84.1827 | 115.6494 | 123.674 | -123.9395 | -123.9349
3349.7188 | 123.7564 | -61.4319 | 62.2101 | 0.052109 | 0.017519 | 0.018113 | 0.014669 | 0.065589 | -0.00033333 | 0.07969 | -58.4518 | 62.2147 | -61.7065 | -61.6196 | 54.2358 | 22.6593 | 7.2693 | 6.6971 | 62.2238 | -61.7249 | -0.27466 | 0.004578 | 2.98 | -0.18768 | -7.9742 | -0.29297 | 0.013733 | 3.2547 | 68.7012 | 68.129 | 115.6677 | 123.6465 | 2.98 | 123.6557 | 84.0912 | -0.29297 | 123.6465 | 2.98 | 84.0912 | 115.6677 | 123.6557 | -123.9166 | -123.9349
3350.7188 | 123.7564 | -61.4182 | 62.2192 | -0.1844 | 0.014101 | 0.016191 | 0.0050564 | 0.064093 | -0.0014013 | 0.080331 | -58.5205 | 62.2375 | -61.7065 | -61.7157 | 54.2404 | 22.6959 | 7.3654 | 6.7749 | 62.2375 | -61.702 | -0.28839 | 0.018311 | 2.8976 | -0.29755 | -7.9788 | -0.28381 | 0.018311 | 3.186 | 68.7836 | 68.1931 | 115.6586 | 123.6557 | 2.8976 | 123.6557 | 84.1141 | -0.28381 | 123.6557 | 2.8976 | 84.1141 | 115.6586 | 123.6557 | -123.9258 | -123.9212
3351.7188 | 123.7518 | -61.4136 | 62.2101 | -0.27596 | 0.017092 | 0.016191 | 0.011038 | 0.061957 | -0.00097413 | 0.078835 | -58.4976 | 62.2101 | -61.7157 | -61.6882 | 54.3457 | 22.7417 | 7.164 | 6.5643 | 62.2467 | -61.7065 | -0.30212 | 0 | 2.916 | -0.27466 | -7.8644 | -0.29297 | 0.036621 | 3.2181 | 68.5776 | 67.9779 | 115.7593 | 123.6237 | 2.916 | 123.6603 | 84.1553 | -0.29297 | 123.6237 | 2.916 | 84.1553 | 115.7593 | 123.6603 | -123.9258 | -123.9166
3352.7188 | 123.7976 | -61.4227 | 62.2421 | -0.23018 | 0.01816 | 0.012986 | 0.013815 | 0.062171 | -0.0011877 | 0.080544 | -58.4747 | 62.2147 | -61.7111 | -61.6241 | 54.2908 | 22.5769 | 7.3334 | 6.6238 | 62.2604 | -61.7111 | -0.28839 | -0.027465 | 2.948 | -0.20142 | -7.9514 | -0.28839 | 0.018311 | 3.2364 | 68.7561 | 68.0466 | 115.7135 | 123.6374 | 2.948 | 123.6832 | 83.9996 | -0.28839 | 123.6374 | 2.948 | 83.9996 | 115.7135 | 123.6832 | -123.9532 | -123.9532
3353.7188 | 123.8113 | -61.409 | 62.1918 | -0.054703 | 0.017733 | 0.019395 | 0.014029 | 0.063452 | -0.0020421 | 0.080117 | -58.4427 | 62.2467 | -61.7111 | -61.6013 | 54.2587 | 22.5998 | 7.2418 | 6.6238 | 62.233 | -61.7249 | -0.30212 | 0.054932 | 2.9663 | -0.19226 | -7.933 | -0.31586 | 0.041199 | 3.2684 | 68.6508 | 68.0328 | 115.6677 | 123.6557 | 2.9663 | 123.642 | 84.0088 | -0.31586 | 123.6557 | 2.9663 | 84.0088 | 115.6677 | 123.642 | -123.9029 | -123.9166
3354.7344 | 123.912 | -61.4182 | 62.1643 | 0.18181 | 0.014315 | 0.015122 | 0.012533 | 0.064948 | -0.00097413 | 0.081613 | -58.4427 | 62.1552 | -61.7386 | -61.5738 | 54.2725 | 22.6227 | 7.0633 | 6.6742 | 62.1872 | -61.6882 | -0.32043 | -0.009156 | 2.9755 | -0.15564 | -7.8918 | -0.27008 | 0.022888 | 3.2959 | 68.4814 | 68.0923 | 115.6906 | 123.5733 | 2.9755 | 123.6053 | 84.0408 | -0.27008 | 123.5733 | 2.9755 | 84.0408 | 115.6906 | 123.6053 | -123.9029 | -123.8525
3355.7188 | 123.7747 | -61.4227 | 62.233 | -0.34462 | 0.016878 | 0.010636 | 0.0084744 | 0.063025 | -0.00011953 | 0.081613 | -58.4793 | 62.2147 | -61.6699 | -61.6241 | 54.3137 | 22.6685 | 7.0816 | 6.0745 | 62.2604 | -61.7065 | -0.24719 | -0.01831 | 2.9434 | -0.20142 | -7.9193 | -0.28381 | 0.027466 | 3.1906 | 68.5043 | 67.4973 | 115.7364 | 123.6374 | 2.9434 | 123.6832 | 84.0912 | -0.28381 | 123.6374 | 2.9434 | 84.0912 | 115.7364 | 123.6832 | -123.9029 | -123.9395
3356.7188 | 123.7427 | -61.4319 | 62.233 | -0.23781 | 0.014956 | 0.012773 | 0.010611 | 0.063025 | 9.4068e-05 | 0.083962 | -58.461 | 62.2055 | -61.6974 | -61.615 | 54.2816 | 22.641 | 7.0541 | 6.0974 | 62.2513 | -61.7065 | -0.2655 | -0.027466 | 2.9709 | -0.1831 | -7.9514 | -0.27466 | 0.018311 | 3.2364 | 68.486 | 67.5293 | 115.7135 | 123.6374 | 2.9709 | 123.6832 | 84.0729 | -0.27466 | 123.6374 | 2.9709 | 84.0729 | 115.7135 | 123.6832 | -123.9304 | -123.9395
3357.7188 | 123.7885 | -61.4273 | 62.2192 | -0.24544 | 0.016238 | 0.01555 | 0.016378 | 0.060462 | -0.00054693 | 0.079263 | -58.6121 | 62.233 | -61.6608 | -61.6562 | 54.2358 | 22.5677 | 7.0999 | 6.1386 | 62.2284 | -61.7111 | -0.23346 | 0.013733 | 2.8152 | -0.22888 | -7.9834 | -0.28381 | 0.009156 | 3.0487 | 68.5272 | 67.5659 | 115.6631 | 123.6603 | 2.8152 | 123.6557 | 83.9951 | -0.28381 | 123.6603 | 2.8152 | 83.9951 | 115.6631 | 123.6557 | -123.88 | -123.9304
3358.7188 | 123.8068 | -61.4273 | 62.2009 | -0.0089264 | 0.016024 | 0.011704 | 0.014242 | 0.064521 | -0.00054693 | 0.079904 | -58.4381 | 62.233 | -61.7157 | -61.615 | 54.2358 | 22.5998 | 7.0312 | 6.189 | 62.2238 | -61.7111 | -0.28839 | 0.032043 | 2.9892 | -0.18768 | -7.9651 | -0.28381 | 0.022888 | 3.2776 | 68.4586 | 67.6163 | 115.6631 | 123.6603 | 2.9892 | 123.6511 | 84.0271 | -0.28381 | 123.6603 | 2.9892 | 84.0271 | 115.6631 | 123.6511 | -123.9166 | -123.912
3359.7188 | 123.7701 | -61.4273 | 62.2238 | 0.04448 | 0.018374 | 0.019395 | 0.013815 | 0.064521 | -0.0020421 | 0.080331 | -58.4885 | 62.2055 | -61.7249 | -61.6653 | 54.2267 | 22.673 | 7.0724 | 6.1249 | 62.2101 | -61.7157 | -0.29755 | -0.018311 | 2.9388 | -0.23804 | -7.9971 | -0.28839 | -0.013733 | 3.2364 | 68.4998 | 67.5522 | 115.654 | 123.6328 | 2.9388 | 123.6374 | 84.1003 | -0.28839 | 123.6328 | 2.9388 | 84.1003 | 115.654 | 123.6374 | -123.9487 | -123.9395
3360.7188 | 123.8068 | -61.4273 | 62.233 | -0.17677 | 0.016024 | 0.015336 | 0.010397 | 0.063452 | -0.0016149 | 0.082681 | -58.4656 | 62.2238 | -61.7249 | -61.6104 | 54.2542 | 22.6181 | 7.0633 | 6.1935 | 62.2559 | -61.702 | -0.29755 | -0.009155 | 2.9617 | -0.18311 | -7.9788 | -0.27466 | 0.022888 | 3.2593 | 68.4906 | 67.6208 | 115.6815 | 123.6511 | 2.9617 | 123.6832 | 84.0454 | -0.27466 | 123.6511 | 2.9617 | 84.0454 | 115.6815 | 123.6832 | -123.9578 | -123.9349
3361.7188 | 123.8251 | -61.4136 | 62.2055 | -0.17677 | 0.016238 | 0.015763 | 0.011465 | 0.06388 | -0.0024695 | 0.07969 | -58.4381 | 62.2559 | -61.6974 | -61.5509 | 54.2725 | 22.6868 | 7.0953 | 6.3126 | 62.2284 | -61.6928 | -0.28381 | 0.050354 | 2.9755 | -0.13733 | -7.933 | -0.27924 | 0.022889 | 3.2593 | 68.5089 | 67.7261 | 115.686 | 123.6694 | 2.9755 | 123.642 | 84.1003 | -0.27924 | 123.6694 | 2.9755 | 84.1003 | 115.686 | 123.642 | -123.9029 | -123.8983
3362.7188 | 123.7793 | -61.409 | 62.2467 | -0.29884 | 0.016024 | 0.014482 | 0.0063382 | 0.063239 | 0.0018031 | 0.082253 | -58.4885 | 62.1964 | -61.7065 | -61.6013 | 54.245 | 22.7234 | 7.1365 | 6.2668 | 62.2833 | -61.702 | -0.29755 | -0.050354 | 2.9205 | -0.19226 | -8.0017 | -0.29297 | 0.036621 | 3.2181 | 68.5455 | 67.6758 | 115.654 | 123.6053 | 2.9205 | 123.6923 | 84.1324 | -0.29297 | 123.6053 | 2.9205 | 84.1324 | 115.654 | 123.6923 | -123.9532 | -123.9487
3363.7188 | 123.8113 | -61.4319 | 62.2055 | -0.09285 | 0.016665 | 0.016404 | 0.014456 | 0.063239 | -0.0020421 | 0.079476 | -58.4335 | 62.233 | -61.6882 | -61.5784 | 54.3182 | 22.7097 | 7.1182 | 6.3538 | 62.2284 | -61.7294 | -0.25635 | 0.027466 | 2.9984 | -0.14648 | -7.8873 | -0.29755 | 0.022889 | 3.2547 | 68.5501 | 67.7856 | 115.7501 | 123.6649 | 2.9984 | 123.6603 | 84.1415 | -0.29755 | 123.6649 | 2.9984 | 84.1415 | 115.7501 | 123.6603 | -123.8937 | -123.9349
3364.7188 | 123.7747 | -61.4319 | 62.2467 | -0.016556 | 0.016665 | 0.014054 | 0.012533 | 0.06388 | -0.0018285 | 0.083322 | -58.4656 | 62.2284 | -61.7294 | -61.6287 | 54.2953 | 22.6089 | 7.1503 | 6.2164 | 62.2696 | -61.6974 | -0.29755 | -0.01831 | 2.9663 | -0.19684 | -7.9514 | -0.2655 | 0.022888 | 3.2639 | 68.5822 | 67.6483 | 115.7272 | 123.6603 | 2.9663 | 123.7015 | 84.0408 | -0.2655 | 123.6603 | 2.9663 | 84.0408 | 115.7272 | 123.7015 | -123.9761 | -123.9441
3365.7188 | 123.8159 | -61.4182 | 62.2192 | -0.13863 | 0.016665 | 0.019608 | 0.014669 | 0.063666 | 0.00073487 | 0.080117 | -58.4473 | 62.2467 | -61.6974 | -61.5784 | 54.245 | 22.6181 | 7.0816 | 6.2164 | 62.2604 | -61.7065 | -0.27924 | 0.027466 | 2.9709 | -0.16022 | -7.9742 | -0.28839 | 0.041199 | 3.2501 | 68.4998 | 67.6346 | 115.6631 | 123.6649 | 2.9709 | 123.6786 | 84.0363 | -0.28839 | 123.6649 | 2.9709 | 84.0363 | 115.6631 | 123.6786 | -123.9166 | -123.9258
3366.7188 | 123.8205 | -61.4319 | 62.2238 | -0.19966 | 0.015597 | 0.015977 | 0.013601 | 0.062812 | 0.00052127 | 0.082253 | -58.429 | 62.2513 | -61.7065 | -61.5784 | 54.2816 | 22.6913 | 7.0816 | 6.2347 | 62.233 | -61.702 | -0.27466 | 0.027466 | 3.0029 | -0.14648 | -7.9422 | -0.27008 | 0.009155 | 3.2776 | 68.5135 | 67.6666 | 115.7135 | 123.6832 | 3.0029 | 123.6649 | 84.1232 | -0.27008 | 123.6832 | 3.0029 | 84.1232 | 115.7135 | 123.6649 | -123.9304 | -123.9258
3367.7188 | 123.8068 | -61.4136 | 62.2238 | -0.20729 | 0.016878 | 0.014054 | 0.013388 | 0.063239 | 0.0013757 | 0.080544 | -58.4427 | 62.2467 | -61.6974 | -61.5829 | 54.3045 | 22.7051 | 7.0816 | 6.2027 | 62.2559 | -61.7157 | -0.28381 | 0.022888 | 2.9709 | -0.16937 | -7.9193 | -0.30212 | 0.032043 | 3.2547 | 68.4952 | 67.6163 | 115.7181 | 123.6603 | 2.9709 | 123.6694 | 84.1187 | -0.30212 | 123.6603 | 2.9709 | 84.1187 | 115.7181 | 123.6694 | -123.9212 | -123.9395
3368.7188 | 123.9166 | -61.4273 | 62.1918 | -0.062332 | 0.01816 | 0.014054 | 0.014456 | 0.065375 | -0.0024695 | 0.078835 | -58.4152 | 62.233 | -61.6974 | -61.5875 | 54.2999 | 22.7371 | 6.9763 | 6.221 | 62.2284 | -61.7065 | -0.27008 | 0.041199 | 3.0121 | -0.16022 | -7.8918 | -0.27924 | 0.036622 | 3.2822 | 68.4036 | 67.6483 | 115.7272 | 123.6603 | 3.0121 | 123.6557 | 84.1644 | -0.27924 | 123.6603 | 3.0121 | 84.1644 | 115.7272 | 123.6557 | -123.8892 | -123.8983
3369.7188 | 123.7976 | -61.4182 | 62.2375 | -0.131 | 0.016024 | 0.015977 | 0.010183 | 0.062598 | 0.0011621 | 0.080544 | -58.4747 | 62.233 | -61.7157 | -61.6241 | 54.2862 | 22.7051 | 7.0175 | 6.1111 | 62.233 | -61.6974 | -0.29755 | -0.004578 | 2.9434 | -0.20599 | -7.9514 | -0.27924 | -0.004578 | 3.241 | 68.4357 | 67.5293 | 115.7043 | 123.6511 | 2.9434 | 123.6511 | 84.1232 | -0.27924 | 123.6511 | 2.9434 | 84.1232 | 115.7043 | 123.6511 | -123.9532 | -123.9349
3370.7188 | 123.8297 | -61.4182 | 62.2055 | -0.16151 | 0.014101 | 0.015336 | 0.011465 | 0.064734 | 0.00030767 | 0.082253 | -58.4518 | 62.233 | -61.702 | -61.5829 | 54.277 | 22.6685 | 7.0267 | 6.189 | 62.2513 | -61.7111 | -0.28381 | 0.027466 | 2.9663 | -0.16479 | -7.9285 | -0.29297 | 0.045777 | 3.2501 | 68.4448 | 67.6071 | 115.6952 | 123.6511 | 2.9663 | 123.6694 | 84.0866 | -0.29297 | 123.6511 | 2.9663 | 84.0866 | 115.6952 | 123.6694 | -123.9075 | -123.9166
3371.7188 | 123.8022 | -61.4044 | 62.2375 | -0.1844 | 0.016878 | 0.012986 | 0.010183 | 0.062812 | 0.00073487 | 0.079904 | -58.4564 | 62.233 | -61.702 | -61.5646 | 54.2725 | 22.7142 | 7.0221 | 6.1935 | 62.2559 | -61.7157 | -0.29755 | -0.004578 | 2.948 | -0.16022 | -7.9651 | -0.31128 | 0.01831 | 3.2455 | 68.4265 | 67.598 | 115.6769 | 123.6374 | 2.948 | 123.6603 | 84.1187 | -0.31128 | 123.6374 | 2.948 | 84.1187 | 115.6769 | 123.6603 | -123.9395 | -123.9532
3372.7188 | 123.8068 | -61.4136 | 62.1872 | -0.08522 | 0.016238 | 0.014909 | 0.014456 | 0.064948 | -0.00011953 | 0.07969 | -58.4244 | 62.2147 | -61.7157 | -61.5601 | 54.3091 | 22.8516 | 7.0999 | 6.5689 | 62.2101 | -61.7294 | -0.30212 | 0.027466 | 2.9892 | -0.14649 | -7.8781 | -0.31586 | 0.022888 | 3.2913 | 68.5135 | 67.9825 | 115.7227 | 123.6282 | 2.9892 | 123.6237 | 84.2651 | -0.31586 | 123.6282 | 2.9892 | 84.2651 | 115.7227 | 123.6237 | -123.9029 | -123.9166
3373.7188 | 123.7564 | -61.4456 | 62.1872 | 0.04448 | 0.018587 | 0.015977 | 0.014029 | 0.065802 | -0.00054693 | 0.081185 | -58.4839 | 62.2192 | -61.7157 | -61.6425 | 54.2542 | 22.7234 | 7.1457 | 6.4774 | 62.2147 | -61.7386 | -0.27008 | 0.032043 | 2.9617 | -0.19684 | -7.933 | -0.29297 | 0.027466 | 3.2318 | 68.5913 | 67.923 | 115.6998 | 123.6649 | 2.9617 | 123.6603 | 84.169 | -0.29297 | 123.6649 | 2.9617 | 84.169 | 115.6998 | 123.6603 | -123.9029 | -123.9258
3374.7188 | 123.8205 | -61.409 | 62.1918 | -0.14626 | 0.018801 | 0.015763 | 0.01232 | 0.065375 | 0.00030767 | 0.080544 | -58.3969 | 62.2147 | -61.6882 | -61.5738 | 54.3457 | 22.8424 | 7.0587 | 6.5186 | 62.2375 | -61.7294 | -0.27923 | 0.022889 | 3.0121 | -0.16479 | -7.8461 | -0.32043 | 0.045777 | 3.2913 | 68.4677 | 67.9276 | 115.7547 | 123.6237 | 3.0121 | 123.6465 | 84.2514 | -0.32043 | 123.6237 | 3.0121 | 84.2514 | 115.7547 | 123.6465 | -123.88 | -123.9212
3375.7188 | 123.8068 | -61.4182 | 62.1918 | -0.069961 | 0.019015 | 0.018113 | 0.014242 | 0.064734 | 0.0030847 | 0.079904 | -58.4152 | 62.2467 | -61.6928 | -61.5921 | 54.277 | 22.7463 | 7.1503 | 6.5094 | 62.2147 | -61.734 | -0.27466 | 0.054932 | 3.0029 | -0.17395 | -7.9147 | -0.31586 | 0.022889 | 3.2776 | 68.5684 | 67.9276 | 115.6952 | 123.6649 | 3.0029 | 123.6328 | 84.1644 | -0.31586 | 123.6649 | 3.0029 | 84.1644 | 115.6952 | 123.6328 | -123.8846 | -123.9258
3376.7188 | 123.7976 | -61.409 | 62.2284 | -0.15388 | 0.015383 | 0.011064 | 0.01296 | 0.062384 | 0.0015893 | 0.081613 | -58.461 | 62.2787 | -61.6928 | -61.6196 | 54.3182 | 22.7646 | 7.0541 | 6.1157 | 62.233 | -61.7249 | -0.28381 | 0.050354 | 2.948 | -0.21057 | -7.9102 | -0.31586 | 0.004577 | 3.2318 | 68.4631 | 67.5247 | 115.7272 | 123.6877 | 2.948 | 123.642 | 84.1736 | -0.31586 | 123.6877 | 2.948 | 84.1736 | 115.7272 | 123.642 | -123.9212 | -123.9532
3377.7188 | 123.7885 | -61.4182 | 62.2238 | -0.21492 | 0.017306 | 0.015977 | 0.014242 | 0.064307 | 0.00073487 | 0.081399 | -58.429 | 62.2421 | -61.7111 | -61.5738 | 54.3823 | 22.8287 | 6.9626 | 6.1661 | 62.2284 | -61.6974 | -0.29297 | 0.01831 | 2.9892 | -0.15564 | -7.8415 | -0.27924 | 0.004578 | 3.2822 | 68.3807 | 67.5842 | 115.8005 | 123.6603 | 2.9892 | 123.6465 | 84.2468 | -0.27924 | 123.6603 | 2.9892 | 84.2468 | 115.8005 | 123.6465 | -123.9349 | -123.9212
3378.7188 | 123.7564 | -61.441 | 62.1872 | 0.10551 | 0.017947 | 0.015336 | 0.013601 | 0.06623 | 0.0018031 | 0.080544 | -58.5068 | 62.2513 | -61.7249 | -61.6791 | 54.2633 | 22.7417 | 6.9534 | 6.0699 | 62.2284 | -61.7249 | -0.28381 | 0.064087 | 2.9343 | -0.23804 | -7.9239 | -0.28381 | 0.041199 | 3.2181 | 68.3945 | 67.511 | 115.7043 | 123.6923 | 2.9343 | 123.6694 | 84.1827 | -0.28381 | 123.6923 | 2.9343 | 84.1827 | 115.7043 | 123.6694 | -123.912 | -123.912
3379.7188 | 123.793 | -61.409 | 62.2101 | -1.1762 | 0.018374 | 0.014054 | 0.015738 | 0.064734 | 0.0022303 | 0.078622 | -58.4518 | 62.2238 | -61.702 | -61.5738 | 54.3137 | 22.7692 | 6.9168 | 6.1615 | 62.2238 | -61.7203 | -0.29297 | 0.013733 | 2.9572 | -0.16479 | -7.8964 | -0.31128 | 0.013733 | 3.2501 | 68.3258 | 67.5705 | 115.7227 | 123.6328 | 2.9572 | 123.6328 | 84.1782 | -0.31128 | 123.6328 | 2.9572 | 84.1782 | 115.7227 | 123.6328 | -123.912 | -123.9304
3380.7188 | 123.7976 | -61.4182 | 62.2192 | -0.10048 | 0.017733 | 0.019822 | 0.013601 | 0.066443 | -0.00076053 | 0.080331 | -58.5892 | 62.1964 | -61.7294 | -61.5967 | 54.3777 | 22.7921 | 6.9672 | 6.2164 | 62.2421 | -61.702 | -0.31128 | -0.022888 | 2.829 | -0.17853 | -7.8415 | -0.28381 | 0.022888 | 3.1403 | 68.3853 | 67.6346 | 115.7959 | 123.6145 | 2.829 | 123.6603 | 84.2102 | -0.28381 | 123.6145 | 2.829 | 84.2102 | 115.7959 | 123.6603 | -123.9487 | -123.9212
3381.7188 | 123.8205 | -61.4136 | 62.2284 | -0.12337 | 0.017947 | 0.015122 | 0.012533 | 0.064307 | 0.00073487 | 0.080331 | -58.4427 | 62.2604 | -61.6974 | -61.5784 | 54.3777 | 22.8561 | 6.9855 | 6.2622 | 62.233 | -61.7386 | -0.28381 | 0.032043 | 2.9709 | -0.1648 | -7.8506 | -0.32501 | 0.004577 | 3.2547 | 68.399 | 67.6758 | 115.7913 | 123.674 | 2.9709 | 123.6465 | 84.2697 | -0.32501 | 123.674 | 2.9709 | 84.2697 | 115.7913 | 123.6465 | -123.9258 | -123.967
3382.7188 | 123.8205 | -61.4319 | 62.2421 | -0.19966 | 0.018587 | 0.012559 | 0.01296 | 0.066016 | 0.0013757 | 0.080331 | -58.4381 | 62.233 | -61.6882 | -61.5784 | 54.3457 | 22.8012 | 7.0496 | 6.3034 | 62.2559 | -61.7203 | -0.25635 | -0.009155 | 2.9938 | -0.14648 | -7.8964 | -0.28839 | 0.013733 | 3.2501 | 68.4814 | 67.7353 | 115.7776 | 123.6649 | 2.9938 | 123.6877 | 84.2331 | -0.28839 | 123.6649 | 2.9938 | 84.2331 | 115.7776 | 123.6877 | -123.9304 | -123.9624
3383.7188 | 123.7885 | -61.4044 | 62.1689 | 0.15129 | 0.017947 | 0.015763 | 0.012106 | 0.065375 | -0.00033333 | 0.079904 | -58.5068 | 62.2101 | -61.7386 | -61.6608 | 54.2679 | 22.7829 | 6.958 | 6.1752 | 62.1964 | -61.734 | -0.33417 | 0.041199 | 2.8976 | -0.25635 | -7.901 | -0.32959 | 0.027466 | 3.2318 | 68.3624 | 67.5797 | 115.6723 | 123.6145 | 2.8976 | 123.6008 | 84.1873 | -0.32959 | 123.6145 | 2.8976 | 84.1873 | 115.6723 | 123.6008 | -123.9075 | -123.9029
3384.7188 | 123.8022 | -61.4273 | 62.1872 | -0.047073 | 0.017092 | 0.018113 | 0.014883 | 0.06623 | -0.0011877 | 0.080972 | -58.4198 | 62.233 | -61.6928 | -61.5967 | 54.2908 | 22.8287 | 7.1411 | 6.633 | 62.2101 | -61.734 | -0.2655 | 0.045776 | 3.0075 | -0.16937 | -7.8964 | -0.3067 | 0.022888 | 3.273 | 68.5684 | 68.0603 | 115.7181 | 123.6603 | 3.0075 | 123.6374 | 84.256 | -0.3067 | 123.6603 | 3.0075 | 84.256 | 115.7181 | 123.6374 | -123.88 | -123.9212
3385.7188 | 123.8159 | -61.4227 | 62.233 | -0.16151 | 0.017306 | 0.01854 | 0.013174 | 0.064521 | -0.0014013 | 0.082894 | -58.4473 | 62.2284 | -61.7065 | -61.5875 | 54.2908 | 22.8287 | 7.1503 | 6.5964 | 62.2421 | -61.7157 | -0.28381 | -0.004577 | 2.9755 | -0.1648 | -7.9422 | -0.29297 | 0.009155 | 3.2593 | 68.573 | 68.0191 | 115.7135 | 123.6511 | 2.9755 | 123.6649 | 84.2514 | -0.29297 | 123.6511 | 2.9755 | 84.2514 | 115.7135 | 123.6649 | -123.9395 | -123.9487
3386.7188 | 123.793 | -61.4273 | 62.2101 | -0.23018 | 0.018587 | 0.016831 | 0.01232 | 0.065589 | -0.0014013 | 0.080117 | -58.429 | 62.2238 | -61.7065 | -61.5921 | 54.2999 | 22.847 | 7.1136 | 6.5872 | 62.2284 | -61.7065 | -0.27924 | 0.013733 | 2.9984 | -0.16479 | -7.9102 | -0.27924 | 0.018311 | 3.2776 | 68.541 | 68.0145 | 115.7272 | 123.6511 | 2.9984 | 123.6557 | 84.2743 | -0.27924 | 123.6511 | 2.9984 | 84.2743 | 115.7272 | 123.6557 | -123.9166 | -123.9166
3387.7188 | 123.8113 | -61.4136 | 62.2375 | -0.0089264 | 0.016878 | 0.017472 | 0.012747 | 0.064307 | -0.00076053 | 0.081826 | -58.5754 | 62.1872 | -61.734 | -61.5921 | 54.2679 | 22.8973 | 6.9763 | 6.3126 | 62.2513 | -61.7203 | -0.32044 | -0.050354 | 2.8381 | -0.17853 | -7.9697 | -0.3067 | 0.013733 | 3.1586 | 68.3899 | 67.7261 | 115.6815 | 123.6008 | 2.8381 | 123.6649 | 84.3109 | -0.3067 | 123.6008 | 2.8381 | 84.3109 | 115.6815 | 123.6649 | -123.9716 | -123.9578
3388.7188 | 123.761 | -61.4456 | 62.1872 | 3.4853 | 0.020937 | 0.011918 | 0.0097562 | 0.064307 | 0.00052127 | 0.080331 | -58.3466 | 62.2009 | -61.7432 | -61.6653 | 54.2542 | 22.7692 | 7.0404 | 6.3766 | 62.2513 | -61.7386 | -0.29755 | 0.013733 | 3.0991 | -0.21973 | -7.933 | -0.29297 | 0.064087 | 3.3966 | 68.486 | 67.8223 | 115.6998 | 123.6465 | 3.0991 | 123.6969 | 84.2148 | -0.29297 | 123.6465 | 3.0991 | 84.2148 | 115.6998 | 123.6969 | -123.9304 | -123.9258
3389.7188 | 123.8205 | -61.4182 | 62.2284 | -0.23018 | 0.019442 | 0.015336 | 0.01296 | 0.064307 | 0.0015893 | 0.079049 | -58.4244 | 62.2742 | -61.6974 | -61.5921 | 54.2633 | 22.8241 | 7.132 | 6.5323 | 62.233 | -61.7432 | -0.27924 | 0.045776 | 2.9938 | -0.17395 | -7.9651 | -0.32501 | 0.004577 | 3.273 | 68.5501 | 67.9504 | 115.6815 | 123.6923 | 2.9938 | 123.6511 | 84.2422 | -0.32501 | 123.6923 | 2.9938 | 84.2422 | 115.6815 | 123.6511 | -123.9258 | -123.9716
3390.7188 | 123.8022 | -61.4182 | 62.2238 | -0.17677 | 0.017733 | 0.013413 | 0.011251 | 0.065375 | 0.00030767 | 0.080331 | -58.4244 | 62.2513 | -61.702 | -61.615 | 54.2862 | 22.7737 | 7.1457 | 6.5231 | 62.2238 | -61.7203 | -0.28381 | 0.027466 | 2.9938 | -0.19684 | -7.9376 | -0.30212 | 0 | 3.2776 | 68.5638 | 67.9413 | 115.7043 | 123.6694 | 2.9938 | 123.642 | 84.1919 | -0.30212 | 123.6694 | 2.9938 | 84.1919 | 115.7043 | 123.642 | -123.9258 | -123.9441
3391.7188 | 123.8159 | -61.4319 | 62.2101 | -0.16914 | 0.016665 | 0.014482 | 0.013601 | 0.064521 | -0.00097413 | 0.081613 | -58.3878 | 62.2284 | -61.702 | -61.5784 | 54.3091 | 22.879 | 7.1045 | 6.5323 | 62.2513 | -61.7249 | -0.27008 | 0.018311 | 3.0441 | -0.14648 | -7.901 | -0.29297 | 0.041199 | 3.3142 | 68.5364 | 67.9642 | 115.741 | 123.6603 | 3.0441 | 123.6832 | 84.3109 | -0.29297 | 123.6603 | 3.0441 | 84.3109 | 115.741 | 123.6832 | -123.912 | -123.9349
3392.7188 | 123.8068 | -61.3998 | 62.2284 | -0.17677 | 0.016024 | 0.014268 | 0.012747 | 0.064734 | 0.0026575 | 0.080331 | -58.4244 | 62.2421 | -61.6974 | -61.5738 | 54.3228 | 22.9111 | 7.1869 | 6.5277 | 62.2467 | -61.7203 | -0.29755 | 0.013732 | 2.9755 | -0.17395 | -7.9056 | -0.32043 | 0.01831 | 3.273 | 68.5867 | 67.9276 | 115.7227 | 123.642 | 2.9755 | 123.6465 | 84.3109 | -0.32043 | 123.642 | 2.9755 | 84.3109 | 115.7227 | 123.6465 | -123.9258 | -123.9487
3393.7344 | 123.8617 | -61.4136 | 62.1414 | 1.5017 | 0.016665 | 0.015336 | 0.0095424 | 0.064093 | 0.0028711 | 0.081826 | -58.4656 | 62.1048 | -61.702 | -61.5784 | 54.4281 | 22.9797 | 6.9443 | 6.5414 | 62.1826 | -61.7065 | -0.28839 | -0.036621 | 2.948 | -0.1648 | -7.7133 | -0.29297 | 0.041199 | 3.2364 | 68.3578 | 67.955 | 115.8417 | 123.5184 | 2.948 | 123.5962 | 84.3933 | -0.29297 | 123.5184 | 2.948 | 84.3933 | 115.8417 | 123.5962 | -123.8434 | -123.848
3394.7188 | 123.8113 | -61.3998 | 62.2009 | -0.14626 | 0.01816 | 0.013627 | 0.015097 | 0.062384 | 0.00052127 | 0.081399 | -58.3969 | 62.2147 | -61.702 | -61.5738 | 54.4098 | 22.8882 | 7.1457 | 6.514 | 62.2284 | -61.7432 | -0.30212 | 0.013733 | 3.0029 | -0.17395 | -7.7911 | -0.34332 | 0.027466 | 3.3051 | 68.5455 | 67.9138 | 115.8096 | 123.6145 | 3.0029 | 123.6282 | 84.288 | -0.34332 | 123.6145 | 3.0029 | 84.288 | 115.8096 | 123.6282 | -123.9029 | -123.9441
3395.7188 | 123.8297 | -61.3998 | 62.178 | -0.131 | 0.01581 | 0.015763 | 0.014456 | 0.064521 | 0.00052127 | 0.083535 | -58.3923 | 62.2238 | -61.7111 | -61.5692 | 54.332 | 22.8287 | 7.0908 | 6.4957 | 62.233 | -61.7111 | -0.31128 | 0.045776 | 3.0075 | -0.16937 | -7.8461 | -0.31128 | 0.054931 | 3.3188 | 68.4906 | 67.8955 | 115.7318 | 123.6237 | 3.0075 | 123.6328 | 84.2285 | -0.31128 | 123.6237 | 3.0075 | 84.2285 | 115.7318 | 123.6328 | -123.8892 | -123.8892
3396.7188 | 123.761 | -61.4227 | 62.2192 | -0.19203 | 0.014315 | 0.014268 | 0.010183 | 0.063239 | -0.00033333 | 0.080331 | -58.4747 | 62.233 | -61.7203 | -61.615 | 54.3365 | 22.8149 | 7.1686 | 6.5506 | 62.2559 | -61.7249 | -0.29755 | 0.013733 | 2.948 | -0.19226 | -7.8827 | -0.30213 | 0.036621 | 3.2455 | 68.5913 | 67.9733 | 115.7593 | 123.6557 | 2.948 | 123.6786 | 84.2377 | -0.30213 | 123.6557 | 2.948 | 84.2377 | 115.7593 | 123.6786 | -123.9395 | -123.9441
3397.7188 | 123.761 | -61.4365 | 62.2101 | -0.93208 | 0.016024 | 0.011918 | 0.013174 | 0.064734 | -0.0022559 | 0.081185 | -58.5068 | 62.233 | -61.7203 | -61.615 | 54.2725 | 22.7051 | 7.2098 | 6.4728 | 62.2742 | -61.7249 | -0.28381 | 0.022888 | 2.9297 | -0.17853 | -7.9376 | -0.28839 | 0.064087 | 3.2135 | 68.6462 | 67.9092 | 115.7089 | 123.6694 | 2.9297 | 123.7106 | 84.1415 | -0.28839 | 123.6694 | 2.9297 | 84.1415 | 115.7089 | 123.7106 | -123.9304 | -123.9349
3398.7188 | 123.8022 | -61.4273 | 62.2192 | 1.6238 | 0.014529 | 0.021104 | 0.017233 | 0.06623 | 0.00094847 | 0.079904 | -58.3099 | 62.2192 | -61.7157 | -61.6058 | 54.3274 | 22.8836 | 7.1457 | 6.5552 | 62.2238 | -61.7111 | -0.28839 | 0 | 3.1174 | -0.17853 | -7.8918 | -0.28381 | 0.004578 | 3.4058 | 68.573 | 67.9825 | 115.7547 | 123.6465 | 3.1174 | 123.6511 | 84.3109 | -0.28381 | 123.6465 | 3.1174 | 84.3109 | 115.7547 | 123.6511 | -123.9349 | -123.9304
3399.7188 | 123.7839 | -61.4319 | 62.2147 | -0.21492 | 0.016451 | 0.014054 | 0.012747 | 0.063666 | 0.0011621 | 0.081826 | -58.4702 | 62.2284 | -61.7065 | -61.615 | 54.277 | 22.7554 | 7.2189 | 6.5277 | 62.2604 | -61.7111 | -0.27466 | 0.013733 | 2.9617 | -0.1831 | -7.9376 | -0.27924 | 0.045776 | 3.2364 | 68.6508 | 67.9596 | 115.7089 | 123.6603 | 2.9617 | 123.6923 | 84.1873 | -0.27924 | 123.6603 | 2.9617 | 84.1873 | 115.7089 | 123.6923 | -123.9212 | -123.9258
3400.7188 | 123.8297 | -61.4044 | 62.2238 | -0.131 | 0.016024 | 0.013627 | 0.011465 | 0.062384 | 9.4068e-05 | 0.081185 | -58.4518 | 62.2467 | -61.7203 | -61.6013 | 54.3045 | 22.8058 | 7.2418 | 6.5598 | 62.2375 | -61.7157 | -0.31586 | 0.022888 | 2.9526 | -0.19684 | -7.9193 | -0.31128 | 0.013733 | 3.2684 | 68.6462 | 67.9642 | 115.7089 | 123.6511 | 2.9526 | 123.642 | 84.2102 | -0.31128 | 123.6511 | 2.9526 | 84.2102 | 115.7089 | 123.642 | -123.9441 | -123.9395
3401.7188 | 123.8297 | -61.3953 | 62.2375 | -0.20729 | 0.014742 | 0.016618 | 0.010824 | 0.064521 | 0.0011621 | 0.081613 | -58.4702 | 62.2375 | -61.7065 | -61.615 | 54.3137 | 22.7463 | 7.2647 | 6.5552 | 62.2696 | -61.7065 | -0.31128 | 0 | 2.9251 | -0.21973 | -7.9239 | -0.31128 | 0.032043 | 3.2364 | 68.66 | 67.9504 | 115.7089 | 123.6328 | 2.9251 | 123.6649 | 84.1415 | -0.31128 | 123.6328 | 2.9251 | 84.1415 | 115.7089 | 123.6649 | -123.9441 | -123.9441
3402.7188 | 123.7564 | -61.4044 | 62.2147 | -0.23018 | 0.01581 | 0.018968 | 0.013174 | 0.063239 | 0.00030767 | 0.080972 | -58.461 | 62.2192 | -61.7157 | -61.6104 | 54.2725 | 22.6593 | 7.3242 | 6.5598 | 62.265 | -61.7065 | -0.31128 | 0.004577 | 2.9434 | -0.20599 | -7.9422 | -0.30212 | 0.050354 | 3.2547 | 68.7286 | 67.9642 | 115.6769 | 123.6237 | 2.9434 | 123.6694 | 84.0637 | -0.30212 | 123.6237 | 2.9434 | 84.0637 | 115.6769 | 123.6694 | -123.9304 | -123.9212
3403.7188 | 123.7747 | -61.4502 | 62.1918 | 0.059738 | 0.018801 | 0.017045 | 0.013601 | 0.066443 | -0.00033333 | 0.079263 | -58.4244 | 62.2284 | -61.7111 | -61.6562 | 54.2679 | 22.728 | 7.2784 | 6.514 | 62.2192 | -61.734 | -0.26093 | 0.036622 | 3.0258 | -0.20599 | -7.9239 | -0.28381 | 0.027466 | 3.2867 | 68.7286 | 67.9642 | 115.7181 | 123.6786 | 3.0258 | 123.6694 | 84.1782 | -0.28381 | 123.6786 | 3.0258 | 84.1782 | 115.7181 | 123.6694 | -123.9029 | -123.9258
3404.7188 | 123.793 | -61.4365 | 62.2009 | -0.22255 | 0.015169 | 0.015977 | 0.0099698 | 0.063452 | -0.00076053 | 0.080758 | -58.4473 | 62.2009 | -61.702 | -61.615 | 54.3457 | 22.8149 | 7.3196 | 6.5826 | 62.2513 | -61.6882 | -0.2655 | 0 | 2.9892 | -0.17853 | -7.8552 | -0.25177 | 0.050354 | 3.2547 | 68.7561 | 68.0191 | 115.7822 | 123.6374 | 2.9892 | 123.6877 | 84.2514 | -0.25177 | 123.6374 | 2.9892 | 84.2514 | 115.7822 | 123.6877 | -123.9029 | -123.8892
3405.7188 | 123.7473 | -61.441 | 62.2147 | -0.21492 | 0.014529 | 0.013841 | 0.010183 | 0.060462 | 0.00052127 | 0.080758 | -58.4656 | 62.1964 | -61.734 | -61.4456 | 54.1946 | 22.6044 | 7.37 | 6.633 | 62.2696 | -61.7294 | -0.29297 | -0.018311 | 2.9755 | -0.004578 | -8.02 | -0.28839 | 0.054931 | 3.2684 | 68.811 | 68.074 | 115.6357 | 123.6374 | 2.9755 | 123.7106 | 84.0454 | -0.28839 | 123.6374 | 2.9755 | 84.0454 | 115.6357 | 123.7106 | -123.9487 | -123.9441
3406.7188 | 123.8113 | -61.409 | 62.2742 | -0.16914 | 0.015383 | 0.012773 | 0.011251 | 0.062598 | 0.00052127 | 0.080972 | -58.4885 | 62.1964 | -61.7203 | -61.6058 | 54.2908 | 22.7509 | 7.3746 | 6.6055 | 62.265 | -61.6928 | -0.31128 | -0.07782 | 2.9205 | -0.19684 | -7.9834 | -0.28381 | -0.009155 | 3.2318 | 68.7836 | 68.0145 | 115.6998 | 123.6053 | 2.9205 | 123.674 | 84.1599 | -0.28381 | 123.6053 | 2.9205 | 84.1599 | 115.6998 | 123.674 | -123.9944 | -123.967
3407.7188 | 123.7564 | -61.4227 | 62.2284 | -0.26833 | 0.017519 | 0.013627 | 0.011892 | 0.062598 | 0.0013757 | 0.081185 | -58.461 | 62.2009 | -61.702 | -61.6241 | 54.2725 | 22.7646 | 7.338 | 6.6147 | 62.2238 | -61.7111 | -0.27924 | -0.027466 | 2.9617 | -0.20142 | -7.9559 | -0.28839 | -0.004578 | 3.241 | 68.7607 | 68.0374 | 115.6952 | 123.6237 | 2.9617 | 123.6465 | 84.1873 | -0.28839 | 123.6237 | 2.9617 | 84.1873 | 115.6952 | 123.6465 | -123.9304 | -123.9395
3408.7188 | 123.8022 | -61.4273 | 62.2192 | 0.029221 | 0.019442 | 0.014695 | 0.01531 | 0.064093 | 0.0011621 | 0.082467 | -58.4473 | 62.2147 | -61.702 | -61.6333 | 54.1901 | 22.7005 | 7.2144 | 6.4774 | 62.233 | -61.7432 | -0.27466 | -0.004577 | 2.98 | -0.20599 | -8.0292 | -0.31586 | 0.013733 | 3.2547 | 68.6417 | 67.9047 | 115.6174 | 123.642 | 2.98 | 123.6603 | 84.1278 | -0.31586 | 123.642 | 2.98 | 84.1278 | 115.6174 | 123.6603 | -123.9212 | -123.9624
3409.7188 | 123.8022 | -61.4044 | 62.2513 | -0.94734 | 0.019015 | 0.012132 | 0.010183 | 0.062384 | 0.00030767 | 0.078835 | -58.5159 | 62.1964 | -61.7203 | -61.6241 | 54.2175 | 22.6868 | 7.3196 | 6.5826 | 62.2375 | -61.7157 | -0.31586 | -0.054932 | 2.8885 | -0.21973 | -8.0338 | -0.31128 | -0.013733 | 3.2043 | 68.7241 | 67.9871 | 115.6219 | 123.6008 | 2.8885 | 123.642 | 84.0912 | -0.31128 | 123.6008 | 2.8885 | 84.0912 | 115.6219 | 123.642 | -123.9716 | -123.967
3410.7188 | 123.7701 | -61.4044 | 62.2009 | -0.29884 | 0.016665 | 0.015336 | 0.0082608 | 0.06388 | 0.00073487 | 0.080331 | -58.4564 | 62.178 | -61.6882 | -61.615 | 54.2679 | 22.8561 | 7.3746 | 6.7154 | 62.2238 | -61.7157 | -0.28381 | -0.022888 | 2.948 | -0.21057 | -7.933 | -0.31128 | 0.022888 | 3.2318 | 68.779 | 68.1198 | 115.6723 | 123.5825 | 2.948 | 123.6282 | 84.2606 | -0.31128 | 123.5825 | 2.948 | 84.2606 | 115.6723 | 123.6282 | -123.8892 | -123.9166
3411.7188 | 123.7793 | -61.4182 | 62.2467 | -0.25307 | 0.014315 | 0.01555 | 0.010183 | 0.06153 | -0.00033333 | 0.081826 | -58.4335 | 62.1918 | -61.6928 | -61.5875 | 54.2679 | 22.8149 | 7.3196 | 6.6376 | 62.2375 | -61.7065 | -0.27466 | -0.054932 | 2.9846 | -0.16937 | -7.9788 | -0.28839 | -0.009155 | 3.2593 | 68.7378 | 68.0557 | 115.686 | 123.6099 | 2.9846 | 123.6557 | 84.2331 | -0.28839 | 123.6099 | 2.9846 | 84.2331 | 115.686 | 123.6557 | -123.9395 | -123.9532
3412.7188 | 123.7518 | -61.4365 | 62.2284 | -0.23781 | 0.017092 | 0.0132 | 0.0097562 | 0.060248 | 0.00052127 | 0.081185 | -58.4793 | 62.1964 | -61.7294 | -61.7432 | 54.2038 | 22.8287 | 7.2372 | 6.5598 | 62.2192 | -61.734 | -0.29297 | -0.032044 | 2.9572 | -0.3067 | -8.0246 | -0.29755 | -0.009156 | 3.2501 | 68.6737 | 67.9962 | 115.6403 | 123.6328 | 2.9572 | 123.6557 | 84.2651 | -0.29755 | 123.6328 | 2.9572 | 84.2651 | 115.6403 | 123.6557 | -123.9578 | -123.9624
3413.7188 | 123.7793 | -61.441 | 62.2147 | -0.0089264 | 0.018374 | 0.018327 | 0.01766 | 0.062598 | 0.0028711 | 0.079904 | -58.429 | 62.2192 | -61.6882 | -61.615 | 54.2816 | 22.7829 | 7.283 | 6.6284 | 62.2375 | -61.7294 | -0.24719 | 0.004577 | 3.0121 | -0.17395 | -7.933 | -0.28839 | 0.022888 | 3.2593 | 68.7241 | 68.0695 | 115.7227 | 123.6603 | 3.0121 | 123.6786 | 84.2239 | -0.28839 | 123.6603 | 3.0121 | 84.2239 | 115.7227 | 123.6786 | -123.9029 | -123.9441
3414.7188 | 123.793 | -61.4227 | 62.2147 | -0.19966 | 0.017947 | 0.012345 | 0.011038 | 0.06388 | 0.00030767 | 0.079263 | -58.4381 | 62.2421 | -61.734 | -61.6104 | 54.2542 | 22.7325 | 7.3105 | 6.6055 | 62.265 | -61.6928 | -0.31128 | 0.027465 | 2.9846 | -0.18768 | -7.9605 | -0.27008 | 0.050354 | 3.2959 | 68.7332 | 68.0283 | 115.6769 | 123.6649 | 2.9846 | 123.6877 | 84.1553 | -0.27008 | 123.6649 | 2.9846 | 84.1553 | 115.6769 | 123.6877 | -123.9487 | -123.9075
3415.7188 | 123.793 | -61.4456 | 62.233 | -0.22255 | 0.017306 | 0.011918 | 0.011892 | 0.064307 | 0.00030767 | 0.079263 | -58.4518 | 62.2284 | -61.7386 | -61.6104 | 54.2953 | 22.7737 | 7.283 | 6.5826 | 62.2559 | -61.6974 | -0.29297 | -0.004577 | 2.9938 | -0.16479 | -7.9376 | -0.25177 | 0.022888 | 3.2867 | 68.7286 | 68.0283 | 115.741 | 123.674 | 2.9938 | 123.7015 | 84.2194 | -0.25177 | 123.674 | 2.9938 | 84.2194 | 115.741 | 123.7015 | -123.9716 | -123.9304
3416.7188 | 123.7885 | -61.4227 | 62.2192 | -0.21492 | 0.01816 | 0.014054 | 0.011038 | 0.061957 | 9.4068e-05 | 0.080758 | -58.4747 | 62.2055 | -61.702 | -61.615 | 54.2404 | 22.7097 | 7.3471 | 6.6788 | 62.2421 | -61.7157 | -0.27924 | -0.013733 | 2.948 | -0.19226 | -7.9788 | -0.29297 | 0.022888 | 3.2272 | 68.7698 | 68.1015 | 115.6631 | 123.6282 | 2.948 | 123.6649 | 84.1324 | -0.29297 | 123.6282 | 2.948 | 84.1324 | 115.6631 | 123.6649 | -123.9212 | -123.9349
3417.7188 | 123.7885 | -61.409 | 62.2192 | -0.36751 | 0.015597 | 0.011277 | 0.012533 | 0.065161 | -0.00054693 | 0.081613 | -58.493 | 62.233 | -61.7111 | -61.6196 | 54.2084 | 22.7051 | 7.3196 | 6.6238 | 62.2421 | -61.6974 | -0.30212 | 0.013733 | 2.916 | -0.21057 | -8.0109 | -0.28839 | 0.022888 | 3.2181 | 68.7286 | 68.0328 | 115.6174 | 123.642 | 2.916 | 123.6511 | 84.1141 | -0.28839 | 123.642 | 2.916 | 84.1141 | 115.6174 | 123.6511 | -123.9304 | -123.9166
3418.7188 | 123.7656 | -61.4227 | 62.2284 | -0.016556 | 0.019015 | 0.015336 | 0.015524 | 0.065802 | -0.00097413 | 0.081399 | -58.461 | 62.2192 | -61.7249 | -61.6333 | 54.1351 | 22.673 | 7.2922 | 6.6193 | 62.2009 | -61.7569 | -0.30213 | -0.009156 | 2.9617 | -0.21057 | -8.0933 | -0.33417 | -0.027466 | 3.2639 | 68.7149 | 68.042 | 115.5579 | 123.642 | 2.9617 | 123.6237 | 84.0958 | -0.33417 | 123.642 | 2.9617 | 84.0958 | 115.5579 | 123.6237 | -123.9532 | -123.9853
3419.7188 | 123.8022 | -61.4365 | 62.2284 | 0.082626 | 0.016024 | 0.015122 | 0.0099698 | 0.062384 | 0.00030767 | 0.082894 | -58.461 | 62.2421 | -61.734 | -61.6196 | 54.2496 | 22.7005 | 7.37 | 6.665 | 62.2742 | -61.7294 | -0.29755 | 0.013732 | 2.9755 | -0.18311 | -7.9788 | -0.29297 | 0.045776 | 3.273 | 68.8065 | 68.1015 | 115.686 | 123.6786 | 2.9755 | 123.7106 | 84.137 | -0.29297 | 123.6786 | 2.9755 | 84.137 | 115.686 | 123.7106 | -123.9624 | -123.9578
3420.7188 | 123.8113 | -61.4456 | 62.2467 | -0.26833 | 0.016451 | 0.012559 | 0.013388 | 0.062812 | -0.00033333 | 0.081399 | -58.4244 | 62.2238 | -61.6974 | -61.5875 | 54.2084 | 22.6959 | 7.3608 | 6.72 | 62.2421 | -61.6928 | -0.25177 | -0.022888 | 3.0212 | -0.14191 | -8.0383 | -0.24719 | -0.004578 | 3.273 | 68.8065 | 68.1656 | 115.654 | 123.6694 | 3.0212 | 123.6877 | 84.1415 | -0.24719 | 123.6694 | 3.0212 | 84.1415 | 115.654 | 123.6877 | -123.9441 | -123.9395
3421.7188 | 123.7839 | -61.4136 | 62.2238 | -0.10811 | 0.01581 | 0.014482 | 0.011892 | 0.064093 | 0.0011621 | 0.081826 | -58.461 | 62.2284 | -61.734 | -61.5829 | 54.1672 | 22.7554 | 7.3975 | 6.7108 | 62.265 | -61.6974 | -0.32044 | 0.004578 | 2.9526 | -0.16937 | -8.0566 | -0.28381 | 0.041199 | 3.273 | 68.811 | 68.1244 | 115.5807 | 123.642 | 2.9526 | 123.6786 | 84.169 | -0.28381 | 123.642 | 2.9526 | 84.169 | 115.5807 | 123.6786 | -123.9578 | -123.9212
3422.7188 | 123.8251 | -61.4182 | 62.2238 | -0.23018 | 0.017947 | 0.014482 | 0.011892 | 0.062598 | 0.0013757 | 0.078408 | -58.4427 | 62.2238 | -61.7111 | -61.6104 | 54.213 | 22.7234 | 7.3975 | 6.72 | 62.2375 | -61.7157 | -0.29297 | 0 | 2.9755 | -0.19226 | -8.0109 | -0.29755 | 0.013733 | 3.2684 | 68.8156 | 68.1381 | 115.6311 | 123.642 | 2.9755 | 123.6557 | 84.1415 | -0.29755 | 123.642 | 2.9755 | 84.1415 | 115.6311 | 123.6557 | -123.9349 | -123.9395
3423.7344 | 123.8342 | -61.4182 | 62.1964 | 0.18944 | 0.017519 | 0.017899 | 0.013815 | 0.065802 | 0.00073487 | 0.080758 | -58.4656 | 62.1872 | -61.6974 | -61.6196 | 54.2267 | 22.8561 | 7.2052 | 6.7154 | 62.1872 | -61.7203 | -0.27924 | -0.009155 | 2.9526 | -0.20142 | -7.9697 | -0.30212 | -0.009155 | 3.2318 | 68.6234 | 68.1335 | 115.6448 | 123.6053 | 2.9526 | 123.6053 | 84.2743 | -0.30212 | 123.6053 | 2.9526 | 84.2743 | 115.6448 | 123.6053 | -123.8937 | -123.9166
3424.7188 | 123.7427 | -61.4182 | 62.2192 | -0.27596 | 0.015597 | 0.012773 | 0.012106 | 0.063666 | -0.00033333 | 0.081826 | -58.4747 | 62.2238 | -61.702 | -61.6608 | 54.158 | 22.7829 | 7.4799 | 6.6879 | 62.2513 | -61.7249 | -0.28381 | 0.004578 | 2.9434 | -0.24262 | -8.0612 | -0.3067 | 0.032044 | 3.2272 | 68.898 | 68.1061 | 115.5762 | 123.642 | 2.9434 | 123.6694 | 84.201 | -0.3067 | 123.642 | 2.9434 | 84.201 | 115.5762 | 123.6694 | -123.9212 | -123.9441
3425.7188 | 123.7518 | -61.409 | 62.2192 | -0.26833 | 0.016451 | 0.010423 | 0.01296 | 0.063239 | -0.0035375 | 0.080758 | -58.4747 | 62.2559 | -61.7065 | -61.6562 | 54.213 | 22.8241 | 7.4341 | 6.6742 | 62.2467 | -61.7157 | -0.29755 | 0.036621 | 2.9343 | -0.24719 | -8.0063 | -0.3067 | 0.027466 | 3.2318 | 68.8431 | 68.0832 | 115.6219 | 123.6649 | 2.9343 | 123.6557 | 84.2331 | -0.3067 | 123.6649 | 2.9343 | 84.2331 | 115.6219 | 123.6557 | -123.9258 | -123.9349
3426.7188 | 123.793 | -61.4182 | 62.2284 | -0.14626 | 0.016451 | 0.0132 | 0.012747 | 0.063452 | 0.00030767 | 0.081826 | -58.4656 | 62.2284 | -61.7203 | -61.6196 | 54.3182 | 22.8287 | 7.4203 | 6.7612 | 62.233 | -61.6928 | -0.30212 | 0 | 2.9526 | -0.20142 | -7.9102 | -0.27466 | 0.004577 | 3.2547 | 68.8385 | 68.1793 | 115.7364 | 123.6465 | 2.9526 | 123.6511 | 84.2468 | -0.27466 | 123.6465 | 2.9526 | 84.2468 | 115.7364 | 123.6511 | -123.9487 | -123.9212
3427.7188 | 123.7885 | -61.4182 | 62.2147 | -0.21492 | 0.017092 | 0.015122 | 0.012533 | 0.062598 | -0.00011953 | 0.080331 | -58.4381 | 62.2192 | -61.7294 | -61.6058 | 54.2725 | 22.7966 | 7.4066 | 6.7612 | 62.2375 | -61.7294 | -0.31128 | 0.004577 | 2.98 | -0.18768 | -7.9422 | -0.31128 | 0.022888 | 3.2913 | 68.8248 | 68.1793 | 115.6906 | 123.6374 | 2.98 | 123.6557 | 84.2148 | -0.31128 | 123.6374 | 2.98 | 84.2148 | 115.6906 | 123.6557 | -123.9441 | -123.9441
3428.7188 | 123.7793 | -61.4594 | 62.2009 | 0.34966 | 0.017092 | 0.015336 | 0.01296 | 0.063452 | 9.4068e-05 | 0.07969 | -58.4747 | 62.1826 | -61.7386 | -61.6516 | 54.277 | 22.7966 | 7.3242 | 6.6559 | 62.2055 | -61.7294 | -0.27923 | -0.018311 | 2.9846 | -0.19226 | -7.9239 | -0.27008 | 0.004577 | 3.2639 | 68.7836 | 68.1152 | 115.7364 | 123.642 | 2.9846 | 123.6649 | 84.256 | -0.27008 | 123.642 | 2.9846 | 84.256 | 115.7364 | 123.6649 | -123.9395 | -123.9304
3429.7188 | 123.8022 | -61.4182 | 62.1964 | -0.13863 | 0.017519 | 0.014695 | 0.015524 | 0.064307 | -0.00097413 | 0.080331 | -58.3832 | 62.233 | -61.7294 | -61.6013 | 54.3182 | 22.8653 | 7.3608 | 6.8024 | 62.2055 | -61.7294 | -0.31128 | 0.036621 | 3.035 | -0.1831 | -7.8781 | -0.31128 | 0.009155 | 3.3463 | 68.779 | 68.2205 | 115.7364 | 123.6511 | 3.035 | 123.6237 | 84.2834 | -0.31128 | 123.6511 | 3.035 | 84.2834 | 115.7364 | 123.6237 | -123.9258 | -123.9258
3430.7344 | 123.8617 | -61.3953 | 62.1414 | 0.17418 | 0.014101 | 0.014268 | 0.0091152 | 0.06388 | 0.0028711 | 0.079263 | -58.4198 | 62.1094 | -61.7157 | -61.5967 | 54.3411 | 22.934 | 7.196 | 6.8344 | 62.1597 | -61.6837 | -0.32043 | -0.032043 | 2.9755 | -0.20142 | -7.8003 | -0.28839 | 0.018311 | 3.2959 | 68.5913 | 68.2297 | 115.7364 | 123.5046 | 2.9755 | 123.555 | 84.3292 | -0.28839 | 123.5046 | 2.9755 | 84.3292 | 115.7364 | 123.555 | -123.8571 | -123.8251
3431.7188 | 123.8022 | -61.4227 | 62.2192 | -0.12337 | 0.016665 | 0.013841 | 0.014669 | 0.061743 | 0.0037257 | 0.082253 | -58.429 | 62.2467 | -61.6974 | -61.5921 | 54.3228 | 22.879 | 7.4615 | 6.8848 | 62.2192 | -61.7477 | -0.27466 | 0.027466 | 2.9938 | -0.16937 | -7.8964 | -0.32501 | 0 | 3.2684 | 68.8843 | 68.3075 | 115.7455 | 123.6694 | 2.9938 | 123.642 | 84.3018 | -0.32501 | 123.6694 | 2.9938 | 84.3018 | 115.7455 | 123.642 | -123.9166 | -123.967
3432.7188 | 123.8022 | -61.4227 | 62.2375 | -0.2607 | 0.017947 | 0.016404 | 0.013601 | 0.063452 | -0.00076053 | 0.078835 | -58.4702 | 62.2467 | -61.734 | -61.6013 | 54.3228 | 22.879 | 7.3929 | 6.7749 | 62.2604 | -61.734 | -0.31128 | 0.009155 | 2.9526 | -0.17853 | -7.9147 | -0.31128 | 0.022888 | 3.2639 | 68.8156 | 68.1976 | 115.7455 | 123.6694 | 2.9526 | 123.6832 | 84.3018 | -0.31128 | 123.6694 | 2.9526 | 84.3018 | 115.7455 | 123.6832 | -123.9716 | -123.9716
3433.7188 | 123.8022 | -61.4365 | 62.1735 | 0.1284 | 0.017519 | 0.016831 | 0.011038 | 0.064734 | 0.00094847 | 0.082681 | -58.4702 | 62.1918 | -61.734 | -61.6562 | 54.2267 | 22.8012 | 7.2647 | 6.6513 | 62.1918 | -61.7249 | -0.29755 | 0.01831 | 2.9663 | -0.21973 | -7.9468 | -0.28839 | 0.01831 | 3.2639 | 68.7012 | 68.0878 | 115.6631 | 123.6282 | 2.9663 | 123.6282 | 84.2377 | -0.28839 | 123.6282 | 2.9663 | 84.2377 | 115.6631 | 123.6282 | -123.9075 | -123.8983
3434.7188 | 123.9166 | -61.409 | 62.1597 | -0.15388 | 0.017092 | 0.015336 | 0.014242 | 0.064948 | -0.00076053 | 0.080331 | -58.4061 | 62.2238 | -61.7111 | -61.5829 | 54.277 | 22.8607 | 7.2968 | 6.7291 | 62.2284 | -61.7157 | -0.30212 | 0.064087 | 3.0029 | -0.17395 | -7.8827 | -0.3067 | 0.068665 | 3.3051 | 68.7057 | 68.1381 | 115.686 | 123.6328 | 3.0029 | 123.6374 | 84.2697 | -0.3067 | 123.6328 | 3.0029 | 84.2697 | 115.686 | 123.6374 | -123.8708 | -123.8754
3435.7344 | 123.8251 | -61.409 | 62.1597 | 0.10551 | 0.01581 | 0.012345 | 0.0071926 | 0.064521 | -0.00097413 | 0.081826 | -58.4473 | 62.1277 | -61.7203 | -61.5967 | 54.2679 | 22.8333 | 7.1457 | 6.7795 | 62.1552 | -61.6791 | -0.31128 | -0.032043 | 2.9617 | -0.18768 | -7.8918 | -0.27008 | -0.004578 | 3.273 | 68.5547 | 68.1885 | 115.6769 | 123.5367 | 2.9617 | 123.5641 | 84.2422 | -0.27008 | 123.5367 | 2.9617 | 84.2422 | 115.6769 | 123.5641 | -123.88 | -123.8388
3436.7188 | 123.7656 | -61.4182 | 62.1918 | -0.054703 | 0.015383 | 0.019181 | 0.016592 | 0.06153 | 0.00030767 | 0.081399 | -58.3969 | 62.233 | -61.7249 | -61.6013 | 54.2496 | 22.8104 | 7.3105 | 6.7062 | 62.2009 | -61.7569 | -0.3067 | 0.041199 | 3.0212 | -0.1831 | -7.9422 | -0.33875 | 0.009156 | 3.3279 | 68.7286 | 68.1244 | 115.6677 | 123.6511 | 3.0212 | 123.6191 | 84.2285 | -0.33875 | 123.6511 | 3.0212 | 84.2285 | 115.6677 | 123.6191 | -123.9166 | -123.9487
3437.7188 | 123.7747 | -61.4273 | 62.2101 | -0.031814 | 0.018587 | 0.015977 | 0.014456 | 0.064734 | 0.00094847 | 0.078835 | -58.4244 | 62.2101 | -61.7249 | -61.615 | 54.2221 | 22.7692 | 7.3196 | 6.6971 | 62.2147 | -61.7249 | -0.29755 | 0 | 3.0029 | -0.18768 | -7.988 | -0.29755 | 0.004578 | 3.3005 | 68.7469 | 68.1244 | 115.6494 | 123.6374 | 3.0029 | 123.642 | 84.1965 | -0.29755 | 123.6374 | 3.0029 | 84.1965 | 115.6494 | 123.642 | -123.9349 | -123.9349
3438.7188 | 123.7427 | -61.4456 | 62.2009 | 0.03685 | 0.018801 | 0.016404 | 0.014456 | 0.064948 | -0.0028967 | 0.081185 | -58.4656 | 62.2238 | -61.7249 | -61.6516 | 54.2175 | 22.7737 | 7.3151 | 6.5826 | 62.2147 | -61.7477 | -0.27924 | 0.022888 | 2.98 | -0.20599 | -7.9834 | -0.30212 | 0.013733 | 3.2593 | 68.7607 | 68.0283 | 115.6631 | 123.6694 | 2.98 | 123.6603 | 84.2194 | -0.30212 | 123.6694 | 2.98 | 84.2194 | 115.6631 | 123.6603 | -123.9258 | -123.9487
3439.7188 | 123.7885 | -61.4273 | 62.1918 | -0.039444 | 0.017092 | 0.016404 | 0.01531 | 0.065589 | 0.0020167 | 0.081399 | -58.3969 | 62.2375 | -61.6882 | -61.5829 | 54.364 | 22.7875 | 7.3746 | 6.7154 | 62.2284 | -61.7203 | -0.26093 | 0.045777 | 3.0304 | -0.15564 | -7.8278 | -0.29297 | 0.036622 | 3.2913 | 68.8019 | 68.1427 | 115.7913 | 123.6649 | 3.0304 | 123.6557 | 84.2148 | -0.29297 | 123.6649 | 3.0304 | 84.2148 | 115.7913 | 123.6557 | -123.88 | -123.912
3440.7344 | 123.9487 | -61.4136 | 62.1964 | 0.0063326 | 0.014742 | 0.014909 | 0.0027066 | 0.062598 | -0.0014013 | 0.081826 | -58.4976 | 62.1277 | -61.734 | -61.6196 | 54.3274 | 22.8516 | 7.251 | 6.7703 | 62.1735 | -61.6699 | -0.32044 | -0.068664 | 2.916 | -0.20599 | -7.869 | -0.25635 | -0.022888 | 3.2364 | 68.6646 | 68.1839 | 115.741 | 123.5413 | 2.916 | 123.587 | 84.2651 | -0.25635 | 123.5413 | 2.916 | 84.2651 | 115.741 | 123.587 | -123.9304 | -123.8663
3441.7188 | 123.7656 | -61.4273 | 62.233 | 0.029221 | 0.01816 | 0.017259 | 0.015738 | 0.064093 | -0.0020421 | 0.080758 | -58.4244 | 62.265 | -61.7111 | -61.6379 | 54.2038 | 22.76 | 7.3563 | 6.7108 | 62.1964 | -61.7386 | -0.28381 | 0.032044 | 3.0029 | -0.21057 | -8.0292 | -0.31128 | -0.036621 | 3.2867 | 68.7836 | 68.1381 | 115.6311 | 123.6923 | 3.0029 | 123.6237 | 84.1873 | -0.31128 | 123.6923 | 3.0029 | 84.1873 | 115.6311 | 123.6237 | -123.9441 | -123.9716
3442.7188 | 123.7427 | -61.4502 | 62.1918 | 0.04448 | 0.015597 | 0.018327 | 0.014456 | 0.06388 | -0.00033333 | 0.080544 | -58.5022 | 62.2513 | -61.7294 | -61.6745 | 54.1534 | 22.7692 | 7.3151 | 6.6055 | 62.2101 | -61.7523 | -0.27924 | 0.05951 | 2.948 | -0.22431 | -8.0383 | -0.30212 | 0.018311 | 3.2272 | 68.7653 | 68.0557 | 115.6036 | 123.7015 | 2.948 | 123.6603 | 84.2194 | -0.30212 | 123.7015 | 2.948 | 84.2194 | 115.6036 | 123.6603 | -123.9212 | -123.9441
3443.7188 | 123.8251 | -61.4273 | 62.1368 | 0.24284 | 0.019869 | 0.021958 | 0.01232 | 0.06623 | 9.4068e-05 | 0.079904 | -58.4518 | 62.1826 | -61.7386 | -61.6516 | 54.2908 | 22.8973 | 7.2784 | 6.7291 | 62.1597 | -61.7386 | -0.31128 | 0.045776 | 2.9755 | -0.2243 | -7.8461 | -0.31128 | 0.022888 | 3.2867 | 68.7057 | 68.1564 | 115.7181 | 123.6099 | 2.9755 | 123.587 | 84.3246 | -0.31128 | 123.6099 | 2.9755 | 84.3246 | 115.7181 | 123.587 | -123.8754 | -123.8754
3444.7188 | 123.7289 | -61.4594 | 62.1872 | 0.11314 | 0.014529 | 0.017899 | 0.016165 | 0.064307 | -0.00033333 | 0.080758 | -58.4747 | 62.2101 | -61.7157 | -61.6745 | 54.1489 | 22.76 | 7.3883 | 6.6605 | 62.2192 | -61.7661 | -0.25635 | 0.022888 | 2.9846 | -0.21515 | -8.0383 | -0.3067 | 0.032043 | 3.241 | 68.8477 | 68.1198 | 115.6082 | 123.6694 | 2.9846 | 123.6786 | 84.2194 | -0.3067 | 123.6694 | 2.9846 | 84.2194 | 115.6082 | 123.6786 | -123.9029 | -123.9532
3445.7344 | 123.9029 | -61.4044 | 62.1689 | -0.08522 | 0.014956 | 0.011277 | 0.0048428 | 0.062171 | -0.00011953 | 0.082681 | -58.4244 | 62.1002 | -61.7157 | -61.5417 | 54.3365 | 23.0026 | 7.2876 | 6.926 | 62.2055 | -61.6653 | -0.31128 | -0.068664 | 2.98 | -0.13733 | -7.8323 | -0.26093 | 0.036621 | 3.2913 | 68.692 | 68.3304 | 115.741 | 123.5046 | 2.98 | 123.6099 | 84.407 | -0.26093 | 123.5046 | 2.98 | 84.407 | 115.741 | 123.6099 | -123.8846 | -123.8342
3446.7188 | 123.7518 | -61.4319 | 62.1918 | 0.059738 | 0.018587 | 0.01854 | 0.017233 | 0.063239 | 0.00073487 | 0.081826 | -58.4427 | 62.2238 | -61.7111 | -61.6745 | 54.1809 | 22.7646 | 7.3517 | 6.6696 | 62.1964 | -61.7615 | -0.27924 | 0.032044 | 2.9892 | -0.24262 | -8.0109 | -0.32959 | 0.004578 | 3.2684 | 68.7836 | 68.1015 | 115.6128 | 123.6557 | 2.9892 | 123.6282 | 84.1965 | -0.32959 | 123.6557 | 2.9892 | 84.1965 | 115.6128 | 123.6282 | -123.9029 | -123.9532
3447.7188 | 123.7152 | -61.441 | 62.1918 | 0.052109 | 0.019015 | 0.01555 | 0.015738 | 0.065161 | -0.0016149 | 0.080117 | -58.4747 | 62.2192 | -61.7203 | -61.6608 | 54.1306 | 22.7875 | 7.4295 | 6.7245 | 62.233 | -61.7386 | -0.27924 | 0.027466 | 2.9663 | -0.21973 | -8.0612 | -0.29755 | 0.041199 | 3.2455 | 68.8705 | 68.1656 | 115.5716 | 123.6603 | 2.9663 | 123.674 | 84.2285 | -0.29755 | 123.6603 | 2.9663 | 84.2285 | 115.5716 | 123.674 | -123.912 | -123.9304
3448.7344 | 123.8297 | -61.409 | 62.146 | 0.052109 | 0.016024 | 0.011918 | 0.0067654 | 0.062598 | 0.0015893 | 0.084603 | -58.4793 | 62.1094 | -61.7249 | -61.6104 | 54.2038 | 22.8928 | 7.2418 | 6.7612 | 62.178 | -61.6837 | -0.31586 | -0.036621 | 2.9297 | -0.20142 | -7.9422 | -0.27466 | 0.032044 | 3.2455 | 68.6508 | 68.1702 | 115.6128 | 123.5184 | 2.9297 | 123.587 | 84.3018 | -0.27466 | 123.5184 | 2.9297 | 84.3018 | 115.6128 | 123.587 | -123.8708 | -123.8297
3449.7188 | 123.7793 | -61.4594 | 62.1872 | 0.17418 | 0.024142 | 0.017686 | 0.018515 | 0.060034 | -0.00097413 | 0.080972 | -58.7494 | 62.1597 | -61.7477 | -61.6974 | 54.1214 | 22.7966 | 7.4203 | 6.6833 | 62.1735 | -61.7752 | -0.28839 | -0.027466 | 2.71 | -0.23804 | -8.0658 | -0.31586 | -0.013733 | 2.9984 | 68.8797 | 68.1427 | 115.5807 | 123.6191 | 2.71 | 123.6328 | 84.256 | -0.31586 | 123.6191 | 2.71 | 84.256 | 115.5807 | 123.6328 | -123.9349 | -123.9624
3450.7188 | 123.7381 | -61.441 | 62.1826 | 0.15129 | 0.017947 | 0.01854 | 0.012106 | 0.06388 | 0.0020167 | 0.080117 | -58.3099 | 62.1918 | -61.7569 | -61.5829 | 54.1855 | 22.7737 | 7.402 | 6.6833 | 62.1689 | -61.7523 | -0.31586 | 0.009155 | 3.1311 | -0.14191 | -7.9971 | -0.31128 | -0.013733 | 3.447 | 68.8431 | 68.1244 | 115.6265 | 123.6328 | 3.1311 | 123.6099 | 84.2148 | -0.31128 | 123.6328 | 3.1311 | 84.2148 | 115.6265 | 123.6099 | -123.9395 | -123.9349
3451.7188 | 123.7564 | -61.4273 | 62.1918 | 0.18181 | 0.018587 | 0.018113 | 0.013174 | 0.058966 | 0.00094847 | 0.080117 | -58.461 | 62.2238 | -61.7294 | -61.6653 | 54.2679 | 22.8333 | 7.3105 | 6.6513 | 62.1826 | -61.7569 | -0.30212 | 0.032044 | 2.9663 | -0.23804 | -7.9239 | -0.32959 | -0.009155 | 3.2684 | 68.7378 | 68.0786 | 115.6952 | 123.6511 | 2.9663 | 123.6099 | 84.2606 | -0.32959 | 123.6511 | 2.9663 | 84.2606 | 115.6952 | 123.6099 | -123.9212 | -123.9487
3452.7188 | 123.7656 | -61.4548 | 62.1918 | 0.04448 | 0.018801 | 0.015122 | 0.01531 | 0.06623 | 0.00052127 | 0.079049 | -58.4747 | 62.233 | -61.6974 | -61.6425 | 54.2084 | 22.7829 | 7.4158 | 6.6284 | 62.2375 | -61.7661 | -0.24261 | 0.041199 | 2.98 | -0.18768 | -7.9834 | -0.31128 | 0.045777 | 3.2227 | 68.8705 | 68.0832 | 115.6631 | 123.6877 | 2.98 | 123.6923 | 84.2377 | -0.31128 | 123.6877 | 2.98 | 84.2377 | 115.6631 | 123.6923 | -123.8892 | -123.9578
3453.7188 | 123.8388 | -61.3907 | 62.1643 | 0.2047 | 0.015169 | 0.012773 | 0.005911 | 0.06388 | 0.0011621 | 0.081613 | -58.429 | 62.114 | -61.7203 | -61.5921 | 54.2038 | 22.879 | 7.2372 | 6.8024 | 62.1506 | -61.6882 | -0.32959 | -0.050354 | 2.9617 | -0.20142 | -7.9605 | -0.29755 | -0.013733 | 3.2913 | 68.6279 | 68.1931 | 115.5945 | 123.5046 | 2.9617 | 123.5413 | 84.2697 | -0.29755 | 123.5046 | 2.9617 | 84.2697 | 115.5945 | 123.5413 | -123.8846 | -123.8525
3454.7188 | 123.7885 | -61.4365 | 62.2055 | 0.13603 | 0.017733 | 0.011704 | 0.020865 | 0.062598 | -0.0022559 | 0.077554 | -58.4747 | 62.2238 | -61.7432 | -61.5189 | 54.126 | 22.7783 | 7.5531 | 6.6925 | 62.1964 | -61.7661 | -0.3067 | 0.018311 | 2.9617 | -0.082398 | -8.0795 | -0.32959 | -0.009155 | 3.2684 | 68.9896 | 68.129 | 115.5624 | 123.6603 | 2.9617 | 123.6328 | 84.2148 | -0.32959 | 123.6603 | 2.9617 | 84.2148 | 115.5624 | 123.6328 | -123.9487 | -123.9716
3455.7188 | 123.793 | -61.4273 | 62.1597 | 0.18944 | 0.016238 | 0.016404 | 0.013815 | 0.064093 | -0.00033333 | 0.083322 | -58.4518 | 62.2055 | -61.734 | -61.6379 | 54.2084 | 22.7692 | 7.4203 | 6.7841 | 62.2101 | -61.7523 | -0.3067 | 0.045776 | 2.9755 | -0.21057 | -7.9514 | -0.32501 | 0.050354 | 3.2822 | 68.8477 | 68.2114 | 115.6357 | 123.6328 | 2.9755 | 123.6374 | 84.1965 | -0.32501 | 123.6328 | 2.9755 | 84.1965 | 115.6357 | 123.6374 | -123.8937 | -123.912
3456.7188 | 123.912 | -61.3953 | 62.1552 | 0.14366 | 0.016024 | 0.020036 | 0.011465 | 0.061957 | -0.00054693 | 0.081399 | -58.374 | 62.1643 | -61.7249 | -61.5784 | 54.2816 | 22.8836 | 7.2784 | 6.8802 | 62.1277 | -61.7157 | -0.32959 | 0.009156 | 3.0212 | -0.18311 | -7.8735 | -0.32043 | -0.027465 | 3.3508 | 68.6737 | 68.2755 | 115.6769 | 123.5596 | 3.0212 | 123.5229 | 84.2789 | -0.32043 | 123.5596 | 3.0212 | 84.2789 | 115.6769 | 123.5229 | -123.88 | -123.8708
3457.7188 | 123.8113 | -61.4548 | 62.1552 | 0.14366 | 0.018374 | 0.015122 | 0.014242 | 0.065161 | 0.0024439 | 0.081399 | -58.4564 | 62.2101 | -61.7294 | -61.6287 | 54.1626 | 22.7921 | 7.4615 | 6.8069 | 62.2009 | -61.7706 | -0.27466 | 0.054932 | 2.9984 | -0.17395 | -7.9926 | -0.31586 | 0.045777 | 3.273 | 68.9163 | 68.2617 | 115.6174 | 123.6649 | 2.9984 | 123.6557 | 84.2468 | -0.31586 | 123.6649 | 2.9984 | 84.2468 | 115.6174 | 123.6557 | -123.8846 | -123.9258
3458.7344 | 123.8937 | -61.3861 | 62.1643 | -0.062332 | 0.016024 | 0.014909 | 0.0063382 | 0.062384 | 0.0024439 | 0.082681 | -58.4335 | 62.1002 | -61.7111 | -61.5509 | 54.3686 | 22.9523 | 7.3975 | 6.9809 | 62.1506 | -61.6745 | -0.32501 | -0.064087 | 2.9526 | -0.16479 | -7.7957 | -0.28839 | -0.013733 | 3.2776 | 68.7836 | 68.367 | 115.7547 | 123.4863 | 2.9526 | 123.5367 | 84.3384 | -0.28839 | 123.4863 | 2.9526 | 84.3384 | 115.7547 | 123.5367 | -123.8754 | -123.8388
3459.7188 | 123.7747 | -61.4319 | 62.1826 | 2.8216 | 0.017947 | 0.013841 | 0.01531 | 0.061743 | -0.00011953 | 0.081826 | -58.6166 | 62.1735 | -61.7386 | -61.6928 | 54.3182 | 22.9477 | 7.5439 | 6.8024 | 62.146 | -61.7661 | -0.3067 | -0.009155 | 2.8152 | -0.26093 | -7.8644 | -0.33417 | -0.036621 | 3.1219 | 68.9758 | 68.2343 | 115.7501 | 123.6053 | 2.8152 | 123.5779 | 84.3796 | -0.33417 | 123.6053 | 2.8152 | 84.3796 | 115.7501 | 123.5779 | -123.9212 | -123.9487
3460.7188 | 123.8068 | -61.441 | 62.178 | 0.18181 | 0.018801 | 0.013841 | 0.012747 | 0.063025 | 0.0022303 | 0.079263 | -58.4885 | 62.1918 | -61.734 | -61.647 | 54.3045 | 22.9111 | 7.4615 | 6.7978 | 62.1689 | -61.7523 | -0.29297 | 0.013732 | 2.9526 | -0.20599 | -7.8735 | -0.31128 | -0.009156 | 3.2455 | 68.9026 | 68.2388 | 115.7455 | 123.6328 | 2.9526 | 123.6099 | 84.3521 | -0.31128 | 123.6328 | 2.9526 | 84.3521 | 115.7455 | 123.6099 | -123.912 | -123.9304
3461.7188 | 123.8205 | -61.3998 | 62.1735 | 0.17418 | 0.018374 | 0.019395 | 0.013601 | 0.061957 | 0.00094847 | 0.078835 | -58.4793 | 62.2101 | -61.7203 | -61.6287 | 54.3274 | 22.9111 | 7.3517 | 6.7657 | 62.1735 | -61.7569 | -0.32043 | 0.036621 | 2.9205 | -0.22888 | -7.8461 | -0.35706 | 0 | 3.241 | 68.7515 | 68.1656 | 115.7272 | 123.6099 | 2.9205 | 123.5733 | 84.3109 | -0.35706 | 123.6099 | 2.9205 | 84.3109 | 115.7272 | 123.5733 | -123.8937 | -123.9304
3462.7188 | 123.9075 | -61.3998 | 62.146 | -0.077591 | 0.016451 | 0.017472 | 0.011465 | 0.061743 | 0.0020167 | 0.080544 | -58.3832 | 62.146 | -61.7157 | -61.5646 | 54.364 | 23.0255 | 7.2784 | 6.8024 | 62.114 | -61.702 | -0.31586 | 0 | 3.0167 | -0.16479 | -7.782 | -0.30212 | -0.032043 | 3.3325 | 68.6783 | 68.2022 | 115.7639 | 123.5458 | 3.0167 | 123.5138 | 84.4254 | -0.30212 | 123.5458 | 3.0167 | 84.4254 | 115.7639 | 123.5138 | -123.8617 | -123.848
3463.7344 | 123.88 | -61.3998 | 62.146 | -0.054703 | 0.014956 | 0.0059366 | 0.006979 | 0.059607 | 0.00030767 | 0.081613 | -58.4061 | 62.1002 | -61.702 | -61.5555 | 54.3823 | 23.0164 | 7.4158 | 6.9214 | 62.1735 | -61.6791 | -0.30212 | -0.045776 | 2.9938 | -0.15564 | -7.7637 | -0.27924 | 0.027466 | 3.2959 | 68.8156 | 68.3212 | 115.7822 | 123.5001 | 2.9938 | 123.5733 | 84.4162 | -0.27924 | 123.5001 | 2.9938 | 84.4162 | 115.7822 | 123.5733 | -123.848 | -123.8251
3464.7188 | 123.8937 | -61.3907 | 62.1552 | 0.17418 | 0.014315 | 0.015122 | 0.014883 | 0.062171 | 0.00030767 | 0.080972 | -58.3878 | 62.114 | -61.7386 | -61.5692 | 54.3503 | 22.9797 | 7.3013 | 6.8436 | 62.1277 | -61.702 | -0.3479 | -0.041198 | 3.0029 | -0.17853 | -7.8049 | -0.31128 | -0.027465 | 3.3508 | 68.692 | 68.2343 | 115.741 | 123.5046 | 3.0029 | 123.5184 | 84.3704 | -0.31128 | 123.5046 | 3.0029 | 84.3704 | 115.741 | 123.5184 | -123.8937 | -123.8571
3465.7188 | 123.8709 | -61.4044 | 62.1552 | 0.2581 | 0.014956 | 0.016404 | 0.013601 | 0.062171 | -0.00011953 | 0.078835 | -58.3969 | 62.146 | -61.6882 | -61.5509 | 54.3503 | 22.9706 | 7.2372 | 6.7703 | 62.146 | -61.7157 | -0.28381 | -0.009155 | 3.0075 | -0.14648 | -7.8049 | -0.31128 | -0.009155 | 3.2913 | 68.6417 | 68.1747 | 115.7547 | 123.5504 | 3.0075 | 123.5504 | 84.375 | -0.31128 | 123.5504 | 3.0075 | 84.375 | 115.7547 | 123.5504 | -123.8434 | -123.8708
3466.7188 | 123.8022 | -61.4227 | 62.1872 | 0.21233 | 0.016451 | 0.017259 | 0.015524 | 0.061743 | 0.0035121 | 0.07969 | -58.4473 | 62.178 | -61.7203 | -61.6425 | 54.3457 | 22.9523 | 7.3471 | 6.7017 | 62.1735 | -61.7111 | -0.29755 | -0.009155 | 2.9755 | -0.21973 | -7.8415 | -0.28839 | -0.013733 | 3.273 | 68.7698 | 68.1244 | 115.7684 | 123.6008 | 2.9755 | 123.5962 | 84.375 | -0.28839 | 123.6008 | 2.9755 | 84.375 | 115.7684 | 123.5962 | -123.9075 | -123.8983
3467.7188 | 123.9075 | -61.3815 | 62.1323 | 0.21233 | 0.018374 | 0.012345 | 0.012747 | 0.063239 | 0.0028711 | 0.081826 | -58.4061 | 62.1323 | -61.7157 | -61.5509 | 54.364 | 22.9752 | 7.3883 | 6.8848 | 62.1506 | -61.7249 | -0.33417 | 0 | 2.9755 | -0.16937 | -7.7682 | -0.34332 | 0.018311 | 3.3096 | 68.7698 | 68.2663 | 115.7455 | 123.5138 | 2.9755 | 123.5321 | 84.3567 | -0.34332 | 123.5138 | 2.9755 | 84.3567 | 115.7455 | 123.5321 | -123.848 | -123.8571
3468.7344 | 123.9395 | -61.3586 | 62.2375 | -0.19203 | 0.012179 | 0.011491 | 0.0080472 | 0.062171 | -0.0016149 | 0.079049 | -58.4015 | 62.1002 | -61.6928 | -61.496 | 54.3732 | 23.0072 | 7.5439 | 7.0129 | 62.1597 | -61.6928 | -0.33417 | -0.13733 | 2.9572 | -0.13733 | -7.8644 | -0.33417 | -0.07782 | 3.2913 | 68.9026 | 68.3716 | 115.7318 | 123.4589 | 2.9572 | 123.5184 | 84.3658 | -0.33417 | 123.4589 | 2.9572 | 84.3658 | 115.7318 | 123.5184 | -123.9304 | -123.9304
3469.7188 | 123.8892 | -61.3998 | 62.1597 | -1.4204 | 0.015169 | 0.017045 | 0.012747 | 0.060034 | -0.00054693 | 0.08204 | -58.342 | 62.1277 | -61.6928 | -61.5601 | 54.2633 | 22.966 | 7.4066 | 6.9489 | 62.1277 | -61.6882 | -0.29297 | -0.032043 | 3.0579 | -0.16022 | -7.8964 | -0.28839 | -0.032043 | 3.3508 | 68.8065 | 68.3487 | 115.6631 | 123.5275 | 3.0579 | 123.5275 | 84.3658 | -0.28839 | 123.5275 | 3.0579 | 84.3658 | 115.6631 | 123.5275 | -123.8525 | -123.848
3470.7188 | 123.8937 | -61.3998 | 62.1414 | 0.94475 | 0.014101 | 0.015763 | 0.01296 | 0.063452 | -0.00033333 | 0.079049 | -58.2825 | 62.114 | -61.6974 | -61.5417 | 54.2999 | 22.879 | 7.4295 | 6.9809 | 62.1231 | -61.6974 | -0.29755 | -0.027465 | 3.1174 | -0.14191 | -7.8415 | -0.29755 | -0.01831 | 3.4149 | 68.8293 | 68.3807 | 115.6998 | 123.5138 | 3.1174 | 123.5229 | 84.2789 | -0.29755 | 123.5138 | 3.1174 | 84.2789 | 115.6998 | 123.5229 | -123.8388 | -123.8388
3471.7188 | 123.88 | -61.3724 | 62.1597 | 1.5093 | 0.015169 | 0.016831 | 0.01232 | 0.061743 | -0.00033333 | 0.081185 | -58.3832 | 62.0819 | -61.6882 | -61.5463 | 54.4098 | 22.9935 | 7.3883 | 7.045 | 62.114 | -61.7065 | -0.31586 | -0.07782 | 2.9892 | -0.17395 | -7.7499 | -0.33417 | -0.045776 | 3.3051 | 68.7607 | 68.4174 | 115.7822 | 123.4543 | 2.9892 | 123.4863 | 84.3658 | -0.33417 | 123.4543 | 2.9892 | 84.3658 | 115.7822 | 123.4863 | -123.848 | -123.8663
3472.7188 | 123.8709 | -61.3861 | 62.1689 | 0.17418 | 0.014529 | 0.012773 | 0.017019 | 0.061316 | 0.0020167 | 0.079904 | -58.3969 | 62.146 | -61.7386 | -61.5829 | 54.364 | 22.9706 | 7.4249 | 7.0129 | 62.0911 | -61.7157 | -0.35248 | -0.022888 | 2.9892 | -0.19684 | -7.8049 | -0.32959 | -0.07782 | 3.3417 | 68.811 | 68.399 | 115.7501 | 123.5321 | 2.9892 | 123.4772 | 84.3567 | -0.32959 | 123.5321 | 2.9892 | 84.3567 | 115.7501 | 123.4772 | -123.9075 | -123.8846
3473.7188 | 123.8205 | -61.3815 | 62.1643 | 0.13603 | 0.014742 | 0.014695 | 0.0071926 | 0.061103 | 0.00094847 | 0.081399 | -58.461 | 62.0819 | -61.7111 | -61.6013 | 54.2221 | 22.8973 | 7.5302 | 7.0221 | 62.1506 | -61.6974 | -0.32959 | -0.082398 | 2.9205 | -0.21973 | -7.9422 | -0.31586 | -0.013733 | 3.2501 | 68.9117 | 68.4036 | 115.6036 | 123.4634 | 2.9205 | 123.5321 | 84.2789 | -0.31586 | 123.4634 | 2.9205 | 84.2789 | 115.6036 | 123.5321 | -123.8754 | -123.8617
3474.7188 | 123.8525 | -61.3861 | 62.1552 | 0.22758 | 0.014742 | 0.016404 | 0.0093288 | 0.058753 | 0.00073487 | 0.079476 | -58.3923 | 62.0956 | -61.702 | -61.5372 | 54.3549 | 22.9202 | 7.3975 | 7.1091 | 62.1048 | -61.7203 | -0.31586 | -0.059509 | 2.9938 | -0.15106 | -7.8003 | -0.33417 | -0.050354 | 3.3096 | 68.7836 | 68.4952 | 115.741 | 123.4818 | 2.9938 | 123.4909 | 84.3063 | -0.33417 | 123.4818 | 2.9938 | 84.3063 | 115.741 | 123.4909 | -123.8571 | -123.8754
3475.7188 | 123.9029 | -61.409 | 62.1323 | 0.2047 | 0.01346 | 0.016831 | 0.010397 | 0.060675 | -0.0014013 | 0.079904 | -58.3099 | 62.1185 | -61.7203 | -61.5097 | 54.2496 | 22.8607 | 7.4066 | 7.0496 | 62.1323 | -61.7065 | -0.31128 | -0.013733 | 3.0991 | -0.10071 | -7.8827 | -0.29755 | 0 | 3.4103 | 68.8156 | 68.4586 | 115.6586 | 123.5275 | 3.0991 | 123.5413 | 84.2697 | -0.29755 | 123.5275 | 3.0991 | 84.2697 | 115.6586 | 123.5413 | -123.8525 | -123.8388
3476.7188 | 123.8617 | -61.4044 | 62.1323 | 0.12077 | 0.014529 | 0.016618 | 0.012106 | 0.062812 | 0.0015893 | 0.080758 | -58.4106 | 62.0773 | -61.7065 | -61.5738 | 54.1992 | 22.8928 | 7.3837 | 6.9809 | 62.1277 | -61.702 | -0.30212 | -0.054931 | 2.9938 | -0.16937 | -7.933 | -0.29755 | -0.004577 | 3.2959 | 68.7881 | 68.3853 | 115.6036 | 123.4818 | 2.9938 | 123.5321 | 84.2972 | -0.29755 | 123.4818 | 2.9938 | 84.2972 | 115.6036 | 123.5321 | -123.8388 | -123.8342
3477.7188 | 123.848 | -61.4182 | 62.1231 | 0.15892 | 0.013888 | 0.014909 | 0.011251 | 0.06153 | -0.00033333 | 0.080117 | -58.4152 | 62.114 | -61.7111 | -61.5692 | 54.3137 | 22.9385 | 7.3883 | 7.0129 | 62.1323 | -61.702 | -0.29297 | -0.009155 | 3.0029 | -0.15106 | -7.8094 | -0.28381 | 0.009155 | 3.2959 | 68.8065 | 68.4311 | 115.7318 | 123.5321 | 3.0029 | 123.5504 | 84.3567 | -0.28381 | 123.5321 | 3.0029 | 84.3567 | 115.7318 | 123.5504 | -123.8342 | -123.8251
3478.7188 | 123.8937 | -61.3724 | 62.1735 | -0.16151 | 0.015383 | 0.012773 | 0.010183 | 0.059607 | -0.00011953 | 0.08204 | -58.374 | 62.0956 | -61.6653 | -61.4914 | 54.3594 | 23.0896 | 7.4524 | 7.0816 | 62.1552 | -61.6745 | -0.29297 | -0.07782 | 2.9984 | -0.11902 | -7.814 | -0.30213 | -0.018311 | 3.2913 | 68.8248 | 68.454 | 115.7318 | 123.468 | 2.9984 | 123.5275 | 84.462 | -0.30213 | 123.468 | 2.9984 | 84.462 | 115.7318 | 123.5275 | -123.8388 | -123.848
3479.7188 | 123.8663 | -61.3998 | 62.1323 | 0.24284 | 0.016024 | 0.014268 | 0.015097 | 0.060889 | -0.0024695 | 0.080972 | -58.5526 | 62.0636 | -61.7111 | -61.5784 | 54.1718 | 23.0347 | 7.3975 | 7.0221 | 62.1002 | -61.6837 | -0.31128 | -0.068664 | 2.8473 | -0.17853 | -7.9605 | -0.28381 | -0.032043 | 3.1586 | 68.7973 | 68.4219 | 115.5716 | 123.4634 | 2.8473 | 123.5001 | 84.4345 | -0.28381 | 123.4634 | 2.8473 | 84.4345 | 115.5716 | 123.5001 | -123.8434 | -123.8159
3480.7188 | 123.8709 | -61.3907 | 62.1506 | 0.15892 | 0.015383 | 0.014695 | 0.013815 | 0.060248 | -0.00097413 | 0.080117 | -58.2825 | 62.1002 | -61.7157 | -61.5463 | 54.1077 | 22.9523 | 7.3792 | 7.0221 | 62.1185 | -61.6745 | -0.32501 | -0.050354 | 3.1082 | -0.15564 | -8.0429 | -0.28381 | -0.032044 | 3.4332 | 68.7698 | 68.4128 | 115.4984 | 123.4909 | 3.1082 | 123.5092 | 84.343 | -0.28381 | 123.4909 | 3.1082 | 84.343 | 115.4984 | 123.5092 | -123.8663 | -123.8251
3481.7188 | 123.8571 | -61.4136 | 62.1506 | 0.19707 | 0.015169 | 0.015122 | 0.01232 | 0.061316 | 0.0011621 | 0.078835 | -58.461 | 62.0956 | -61.7203 | -61.5829 | 54.1122 | 22.9065 | 7.4615 | 7.0404 | 62.1231 | -61.6882 | -0.3067 | -0.054932 | 2.9526 | -0.16937 | -8.0383 | -0.27466 | -0.027466 | 3.2593 | 68.8751 | 68.454 | 115.5258 | 123.5092 | 2.9526 | 123.5367 | 84.3201 | -0.27466 | 123.5092 | 2.9526 | 84.3201 | 115.5258 | 123.5367 | -123.8708 | -123.8388
3482.7188 | 123.8297 | -61.4319 | 62.146 | 0.10551 | 0.016238 | 0.012986 | 0.01296 | 0.061743 | 0.00073487 | 0.081399 | -58.4152 | 62.114 | -61.7065 | -61.5829 | 54.0482 | 22.966 | 7.4249 | 7.0129 | 62.1231 | -61.7157 | -0.27466 | -0.032043 | 3.0167 | -0.15106 | -8.0978 | -0.28381 | -0.022888 | 3.2913 | 68.8568 | 68.4448 | 115.48 | 123.5458 | 3.0167 | 123.555 | 84.3979 | -0.28381 | 123.5458 | 3.0167 | 84.3979 | 115.48 | 123.555 | -123.8525 | -123.8617
3483.7188 | 123.8525 | -61.3815 | 62.1872 | -0.20729 | 0.012606 | 0.014695 | 0.013174 | 0.057898 | -0.00054693 | 0.077981 | -58.4198 | 62.1185 | -61.6928 | -61.5097 | 54.1763 | 23.0209 | 7.5348 | 7.1228 | 62.1506 | -61.6699 | -0.31128 | -0.068665 | 2.9617 | -0.12817 | -8.0109 | -0.28839 | -0.036621 | 3.273 | 68.9163 | 68.5043 | 115.5579 | 123.5001 | 2.9617 | 123.5321 | 84.4025 | -0.28839 | 123.5001 | 2.9617 | 84.4025 | 115.5579 | 123.5321 | -123.88 | -123.8571
3484.7188 | 123.8434 | -61.4319 | 62.1643 | 0.082626 | 0.014101 | 0.011704 | 0.0093288 | 0.058966 | 0.0013757 | 0.08204 | -58.4747 | 62.1048 | -61.6928 | -61.5921 | 54.0985 | 22.966 | 7.5531 | 7.0496 | 62.1323 | -61.6882 | -0.26093 | -0.05951 | 2.9572 | -0.16022 | -8.0658 | -0.25635 | -0.032044 | 3.2181 | 68.985 | 68.4814 | 115.5304 | 123.5367 | 2.9572 | 123.5641 | 84.3979 | -0.25635 | 123.5367 | 2.9572 | 84.3979 | 115.5304 | 123.5641 | -123.8571 | -123.8525
3485.7188 | 123.8251 | -61.3998 | 62.1918 | 0.03685 | 0.015597 | 0.01555 | 0.0097562 | 0.05918 | 0.00073487 | 0.078835 | -58.5159 | 62.0911 | -61.6699 | -61.5875 | 54.0344 | 22.879 | 7.5943 | 7.0496 | 62.1048 | -61.7111 | -0.27008 | -0.10071 | 2.8839 | -0.18768 | -8.1573 | -0.31128 | -0.086975 | 3.154 | 68.9941 | 68.4494 | 115.4343 | 123.4909 | 2.8839 | 123.5046 | 84.2789 | -0.31128 | 123.4909 | 2.8839 | 84.2789 | 115.4343 | 123.5046 | -123.8617 | -123.9029
3486.7188 | 123.8159 | -61.4273 | 62.146 | 0.12077 | 0.014956 | 0.012345 | 0.012533 | 0.060034 | -0.00033333 | 0.080544 | -58.4061 | 62.0911 | -61.7111 | -61.5738 | 54.126 | 22.9706 | 7.5073 | 7.045 | 62.1231 | -61.6745 | -0.28381 | -0.054932 | 3.0212 | -0.14648 | -8.02 | -0.24719 | -0.022888 | 3.3051 | 68.9346 | 68.4723 | 115.5533 | 123.5184 | 3.0212 | 123.5504 | 84.3979 | -0.24719 | 123.5184 | 3.0212 | 84.3979 | 115.5533 | 123.5504 | -123.8571 | -123.8205
3487.7188 | 123.8159 | -61.4136 | 62.146 | 0.17418 | 0.01581 | 0.01854 | 0.0093288 | 0.059821 | 0.00052127 | 0.080972 | -58.4473 | 62.0819 | -61.7065 | -61.5692 | 54.0939 | 22.9568 | 7.4844 | 6.9855 | 62.1048 | -61.7111 | -0.29297 | -0.064087 | 2.9663 | -0.15564 | -8.0521 | -0.29755 | -0.041199 | 3.2593 | 68.898 | 68.399 | 115.5075 | 123.4955 | 2.9663 | 123.5184 | 84.3704 | -0.29755 | 123.4955 | 2.9663 | 84.3704 | 115.5075 | 123.5184 | -123.8525 | -123.8571
3488.7188 | 123.8388 | -61.377 | 62.1964 | -0.19203 | 0.01346 | 0.012132 | 0.011892 | 0.058112 | -0.0018285 | 0.079049 | -58.3694 | 62.1552 | -61.7111 | -61.5234 | 54.0665 | 22.9385 | 7.6309 | 7.1365 | 62.1506 | -61.6791 | -0.33417 | -0.041199 | 3.0075 | -0.14648 | -8.1299 | -0.30212 | -0.045776 | 3.3417 | 69.0079 | 68.5135 | 115.4434 | 123.5321 | 3.0075 | 123.5275 | 84.3155 | -0.30212 | 123.5321 | 3.0075 | 84.3155 | 115.4434 | 123.5275 | -123.9075 | -123.8754
3489.7188 | 123.8617 | -61.3953 | 62.1597 | -0.024185 | 0.012606 | 0.012345 | 0.011038 | 0.058753 | -0.00076053 | 0.078835 | -58.4564 | 62.1094 | -61.7203 | -61.5875 | 54.0573 | 22.9248 | 7.7179 | 7.1823 | 62.1506 | -61.647 | -0.32501 | -0.050354 | 2.9388 | -0.19226 | -8.1024 | -0.25177 | -0.009155 | 3.2639 | 69.1132 | 68.5776 | 115.4526 | 123.5046 | 2.9388 | 123.5458 | 84.3201 | -0.25177 | 123.5046 | 2.9388 | 84.3201 | 115.4526 | 123.5458 | -123.88 | -123.8068
3490.7188 | 123.8754 | -61.377 | 62.1552 | -0.031814 | 0.013033 | 0.011064 | 0.010183 | 0.058325 | -0.00054693 | 0.080117 | -58.461 | 62.1094 | -61.7157 | -61.5646 | 54.1992 | 22.998 | 7.5439 | 7.1136 | 62.146 | -61.6608 | -0.33875 | -0.045776 | 2.916 | -0.18768 | -7.9559 | -0.28381 | -0.009155 | 3.2547 | 68.9209 | 68.4906 | 115.5762 | 123.4863 | 2.916 | 123.5229 | 84.375 | -0.28381 | 123.4863 | 2.916 | 84.375 | 115.5762 | 123.5229 | -123.8708 | -123.8159
3491.7188 | 123.8617 | -61.409 | 62.1689 | 0.013962 | 0.015383 | 0.012345 | 0.010824 | 0.057471 | 0.0018031 | 0.082681 | -58.4518 | 62.1094 | -61.6837 | -61.5509 | 54.1946 | 22.9752 | 7.5073 | 7.0908 | 62.1277 | -61.6791 | -0.27466 | -0.059509 | 2.9572 | -0.14191 | -7.9742 | -0.27008 | -0.041198 | 3.2318 | 68.9163 | 68.4998 | 115.6036 | 123.5184 | 2.9572 | 123.5367 | 84.3842 | -0.27008 | 123.5184 | 2.9572 | 84.3842 | 115.6036 | 123.5367 | -123.8525 | -123.848
3492.7188 | 123.8571 | -61.4044 | 62.178 | -0.0089264 | 0.014101 | 0.011064 | 0.0093288 | 0.056617 | -0.00011953 | 0.080544 | -58.4564 | 62.0819 | -61.7157 | -61.5463 | 54.3045 | 23.1216 | 7.5256 | 7.1136 | 62.1368 | -61.6608 | -0.31128 | -0.096131 | 2.948 | -0.14191 | -7.8735 | -0.25635 | -0.041199 | 3.2593 | 68.9301 | 68.5181 | 115.7089 | 123.4863 | 2.948 | 123.5413 | 84.5261 | -0.25635 | 123.4863 | 2.948 | 84.5261 | 115.7089 | 123.5413 | -123.8937 | -123.8388
3493.7188 | 123.7839 | -61.4273 | 62.1964 | -0.13863 | 0.016451 | 0.018113 | 0.017233 | 0.060889 | -0.00033333 | 0.078622 | -58.4015 | 62.1872 | -61.7157 | -61.5417 | 54.1992 | 23.0209 | 7.6263 | 7.0862 | 62.1735 | -61.7111 | -0.28839 | -0.009155 | 3.0258 | -0.11444 | -7.9971 | -0.28381 | -0.022888 | 3.3142 | 69.0537 | 68.5135 | 115.6265 | 123.6145 | 3.0258 | 123.6008 | 84.4482 | -0.28381 | 123.6145 | 3.0258 | 84.4482 | 115.6265 | 123.6008 | -123.912 | -123.9075
3494.7188 | 123.8709 | -61.3998 | 62.1872 | 0.059738 | 0.01346 | 0.014054 | 0.0093288 | 0.060889 | -0.0026831 | 0.078622 | -58.4793 | 62.0911 | -61.7157 | -61.3907 | 54.2862 | 22.9568 | 7.5394 | 7.0724 | 62.1414 | -61.6745 | -0.31586 | -0.096131 | 2.9205 | 0.009155 | -7.901 | -0.27466 | -0.045777 | 3.2364 | 68.9392 | 68.4723 | 115.686 | 123.4909 | 2.9205 | 123.5413 | 84.3567 | -0.27466 | 123.4909 | 2.9205 | 84.3567 | 115.686 | 123.5413 | -123.9029 | -123.8617
3495.7188 | 123.8846 | -61.3907 | 62.1872 | -0.0012969 | 0.014956 | 0.012559 | 0.0080472 | 0.057898 | 0.00030767 | 0.081613 | -58.4518 | 62.0956 | -61.702 | -61.5601 | 54.2862 | 23.0621 | 7.5851 | 7.1228 | 62.1231 | -61.6699 | -0.31128 | -0.091553 | 2.9388 | -0.16937 | -7.901 | -0.27924 | -0.064087 | 3.2501 | 68.9758 | 68.5135 | 115.6769 | 123.4863 | 2.9388 | 123.5138 | 84.4528 | -0.27924 | 123.4863 | 2.9388 | 84.4528 | 115.6769 | 123.5138 | -123.8892 | -123.8571
3496.7188 | 123.88 | -61.4136 | 62.1689 | -0.0012969 | 0.012606 | 0.011277 | 0.008688 | 0.057471 | -0.00011953 | 0.081399 | -58.4839 | 62.1185 | -61.7157 | -61.5509 | 54.2358 | 23.0759 | 7.5897 | 7.132 | 62.146 | -61.647 | -0.30212 | -0.050354 | 2.9297 | -0.13733 | -7.933 | -0.23346 | -0.022888 | 3.2318 | 69.0033 | 68.5455 | 115.6494 | 123.5321 | 2.9297 | 123.5596 | 84.4894 | -0.23346 | 123.5321 | 2.9297 | 84.4894 | 115.6494 | 123.5596 | -123.8846 | -123.8159
3497.7188 | 123.8663 | -61.377 | 62.1643 | -0.16151 | 0.01282 | 0.013841 | 0.0078336 | 0.059394 | 0.00052127 | 0.078408 | -58.4381 | 62.1002 | -61.6928 | -61.5097 | 54.364 | 23.1583 | 7.5256 | 7.1686 | 62.1231 | -61.6516 | -0.31586 | -0.064087 | 2.9388 | -0.13275 | -7.8003 | -0.27466 | -0.041199 | 3.2547 | 68.9026 | 68.5455 | 115.741 | 123.4772 | 2.9388 | 123.5001 | 84.5352 | -0.27466 | 123.4772 | 2.9388 | 84.5352 | 115.741 | 123.5001 | -123.8571 | -123.8159
3498.7188 | 123.7885 | -61.3815 | 62.2284 | -0.38277 | 0.015383 | 0.013413 | 0.011679 | 0.057471 | -0.0014013 | 0.080758 | -58.461 | 62.1643 | -61.6837 | -61.5921 | 54.1809 | 23.0347 | 7.695 | 6.9901 | 62.178 | -61.7065 | -0.30212 | -0.064087 | 2.9205 | -0.21057 | -8.0475 | -0.32501 | -0.050354 | 3.2227 | 69.0765 | 68.3716 | 115.5624 | 123.5458 | 2.9205 | 123.5596 | 84.4162 | -0.32501 | 123.5458 | 2.9205 | 84.4162 | 115.5624 | 123.5596 | -123.912 | -123.9349
3499.7188 | 123.9029 | -61.3678 | 62.178 | -0.10811 | 0.013888 | 0.012559 | 0.0063382 | 0.059821 | 9.4068e-05 | 0.080331 | -58.4335 | 62.1094 | -61.6745 | -61.5005 | 54.2679 | 23.1354 | 7.5348 | 7.1869 | 62.146 | -61.6425 | -0.3067 | -0.068665 | 2.9343 | -0.13275 | -7.9102 | -0.27466 | -0.032044 | 3.241 | 68.9026 | 68.5547 | 115.6357 | 123.4772 | 2.9343 | 123.5138 | 84.5032 | -0.27466 | 123.4772 | 2.9343 | 84.5032 | 115.6357 | 123.5138 | -123.8525 | -123.8205
3500.7188 | 123.8892 | -61.3907 | 62.1964 | 0.021591 | 0.014315 | 0.0132 | 0.0078336 | 0.058112 | -0.0016149 | 0.079476 | -58.5342 | 62.0865 | -61.6974 | -61.5601 | 54.245 | 23.1125 | 7.5897 | 7.1503 | 62.1185 | -61.6653 | -0.3067 | -0.10986 | 2.8564 | -0.16937 | -7.9514 | -0.27466 | -0.07782 | 3.1631 | 68.9804 | 68.541 | 115.6357 | 123.4772 | 2.8564 | 123.5092 | 84.5032 | -0.27466 | 123.4772 | 2.8564 | 84.5032 | 115.6357 | 123.5092 | -123.8937 | -123.8617
3501.7188 | 123.8617 | -61.4044 | 62.1689 | -0.024185 | 0.015597 | 0.0087138 | 0.011038 | 0.05918 | 9.4068e-05 | 0.079049 | -58.4656 | 62.0911 | -61.6791 | -61.5738 | 54.2175 | 23.1537 | 7.5851 | 7.1228 | 62.1094 | -61.6699 | -0.27466 | -0.07782 | 2.9388 | -0.16937 | -7.9514 | -0.2655 | -0.059509 | 3.2135 | 68.9896 | 68.5272 | 115.6219 | 123.4955 | 2.9388 | 123.5138 | 84.5581 | -0.2655 | 123.4955 | 2.9388 | 84.5581 | 115.6219 | 123.5138 | -123.848 | -123.8388
3502.7188 | 123.8937 | -61.3861 | 62.1918 | -0.054703 | 0.013247 | 0.011918 | 0.0093288 | 0.058539 | 0.00073487 | 0.079904 | -58.4381 | 62.114 | -61.7065 | -61.528 | 54.2725 | 23.2132 | 7.5348 | 7.1457 | 62.1048 | -61.6653 | -0.32044 | -0.077819 | 2.948 | -0.14191 | -7.9193 | -0.27924 | -0.086975 | 3.2684 | 68.9209 | 68.5318 | 115.6586 | 123.5001 | 2.948 | 123.4909 | 84.5993 | -0.27924 | 123.5001 | 2.948 | 84.5993 | 115.6586 | 123.4909 | -123.8983 | -123.8571
3503.7188 | 123.793 | -61.4273 | 62.2375 | -0.23018 | 0.014529 | 0.0097818 | 0.015524 | 0.057257 | -0.0031103 | 0.081826 | -58.4885 | 62.2147 | -61.7157 | -61.7477 | 53.9978 | 23.0209 | 7.6859 | 6.958 | 62.1643 | -61.702 | -0.28839 | -0.022888 | 2.9388 | -0.32044 | -8.2397 | -0.27466 | -0.073242 | 3.2272 | 69.1132 | 68.3853 | 115.4251 | 123.642 | 2.9388 | 123.5916 | 84.4482 | -0.27466 | 123.642 | 2.9388 | 84.4482 | 115.4251 | 123.5916 | -123.9532 | -123.9395
3504.7188 | 123.9944 | -61.3586 | 62.2696 | -0.14626 | 0.013888 | 0.011064 | 0.0080472 | 0.061103 | 0.0011621 | 0.078835 | -58.4015 | 62.1002 | -61.6745 | -61.496 | 54.2816 | 23.1903 | 7.5439 | 7.1823 | 62.1368 | -61.6287 | -0.31586 | -0.16937 | 2.9572 | -0.13733 | -7.988 | -0.27008 | -0.13275 | 3.273 | 68.9026 | 68.541 | 115.6403 | 123.4589 | 2.9572 | 123.4955 | 84.549 | -0.27008 | 123.4589 | 2.9572 | 84.549 | 115.6403 | 123.4955 | -123.9441 | -123.8983
3505.7188 | 123.9029 | -61.3724 | 62.2101 | -0.16151 | 0.01282 | 0.01085 | 0.0089016 | 0.056403 | -0.00076053 | 0.077767 | -58.4015 | 62.0865 | -61.6882 | -61.4822 | 54.4373 | 23.2864 | 7.5165 | 7.196 | 62.1506 | -61.6287 | -0.31586 | -0.1236 | 2.9709 | -0.10986 | -7.7728 | -0.25635 | -0.059509 | 3.2867 | 68.8889 | 68.5684 | 115.8096 | 123.4589 | 2.9709 | 123.5229 | 84.6588 | -0.25635 | 123.4589 | 2.9709 | 84.6588 | 115.8096 | 123.5229 | -123.8983 | -123.8388
3506.7188 | 123.9212 | -61.3907 | 62.1918 | -0.17677 | 0.014101 | 0.01085 | 0.010397 | 0.05918 | 0.00052127 | 0.077981 | -58.4015 | 62.1002 | -61.6837 | -61.4777 | 54.4235 | 23.2361 | 7.5714 | 7.2464 | 62.1414 | -61.6379 | -0.29297 | -0.091552 | 2.9892 | -0.086975 | -7.7682 | -0.24719 | -0.050354 | 3.2822 | 68.9621 | 68.6371 | 115.8142 | 123.4909 | 2.9892 | 123.5321 | 84.6268 | -0.24719 | 123.4909 | 2.9892 | 84.6268 | 115.8142 | 123.5321 | -123.8754 | -123.8297
3507.7188 | 123.8709 | -61.3907 | 62.1918 | -0.069961 | 0.012392 | 0.012986 | 0.0097562 | 0.057257 | 0.00073487 | 0.079263 | -58.4381 | 62.1277 | -61.7065 | -61.5189 | 54.4785 | 23.2361 | 7.5668 | 7.1594 | 62.1048 | -61.6791 | -0.31586 | -0.064086 | 2.9526 | -0.12817 | -7.7133 | -0.28839 | -0.086975 | 3.2684 | 68.9575 | 68.5501 | 115.8691 | 123.5184 | 2.9526 | 123.4955 | 84.6268 | -0.28839 | 123.5184 | 2.9526 | 84.6268 | 115.8691 | 123.4955 | -123.8983 | -123.8708
3508.7188 | 123.7839 | -61.4273 | 62.2009 | -0.3141 | 0.016665 | 0.014909 | 0.014883 | 0.060248 | 0.00094847 | 0.080972 | -58.4793 | 62.1918 | -61.7157 | -61.5921 | 54.2313 | 23.2681 | 7.8781 | 6.8161 | 62.1872 | -61.7294 | -0.28839 | -0.009156 | 2.948 | -0.16479 | -7.9697 | -0.30212 | -0.013733 | 3.2364 | 69.3054 | 68.2434 | 115.6586 | 123.6191 | 2.948 | 123.6145 | 84.6954 | -0.30212 | 123.6191 | 2.948 | 84.6954 | 115.6586 | 123.6145 | -123.9166 | -123.9304
3509.7188 | 123.8754 | -61.3403 | 62.1918 | -0.15388 | 0.013033 | 0.013413 | 0.010824 | 0.059821 | -0.00011953 | 0.079263 | -58.4106 | 62.1002 | -61.6928 | -61.5005 | 54.5197 | 23.3185 | 7.5302 | 7.196 | 62.1277 | -61.6425 | -0.35248 | -0.091552 | 2.9297 | -0.16022 | -7.6721 | -0.30212 | -0.064086 | 3.2822 | 68.8705 | 68.5364 | 115.86 | 123.4406 | 2.9297 | 123.468 | 84.6588 | -0.30212 | 123.4406 | 2.9297 | 84.6588 | 115.86 | 123.468 | -123.8846 | -123.8342
3510.7188 | 123.9166 | -61.3953 | 62.1872 | -0.13863 | 0.01346 | 0.009141 | 0.0089016 | 0.060675 | -0.00011953 | 0.080758 | -58.3969 | 62.0819 | -61.6974 | -61.5005 | 54.5105 | 23.2361 | 7.5165 | 7.1594 | 62.1323 | -61.6516 | -0.30212 | -0.10529 | 2.9984 | -0.10529 | -7.6767 | -0.25635 | -0.054932 | 3.3005 | 68.9117 | 68.5547 | 115.9058 | 123.4772 | 2.9984 | 123.5275 | 84.6313 | -0.25635 | 123.4772 | 2.9984 | 84.6313 | 115.9058 | 123.5275 | -123.8846 | -123.8388
3511.7188 | 123.7839 | -61.409 | 62.2238 | -0.24544 | 0.013888 | 0.012773 | 0.010183 | 0.058539 | -0.00097413 | 0.078622 | -58.4518 | 62.1368 | -61.7203 | -61.5692 | 54.4464 | 23.2269 | 7.6492 | 7.077 | 62.1552 | -61.6882 | -0.31128 | -0.086975 | 2.9572 | -0.16022 | -7.7774 | -0.27923 | -0.068665 | 3.2684 | 69.0582 | 68.486 | 115.8554 | 123.5458 | 2.9572 | 123.5641 | 84.6359 | -0.27923 | 123.5458 | 2.9572 | 84.6359 | 115.8554 | 123.5641 | -123.9441 | -123.912
3512.7188 | 123.8434 | -61.3632 | 62.1735 | -0.24544 | 0.013033 | 0.012986 | 0.010183 | 0.059821 | 0.0015893 | 0.078195 | -58.4244 | 62.1414 | -61.6791 | -61.5051 | 54.483 | 23.2681 | 7.5211 | 7.1274 | 62.1094 | -61.6745 | -0.31586 | -0.032044 | 2.9388 | -0.14191 | -7.6904 | -0.31128 | -0.064087 | 3.2547 | 68.8843 | 68.4906 | 115.8463 | 123.5046 | 2.9388 | 123.4726 | 84.6313 | -0.31128 | 123.5046 | 2.9388 | 84.6313 | 115.8463 | 123.4726 | -123.8525 | -123.848
3513.7188 | 123.8022 | -61.4044 | 62.2284 | -0.20729 | 0.016024 | 0.012559 | 0.016165 | 0.061103 | -0.00033333 | 0.079904 | -58.4793 | 62.2055 | -61.7065 | -61.6058 | 54.3823 | 23.1949 | 7.7087 | 7.045 | 62.2055 | -61.7294 | -0.30212 | -0.022889 | 2.9251 | -0.20142 | -7.8461 | -0.32501 | -0.022889 | 3.2272 | 69.1132 | 68.4494 | 115.7867 | 123.6099 | 2.9251 | 123.6099 | 84.5993 | -0.32501 | 123.6099 | 2.9251 | 84.5993 | 115.7867 | 123.6099 | -123.9349 | -123.9578
3514.7188 | 123.7564 | -61.3541 | 62.1689 | -0.1844 | 0.011111 | 0.0132 | 0.0074062 | 0.06153 | -0.0016149 | 0.081399 | -58.4198 | 62.1185 | -61.6882 | -61.5051 | 54.451 | 23.3505 | 7.5577 | 7.4661 | 62.178 | -61.6287 | -0.33417 | -0.050354 | 2.9343 | -0.15106 | -7.7179 | -0.27466 | 0.009156 | 3.2684 | 68.9117 | 68.8202 | 115.8051 | 123.4726 | 2.9343 | 123.5321 | 84.7046 | -0.27466 | 123.4726 | 2.9343 | 84.7046 | 115.8051 | 123.5321 | -123.8571 | -123.7976
3515.7188 | 123.8983 | -61.377 | 62.1552 | -0.21492 | 0.014101 | 0.012345 | 0.0097562 | 0.060889 | -0.0011877 | 0.079904 | -58.4015 | 62.1094 | -61.6882 | -61.5143 | 54.5151 | 23.3231 | 8.0841 | 7.3929 | 62.1918 | -61.6104 | -0.31128 | -0.045776 | 2.9755 | -0.13733 | -7.6401 | -0.23346 | 0.036621 | 3.2867 | 69.4611 | 68.7698 | 115.892 | 123.4863 | 2.9755 | 123.5687 | 84.7 | -0.23346 | 123.4863 | 2.9755 | 84.7 | 115.892 | 123.5687 | -123.8434 | -123.7656
3516.7188 | 123.8617 | -61.3724 | 62.2009 | -0.17677 | 0.01282 | 0.011918 | 0.012106 | 0.059607 | -0.00054693 | 0.079904 | -58.4152 | 62.114 | -61.6653 | -61.5189 | 54.4922 | 23.2773 | 7.6675 | 7.2006 | 62.1277 | -61.6516 | -0.29297 | -0.086975 | 2.9572 | -0.14648 | -7.7087 | -0.27924 | -0.073242 | 3.2501 | 69.0399 | 68.573 | 115.8646 | 123.4863 | 2.9572 | 123.5001 | 84.6497 | -0.27924 | 123.4863 | 2.9572 | 84.6497 | 115.8646 | 123.5001 | -123.8663 | -123.8525
3517.7188 | 123.8342 | -61.3815 | 62.1826 | -0.16151 | 0.011538 | 0.013413 | 0.011465 | 0.059821 | -0.0011877 | 0.080117 | -58.3923 | 62.1185 | -61.7157 | -61.528 | 54.5151 | 23.2681 | 7.6492 | 7.1823 | 62.146 | -61.6379 | -0.33417 | -0.064087 | 2.9892 | -0.14648 | -7.6675 | -0.25635 | -0.036621 | 3.3234 | 69.0308 | 68.5638 | 115.8966 | 123.5001 | 2.9892 | 123.5275 | 84.6497 | -0.25635 | 123.5001 | 2.9892 | 84.6497 | 115.8966 | 123.5275 | -123.8983 | -123.8205
3518.7188 | 123.793 | -61.3907 | 62.2009 | -0.19203 | 0.018587 | 0.011491 | 0.017447 | 0.061957 | -0.00097413 | 0.081826 | -58.4015 | 62.2284 | -61.6745 | -61.5601 | 54.364 | 23.0988 | 7.6447 | 7.0404 | 62.1643 | -61.7249 | -0.28381 | 0.027466 | 2.9892 | -0.16937 | -7.8369 | -0.33417 | -0.036621 | 3.273 | 69.0353 | 68.4311 | 115.7547 | 123.6191 | 2.9892 | 123.555 | 84.4894 | -0.33417 | 123.6191 | 2.9892 | 84.4894 | 115.7547 | 123.555 | -123.8754 | -123.9258
3519.7188 | 123.7564 | -61.4319 | 62.2421 | -0.2607 | 0.015597 | 0.012773 | 0.011251 | 0.059394 | -0.0020421 | 0.07969 | -58.4793 | 62.1872 | -61.6974 | -61.6104 | 54.3961 | 23.0621 | 7.7454 | 7.045 | 62.1872 | -61.6699 | -0.2655 | -0.054931 | 2.9526 | -0.17853 | -7.8461 | -0.23804 | -0.054931 | 3.2181 | 69.1772 | 68.4769 | 115.8279 | 123.6191 | 2.9526 | 123.6191 | 84.494 | -0.23804 | 123.6191 | 2.9526 | 84.494 | 115.8279 | 123.6191 | -123.9395 | -123.912
3520.7188 | 123.7747 | -61.4182 | 62.2238 | -0.24544 | 0.016665 | 0.0132 | 0.01232 | 0.06153 | -0.00054693 | 0.080544 | -58.4702 | 62.1643 | -61.7386 | -61.5875 | 54.3365 | 23.0988 | 7.7271 | 7.0404 | 62.1964 | -61.6837 | -0.32043 | -0.059509 | 2.948 | -0.16937 | -7.8873 | -0.2655 | -0.027466 | 3.2684 | 69.1452 | 68.4586 | 115.7547 | 123.5825 | 2.948 | 123.6145 | 84.5169 | -0.2655 | 123.5825 | 2.948 | 84.5169 | 115.7547 | 123.6145 | -123.9624 | -123.9075
3521.7344 | 123.848 | -61.4182 | 62.1597 | 0.25047 | 0.014315 | 0.013627 | 0.014242 | 0.061316 | -0.0020421 | 0.079049 | -58.4152 | 62.1597 | -61.7203 | -61.5967 | 54.3503 | 23.1995 | 7.5851 | 7.0908 | 62.1323 | -61.6837 | -0.30212 | 0 | 3.0029 | -0.17853 | -7.8094 | -0.2655 | -0.027466 | 3.3051 | 69.0033 | 68.5089 | 115.7684 | 123.5779 | 3.0029 | 123.5504 | 84.6176 | -0.2655 | 123.5779 | 3.0029 | 84.6176 | 115.7684 | 123.5504 | -123.88 | -123.8434
3522.7188 | 123.8434 | -61.3998 | 62.178 | -0.24544 | 0.013888 | 0.0132 | 0.0091152 | 0.060034 | 0.00030767 | 0.080117 | -58.4015 | 62.1506 | -61.6837 | -61.5417 | 54.3549 | 23.204 | 7.6767 | 7.1823 | 62.1552 | -61.6562 | -0.28381 | -0.027466 | 2.9984 | -0.14191 | -7.8232 | -0.25635 | -0.022889 | 3.2822 | 69.0765 | 68.5822 | 115.7547 | 123.5504 | 2.9984 | 123.555 | 84.6039 | -0.25635 | 123.5504 | 2.9984 | 84.6039 | 115.7547 | 123.555 | -123.8617 | -123.8342
3523.7188 | 123.793 | -61.4365 | 62.1872 | -0.054703 | 0.017092 | 0.014909 | 0.01766 | 0.063666 | 0.0013757 | 0.079904 | -58.429 | 62.2192 | -61.6974 | -61.5875 | 54.3274 | 23.1171 | 7.7179 | 7.0862 | 62.1643 | -61.7065 | -0.26093 | 0.032043 | 3.0075 | -0.15106 | -7.8598 | -0.27008 | -0.022888 | 3.2684 | 69.1544 | 68.5226 | 115.7639 | 123.6557 | 3.0075 | 123.6008 | 84.5535 | -0.27008 | 123.6557 | 3.0075 | 84.5535 | 115.7639 | 123.6008 | -123.8846 | -123.8937
3524.7188 | 123.7747 | -61.4227 | 62.2147 | -0.3904 | 0.015169 | 0.0080728 | 0.013601 | 0.060675 | -0.0014013 | 0.079904 | -58.5342 | 62.2101 | -61.734 | -61.6104 | 54.2816 | 23.1308 | 7.7454 | 7.0541 | 62.2009 | -61.6882 | -0.31128 | -0.004578 | 2.8885 | -0.18768 | -7.933 | -0.2655 | -0.013733 | 3.1998 | 69.1681 | 68.4769 | 115.7043 | 123.6328 | 2.8885 | 123.6237 | 84.5535 | -0.2655 | 123.6328 | 2.8885 | 84.5535 | 115.7043 | 123.6237 | -123.9487 | -123.9029
3525.7188 | 123.761 | -61.4227 | 62.233 | -0.27596 | 0.016024 | 0.012986 | 0.012747 | 0.062812 | -0.00076053 | 0.081185 | -58.5205 | 62.2009 | -61.7294 | -61.615 | 54.2908 | 23.0896 | 7.7683 | 7.0587 | 62.2101 | -61.6928 | -0.3067 | -0.032043 | 2.9022 | -0.19226 | -7.9422 | -0.27008 | -0.022888 | 3.2089 | 69.191 | 68.4814 | 115.7135 | 123.6237 | 2.9022 | 123.6328 | 84.5123 | -0.27008 | 123.6237 | 2.9022 | 84.5123 | 115.7135 | 123.6328 | -123.9624 | -123.9258
3526.7344 | 123.8709 | -61.4273 | 62.1231 | 0.21996 | 0.014956 | 0.012986 | 0.0097562 | 0.063239 | -0.00011953 | 0.080972 | -58.3237 | 62.1231 | -61.7249 | -61.5234 | 54.3823 | 23.1949 | 7.5348 | 7.1411 | 62.1277 | -61.702 | -0.29755 | 0 | 3.1036 | -0.09613 | -7.7408 | -0.27466 | 0.004578 | 3.4012 | 68.9621 | 68.5684 | 115.8096 | 123.5504 | 3.1036 | 123.555 | 84.6222 | -0.27466 | 123.5504 | 3.1036 | 84.6222 | 115.8096 | 123.555 | -123.848 | -123.8251
3527.7188 | 123.7839 | -61.441 | 62.2238 | -0.30647 | 0.016878 | 0.01555 | 0.013174 | 0.059821 | -0.00011953 | 0.078622 | -58.5022 | 62.2009 | -61.734 | -61.6333 | 54.4418 | 23.2224 | 7.7728 | 7.077 | 62.1872 | -61.7111 | -0.29297 | -0.022888 | 2.9388 | -0.19226 | -7.782 | -0.27008 | -0.036621 | 3.2318 | 69.2139 | 68.5181 | 115.8829 | 123.642 | 2.9388 | 123.6282 | 84.6634 | -0.27008 | 123.642 | 2.9388 | 84.6634 | 115.8829 | 123.6282 | -123.9578 | -123.9349
3528.7188 | 123.7839 | -61.4319 | 62.2192 | -0.30647 | 0.015383 | 0.016618 | 0.011679 | 0.060462 | -0.0014013 | 0.080972 | -58.4656 | 62.1872 | -61.6928 | -61.6241 | 54.3777 | 23.2315 | 7.8278 | 7.1411 | 62.1964 | -61.7157 | -0.26093 | -0.032043 | 2.9663 | -0.19226 | -7.8415 | -0.28381 | -0.022888 | 3.2272 | 69.2596 | 68.573 | 115.8096 | 123.6191 | 2.9663 | 123.6282 | 84.6634 | -0.28381 | 123.6191 | 2.9663 | 84.6634 | 115.8096 | 123.6282 | -123.912 | -123.9349
3529.7188 | 123.7427 | -61.4182 | 62.2192 | -0.19966 | 0.014529 | 0.01085 | 0.011892 | 0.060889 | 9.4068e-05 | 0.079476 | -58.4747 | 62.1872 | -61.7111 | -61.6333 | 54.3411 | 23.2315 | 7.7683 | 7.1091 | 62.1826 | -61.702 | -0.29297 | -0.032043 | 2.9434 | -0.21515 | -7.8781 | -0.28381 | -0.036621 | 3.2364 | 69.1864 | 68.5272 | 115.7593 | 123.6053 | 2.9434 | 123.6008 | 84.6497 | -0.28381 | 123.6053 | 2.9434 | 84.6497 | 115.7593 | 123.6008 | -123.9304 | -123.9212
3530.7188 | 123.7701 | -61.4182 | 62.2192 | 0.17418 | 0.017947 | 0.013413 | 0.01296 | 0.062384 | -0.0020421 | 0.078835 | -58.4747 | 62.2192 | -61.7432 | -61.6013 | 54.3594 | 23.2132 | 7.8232 | 7.0953 | 62.1964 | -61.7065 | -0.32501 | 0 | 2.9434 | -0.1831 | -7.8598 | -0.28839 | -0.022888 | 3.2684 | 69.2413 | 68.5135 | 115.7776 | 123.6374 | 2.9434 | 123.6145 | 84.6313 | -0.28839 | 123.6374 | 2.9434 | 84.6313 | 115.7776 | 123.6145 | -123.9624 | -123.9258
3531.7344 | 123.8709 | -61.409 | 62.1643 | 0.14366 | 0.017092 | 0.011491 | 0.014669 | 0.064307 | -0.00097413 | 0.079904 | -58.4106 | 62.1414 | -61.7523 | -61.5921 | 54.3365 | 23.1903 | 7.5989 | 7.1045 | 62.1414 | -61.7157 | -0.34332 | -0.022889 | 2.9984 | -0.1831 | -7.8278 | -0.3067 | -0.022889 | 3.3417 | 69.0079 | 68.5135 | 115.7455 | 123.5504 | 2.9984 | 123.5504 | 84.5993 | -0.3067 | 123.5504 | 2.9984 | 84.5993 | 115.7455 | 123.5504 | -123.9166 | -123.88
3532.7188 | 123.8068 | -61.409 | 62.2147 | -0.19203 | 0.01581 | 0.013413 | 0.01531 | 0.061957 | 0.00052127 | 0.080544 | -58.4656 | 62.2192 | -61.734 | -61.6013 | 54.3732 | 23.204 | 7.8094 | 7.1045 | 62.1918 | -61.7249 | -0.32501 | 0.004577 | 2.9434 | -0.19226 | -7.8415 | -0.31586 | -0.022889 | 3.2684 | 69.2184 | 68.5135 | 115.7822 | 123.6282 | 2.9434 | 123.6008 | 84.613 | -0.31586 | 123.6282 | 2.9434 | 84.613 | 115.7822 | 123.6008 | -123.9487 | -123.9395
3533.7188 | 123.761 | -61.441 | 62.1735 | 0.03685 | 0.017519 | 0.017899 | 0.016165 | 0.064093 | -0.0014013 | 0.079904 | -58.4381 | 62.2147 | -61.7157 | -61.6379 | 54.2999 | 23.1674 | 7.6996 | 7.0541 | 62.1735 | -61.7111 | -0.27466 | 0.041199 | 3.0029 | -0.19684 | -7.8735 | -0.27008 | 0 | 3.2776 | 69.1406 | 68.4952 | 115.741 | 123.6557 | 3.0029 | 123.6145 | 84.6085 | -0.27008 | 123.6557 | 3.0029 | 84.6085 | 115.741 | 123.6145 | -123.8892 | -123.8846
3534.7188 | 123.7793 | -61.4182 | 62.1872 | -0.23018 | 0.014529 | 0.016404 | 0.01232 | 0.06388 | -0.0020421 | 0.079476 | -58.4564 | 62.2238 | -61.7203 | -61.6241 | 54.2862 | 23.1949 | 7.8049 | 7.1274 | 62.2192 | -61.7203 | -0.30212 | 0.036621 | 2.9617 | -0.20599 | -7.901 | -0.30212 | 0.032043 | 3.2639 | 69.223 | 68.5455 | 115.7043 | 123.642 | 2.9617 | 123.6374 | 84.613 | -0.30212 | 123.642 | 2.9617 | 84.613 | 115.7043 | 123.6374 | -123.9075 | -123.9075
3535.7188 | 123.7793 | -61.4365 | 62.2238 | -0.27596 | 0.014529 | 0.012132 | 0.0091152 | 0.063666 | -0.00033333 | 0.078622 | -58.5022 | 62.2101 | -61.7203 | -61.6425 | 54.2908 | 23.3597 | 7.8873 | 6.8344 | 62.2192 | -61.7065 | -0.28381 | -0.013733 | 2.9343 | -0.20599 | -7.933 | -0.27008 | -0.004578 | 3.2181 | 69.3237 | 68.2709 | 115.7272 | 123.6465 | 2.9343 | 123.6557 | 84.7961 | -0.27008 | 123.6465 | 2.9343 | 84.7961 | 115.7272 | 123.6557 | -123.9441 | -123.9304
3536.7188 | 123.8022 | -61.4365 | 62.2604 | -0.16151 | 0.016024 | 0.011704 | 0.011465 | 0.062812 | -0.0011877 | 0.078835 | -58.5068 | 62.2284 | -61.7294 | -61.6379 | 54.364 | 23.3185 | 7.8369 | 7.0816 | 62.2147 | -61.7111 | -0.29297 | -0.032043 | 2.9297 | -0.20142 | -7.8964 | -0.27466 | -0.045776 | 3.2227 | 69.2734 | 68.5181 | 115.8005 | 123.6649 | 2.9297 | 123.6511 | 84.7549 | -0.27466 | 123.6649 | 2.9297 | 84.7549 | 115.8005 | 123.6511 | -123.9899 | -123.9716
3537.7188 | 123.7564 | -61.441 | 62.2192 | -0.35225 | 0.014956 | 0.011704 | 0.011892 | 0.061957 | 0.00052127 | 0.079904 | -58.4885 | 62.233 | -61.7203 | -61.6241 | 54.3503 | 23.2727 | 7.8049 | 7.0724 | 62.2009 | -61.7203 | -0.27924 | 0.013733 | 2.9526 | -0.18311 | -7.869 | -0.27924 | -0.01831 | 3.2318 | 69.2459 | 68.5135 | 115.7913 | 123.674 | 2.9526 | 123.642 | 84.7137 | -0.27924 | 123.674 | 2.9526 | 84.7137 | 115.7913 | 123.642 | -123.9395 | -123.9395
3538.7188 | 123.7747 | -61.4227 | 62.1918 | -0.016556 | 0.017947 | 0.01854 | 0.014029 | 0.063666 | 0.00073487 | 0.077981 | -58.3694 | 62.2147 | -61.7249 | -61.6058 | 54.3503 | 23.3597 | 7.7362 | 7.0129 | 62.1964 | -61.7203 | -0.30213 | 0.022889 | 3.0533 | -0.18311 | -7.8415 | -0.29755 | 0.004578 | 3.3554 | 69.1589 | 68.4357 | 115.773 | 123.6374 | 3.0533 | 123.6191 | 84.7824 | -0.29755 | 123.6374 | 3.0533 | 84.7824 | 115.773 | 123.6191 | -123.9166 | -123.912
3539.7188 | 123.7885 | -61.4365 | 62.2147 | -0.29121 | 0.016238 | 0.015977 | 0.013174 | 0.063452 | -0.00097413 | 0.081185 | -58.4381 | 62.2055 | -61.7111 | -61.6104 | 54.4189 | 23.2773 | 7.7454 | 7.045 | 62.2147 | -61.702 | -0.27466 | -0.009156 | 2.9984 | -0.17395 | -7.7957 | -0.2655 | 0 | 3.273 | 69.1818 | 68.4814 | 115.8554 | 123.642 | 2.9984 | 123.6511 | 84.7137 | -0.2655 | 123.642 | 2.9984 | 84.7137 | 115.8554 | 123.6511 | -123.9258 | -123.9166
3540.7188 | 123.8022 | -61.4319 | 62.1918 | -0.19203 | 0.016451 | 0.014268 | 0.013601 | 0.065589 | 9.4068e-05 | 0.079049 | -58.4518 | 62.2238 | -61.7249 | -61.6058 | 54.4418 | 23.3231 | 7.7454 | 7.0038 | 62.2192 | -61.702 | -0.29297 | 0.032044 | 2.98 | -0.17395 | -7.7499 | -0.27008 | 0.027466 | 3.273 | 69.1772 | 68.4357 | 115.8737 | 123.6557 | 2.98 | 123.6511 | 84.7549 | -0.27008 | 123.6557 | 2.98 | 84.7549 | 115.8737 | 123.6511 | -123.9166 | -123.8937
3541.7188 | 123.8022 | -61.4044 | 62.2009 | -0.16151 | 0.016878 | 0.017686 | 0.01296 | 0.062598 | -0.00054693 | 0.080544 | -58.4702 | 62.2101 | -61.7203 | -61.6058 | 54.3549 | 23.259 | 7.7637 | 7.0221 | 62.2147 | -61.734 | -0.31586 | 0.009155 | 2.9343 | -0.20142 | -7.8461 | -0.32959 | 0.013733 | 3.2501 | 69.1681 | 68.4265 | 115.7593 | 123.6145 | 2.9343 | 123.6191 | 84.6634 | -0.32959 | 123.6145 | 2.9343 | 84.6634 | 115.7593 | 123.6191 | -123.9212 | -123.9349
3542.7188 | 123.7289 | -61.4319 | 62.233 | -0.29121 | 0.015169 | 0.0082864 | 0.008688 | 0.062171 | 0.00030767 | 0.077981 | -58.2825 | 62.233 | -61.6974 | -61.6287 | 54.3594 | 23.2498 | 7.8323 | 7.0404 | 62.2192 | -61.734 | -0.2655 | 0 | 3.1494 | -0.19684 | -7.8735 | -0.30212 | -0.013733 | 3.4149 | 69.2642 | 68.4723 | 115.7913 | 123.6649 | 3.1494 | 123.6511 | 84.6817 | -0.30212 | 123.6649 | 3.1494 | 84.6817 | 115.7913 | 123.6511 | -123.9304 | -123.967
3543.7188 | 123.7701 | -61.4273 | 62.1872 | 0.013962 | 0.016451 | 0.017686 | 0.015951 | 0.063025 | 9.4068e-05 | 0.077554 | -58.4061 | 62.1826 | -61.7294 | -61.6516 | 54.2999 | 23.204 | 7.7637 | 6.9992 | 62.2055 | -61.7432 | -0.30212 | -0.004578 | 3.0212 | -0.2243 | -7.8873 | -0.31586 | 0.01831 | 3.3234 | 69.191 | 68.4265 | 115.7272 | 123.6099 | 3.0212 | 123.6328 | 84.6313 | -0.31586 | 123.6099 | 3.0212 | 84.6313 | 115.7272 | 123.6328 | -123.9166 | -123.9304
3544.7188 | 123.8022 | -61.4319 | 62.2238 | -0.19203 | 0.017306 | 0.015977 | 0.011038 | 0.064307 | -0.00076053 | 0.078835 | -58.3832 | 62.2192 | -61.7203 | -61.6287 | 54.3594 | 23.2819 | 7.8003 | 6.9946 | 62.2284 | -61.702 | -0.28839 | -0.004578 | 3.0487 | -0.19684 | -7.8644 | -0.27008 | 0.004578 | 3.3371 | 69.2322 | 68.4265 | 115.7913 | 123.6511 | 3.0487 | 123.6603 | 84.7137 | -0.27008 | 123.6511 | 3.0487 | 84.7137 | 115.7913 | 123.6603 | -123.9441 | -123.9258
3545.7188 | 123.7885 | -61.4182 | 62.2055 | -0.10048 | 0.015383 | 0.013413 | 0.014456 | 0.06388 | 0.0011621 | 0.082467 | -58.3282 | 62.2055 | -61.734 | -61.5829 | 54.3915 | 23.3002 | 7.7225 | 6.9992 | 62.2238 | -61.7432 | -0.31586 | 0 | 3.0899 | -0.16479 | -7.814 | -0.32501 | 0.018311 | 3.4058 | 69.1406 | 68.4174 | 115.8096 | 123.6237 | 3.0899 | 123.642 | 84.7183 | -0.32501 | 123.6237 | 3.0899 | 84.7183 | 115.8096 | 123.642 | -123.9395 | -123.9487
3546.7188 | 123.8068 | -61.4365 | 62.2009 | -0.13863 | 0.016878 | 0.015977 | 0.014242 | 0.063239 | -0.0016149 | 0.081399 | -58.3328 | 62.2055 | -61.7111 | -61.5921 | 54.3869 | 23.3139 | 7.6767 | 6.9763 | 62.1964 | -61.734 | -0.27466 | 0.004577 | 3.1036 | -0.15564 | -7.814 | -0.29755 | -0.004578 | 3.3783 | 69.1132 | 68.4128 | 115.8234 | 123.642 | 3.1036 | 123.6328 | 84.7504 | -0.29755 | 123.642 | 3.1036 | 84.7504 | 115.8234 | 123.6328 | -123.912 | -123.9349
3547.7188 | 123.7976 | -61.409 | 62.1964 | -0.20729 | 0.014742 | 0.012986 | 0.011679 | 0.065161 | 9.4068e-05 | 0.082467 | -58.429 | 62.2375 | -61.7111 | -61.5967 | 54.3823 | 23.2773 | 7.7316 | 7.0221 | 62.1964 | -61.734 | -0.30212 | 0.041199 | 2.98 | -0.18768 | -7.814 | -0.32501 | 0 | 3.2822 | 69.1406 | 68.4311 | 115.7913 | 123.6465 | 2.98 | 123.6053 | 84.6863 | -0.32501 | 123.6465 | 2.98 | 84.6863 | 115.7913 | 123.6053 | -123.9075 | -123.9304
3548.7188 | 123.7839 | -61.4502 | 62.1643 | -0.82527 | 0.01581 | 0.013627 | 0.014883 | 0.062812 | -0.00076053 | 0.081826 | -58.5068 | 62.2101 | -61.7569 | -61.6837 | 54.2725 | 23.1903 | 7.6401 | 6.8985 | 62.2101 | -61.7386 | -0.3067 | 0.045776 | 2.9434 | -0.23346 | -7.8918 | -0.28839 | 0.045776 | 3.2501 | 69.0903 | 68.3487 | 115.7227 | 123.6603 | 2.9434 | 123.6603 | 84.6405 | -0.28839 | 123.6603 | 2.9434 | 84.6405 | 115.7227 | 123.6603 | -123.9212 | -123.9029
3549.7188 | 123.7885 | -61.4182 | 62.1964 | -0.1844 | 0.018587 | 0.01555 | 0.01232 | 0.063452 | 0.00073487 | 0.079904 | -58.3832 | 62.2421 | -61.702 | -61.6196 | 54.3549 | 23.2361 | 7.7454 | 7.0038 | 62.233 | -61.7203 | -0.28381 | 0.045776 | 3.035 | -0.20142 | -7.8415 | -0.30212 | 0.036621 | 3.3188 | 69.1635 | 68.4219 | 115.773 | 123.6603 | 3.035 | 123.6511 | 84.6542 | -0.30212 | 123.6603 | 3.035 | 84.6542 | 115.773 | 123.6511 | -123.8983 | -123.9166
3550.7188 | 123.7518 | -61.4227 | 62.2009 | -0.15388 | 0.01346 | 0.011918 | 0.011892 | 0.062598 | -0.00076053 | 0.080331 | -58.4976 | 62.2101 | -61.7249 | -61.6333 | 54.3457 | 23.2361 | 7.7271 | 6.9855 | 62.2421 | -61.7294 | -0.30213 | 0.009155 | 2.9251 | -0.21057 | -7.8552 | -0.3067 | 0.041198 | 3.2272 | 69.1498 | 68.4082 | 115.7684 | 123.6328 | 2.9251 | 123.6649 | 84.6588 | -0.3067 | 123.6328 | 2.9251 | 84.6588 | 115.7684 | 123.6649 | -123.9258 | -123.9304
3551.7188 | 123.8022 | -61.4227 | 62.1918 | -0.15388 | 0.016878 | 0.01555 | 0.014883 | 0.064948 | 0.00030767 | 0.078835 | -58.3237 | 62.233 | -61.6974 | -61.5829 | 54.3777 | 23.3047 | 7.7316 | 7.0084 | 62.2147 | -61.7203 | -0.27466 | 0.041199 | 3.0991 | -0.16022 | -7.814 | -0.29755 | 0.022889 | 3.3737 | 69.1544 | 68.4311 | 115.8005 | 123.6557 | 3.0991 | 123.6374 | 84.7275 | -0.29755 | 123.6557 | 3.0991 | 84.7275 | 115.8005 | 123.6374 | -123.8892 | -123.912
3552.7188 | 123.8113 | -61.4365 | 62.178 | 0.0063326 | 0.017733 | 0.017045 | 0.013815 | 0.06687 | 0.00052127 | 0.078195 | -58.3466 | 62.2147 | -61.7111 | -61.5051 | 54.3274 | 23.259 | 7.6813 | 6.9946 | 62.233 | -61.7294 | -0.27466 | 0.036621 | 3.0899 | -0.068665 | -7.8506 | -0.29297 | 0.054931 | 3.3646 | 69.1177 | 68.4311 | 115.7639 | 123.6511 | 3.0899 | 123.6694 | 84.6954 | -0.29297 | 123.6511 | 3.0899 | 84.6954 | 115.7639 | 123.6694 | -123.8892 | -123.9075
3553.7188 | 123.7656 | -61.4639 | 62.1826 | 0.16655 | 0.022646 | 0.02089 | 0.01296 | 0.064734 | 0.0011621 | 0.078835 | -58.7311 | 62.1277 | -61.7889 | -61.7157 | 54.277 | 23.2269 | 7.6813 | 6.8893 | 62.2009 | -61.7569 | -0.32501 | -0.054931 | 2.7328 | -0.25177 | -7.9056 | -0.29297 | 0.018311 | 3.0579 | 69.1452 | 68.3533 | 115.741 | 123.5916 | 2.7328 | 123.6649 | 84.6909 | -0.29297 | 123.5916 | 2.7328 | 84.6909 | 115.741 | 123.6649 | -123.9716 | -123.9395
3554.7188 | 123.8113 | -61.4273 | 62.1735 | -0.0089264 | 0.015597 | 0.015122 | 0.011679 | 0.064093 | 0.0015893 | 0.079263 | -58.3786 | 62.2284 | -61.7157 | -61.5921 | 54.5425 | 23.1857 | 7.6309 | 7.0862 | 62.1918 | -61.7569 | -0.28839 | 0.054932 | 3.0487 | -0.16479 | -7.6309 | -0.32959 | 0.01831 | 3.3371 | 69.0582 | 68.5135 | 115.9698 | 123.6557 | 3.0487 | 123.6191 | 84.613 | -0.32959 | 123.6557 | 3.0487 | 84.613 | 115.9698 | 123.6191 | -123.8892 | -123.9304
3555.7188 | 123.7106 | -61.4319 | 62.1689 | -0.10048 | 0.017519 | 0.012559 | 0.01296 | 0.064948 | 0.0011621 | 0.079049 | -58.3237 | 62.2101 | -61.7065 | -61.5921 | 54.3503 | 23.3185 | 7.6492 | 6.9809 | 62.2192 | -61.7294 | -0.27466 | 0.041199 | 3.1082 | -0.16022 | -7.8186 | -0.29755 | 0.050354 | 3.3829 | 69.0811 | 68.4128 | 115.7822 | 123.642 | 3.1082 | 123.6511 | 84.7504 | -0.29755 | 123.642 | 3.1082 | 84.7504 | 115.7822 | 123.6511 | -123.8754 | -123.8983
3556.7188 | 123.7885 | -61.409 | 62.1918 | -0.26833 | 0.017092 | 0.015977 | 0.012533 | 0.064093 | -0.00033333 | 0.082681 | -58.3511 | 62.2513 | -61.7157 | -61.6104 | 54.3457 | 23.2224 | 7.6492 | 6.9443 | 62.2421 | -61.7203 | -0.3067 | 0.05951 | 3.0579 | -0.20142 | -7.8461 | -0.31128 | 0.050354 | 3.3646 | 69.0582 | 68.3533 | 115.7547 | 123.6603 | 3.0579 | 123.6511 | 84.6313 | -0.31128 | 123.6603 | 3.0579 | 84.6313 | 115.7547 | 123.6511 | -123.9075 | -123.912
3557.7188 | 123.7793 | -61.4044 | 62.1918 | -0.08522 | 0.01581 | 0.018754 | 0.013174 | 0.064734 | -0.00011953 | 0.078195 | -58.342 | 62.233 | -61.7386 | -61.5921 | 54.4281 | 23.291 | 7.6035 | 6.9901 | 62.2101 | -61.7249 | -0.33417 | 0.041199 | 3.0624 | -0.18768 | -7.7637 | -0.32044 | 0.018311 | 3.3966 | 69.0079 | 68.3945 | 115.8325 | 123.6374 | 3.0624 | 123.6145 | 84.6954 | -0.32044 | 123.6374 | 3.0624 | 84.6954 | 115.8325 | 123.6145 | -123.9304 | -123.9166
3558.7188 | 123.7381 | -61.4548 | 62.1872 | 0.074997 | 0.016451 | 0.015977 | 0.013388 | 0.065161 | 0.0013757 | 0.080758 | -58.4564 | 62.2147 | -61.7386 | -61.6882 | 54.3594 | 23.1812 | 7.6584 | 6.8893 | 62.1918 | -61.7615 | -0.28381 | 0.027466 | 2.9984 | -0.23346 | -7.8278 | -0.3067 | 0.004577 | 3.2822 | 69.1132 | 68.3441 | 115.8142 | 123.6694 | 2.9984 | 123.6465 | 84.6359 | -0.3067 | 123.6694 | 2.9984 | 84.6359 | 115.8142 | 123.6465 | -123.9258 | -123.9487
3559.7188 | 123.793 | -61.4273 | 62.1689 | -0.10811 | 0.02051 | 0.014695 | 0.01296 | 0.064734 | -0.00011953 | 0.080544 | -58.5068 | 62.1735 | -61.7157 | -61.6058 | 54.3549 | 23.259 | 7.6218 | 6.9672 | 62.2147 | -61.7203 | -0.28839 | 0.004578 | 2.9205 | -0.17853 | -7.814 | -0.29297 | 0.045777 | 3.2089 | 69.0491 | 68.3945 | 115.7822 | 123.6008 | 2.9205 | 123.642 | 84.6863 | -0.29297 | 123.6008 | 2.9205 | 84.6863 | 115.7822 | 123.642 | -123.8846 | -123.8892
3560.7188 | 123.8068 | -61.409 | 62.2055 | -0.031814 | 0.01282 | 0.018968 | 0.010824 | 0.06623 | -0.00097413 | 0.080758 | -58.3786 | 62.1826 | -61.734 | -61.5967 | 54.4418 | 23.2544 | 7.6218 | 6.9901 | 62.2101 | -61.7432 | -0.32501 | -0.022888 | 3.0304 | -0.18768 | -7.7637 | -0.33417 | 0.004578 | 3.3554 | 69.0308 | 68.399 | 115.8508 | 123.5916 | 3.0304 | 123.6191 | 84.6634 | -0.33417 | 123.5916 | 3.0304 | 84.6634 | 115.8508 | 123.6191 | -123.9395 | -123.9487
3561.7188 | 123.7701 | -61.409 | 62.178 | -0.12337 | 0.017519 | 0.016618 | 0.013601 | 0.066443 | 0.00094847 | 0.081613 | -58.374 | 62.1964 | -61.7111 | -61.6379 | 54.2038 | 23.1033 | 7.7454 | 6.9305 | 62.2147 | -61.7386 | -0.30212 | 0.01831 | 3.035 | -0.22888 | -7.9742 | -0.32959 | 0.036621 | 3.3371 | 69.1544 | 68.3395 | 115.6128 | 123.6053 | 3.035 | 123.6237 | 84.5123 | -0.32959 | 123.6053 | 3.035 | 84.5123 | 115.6128 | 123.6237 | -123.8892 | -123.9166
3562.7188 | 123.793 | -61.4227 | 62.2055 | -0.22255 | 0.016665 | 0.015336 | 0.014669 | 0.064734 | 0.00073487 | 0.079263 | -58.4015 | 62.2467 | -61.7386 | -61.6058 | 54.3823 | 23.2956 | 7.6538 | 6.9809 | 62.2238 | -61.7157 | -0.31586 | 0.041199 | 3.0212 | -0.18311 | -7.8232 | -0.29297 | 0.018311 | 3.3371 | 69.0765 | 68.4036 | 115.8051 | 123.6694 | 3.0212 | 123.6465 | 84.7183 | -0.29297 | 123.6694 | 3.0212 | 84.7183 | 115.8051 | 123.6465 | -123.9441 | -123.9212
3563.7188 | 123.7427 | -61.441 | 62.2009 | 0.090256 | 0.017733 | 0.015763 | 0.01232 | 0.065375 | -0.00011953 | 0.080544 | -58.4793 | 62.2147 | -61.7477 | -61.6928 | 54.3823 | 23.3597 | 7.0953 | 6.6925 | 62.1414 | -61.7706 | -0.3067 | 0.013733 | 2.9617 | -0.25177 | -7.8186 | -0.32959 | -0.05951 | 3.2684 | 68.5364 | 68.1335 | 115.8234 | 123.6557 | 2.9617 | 123.5825 | 84.8007 | -0.32959 | 123.6557 | 2.9617 | 84.8007 | 115.8234 | 123.5825 | -123.9487 | -123.9716
3564.7188 | 123.7747 | -61.4044 | 62.1689 | -0.09285 | 0.016665 | 0.017045 | 0.013388 | 0.06388 | 9.4068e-05 | 0.081185 | -58.4015 | 62.2375 | -61.6928 | -61.5829 | 54.3915 | 23.1903 | 7.6401 | 6.9717 | 62.1964 | -61.7386 | -0.28839 | 0.068665 | 3.0029 | -0.17853 | -7.7774 | -0.33417 | 0.027466 | 3.2913 | 69.0445 | 68.3762 | 115.7959 | 123.642 | 3.0029 | 123.6008 | 84.5947 | -0.33417 | 123.642 | 3.0029 | 84.5947 | 115.7959 | 123.6008 | -123.8617 | -123.9075
3565.7188 | 123.7976 | -61.4548 | 62.2009 | -0.10811 | 0.018587 | 0.015763 | 0.014242 | 0.064307 | -0.00076053 | 0.079904 | -58.3923 | 62.2238 | -61.7065 | -61.6013 | 54.364 | 23.14 | 7.6584 | 6.9901 | 62.2147 | -61.7249 | -0.25177 | 0.022888 | 3.0624 | -0.14648 | -7.8369 | -0.27008 | 0.013733 | 3.3142 | 69.1132 | 68.4448 | 115.8188 | 123.6786 | 3.0624 | 123.6694 | 84.5947 | -0.27008 | 123.6786 | 3.0624 | 84.5947 | 115.8188 | 123.6694 | -123.9075 | -123.9258
3566.7188 | 123.761 | -61.4182 | 62.2009 | -0.73372 | 0.016451 | 0.019181 | 0.013388 | 0.065589 | 0.00052127 | 0.079476 | -58.4427 | 62.2055 | -61.7249 | -61.5875 | 54.3503 | 23.1674 | 7.6675 | 7.0084 | 62.233 | -61.7294 | -0.3067 | 0.004577 | 2.9755 | -0.16937 | -7.8506 | -0.31128 | 0.032043 | 3.2822 | 69.0857 | 68.4265 | 115.7684 | 123.6237 | 2.9755 | 123.6511 | 84.5856 | -0.31128 | 123.6237 | 2.9755 | 84.5856 | 115.7684 | 123.6511 | -123.9258 | -123.9304
3567.7188 | 123.7885 | -61.4227 | 62.1643 | -0.054703 | 0.017092 | 0.016404 | 0.014456 | 0.064307 | -0.00097413 | 0.079263 | -58.4564 | 62.1964 | -61.7294 | -61.6196 | 54.2953 | 23.0942 | 7.6218 | 6.9901 | 62.2467 | -61.7203 | -0.3067 | 0.032043 | 2.9663 | -0.19684 | -7.869 | -0.29755 | 0.082397 | 3.273 | 69.0445 | 68.4128 | 115.7181 | 123.6191 | 2.9663 | 123.6694 | 84.5169 | -0.29755 | 123.6191 | 2.9663 | 84.5169 | 115.7181 | 123.6694 | -123.8937 | -123.8846
3568.7188 | 123.8113 | -61.4365 | 62.146 | 0.16655 | 0.01581 | 0.015763 | 0.0095424 | 0.065375 | 0.0022303 | 0.082253 | -58.461 | 62.178 | -61.7432 | -61.6653 | 54.2404 | 23.1445 | 7.5577 | 6.9305 | 62.1689 | -61.734 | -0.3067 | 0.032044 | 2.9755 | -0.22888 | -7.9056 | -0.29755 | 0.022888 | 3.2822 | 68.9941 | 68.367 | 115.6769 | 123.6145 | 2.9755 | 123.6053 | 84.581 | -0.29755 | 123.6145 | 2.9755 | 84.581 | 115.6769 | 123.6053 | -123.8892 | -123.88
3569.7188 | 123.8342 | -61.4227 | 62.2055 | -0.12337 | 0.016665 | 0.014268 | 0.014456 | 0.065375 | 0.0020167 | 0.081613 | -58.4564 | 62.2421 | -61.7111 | -61.6058 | 54.3228 | 23.1812 | 7.6767 | 6.9809 | 62.2238 | -61.7523 | -0.28839 | 0.036621 | 2.9663 | -0.18311 | -7.8827 | -0.32959 | 0.018311 | 3.2547 | 69.0994 | 68.4036 | 115.7455 | 123.6649 | 2.9663 | 123.6465 | 84.6039 | -0.32959 | 123.6649 | 2.9663 | 84.6039 | 115.7455 | 123.6465 | -123.9166 | -123.9578
3570.7188 | 123.8205 | -61.4227 | 62.2009 | -0.14626 | 0.017306 | 0.014482 | 0.012106 | 0.064521 | 0.00073487 | 0.082467 | -58.4152 | 62.2559 | -61.7249 | -61.5921 | 54.2862 | 23.0988 | 7.695 | 7.0267 | 62.2375 | -61.7294 | -0.30213 | 0.054931 | 3.0075 | -0.16937 | -7.9147 | -0.3067 | 0.036621 | 3.3096 | 69.1177 | 68.4494 | 115.7089 | 123.6786 | 3.0075 | 123.6603 | 84.5215 | -0.3067 | 123.6786 | 3.0075 | 84.5215 | 115.7089 | 123.6603 | -123.9258 | -123.9304
3571.7188 | 123.7656 | -61.409 | 62.178 | -0.15388 | 0.018587 | 0.018754 | 0.013815 | 0.064734 | -0.0016149 | 0.082253 | -58.3969 | 62.2009 | -61.7065 | -61.5921 | 54.2496 | 23.1445 | 7.6309 | 6.9534 | 62.2375 | -61.7432 | -0.29755 | 0.022888 | 3.0121 | -0.1831 | -7.9285 | -0.33417 | 0.059509 | 3.3096 | 69.0399 | 68.3624 | 115.6586 | 123.6099 | 3.0121 | 123.6465 | 84.5535 | -0.33417 | 123.6099 | 3.0121 | 84.5535 | 115.6586 | 123.6465 | -123.8846 | -123.9212
3572.7188 | 123.7976 | -61.4182 | 62.178 | -0.15388 | 0.015597 | 0.015977 | 0.013388 | 0.063239 | -0.0020421 | 0.080331 | -58.3832 | 62.2009 | -61.7203 | -61.6013 | 54.2816 | 23.1491 | 7.6126 | 6.9717 | 62.2055 | -61.7249 | -0.30212 | 0.022888 | 3.035 | -0.1831 | -7.8964 | -0.3067 | 0.027465 | 3.3371 | 69.0308 | 68.3899 | 115.6998 | 123.6191 | 3.035 | 123.6237 | 84.5673 | -0.3067 | 123.6191 | 3.035 | 84.5673 | 115.6998 | 123.6237 | -123.8983 | -123.9029
3573.7344 | 123.8937 | -61.3815 | 62.1643 | 0.23521 | 0.015597 | 0.017686 | 0.0095424 | 0.065802 | -0.00054693 | 0.081185 | -58.4106 | 62.1277 | -61.6928 | -61.5051 | 54.1946 | 23.0209 | 7.7133 | 7.164 | 62.1552 | -61.7157 | -0.31128 | -0.036621 | 2.9709 | -0.1236 | -7.9697 | -0.33417 | -0.009156 | 3.2822 | 69.0948 | 68.5455 | 115.5762 | 123.5092 | 2.9709 | 123.5367 | 84.4025 | -0.33417 | 123.5092 | 2.9709 | 84.4025 | 115.5762 | 123.5367 | -123.8571 | -123.88
3574.7188 | 123.8159 | -61.4227 | 62.1826 | -1.1762 | 0.018587 | 0.014482 | 0.014883 | 0.063025 | 0.00052127 | 0.080758 | -58.4198 | 62.2147 | -61.7249 | -61.5875 | 54.277 | 23.2086 | 7.695 | 7.0084 | 62.2009 | -61.7661 | -0.30213 | 0.032044 | 3.0029 | -0.1648 | -7.9056 | -0.34332 | 0.018311 | 3.3051 | 69.1177 | 68.4311 | 115.6998 | 123.6374 | 3.0029 | 123.6237 | 84.6313 | -0.34332 | 123.6374 | 3.0029 | 84.6313 | 115.6998 | 123.6237 | -123.9075 | -123.9487
3575.7188 | 123.7747 | -61.4227 | 62.2101 | -0.0089264 | 0.018374 | 0.015977 | 0.015097 | 0.064307 | -0.00033333 | 0.07969 | -58.58 | 62.1826 | -61.7432 | -61.5967 | 54.277 | 23.2407 | 7.6859 | 7.0038 | 62.2238 | -61.7432 | -0.32044 | -0.027466 | 2.8427 | -0.17395 | -7.933 | -0.32044 | 0.013733 | 3.1631 | 69.1086 | 68.4265 | 115.6998 | 123.6053 | 2.8427 | 123.6465 | 84.6634 | -0.32044 | 123.6053 | 2.8427 | 84.6634 | 115.6998 | 123.6465 | -123.9532 | -123.9532
3576.7188 | 123.7885 | -61.409 | 62.1964 | -0.13863 | 0.016024 | 0.015977 | 0.014029 | 0.063666 | -0.00097413 | 0.080758 | -58.4106 | 62.2192 | -61.702 | -61.5829 | 54.2633 | 23.2086 | 7.7362 | 7.0221 | 62.2513 | -61.7477 | -0.29297 | 0.022888 | 2.9984 | -0.17395 | -7.933 | -0.33875 | 0.054932 | 3.2913 | 69.1452 | 68.4311 | 115.6723 | 123.6282 | 2.9984 | 123.6603 | 84.6176 | -0.33875 | 123.6282 | 2.9984 | 84.6176 | 115.6723 | 123.6603 | -123.8983 | -123.9441
3577.7188 | 123.8022 | -61.4365 | 62.1826 | -0.21492 | 0.016238 | 0.016618 | 0.01232 | 0.064521 | -0.0026831 | 0.080544 | -58.4152 | 62.2284 | -61.7249 | -61.5829 | 54.245 | 23.1491 | 7.7042 | 6.9946 | 62.2559 | -61.7569 | -0.28839 | 0.045777 | 3.0212 | -0.14648 | -7.9376 | -0.32044 | 0.073242 | 3.3096 | 69.1406 | 68.4311 | 115.6815 | 123.6649 | 3.0212 | 123.6923 | 84.5856 | -0.32044 | 123.6649 | 3.0212 | 84.5856 | 115.6815 | 123.6923 | -123.9075 | -123.9395
3578.7188 | 123.761 | -61.4502 | 62.2192 | 0.13603 | 0.018374 | 0.014909 | 0.01296 | 0.065589 | 0.00073487 | 0.081185 | -58.4976 | 62.2009 | -61.7569 | -61.6653 | 53.9841 | 22.8882 | 7.988 | 7.1777 | 62.1964 | -61.7569 | -0.3067 | -0.01831 | 2.9526 | -0.21515 | -8.2352 | -0.3067 | -0.022888 | 3.2593 | 69.4382 | 68.6279 | 115.4343 | 123.6511 | 2.9526 | 123.6465 | 84.3384 | -0.3067 | 123.6511 | 2.9526 | 84.3384 | 115.4343 | 123.6465 | -123.9761 | -123.9761
3579.7188 | 123.7885 | -61.4319 | 62.1964 | -0.16151 | 0.017519 | 0.019395 | 0.014242 | 0.065161 | -0.00033333 | 0.07969 | -58.3969 | 62.2009 | -61.7249 | -61.5967 | 54.2404 | 23.1903 | 7.7362 | 7.0267 | 62.2284 | -61.7294 | -0.29297 | 0.004578 | 3.035 | -0.16479 | -7.9559 | -0.29755 | 0.032044 | 3.3279 | 69.1681 | 68.4586 | 115.6723 | 123.6328 | 3.035 | 123.6603 | 84.6222 | -0.29755 | 123.6328 | 3.035 | 84.6222 | 115.6723 | 123.6603 | -123.9212 | -123.9258
3580.7188 | 123.8159 | -61.4044 | 62.1964 | -0.19966 | 0.014529 | 0.018327 | 0.014456 | 0.064307 | 0.0011621 | 0.080758 | -58.3923 | 62.2147 | -61.7157 | -61.5967 | 54.2358 | 23.2407 | 7.7225 | 6.9992 | 62.2147 | -61.7477 | -0.31128 | 0.018311 | 3.0121 | -0.19226 | -7.9605 | -0.34332 | 0.018311 | 3.3234 | 69.1269 | 68.4036 | 115.6403 | 123.6191 | 3.0121 | 123.6191 | 84.6451 | -0.34332 | 123.6191 | 3.0121 | 84.6451 | 115.6403 | 123.6191 | -123.912 | -123.9441
3581.7188 | 123.7885 | -61.4227 | 62.1964 | 1.1813 | 0.016024 | 0.012986 | 0.014456 | 0.065802 | -0.0011877 | 0.080972 | -58.287 | 62.2055 | -61.7432 | -61.6013 | 54.2267 | 23.2315 | 7.7087 | 7.0175 | 62.233 | -61.7249 | -0.32044 | 0.009155 | 3.1357 | -0.17853 | -7.9697 | -0.30213 | 0.036621 | 3.4561 | 69.1315 | 68.4402 | 115.6494 | 123.6282 | 3.1357 | 123.6557 | 84.6542 | -0.30213 | 123.6282 | 3.1357 | 84.6542 | 115.6494 | 123.6557 | -123.9395 | -123.9212
3582.7188 | 123.8068 | -61.4044 | 62.1872 | -0.054703 | 0.014956 | 0.0132 | 0.01232 | 0.063239 | 0.0015893 | 0.081613 | -58.4061 | 62.2055 | -61.7432 | -61.5967 | 54.2953 | 23.1766 | 7.6538 | 7.0221 | 62.2101 | -61.7386 | -0.33875 | 0.01831 | 2.9984 | -0.19226 | -7.8918 | -0.33417 | 0.022888 | 3.3371 | 69.0582 | 68.4265 | 115.6998 | 123.6099 | 2.9984 | 123.6145 | 84.581 | -0.33417 | 123.6099 | 2.9984 | 84.581 | 115.6998 | 123.6145 | -123.9304 | -123.9258
3583.7188 | 123.8022 | -61.4319 | 62.1506 | 0.19707 | 0.017733 | 0.018113 | 0.01296 | 0.06388 | 0.0011621 | 0.081613 | -58.4839 | 62.2055 | -61.7569 | -61.6653 | 54.245 | 23.1445 | 7.5897 | 6.9717 | 62.2009 | -61.7294 | -0.32501 | 0.054931 | 2.948 | -0.23346 | -7.9056 | -0.29755 | 0.050354 | 3.273 | 69.0216 | 68.4036 | 115.6769 | 123.6374 | 2.948 | 123.6328 | 84.5764 | -0.29755 | 123.6374 | 2.948 | 84.5764 | 115.6769 | 123.6328 | -123.9075 | -123.88
3584.7188 | 123.7839 | -61.4227 | 62.1826 | -0.27596 | 0.017519 | 0.013413 | 0.01531 | 0.064948 | 0.0013757 | 0.079263 | -58.4015 | 62.2238 | -61.7294 | -61.5784 | 54.2542 | 23.1812 | 7.7271 | 7.045 | 62.2467 | -61.7477 | -0.3067 | 0.041199 | 3.0212 | -0.15564 | -7.9285 | -0.32501 | 0.064087 | 3.3279 | 69.1498 | 68.4677 | 115.6769 | 123.6465 | 3.0212 | 123.6694 | 84.6039 | -0.32501 | 123.6465 | 3.0212 | 84.6039 | 115.6769 | 123.6694 | -123.912 | -123.9304
3585.7188 | 123.8892 | -61.4273 | 62.1735 | -0.13863 | 0.019015 | 0.014695 | 0.013601 | 0.064521 | -0.0014013 | 0.080972 | -58.4244 | 62.2375 | -61.7157 | -61.5921 | 54.3961 | 23.2178 | 7.7271 | 7.0587 | 62.2147 | -61.7386 | -0.28839 | 0.064087 | 3.0029 | -0.16479 | -7.7774 | -0.31128 | 0.041199 | 3.2913 | 69.1544 | 68.486 | 115.8234 | 123.6649 | 3.0029 | 123.642 | 84.6451 | -0.31128 | 123.6649 | 3.0029 | 84.6451 | 115.8234 | 123.642 | -123.8892 | -123.912
3586.7188 | 123.793 | -61.4365 | 62.1826 | -0.077591 | 0.017947 | 0.017045 | 0.012533 | 0.065375 | -0.0018285 | 0.08204 | -58.4061 | 62.2009 | -61.7203 | -61.6058 | 54.3365 | 23.1354 | 7.7454 | 7.0496 | 62.233 | -61.7523 | -0.28381 | 0.018311 | 3.0304 | -0.16937 | -7.8461 | -0.31586 | 0.050354 | 3.3142 | 69.1818 | 68.486 | 115.773 | 123.6374 | 3.0304 | 123.6694 | 84.5718 | -0.31586 | 123.6374 | 3.0304 | 84.5718 | 115.773 | 123.6694 | -123.9029 | -123.9349
3587.7188 | 123.7747 | -61.4319 | 62.2009 | 0.021591 | 0.017519 | 0.015122 | 0.013815 | 0.066443 | -0.00033333 | 0.079263 | -58.4015 | 62.2101 | -61.6928 | -61.6196 | 54.2587 | 23.0988 | 7.7774 | 7.0724 | 62.233 | -61.7432 | -0.26093 | 0.009155 | 3.0304 | -0.18768 | -7.9422 | -0.31128 | 0.032043 | 3.2913 | 69.2093 | 68.5043 | 115.6906 | 123.642 | 3.0304 | 123.6649 | 84.5306 | -0.31128 | 123.642 | 3.0304 | 84.5306 | 115.6906 | 123.6649 | -123.8937 | -123.9441
3588.7188 | 123.7289 | -61.4685 | 62.1735 | 0.052109 | 0.014742 | 0.019181 | 0.012747 | 0.06623 | -0.00054693 | 0.080758 | -58.4839 | 62.2101 | -61.7432 | -61.7111 | 54.2175 | 23.0759 | 7.7408 | 6.9489 | 62.2192 | -61.7798 | -0.27466 | 0.036621 | 2.9846 | -0.24262 | -7.9559 | -0.31128 | 0.045776 | 3.2593 | 69.2093 | 68.4174 | 115.686 | 123.6786 | 2.9846 | 123.6877 | 84.5444 | -0.31128 | 123.6786 | 2.9846 | 84.5444 | 115.686 | 123.6877 | -123.9166 | -123.9532
3589.7188 | 123.8113 | -61.3998 | 62.178 | -0.35225 | 0.017947 | 0.016404 | 0.015097 | 0.064307 | -0.0011877 | 0.080117 | -58.4335 | 62.2009 | -61.7203 | -61.6196 | 54.2908 | 23.1354 | 7.7042 | 7.0267 | 62.2284 | -61.7615 | -0.32043 | 0.022888 | 2.9663 | -0.21973 | -7.8873 | -0.36163 | 0.050354 | 3.2867 | 69.104 | 68.4265 | 115.6906 | 123.6008 | 2.9663 | 123.6282 | 84.5352 | -0.36163 | 123.6008 | 2.9663 | 84.5352 | 115.6906 | 123.6282 | -123.8983 | -123.9395
3590.7188 | 123.7656 | -61.4227 | 62.1597 | -0.12337 | 0.017947 | 0.012345 | 0.012106 | 0.065589 | -0.0033239 | 0.081185 | -58.4106 | 62.2284 | -61.7111 | -61.5875 | 54.2908 | 23.1583 | 7.782 | 7.0724 | 62.2284 | -61.734 | -0.28839 | 0.068665 | 3.0121 | -0.1648 | -7.869 | -0.31128 | 0.068665 | 3.3005 | 69.2047 | 68.4952 | 115.7135 | 123.6511 | 3.0121 | 123.6511 | 84.581 | -0.31128 | 123.6511 | 3.0121 | 84.581 | 115.7135 | 123.6511 | -123.8708 | -123.8937
3591.7188 | 123.8068 | -61.4365 | 62.1918 | -0.14626 | 0.019442 | 0.012559 | 0.014242 | 0.066016 | -0.0020421 | 0.081399 | -58.4198 | 62.2375 | -61.7477 | -61.5829 | 54.2679 | 23.0988 | 7.7683 | 7.0541 | 62.2238 | -61.7477 | -0.31128 | 0.045777 | 3.0167 | -0.14648 | -7.9239 | -0.31128 | 0.032044 | 3.3279 | 69.2047 | 68.4906 | 115.7043 | 123.674 | 3.0167 | 123.6603 | 84.5352 | -0.31128 | 123.674 | 3.0167 | 84.5352 | 115.7043 | 123.6603 | -123.9395 | -123.9395
3592.7188 | 123.7656 | -61.441 | 62.1918 | -0.72609 | 0.01581 | 0.017686 | 0.010824 | 0.066016 | 0.00094847 | 0.081613 | -58.4152 | 62.2101 | -61.7386 | -61.5921 | 54.277 | 23.1766 | 7.7316 | 7.0633 | 62.2101 | -61.7249 | -0.29755 | 0.018311 | 3.0258 | -0.15106 | -7.9147 | -0.28381 | 0.018311 | 3.3234 | 69.1727 | 68.5043 | 115.7181 | 123.6511 | 3.0258 | 123.6511 | 84.6176 | -0.28381 | 123.6511 | 3.0258 | 84.6176 | 115.7181 | 123.6511 | -123.9304 | -123.9166
3593.7188 | 123.848 | -61.409 | 62.1323 | 0.2047 | 0.016238 | 0.01555 | 0.0099698 | 0.063666 | 9.4068e-05 | 0.078408 | -58.429 | 62.114 | -61.7111 | -61.5967 | 54.3457 | 23.1628 | 7.5531 | 7.0908 | 62.1597 | -61.7203 | -0.30212 | -0.01831 | 2.98 | -0.18768 | -7.7866 | -0.31128 | 0.027466 | 3.2822 | 68.9621 | 68.4998 | 115.7547 | 123.523 | 2.98 | 123.5687 | 84.5718 | -0.31128 | 123.523 | 2.98 | 84.5718 | 115.7547 | 123.5687 | -123.8434 | -123.8525
3594.7188 | 123.761 | -61.4456 | 62.1735 | 0.021591 | 0.016665 | 0.020036 | 0.015524 | 0.064734 | 9.4068e-05 | 0.080117 | -58.4473 | 62.2147 | -61.7249 | -61.6196 | 54.3228 | 23.0988 | 7.7362 | 7.0496 | 62.2055 | -61.7569 | -0.27924 | 0.041199 | 2.9984 | -0.17395 | -7.8506 | -0.31128 | 0.032043 | 3.2776 | 69.1818 | 68.4952 | 115.7684 | 123.6603 | 2.9984 | 123.6511 | 84.5444 | -0.31128 | 123.6603 | 2.9984 | 84.5444 | 115.7684 | 123.6511 | -123.8983 | -123.9304
3595.7188 | 123.7427 | -61.4548 | 62.178 | -0.054703 | 0.016665 | 0.018968 | 0.013174 | 0.065802 | -0.0011877 | 0.080972 | -58.4473 | 62.233 | -61.7294 | -61.6379 | 54.332 | 23.053 | 7.6675 | 7.0541 | 62.2192 | -61.7706 | -0.27466 | 0.054931 | 3.0075 | -0.1831 | -7.8461 | -0.31586 | 0.041198 | 3.2822 | 69.1223 | 68.5089 | 115.7867 | 123.6877 | 3.0075 | 123.674 | 84.5078 | -0.31586 | 123.6877 | 3.0075 | 84.5078 | 115.7867 | 123.674 | -123.9075 | -123.9487
3596.7188 | 123.7656 | -61.4319 | 62.178 | -0.024185 | 0.016665 | 0.013841 | 0.014669 | 0.06623 | -0.00054693 | 0.08204 | -58.429 | 62.2238 | -61.7111 | -61.647 | 54.2908 | 23.0118 | 7.7362 | 7.077 | 62.2238 | -61.7706 | -0.27924 | 0.045776 | 3.0029 | -0.21515 | -7.8873 | -0.33874 | 0.045776 | 3.2822 | 69.1681 | 68.5089 | 115.7227 | 123.6557 | 3.0029 | 123.6557 | 84.4437 | -0.33874 | 123.6557 | 3.0029 | 84.4437 | 115.7227 | 123.6557 | -123.8892 | -123.9487
3597.7188 | 123.8251 | -61.4319 | 62.1872 | -0.12337 | 0.017306 | 0.01854 | 0.013174 | 0.063452 | 0.00052127 | 0.080331 | -58.4198 | 62.2147 | -61.7111 | -61.4777 | 54.364 | 22.998 | 7.7042 | 7.0816 | 62.2192 | -61.7294 | -0.27924 | 0.027466 | 3.0121 | -0.045776 | -7.8232 | -0.29755 | 0.032043 | 3.2913 | 69.136 | 68.5135 | 115.7959 | 123.6465 | 3.0121 | 123.6511 | 84.4299 | -0.29755 | 123.6465 | 3.0121 | 84.4299 | 115.7959 | 123.6511 | -123.8983 | -123.9166
3598.7188 | 123.7839 | -61.4365 | 62.1872 | 0.17418 | 0.023714 | 0.0132 | 0.01296 | 0.064948 | 9.4068e-05 | 0.081185 | -58.8181 | 62.1414 | -61.7889 | -61.7203 | 54.3228 | 22.966 | 7.6263 | 6.9214 | 62.2009 | -61.7661 | -0.35248 | -0.045777 | 2.6184 | -0.28381 | -7.8644 | -0.32959 | 0.013733 | 2.9709 | 69.0628 | 68.3578 | 115.7593 | 123.5779 | 2.6184 | 123.6374 | 84.4025 | -0.32959 | 123.5779 | 2.6184 | 84.4025 | 115.7593 | 123.6374 | -123.9761 | -123.9532
3599.7188 | 123.7793 | -61.4319 | 62.1872 | -0.024185 | 0.01816 | 0.014268 | 0.015097 | 0.066443 | -0.00097413 | 0.079904 | -58.429 | 62.2055 | -61.7203 | -61.6196 | 54.3457 | 22.998 | 7.7133 | 7.1136 | 62.2192 | -61.7615 | -0.28839 | 0.01831 | 3.0029 | -0.18768 | -7.8415 | -0.32959 | 0.032043 | 3.2913 | 69.1452 | 68.5455 | 115.7776 | 123.6374 | 3.0029 | 123.6511 | 84.4299 | -0.32959 | 123.6374 | 3.0029 | 84.4299 | 115.7776 | 123.6511 | -123.9075 | -123.9487
3600.7188 | 123.7793 | -61.4365 | 62.2055 | -0.069961 | 0.018374 | 0.014695 | 0.013388 | 0.06687 | -0.0020421 | 0.080544 | -58.4381 | 62.2147 | -61.7249 | -61.6196 | 54.3411 | 22.9843 | 7.7683 | 7.1411 | 62.2147 | -61.7294 | -0.28839 | 0.009156 | 2.9984 | -0.18311 | -7.8644 | -0.29297 | 0.009156 | 3.2867 | 69.2047 | 68.5776 | 115.7776 | 123.6511 | 2.9984 | 123.6511 | 84.4208 | -0.29297 | 123.6511 | 2.9984 | 84.4208 | 115.7776 | 123.6511 | -123.9304 | -123.9349
3601.7188 | 123.7518 | -61.4227 | 62.2101 | 0.03685 | 0.017733 | 0.013627 | 0.01531 | 0.066016 | 9.4068e-05 | 0.080117 | -58.4839 | 62.2375 | -61.7386 | -61.6608 | 54.2542 | 23.0164 | 7.7637 | 7.0541 | 62.2055 | -61.7569 | -0.31586 | 0.027466 | 2.9388 | -0.23804 | -7.9559 | -0.33417 | -0.004578 | 3.2547 | 69.1864 | 68.4769 | 115.6769 | 123.6603 | 2.9388 | 123.6282 | 84.4391 | -0.33417 | 123.6603 | 2.9388 | 84.4391 | 115.6769 | 123.6282 | -123.9487 | -123.967
3602.7188 | 123.8571 | -61.3953 | 62.1231 | 0.21996 | 0.01346 | 0.017899 | 0.013174 | 0.062171 | 0.00094847 | 0.080972 | -58.4152 | 62.1231 | -61.7111 | -61.5921 | 54.3503 | 23.172 | 7.4844 | 7.1594 | 62.1552 | -61.7157 | -0.31586 | 0 | 2.98 | -0.19684 | -7.7728 | -0.32043 | 0.032043 | 3.2959 | 68.8797 | 68.5547 | 115.7455 | 123.5184 | 2.98 | 123.5504 | 84.5673 | -0.32043 | 123.5184 | 2.98 | 84.5673 | 115.7455 | 123.5504 | -123.8342 | -123.8388
3603.7188 | 123.8297 | -61.4136 | 62.1552 | 0.090256 | 0.014101 | 0.012559 | 0.0039882 | 0.061957 | 0.00030767 | 0.081185 | -58.4793 | 62.1094 | -61.7065 | -61.6196 | 54.1855 | 23.2956 | 7.5623 | 7.0679 | 62.1597 | -61.7157 | -0.29297 | -0.045776 | 2.9343 | -0.20599 | -7.9697 | -0.30212 | 0.004578 | 3.2272 | 68.9758 | 68.4814 | 115.5991 | 123.5229 | 2.9343 | 123.5733 | 84.7092 | -0.30212 | 123.5229 | 2.9343 | 84.7092 | 115.5991 | 123.5733 | -123.8617 | -123.8708
3604.7188 | 123.7839 | -61.4182 | 62.2101 | -0.26833 | 0.018374 | 0.015763 | 0.016806 | 0.06388 | 0.0018031 | 0.079049 | -58.3969 | 62.2101 | -61.7111 | -61.6196 | 54.2313 | 23.0759 | 7.7362 | 7.1915 | 62.178 | -61.7569 | -0.29297 | 0 | 3.0212 | -0.20142 | -7.9788 | -0.33875 | -0.032043 | 3.3142 | 69.1544 | 68.6096 | 115.6494 | 123.6282 | 3.0212 | 123.5962 | 84.494 | -0.33875 | 123.6282 | 3.0212 | 84.494 | 115.6494 | 123.5962 | -123.9212 | -123.967
3605.7188 | 123.8205 | -61.4182 | 62.178 | 0.56328 | 0.016878 | 0.012132 | 0.014883 | 0.062812 | -0.00054693 | 0.078408 | -58.3923 | 62.2009 | -61.702 | -61.5784 | 54.3045 | 23.0072 | 7.7271 | 7.1777 | 62.178 | -61.7249 | -0.28381 | 0.022888 | 3.0258 | -0.16022 | -7.8735 | -0.3067 | 0 | 3.3096 | 69.1452 | 68.5959 | 115.7227 | 123.6191 | 3.0258 | 123.5962 | 84.4254 | -0.3067 | 123.6191 | 3.0258 | 84.4254 | 115.7227 | 123.5962 | -123.88 | -123.9029
3606.7188 | 123.7656 | -61.4182 | 62.2009 | 0.013962 | 0.016238 | 0.014695 | 0.013388 | 0.064093 | -0.0018285 | 0.080544 | -58.4702 | 62.233 | -61.7249 | -61.6379 | 54.3274 | 23.0301 | 7.7179 | 7.1228 | 62.2467 | -61.734 | -0.3067 | 0.032043 | 2.948 | -0.21973 | -7.8735 | -0.31586 | 0.045776 | 3.2547 | 69.136 | 68.541 | 115.7455 | 123.6511 | 2.948 | 123.6649 | 84.4482 | -0.31586 | 123.6511 | 2.948 | 84.4482 | 115.7455 | 123.6649 | -123.9258 | -123.9349
3607.7188 | 123.8571 | -61.3907 | 62.1368 | -0.062332 | 0.013033 | 0.018754 | 0.012747 | 0.063239 | 0.0013757 | 0.079904 | -58.4564 | 62.1185 | -61.7386 | -61.5784 | 54.3549 | 23.0759 | 7.5394 | 7.1823 | 62.1506 | -61.6837 | -0.3479 | -0.018311 | 2.9343 | -0.18768 | -7.782 | -0.29297 | 0.013733 | 3.2822 | 68.9301 | 68.573 | 115.7455 | 123.5092 | 2.9343 | 123.5413 | 84.4666 | -0.29297 | 123.5092 | 2.9343 | 84.4666 | 115.7455 | 123.5413 | -123.8754 | -123.8205
3608.7188 | 123.8663 | -61.3907 | 62.1368 | -0.16914 | 0.016451 | 0.0132 | 0.010183 | 0.06388 | 0.00052127 | 0.08204 | -58.4518 | 62.1048 | -61.7111 | -61.5692 | 54.2816 | 23.0621 | 7.576 | 7.2006 | 62.1277 | -61.7294 | -0.32043 | -0.032044 | 2.9388 | -0.17853 | -7.8552 | -0.33874 | -0.009155 | 3.2593 | 68.9667 | 68.5913 | 115.6723 | 123.4955 | 2.9388 | 123.5184 | 84.4528 | -0.33874 | 123.4955 | 2.9388 | 84.4528 | 115.6723 | 123.5184 | -123.848 | -123.8663
3609.7188 | 123.7473 | -61.4456 | 62.1735 | 0.03685 | 0.018587 | 0.014054 | 0.01531 | 0.064093 | 0.00073487 | 0.079476 | -58.461 | 62.2147 | -61.734 | -61.647 | 54.1168 | 22.8287 | 7.7454 | 7.0633 | 62.2009 | -61.7752 | -0.28839 | 0.041199 | 2.9846 | -0.20142 | -8.0566 | -0.32959 | 0.027466 | 3.273 | 69.191 | 68.5089 | 115.5624 | 123.6603 | 2.9846 | 123.6465 | 84.2743 | -0.32959 | 123.6603 | 2.9846 | 84.2743 | 115.5624 | 123.6465 | -123.9075 | -123.9487
3610.7188 | 123.7564 | -61.4456 | 62.1918 | 0.029221 | 0.01816 | 0.017472 | 0.014242 | 0.063452 | 0.0020167 | 0.080117 | -58.4793 | 62.2147 | -61.7294 | -61.6379 | 54.2038 | 22.9752 | 7.782 | 7.0633 | 62.2147 | -61.7661 | -0.28381 | 0.022889 | 2.9663 | -0.19226 | -7.988 | -0.32043 | 0.022889 | 3.2501 | 69.2276 | 68.5089 | 115.6494 | 123.6603 | 2.9663 | 123.6603 | 84.4208 | -0.32043 | 123.6603 | 2.9663 | 84.4208 | 115.6494 | 123.6603 | -123.9212 | -123.9578
3611.7188 | 123.7793 | -61.4273 | 62.1872 | -0.062332 | 0.019869 | 0.014695 | 0.01296 | 0.064093 | -0.0026831 | 0.081185 | -58.4244 | 62.233 | -61.7065 | -61.5921 | 54.2496 | 22.9431 | 7.7499 | 7.132 | 62.2375 | -61.7569 | -0.27924 | 0.045776 | 3.0029 | -0.16479 | -7.9376 | -0.32959 | 0.050354 | 3.2822 | 69.1772 | 68.5593 | 115.6769 | 123.6603 | 3.0029 | 123.6649 | 84.3704 | -0.32959 | 123.6603 | 3.0029 | 84.3704 | 115.6769 | 123.6649 | -123.8937 | -123.9441
3612.7188 | 123.9029 | -61.409 | 62.1185 | 0.18944 | 0.016878 | 0.018754 | 0.0093288 | 0.061957 | 0.00030767 | 0.080758 | -58.6349 | 62.0773 | -61.7477 | -61.6104 | 54.2999 | 23.0164 | 7.5989 | 7.2006 | 62.1506 | -61.7065 | -0.33875 | -0.041198 | 2.774 | -0.20142 | -7.8186 | -0.29755 | 0.032044 | 3.1128 | 69.0079 | 68.6096 | 115.7089 | 123.4863 | 2.774 | 123.5596 | 84.4254 | -0.29755 | 123.4863 | 2.774 | 84.4254 | 115.7089 | 123.5596 | -123.8663 | -123.8251
3613.7188 | 123.8754 | -61.3998 | 62.1323 | 2.5088 | 0.014529 | 0.013841 | 0.0078336 | 0.062171 | 0.00094847 | 0.080972 | -58.3282 | 62.0911 | -61.7294 | -61.5509 | 54.3137 | 22.9614 | 7.5623 | 7.2281 | 62.1414 | -61.734 | -0.32959 | -0.041199 | 3.0716 | -0.15106 | -7.8186 | -0.33417 | 0.009155 | 3.4012 | 68.9621 | 68.6279 | 115.7135 | 123.4909 | 3.0716 | 123.5413 | 84.3613 | -0.33417 | 123.4909 | 3.0716 | 84.3613 | 115.7135 | 123.5413 | -123.8617 | -123.8663
3614.7188 | 123.761 | -61.4548 | 62.1643 | 0.17418 | 0.014742 | 0.015122 | 0.021933 | 0.063025 | -0.00054693 | 0.080117 | -58.4976 | 62.178 | -61.7477 | -61.5509 | 54.0848 | 22.76 | 7.9147 | 7.0679 | 62.1826 | -61.7889 | -0.29297 | 0.013733 | 2.9572 | -0.09613 | -8.0795 | -0.33417 | 0.01831 | 3.2501 | 69.3695 | 68.5226 | 115.5396 | 123.6328 | 2.9572 | 123.6374 | 84.2148 | -0.33417 | 123.6328 | 2.9572 | 84.2148 | 115.5396 | 123.6374 | -123.912 | -123.9532
3615.7188 | 123.7244 | -61.4227 | 62.1918 | 0.16655 | 0.016238 | 0.017899 | 0.014456 | 0.063025 | -0.0024695 | 0.081185 | -58.4839 | 62.2009 | -61.7477 | -61.7157 | 54.1168 | 22.879 | 7.7408 | 7.0312 | 62.2009 | -61.7477 | -0.32501 | 0.009156 | 2.9388 | -0.29297 | -8.075 | -0.32501 | 0.009156 | 3.2639 | 69.1635 | 68.454 | 115.5395 | 123.6237 | 2.9388 | 123.6237 | 84.3018 | -0.32501 | 123.6237 | 2.9388 | 84.3018 | 115.5395 | 123.6237 | -123.9395 | -123.9395
3616.7188 | 123.7289 | -61.4639 | 62.1643 | 0.14366 | 0.015597 | 0.014268 | 0.015738 | 0.059821 | -0.00076053 | 0.080331 | -58.493 | 62.2238 | -61.7523 | -61.6974 | 54.332 | 22.9935 | 7.7271 | 7.0953 | 62.2192 | -61.7661 | -0.28839 | 0.059509 | 2.9709 | -0.23346 | -7.8323 | -0.30212 | 0.054931 | 3.2593 | 69.191 | 68.5593 | 115.7959 | 123.6877 | 2.9709 | 123.6832 | 84.4574 | -0.30212 | 123.6877 | 2.9709 | 84.4574 | 115.7959 | 123.6832 | -123.9166 | -123.9304
3617.7188 | 123.8709 | -61.3815 | 62.1506 | -0.08522 | 0.01282 | 0.020249 | 0.0056972 | 0.06153 | -0.00054693 | 0.081185 | -58.4747 | 62.1185 | -61.7249 | -61.5692 | 54.3503 | 22.9752 | 7.6767 | 7.2647 | 62.1735 | -61.6562 | -0.34332 | -0.032044 | 2.9068 | -0.18768 | -7.8003 | -0.27466 | 0.022888 | 3.2501 | 69.0582 | 68.6462 | 115.7318 | 123.5001 | 2.9068 | 123.555 | 84.3567 | -0.27466 | 123.5001 | 2.9068 | 84.3567 | 115.7318 | 123.555 | -123.8754 | -123.8068
3618.7188 | 123.7335 | -61.4319 | 62.1689 | 0.18181 | 0.017092 | 0.013627 | 0.0095424 | 0.061743 | -0.00011953 | 0.080544 | -58.4793 | 62.2192 | -61.7523 | -61.6241 | 54.2633 | 22.8653 | 7.7545 | 7.1365 | 62.178 | -61.7661 | -0.32043 | 0.050354 | 2.9526 | -0.19226 | -7.9056 | -0.33417 | 0.009156 | 3.273 | 69.1864 | 68.5684 | 115.6952 | 123.6511 | 2.9526 | 123.6099 | 84.2972 | -0.33417 | 123.6511 | 2.9526 | 84.2972 | 115.6952 | 123.6099 | -123.9212 | -123.9349
3619.7188 | 123.7564 | -61.4594 | 62.1872 | 0.074997 | 0.018587 | 0.015763 | 0.017233 | 0.063025 | -0.00054693 | 0.079263 | -58.4793 | 62.2238 | -61.702 | -61.6745 | 54.1718 | 22.8333 | 7.8735 | 7.0999 | 62.2055 | -61.7477 | -0.24261 | 0.036621 | 2.98 | -0.21515 | -8.0154 | -0.28839 | 0.01831 | 3.2227 | 69.3329 | 68.5593 | 115.6311 | 123.6832 | 2.98 | 123.6649 | 84.2926 | -0.28839 | 123.6832 | 2.98 | 84.2926 | 115.6311 | 123.6649 | -123.8892 | -123.9349
3620.7188 | 123.7564 | -61.4731 | 62.178 | 0.16655 | 0.016238 | 0.018327 | 0.020865 | 0.06623 | -0.00011953 | 0.077981 | -58.5022 | 62.2192 | -61.7615 | -61.4548 | 54.1489 | 22.7875 | 7.9971 | 7.1182 | 62.2101 | -61.7569 | -0.28839 | 0.041198 | 2.9709 | 0.01831 | -8.0292 | -0.28381 | 0.032043 | 3.2593 | 69.4702 | 68.5913 | 115.6219 | 123.6923 | 2.9709 | 123.6832 | 84.2606 | -0.28381 | 123.6923 | 2.9709 | 84.2606 | 115.6219 | 123.6832 | -123.9395 | -123.9349
3621.7188 | 123.8159 | -61.4502 | 62.1414 | 0.10551 | 0.017519 | 0.014054 | 0.01296 | 0.064093 | -0.0018285 | 0.079476 | -58.4976 | 62.1872 | -61.734 | -61.6562 | 54.1992 | 22.8516 | 7.8003 | 7.1365 | 62.2009 | -61.7706 | -0.28381 | 0.045777 | 2.9526 | -0.20599 | -7.9422 | -0.32043 | 0.05951 | 3.2364 | 69.2505 | 68.5867 | 115.6494 | 123.6374 | 2.9526 | 123.6511 | 84.3018 | -0.32043 | 123.6374 | 2.9526 | 84.3018 | 115.6494 | 123.6511 | -123.8754 | -123.912
3622.7188 | 123.7839 | -61.4731 | 62.1597 | 0.090256 | 0.016238 | 0.014054 | 0.01296 | 0.063239 | -0.00033333 | 0.080972 | -58.4793 | 62.1872 | -61.7477 | -61.6608 | 54.2221 | 22.8882 | 7.8415 | 7.1365 | 62.1964 | -61.7706 | -0.27466 | 0.027466 | 2.9938 | -0.18768 | -7.9376 | -0.29755 | 0.036621 | 3.2684 | 69.3146 | 68.6096 | 115.6952 | 123.6603 | 2.9938 | 123.6694 | 84.3613 | -0.29755 | 123.6603 | 2.9938 | 84.3613 | 115.6952 | 123.6694 | -123.9075 | -123.9304
3623.7188 | 123.8846 | -61.377 | 62.1643 | -0.077591 | 0.014101 | 0.010423 | 0.0039882 | 0.061957 | 0.00073487 | 0.079904 | -58.4564 | 62.114 | -61.7111 | -61.5372 | 54.4098 | 23.0713 | 7.7545 | 7.2922 | 62.1643 | -61.702 | -0.33417 | -0.050354 | 2.9205 | -0.16022 | -7.7545 | -0.32501 | 0 | 3.2547 | 69.1315 | 68.6691 | 115.7867 | 123.4909 | 2.9205 | 123.5413 | 84.4482 | -0.32501 | 123.4909 | 2.9205 | 84.4482 | 115.7867 | 123.5413 | -123.8754 | -123.8663
3624.7188 | 123.7518 | -61.4319 | 62.1597 | 0.14366 | 0.018801 | 0.014909 | 0.01232 | 0.063239 | -0.00033333 | 0.081826 | -58.4839 | 62.2147 | -61.7477 | -61.647 | 54.2633 | 22.9202 | 7.8278 | 7.1045 | 62.1414 | -61.7752 | -0.31586 | 0.054932 | 2.948 | -0.21515 | -7.8964 | -0.34332 | -0.018311 | 3.2639 | 69.2596 | 68.5364 | 115.6952 | 123.6465 | 2.948 | 123.5733 | 84.3521 | -0.34332 | 123.6465 | 2.948 | 84.3521 | 115.6952 | 123.5733 | -123.9075 | -123.9349
3625.7188 | 123.7381 | -61.4319 | 62.1689 | 0.052109 | 0.016878 | 0.014268 | 0.016165 | 0.062812 | 0.00094847 | 0.081185 | -58.5114 | 62.2147 | -61.734 | -61.6837 | 54.2587 | 22.879 | 7.8918 | 7.0862 | 62.1964 | -61.7661 | -0.30212 | 0.045777 | 2.9205 | -0.25177 | -7.9102 | -0.33417 | 0.027466 | 3.2227 | 69.3237 | 68.5181 | 115.6906 | 123.6465 | 2.9205 | 123.6282 | 84.3109 | -0.33417 | 123.6465 | 2.9205 | 84.3109 | 115.6906 | 123.6282 | -123.9029 | -123.9349
3626.7188 | 123.7244 | -61.4548 | 62.178 | 0.14366 | 0.016238 | 0.015763 | 0.014029 | 0.06388 | -0.00011953 | 0.080331 | -58.4885 | 62.2147 | -61.734 | -61.6653 | 54.2725 | 22.9843 | 7.8781 | 7.1045 | 62.1918 | -61.7477 | -0.27924 | 0.036621 | 2.9663 | -0.21057 | -7.9056 | -0.29297 | 0.013732 | 3.2455 | 69.3329 | 68.5593 | 115.7272 | 123.6694 | 2.9663 | 123.6465 | 84.4391 | -0.29297 | 123.6694 | 2.9663 | 84.4391 | 115.7272 | 123.6465 | -123.912 | -123.9258
3627.7188 | 123.7564 | -61.441 | 62.1689 | 0.35728 | 0.016238 | 0.0132 | 0.014456 | 0.065589 | -0.0031103 | 0.07969 | -58.287 | 62.233 | -61.7386 | -61.6379 | 54.2862 | 22.9294 | 7.8873 | 7.1228 | 62.2055 | -61.7844 | -0.29755 | 0.064087 | 3.154 | -0.19684 | -7.8827 | -0.34332 | 0.036621 | 3.4515 | 69.3283 | 68.5638 | 115.7272 | 123.674 | 3.154 | 123.6465 | 84.3704 | -0.34332 | 123.674 | 3.154 | 84.3704 | 115.7272 | 123.6465 | -123.9075 | -123.9532
3628.7188 | 123.8297 | -61.4273 | 62.1552 | 0.059738 | 0.01346 | 0.012345 | 0.0048428 | 0.061316 | 0.0013757 | 0.080972 | -58.5022 | 62.1094 | -61.7432 | -61.6104 | 54.3457 | 23.0988 | 7.7454 | 7.1915 | 62.1368 | -61.6974 | -0.31586 | -0.045776 | 2.9251 | -0.18311 | -7.8094 | -0.27008 | -0.01831 | 3.241 | 69.1727 | 68.6188 | 115.773 | 123.5367 | 2.9251 | 123.5641 | 84.5261 | -0.27008 | 123.5367 | 2.9251 | 84.5261 | 115.773 | 123.5641 | -123.8983 | -123.8525
3629.7188 | 123.7793 | -61.4639 | 62.1414 | 0.090256 | 0.019015 | 0.015336 | 0.015738 | 0.062812 | 0.00094847 | 0.079263 | -58.4885 | 62.1964 | -61.7386 | -61.6837 | 54.3045 | 23.0713 | 7.8461 | 7.1594 | 62.1506 | -61.7798 | -0.27466 | 0.054932 | 2.9755 | -0.21973 | -7.8369 | -0.31586 | 0.009156 | 3.2501 | 69.31 | 68.6234 | 115.7684 | 123.6603 | 2.9755 | 123.6145 | 84.5352 | -0.31586 | 123.6603 | 2.9755 | 84.5352 | 115.7684 | 123.6145 | -123.88 | -123.9212
3630.7188 | 123.7793 | -61.4594 | 62.1597 | 0.10551 | 0.017947 | 0.017045 | 0.012747 | 0.062384 | 0.0013757 | 0.080544 | -58.4793 | 62.1872 | -61.7523 | -61.6699 | 54.2404 | 23.0301 | 7.8598 | 7.1594 | 62.146 | -61.7706 | -0.29297 | 0.027466 | 2.98 | -0.21057 | -7.9193 | -0.31128 | -0.013733 | 3.273 | 69.3192 | 68.6188 | 115.6998 | 123.6465 | 2.98 | 123.6053 | 84.4894 | -0.31128 | 123.6465 | 2.98 | 84.4894 | 115.6998 | 123.6053 | -123.912 | -123.9304
3631.7188 | 123.7701 | -61.4365 | 62.1597 | 0.18181 | 0.016451 | 0.015336 | 0.014456 | 0.062598 | 9.4068e-05 | 0.080117 | -58.5022 | 62.2055 | -61.7294 | -61.6653 | 54.2999 | 23.1308 | 7.869 | 7.1503 | 62.2009 | -61.7386 | -0.29297 | 0.045776 | 2.9343 | -0.22888 | -7.8598 | -0.30212 | 0.041199 | 3.2272 | 69.3054 | 68.5867 | 115.7364 | 123.642 | 2.9343 | 123.6374 | 84.5673 | -0.30212 | 123.642 | 2.9343 | 84.5673 | 115.7364 | 123.6374 | -123.8892 | -123.8983
3632.7188 | 123.7335 | -61.4594 | 62.1735 | 0.082626 | 0.017947 | 0.017899 | 0.013388 | 0.064307 | 0.00073487 | 0.079476 | -58.4793 | 62.2192 | -61.7386 | -61.6882 | 54.2587 | 22.998 | 7.933 | 7.1136 | 62.1964 | -61.7706 | -0.27923 | 0.045776 | 2.98 | -0.22888 | -7.9147 | -0.31128 | 0.022888 | 3.2593 | 69.3924 | 68.573 | 115.7181 | 123.6786 | 2.98 | 123.6557 | 84.4574 | -0.31128 | 123.6786 | 2.98 | 84.4574 | 115.7181 | 123.6557 | -123.912 | -123.9441
3633.7188 | 123.8846 | -61.3953 | 62.146 | 0.21996 | 0.016878 | 0.015336 | 0.011679 | 0.062812 | 0.00073487 | 0.081826 | -58.4198 | 62.1094 | -61.7432 | -61.5738 | 54.3961 | 23.0896 | 7.7316 | 7.2601 | 62.1506 | -61.7249 | -0.3479 | -0.036621 | 2.9755 | -0.17853 | -7.7499 | -0.32959 | 0.004578 | 3.3234 | 69.1269 | 68.6554 | 115.7913 | 123.5046 | 2.9755 | 123.5458 | 84.4849 | -0.32959 | 123.5046 | 2.9755 | 84.4849 | 115.7913 | 123.5458 | -123.8892 | -123.8708
3634.7188 | 123.7473 | -61.4548 | 62.1506 | 3.3709 | 0.018374 | 0.015336 | 0.013388 | 0.061316 | -0.00076053 | 0.078835 | -58.6075 | 62.1597 | -61.7615 | -61.6974 | 54.3549 | 23.0164 | 7.901 | 7.1182 | 62.1964 | -61.7844 | -0.3067 | 0.009155 | 2.8473 | -0.24261 | -7.7957 | -0.32959 | 0.045776 | 3.154 | 69.3558 | 68.573 | 115.8096 | 123.6145 | 2.8473 | 123.6511 | 84.4711 | -0.32959 | 123.6145 | 2.8473 | 84.4711 | 115.8096 | 123.6511 | -123.912 | -123.9349
3635.7188 | 123.7701 | -61.4639 | 62.1552 | 0.097885 | 0.017947 | 0.012345 | 0.013601 | 0.064093 | 0.0026575 | 0.081399 | -58.4839 | 62.2009 | -61.7477 | -61.6653 | 54.2862 | 23.0347 | 7.8781 | 7.1777 | 62.1735 | -61.7386 | -0.28381 | 0.045777 | 2.98 | -0.20142 | -7.869 | -0.27466 | 0.018311 | 3.2639 | 69.342 | 68.6417 | 115.7501 | 123.6649 | 2.98 | 123.6374 | 84.4986 | -0.27466 | 123.6649 | 2.98 | 84.4986 | 115.7501 | 123.6374 | -123.9029 | -123.8937
3636.7188 | 123.7747 | -61.4502 | 62.146 | 0.1284 | 0.020083 | 0.012559 | 0.014456 | 0.065161 | 0.0011621 | 0.079263 | -58.5068 | 62.2192 | -61.7706 | -61.6653 | 54.2633 | 22.966 | 7.869 | 7.1274 | 62.1735 | -61.7752 | -0.32043 | 0.073242 | 2.9434 | -0.21515 | -7.8827 | -0.32501 | 0.027466 | 3.2639 | 69.3192 | 68.5776 | 115.7135 | 123.6694 | 2.9434 | 123.6237 | 84.4162 | -0.32501 | 123.6694 | 2.9434 | 84.4162 | 115.7135 | 123.6237 | -123.9166 | -123.9212
3637.7188 | 123.7701 | -61.4365 | 62.1323 | 0.021591 | 0.016238 | 0.014482 | 0.014883 | 0.063666 | -0.00011953 | 0.081613 | -58.493 | 62.2009 | -61.7477 | -61.6653 | 54.3045 | 23.0209 | 7.8735 | 7.1228 | 62.178 | -61.7798 | -0.31128 | 0.068665 | 2.9434 | -0.22888 | -7.8278 | -0.34332 | 0.045777 | 3.2547 | 69.31 | 68.5593 | 115.741 | 123.6374 | 2.9434 | 123.6145 | 84.4574 | -0.34332 | 123.6374 | 2.9434 | 84.4574 | 115.741 | 123.6145 | -123.88 | -123.912
3638.7188 | 123.8617 | -61.4136 | 62.1277 | 0.082626 | 0.017519 | 0.014695 | 0.010183 | 0.064307 | -0.00033333 | 0.082681 | -58.4381 | 62.1048 | -61.6974 | -61.5646 | 54.4006 | 23.1903 | 7.7316 | 7.2464 | 62.1323 | -61.7249 | -0.28381 | -0.022889 | 2.9755 | -0.15106 | -7.7271 | -0.31128 | 0.004577 | 3.2593 | 69.1452 | 68.66 | 115.8142 | 123.5184 | 2.9755 | 123.5458 | 84.6039 | -0.31128 | 123.5184 | 2.9755 | 84.6039 | 115.8142 | 123.5458 | -123.8251 | -123.8525
3639.7188 | 123.7656 | -61.4548 | 62.1918 | 0.03685 | 0.017306 | 0.014909 | 0.016165 | 0.062598 | -0.00076053 | 0.080331 | -58.4747 | 62.2238 | -61.7386 | -61.6516 | 54.3091 | 23.0255 | 7.9147 | 7.1182 | 62.1735 | -61.7844 | -0.28381 | 0.032044 | 2.98 | -0.19684 | -7.8827 | -0.32959 | -0.01831 | 3.2639 | 69.3695 | 68.573 | 115.7639 | 123.6786 | 2.98 | 123.6282 | 84.4803 | -0.32959 | 123.6786 | 2.98 | 84.4803 | 115.7639 | 123.6282 | -123.9304 | -123.9761
3640.7188 | 123.7106 | -61.4319 | 62.1735 | 0.14366 | 0.01816 | 0.014695 | 0.015097 | 0.067084 | 0.0022303 | 0.079476 | -58.5159 | 62.1872 | -61.7523 | -61.5509 | 54.5334 | 23.0438 | 7.8781 | 7.2784 | 62.2238 | -61.7477 | -0.32043 | 0.013733 | 2.916 | -0.11902 | -7.6401 | -0.31586 | 0.050354 | 3.2364 | 69.31 | 68.7103 | 115.9653 | 123.6191 | 2.916 | 123.6557 | 84.4757 | -0.31586 | 123.6191 | 2.916 | 84.4757 | 115.9653 | 123.6557 | -123.9258 | -123.9212
3641.7188 | 123.7747 | -61.4685 | 62.1643 | 0.090256 | 0.017733 | 0.014482 | 0.013174 | 0.064948 | 0.00073487 | 0.07969 | -58.5159 | 62.1918 | -61.7569 | -61.6837 | 54.213 | 22.9935 | 7.8918 | 7.1045 | 62.2101 | -61.7798 | -0.28839 | 0.027465 | 2.9526 | -0.21515 | -7.9514 | -0.31128 | 0.045776 | 3.241 | 69.3604 | 68.573 | 115.6815 | 123.6603 | 2.9526 | 123.6786 | 84.462 | -0.31128 | 123.6603 | 2.9526 | 84.462 | 115.6815 | 123.6786 | -123.9212 | -123.9441
3642.7188 | 123.7747 | -61.4502 | 62.1689 | 0.21996 | 0.017947 | 0.019608 | 0.012747 | 0.064521 | -0.0011877 | 0.081826 | -58.5342 | 62.2101 | -61.734 | -61.6699 | 54.2313 | 22.9568 | 7.8735 | 7.1365 | 62.2192 | -61.7477 | -0.28381 | 0.041199 | 2.916 | -0.21973 | -7.9376 | -0.29755 | 0.050354 | 3.1998 | 69.3237 | 68.5867 | 115.6815 | 123.6603 | 2.916 | 123.6694 | 84.407 | -0.29755 | 123.6603 | 2.916 | 84.407 | 115.6815 | 123.6694 | -123.9029 | -123.9166
3643.7188 | 123.8159 | -61.4365 | 62.1552 | 0.24284 | 0.016451 | 0.018968 | 0.01232 | 0.063452 | 0.0022303 | 0.079476 | -58.493 | 62.1643 | -61.7432 | -61.6379 | 54.2267 | 22.9568 | 7.782 | 7.196 | 62.1597 | -61.7477 | -0.3067 | 0.009156 | 2.9434 | -0.20142 | -7.9285 | -0.31128 | 0.004578 | 3.2501 | 69.2184 | 68.6325 | 115.6631 | 123.6008 | 2.9434 | 123.5962 | 84.3933 | -0.31128 | 123.6008 | 2.9434 | 84.3933 | 115.6631 | 123.5962 | -123.8983 | -123.9029
3644.7188 | 123.7793 | -61.4685 | 62.1597 | 0.15892 | 0.021364 | 0.015122 | 0.013388 | 0.064521 | -0.0011877 | 0.079476 | -58.8455 | 62.1414 | -61.7477 | -61.702 | 54.2221 | 22.966 | 7.8323 | 7.1182 | 62.1964 | -61.7477 | -0.27924 | -0.018311 | 2.623 | -0.23346 | -7.9376 | -0.27924 | 0.036621 | 2.9022 | 69.3008 | 68.5867 | 115.6906 | 123.6099 | 2.623 | 123.6649 | 84.4345 | -0.27924 | 123.6099 | 2.623 | 84.4345 | 115.6906 | 123.6649 | -123.9075 | -123.9075
3645.7188 | 123.7427 | -61.4639 | 62.1826 | 0.12077 | 0.019228 | 0.01555 | 0.01531 | 0.066443 | 0.0020167 | 0.077554 | -58.5114 | 62.2192 | -61.7615 | -61.6241 | 54.6249 | 23.0347 | 7.814 | 7.2281 | 62.2009 | -61.7386 | -0.29755 | 0.036621 | 2.9526 | -0.16022 | -7.5577 | -0.27466 | 0.018311 | 3.2501 | 69.278 | 68.692 | 116.0889 | 123.6832 | 2.9526 | 123.6649 | 84.4986 | -0.27466 | 123.6832 | 2.9526 | 84.4986 | 116.0889 | 123.6649 | -123.9441 | -123.9212
3646.7188 | 123.7473 | -61.4319 | 62.178 | 0.0063326 | 0.016878 | 0.017472 | 0.012747 | 0.065589 | -0.00054693 | 0.079263 | -58.4793 | 62.2192 | -61.7386 | -61.6562 | 54.2267 | 22.9202 | 7.8598 | 7.1686 | 62.1826 | -61.7477 | -0.3067 | 0.041198 | 2.9526 | -0.2243 | -7.9514 | -0.31586 | 0.004577 | 3.2593 | 69.2917 | 68.6005 | 115.6586 | 123.6511 | 2.9526 | 123.6145 | 84.3521 | -0.31586 | 123.6511 | 2.9526 | 84.3521 | 115.6586 | 123.6145 | -123.9166 | -123.9258
3647.7188 | 123.7335 | -61.4594 | 62.1826 | 0.097885 | 0.017947 | 0.016191 | 0.013601 | 0.067511 | 0.00030767 | 0.078622 | -58.5159 | 62.2284 | -61.7615 | -61.6974 | 54.2175 | 22.9248 | 7.8552 | 7.1091 | 62.233 | -61.7569 | -0.30212 | 0.045777 | 2.9434 | -0.23804 | -7.9651 | -0.29755 | 0.050354 | 3.2455 | 69.3146 | 68.5684 | 115.6769 | 123.6877 | 2.9434 | 123.6923 | 84.3842 | -0.29755 | 123.6877 | 2.9434 | 84.3842 | 115.6769 | 123.6923 | -123.9441 | -123.9395
3648.7344 | 123.8525 | -61.3953 | 62.1368 | -0.024185 | 0.01581 | 0.011277 | 0.00527 | 0.064093 | -0.0016149 | 0.080758 | -58.493 | 62.1002 | -61.7249 | -61.4136 | 54.4693 | 22.9889 | 7.7957 | 7.2235 | 62.1597 | -61.702 | -0.32959 | -0.036621 | 2.9022 | -0.01831 | -7.6675 | -0.3067 | 0.022888 | 3.2318 | 69.191 | 68.6188 | 115.8646 | 123.4955 | 2.9022 | 123.555 | 84.3842 | -0.3067 | 123.4955 | 2.9022 | 84.3842 | 115.8646 | 123.555 | -123.8617 | -123.8388
3649.7188 | 123.7335 | -61.4502 | 62.178 | -0.39803 | 0.017947 | 0.017259 | 0.014029 | 0.06153 | -0.00097413 | 0.080544 | -58.5663 | 62.233 | -61.7203 | -61.702 | 54.3365 | 23.0438 | 7.8644 | 7.1365 | 62.178 | -61.7569 | -0.27008 | 0.054931 | 2.8839 | -0.25177 | -7.8415 | -0.3067 | 0 | 3.154 | 69.3146 | 68.5867 | 115.7867 | 123.6832 | 2.8839 | 123.6282 | 84.494 | -0.3067 | 123.6832 | 2.8839 | 84.494 | 115.7867 | 123.6282 | -123.8983 | -123.9349
3650.7188 | 123.8068 | -61.4548 | 62.1689 | 0.17418 | 0.018374 | 0.017259 | 0.0091152 | 0.063452 | 0.0030847 | 0.080331 | -58.3649 | 62.1964 | -61.7294 | -61.6241 | 54.3869 | 23.0347 | 7.8506 | 7.1686 | 62.2055 | -61.7661 | -0.27466 | 0.027466 | 3.0899 | -0.16937 | -7.782 | -0.31128 | 0.036621 | 3.3646 | 69.3054 | 68.6234 | 115.8417 | 123.6511 | 3.0899 | 123.6603 | 84.4894 | -0.31128 | 123.6511 | 3.0899 | 84.4894 | 115.8417 | 123.6603 | -123.8983 | -123.9349
3651.7188 | 123.8159 | -61.4365 | 62.1735 | 0.13603 | 0.01816 | 0.016404 | 0.015524 | 0.063666 | -0.0014013 | 0.080972 | -58.5205 | 62.2101 | -61.7569 | -61.734 | 53.9383 | 22.7142 | 8.2809 | 7.1869 | 62.1918 | -61.7706 | -0.32044 | 0.036621 | 2.916 | -0.29755 | -8.2352 | -0.33417 | 0.01831 | 3.2364 | 69.7174 | 68.6234 | 115.3748 | 123.6465 | 2.916 | 123.6282 | 84.1507 | -0.33417 | 123.6465 | 2.916 | 84.1507 | 115.3748 | 123.6282 | -123.9304 | -123.9441
3652.7188 | 123.6053 | -61.4685 | 62.0956 | 0.090256 | 0.016238 | 0.018113 | 0.01531 | 0.064307 | 0.00094847 | 0.079476 | -58.4976 | 62.2192 | -61.7523 | -61.6974 | 54.2862 | 22.9797 | 7.8781 | 7.1228 | 62.1872 | -61.7569 | -0.28381 | 0.1236 | 2.9709 | -0.22888 | -7.8094 | -0.28839 | 0.091553 | 3.2547 | 69.3466 | 68.5913 | 115.7547 | 123.6877 | 2.9709 | 123.6557 | 84.4482 | -0.28839 | 123.6877 | 2.9709 | 84.4482 | 115.7547 | 123.6557 | -123.848 | -123.8525
3653.7188 | 123.7747 | -61.4273 | 62.1735 | 0.26573 | 0.019656 | 0.016191 | 0.012747 | 0.064093 | 0.00094847 | 0.081185 | -58.5159 | 62.1964 | -61.7615 | -61.6562 | 54.3457 | 23.0667 | 7.8461 | 7.0908 | 62.2055 | -61.7477 | -0.33417 | 0.022888 | 2.9114 | -0.22888 | -7.8278 | -0.32044 | 0.032043 | 3.2455 | 69.2734 | 68.5181 | 115.773 | 123.6237 | 2.9114 | 123.6328 | 84.494 | -0.32044 | 123.6237 | 2.9114 | 84.494 | 115.773 | 123.6328 | -123.9349 | -123.9212
3654.7188 | 123.7198 | -61.4639 | 62.1597 | 0.14366 | 0.018801 | 0.014909 | 0.011892 | 0.064307 | 0.0013757 | 0.080972 | -58.4976 | 62.2101 | -61.7386 | -61.6791 | 54.2999 | 22.998 | 7.8918 | 7.0312 | 62.2147 | -61.7752 | -0.27466 | 0.050354 | 2.9663 | -0.21515 | -7.8598 | -0.31128 | 0.054932 | 3.241 | 69.3558 | 68.4952 | 115.7639 | 123.674 | 2.9663 | 123.6786 | 84.462 | -0.31128 | 123.674 | 2.9663 | 84.462 | 115.7639 | 123.6786 | -123.8983 | -123.9349
3655.7188 | 123.7335 | -61.4365 | 62.1689 | 0.067368 | 0.018801 | 0.014482 | 0.014669 | 0.064521 | 0.00052127 | 0.082253 | -58.5068 | 62.2284 | -61.7294 | -61.6699 | 54.3503 | 23.0072 | 7.8781 | 7.0679 | 62.1872 | -61.7752 | -0.29297 | 0.05951 | 2.9297 | -0.23346 | -7.8186 | -0.33875 | 0.018311 | 3.2227 | 69.3146 | 68.5043 | 115.7867 | 123.6649 | 2.9297 | 123.6237 | 84.4437 | -0.33875 | 123.6649 | 2.9297 | 84.4437 | 115.7867 | 123.6237 | -123.8983 | -123.9441
3656.7188 | 123.7564 | -61.441 | 62.1826 | 0.15129 | 0.01816 | 0.014695 | 0.014669 | 0.062812 | -0.00033333 | 0.080972 | -58.5342 | 62.2101 | -61.7523 | -61.7386 | 54.2999 | 23.0804 | 7.814 | 7.0129 | 62.2101 | -61.7569 | -0.31128 | 0.027466 | 2.9068 | -0.29755 | -7.8827 | -0.31586 | 0.027466 | 3.2181 | 69.2551 | 68.454 | 115.741 | 123.6511 | 2.9068 | 123.6511 | 84.5215 | -0.31586 | 123.6511 | 2.9068 | 84.5215 | 115.741 | 123.6511 | -123.9349 | -123.9395
3657.7188 | 123.7381 | -61.441 | 62.1964 | 0.13603 | 0.01816 | 0.017472 | 0.012106 | 0.064948 | 0.0069299 | 0.083108 | -58.5342 | 62.2192 | -61.7386 | -61.9034 | 54.483 | 23.2224 | 7.7042 | 7.1228 | 62.2009 | -61.7798 | -0.29755 | 0.022888 | 2.9068 | -0.46234 | -7.7133 | -0.33874 | 0.004578 | 3.2043 | 69.1452 | 68.5638 | 115.9241 | 123.6603 | 2.9068 | 123.642 | 84.6634 | -0.33874 | 123.6603 | 2.9068 | 84.6634 | 115.9241 | 123.642 | -123.9349 | -123.9761
3658.7188 | 123.7793 | -61.4594 | 62.1552 | 0.097885 | 0.015597 | 0.017686 | 0.013174 | 0.06388 | 0.0013757 | 0.080331 | -58.5022 | 62.1964 | -61.7569 | -61.6653 | 54.1718 | 23.053 | 7.8278 | 7.0953 | 62.2284 | -61.7569 | -0.29755 | 0.041199 | 2.9572 | -0.20599 | -7.9834 | -0.29755 | 0.073243 | 3.2547 | 69.2871 | 68.5547 | 115.6311 | 123.6557 | 2.9572 | 123.6877 | 84.5123 | -0.29755 | 123.6557 | 2.9572 | 84.5123 | 115.6311 | 123.6877 | -123.912 | -123.912
3659.7188 | 123.7793 | -61.4548 | 62.1643 | -0.031814 | 0.017519 | 0.014695 | 0.014669 | 0.064521 | -0.00033333 | 0.078835 | -58.4747 | 62.2009 | -61.7157 | -61.6653 | 54.2587 | 22.9614 | 7.8598 | 7.0953 | 62.1964 | -61.7706 | -0.26093 | 0.036621 | 2.98 | -0.21057 | -7.9056 | -0.31586 | 0.032043 | 3.241 | 69.3146 | 68.5501 | 115.7135 | 123.6557 | 2.98 | 123.6511 | 84.4162 | -0.31586 | 123.6557 | 2.98 | 84.4162 | 115.7135 | 123.6511 | -123.88 | -123.9349
3660.7188 | 123.7244 | -61.4182 | 62.178 | 0.052109 | 0.016878 | 0.017899 | 0.014456 | 0.064307 | 0.00030767 | 0.083962 | -58.4747 | 62.2284 | -61.7523 | -61.647 | 54.2679 | 22.9202 | 7.8369 | 7.0633 | 62.2238 | -61.734 | -0.33417 | 0.050354 | 2.9434 | -0.22888 | -7.9102 | -0.31586 | 0.045776 | 3.2776 | 69.2551 | 68.4814 | 115.686 | 123.6465 | 2.9434 | 123.642 | 84.3384 | -0.31586 | 123.6465 | 2.9434 | 84.3384 | 115.686 | 123.642 | -123.9304 | -123.912
3661.7188 | 123.7564 | -61.4227 | 62.1826 | 0.021591 | 0.017519 | 0.018113 | 0.012533 | 0.063452 | 0.00030767 | 0.081185 | -58.4564 | 62.2375 | -61.734 | -61.6562 | 54.3228 | 22.9019 | 7.8506 | 7.0724 | 62.2147 | -61.7569 | -0.31128 | 0.054932 | 2.9663 | -0.23346 | -7.8598 | -0.33417 | 0.032044 | 3.2776 | 69.2734 | 68.4952 | 115.7455 | 123.6603 | 2.9663 | 123.6374 | 84.3246 | -0.33417 | 123.6603 | 2.9663 | 84.3246 | 115.7455 | 123.6374 | -123.9166 | -123.9395
3662.7188 | 123.7518 | -61.4639 | 62.2009 | 0.0063326 | 0.019228 | 0.017259 | 0.013174 | 0.064734 | 9.4068e-05 | 0.079904 | -58.461 | 62.2238 | -61.734 | -61.6425 | 54.2404 | 22.9156 | 7.8278 | 7.0724 | 62.2101 | -61.7432 | -0.27008 | 0.022888 | 3.0029 | -0.17853 | -7.9605 | -0.27924 | 0.009155 | 3.273 | 69.2917 | 68.5364 | 115.7043 | 123.6877 | 3.0029 | 123.674 | 84.3796 | -0.27924 | 123.6877 | 3.0029 | 84.3796 | 115.7043 | 123.674 | -123.9349 | -123.9441
3663.7188 | 123.8068 | -61.4182 | 62.114 | 0.16655 | 0.017306 | 0.014909 | 0.0091152 | 0.064734 | 0.0024439 | 0.079049 | -58.4152 | 62.1414 | -61.7111 | -61.5829 | 54.3411 | 23.0347 | 7.6492 | 7.1915 | 62.1277 | -61.7249 | -0.29297 | 0.027465 | 3.0029 | -0.16479 | -7.7728 | -0.3067 | 0.013733 | 3.2959 | 69.0674 | 68.6096 | 115.7593 | 123.5596 | 3.0029 | 123.5458 | 84.4528 | -0.3067 | 123.5596 | 3.0029 | 84.4528 | 115.7593 | 123.5458 | -123.8251 | -123.8388
3664.7188 | 123.7244 | -61.4639 | 62.1689 | 0.067368 | 0.017733 | 0.015122 | 0.015951 | 0.063666 | 0.0013757 | 0.083322 | -58.4518 | 62.2147 | -61.734 | -61.7111 | 54.1718 | 22.998 | 7.8323 | 7.0221 | 62.178 | -61.7752 | -0.27008 | 0.045777 | 3.0121 | -0.24719 | -7.9971 | -0.31128 | 0.009156 | 3.2822 | 69.2963 | 68.486 | 115.6357 | 123.6786 | 3.0121 | 123.642 | 84.462 | -0.31128 | 123.6786 | 3.0121 | 84.462 | 115.6357 | 123.642 | -123.9029 | -123.9441
3665.7188 | 123.7381 | -61.4456 | 62.1735 | 0.11314 | 0.016878 | 0.017259 | 0.014883 | 0.064521 | 0.00030767 | 0.079263 | -58.4885 | 62.2192 | -61.7523 | -61.6928 | 54.1763 | 22.9156 | 7.8278 | 7.0221 | 62.2009 | -61.7889 | -0.3067 | 0.045776 | 2.9572 | -0.24719 | -7.9971 | -0.34332 | 0.027466 | 3.2639 | 69.2734 | 68.4677 | 115.6219 | 123.6649 | 2.9572 | 123.6465 | 84.3613 | -0.34332 | 123.6649 | 2.9572 | 84.3613 | 115.6219 | 123.6465 | -123.9258 | -123.9624
3666.7188 | 123.7518 | -61.441 | 62.1689 | 0.03685 | 0.017947 | 0.014268 | 0.01531 | 0.065802 | -0.00076053 | 0.082467 | -58.4381 | 62.2147 | -61.7111 | -61.647 | 54.2587 | 22.7966 | 7.8323 | 7.0404 | 62.233 | -61.7661 | -0.27008 | 0.045777 | 3.0029 | -0.20599 | -7.9102 | -0.32501 | 0.064087 | 3.273 | 69.2734 | 68.4814 | 115.6998 | 123.6557 | 3.0029 | 123.674 | 84.2377 | -0.32501 | 123.6557 | 3.0029 | 84.2377 | 115.6998 | 123.674 | -123.88 | -123.9349
3667.7188 | 123.7427 | -61.441 | 62.178 | 0.04448 | 0.017519 | 0.015763 | 0.014669 | 0.066443 | -0.0011877 | 0.08204 | -58.4564 | 62.1918 | -61.7432 | -61.6562 | 54.2908 | 22.847 | 7.8461 | 7.0816 | 62.2375 | -61.7477 | -0.30212 | 0.013732 | 2.9846 | -0.21515 | -7.8873 | -0.3067 | 0.059509 | 3.2867 | 69.2871 | 68.5226 | 115.7318 | 123.6328 | 2.9846 | 123.6786 | 84.288 | -0.3067 | 123.6328 | 2.9846 | 84.288 | 115.7318 | 123.6786 | -123.9212 | -123.9258
3668.7188 | 123.7289 | -61.4502 | 62.1643 | 0.090256 | 0.01581 | 0.014695 | 0.013601 | 0.065589 | 0.00052127 | 0.081185 | -58.4976 | 62.2284 | -61.7157 | -61.7157 | 54.2175 | 22.7371 | 7.8232 | 7.0496 | 62.2238 | -61.7569 | -0.2655 | 0.064087 | 2.9526 | -0.2655 | -7.9468 | -0.3067 | 0.059509 | 3.2181 | 69.2734 | 68.4998 | 115.6677 | 123.6786 | 2.9526 | 123.674 | 84.1873 | -0.3067 | 123.6786 | 2.9526 | 84.1873 | 115.6677 | 123.674 | -123.88 | -123.9212
3669.7188 | 123.848 | -61.409 | 62.1414 | 0.2047 | 0.018374 | 0.018968 | 0.0097562 | 0.065802 | -0.00097413 | 0.080972 | -58.4564 | 62.1872 | -61.7294 | -61.6196 | 54.2953 | 22.8241 | 7.6584 | 7.1365 | 62.1597 | -61.7294 | -0.32043 | 0.045777 | 2.9526 | -0.21057 | -7.8461 | -0.32043 | 0.018311 | 3.273 | 69.0674 | 68.5455 | 115.7043 | 123.5962 | 2.9526 | 123.5687 | 84.2331 | -0.32043 | 123.5962 | 2.9526 | 84.2331 | 115.7043 | 123.5687 | -123.8708 | -123.8708
3670.7188 | 123.7656 | -61.4273 | 62.1964 | 0.14366 | 0.016451 | 0.016404 | 0.013601 | 0.063025 | 0.0020167 | 0.078195 | -58.4656 | 62.2055 | -61.734 | -61.6837 | 54.2679 | 22.8607 | 7.7957 | 7.045 | 62.2009 | -61.7661 | -0.3067 | 0.009155 | 2.9617 | -0.25635 | -7.9285 | -0.33875 | 0.004578 | 3.2684 | 69.223 | 68.4723 | 115.6952 | 123.6328 | 2.9617 | 123.6282 | 84.288 | -0.33875 | 123.6328 | 2.9617 | 84.288 | 115.6952 | 123.6282 | -123.9304 | -123.9624
3671.7188 | 123.7793 | -61.4594 | 62.1506 | 0.17418 | 0.017519 | 0.015763 | 0.01232 | 0.06388 | -0.00054693 | 0.082681 | -58.4839 | 62.1918 | -61.7249 | -61.6562 | 54.2404 | 22.8424 | 7.782 | 7.0312 | 62.2009 | -61.7386 | -0.2655 | 0.041198 | 2.9755 | -0.19684 | -7.9102 | -0.27923 | 0.050354 | 3.241 | 69.2413 | 68.4906 | 115.6998 | 123.6511 | 2.9755 | 123.6603 | 84.3018 | -0.27923 | 123.6511 | 2.9755 | 84.3018 | 115.6998 | 123.6603 | -123.8754 | -123.8892
3672.7188 | 123.7839 | -61.4548 | 62.1643 | 0.18944 | 0.016024 | 0.014054 | 0.013601 | 0.065161 | 0.0018031 | 0.081399 | -58.4885 | 62.2055 | -61.7432 | -61.6562 | 54.2404 | 22.7783 | 7.7408 | 6.9717 | 62.1872 | -61.7844 | -0.28839 | 0.041198 | 2.9663 | -0.20142 | -7.9239 | -0.32959 | 0.022888 | 3.2547 | 69.1956 | 68.4265 | 115.6952 | 123.6603 | 2.9663 | 123.642 | 84.2331 | -0.32959 | 123.6603 | 2.9663 | 84.2331 | 115.6952 | 123.642 | -123.9075 | -123.9487
3673.7188 | 123.7244 | -61.4456 | 62.1185 | 0.11314 | 0.01816 | 0.017259 | 0.014456 | 0.063452 | -0.0016149 | 0.080544 | -58.461 | 62.2147 | -61.7432 | -61.6837 | 54.1534 | 22.6868 | 7.7957 | 6.9672 | 62.2284 | -61.7569 | -0.29755 | 0.096131 | 2.9846 | -0.23804 | -7.9651 | -0.31128 | 0.10986 | 3.2822 | 69.2413 | 68.4128 | 115.5991 | 123.6603 | 2.9846 | 123.674 | 84.1324 | -0.31128 | 123.6603 | 2.9846 | 84.1324 | 115.5991 | 123.674 | -123.8617 | -123.8754
3674.7188 | 123.7289 | -61.4365 | 62.0956 | 0.097885 | 0.017092 | 0.018327 | 0.013815 | 0.065375 | 9.4068e-05 | 0.07969 | -58.4656 | 62.2055 | -61.7386 | -61.702 | 54.1809 | 22.6776 | 7.8049 | 7.0267 | 62.2284 | -61.7752 | -0.30212 | 0.10986 | 2.9709 | -0.2655 | -7.9147 | -0.33875 | 0.13275 | 3.273 | 69.2413 | 68.4631 | 115.6174 | 123.642 | 2.9709 | 123.6649 | 84.1141 | -0.33875 | 123.642 | 2.9709 | 84.1141 | 115.6174 | 123.6649 | -123.8342 | -123.8708
3675.7188 | 123.7839 | -61.4365 | 62.1826 | 0.18181 | 0.01816 | 0.012132 | 0.0084744 | 0.065589 | 0.0015893 | 0.080972 | -58.5159 | 62.2467 | -61.7386 | -61.6745 | 54.2038 | 22.8836 | 7.8186 | 7.0816 | 62.2192 | -61.7569 | -0.30212 | 0.064087 | 2.9205 | -0.23804 | -7.9788 | -0.32044 | 0.036621 | 3.2227 | 69.2551 | 68.5181 | 115.6403 | 123.6832 | 2.9205 | 123.6557 | 84.3201 | -0.32044 | 123.6832 | 2.9205 | 84.3201 | 115.6403 | 123.6557 | -123.9212 | -123.9395
3676.7188 | 123.848 | -61.4136 | 62.1231 | 0.21996 | 0.014956 | 0.017259 | 0.011038 | 0.064948 | 0.00073487 | 0.080117 | -58.4244 | 62.178 | -61.7294 | -61.6333 | 54.2542 | 22.9156 | 7.7362 | 7.1732 | 62.146 | -61.7386 | -0.31586 | 0.054932 | 2.9892 | -0.21973 | -7.869 | -0.32501 | 0.022888 | 3.3051 | 69.1498 | 68.5867 | 115.6677 | 123.5916 | 2.9892 | 123.5596 | 84.3292 | -0.32501 | 123.5916 | 2.9892 | 84.3292 | 115.6677 | 123.5596 | -123.8525 | -123.8617
3677.7188 | 123.8251 | -61.4273 | 62.1231 | 0.15892 | 0.014529 | 0.015336 | 0.010824 | 0.063452 | 0.0011621 | 0.081399 | -58.4656 | 62.1643 | -61.7249 | -61.6241 | 54.213 | 22.8012 | 7.7225 | 7.0999 | 62.1826 | -61.7386 | -0.29755 | 0.041199 | 2.9617 | -0.19684 | -7.9102 | -0.31128 | 0.059509 | 3.2593 | 69.1498 | 68.5272 | 115.6403 | 123.5916 | 2.9617 | 123.6099 | 84.2285 | -0.31128 | 123.5916 | 2.9617 | 84.2285 | 115.6403 | 123.6099 | -123.848 | -123.8617
3678.7188 | 123.8663 | -61.3724 | 62.1735 | -0.27596 | 0.016024 | 0.013841 | 0.006979 | 0.061103 | 9.4068e-05 | 0.081613 | -58.3969 | 62.114 | -61.6974 | -61.5417 | 54.3411 | 22.8561 | 7.7683 | 7.2372 | 62.178 | -61.647 | -0.32501 | -0.059509 | 2.9755 | -0.16937 | -7.8323 | -0.27466 | 0.004578 | 3.3005 | 69.1406 | 68.6096 | 115.7135 | 123.4863 | 2.9755 | 123.5504 | 84.2285 | -0.27466 | 123.4863 | 2.9755 | 84.2285 | 115.7135 | 123.5504 | -123.8708 | -123.8205
3679.7188 | 123.793 | -61.4136 | 62.1597 | 0.17418 | 0.016665 | 0.018327 | 0.012533 | 0.062171 | 0.00030767 | 0.080758 | -58.4381 | 62.1735 | -61.7477 | -61.6516 | 54.213 | 22.8104 | 7.7545 | 7.1045 | 62.1597 | -61.7523 | -0.33417 | 0.013733 | 2.9755 | -0.23804 | -7.9468 | -0.33875 | 0 | 3.3096 | 69.1681 | 68.5181 | 115.6265 | 123.587 | 2.9755 | 123.5733 | 84.2239 | -0.33875 | 123.587 | 2.9755 | 84.2239 | 115.6265 | 123.5733 | -123.9075 | -123.912
3680.7188 | 123.7701 | -61.4456 | 62.1597 | 0.1284 | 0.019869 | 0.013627 | 0.01296 | 0.065375 | 0.00052127 | 0.077767 | -58.3969 | 62.1597 | -61.7615 | -61.5738 | 54.2862 | 22.7005 | 7.8461 | 7.0679 | 62.1918 | -61.7752 | -0.31586 | 0 | 3.0487 | -0.12817 | -7.8735 | -0.32959 | 0.032043 | 3.3646 | 69.2917 | 68.5135 | 115.7318 | 123.6053 | 3.0487 | 123.6374 | 84.1461 | -0.32959 | 123.6053 | 3.0487 | 84.1461 | 115.7318 | 123.6374 | -123.9212 | -123.9349
3681.7188 | 123.7473 | -61.4502 | 62.1643 | 0.16655 | 0.017733 | 0.014482 | 0.015951 | 0.064734 | 0.0079981 | 0.080972 | -58.4885 | 62.2284 | -61.7249 | -61.9446 | 54.2038 | 23.0484 | 7.7362 | 7.0312 | 62.2238 | -61.7661 | -0.27466 | 0.064087 | 2.9617 | -0.49439 | -7.9605 | -0.31586 | 0.059509 | 3.2364 | 69.1864 | 68.4814 | 115.654 | 123.6786 | 2.9617 | 123.674 | 84.4986 | -0.31586 | 123.6786 | 2.9617 | 84.4986 | 115.654 | 123.674 | -123.8892 | -123.9304
3682.7188 | 123.7793 | -61.441 | 62.1872 | 0.15129 | 0.018587 | 0.012345 | 0.013174 | 0.065802 | 0.0022303 | 0.080758 | -58.4702 | 62.2055 | -61.7294 | -61.6608 | 54.2175 | 22.7875 | 7.782 | 7.0175 | 62.1872 | -61.7661 | -0.28839 | 0.01831 | 2.9709 | -0.21973 | -7.9697 | -0.32501 | 0 | 3.2593 | 69.223 | 68.4586 | 115.6586 | 123.6465 | 2.9709 | 123.6282 | 84.2285 | -0.32501 | 123.6465 | 2.9709 | 84.2285 | 115.6586 | 123.6282 | -123.9166 | -123.9532
3683.7188 | 123.8434 | -61.441 | 62.1277 | 0.15129 | 0.01816 | 0.01555 | 0.0080472 | 0.063666 | 0.00052127 | 0.081399 | -58.4198 | 62.0956 | -61.7157 | -61.5921 | 54.3045 | 22.8882 | 7.6767 | 7.1732 | 62.114 | -61.702 | -0.27466 | -0.032044 | 3.0212 | -0.15106 | -7.8232 | -0.26093 | -0.013733 | 3.2959 | 69.1177 | 68.6142 | 115.7455 | 123.5367 | 3.0212 | 123.555 | 84.3292 | -0.26093 | 123.5367 | 3.0212 | 84.3292 | 115.7455 | 123.555 | -123.8434 | -123.8297
3684.7188 | 123.7976 | -61.441 | 62.178 | 0.21233 | 0.017092 | 0.018968 | 0.013388 | 0.062598 | -0.00076053 | 0.080972 | -58.461 | 62.178 | -61.7477 | -61.6516 | 54.2725 | 22.7829 | 7.7911 | 7.1091 | 62.1414 | -61.7523 | -0.3067 | 0 | 2.98 | -0.21057 | -7.9056 | -0.31128 | -0.036622 | 3.2867 | 69.2322 | 68.5501 | 115.7135 | 123.6191 | 2.98 | 123.5825 | 84.2239 | -0.31128 | 123.6191 | 2.98 | 84.2239 | 115.7135 | 123.5825 | -123.9258 | -123.9304
3685.7188 | 123.8113 | -61.4365 | 62.1597 | 0.1284 | 0.016665 | 0.014909 | 0.014669 | 0.064093 | 0.00094847 | 0.080972 | -58.4473 | 62.1964 | -61.7294 | -61.6562 | 54.1809 | 22.7371 | 7.7637 | 7.0496 | 62.1826 | -61.7432 | -0.29297 | 0.036621 | 2.9892 | -0.21973 | -7.9788 | -0.3067 | 0.022888 | 3.2822 | 69.2001 | 68.486 | 115.6174 | 123.6328 | 2.9892 | 123.6191 | 84.1736 | -0.3067 | 123.6328 | 2.9892 | 84.1736 | 115.6174 | 123.6191 | -123.8892 | -123.9029
3686.7188 | 123.7701 | -61.4502 | 62.1597 | 0.14366 | 0.017947 | 0.016831 | 0.01531 | 0.063025 | 0.0015893 | 0.081185 | -58.4702 | 62.2009 | -61.7386 | -61.6791 | 54.158 | 22.641 | 7.8094 | 7.0541 | 62.2147 | -61.734 | -0.28839 | 0.041199 | 2.98 | -0.22888 | -8.0017 | -0.28381 | 0.054932 | 3.2684 | 69.2596 | 68.5043 | 115.6082 | 123.6511 | 2.98 | 123.6649 | 84.0912 | -0.28381 | 123.6511 | 2.98 | 84.0912 | 115.6082 | 123.6649 | -123.8983 | -123.8937
3687.7188 | 123.7289 | -61.4502 | 62.1689 | 0.067368 | 0.017306 | 0.014054 | 0.016165 | 0.06388 | -0.00054693 | 0.07969 | -58.4702 | 62.1964 | -61.7477 | -61.6745 | 54.1992 | 22.6868 | 7.8461 | 6.9992 | 62.1964 | -61.7798 | -0.29755 | 0.027466 | 2.98 | -0.22431 | -7.9697 | -0.32959 | 0.027466 | 3.2776 | 69.2963 | 68.4494 | 115.6494 | 123.6465 | 2.98 | 123.6465 | 84.137 | -0.32959 | 123.6465 | 2.98 | 84.137 | 115.6494 | 123.6465 | -123.9166 | -123.9487
3688.7344 | 123.793 | -61.4044 | 62.1918 | -0.20729 | 0.016665 | 0.017259 | 0.012747 | 0.061743 | 0.00030767 | 0.080331 | -58.461 | 62.2284 | -61.7661 | -61.5967 | 54.3045 | 22.8287 | 7.8873 | 7.1228 | 62.2375 | -61.7294 | -0.36163 | 0.036622 | 2.9434 | -0.19226 | -7.8873 | -0.32501 | 0.045777 | 3.3051 | 69.2917 | 68.5272 | 115.7089 | 123.6328 | 2.9434 | 123.642 | 84.2331 | -0.32501 | 123.6328 | 2.9434 | 84.2331 | 115.7089 | 123.642 | -123.9578 | -123.9212
3689.7188 | 123.7793 | -61.4502 | 62.1689 | 0.15129 | 0.015597 | 0.017686 | 0.011679 | 0.06388 | 0.00094847 | 0.082467 | -58.4702 | 62.2009 | -61.7294 | -61.6562 | 54.245 | 22.728 | 7.8232 | 7.0541 | 62.1735 | -61.7569 | -0.27924 | 0.032044 | 2.98 | -0.20599 | -7.9239 | -0.3067 | 0.004578 | 3.2593 | 69.2734 | 68.5043 | 115.6952 | 123.6511 | 2.98 | 123.6237 | 84.1782 | -0.3067 | 123.6511 | 2.98 | 84.1782 | 115.6952 | 123.6237 | -123.8983 | -123.9258
3690.7188 | 123.7518 | -61.441 | 62.1735 | 0.12077 | 0.018801 | 0.016618 | 0.013388 | 0.064093 | 0.0018031 | 0.080331 | -58.4473 | 62.2192 | -61.7432 | -61.6699 | 54.2267 | 22.7371 | 7.8415 | 7.0724 | 62.1872 | -61.7477 | -0.30212 | 0.045776 | 2.9938 | -0.22888 | -7.9468 | -0.3067 | 0.013733 | 3.2959 | 69.2825 | 68.5135 | 115.6677 | 123.6603 | 2.9938 | 123.6282 | 84.1782 | -0.3067 | 123.6603 | 2.9938 | 84.1782 | 115.6677 | 123.6282 | -123.9166 | -123.9212
3691.7188 | 123.7427 | -61.4365 | 62.146 | 0.14366 | 0.014315 | 0.018327 | 0.016592 | 0.064734 | -0.00097413 | 0.08204 | -58.7723 | 62.1552 | -61.7844 | -61.7065 | 54.1214 | 22.7875 | 7.8049 | 6.9443 | 62.2238 | -61.7477 | -0.3479 | 0.009155 | 2.6642 | -0.27008 | -8.0246 | -0.31128 | 0.07782 | 3.0121 | 69.2413 | 68.3807 | 115.5579 | 123.5916 | 2.6642 | 123.6603 | 84.2239 | -0.31128 | 123.5916 | 2.6642 | 84.2239 | 115.5579 | 123.6603 | -123.9304 | -123.8937
3692.7188 | 123.7747 | -61.441 | 62.1872 | 0.17418 | 0.018587 | 0.016618 | 0.013815 | 0.063025 | 0.0020167 | 0.080972 | -58.5022 | 62.2101 | -61.7111 | -61.6333 | 53.8925 | 22.3663 | 8.2443 | 7.1915 | 62.2147 | -61.7798 | -0.27008 | 0.022888 | 2.9388 | -0.19226 | -8.2947 | -0.33874 | 0.027466 | 3.2089 | 69.6854 | 68.6325 | 115.3336 | 123.6511 | 2.9388 | 123.6557 | 83.8074 | -0.33874 | 123.6511 | 2.9388 | 83.8074 | 115.3336 | 123.6557 | -123.8983 | -123.967
3693.7344 | 123.8388 | -61.3953 | 62.1826 | -0.23781 | 0.01346 | 0.012986 | 0.0074062 | 0.061957 | -0.0014013 | 0.079904 | -58.4152 | 62.1643 | -61.702 | -61.5692 | 54.4006 | 22.9156 | 7.782 | 7.1411 | 62.1964 | -61.702 | -0.3067 | -0.01831 | 2.98 | -0.17395 | -7.782 | -0.3067 | 0.013733 | 3.2867 | 69.1772 | 68.5364 | 115.7959 | 123.5596 | 2.98 | 123.5916 | 84.3109 | -0.3067 | 123.5596 | 2.98 | 84.3109 | 115.7959 | 123.5916 | -123.8846 | -123.8846
3694.7188 | 123.761 | -61.4227 | 62.1918 | -0.0089264 | 0.016878 | 0.019395 | 0.016378 | 0.062171 | -0.00076053 | 0.081613 | -58.4152 | 62.1918 | -61.6928 | -61.6241 | 54.2542 | 22.7554 | 7.7911 | 7.0221 | 62.2238 | -61.7432 | -0.27008 | 0 | 3.0075 | -0.20142 | -7.9376 | -0.32044 | 0.032044 | 3.2776 | 69.2139 | 68.4448 | 115.6769 | 123.6145 | 3.0075 | 123.6465 | 84.1782 | -0.32044 | 123.6145 | 3.0075 | 84.1782 | 115.6769 | 123.6465 | -123.8846 | -123.9349
3695.7188 | 123.7701 | -61.4136 | 62.1735 | -0.016556 | 0.015383 | 0.014268 | 0.016378 | 0.065375 | -0.0014013 | 0.079904 | -58.3923 | 62.2009 | -61.7065 | -61.6013 | 54.3732 | 22.8333 | 7.8094 | 7.0267 | 62.2147 | -61.7615 | -0.29297 | 0.027466 | 3.0212 | -0.18768 | -7.8003 | -0.3479 | 0.041199 | 3.3142 | 69.223 | 68.4402 | 115.7867 | 123.6145 | 3.0212 | 123.6282 | 84.2468 | -0.3479 | 123.6145 | 3.0212 | 84.2468 | 115.7867 | 123.6282 | -123.88 | -123.9349
3696.7188 | 123.7564 | -61.4502 | 62.1826 | 0.013962 | 0.017733 | 0.016831 | 0.016378 | 0.066443 | 9.4068e-05 | 0.080544 | -58.4381 | 62.1872 | -61.7111 | -61.6379 | 54.3365 | 22.847 | 7.869 | 7.0404 | 62.2147 | -61.7203 | -0.26093 | 0.004578 | 3.0121 | -0.18768 | -7.8461 | -0.27008 | 0.032044 | 3.273 | 69.3192 | 68.4906 | 115.7867 | 123.6374 | 3.0121 | 123.6649 | 84.2972 | -0.27008 | 123.6374 | 3.0121 | 84.2972 | 115.7867 | 123.6649 | -123.8937 | -123.9029
3697.7188 | 123.7061 | -61.4456 | 62.1735 | 0.1284 | 0.016451 | 0.014268 | 0.01296 | 0.064307 | 9.4068e-05 | 0.080544 | -58.493 | 62.2284 | -61.7249 | -61.6791 | 54.2679 | 22.7051 | 7.8369 | 6.9534 | 62.2101 | -61.7477 | -0.27924 | 0.054932 | 2.9526 | -0.23346 | -7.9056 | -0.30212 | 0.036621 | 3.2318 | 69.2825 | 68.399 | 115.7135 | 123.674 | 2.9526 | 123.6557 | 84.1507 | -0.30212 | 123.674 | 2.9526 | 84.1507 | 115.7135 | 123.6557 | -123.8983 | -123.9212
3698.7344 | 123.8983 | -61.3678 | 62.1414 | -0.16914 | 0.013033 | 0.015977 | 0.0037746 | 0.06153 | 9.4068e-05 | 0.080972 | -58.3832 | 62.0819 | -61.7111 | -61.5189 | 54.4785 | 22.7646 | 8.2306 | 7.3929 | 62.2559 | -61.6241 | -0.34332 | -0.059509 | 2.9846 | -0.15106 | -7.663 | -0.25635 | 0.11444 | 3.3279 | 69.5984 | 68.7607 | 115.8463 | 123.4497 | 2.9846 | 123.6237 | 84.1324 | -0.25635 | 123.4497 | 2.9846 | 84.1324 | 115.8463 | 123.6237 | -123.8525 | -123.7656
3699.7188 | 123.7564 | -61.441 | 62.1918 | 0.04448 | 0.017306 | 0.012559 | 0.015097 | 0.062598 | -0.0016149 | 0.081399 | -58.4656 | 62.2192 | -61.7249 | -61.6379 | 54.1763 | 22.5769 | 7.7911 | 6.9763 | 62.1964 | -61.7615 | -0.28381 | 0.027466 | 2.9755 | -0.19684 | -8.0154 | -0.32043 | 0.004578 | 3.2593 | 69.2322 | 68.4174 | 115.6174 | 123.6603 | 2.9755 | 123.6374 | 84.0179 | -0.32043 | 123.6603 | 2.9755 | 84.0179 | 115.6174 | 123.6374 | -123.9166 | -123.9532
3700.7188 | 123.761 | -61.4456 | 62.1872 | 0.052109 | 0.016451 | 0.017899 | 0.012533 | 0.064734 | -0.00011953 | 0.081613 | -58.4656 | 62.1918 | -61.7294 | -61.6333 | 54.2953 | 22.6456 | 7.7911 | 6.9901 | 62.2055 | -61.7432 | -0.28381 | 0.004577 | 2.98 | -0.18768 | -7.8918 | -0.29755 | 0.01831 | 3.2639 | 69.2368 | 68.4357 | 115.741 | 123.6374 | 2.98 | 123.6511 | 84.0912 | -0.29755 | 123.6374 | 2.98 | 84.0912 | 115.741 | 123.6511 | -123.9166 | -123.9304
3701.7188 | 123.8159 | -61.4227 | 62.178 | 0.19707 | 0.016878 | 0.012986 | 0.014883 | 0.064948 | -0.0016149 | 0.080544 | -58.3328 | 62.2192 | -61.7249 | -61.5738 | 54.3594 | 22.8104 | 7.782 | 7.0633 | 62.2238 | -61.7386 | -0.30213 | 0.041198 | 3.0899 | -0.15106 | -7.8186 | -0.31586 | 0.045776 | 3.392 | 69.2047 | 68.486 | 115.7822 | 123.642 | 3.0899 | 123.6465 | 84.2331 | -0.31586 | 123.642 | 3.0899 | 84.2331 | 115.7822 | 123.6465 | -123.9029 | -123.9166
3702.7188 | 123.7701 | -61.4227 | 62.1735 | -0.054703 | 0.015169 | 0.014695 | 0.014669 | 0.066443 | 0.00030767 | 0.079476 | -58.429 | 62.2055 | -61.6837 | -61.615 | 54.3274 | 22.6273 | 7.814 | 7.0404 | 62.2009 | -61.7432 | -0.26093 | 0.032043 | 2.9938 | -0.19226 | -7.8461 | -0.32044 | 0.027466 | 3.2547 | 69.2368 | 68.4631 | 115.7501 | 123.6282 | 2.9938 | 123.6237 | 84.05 | -0.32044 | 123.6282 | 2.9938 | 84.05 | 115.7501 | 123.6237 | -123.8571 | -123.9166
3703.7344 | 123.8617 | -61.3907 | 62.1506 | -0.09285 | 0.014529 | 0.0132 | 0.0054836 | 0.063452 | -0.00054693 | 0.079904 | -58.4244 | 62.1597 | -61.6837 | -61.5646 | 54.4052 | 22.7417 | 7.7271 | 7.1732 | 62.178 | -61.6974 | -0.29297 | 0.009155 | 2.9663 | -0.17395 | -7.7454 | -0.3067 | 0.027466 | 3.2593 | 69.1177 | 68.5638 | 115.7959 | 123.5504 | 2.9663 | 123.5687 | 84.1324 | -0.3067 | 123.5504 | 2.9663 | 84.1324 | 115.7959 | 123.5687 | -123.8342 | -123.848
3704.7188 | 123.7564 | -61.441 | 62.2009 | 0.059738 | 0.01816 | 0.01555 | 0.015524 | 0.06388 | 0.0011621 | 0.081613 | -58.493 | 62.2147 | -61.6928 | -61.6333 | 54.3503 | 22.6913 | 7.814 | 7.0129 | 62.1872 | -61.7615 | -0.25177 | 0.013733 | 2.948 | -0.19226 | -7.8506 | -0.32043 | -0.013733 | 3.1998 | 69.2551 | 68.454 | 115.7913 | 123.6557 | 2.948 | 123.6282 | 84.1324 | -0.32043 | 123.6557 | 2.948 | 84.1324 | 115.7913 | 123.6282 | -123.8937 | -123.9624
3705.7188 | 123.7701 | -61.4319 | 62.1918 | -0.016556 | 0.016878 | 0.016618 | 0.01766 | 0.065589 | 0.00052127 | 0.081613 | -58.4564 | 62.233 | -61.7157 | -61.6287 | 54.3457 | 22.7325 | 7.782 | 7.0175 | 62.2101 | -61.7477 | -0.28381 | 0.041199 | 2.9755 | -0.19684 | -7.8461 | -0.31586 | 0.018311 | 3.2593 | 69.2139 | 68.4494 | 115.7776 | 123.6649 | 2.9755 | 123.642 | 84.1644 | -0.31586 | 123.6649 | 2.9755 | 84.1644 | 115.7776 | 123.642 | -123.9075 | -123.9395
3706.7188 | 123.7701 | -61.4365 | 62.1597 | 0.0063326 | 0.017092 | 0.018113 | 0.013815 | 0.067298 | 0.00094847 | 0.079904 | -58.429 | 62.2238 | -61.7294 | -61.6333 | 54.332 | 22.6959 | 7.7774 | 7.0312 | 62.2101 | -61.7386 | -0.29297 | 0.064087 | 3.0075 | -0.19684 | -7.8278 | -0.30212 | 0.050354 | 3.3005 | 69.2139 | 68.4677 | 115.7684 | 123.6603 | 3.0075 | 123.6465 | 84.1324 | -0.30212 | 123.6603 | 3.0075 | 84.1324 | 115.7684 | 123.6465 | -123.8892 | -123.8983
3707.7188 | 123.7564 | -61.409 | 62.2101 | 0.013962 | 0.018374 | 0.016618 | 0.016378 | 0.064948 | -0.00054693 | 0.080972 | -58.4335 | 62.2375 | -61.7249 | -61.6653 | 54.3274 | 22.641 | 7.7911 | 6.9901 | 62.2284 | -61.7615 | -0.31586 | 0.027466 | 2.9755 | -0.25635 | -7.8827 | -0.35248 | 0.018311 | 3.2913 | 69.2001 | 68.399 | 115.7364 | 123.6465 | 2.9755 | 123.6374 | 84.05 | -0.35248 | 123.6465 | 2.9755 | 84.05 | 115.7364 | 123.6374 | -123.9349 | -123.9716
3708.7188 | 123.8113 | -61.4182 | 62.1552 | -0.047073 | 0.01816 | 0.020677 | 0.014669 | 0.066443 | -0.00076053 | 0.079263 | -58.3786 | 62.2147 | -61.7249 | -61.6013 | 54.3594 | 22.9111 | 7.782 | 7.0816 | 62.2101 | -61.7294 | -0.3067 | 0.05951 | 3.0396 | -0.1831 | -7.7957 | -0.31128 | 0.054932 | 3.3463 | 69.2001 | 68.4998 | 115.7776 | 123.6328 | 3.0396 | 123.6282 | 84.3292 | -0.31128 | 123.6328 | 3.0396 | 84.3292 | 115.7776 | 123.6282 | -123.88 | -123.8846
3709.7188 | 123.7244 | -61.4456 | 62.178 | 0.082626 | 0.017519 | 0.016831 | 0.014029 | 0.064521 | -0.00011953 | 0.080544 | -58.4702 | 62.2284 | -61.7249 | -61.6928 | 54.332 | 22.7646 | 7.8232 | 6.9626 | 62.1918 | -61.7752 | -0.27924 | 0.050354 | 2.9755 | -0.24719 | -7.8461 | -0.32959 | 0.013732 | 3.2547 | 69.2688 | 68.4082 | 115.7776 | 123.674 | 2.9755 | 123.6374 | 84.2102 | -0.32959 | 123.674 | 2.9755 | 84.2102 | 115.7776 | 123.6374 | -123.9029 | -123.9532
3710.7188 | 123.7564 | -61.4227 | 62.1689 | -0.031814 | 0.018587 | 0.020677 | 0.015524 | 0.064521 | 0.0018031 | 0.080972 | -58.429 | 62.2238 | -61.6974 | -61.6379 | 54.3182 | 22.7737 | 7.7683 | 7.0267 | 62.1964 | -61.7432 | -0.27466 | 0.054932 | 2.9938 | -0.21515 | -7.8506 | -0.32044 | 0.027466 | 3.2684 | 69.191 | 68.4494 | 115.741 | 123.6465 | 2.9938 | 123.6191 | 84.1965 | -0.32044 | 123.6465 | 2.9938 | 84.1965 | 115.741 | 123.6191 | -123.8663 | -123.912
3711.7188 | 123.7564 | -61.4502 | 62.1826 | 0.013962 | 0.016238 | 0.016404 | 0.01296 | 0.06623 | -0.00097413 | 0.080544 | -58.4518 | 62.233 | -61.7157 | -61.647 | 54.2953 | 22.8287 | 7.814 | 7.0038 | 62.2192 | -61.7432 | -0.2655 | 0.050354 | 2.9984 | -0.19684 | -7.8873 | -0.29297 | 0.036621 | 3.2639 | 69.2642 | 68.454 | 115.7455 | 123.6832 | 2.9984 | 123.6694 | 84.2789 | -0.29297 | 123.6832 | 2.9984 | 84.2789 | 115.7455 | 123.6694 | -123.8983 | -123.9258
3712.7188 | 123.7564 | -61.4456 | 62.1918 | 0.0063326 | 0.020083 | 0.016404 | 0.014029 | 0.066443 | -0.00097413 | 0.079476 | -58.4656 | 62.1964 | -61.7203 | -61.6516 | 54.3274 | 22.8653 | 7.8186 | 7.0404 | 62.2147 | -61.7386 | -0.27466 | 0.004578 | 2.98 | -0.20599 | -7.8644 | -0.29297 | 0.022889 | 3.2547 | 69.2642 | 68.486 | 115.773 | 123.642 | 2.98 | 123.6603 | 84.3109 | -0.29297 | 123.642 | 2.98 | 84.3109 | 115.773 | 123.6603 | -123.912 | -123.9304
3713.7188 | 123.8525 | -61.3953 | 62.1414 | 0.23521 | 0.015383 | 0.012559 | 0.010397 | 0.066016 | 0.00052127 | 0.081826 | -58.4061 | 62.1231 | -61.7111 | -61.5875 | 54.4006 | 23.0301 | 7.3151 | 7.1136 | 62.146 | -61.7294 | -0.31586 | -0.01831 | 2.9892 | -0.19226 | -7.7408 | -0.33417 | 0.004578 | 3.3051 | 68.7103 | 68.5089 | 115.7959 | 123.5184 | 2.9892 | 123.5413 | 84.4254 | -0.33417 | 123.5184 | 2.9892 | 84.4254 | 115.7959 | 123.5413 | -123.8525 | -123.8708
3714.7188 | 123.7656 | -61.4548 | 62.1689 | 0.0063326 | 0.016878 | 0.018968 | 0.01531 | 0.062171 | -0.0024695 | 0.079904 | -58.4152 | 62.2009 | -61.7294 | -61.6516 | 54.3365 | 22.9431 | 7.8049 | 7.077 | 62.2009 | -61.7615 | -0.27466 | 0.032044 | 3.0396 | -0.19684 | -7.8323 | -0.3067 | 0.032044 | 3.3142 | 69.2596 | 68.5318 | 115.7913 | 123.6557 | 3.0396 | 123.6557 | 84.3979 | -0.3067 | 123.6557 | 3.0396 | 84.3979 | 115.7913 | 123.6557 | -123.8983 | -123.9304
3715.7188 | 123.7793 | -61.4136 | 62.1964 | -0.12337 | 0.017519 | 0.01555 | 0.014456 | 0.064093 | 0.0030847 | 0.079476 | -58.4106 | 62.2467 | -61.6974 | -61.6928 | 54.5975 | 23.0072 | 7.8323 | 7.1686 | 62.2147 | -61.7477 | -0.28381 | 0.050354 | 3.0029 | -0.27924 | -7.5989 | -0.33417 | 0.018311 | 3.2867 | 69.2459 | 68.5822 | 116.011 | 123.6603 | 3.0029 | 123.6282 | 84.4208 | -0.33417 | 123.6603 | 3.0029 | 84.4208 | 116.011 | 123.6282 | -123.8937 | -123.9441
3716.7188 | 123.6603 | -61.409 | 62.1735 | -0.11574 | 0.017947 | 0.011491 | 0.01296 | 0.064307 | 0.00052127 | 0.080544 | -58.4015 | 62.233 | -61.7203 | -61.6058 | 54.3182 | 22.8699 | 7.7911 | 7.1136 | 62.2055 | -61.7569 | -0.31128 | 0.059509 | 3.0075 | -0.19684 | -7.8552 | -0.3479 | 0.032043 | 3.3188 | 69.2001 | 68.5226 | 115.7272 | 123.642 | 3.0075 | 123.6145 | 84.2789 | -0.3479 | 123.642 | 3.0075 | 84.2789 | 115.7272 | 123.6145 | -123.8937 | -123.9304
3717.7188 | 123.7701 | -61.4227 | 62.1872 | -0.09285 | 0.016451 | 0.014909 | 0.015524 | 0.065375 | 9.4068e-05 | 0.079904 | -58.4061 | 62.2238 | -61.7203 | -61.6104 | 54.4144 | 22.9706 | 7.7957 | 7.0999 | 62.233 | -61.7432 | -0.29755 | 0.036621 | 3.0167 | -0.18768 | -7.7728 | -0.32044 | 0.045776 | 3.3142 | 69.2184 | 68.5226 | 115.8371 | 123.6465 | 3.0167 | 123.6557 | 84.3933 | -0.32044 | 123.6465 | 3.0167 | 84.3933 | 115.8371 | 123.6557 | -123.9075 | -123.9304
3718.7188 | 123.7793 | -61.4227 | 62.1872 | -0.054703 | 0.017519 | 0.014054 | 0.014883 | 0.065161 | 0.00073487 | 0.080331 | -58.4518 | 62.2192 | -61.7249 | -61.6333 | 54.3549 | 22.8745 | 7.8323 | 7.0587 | 62.2192 | -61.734 | -0.30213 | 0.032043 | 2.9709 | -0.21057 | -7.8323 | -0.31128 | 0.032043 | 3.273 | 69.2551 | 68.4814 | 115.7776 | 123.642 | 2.9709 | 123.642 | 84.2972 | -0.31128 | 123.642 | 2.9709 | 84.2972 | 115.7776 | 123.642 | -123.912 | -123.9212
3719.7188 | 123.7518 | -61.4319 | 62.178 | -0.10048 | 0.016878 | 0.012345 | 0.014669 | 0.066016 | 9.4068e-05 | 0.07969 | -58.3878 | 62.2192 | -61.7386 | -61.6241 | 54.3274 | 22.9477 | 7.7728 | 7.0587 | 62.1964 | -61.7432 | -0.3067 | 0.041198 | 3.0441 | -0.19226 | -7.8506 | -0.31128 | 0.01831 | 3.3508 | 69.2047 | 68.4906 | 115.7593 | 123.6511 | 3.0441 | 123.6282 | 84.3796 | -0.31128 | 123.6511 | 3.0441 | 84.3796 | 115.7593 | 123.6282 | -123.9166 | -123.9212
3720.7188 | 123.7976 | -61.4182 | 62.1918 | -0.12337 | 0.015597 | 0.015122 | 0.014669 | 0.066016 | -0.0026831 | 0.080758 | -58.3832 | 62.2055 | -61.7111 | -61.6104 | 54.3594 | 22.9019 | 7.7454 | 7.0541 | 62.2421 | -61.7615 | -0.29297 | 0.013733 | 3.035 | -0.19226 | -7.8323 | -0.34332 | 0.050354 | 3.3279 | 69.1635 | 68.4723 | 115.7776 | 123.6237 | 3.035 | 123.6603 | 84.3201 | -0.34332 | 123.6237 | 3.035 | 84.3201 | 115.7776 | 123.6603 | -123.9029 | -123.9532
3721.7188 | 123.7976 | -61.4227 | 62.1552 | 2.0205 | 0.015383 | 0.012773 | 0.015951 | 0.065802 | -0.00054693 | 0.081399 | -58.2779 | 62.2147 | -61.7294 | -61.5829 | 54.3411 | 22.8607 | 7.814 | 7.1823 | 62.2284 | -61.7111 | -0.3067 | 0.05951 | 3.1448 | -0.16022 | -7.814 | -0.28839 | 0.073243 | 3.4515 | 69.2368 | 68.605 | 115.7639 | 123.6374 | 3.1448 | 123.6511 | 84.2834 | -0.28839 | 123.6374 | 3.1448 | 84.2834 | 115.7639 | 123.6511 | -123.8846 | -123.8663
3722.7188 | 123.7976 | -61.4044 | 62.178 | -0.12337 | 0.016451 | 0.013841 | 0.012533 | 0.064093 | -0.00011953 | 0.079904 | -58.4198 | 62.2375 | -61.7065 | -61.5967 | 54.3045 | 22.8516 | 7.8186 | 7.0816 | 62.233 | -61.734 | -0.30212 | 0.059509 | 2.9846 | -0.19226 | -7.8735 | -0.32959 | 0.054931 | 3.2867 | 69.223 | 68.486 | 115.7089 | 123.642 | 2.9846 | 123.6374 | 84.256 | -0.32959 | 123.642 | 2.9846 | 84.256 | 115.7089 | 123.6374 | -123.8846 | -123.912
3723.7188 | 123.7427 | -61.4639 | 62.1872 | 0.04448 | 0.018374 | 0.015336 | 0.015097 | 0.065375 | -0.0018285 | 0.07969 | -58.4381 | 62.2101 | -61.7294 | -61.6608 | 54.2633 | 22.7142 | 7.8049 | 6.9809 | 62.2055 | -61.7203 | -0.2655 | 0.022888 | 3.0258 | -0.19684 | -7.9239 | -0.25635 | 0.01831 | 3.2913 | 69.2688 | 68.4448 | 115.7272 | 123.674 | 3.0258 | 123.6694 | 84.1782 | -0.25635 | 123.674 | 3.0258 | 84.1782 | 115.7272 | 123.6694 | -123.9166 | -123.9075
3724.7188 | 123.7747 | -61.4182 | 62.1826 | -0.09285 | 0.016238 | 0.015122 | 0.014242 | 0.063666 | -0.00054693 | 0.081826 | -58.4152 | 62.1872 | -61.7386 | -61.5921 | 54.3869 | 22.8928 | 7.782 | 7.0953 | 62.1964 | -61.734 | -0.32043 | 0.004578 | 3.0029 | -0.17395 | -7.7957 | -0.31586 | 0.013733 | 3.3234 | 69.2001 | 68.5135 | 115.8051 | 123.6053 | 3.0029 | 123.6145 | 84.3109 | -0.31586 | 123.6053 | 3.0029 | 84.3109 | 115.8051 | 123.6145 | -123.9212 | -123.9166
3725.7188 | 123.8022 | -61.4273 | 62.1597 | -0.1844 | 0.019015 | 0.017045 | 0.016378 | 0.065375 | -0.00033333 | 0.084176 | -58.4061 | 62.2192 | -61.7111 | -61.5875 | 54.3411 | 22.8195 | 7.7637 | 7.0862 | 62.233 | -61.7294 | -0.28381 | 0.059509 | 3.0212 | -0.16022 | -7.8186 | -0.30212 | 0.073242 | 3.3051 | 69.191 | 68.5135 | 115.7684 | 123.6465 | 3.0212 | 123.6603 | 84.2468 | -0.30212 | 123.6465 | 3.0212 | 84.2468 | 115.7684 | 123.6603 | -123.8708 | -123.8892
3726.7188 | 123.7885 | -61.4136 | 62.2284 | -0.16914 | 0.014956 | 0.016191 | 0.013815 | 0.064948 | 0.0013757 | 0.081399 | -58.4152 | 62.2192 | -61.7157 | -61.5875 | 54.3228 | 22.7921 | 7.7408 | 7.0953 | 62.2147 | -61.7111 | -0.30212 | -0.009156 | 2.9984 | -0.17395 | -7.9056 | -0.29755 | -0.013733 | 3.3005 | 69.1544 | 68.5089 | 115.7364 | 123.6328 | 2.9984 | 123.6282 | 84.2056 | -0.29755 | 123.6328 | 2.9984 | 84.2056 | 115.7364 | 123.6282 | -123.9441 | -123.9395
3727.7188 | 123.7747 | -61.4136 | 62.1872 | -0.23781 | 0.016665 | 0.014695 | 0.012747 | 0.064093 | -0.00054693 | 0.081613 | -58.3923 | 62.1964 | -61.7157 | -61.5967 | 54.3274 | 22.8058 | 7.7774 | 7.0999 | 62.2284 | -61.7111 | -0.30212 | 0.009155 | 3.0212 | -0.18311 | -7.8598 | -0.29755 | 0.041199 | 3.3234 | 69.191 | 68.5135 | 115.741 | 123.6099 | 3.0212 | 123.642 | 84.2194 | -0.29755 | 123.6099 | 3.0212 | 84.2194 | 115.741 | 123.642 | -123.9029 | -123.8983
3728.7188 | 123.7061 | -61.4365 | 62.1918 | 0.052109 | 0.019015 | 0.017472 | 0.016378 | 0.066443 | 0.00073487 | 0.079904 | -58.4473 | 62.2147 | -61.7477 | -61.6562 | 54.245 | 22.673 | 7.8049 | 7.0129 | 62.2238 | -61.7249 | -0.31128 | 0.022889 | 2.9892 | -0.21973 | -7.9468 | -0.28839 | 0.032044 | 3.3005 | 69.2413 | 68.4494 | 115.6815 | 123.6511 | 2.9892 | 123.6603 | 84.1095 | -0.28839 | 123.6511 | 2.9892 | 84.1095 | 115.6815 | 123.6603 | -123.9395 | -123.9166
3729.7188 | 123.7473 | -61.4365 | 62.2238 | -0.19966 | 0.014956 | 0.0099954 | 0.012747 | 0.063025 | -0.00076053 | 0.081185 | -58.4518 | 62.233 | -61.7203 | -61.6333 | 54.2404 | 22.7234 | 7.8827 | 7.0175 | 62.233 | -61.7249 | -0.28381 | 0.009155 | 2.9846 | -0.19684 | -7.9834 | -0.28839 | 0.009155 | 3.2684 | 69.3192 | 68.454 | 115.6769 | 123.6694 | 2.9846 | 123.6694 | 84.1599 | -0.28839 | 123.6694 | 2.9846 | 84.1599 | 115.6769 | 123.6694 | -123.9441 | -123.9487
3730.7188 | 123.793 | -61.3861 | 62.2375 | -0.24544 | 0.015169 | 0.013413 | 0.0099698 | 0.061103 | 0.00094847 | 0.078408 | -58.4793 | 62.2192 | -61.7111 | -61.6287 | 54.2999 | 22.7097 | 7.8644 | 7.0724 | 62.265 | -61.7294 | -0.32501 | -0.018311 | 2.9068 | -0.24262 | -7.9376 | -0.34332 | 0.027466 | 3.2318 | 69.2505 | 68.4586 | 115.686 | 123.6053 | 2.9068 | 123.6511 | 84.0958 | -0.34332 | 123.6053 | 2.9068 | 84.0958 | 115.686 | 123.6511 | -123.9487 | -123.967
3731.7188 | 123.8297 | -61.3907 | 62.2009 | -0.21492 | 0.016024 | 0.011918 | 0.012747 | 0.063666 | 9.4068e-05 | 0.080758 | -58.4335 | 62.2192 | -61.7111 | -61.5921 | 54.277 | 22.7097 | 7.782 | 7.0679 | 62.2284 | -61.7294 | -0.32043 | 0.01831 | 2.9572 | -0.20142 | -7.9239 | -0.33874 | 0.027466 | 3.2776 | 69.1727 | 68.4586 | 115.6677 | 123.6099 | 2.9572 | 123.6191 | 84.1003 | -0.33874 | 123.6099 | 2.9572 | 84.1003 | 115.6677 | 123.6191 | -123.912 | -123.9304
3732.7188 | 123.7793 | -61.4182 | 62.2192 | -0.16914 | 0.012606 | 0.015977 | 0.011251 | 0.063025 | -0.0020421 | 0.080117 | -58.4473 | 62.2192 | -61.7477 | -61.6287 | 54.2953 | 22.7097 | 7.8552 | 7.045 | 62.2421 | -61.7065 | -0.32959 | 0 | 2.9709 | -0.21057 | -7.9239 | -0.28839 | 0.022888 | 3.3005 | 69.2734 | 68.4631 | 115.7135 | 123.6374 | 2.9709 | 123.6603 | 84.1278 | -0.28839 | 123.6374 | 2.9709 | 84.1278 | 115.7135 | 123.6603 | -123.967 | -123.9258
3733.7344 | 123.7427 | -61.4639 | 62.1552 | 1.0516 | 0.015383 | 0.012132 | 0.011679 | 0.064093 | 0.0020167 | 0.079904 | -58.223 | 62.1826 | -61.7203 | -61.6287 | 54.2542 | 22.6273 | 7.7179 | 6.9305 | 62.2238 | -61.7615 | -0.25635 | 0.027466 | 3.241 | -0.16479 | -7.901 | -0.29755 | 0.068665 | 3.4973 | 69.1818 | 68.3945 | 115.7181 | 123.6465 | 3.241 | 123.6877 | 84.0912 | -0.29755 | 123.6465 | 3.241 | 84.0912 | 115.7181 | 123.6877 | -123.8754 | -123.9166
3734.7188 | 123.7289 | -61.4044 | 62.2192 | -0.23018 | 0.017733 | 0.011704 | 0.010183 | 0.06388 | 0.00052127 | 0.077554 | -58.5068 | 62.2055 | -61.7157 | -61.6287 | 54.2542 | 22.8195 | 7.8552 | 7.0129 | 62.233 | -61.7203 | -0.31128 | -0.013733 | 2.8976 | -0.2243 | -7.9651 | -0.31586 | 0.013733 | 3.2089 | 69.2596 | 68.4174 | 115.6586 | 123.6099 | 2.8976 | 123.6374 | 84.2239 | -0.31586 | 123.6099 | 2.8976 | 84.2239 | 115.6586 | 123.6374 | -123.9349 | -123.9395
3735.7188 | 123.7701 | -61.4273 | 62.2375 | -0.20729 | 0.015597 | 0.011918 | 0.010824 | 0.063452 | 0.0011621 | 0.080972 | -58.342 | 62.2147 | -61.702 | -61.615 | 54.2862 | 22.6959 | 7.9056 | 7.0404 | 62.2467 | -61.7157 | -0.27466 | -0.022888 | 3.0853 | -0.18768 | -7.9514 | -0.28839 | 0.009155 | 3.36 | 69.3329 | 68.4677 | 115.7135 | 123.642 | 3.0853 | 123.674 | 84.1232 | -0.28839 | 123.642 | 3.0853 | 84.1232 | 115.7135 | 123.674 | -123.9395 | -123.9532
3736.7188 | 123.7793 | -61.3907 | 62.2147 | -0.29121 | 0.01581 | 0.017045 | 0.0084744 | 0.061957 | 0.00073487 | 0.079049 | -58.4061 | 62.1918 | -61.6699 | -61.6013 | 54.2816 | 22.7417 | 7.7866 | 7.0404 | 62.2421 | -61.6837 | -0.27924 | -0.022889 | 2.9846 | -0.21057 | -7.933 | -0.29297 | 0.027465 | 3.2639 | 69.1772 | 68.4311 | 115.6723 | 123.5825 | 2.9846 | 123.6328 | 84.1324 | -0.29297 | 123.5825 | 2.9846 | 84.1324 | 115.6723 | 123.6328 | -123.8846 | -123.8983
3737.7188 | 123.7656 | -61.4365 | 62.2009 | -0.19966 | 0.016024 | 0.014268 | 0.012106 | 0.059607 | 0.0015893 | 0.078408 | -58.461 | 62.2238 | -61.7157 | -61.6333 | 54.3365 | 22.7646 | 7.901 | 7.045 | 62.2147 | -61.7294 | -0.27924 | 0.022888 | 2.9755 | -0.19684 | -7.8644 | -0.29297 | 0.013733 | 3.2547 | 69.3375 | 68.4814 | 115.773 | 123.6603 | 2.9755 | 123.6511 | 84.201 | -0.29297 | 123.6603 | 2.9755 | 84.201 | 115.773 | 123.6511 | -123.9166 | -123.9304
3738.7188 | 123.7656 | -61.4044 | 62.1918 | -0.19203 | 0.017519 | 0.010423 | 0.015738 | 0.062812 | -0.00011953 | 0.078622 | -58.4061 | 62.1918 | -61.7111 | -61.5829 | 54.3411 | 22.8104 | 7.7774 | 7.0587 | 62.2101 | -61.734 | -0.3067 | 0 | 2.9984 | -0.17853 | -7.8506 | -0.32959 | 0.018311 | 3.3051 | 69.1818 | 68.4631 | 115.7455 | 123.5962 | 2.9984 | 123.6145 | 84.2148 | -0.32959 | 123.5962 | 2.9984 | 84.2148 | 115.7455 | 123.6145 | -123.9029 | -123.9258
3739.7188 | 123.7381 | -61.441 | 62.2192 | -0.23018 | 0.017306 | 0.0095682 | 0.012533 | 0.060462 | -0.0014013 | 0.080331 | -58.6075 | 62.1826 | -61.7111 | -61.6745 | 54.2862 | 22.6868 | 7.8369 | 6.9855 | 62.2192 | -61.7065 | -0.27008 | -0.036621 | 2.8336 | -0.23346 | -7.933 | -0.2655 | 0 | 3.1036 | 69.278 | 68.4265 | 115.7272 | 123.6237 | 2.8336 | 123.6603 | 84.1278 | -0.2655 | 123.6237 | 2.8336 | 84.1278 | 115.7272 | 123.6603 | -123.9304 | -123.9258
3740.7188 | 123.7839 | -61.409 | 62.2147 | -0.23781 | 0.011965 | 0.014268 | 0.012747 | 0.060675 | -0.00033333 | 0.080117 | -58.4747 | 62.1918 | -61.7203 | -61.6379 | 54.3091 | 22.6501 | 8.1573 | 7.0221 | 62.2604 | -61.6791 | -0.31128 | -0.022889 | 2.9343 | -0.22888 | -7.9056 | -0.27008 | 0.045776 | 3.2455 | 69.5663 | 68.4311 | 115.7181 | 123.6008 | 2.9343 | 123.6694 | 84.0591 | -0.27008 | 123.6008 | 2.9343 | 84.0591 | 115.7181 | 123.6694 | -123.9349 | -123.8937
3741.7188 | 123.761 | -61.409 | 62.233 | -0.16151 | 0.014315 | 0.011918 | 0.0099698 | 0.062598 | 9.4068e-05 | 0.080117 | -58.4702 | 62.1872 | -61.7249 | -61.6287 | 54.3732 | 22.8058 | 7.9056 | 7.0404 | 62.2375 | -61.7111 | -0.31586 | -0.045776 | 2.9388 | -0.21973 | -7.8598 | -0.30212 | 0.004578 | 3.2547 | 69.3146 | 68.4494 | 115.7822 | 123.5962 | 2.9388 | 123.6465 | 84.2148 | -0.30212 | 123.5962 | 2.9388 | 84.2148 | 115.7822 | 123.6465 | -123.9578 | -123.9441
3742.7188 | 123.7518 | -61.4319 | 62.2284 | -0.19966 | 0.012179 | 0.0093546 | 0.0093288 | 0.058325 | -0.00011953 | 0.079476 | -58.4656 | 62.1643 | -61.7111 | -61.6104 | 54.364 | 22.8424 | 7.8781 | 7.0129 | 62.2055 | -61.7065 | -0.27924 | -0.064087 | 2.9663 | -0.17853 | -7.8644 | -0.27466 | -0.022889 | 3.2455 | 69.31 | 68.4448 | 115.7959 | 123.5962 | 2.9663 | 123.6374 | 84.2743 | -0.27466 | 123.5962 | 2.9663 | 84.2743 | 115.7959 | 123.6374 | -123.9395 | -123.9349
3743.7188 | 123.7518 | -61.4319 | 62.1918 | -0.1844 | 0.016878 | 0.014695 | 0.013815 | 0.06153 | -0.00011953 | 0.07734 | -58.4335 | 62.2238 | -61.7065 | -61.615 | 54.3549 | 22.8378 | 7.8278 | 7.0084 | 62.2421 | -61.7203 | -0.27466 | 0.032044 | 2.9984 | -0.1831 | -7.8369 | -0.28839 | 0.050354 | 3.273 | 69.2596 | 68.4402 | 115.7867 | 123.6557 | 2.9984 | 123.674 | 84.2697 | -0.28839 | 123.6557 | 2.9984 | 84.2697 | 115.7867 | 123.674 | -123.8983 | -123.912
3744.7188 | 123.7976 | -61.4044 | 62.2009 | -0.27596 | 0.014956 | 0.012773 | 0.010611 | 0.058112 | 9.4068e-05 | 0.081613 | -58.3923 | 62.146 | -61.7065 | -61.5646 | 54.3823 | 22.8836 | 7.7591 | 7.0724 | 62.1964 | -61.6608 | -0.30212 | -0.054932 | 3.0121 | -0.16022 | -7.8186 | -0.25635 | -0.004578 | 3.3142 | 69.1635 | 68.4769 | 115.7867 | 123.5504 | 3.0121 | 123.6008 | 84.288 | -0.25635 | 123.5504 | 3.0121 | 84.288 | 115.7867 | 123.6008 | -123.9075 | -123.8617
3745.7188 | 123.7656 | -61.4319 | 62.2009 | -0.32936 | 0.014315 | 0.010423 | 0.0095424 | 0.060034 | 0.0026575 | 0.080758 | -58.4427 | 62.1597 | -61.7203 | -61.615 | 54.3594 | 22.7875 | 7.8323 | 7.0038 | 62.233 | -61.7111 | -0.28839 | -0.041199 | 2.9892 | -0.1831 | -7.8415 | -0.27924 | 0.032043 | 3.2776 | 69.2642 | 68.4357 | 115.7913 | 123.5916 | 2.9892 | 123.6649 | 84.2194 | -0.27924 | 123.5916 | 2.9892 | 84.2194 | 115.7913 | 123.6649 | -123.9212 | -123.912
3746.7188 | 123.7885 | -61.3861 | 62.2421 | -0.2607 | 0.01346 | 0.011918 | 0.008688 | 0.060462 | 0.0011621 | 0.079476 | -58.4152 | 62.1323 | -61.6745 | -61.5601 | 54.3503 | 22.7875 | 7.782 | 7.045 | 62.1964 | -61.6745 | -0.28839 | -0.10986 | 2.9709 | -0.17395 | -7.8918 | -0.28839 | -0.045776 | 3.2593 | 69.1681 | 68.4311 | 115.7364 | 123.5184 | 2.9709 | 123.5825 | 84.1736 | -0.28839 | 123.5184 | 2.9709 | 84.1736 | 115.7364 | 123.5825 | -123.9166 | -123.9166
3747.7188 | 123.8297 | -61.3998 | 62.1826 | -0.17677 | 0.014529 | 0.013627 | 0.010397 | 0.058753 | -0.00054693 | 0.079476 | -58.3923 | 62.1643 | -61.6928 | -61.5417 | 54.3732 | 22.9202 | 7.7362 | 7.0953 | 62.1735 | -61.6882 | -0.29297 | -0.01831 | 3.0075 | -0.14191 | -7.8094 | -0.28839 | -0.009155 | 3.3005 | 69.136 | 68.4952 | 115.773 | 123.5641 | 3.0075 | 123.5733 | 84.3201 | -0.28839 | 123.5641 | 3.0075 | 84.3201 | 115.773 | 123.5733 | -123.8754 | -123.8708
3748.7188 | 123.8525 | -61.3586 | 62.2101 | -0.19203 | 0.012606 | 0.010423 | 0.010611 | 0.058966 | -0.0011877 | 0.080544 | -58.3923 | 62.1231 | -61.6928 | -61.528 | 54.3594 | 22.9248 | 7.6996 | 7.1411 | 62.1597 | -61.6928 | -0.33417 | -0.086975 | 2.9663 | -0.16937 | -7.8506 | -0.33417 | -0.050354 | 3.3005 | 69.0582 | 68.4998 | 115.7181 | 123.4818 | 2.9663 | 123.5184 | 84.2834 | -0.33417 | 123.4818 | 2.9663 | 84.2834 | 115.7181 | 123.5184 | -123.9029 | -123.9029
3749.7188 | 123.8525 | -61.3815 | 62.2055 | 3.0581 | 0.013247 | 0.007432 | 0.0093288 | 0.059607 | -0.00097413 | 0.079904 | -58.3328 | 62.0956 | -61.6928 | -61.5005 | 54.4189 | 22.9202 | 7.6721 | 7.1411 | 62.1689 | -61.6699 | -0.31128 | -0.10986 | 3.0487 | -0.11902 | -7.7866 | -0.28839 | -0.036621 | 3.36 | 69.0537 | 68.5226 | 115.8005 | 123.4772 | 3.0487 | 123.5504 | 84.3018 | -0.28839 | 123.4772 | 3.0487 | 84.3018 | 115.8005 | 123.5504 | -123.8983 | -123.8754
3750.7188 | 123.8846 | -61.3632 | 62.1872 | -0.054703 | 0.012392 | 0.010423 | 0.010397 | 0.055548 | -0.0011877 | 0.080972 | -58.4564 | 62.0956 | -61.6928 | -61.5417 | 54.3503 | 22.8516 | 7.6675 | 7.1091 | 62.146 | -61.6974 | -0.32959 | -0.091553 | 2.9068 | -0.17853 | -7.8369 | -0.33417 | -0.041199 | 3.2364 | 69.0308 | 68.4723 | 115.7135 | 123.4589 | 2.9068 | 123.5092 | 84.2148 | -0.33417 | 123.4589 | 2.9068 | 84.2148 | 115.7135 | 123.5092 | -123.88 | -123.8846
3751.7188 | 123.8983 | -61.377 | 62.178 | -0.12337 | 0.011538 | 0.014482 | 0.0095424 | 0.057044 | -0.0011877 | 0.078408 | -58.3786 | 62.0956 | -61.6699 | -61.5143 | 54.3549 | 22.9843 | 7.6492 | 7.1365 | 62.1277 | -61.6516 | -0.29297 | -0.082398 | 2.9984 | -0.13733 | -7.8232 | -0.27466 | -0.050354 | 3.2913 | 69.0262 | 68.5135 | 115.7318 | 123.4726 | 2.9984 | 123.5046 | 84.3613 | -0.27466 | 123.4726 | 2.9984 | 84.3613 | 115.7318 | 123.5046 | -123.848 | -123.8297
3752.7188 | 123.9395 | -61.3861 | 62.1506 | -0.19966 | 0.015169 | 0.011918 | 0.0095424 | 0.057044 | -0.00097413 | 0.079476 | -58.3649 | 62.0956 | -61.6791 | -61.5051 | 54.2862 | 22.6959 | 8.2214 | 7.2235 | 62.2238 | -61.6104 | -0.29297 | -0.054932 | 3.0212 | -0.11902 | -7.8644 | -0.22431 | 0.073242 | 3.3142 | 69.6075 | 68.6096 | 115.6723 | 123.4818 | 3.0212 | 123.6099 | 84.082 | -0.22431 | 123.4818 | 3.0212 | 84.082 | 115.6723 | 123.6099 | -123.8297 | -123.761
3753.7188 | 123.761 | -61.409 | 62.2009 | -0.19966 | 0.015169 | 0.011704 | 0.016165 | 0.059394 | -0.0014013 | 0.078408 | -58.4473 | 62.2055 | -61.702 | -61.6058 | 54.1763 | 22.5494 | 7.8461 | 7.0175 | 62.1872 | -61.7157 | -0.29297 | 0.004577 | 2.9617 | -0.19684 | -8.0246 | -0.3067 | -0.013733 | 3.2547 | 69.2551 | 68.4265 | 115.5853 | 123.6145 | 2.9617 | 123.5962 | 83.9584 | -0.3067 | 123.6145 | 2.9617 | 83.9584 | 115.5853 | 123.5962 | -123.9029 | -123.9166
3754.7188 | 123.8617 | -61.3861 | 62.1826 | -0.077591 | 0.01346 | 0.014054 | 0.0078336 | 0.058539 | 0.00073487 | 0.080544 | -58.4152 | 62.1048 | -61.6974 | -61.5234 | 54.3503 | 22.8378 | 7.6447 | 7.132 | 62.1368 | -61.6653 | -0.31128 | -0.07782 | 2.9709 | -0.13733 | -7.8323 | -0.27924 | -0.045776 | 3.2822 | 69.0308 | 68.5181 | 115.7364 | 123.4909 | 2.9709 | 123.5229 | 84.2239 | -0.27924 | 123.4909 | 2.9709 | 84.2239 | 115.7364 | 123.5229 | -123.88 | -123.848
3755.7188 | 123.8709 | -61.377 | 62.1689 | -0.10048 | 0.01346 | 0.011277 | 0.010397 | 0.057685 | -0.00076053 | 0.079904 | -58.4473 | 62.1048 | -61.6928 | -61.5326 | 54.2953 | 22.7966 | 7.6675 | 7.1091 | 62.1277 | -61.6699 | -0.31586 | -0.064087 | 2.9297 | -0.15564 | -7.8735 | -0.29297 | -0.041198 | 3.2455 | 69.0445 | 68.486 | 115.6723 | 123.4818 | 2.9297 | 123.5046 | 84.1736 | -0.29297 | 123.4818 | 2.9297 | 84.1736 | 115.6723 | 123.5046 | -123.8617 | -123.8388
3756.7188 | 123.8068 | -61.3861 | 62.1826 | -0.016556 | 0.010256 | 0.01085 | 0.0080472 | 0.057898 | -0.00011953 | 0.080117 | -58.4656 | 62.0956 | -61.6974 | -61.5921 | 54.2725 | 22.8378 | 7.695 | 7.0587 | 62.1048 | -61.6837 | -0.31128 | -0.086975 | 2.9205 | -0.20599 | -7.9102 | -0.29755 | -0.07782 | 3.2318 | 69.0811 | 68.4448 | 115.6586 | 123.4818 | 2.9205 | 123.4909 | 84.2239 | -0.29755 | 123.4818 | 2.9205 | 84.2239 | 115.6586 | 123.4909 | -123.88 | -123.8663
3757.7188 | 123.7976 | -61.3907 | 62.1597 | 0.18944 | 0.013033 | 0.0080728 | 0.01232 | 0.058112 | 0.00073487 | 0.07969 | -58.4747 | 62.0911 | -61.702 | -61.5829 | 54.2633 | 22.8836 | 7.7042 | 7.0908 | 62.1277 | -61.6882 | -0.31128 | -0.068665 | 2.916 | -0.19226 | -7.8964 | -0.29755 | -0.032043 | 3.2272 | 69.0948 | 68.4814 | 115.654 | 123.4818 | 2.916 | 123.5184 | 84.2743 | -0.29755 | 123.4818 | 2.916 | 84.2743 | 115.654 | 123.5184 | -123.8617 | -123.848
3758.7188 | 123.8342 | -61.3953 | 62.1643 | 0.029221 | 0.016665 | 0.012132 | 0.0084744 | 0.05918 | -0.00076053 | 0.080117 | -58.4473 | 62.0956 | -61.6974 | -61.5784 | 54.245 | 22.8378 | 7.8918 | 7.2189 | 62.1826 | -61.6562 | -0.30212 | -0.068665 | 2.948 | -0.18311 | -7.9193 | -0.26093 | 0.01831 | 3.2501 | 69.2871 | 68.6142 | 115.6403 | 123.4909 | 2.948 | 123.5779 | 84.2331 | -0.26093 | 123.4909 | 2.948 | 84.2331 | 115.6403 | 123.5779 | -123.8617 | -123.8205
3759.7188 | 123.8388 | -61.377 | 62.178 | -0.19966 | 0.014529 | 0.011918 | 0.010397 | 0.060675 | 0.0015893 | 0.078408 | -58.461 | 62.1094 | -61.6974 | -61.5738 | 54.2862 | 22.8699 | 7.7133 | 7.0908 | 62.1277 | -61.6791 | -0.32043 | -0.068665 | 2.916 | -0.19684 | -7.8918 | -0.30212 | -0.050354 | 3.2364 | 69.0903 | 68.4677 | 115.6631 | 123.4863 | 2.916 | 123.5046 | 84.2468 | -0.30212 | 123.4863 | 2.916 | 84.2468 | 115.6631 | 123.5046 | -123.8754 | -123.8571
3760.7188 | 123.8113 | -61.3815 | 62.1643 | -0.039444 | 0.015169 | 0.011277 | 0.0091152 | 0.055121 | 0.0011621 | 0.081185 | -58.4839 | 62.1094 | -61.7249 | -61.6653 | 54.2908 | 22.9385 | 7.6584 | 7.1045 | 62.1323 | -61.6791 | -0.34332 | -0.054932 | 2.8976 | -0.28381 | -7.8735 | -0.29755 | -0.032044 | 3.241 | 69.0399 | 68.486 | 115.6723 | 123.4909 | 2.8976 | 123.5138 | 84.3201 | -0.29755 | 123.4909 | 2.8976 | 84.3201 | 115.6723 | 123.5138 | -123.8892 | -123.8434
3761.7188 | 123.8342 | -61.4044 | 62.1918 | 0.013962 | 0.015169 | 0.0099954 | 0.010397 | 0.058753 | 9.4068e-05 | 0.079263 | -58.461 | 62.1094 | -61.7294 | -61.5921 | 54.2267 | 22.8973 | 7.6584 | 7.077 | 62.1323 | -61.6745 | -0.32501 | -0.082397 | 2.9434 | -0.18768 | -7.9651 | -0.27008 | -0.059509 | 3.2684 | 69.0628 | 68.4814 | 115.6311 | 123.5138 | 2.9434 | 123.5367 | 84.3018 | -0.27008 | 123.5138 | 2.9434 | 84.3018 | 115.6311 | 123.5367 | -123.9212 | -123.8663
3762.7188 | 123.8434 | -61.3907 | 62.178 | 0.0063326 | 0.014529 | 0.012986 | 0.012106 | 0.058966 | 0.0022303 | 0.07969 | -58.4747 | 62.0865 | -61.702 | -61.5875 | 54.2908 | 22.8561 | 7.6813 | 7.0862 | 62.0956 | -61.6791 | -0.31128 | -0.091553 | 2.916 | -0.19684 | -7.8873 | -0.28839 | -0.082398 | 3.2272 | 69.072 | 68.4769 | 115.6815 | 123.4772 | 2.916 | 123.4863 | 84.2468 | -0.28839 | 123.4772 | 2.916 | 84.2468 | 115.6815 | 123.4863 | -123.88 | -123.8571
3763.7188 | 123.7152 | -61.441 | 62.2009 | -0.2607 | 0.017306 | 0.013413 | 0.011465 | 0.05683 | -0.00011953 | 0.079049 | -58.4656 | 62.2147 | -61.7249 | -61.7065 | 54.2633 | 22.8973 | 7.8094 | 7.0908 | 62.178 | -61.7432 | -0.28381 | 0.013733 | 2.9755 | -0.2655 | -7.9376 | -0.30212 | -0.022888 | 3.2593 | 69.2505 | 68.5318 | 115.7043 | 123.6557 | 2.9755 | 123.6191 | 84.3384 | -0.30212 | 123.6557 | 2.9755 | 84.3384 | 115.7043 | 123.6191 | -123.9258 | -123.9441
3764.7188 | 123.8617 | -61.3953 | 62.1368 | 0.54802 | 0.014529 | 0.012559 | 0.0099698 | 0.060462 | -0.0011877 | 0.078835 | -58.3694 | 62.1323 | -61.7065 | -61.5555 | 54.4052 | 22.9889 | 7.576 | 7.1228 | 62.114 | -61.6974 | -0.31128 | -0.004578 | 3.0258 | -0.16022 | -7.7316 | -0.30212 | -0.022888 | 3.3371 | 68.9713 | 68.5181 | 115.8005 | 123.5275 | 3.0258 | 123.5092 | 84.3842 | -0.30212 | 123.5275 | 3.0258 | 84.3842 | 115.8005 | 123.5092 | -123.8434 | -123.8342
3765.7188 | 123.8205 | -61.3953 | 62.1414 | 0.1284 | 0.016024 | 0.014482 | 0.0078336 | 0.059821 | -0.00054693 | 0.080758 | -58.4518 | 62.0865 | -61.7386 | -61.6013 | 54.332 | 22.879 | 7.6675 | 7.1136 | 62.146 | -61.6791 | -0.34332 | -0.054931 | 2.9434 | -0.20599 | -7.8094 | -0.28381 | 0.004578 | 3.2867 | 69.0628 | 68.5089 | 115.7272 | 123.4818 | 2.9434 | 123.5413 | 84.2743 | -0.28381 | 123.4818 | 2.9434 | 84.2743 | 115.7272 | 123.5413 | -123.88 | -123.8205
3766.7188 | 123.8113 | -61.3861 | 62.1414 | 0.18181 | 0.013888 | 0.014482 | 0.011465 | 0.05918 | 0.00073487 | 0.080758 | -58.4564 | 62.0911 | -61.7065 | -61.5829 | 54.2542 | 22.9111 | 7.663 | 7.0862 | 62.1048 | -61.702 | -0.32044 | -0.050354 | 2.9297 | -0.19684 | -7.8873 | -0.31586 | -0.036621 | 3.2501 | 69.0491 | 68.4723 | 115.6403 | 123.4772 | 2.9297 | 123.4909 | 84.2972 | -0.31586 | 123.4772 | 2.9297 | 84.2972 | 115.6403 | 123.4909 | -123.848 | -123.8434
3767.7188 | 123.8388 | -61.3953 | 62.1506 | 0.17418 | 0.013888 | 0.0072184 | 0.011038 | 0.058966 | 0.0039393 | 0.080972 | -58.4244 | 62.0865 | -61.702 | -61.5601 | 54.2862 | 22.8745 | 7.6675 | 7.1365 | 62.1048 | -61.6974 | -0.3067 | -0.064087 | 2.9709 | -0.1648 | -7.8644 | -0.30212 | -0.045777 | 3.2776 | 69.0628 | 68.5318 | 115.6815 | 123.4818 | 2.9709 | 123.5001 | 84.2697 | -0.30212 | 123.4818 | 2.9709 | 84.2697 | 115.6815 | 123.5001 | -123.8525 | -123.848
3768.7188 | 123.8342 | -61.4136 | 62.1735 | 0.074997 | 0.013247 | 0.011491 | 0.0084744 | 0.058325 | 0.00030767 | 0.080331 | -58.3969 | 62.1506 | -61.6653 | -61.5646 | 54.2999 | 22.8104 | 7.7362 | 7.1045 | 62.1277 | -61.6653 | -0.25177 | -0.022888 | 3.0167 | -0.15106 | -7.8735 | -0.25177 | -0.045776 | 3.2684 | 69.1498 | 68.5181 | 115.7135 | 123.5641 | 3.0167 | 123.5413 | 84.2239 | -0.25177 | 123.5641 | 3.0167 | 84.2239 | 115.7135 | 123.5413 | -123.8388 | -123.8388
3769.7344 | 123.7473 | -61.4182 | 62.2421 | -0.25307 | 0.016665 | 0.011918 | 0.011892 | 0.058539 | 0.00094847 | 0.080117 | -58.4564 | 62.1689 | -61.7065 | -61.5829 | 54.2633 | 22.934 | 7.8918 | 7.1136 | 62.1735 | -61.7065 | -0.28839 | -0.073242 | 2.9617 | -0.16479 | -7.9788 | -0.28839 | -0.068664 | 3.2501 | 69.31 | 68.5318 | 115.6815 | 123.587 | 2.9617 | 123.5916 | 84.3521 | -0.28839 | 123.587 | 2.9617 | 84.3521 | 115.6815 | 123.5916 | -123.9487 | -123.9487
3770.7188 | 123.8663 | -61.3998 | 62.1368 | 0.19707 | 0.015597 | 0.014054 | 0.015524 | 0.061316 | -0.0018285 | 0.080331 | -58.3969 | 62.1277 | -61.7386 | -61.5555 | 54.2953 | 22.9477 | 7.6675 | 7.1411 | 62.1048 | -61.6745 | -0.33874 | -0.009155 | 3.0029 | -0.15564 | -7.8415 | -0.27466 | -0.032044 | 3.3417 | 69.0674 | 68.541 | 115.6952 | 123.5275 | 3.0029 | 123.5046 | 84.3475 | -0.27466 | 123.5275 | 3.0029 | 84.3475 | 115.6952 | 123.5046 | -123.8754 | -123.8113
3771.7188 | 123.88 | -61.3907 | 62.1231 | 0.17418 | 0.019228 | 0.017045 | 0.013388 | 0.063025 | -0.0014013 | 0.081399 | -58.429 | 62.1231 | -61.7477 | -61.5738 | 54.2953 | 22.9568 | 7.7042 | 7.1365 | 62.114 | -61.7157 | -0.35706 | 0 | 2.9617 | -0.18311 | -7.8278 | -0.32501 | -0.009155 | 3.3188 | 69.0948 | 68.5272 | 115.686 | 123.5138 | 2.9617 | 123.5046 | 84.3475 | -0.32501 | 123.5138 | 2.9617 | 84.3475 | 115.686 | 123.5046 | -123.8709 | -123.8388
3772.7188 | 123.8571 | -61.4136 | 62.0819 | 0.21233 | 0.015597 | 0.015763 | 0.01531 | 0.061103 | -0.0018285 | 0.083962 | -58.3786 | 62.1414 | -61.7203 | -61.5326 | 54.3228 | 22.9935 | 7.6263 | 7.1503 | 62.0911 | -61.6837 | -0.3067 | 0.059509 | 3.035 | -0.11902 | -7.7591 | -0.27008 | 0.009155 | 3.3417 | 69.0399 | 68.5638 | 115.7364 | 123.555 | 3.035 | 123.5046 | 84.407 | -0.27008 | 123.555 | 3.035 | 84.407 | 115.7364 | 123.5046 | -123.8022 | -123.7656
3773.7188 | 123.8571 | -61.3953 | 62.1506 | 0.029221 | 0.011751 | 0.014054 | 0.0089016 | 0.058966 | 9.4068e-05 | 0.081185 | -58.4839 | 62.0911 | -61.7432 | -61.5829 | 54.3503 | 23.053 | 7.7637 | 7.1823 | 62.1323 | -61.6837 | -0.3479 | -0.05951 | 2.9114 | -0.18768 | -7.8003 | -0.28839 | -0.018311 | 3.2593 | 69.1589 | 68.5776 | 115.7455 | 123.4863 | 2.9114 | 123.5275 | 84.4482 | -0.28839 | 123.4863 | 2.9114 | 84.4482 | 115.7455 | 123.5275 | -123.8937 | -123.8342
3774.7344 | 123.7747 | -61.4182 | 62.1918 | -0.29121 | 0.016238 | 0.014695 | 0.01232 | 0.058112 | 9.4068e-05 | 0.07969 | -58.4152 | 62.1643 | -61.6974 | -61.5738 | 54.3503 | 23.0484 | 7.8873 | 7.1411 | 62.1597 | -61.6974 | -0.27924 | -0.027465 | 3.0029 | -0.15564 | -7.8415 | -0.27924 | -0.032043 | 3.2822 | 69.3054 | 68.5593 | 115.7684 | 123.5825 | 3.0029 | 123.5779 | 84.4666 | -0.27924 | 123.5825 | 3.0029 | 84.4666 | 115.7684 | 123.5779 | -123.8892 | -123.8892
3775.7188 | 123.8388 | -61.4044 | 62.1323 | 0.24284 | 0.016238 | 0.013627 | 0.016165 | 0.059607 | -0.00097413 | 0.080117 | -58.3923 | 62.0956 | -61.7157 | -61.5875 | 54.4098 | 23.2361 | 7.6309 | 7.1503 | 62.0728 | -61.6928 | -0.31128 | -0.036621 | 3.0121 | -0.18311 | -7.7225 | -0.28839 | -0.059509 | 3.3234 | 69.0353 | 68.5547 | 115.8142 | 123.5001 | 3.0121 | 123.4772 | 84.6405 | -0.28839 | 123.5001 | 3.0121 | 84.6405 | 115.8142 | 123.4772 | -123.848 | -123.8251
3776.7188 | 123.88 | -61.3998 | 62.1368 | 0.18181 | 0.016024 | 0.018327 | 0.015097 | 0.059821 | -0.00011953 | 0.078622 | -58.3832 | 62.1231 | -61.7065 | -61.528 | 54.2496 | 22.8745 | 7.9056 | 7.3059 | 62.0728 | -61.6928 | -0.3067 | -0.013733 | 3.0167 | -0.12817 | -7.8873 | -0.29297 | -0.064087 | 3.3234 | 69.3054 | 68.7057 | 115.6494 | 123.5229 | 3.0167 | 123.4726 | 84.2743 | -0.29297 | 123.5229 | 3.0167 | 84.2743 | 115.6494 | 123.4726 | -123.8434 | -123.8297
3777.7188 | 123.8113 | -61.3953 | 62.1414 | 0.18181 | 0.017306 | 0.016191 | 0.016165 | 0.061957 | 0.00052127 | 0.078835 | -58.4564 | 62.1552 | -61.7203 | -61.5921 | 54.2358 | 23.0072 | 7.782 | 7.0724 | 62.1094 | -61.7157 | -0.32501 | 0.013733 | 2.9388 | -0.19684 | -7.9056 | -0.32043 | -0.032043 | 3.2639 | 69.1772 | 68.4677 | 115.6311 | 123.5504 | 2.9388 | 123.5046 | 84.4025 | -0.32043 | 123.5504 | 2.9388 | 84.4025 | 115.6311 | 123.5046 | -123.8617 | -123.8571
3778.7188 | 123.8571 | -61.3907 | 62.1277 | 0.097885 | 0.014315 | 0.016618 | 0.014669 | 0.061103 | 9.4068e-05 | 0.08204 | -58.4061 | 62.114 | -61.7111 | -61.5555 | 54.2862 | 23.0301 | 7.7454 | 7.164 | 62.1094 | -61.7111 | -0.32043 | -0.013733 | 2.9846 | -0.16479 | -7.8415 | -0.32043 | -0.018311 | 3.3051 | 69.136 | 68.5547 | 115.6769 | 123.5046 | 2.9846 | 123.5001 | 84.4208 | -0.32043 | 123.5046 | 2.9846 | 84.4208 | 115.6769 | 123.5001 | -123.8388 | -123.8388
3779.7188 | 123.8617 | -61.3907 | 62.146 | 0.052109 | 0.013247 | 0.01085 | 0.0078336 | 0.060248 | -0.00076053 | 0.080331 | -58.493 | 62.1002 | -61.7203 | -61.5829 | 54.2999 | 22.998 | 7.8003 | 7.1411 | 62.1323 | -61.6928 | -0.32959 | -0.045776 | 2.8976 | -0.19226 | -7.8461 | -0.30212 | -0.013733 | 3.2272 | 69.191 | 68.5318 | 115.6906 | 123.4909 | 2.8976 | 123.5229 | 84.3887 | -0.30212 | 123.4909 | 2.8976 | 84.3887 | 115.6906 | 123.5229 | -123.8663 | -123.8388
3780.7188 | 123.8617 | -61.4182 | 62.1185 | 0.18944 | 0.015169 | 0.015122 | 0.014029 | 0.062384 | -0.0011877 | 0.07969 | -58.5617 | 62.0865 | -61.702 | -61.5646 | 54.3411 | 23.1033 | 7.7179 | 7.1594 | 62.0865 | -61.7065 | -0.28381 | -0.032043 | 2.8564 | -0.14648 | -7.7774 | -0.28839 | -0.032043 | 3.1403 | 69.136 | 68.5776 | 115.7593 | 123.5046 | 2.8564 | 123.5046 | 84.5215 | -0.28839 | 123.5046 | 2.8564 | 84.5215 | 115.7593 | 123.5046 | -123.8205 | -123.8251
3781.7188 | 123.8754 | -61.3998 | 62.1185 | 0.15892 | 0.015169 | 0.014909 | 0.014883 | 0.06388 | -0.00076053 | 0.080117 | -58.3969 | 62.0819 | -61.6882 | -61.377 | 54.3915 | 23.0347 | 7.6904 | 7.2052 | 62.114 | -61.6882 | -0.28839 | -0.036621 | 3.0029 | 0.022888 | -7.7271 | -0.28839 | -0.004577 | 3.2913 | 69.0903 | 68.605 | 115.7913 | 123.4818 | 3.0029 | 123.5138 | 84.4345 | -0.28839 | 123.4818 | 3.0029 | 84.4345 | 115.7913 | 123.5138 | -123.8068 | -123.8068
3782.7188 | 123.8434 | -61.3861 | 62.1323 | 0.12077 | 0.017306 | 0.014695 | 0.01531 | 0.059607 | 0.00030767 | 0.078835 | -58.3832 | 62.1048 | -61.6974 | -61.5555 | 54.332 | 23.204 | 7.3334 | 7.0724 | 62.0819 | -61.7249 | -0.31128 | -0.027466 | 3.0029 | -0.16937 | -7.8003 | -0.33875 | -0.050354 | 3.3142 | 68.7195 | 68.4586 | 115.7181 | 123.4909 | 3.0029 | 123.468 | 84.5901 | -0.33875 | 123.4909 | 3.0029 | 84.5901 | 115.7181 | 123.468 | -123.8297 | -123.8571
3783.7188 | 123.8388 | -61.3998 | 62.1414 | 0.074997 | 0.01346 | 0.0132 | 0.0093288 | 0.057685 | -0.00033333 | 0.080117 | -58.4518 | 62.0728 | -61.7203 | -61.6058 | 54.3503 | 23.0759 | 7.6813 | 7.0816 | 62.1368 | -61.6882 | -0.32043 | -0.068664 | 2.948 | -0.20599 | -7.7911 | -0.28839 | -0.004577 | 3.2684 | 69.0811 | 68.4814 | 115.7501 | 123.4726 | 2.948 | 123.5367 | 84.4757 | -0.28839 | 123.4726 | 2.948 | 84.4757 | 115.7501 | 123.5367 | -123.8617 | -123.8297
3784.7188 | 123.8434 | -61.4273 | 62.1414 | 0.15129 | 0.014956 | 0.014695 | 0.011038 | 0.059607 | -0.00011953 | 0.07969 | -58.4335 | 62.114 | -61.6928 | -61.6058 | 54.2633 | 23.0438 | 7.7454 | 7.1869 | 62.1048 | -61.7065 | -0.2655 | -0.027465 | 2.9938 | -0.17853 | -7.8781 | -0.27924 | -0.036621 | 3.2593 | 69.1727 | 68.6142 | 115.6906 | 123.5413 | 2.9938 | 123.5321 | 84.4711 | -0.27924 | 123.5413 | 2.9938 | 84.4711 | 115.6906 | 123.5321 | -123.8342 | -123.848
3785.7188 | 123.7976 | -61.441 | 62.1735 | 0.12077 | 0.017306 | 0.012132 | 0.016378 | 0.059821 | -0.0016149 | 0.080758 | -58.4747 | 62.1872 | -61.7249 | -61.6333 | 54.2313 | 22.9706 | 7.7774 | 7.0679 | 62.1277 | -61.7111 | -0.28381 | 0.013733 | 2.9663 | -0.19226 | -7.9422 | -0.27008 | -0.045776 | 3.2501 | 69.2184 | 68.5089 | 115.6723 | 123.6282 | 2.9663 | 123.5687 | 84.4116 | -0.27008 | 123.6282 | 2.9663 | 84.4116 | 115.6723 | 123.5687 | -123.8983 | -123.8846
3786.7188 | 123.8754 | -61.3861 | 62.1368 | -0.82527 | 0.016024 | 0.012132 | 0.012533 | 0.061743 | 0.0011621 | 0.082253 | -58.4702 | 62.114 | -61.702 | -61.5784 | 54.3411 | 23.0759 | 7.6401 | 7.1503 | 62.1048 | -61.7111 | -0.31586 | -0.022888 | 2.916 | -0.19226 | -7.7957 | -0.32501 | -0.032044 | 3.2318 | 69.0262 | 68.5364 | 115.7272 | 123.5001 | 2.916 | 123.4909 | 84.462 | -0.32501 | 123.5001 | 2.916 | 84.462 | 115.7272 | 123.4909 | -123.8388 | -123.848
3787.7188 | 123.8709 | -61.3907 | 62.1185 | 1.9137 | 0.013033 | 0.01555 | 0.013388 | 0.059821 | 0.0018031 | 0.079263 | -58.3054 | 62.1048 | -61.6974 | -61.5189 | 54.4281 | 23.0667 | 7.6309 | 7.1548 | 62.1414 | -61.6882 | -0.3067 | -0.013733 | 3.0853 | -0.12817 | -7.6904 | -0.29755 | 0.022888 | 3.392 | 69.0216 | 68.5455 | 115.8188 | 123.4955 | 3.0853 | 123.5321 | 84.4574 | -0.29755 | 123.4955 | 3.0853 | 84.4574 | 115.8188 | 123.5321 | -123.8159 | -123.8068
3788.7188 | 123.88 | -61.409 | 62.146 | -0.054703 | 0.015169 | 0.017472 | 0.0082608 | 0.05918 | 0.00073487 | 0.082253 | -58.4518 | 62.1002 | -61.7249 | -61.5555 | 54.3549 | 23.2132 | 7.7408 | 7.196 | 62.1323 | -61.6562 | -0.31586 | -0.045776 | 2.9572 | -0.14648 | -7.7911 | -0.24719 | -0.013733 | 3.273 | 69.1498 | 68.605 | 115.7639 | 123.5092 | 2.9572 | 123.5413 | 84.6222 | -0.24719 | 123.5092 | 2.9572 | 84.6222 | 115.7639 | 123.5413 | -123.8708 | -123.8022
3789.7188 | 123.8663 | -61.3907 | 62.1323 | 0.21996 | 0.016451 | 0.015122 | 0.014029 | 0.058539 | -0.00054693 | 0.080117 | -58.3878 | 62.1094 | -61.6974 | -61.5601 | 54.3686 | 23.0942 | 7.6447 | 7.1732 | 62.0865 | -61.6928 | -0.3067 | -0.022888 | 3.0029 | -0.16937 | -7.7637 | -0.30212 | -0.045776 | 3.3096 | 69.0353 | 68.5638 | 115.7593 | 123.5001 | 3.0029 | 123.4772 | 84.4849 | -0.30212 | 123.5001 | 3.0029 | 84.4849 | 115.7593 | 123.4772 | -123.8297 | -123.8251
3790.7188 | 123.8571 | -61.3586 | 62.1552 | 0.19707 | 0.015383 | 0.015336 | 0.012747 | 0.062598 | 0.0045801 | 0.079049 | -58.3832 | 62.0911 | -61.7523 | -61.5417 | 54.5105 | 23.1491 | 7.6218 | 7.2052 | 62.1094 | -61.6974 | -0.39368 | -0.064087 | 2.9755 | -0.1831 | -7.6447 | -0.33874 | -0.045776 | 3.3691 | 68.9804 | 68.5638 | 115.8691 | 123.4497 | 2.9755 | 123.468 | 84.5078 | -0.33874 | 123.4497 | 2.9755 | 84.5078 | 115.8691 | 123.468 | -123.9075 | -123.8525
3791.7188 | 123.8434 | -61.4136 | 62.1414 | 0.21996 | 0.017519 | 0.014695 | 0.018087 | 0.061957 | 0.00073487 | 0.079263 | -58.429 | 62.1506 | -61.734 | -61.5829 | 54.3045 | 22.9431 | 7.6721 | 7.1228 | 62.1277 | -61.7065 | -0.32044 | 0.009156 | 2.9846 | -0.16937 | -7.8369 | -0.29297 | -0.013732 | 3.3051 | 69.0857 | 68.5364 | 115.7181 | 123.5641 | 2.9846 | 123.5413 | 84.3567 | -0.29297 | 123.5641 | 2.9846 | 84.3567 | 115.7181 | 123.5413 | -123.8754 | -123.848
3792.7188 | 123.8159 | -61.4136 | 62.1231 | 0.21233 | 0.016665 | 0.014482 | 0.017019 | 0.063666 | 0.00030767 | 0.079263 | -58.4518 | 62.1414 | -61.7523 | -61.5921 | 54.3137 | 23.0576 | 7.7179 | 7.1045 | 62.1368 | -61.7203 | -0.33875 | 0.01831 | 2.9617 | -0.17853 | -7.8094 | -0.3067 | 0.013733 | 3.3005 | 69.1315 | 68.5181 | 115.7272 | 123.555 | 2.9617 | 123.5504 | 84.4711 | -0.3067 | 123.555 | 2.9617 | 84.4711 | 115.7272 | 123.5504 | -123.8754 | -123.8434
3793.7188 | 123.8388 | -61.3815 | 62.1597 | -0.024185 | 0.014956 | 0.0132 | 0.0074062 | 0.062171 | 9.4068e-05 | 0.080331 | -58.4518 | 62.1094 | -61.7157 | -61.5646 | 54.2908 | 23.0164 | 7.7454 | 7.1869 | 62.1277 | -61.6745 | -0.33417 | -0.050354 | 2.9297 | -0.1831 | -7.869 | -0.29297 | -0.032043 | 3.2639 | 69.1269 | 68.5684 | 115.6723 | 123.4909 | 2.9297 | 123.5092 | 84.3979 | -0.29297 | 123.4909 | 2.9297 | 84.3979 | 115.6723 | 123.5092 | -123.8754 | -123.8342
3794.7188 | 123.8663 | -61.3953 | 62.1368 | 0.15129 | 0.014956 | 0.01555 | 0.013174 | 0.060889 | -0.0014013 | 0.080758 | -58.3878 | 62.0728 | -61.6974 | -61.5555 | 54.3274 | 23.0942 | 7.6721 | 7.164 | 62.1277 | -61.6837 | -0.30212 | -0.064087 | 3.0075 | -0.16022 | -7.8094 | -0.28839 | -0.009155 | 3.3096 | 69.0674 | 68.5593 | 115.7227 | 123.468 | 3.0075 | 123.5229 | 84.4894 | -0.28839 | 123.468 | 3.0075 | 84.4894 | 115.7227 | 123.5229 | -123.8342 | -123.8205
3795.7188 | 123.8663 | -61.3998 | 62.1826 | 0.074997 | 0.016665 | 0.016831 | 0.012533 | 0.061743 | -0.0016149 | 0.081185 | -58.3694 | 62.0773 | -61.7157 | -61.528 | 54.2999 | 22.9889 | 7.6721 | 7.1732 | 62.1231 | -61.6791 | -0.31586 | -0.10529 | 3.0304 | -0.12817 | -7.8827 | -0.27924 | -0.059509 | 3.3463 | 69.072 | 68.573 | 115.6998 | 123.4772 | 3.0304 | 123.5229 | 84.3887 | -0.27924 | 123.4772 | 3.0304 | 84.3887 | 115.6998 | 123.5229 | -123.8983 | -123.8617
3796.7188 | 123.8388 | -61.3953 | 62.114 | 0.28099 | 0.015597 | 0.015122 | 0.014242 | 0.060034 | -0.0020421 | 0.081826 | -58.3832 | 62.1002 | -61.7249 | -61.5463 | 54.2587 | 22.9935 | 7.6996 | 7.2418 | 62.1277 | -61.702 | -0.32959 | -0.013733 | 3.0121 | -0.15106 | -7.8552 | -0.3067 | 0.013733 | 3.3417 | 69.0948 | 68.6371 | 115.654 | 123.4955 | 3.0121 | 123.5229 | 84.3887 | -0.3067 | 123.4955 | 3.0121 | 84.3887 | 115.654 | 123.5229 | -123.8388 | -123.8159
3797.7188 | 123.8846 | -61.409 | 62.1231 | 0.31914 | 0.014315 | 0.015763 | 0.015524 | 0.060462 | -0.0014013 | 0.080972 | -58.4061 | 62.0865 | -61.6928 | -61.5417 | 54.3182 | 23.0209 | 7.663 | 7.2006 | 62.114 | -61.7065 | -0.28381 | -0.036621 | 3.0029 | -0.13275 | -7.8049 | -0.29755 | -0.009155 | 3.2867 | 69.072 | 68.6096 | 115.7272 | 123.4955 | 3.0029 | 123.523 | 84.4299 | -0.29755 | 123.4955 | 3.0029 | 84.4299 | 115.7272 | 123.523 | -123.8159 | -123.8297
3798.7188 | 123.7793 | -61.4182 | 62.1826 | -0.26833 | 0.013033 | 0.0089274 | 0.01232 | 0.060675 | -0.00011953 | 0.081399 | -58.4106 | 62.1323 | -61.7111 | -61.5646 | 54.2633 | 23.0347 | 7.9193 | 7.2098 | 62.1643 | -61.6653 | -0.29297 | -0.050354 | 3.0075 | -0.14648 | -7.9193 | -0.24719 | -0.01831 | 3.3005 | 69.3375 | 68.6279 | 115.6815 | 123.5504 | 3.0075 | 123.5825 | 84.4528 | -0.24719 | 123.5504 | 3.0075 | 84.4528 | 115.6815 | 123.5825 | -123.8937 | -123.848
3799.7188 | 123.848 | -61.4044 | 62.1643 | 0.24284 | 0.014101 | 0.011277 | 0.016378 | 0.061957 | -0.0018285 | 0.079049 | -58.3969 | 62.1231 | -61.7203 | -61.5601 | 54.2953 | 23.0759 | 7.6675 | 7.196 | 62.1094 | -61.7111 | -0.31586 | -0.041199 | 3.0075 | -0.15564 | -7.869 | -0.3067 | -0.054932 | 3.3234 | 69.072 | 68.6005 | 115.6998 | 123.5275 | 3.0075 | 123.5138 | 84.4803 | -0.3067 | 123.5275 | 3.0075 | 84.4803 | 115.6998 | 123.5138 | -123.8846 | -123.8754
3800.7188 | 123.8297 | -61.4227 | 62.178 | 0.12077 | 0.017733 | 0.014268 | 0.0095424 | 0.058753 | 0.0011621 | 0.081399 | -58.429 | 62.0911 | -61.702 | -61.5875 | 54.332 | 23.0576 | 7.7454 | 7.1732 | 62.1048 | -61.7065 | -0.27924 | -0.086976 | 2.9938 | -0.1648 | -7.8461 | -0.28381 | -0.073243 | 3.273 | 69.1681 | 68.5959 | 115.7547 | 123.5138 | 2.9938 | 123.5275 | 84.4803 | -0.28381 | 123.5138 | 2.9938 | 84.4803 | 115.7547 | 123.5275 | -123.88 | -123.8846
3801.7188 | 123.8068 | -61.4182 | 62.1506 | 0.074997 | 0.013674 | 0.012345 | 0.013815 | 0.059607 | -0.00097413 | 0.077981 | -58.4473 | 62.0911 | -61.702 | -61.5829 | 54.3411 | 23.085 | 7.7591 | 7.251 | 62.1094 | -61.7203 | -0.28381 | -0.05951 | 2.9709 | -0.16479 | -7.8094 | -0.30212 | -0.041199 | 3.2547 | 69.1772 | 68.6691 | 115.7593 | 123.5092 | 2.9709 | 123.5275 | 84.5032 | -0.30212 | 123.5092 | 2.9709 | 84.5032 | 115.7593 | 123.5275 | -123.8525 | -123.8708
3802.7188 | 123.8251 | -61.4044 | 62.1689 | 0.18181 | 0.013674 | 0.012773 | 0.010824 | 0.058539 | 0.00030767 | 0.080331 | -58.4381 | 62.0728 | -61.7157 | -61.5921 | 54.2816 | 22.9797 | 7.7408 | 7.2144 | 62.114 | -61.6791 | -0.31128 | -0.09613 | 2.9663 | -0.18768 | -7.8873 | -0.27466 | -0.054931 | 3.2776 | 69.1452 | 68.6188 | 115.686 | 123.4772 | 2.9663 | 123.5184 | 84.3842 | -0.27466 | 123.4772 | 2.9663 | 84.3842 | 115.686 | 123.5184 | -123.8846 | -123.848
3803.7188 | 123.7518 | -61.4273 | 62.1918 | -0.19203 | 0.014101 | 0.01085 | 0.015097 | 0.058112 | -0.0016149 | 0.079476 | -58.4747 | 62.1597 | -61.7294 | -61.6241 | 54.4235 | 23.2956 | 7.7866 | 7.0038 | 62.2009 | -61.7203 | -0.30212 | -0.032043 | 2.9526 | -0.19684 | -7.7682 | -0.29297 | 0.009156 | 3.2547 | 69.2139 | 68.4311 | 115.8508 | 123.587 | 2.9526 | 123.6282 | 84.7229 | -0.29297 | 123.587 | 2.9526 | 84.7229 | 115.8508 | 123.6282 | -123.9212 | -123.912
3804.7188 | 123.8251 | -61.4136 | 62.1323 | 0.18944 | 0.013674 | 0.014909 | 0.012106 | 0.060675 | 0.0013757 | 0.082467 | -58.4381 | 62.0773 | -61.7203 | -61.5967 | 54.2999 | 23.0072 | 7.7179 | 7.164 | 62.1048 | -61.6745 | -0.3067 | -0.054931 | 2.9755 | -0.18311 | -7.8323 | -0.26093 | -0.027466 | 3.2822 | 69.1315 | 68.5776 | 115.7135 | 123.4909 | 2.9755 | 123.5184 | 84.4208 | -0.26093 | 123.4909 | 2.9755 | 84.4208 | 115.7135 | 123.5184 | -123.8525 | -123.8068
3805.7188 | 123.8709 | -61.4044 | 62.1323 | 0.15129 | 0.013888 | 0.012986 | 0.015951 | 0.060034 | -0.00033333 | 0.082253 | -58.4152 | 62.0865 | -61.7065 | -61.5646 | 54.3274 | 23.0804 | 7.6767 | 7.2098 | 62.0865 | -61.6974 | -0.30212 | -0.045776 | 2.9892 | -0.16022 | -7.8049 | -0.29297 | -0.045776 | 3.2913 | 69.0811 | 68.6142 | 115.7318 | 123.4909 | 2.9892 | 123.4909 | 84.4849 | -0.29297 | 123.4909 | 2.9892 | 84.4849 | 115.7318 | 123.4909 | -123.8388 | -123.8297
3806.7188 | 123.8571 | -61.4227 | 62.1277 | 0.14366 | 0.014742 | 0.012773 | 0.013601 | 0.062171 | 0.00052127 | 0.079904 | -58.4061 | 62.0728 | -61.6791 | -61.5646 | 54.3457 | 23.0621 | 7.6584 | 7.2418 | 62.1002 | -61.6791 | -0.25635 | -0.054932 | 3.0167 | -0.14191 | -7.782 | -0.25635 | -0.027466 | 3.273 | 69.0811 | 68.6645 | 115.7684 | 123.4955 | 3.0167 | 123.5229 | 84.4849 | -0.25635 | 123.4955 | 3.0167 | 84.4849 | 115.7684 | 123.5229 | -123.8068 | -123.8068
3807.7188 | 123.8251 | -61.3815 | 62.1506 | 0.097885 | 0.012179 | 0.012773 | 0.0091152 | 0.060248 | -0.00011953 | 0.082467 | -58.4656 | 62.1002 | -61.7065 | -61.5784 | 54.3365 | 23.2086 | 7.7454 | 7.0541 | 62.1048 | -61.6791 | -0.32501 | -0.050354 | 2.916 | -0.19684 | -7.814 | -0.29755 | -0.045777 | 3.241 | 69.1269 | 68.4357 | 115.7181 | 123.4818 | 2.916 | 123.4863 | 84.5901 | -0.29755 | 123.4818 | 2.916 | 84.5901 | 115.7181 | 123.4863 | -123.8571 | -123.8297
3808.7188 | 123.8297 | -61.3815 | 62.1826 | -0.031814 | 0.01346 | 0.0080728 | 0.01232 | 0.058539 | 0.0018031 | 0.079904 | -58.4518 | 62.0865 | -61.702 | -61.5646 | 54.3594 | 23.0759 | 7.7225 | 7.1686 | 62.1277 | -61.6745 | -0.32043 | -0.09613 | 2.9297 | -0.1831 | -7.8232 | -0.29297 | -0.054931 | 3.2501 | 69.104 | 68.5501 | 115.741 | 123.468 | 2.9297 | 123.5092 | 84.4574 | -0.29297 | 123.468 | 2.9297 | 84.4574 | 115.741 | 123.5092 | -123.8846 | -123.8571
3809.7188 | 123.7976 | -61.3953 | 62.1597 | 0.097885 | 0.015383 | 0.013413 | 0.011251 | 0.057685 | 0.00030767 | 0.079476 | -58.4473 | 62.1094 | -61.702 | -61.5875 | 54.332 | 23.0072 | 7.7179 | 7.1045 | 62.1414 | -61.702 | -0.3067 | -0.050354 | 2.948 | -0.19226 | -7.8278 | -0.3067 | -0.018311 | 3.2547 | 69.1132 | 68.4998 | 115.7272 | 123.5046 | 2.948 | 123.5367 | 84.4025 | -0.3067 | 123.5046 | 2.948 | 84.4025 | 115.7272 | 123.5367 | -123.8617 | -123.8617
3810.7188 | 123.848 | -61.3861 | 62.1826 | 0.097885 | 0.014315 | 0.012559 | 0.010824 | 0.058325 | 0.00052127 | 0.080544 | -58.4335 | 62.0911 | -61.7065 | -61.5967 | 54.3457 | 23.1033 | 7.6996 | 7.1136 | 62.1185 | -61.6791 | -0.32044 | -0.091553 | 2.9526 | -0.21057 | -7.8369 | -0.29297 | -0.064087 | 3.273 | 69.0857 | 68.4998 | 115.7318 | 123.4772 | 2.9526 | 123.5046 | 84.4894 | -0.29297 | 123.4772 | 2.9526 | 84.4894 | 115.7318 | 123.5046 | -123.8892 | -123.8617
3811.7188 | 123.8297 | -61.4044 | 62.1689 | 0.021591 | 0.013247 | 0.011704 | 0.0089016 | 0.058966 | 0.0028711 | 0.076486 | -58.461 | 62.1002 | -61.6928 | -61.5784 | 54.2999 | 23.0988 | 7.7545 | 7.0999 | 62.1185 | -61.702 | -0.28839 | -0.068664 | 2.9434 | -0.17395 | -7.869 | -0.29755 | -0.050354 | 3.2318 | 69.1589 | 68.5043 | 115.7043 | 123.5046 | 2.9434 | 123.5229 | 84.5032 | -0.29755 | 123.5046 | 2.9434 | 84.5032 | 115.7043 | 123.5229 | -123.8617 | -123.8708
3812.7188 | 123.8159 | -61.3907 | 62.1368 | 0.067368 | 0.013674 | 0.013413 | 0.011892 | 0.060034 | 9.4068e-05 | 0.079904 | -58.4106 | 62.0636 | -61.7249 | -61.5646 | 54.2633 | 23.0392 | 7.6309 | 7.1182 | 62.1094 | -61.6745 | -0.33417 | -0.073242 | 2.98 | -0.17395 | -7.8735 | -0.28381 | -0.027466 | 3.3142 | 69.0216 | 68.5089 | 115.654 | 123.4543 | 2.98 | 123.5001 | 84.4299 | -0.28381 | 123.4543 | 2.98 | 84.4299 | 115.654 | 123.5001 | -123.8617 | -123.8113
3813.7188 | 123.8388 | -61.3861 | 62.1643 | -0.077591 | 0.01346 | 0.011064 | 0.0097562 | 0.058112 | -0.0016149 | 0.078195 | -58.4198 | 62.0956 | -61.6837 | -61.5189 | 54.4006 | 23.1216 | 7.6904 | 7.1869 | 62.1231 | -61.6699 | -0.29755 | -0.068665 | 2.9663 | -0.13275 | -7.7637 | -0.28381 | -0.041199 | 3.2639 | 69.0765 | 68.573 | 115.7867 | 123.4818 | 2.9663 | 123.5092 | 84.5078 | -0.28381 | 123.4818 | 2.9663 | 84.5078 | 115.7867 | 123.5092 | -123.848 | -123.8342
3814.7188 | 123.8434 | -61.3998 | 62.1689 | -0.68794 | 0.013033 | 0.012986 | 0.010183 | 0.057471 | 0.0013757 | 0.080544 | -58.5205 | 62.1277 | -61.7203 | -61.5738 | 54.3137 | 23.1033 | 7.6767 | 7.1228 | 62.1094 | -61.6653 | -0.32043 | -0.041198 | 2.8793 | -0.17395 | -7.8552 | -0.2655 | -0.059509 | 3.1998 | 69.0765 | 68.5226 | 115.7135 | 123.5275 | 2.8793 | 123.5092 | 84.5032 | -0.2655 | 123.5275 | 2.8793 | 84.5032 | 115.7135 | 123.5092 | -123.8892 | -123.8342
3815.7188 | 123.8113 | -61.4136 | 62.1414 | 0.013962 | 0.014529 | 0.014909 | 0.0095424 | 0.05683 | 9.4068e-05 | 0.080117 | -58.3374 | 62.1231 | -61.6837 | -61.5646 | 54.3915 | 23.085 | 7.7271 | 7.0862 | 62.1231 | -61.6928 | -0.27008 | -0.01831 | 3.0762 | -0.15106 | -7.7499 | -0.27924 | -0.01831 | 3.3463 | 69.1406 | 68.4998 | 115.8051 | 123.5367 | 3.0762 | 123.5367 | 84.4986 | -0.27924 | 123.5367 | 3.0762 | 84.4986 | 115.8051 | 123.5367 | -123.8251 | -123.8342
3816.7188 | 123.8113 | -61.409 | 62.1689 | 0.029221 | 0.015383 | 0.013627 | 0.00527 | 0.058325 | 0.00094847 | 0.081185 | -58.4564 | 62.0865 | -61.6974 | -61.5555 | 54.4327 | 22.9111 | 7.7408 | 7.1182 | 62.1048 | -61.6791 | -0.28839 | -0.082397 | 2.9526 | -0.14648 | -7.7362 | -0.27008 | -0.064087 | 3.241 | 69.1498 | 68.5272 | 115.8417 | 123.4955 | 2.9526 | 123.5138 | 84.3201 | -0.27008 | 123.4955 | 2.9526 | 84.3201 | 115.8417 | 123.5138 | -123.8663 | -123.848
3817.7188 | 123.8251 | -61.3953 | 62.1552 | 0.052109 | 0.013247 | 0.009141 | 0.0089016 | 0.059394 | 0.0022303 | 0.07969 | -58.4518 | 62.0636 | -61.7111 | -61.5509 | 54.6021 | 23.0667 | 7.5348 | 7.0953 | 62.1231 | -61.6653 | -0.31586 | -0.091552 | 2.9434 | -0.15564 | -7.5531 | -0.27008 | -0.032043 | 3.2593 | 68.9301 | 68.4906 | 115.9973 | 123.4589 | 2.9434 | 123.5184 | 84.462 | -0.27008 | 123.4589 | 2.9434 | 84.462 | 115.9973 | 123.5184 | -123.8663 | -123.8205
3818.7188 | 123.9441 | -61.3953 | 62.1689 | 0.11314 | 0.011538 | 0.0080728 | 0.010183 | 0.057044 | -0.00033333 | 0.079476 | -58.4564 | 62.1094 | -61.7111 | -61.5555 | 54.3274 | 23.0164 | 7.6996 | 7.0953 | 62.114 | -61.6608 | -0.31586 | -0.059509 | 2.9388 | -0.16022 | -7.8415 | -0.2655 | -0.054931 | 3.2547 | 69.0948 | 68.4906 | 115.7227 | 123.5046 | 2.9388 | 123.5092 | 84.4116 | -0.2655 | 123.5046 | 2.9388 | 84.4116 | 115.7227 | 123.5092 | -123.88 | -123.8297
3819.7188 | 123.8297 | -61.3907 | 62.1368 | 0.11314 | 0.014956 | 0.0132 | 0.0097562 | 0.057685 | 0.0026575 | 0.078835 | -58.4061 | 62.0682 | -61.7386 | -61.5646 | 54.3182 | 23.0072 | 7.6538 | 7.1228 | 62.0773 | -61.7065 | -0.3479 | -0.068665 | 2.9846 | -0.17395 | -7.8186 | -0.31586 | -0.059509 | 3.3325 | 69.0445 | 68.5135 | 115.7089 | 123.4589 | 2.9846 | 123.468 | 84.3979 | -0.31586 | 123.4589 | 2.9846 | 84.3979 | 115.7089 | 123.468 | -123.8754 | -123.8434
3820.7188 | 123.8297 | -61.4227 | 62.1323 | 0.13603 | 0.013033 | 0.017686 | 0.012106 | 0.060248 | 0.00094847 | 0.080331 | -58.4106 | 62.0865 | -61.7203 | -61.5555 | 54.3457 | 23.053 | 7.7042 | 7.1274 | 62.0911 | -61.7065 | -0.29755 | -0.045776 | 3.0121 | -0.13275 | -7.7866 | -0.28381 | -0.041199 | 3.3096 | 69.1269 | 68.5501 | 115.7684 | 123.5092 | 3.0121 | 123.5138 | 84.4757 | -0.28381 | 123.5092 | 3.0121 | 84.4757 | 115.7684 | 123.5138 | -123.8525 | -123.8388
3821.7188 | 123.8113 | -61.3998 | 62.1552 | 0.0063326 | 0.010897 | 0.010423 | 0.010183 | 0.059607 | 9.4068e-05 | 0.080972 | -58.3237 | 62.1231 | -61.6974 | -61.5692 | 54.3182 | 22.9111 | 7.7454 | 7.1365 | 62.114 | -61.6745 | -0.29755 | -0.032043 | 3.0762 | -0.16937 | -7.8369 | -0.27466 | -0.041198 | 3.3737 | 69.1452 | 68.5364 | 115.7181 | 123.5229 | 3.0762 | 123.5138 | 84.3109 | -0.27466 | 123.5229 | 3.0762 | 84.3109 | 115.7181 | 123.5138 | -123.8525 | -123.8297
3822.7188 | 123.8159 | -61.3953 | 62.1414 | 0.090256 | 0.014101 | 0.011064 | 0.008688 | 0.059607 | -0.00097413 | 0.076058 | -58.4564 | 62.1185 | -61.7157 | -61.4914 | 54.2084 | 22.8882 | 7.7499 | 7.1686 | 62.1002 | -61.6699 | -0.32043 | -0.022888 | 2.9388 | -0.09613 | -7.933 | -0.27466 | -0.041198 | 3.2593 | 69.1452 | 68.5638 | 115.6036 | 123.5138 | 2.9388 | 123.4955 | 84.2834 | -0.27466 | 123.5138 | 2.9388 | 84.2834 | 115.6036 | 123.4955 | -123.8571 | -123.8113
3823.7188 | 123.9029 | -61.3861 | 62.1735 | -0.19966 | 0.013888 | 0.016618 | 0.0089016 | 0.058325 | -0.0022559 | 0.079476 | -58.3649 | 62.1231 | -61.6882 | -61.4044 | 54.0527 | 22.7646 | 7.8461 | 7.2006 | 62.1185 | -61.6425 | -0.30212 | -0.050354 | 3.0212 | -0.018311 | -8.1207 | -0.25635 | -0.054932 | 3.3234 | 69.2322 | 68.5867 | 115.4388 | 123.5092 | 3.0212 | 123.5046 | 84.1507 | -0.25635 | 123.5092 | 3.0212 | 84.1507 | 115.4388 | 123.5046 | -123.8617 | -123.8159
3824.7188 | 123.8113 | -61.3998 | 62.1597 | 0.03685 | 0.01282 | 0.013413 | 0.0095424 | 0.060248 | -0.00011953 | 0.081613 | -58.4564 | 62.0682 | -61.7065 | -61.5738 | 54.2862 | 22.9935 | 7.7454 | 7.2006 | 62.1094 | -61.6745 | -0.3067 | -0.091553 | 2.9434 | -0.17395 | -7.8735 | -0.27466 | -0.050354 | 3.2501 | 69.1452 | 68.6005 | 115.686 | 123.468 | 2.9434 | 123.5092 | 84.3933 | -0.27466 | 123.468 | 2.9434 | 84.3933 | 115.686 | 123.5092 | -123.8663 | -123.8342
3825.7188 | 123.8388 | -61.3953 | 62.1323 | 0.090256 | 0.013674 | 0.011491 | 0.008688 | 0.058753 | 0.0028711 | 0.08204 | -58.4473 | 62.0911 | -61.7386 | -61.5921 | 54.3549 | 23.0896 | 7.7774 | 7.1915 | 62.0956 | -61.6699 | -0.34332 | -0.041199 | 2.948 | -0.19684 | -7.7774 | -0.27466 | -0.036621 | 3.2913 | 69.1727 | 68.5867 | 115.7501 | 123.4863 | 2.948 | 123.4909 | 84.4849 | -0.27466 | 123.4863 | 2.948 | 84.4849 | 115.7501 | 123.4909 | -123.8708 | -123.8022
3826.7188 | 123.8297 | -61.4319 | 62.1277 | 0.17418 | 0.013888 | 0.016618 | 0.011038 | 0.058753 | 0.00073487 | 0.078195 | -58.3878 | 62.0773 | -61.6974 | -61.5509 | 54.4052 | 22.9935 | 7.7179 | 7.2006 | 62.1002 | -61.6837 | -0.2655 | -0.050354 | 3.0441 | -0.11902 | -7.7225 | -0.25177 | -0.027466 | 3.3096 | 69.1498 | 68.6325 | 115.8371 | 123.5092 | 3.0441 | 123.5321 | 84.4254 | -0.25177 | 123.5092 | 3.0441 | 84.4254 | 115.8371 | 123.5321 | -123.8251 | -123.8113
3827.7188 | 123.8434 | -61.3861 | 62.1414 | -0.0012969 | 0.014315 | 0.016191 | 0.010397 | 0.059394 | 0.0011621 | 0.079476 | -58.4106 | 62.0956 | -61.7111 | -61.5417 | 54.4327 | 23.0942 | 7.6813 | 7.2098 | 62.0956 | -61.6699 | -0.32501 | -0.045776 | 2.9755 | -0.15564 | -7.7087 | -0.28381 | -0.045776 | 3.3005 | 69.0674 | 68.5959 | 115.8188 | 123.4818 | 2.9755 | 123.4818 | 84.4803 | -0.28381 | 123.4818 | 2.9755 | 84.4803 | 115.8188 | 123.4818 | -123.8525 | -123.8113
3828.7188 | 123.8892 | -61.3586 | 62.2009 | -0.16151 | 0.01346 | 0.011491 | 0.0093288 | 0.05918 | -0.00076053 | 0.079263 | -58.3786 | 62.0865 | -61.6882 | -61.4731 | 54.4556 | 23.0621 | 7.7911 | 7.2876 | 62.1231 | -61.6562 | -0.32959 | -0.11444 | 2.98 | -0.11444 | -7.7454 | -0.29755 | -0.07782 | 3.3096 | 69.1498 | 68.6462 | 115.8142 | 123.4451 | 2.98 | 123.4818 | 84.4208 | -0.29755 | 123.4451 | 2.98 | 84.4208 | 115.8142 | 123.4818 | -123.8892 | -123.8571
3829.7188 | 123.8159 | -61.3861 | 62.1643 | 0.18181 | 0.013247 | 0.007432 | 0.010397 | 0.058966 | 0.00030767 | 0.079049 | -58.4564 | 62.0544 | -61.7111 | -61.5967 | 54.3549 | 23.0072 | 7.8369 | 7.2006 | 62.0865 | -61.6791 | -0.32501 | -0.10986 | 2.9297 | -0.21057 | -7.8094 | -0.29297 | -0.07782 | 3.2547 | 69.223 | 68.5867 | 115.741 | 123.4406 | 2.9297 | 123.4726 | 84.3933 | -0.29297 | 123.4406 | 2.9297 | 84.3933 | 115.741 | 123.4726 | -123.8754 | -123.8434
3830.7188 | 123.8113 | -61.3953 | 62.1506 | 0.10551 | 0.015383 | 0.0089274 | 0.010611 | 0.059394 | 0.00073487 | 0.07969 | -58.4335 | 62.0773 | -61.7111 | -61.5738 | 54.3091 | 23.0804 | 7.7774 | 7.2189 | 62.0956 | -61.6699 | -0.31586 | -0.073242 | 2.9617 | -0.17853 | -7.8415 | -0.27466 | -0.054932 | 3.2776 | 69.1727 | 68.6142 | 115.7043 | 123.4726 | 2.9617 | 123.4909 | 84.4757 | -0.27466 | 123.4726 | 2.9617 | 84.4757 | 115.7043 | 123.4909 | -123.8617 | -123.8205
3831.7188 | 123.8297 | -61.409 | 62.1414 | 0.10551 | 0.01581 | 0.01555 | 0.011251 | 0.058539 | 9.4068e-05 | 0.080117 | -58.4015 | 62.0728 | -61.7157 | -61.5555 | 54.3091 | 23.1308 | 7.7637 | 7.2327 | 62.0865 | -61.6837 | -0.3067 | -0.068664 | 3.0075 | -0.14648 | -7.8323 | -0.27466 | -0.054931 | 3.3142 | 69.1727 | 68.6417 | 115.7181 | 123.4818 | 3.0075 | 123.4955 | 84.5398 | -0.27466 | 123.4818 | 3.0075 | 84.5398 | 115.7181 | 123.4955 | -123.8571 | -123.8251
3832.7188 | 123.8388 | -61.3998 | 62.146 | 0.14366 | 0.014956 | 0.016831 | 0.011465 | 0.059394 | 0.0047937 | 0.080117 | -58.4015 | 62.0956 | -61.702 | -61.5509 | 54.3503 | 23.1216 | 7.7499 | 7.2784 | 62.0865 | -61.6974 | -0.30212 | -0.050354 | 2.9984 | -0.15106 | -7.7957 | -0.29755 | -0.059509 | 3.3005 | 69.1498 | 68.6783 | 115.7501 | 123.4955 | 2.9984 | 123.4863 | 84.5215 | -0.29755 | 123.4955 | 2.9984 | 84.5215 | 115.7501 | 123.4863 | -123.848 | -123.8434
3833.7188 | 123.8251 | -61.3815 | 62.1689 | 0.12077 | 0.013888 | 0.012345 | 0.0076198 | 0.05918 | 0.0018031 | 0.081826 | -58.4702 | 62.1002 | -61.7249 | -61.5784 | 54.3411 | 23.1766 | 7.8506 | 7.3196 | 62.1094 | -61.6837 | -0.34332 | -0.068664 | 2.9114 | -0.19684 | -7.8278 | -0.30212 | -0.059509 | 3.2547 | 69.2322 | 68.7012 | 115.7227 | 123.4818 | 2.9114 | 123.4909 | 84.5581 | -0.30212 | 123.4818 | 2.9114 | 84.5581 | 115.7227 | 123.4909 | -123.8937 | -123.8525
3834.7188 | 123.8571 | -61.4044 | 62.1368 | 0.21233 | 0.015597 | 0.0087138 | 0.014669 | 0.056617 | 0.00073487 | 0.078195 | -58.3649 | 62.0911 | -61.7294 | -61.5509 | 54.3823 | 23.3002 | 7.7362 | 7.2922 | 62.0728 | -61.6882 | -0.32501 | -0.045777 | 3.0396 | -0.14648 | -7.7545 | -0.28381 | -0.064087 | 3.3646 | 69.1406 | 68.6966 | 115.7867 | 123.4955 | 3.0396 | 123.4772 | 84.7046 | -0.28381 | 123.4955 | 3.0396 | 84.7046 | 115.7867 | 123.4772 | -123.8663 | -123.8251
3835.7188 | 123.8571 | -61.3998 | 62.1277 | 0.14366 | 0.015383 | 0.014909 | 0.011465 | 0.060248 | 0.00073487 | 0.081826 | -58.4106 | 62.0956 | -61.6974 | -61.5417 | 54.332 | 23.1857 | 7.7683 | 7.2876 | 62.1002 | -61.6791 | -0.29755 | -0.032044 | 2.9892 | -0.14191 | -7.7957 | -0.27924 | -0.027466 | 3.2867 | 69.1681 | 68.6874 | 115.7318 | 123.4955 | 2.9892 | 123.5001 | 84.5856 | -0.27924 | 123.4955 | 2.9892 | 84.5856 | 115.7318 | 123.5001 | -123.8251 | -123.8068
3836.7188 | 123.8709 | -61.3953 | 62.1368 | 0.91423 | 0.013888 | 0.014054 | 0.013174 | 0.060462 | -0.00011953 | 0.079904 | -58.342 | 62.0819 | -61.7065 | -61.5509 | 54.3961 | 23.3231 | 7.8094 | 7.3334 | 62.0773 | -61.6882 | -0.31128 | -0.054932 | 3.0533 | -0.15564 | -7.7408 | -0.29297 | -0.059509 | 3.3646 | 69.2047 | 68.7286 | 115.7913 | 123.4772 | 3.0533 | 123.4726 | 84.7183 | -0.29297 | 123.4772 | 3.0533 | 84.7183 | 115.7913 | 123.4726 | -123.8434 | -123.8251
3837.7188 | 123.8571 | -61.3953 | 62.1185 | 0.17418 | 0.014315 | 0.017472 | 0.012747 | 0.062384 | -0.0020421 | 0.078622 | -58.4015 | 62.0773 | -61.6974 | -61.7111 | 54.4968 | 23.4192 | 7.7271 | 7.3242 | 62.0865 | -61.702 | -0.30212 | -0.041198 | 2.9938 | -0.31586 | -7.6218 | -0.3067 | -0.032043 | 3.2959 | 69.1223 | 68.7195 | 115.892 | 123.4726 | 2.9938 | 123.4818 | 84.8145 | -0.3067 | 123.4726 | 2.9938 | 84.8145 | 115.892 | 123.4818 | -123.8159 | -123.8205
3838.7188 | 123.8297 | -61.377 | 62.1094 | 0.13603 | 0.013674 | 0.016404 | 0.01296 | 0.059607 | 0.0022303 | 0.079049 | -58.3969 | 62.0911 | -61.7157 | -61.5463 | 54.4098 | 23.2864 | 7.7545 | 7.2968 | 62.1002 | -61.6653 | -0.33875 | -0.018311 | 2.98 | -0.16937 | -7.6996 | -0.28839 | -0.009155 | 3.3188 | 69.1315 | 68.6737 | 115.7867 | 123.468 | 2.98 | 123.4772 | 84.6634 | -0.28839 | 123.468 | 2.98 | 84.6634 | 115.7867 | 123.4772 | -123.8251 | -123.7747
3839.7188 | 123.88 | -61.4182 | 62.1002 | 0.21233 | 0.015169 | 0.016191 | 0.016592 | 0.064521 | -0.00076053 | 0.078408 | -58.4061 | 62.1323 | -61.6974 | -61.5555 | 54.3961 | 23.3093 | 7.8278 | 7.3105 | 62.1002 | -61.7203 | -0.27924 | 0.032043 | 3.0121 | -0.13733 | -7.7042 | -0.30212 | 0 | 3.2913 | 69.2459 | 68.7286 | 115.8142 | 123.5504 | 3.0121 | 123.5184 | 84.7275 | -0.30212 | 123.5504 | 3.0121 | 84.7275 | 115.8142 | 123.5184 | -123.7976 | -123.8205
3840.7188 | 123.7793 | -61.441 | 62.146 | 0.18181 | 0.017519 | 0.01555 | 0.014669 | 0.062171 | 0.00094847 | 0.081399 | -58.4702 | 62.1597 | -61.7523 | -61.647 | 54.332 | 23.259 | 7.9468 | 7.196 | 62.1414 | -61.7569 | -0.31128 | 0.013733 | 2.9709 | -0.20599 | -7.814 | -0.31586 | -0.004578 | 3.2822 | 69.3878 | 68.6371 | 115.773 | 123.6008 | 2.9709 | 123.5825 | 84.7 | -0.31586 | 123.6008 | 2.9709 | 84.7 | 115.773 | 123.5825 | -123.8983 | -123.9029
3841.7188 | 123.8205 | -61.4227 | 62.1277 | 0.2047 | 0.017733 | 0.013841 | 0.016592 | 0.065161 | -0.0011877 | 0.080117 | -58.4518 | 62.1689 | -61.7294 | -61.6058 | 54.3594 | 23.2635 | 7.8735 | 7.2739 | 62.1231 | -61.7615 | -0.3067 | 0.041198 | 2.9709 | -0.18311 | -7.7682 | -0.33875 | -0.004578 | 3.2776 | 69.2963 | 68.6966 | 115.7822 | 123.5916 | 2.9709 | 123.5458 | 84.6863 | -0.33875 | 123.5916 | 2.9709 | 84.6863 | 115.7822 | 123.5458 | -123.8571 | -123.8892
3842.7188 | 123.8663 | -61.3907 | 62.1368 | 0.013962 | 0.016238 | 0.012345 | 0.013388 | 0.063666 | -0.00011953 | 0.07969 | -58.4335 | 62.146 | -61.7249 | -61.5601 | 54.4235 | 23.2727 | 7.8049 | 7.3196 | 62.1231 | -61.702 | -0.33417 | 0.009155 | 2.9572 | -0.16937 | -7.7133 | -0.31128 | -0.013733 | 3.2913 | 69.1956 | 68.7103 | 115.8142 | 123.5367 | 2.9572 | 123.5138 | 84.6634 | -0.31128 | 123.5367 | 2.9572 | 84.6634 | 115.8142 | 123.5138 | -123.8617 | -123.8388
3843.7188 | 123.8251 | -61.377 | 62.1506 | 0.10551 | 0.014529 | 0.012132 | 0.0065518 | 0.061316 | 9.4068e-05 | 0.081185 | -58.4335 | 62.0865 | -61.7203 | -61.615 | 54.3915 | 23.2544 | 7.8461 | 7.3196 | 62.1185 | -61.6837 | -0.34332 | -0.064087 | 2.9434 | -0.23804 | -7.7591 | -0.3067 | -0.032044 | 3.2867 | 69.223 | 68.6966 | 115.7684 | 123.4634 | 2.9434 | 123.4955 | 84.6313 | -0.3067 | 123.4634 | 2.9434 | 84.6313 | 115.7684 | 123.4955 | -123.8708 | -123.8342
3844.7188 | 123.848 | -61.441 | 62.1231 | 0.17418 | 0.016451 | 0.012345 | 0.01766 | 0.062384 | 0.0018031 | 0.080331 | -58.429 | 62.1735 | -61.7249 | -61.6013 | 54.3961 | 23.3414 | 7.8232 | 7.3151 | 62.0911 | -61.7569 | -0.28381 | 0.050354 | 3.0121 | -0.16022 | -7.7271 | -0.31586 | -0.032044 | 3.2959 | 69.2642 | 68.7561 | 115.8371 | 123.6145 | 3.0121 | 123.5321 | 84.7824 | -0.31586 | 123.6145 | 3.0121 | 84.7824 | 115.8371 | 123.5321 | -123.848 | -123.88
3845.7188 | 123.793 | -61.4273 | 62.1368 | 0.16655 | 0.01816 | 0.016618 | 0.014669 | 0.06388 | 9.4068e-05 | 0.081399 | -58.4427 | 62.1552 | -61.7203 | -61.6196 | 54.2633 | 23.2773 | 7.8735 | 7.2601 | 62.146 | -61.7386 | -0.29297 | 0.01831 | 2.9846 | -0.19226 | -7.8735 | -0.31128 | 0.009155 | 3.2776 | 69.3008 | 68.6874 | 115.6906 | 123.5825 | 2.9846 | 123.5733 | 84.7046 | -0.31128 | 123.5825 | 2.9846 | 84.7046 | 115.6906 | 123.5733 | -123.8571 | -123.8754
3846.7188 | 123.7518 | -61.4227 | 62.1597 | 0.15129 | 0.023501 | 0.021531 | 0.018728 | 0.061316 | -0.00076053 | 0.081399 | -58.8089 | 62.1185 | -61.7706 | -61.7065 | 54.2862 | 23.1766 | 7.9788 | 7.2052 | 62.1826 | -61.7661 | -0.3479 | -0.041199 | 2.6138 | -0.28381 | -7.8735 | -0.34332 | 0.022888 | 2.9617 | 69.4016 | 68.6279 | 115.7089 | 123.5413 | 2.6138 | 123.6053 | 84.5993 | -0.34332 | 123.5413 | 2.6138 | 84.5993 | 115.7089 | 123.6053 | -123.9304 | -123.9258
3847.7188 | 123.7793 | -61.4548 | 62.1826 | 0.15892 | 0.019015 | 0.018754 | 0.016165 | 0.063666 | 0.0020167 | 0.078408 | -58.4976 | 62.2055 | -61.7432 | -61.9812 | 53.9108 | 23.2635 | 8.1985 | 7.1594 | 62.1872 | -61.7249 | -0.28839 | 0.022888 | 2.9572 | -0.52643 | -8.2718 | -0.27008 | 0.004578 | 3.2455 | 69.6533 | 68.6142 | 115.3656 | 123.6603 | 2.9572 | 123.642 | 84.7183 | -0.27008 | 123.6603 | 2.9572 | 84.7183 | 115.3656 | 123.642 | -123.9258 | -123.9075
3848.7344 | 123.8434 | -61.4136 | 62.1368 | 0.074997 | 0.012179 | 0.011491 | 0.005911 | 0.063452 | 0.0018031 | 0.079049 | -58.3054 | 62.1506 | -61.702 | -61.5967 | 54.2084 | 23.2315 | 7.9605 | 7.4066 | 62.1689 | -61.6608 | -0.28839 | 0.013733 | 3.1082 | -0.18311 | -7.9285 | -0.24719 | 0.032043 | 3.3966 | 69.3741 | 68.8202 | 115.6219 | 123.5641 | 3.1082 | 123.5825 | 84.6451 | -0.24719 | 123.5641 | 3.1082 | 84.6451 | 115.6219 | 123.5825 | -123.8388 | -123.7976
3849.7188 | 123.8159 | -61.4365 | 62.1414 | 0.22758 | 0.016665 | 0.01555 | 0.013388 | 0.062598 | 0.00094847 | 0.079476 | -58.4518 | 62.1552 | -61.734 | -61.6241 | 54.3045 | 23.2864 | 7.8827 | 7.3105 | 62.114 | -61.7569 | -0.29755 | 0.013733 | 2.9846 | -0.18768 | -7.8369 | -0.32044 | -0.027465 | 3.2822 | 69.3192 | 68.7469 | 115.741 | 123.5916 | 2.9846 | 123.5504 | 84.7229 | -0.32044 | 123.5916 | 2.9846 | 84.7229 | 115.741 | 123.5504 | -123.8754 | -123.8983
3850.7188 | 123.8297 | -61.4319 | 62.1323 | 0.15892 | 0.018374 | 0.018754 | 0.015524 | 0.066016 | 9.4068e-05 | 0.079904 | -58.4793 | 62.1872 | -61.7386 | -61.6425 | 54.3228 | 23.3047 | 7.9468 | 7.338 | 62.114 | -61.7569 | -0.3067 | 0.054932 | 2.9526 | -0.21057 | -7.8094 | -0.32501 | -0.01831 | 3.2593 | 69.3787 | 68.7698 | 115.7547 | 123.6191 | 2.9526 | 123.5458 | 84.7366 | -0.32501 | 123.6191 | 2.9526 | 84.7366 | 115.7547 | 123.5458 | -123.8708 | -123.8892
3851.7188 | 123.793 | -61.4502 | 62.1414 | 0.2047 | 0.019656 | 0.015122 | 0.014456 | 0.063025 | 0.00073487 | 0.082467 | -58.4839 | 62.1826 | -61.7386 | -61.6516 | 54.1992 | 23.1171 | 7.9651 | 7.3105 | 62.1323 | -61.7569 | -0.28839 | 0.041199 | 2.9663 | -0.20142 | -7.9422 | -0.3067 | -0.009155 | 3.2547 | 69.4153 | 68.7607 | 115.6494 | 123.6328 | 2.9663 | 123.5825 | 84.5673 | -0.3067 | 123.6328 | 2.9663 | 84.5673 | 115.6494 | 123.5825 | -123.88 | -123.8983
3852.7188 | 123.7564 | -61.4319 | 62.1643 | 0.15129 | 0.01581 | 0.015977 | 0.01531 | 0.063666 | -0.00011953 | 0.080331 | -58.4564 | 62.1964 | -61.7523 | -61.6608 | 54.2175 | 23.1491 | 8.0292 | 7.3242 | 62.1597 | -61.7432 | -0.32043 | 0.032043 | 2.9755 | -0.22888 | -7.9468 | -0.31128 | -0.004578 | 3.2959 | 69.4611 | 68.7561 | 115.6494 | 123.6282 | 2.9755 | 123.5916 | 84.581 | -0.31128 | 123.6282 | 2.9755 | 84.581 | 115.6494 | 123.5916 | -123.9166 | -123.9075
3853.7188 | 123.7244 | -61.4365 | 62.1597 | 0.013962 | 0.017733 | 0.014909 | 0.014669 | 0.063025 | 0.00073487 | 0.079263 | -58.4976 | 62.2101 | -61.7523 | -61.6837 | 54.2496 | 23.2956 | 8.0887 | 7.2922 | 62.1643 | -61.7386 | -0.31586 | 0.050354 | 2.9388 | -0.24719 | -7.9102 | -0.30212 | 0.004578 | 3.2547 | 69.5251 | 68.7286 | 115.686 | 123.6465 | 2.9388 | 123.6008 | 84.7321 | -0.30212 | 123.6465 | 2.9388 | 84.7321 | 115.686 | 123.6008 | -123.912 | -123.8983
3854.7188 | 123.7198 | -61.4456 | 62.1689 | 0.029221 | 0.01816 | 0.016191 | 0.014883 | 0.066443 | -0.0026831 | 0.083108 | -58.4518 | 62.2009 | -61.7523 | -61.702 | 54.213 | 23.1033 | 8.0887 | 7.283 | 62.1552 | -61.7386 | -0.3067 | 0.032044 | 2.9938 | -0.25635 | -7.9559 | -0.29297 | -0.013733 | 3.3005 | 69.5343 | 68.7286 | 115.6586 | 123.6465 | 2.9938 | 123.6008 | 84.549 | -0.29297 | 123.6465 | 2.9938 | 84.549 | 115.6586 | 123.6008 | -123.9212 | -123.9075
3855.7344 | 123.8342 | -61.3541 | 62.1597 | -0.14626 | 0.011751 | 0.0097818 | 0.0048428 | 0.06153 | -0.00097413 | 0.081613 | -58.3649 | 62.1185 | -61.6882 | -61.5326 | 54.3503 | 23.3963 | 7.9514 | 7.5485 | 62.1689 | -61.6516 | -0.33417 | -0.041199 | 2.9892 | -0.17853 | -7.8094 | -0.29755 | 0.009155 | 3.3234 | 69.3054 | 68.9026 | 115.7043 | 123.4726 | 2.9892 | 123.5229 | 84.7504 | -0.29755 | 123.4726 | 2.9892 | 84.7504 | 115.7043 | 123.5229 | -123.848 | -123.8113
3856.7188 | 123.7473 | -61.441 | 62.1597 | 0.13603 | 0.017092 | 0.014268 | 0.014242 | 0.062598 | -0.00054693 | 0.080117 | -58.4702 | 62.1872 | -61.7249 | -61.6653 | 54.2633 | 23.1445 | 7.9971 | 7.3151 | 62.1277 | -61.7477 | -0.28381 | 0.027466 | 2.9709 | -0.2243 | -7.8964 | -0.3067 | -0.032043 | 3.2547 | 69.4382 | 68.7561 | 115.7043 | 123.6282 | 2.9709 | 123.5687 | 84.5856 | -0.3067 | 123.6282 | 2.9709 | 84.5856 | 115.7043 | 123.5687 | -123.8846 | -123.9075
3857.7188 | 123.7701 | -61.441 | 62.1414 | 0.18181 | 0.017306 | 0.014909 | 0.014883 | 0.061316 | 0.0035121 | 0.079049 | -58.4839 | 62.2055 | -61.7615 | -61.6516 | 54.2633 | 23.2361 | 8.0566 | 7.338 | 62.1872 | -61.7706 | -0.32043 | 0.064087 | 2.9572 | -0.21057 | -7.8781 | -0.32959 | 0.045777 | 3.2776 | 69.4977 | 68.779 | 115.7043 | 123.6465 | 2.9572 | 123.6282 | 84.6771 | -0.32959 | 123.6465 | 2.9572 | 84.6771 | 115.7043 | 123.6282 | -123.9029 | -123.912
3858.7344 | 123.8617 | -61.4227 | 62.1185 | -0.016556 | 0.013674 | 0.015336 | 0.0056972 | 0.059607 | -0.0014013 | 0.081826 | -58.4564 | 62.0911 | -61.7477 | -61.5921 | 54.3457 | 23.4375 | 7.9742 | 7.4387 | 62.1277 | -61.6974 | -0.32501 | -0.027466 | 2.9663 | -0.16937 | -7.7728 | -0.27466 | 0.009156 | 3.2913 | 69.397 | 68.8614 | 115.7684 | 123.5138 | 2.9663 | 123.5504 | 84.8602 | -0.27466 | 123.5138 | 2.9663 | 84.8602 | 115.7684 | 123.5504 | -123.8663 | -123.8159
3859.7188 | 123.7518 | -61.4594 | 62.1643 | -2.9768 | 0.01816 | 0.018327 | 0.016165 | 0.059607 | -0.0011877 | 0.081826 | -58.5526 | 62.2055 | -61.7065 | -61.6837 | 54.1855 | 23.1583 | 8.0109 | 7.283 | 62.178 | -61.7889 | -0.24719 | 0.041198 | 2.9068 | -0.2243 | -7.9788 | -0.32959 | 0.013733 | 3.154 | 69.4702 | 68.7424 | 115.6448 | 123.6649 | 2.9068 | 123.6374 | 84.6176 | -0.32959 | 123.6649 | 2.9068 | 84.6176 | 115.6448 | 123.6374 | -123.8709 | -123.9532
3860.7344 | 123.7701 | -61.3907 | 62.1964 | -0.24544 | 0.014956 | 0.012345 | 0.010611 | 0.060462 | -0.0026831 | 0.079904 | -58.429 | 62.1643 | -61.7111 | -61.6013 | 54.3823 | 23.3368 | 8.0704 | 7.4112 | 62.178 | -61.6974 | -0.32043 | -0.032043 | 2.9617 | -0.21057 | -7.814 | -0.3067 | -0.01831 | 3.2822 | 69.4611 | 68.8019 | 115.773 | 123.555 | 2.9617 | 123.5687 | 84.7275 | -0.3067 | 123.555 | 2.9617 | 84.7275 | 115.773 | 123.5687 | -123.9075 | -123.8937
3861.7188 | 123.7289 | -61.441 | 62.2009 | 0.059738 | 0.01816 | 0.015977 | 0.017447 | 0.063239 | -0.0016149 | 0.078835 | -58.4473 | 62.2101 | -61.7203 | -61.647 | 54.2725 | 23.2864 | 8.0063 | 7.2739 | 62.1689 | -61.7294 | -0.27924 | 0.009155 | 2.9938 | -0.20599 | -7.9285 | -0.28839 | -0.032044 | 3.273 | 69.4473 | 68.7149 | 115.7135 | 123.6511 | 2.9938 | 123.6099 | 84.7275 | -0.28839 | 123.6511 | 2.9938 | 84.7275 | 115.7135 | 123.6099 | -123.9212 | -123.9304
3862.7188 | 123.7701 | -61.4365 | 62.1552 | 0.23521 | 0.017519 | 0.014695 | 0.014669 | 0.064307 | -0.00011953 | 0.081399 | -58.4793 | 62.1735 | -61.7523 | -61.6608 | 54.2953 | 23.2269 | 7.988 | 7.2601 | 62.1689 | -61.7844 | -0.31586 | 0.018311 | 2.9572 | -0.22431 | -7.8598 | -0.3479 | 0.013733 | 3.273 | 69.4244 | 68.6966 | 115.7318 | 123.6099 | 2.9572 | 123.6053 | 84.6634 | -0.3479 | 123.6099 | 2.9572 | 84.6634 | 115.7318 | 123.6053 | -123.9075 | -123.9395
3863.7188 | 123.8388 | -61.409 | 62.1414 | 0.12077 | 0.016878 | 0.013841 | 0.006979 | 0.059607 | -0.0020421 | 0.078835 | -58.4702 | 62.0956 | -61.7386 | -61.6379 | 54.3182 | 23.3139 | 7.869 | 7.3517 | 62.1277 | -61.7065 | -0.32959 | -0.045776 | 2.9388 | -0.22888 | -7.8232 | -0.29755 | -0.013732 | 3.2684 | 69.278 | 68.7607 | 115.7272 | 123.5046 | 2.9388 | 123.5367 | 84.7229 | -0.29755 | 123.5046 | 2.9388 | 84.7229 | 115.7272 | 123.5367 | -123.88 | -123.848
3864.7188 | 123.7656 | -61.441 | 62.1643 | -0.76424 | 0.016665 | 0.018754 | 0.017019 | 0.063666 | 0.00073487 | 0.079263 | -58.5159 | 62.2101 | -61.7432 | -61.6516 | 54.2358 | 23.259 | 8.0521 | 7.3013 | 62.1735 | -61.7523 | -0.30212 | 0.045776 | 2.9251 | -0.21057 | -7.9285 | -0.31128 | 0.009155 | 3.2272 | 69.4931 | 68.7424 | 115.6769 | 123.6511 | 2.9251 | 123.6145 | 84.7 | -0.31128 | 123.6511 | 2.9251 | 84.7 | 115.6769 | 123.6145 | -123.9075 | -123.9166
3865.7188 | 123.848 | -61.409 | 62.1323 | -0.12337 | 0.011538 | 0.014695 | 0.0082608 | 0.060675 | -0.00054693 | 0.080544 | -58.4152 | 62.1048 | -61.7065 | -61.5829 | 54.3549 | 23.3597 | 7.9788 | 7.4615 | 62.1414 | -61.6974 | -0.29755 | -0.027466 | 2.9938 | -0.17395 | -7.7774 | -0.28839 | 0.009155 | 3.2913 | 69.3878 | 68.8705 | 115.7639 | 123.5138 | 2.9938 | 123.5504 | 84.7687 | -0.28839 | 123.5138 | 2.9938 | 84.7687 | 115.7639 | 123.5504 | -123.8388 | -123.8297
3866.7188 | 123.7244 | -61.441 | 62.1918 | 0.14366 | 0.020296 | 0.016404 | 0.017447 | 0.057044 | -0.00011953 | 0.081185 | -58.4564 | 62.1964 | -61.7569 | -61.7249 | 54.2679 | 23.5199 | 8.0246 | 7.2693 | 62.1735 | -61.7523 | -0.31586 | 0.004578 | 2.9846 | -0.28381 | -7.9239 | -0.31128 | -0.01831 | 3.3005 | 69.4656 | 68.7103 | 115.7089 | 123.6374 | 2.9846 | 123.6145 | 84.9609 | -0.31128 | 123.6374 | 2.9846 | 84.9609 | 115.7089 | 123.6145 | -123.9487 | -123.9441
3867.7188 | 123.7518 | -61.441 | 62.178 | 0.029221 | 0.017733 | 0.016831 | 0.017019 | 0.061957 | -0.0016149 | 0.07969 | -58.4473 | 62.2055 | -61.7203 | -61.6608 | 54.2404 | 23.3093 | 8.1024 | 7.3013 | 62.2055 | -61.7661 | -0.27924 | 0.027465 | 2.9938 | -0.21973 | -7.9376 | -0.32501 | 0.027465 | 3.273 | 69.5435 | 68.7424 | 115.6815 | 123.6465 | 2.9938 | 123.6465 | 84.7504 | -0.32501 | 123.6465 | 2.9938 | 84.7504 | 115.6815 | 123.6465 | -123.8983 | -123.9441
3868.7188 | 123.8617 | -61.409 | 62.1323 | 0.17418 | 0.017733 | 0.017259 | 0.012533 | 0.062812 | -0.00097413 | 0.080544 | -58.4793 | 62.1277 | -61.7569 | -61.6013 | 54.3594 | 23.3231 | 7.9834 | 7.3975 | 62.1368 | -61.7294 | -0.3479 | -0.004577 | 2.9297 | -0.19226 | -7.7728 | -0.32043 | 0.004578 | 3.2776 | 69.3924 | 68.8065 | 115.7684 | 123.5367 | 2.9297 | 123.5458 | 84.7321 | -0.32043 | 123.5367 | 2.9297 | 84.7321 | 115.7684 | 123.5458 | -123.8892 | -123.8617
3869.7188 | 123.7152 | -61.4594 | 62.1552 | 0.029221 | 0.019442 | 0.014268 | 0.016806 | 0.062812 | -0.00011953 | 0.077554 | -58.4656 | 62.2055 | -61.7752 | -61.6882 | 54.2816 | 23.2773 | 8.0841 | 7.2601 | 62.1597 | -61.7935 | -0.31586 | 0.050354 | 2.9938 | -0.22888 | -7.8735 | -0.33417 | 0.004578 | 3.3096 | 69.5435 | 68.7195 | 115.741 | 123.6649 | 2.9938 | 123.6191 | 84.7366 | -0.33417 | 123.6649 | 2.9938 | 84.7366 | 115.741 | 123.6191 | -123.9304 | -123.9487
3870.7188 | 123.8709 | -61.3907 | 62.1323 | 0.082626 | 0.016878 | 0.012986 | 0.010397 | 0.063025 | -0.00097413 | 0.077767 | -58.4244 | 62.1094 | -61.7157 | -61.5875 | 54.4052 | 23.3643 | 7.8918 | 7.4203 | 62.1323 | -61.7386 | -0.32501 | -0.022888 | 2.9663 | -0.19684 | -7.7271 | -0.3479 | 0 | 3.2913 | 69.2825 | 68.811 | 115.7959 | 123.5001 | 2.9663 | 123.5229 | 84.7549 | -0.3479 | 123.5001 | 2.9663 | 84.7549 | 115.7959 | 123.5229 | -123.848 | -123.8708
3871.7188 | 123.7381 | -61.4548 | 62.146 | 0.11314 | 0.017306 | 0.017045 | 0.010611 | 0.06153 | 0.0015893 | 0.077767 | -58.3328 | 62.1918 | -61.7752 | -61.615 | 54.3869 | 23.2773 | 8.107 | 7.4341 | 62.1964 | -61.7569 | -0.32043 | 0.045776 | 3.1219 | -0.16022 | -7.7591 | -0.30212 | 0.050354 | 3.4424 | 69.5618 | 68.8889 | 115.8417 | 123.6465 | 3.1219 | 123.6511 | 84.7321 | -0.30212 | 123.6465 | 3.1219 | 84.7321 | 115.8417 | 123.6511 | -123.9212 | -123.9029
3872.7188 | 123.7656 | -61.4273 | 62.1643 | 0.15129 | 0.017092 | 0.013413 | 0.014456 | 0.065161 | 0.0013757 | 0.079476 | -58.4885 | 62.2055 | -61.7661 | -61.6882 | 53.9383 | 23.0209 | 8.5052 | 7.489 | 62.178 | -61.7798 | -0.33875 | 0.041198 | 2.9388 | -0.26093 | -8.226 | -0.35248 | 0.013733 | 3.2776 | 69.9326 | 68.9163 | 115.3656 | 123.6328 | 2.9388 | 123.6053 | 84.4482 | -0.35248 | 123.6328 | 2.9388 | 84.4482 | 115.3656 | 123.6053 | -123.9304 | -123.9441
3873.7188 | 123.8297 | -61.3998 | 62.114 | 0.15892 | 0.013247 | 0.015336 | 0.0076198 | 0.064521 | 9.4068e-05 | 0.080117 | -58.4244 | 62.1323 | -61.7523 | -61.6058 | 54.3869 | 23.4833 | 7.9239 | 7.4753 | 62.1323 | -61.7249 | -0.35248 | 0.01831 | 2.9755 | -0.20599 | -7.7271 | -0.32501 | 0.01831 | 3.3279 | 69.3237 | 68.8751 | 115.7867 | 123.5321 | 2.9755 | 123.5321 | 84.8831 | -0.32501 | 123.5321 | 2.9755 | 84.8831 | 115.7867 | 123.5321 | -123.8663 | -123.8388
3874.7188 | 123.7473 | -61.441 | 62.1872 | -0.0089264 | 0.017733 | 0.015336 | 0.017447 | 0.064307 | -0.0011877 | 0.079904 | -58.4106 | 62.1826 | -61.734 | -61.6104 | 54.2862 | 23.3505 | 8.0978 | 7.4066 | 62.1689 | -61.7889 | -0.29297 | -0.004578 | 3.0304 | -0.16937 | -7.901 | -0.3479 | -0.018311 | 3.3234 | 69.5389 | 68.8477 | 115.7272 | 123.6237 | 3.0304 | 123.6099 | 84.7916 | -0.3479 | 123.6237 | 3.0304 | 84.7916 | 115.7272 | 123.6099 | -123.9212 | -123.9761
3875.7188 | 123.7381 | -61.4319 | 62.1918 | 0.0063326 | 0.01816 | 0.016831 | 0.014669 | 0.063452 | -0.00076053 | 0.079904 | -58.4152 | 62.1872 | -61.7294 | -61.6013 | 54.4235 | 23.3139 | 8.0978 | 7.3746 | 62.2009 | -61.7432 | -0.29755 | -0.004577 | 3.0167 | -0.16937 | -7.7682 | -0.31128 | 0.009156 | 3.3142 | 69.5297 | 68.8065 | 115.8554 | 123.6191 | 3.0167 | 123.6328 | 84.7458 | -0.31128 | 123.6191 | 3.0167 | 84.7458 | 115.8554 | 123.6328 | -123.9212 | -123.9349
3876.7188 | 123.7289 | -61.4548 | 62.1643 | 0.17418 | 0.017306 | 0.015122 | 0.01296 | 0.064521 | 0.0035121 | 0.079049 | -58.493 | 62.2192 | -61.734 | -61.6608 | 54.5975 | 23.4924 | 8.0658 | 7.4478 | 62.1735 | -61.7798 | -0.27924 | 0.054931 | 2.9617 | -0.20599 | -7.5668 | -0.32501 | 0.009155 | 3.241 | 69.5206 | 68.9026 | 116.0522 | 123.674 | 2.9617 | 123.6282 | 84.9472 | -0.32501 | 123.674 | 2.9617 | 84.9472 | 116.0522 | 123.6282 | -123.8983 | -123.9441
3877.7188 | 123.6145 | -61.4731 | 62.0956 | 0.10551 | 0.01816 | 0.014909 | 0.015738 | 0.063666 | 0.0011621 | 0.080544 | -58.4747 | 62.2238 | -61.7661 | -61.6791 | 54.2999 | 23.3414 | 8.0704 | 7.283 | 62.178 | -61.7798 | -0.29297 | 0.12817 | 2.9984 | -0.20599 | -7.7957 | -0.3067 | 0.082398 | 3.2913 | 69.5435 | 68.7561 | 115.773 | 123.6969 | 2.9984 | 123.6511 | 84.8145 | -0.3067 | 123.6969 | 2.9984 | 84.8145 | 115.773 | 123.6511 | -123.8617 | -123.8754
3878.7188 | 123.8251 | -61.3998 | 62.1323 | 0.13603 | 0.017519 | 0.013413 | 0.006979 | 0.063452 | 0.0018031 | 0.079263 | -58.3969 | 62.1048 | -61.7249 | -61.6013 | 54.3457 | 23.5565 | 7.8964 | 7.4158 | 62.114 | -61.7111 | -0.32501 | -0.027466 | 3.0029 | -0.20142 | -7.7866 | -0.31128 | -0.01831 | 3.3279 | 69.2963 | 68.8156 | 115.7455 | 123.5046 | 3.0029 | 123.5138 | 84.9564 | -0.31128 | 123.5046 | 3.0029 | 84.9564 | 115.7455 | 123.5138 | -123.8571 | -123.8434
3879.7188 | 123.7152 | -61.4456 | 62.1597 | 0.1284 | 0.017092 | 0.017899 | 0.015097 | 0.061743 | 0.00030767 | 0.080544 | -58.4106 | 62.2101 | -61.7386 | -61.6837 | 54.1855 | 23.3826 | 8.1528 | 7.3471 | 62.1918 | -61.7798 | -0.29297 | 0.050354 | 3.035 | -0.23804 | -7.9742 | -0.33417 | 0.032043 | 3.3279 | 69.5984 | 68.7927 | 115.6311 | 123.6557 | 3.035 | 123.6374 | 84.8282 | -0.33417 | 123.6557 | 3.035 | 84.8282 | 115.6311 | 123.6374 | -123.8983 | -123.9395
3880.7188 | 123.7289 | -61.4548 | 62.1689 | 0.03685 | 0.01581 | 0.014909 | 0.015951 | 0.061316 | 0.00094847 | 0.079904 | -58.429 | 62.2238 | -61.7294 | -61.6699 | 54.2587 | 23.5703 | 8.0795 | 7.3013 | 62.178 | -61.7706 | -0.27466 | 0.054932 | 3.0258 | -0.21515 | -7.9102 | -0.31586 | 0.009156 | 3.3005 | 69.5343 | 68.7561 | 115.7135 | 123.6786 | 3.0258 | 123.6328 | 85.025 | -0.31586 | 123.6786 | 3.0258 | 85.025 | 115.7135 | 123.6328 | -123.8983 | -123.9395
3881.7188 | 123.7747 | -61.4502 | 62.1918 | -0.069961 | 0.018801 | 0.016618 | 0.013815 | 0.061743 | 0.00073487 | 0.078622 | -58.3786 | 62.2055 | -61.7249 | -61.6104 | 54.2267 | 23.4421 | 8.0429 | 7.3563 | 62.1918 | -61.7523 | -0.27466 | 0.013733 | 3.0716 | -0.16022 | -7.9651 | -0.30212 | 0 | 3.3463 | 69.4931 | 68.8065 | 115.6769 | 123.6557 | 3.0716 | 123.642 | 84.8923 | -0.30212 | 123.6557 | 3.0716 | 84.8923 | 115.6769 | 123.642 | -123.9166 | -123.9441
3882.7188 | 123.7839 | -61.4182 | 62.1643 | -0.10811 | 0.016878 | 0.017045 | 0.015738 | 0.062384 | -0.0016149 | 0.079904 | -58.3649 | 62.2147 | -61.7065 | -61.615 | 54.2862 | 23.4055 | 8.0292 | 7.3608 | 62.1826 | -61.7386 | -0.28839 | 0.050354 | 3.0533 | -0.19684 | -7.8781 | -0.32043 | 0.01831 | 3.3417 | 69.4473 | 68.779 | 115.7043 | 123.6328 | 3.0533 | 123.6008 | 84.8236 | -0.32043 | 123.6328 | 3.0533 | 84.8236 | 115.7043 | 123.6008 | -123.8709 | -123.9029
3883.7188 | 123.8663 | -61.4182 | 62.1368 | 0.21996 | 0.015383 | 0.016191 | 0.0095424 | 0.065589 | 0.0011621 | 0.07969 | -58.4152 | 62.1094 | -61.7294 | -61.6013 | 54.2542 | 23.4833 | 7.7225 | 7.1823 | 62.0865 | -61.7249 | -0.31128 | -0.027466 | 3.0029 | -0.1831 | -7.8827 | -0.3067 | -0.050354 | 3.3142 | 69.1406 | 68.6005 | 115.6723 | 123.5275 | 3.0029 | 123.5046 | 84.9014 | -0.3067 | 123.5275 | 3.0029 | 84.9014 | 115.6723 | 123.5046 | -123.8663 | -123.8617
3884.7188 | 123.7198 | -61.4639 | 62.1735 | 0.2047 | 0.01816 | 0.014268 | 0.012747 | 0.062598 | 0.00052127 | 0.081399 | -58.4061 | 62.2101 | -61.7615 | -61.6928 | 54.2084 | 23.4787 | 8.0978 | 7.2693 | 62.1872 | -61.7935 | -0.29755 | 0.036621 | 3.0579 | -0.22888 | -7.9651 | -0.32959 | 0.013733 | 3.3554 | 69.5618 | 68.7332 | 115.6723 | 123.674 | 3.0579 | 123.6511 | 84.9426 | -0.32959 | 123.674 | 3.0579 | 84.9426 | 115.6723 | 123.6511 | -123.9349 | -123.967
3885.7188 | 123.6832 | -61.4594 | 62.1506 | 0.15129 | 0.017092 | 0.013841 | 0.01296 | 0.064734 | 0.00030767 | 0.080758 | -58.4061 | 62.2101 | -61.7477 | -61.6882 | 54.2358 | 23.4787 | 8.1299 | 7.2784 | 62.1826 | -61.7752 | -0.28839 | 0.059509 | 3.0533 | -0.22888 | -7.9147 | -0.31586 | 0.032043 | 3.3417 | 69.5892 | 68.7378 | 115.6952 | 123.6694 | 3.0533 | 123.642 | 84.9381 | -0.31586 | 123.6694 | 3.0533 | 84.9381 | 115.6952 | 123.642 | -123.8983 | -123.9258
3886.7188 | 123.7244 | -61.4548 | 62.178 | 0.090256 | 0.016238 | 0.016191 | 0.011679 | 0.063452 | 0.0015893 | 0.080117 | -58.4061 | 62.2101 | -61.7294 | -61.6882 | 54.3045 | 23.5291 | 8.1619 | 7.3151 | 62.178 | -61.7889 | -0.27466 | 0.032043 | 3.0487 | -0.23346 | -7.8735 | -0.33417 | 0 | 3.3234 | 69.6167 | 68.7698 | 115.7593 | 123.6649 | 3.0487 | 123.6328 | 84.9838 | -0.33417 | 123.6649 | 3.0487 | 84.9838 | 115.7593 | 123.6328 | -123.9075 | -123.967
3887.7188 | 123.6969 | -61.4502 | 62.1643 | 0.082626 | 0.017947 | 0.012773 | 0.013815 | 0.062812 | -0.0024695 | 0.078408 | -58.3969 | 62.1826 | -61.7386 | -61.6882 | 54.2633 | 23.378 | 8.107 | 7.2876 | 62.1918 | -61.7752 | -0.28839 | 0.01831 | 3.0533 | -0.23804 | -7.901 | -0.32501 | 0.027465 | 3.3417 | 69.5572 | 68.7378 | 115.7135 | 123.6328 | 3.0533 | 123.642 | 84.8282 | -0.32501 | 123.6328 | 3.0533 | 84.8282 | 115.7135 | 123.642 | -123.9029 | -123.9395
3888.7188 | 123.8342 | -61.4319 | 62.1506 | 0.92186 | 0.014315 | 0.015122 | 0.0046292 | 0.063025 | 0.00073487 | 0.082894 | -58.3786 | 62.114 | -61.7294 | -61.6287 | 54.332 | 23.4604 | 8.0017 | 7.3929 | 62.1643 | -61.6974 | -0.29755 | -0.036621 | 3.0533 | -0.19684 | -7.8186 | -0.2655 | 0.013733 | 3.3508 | 69.4336 | 68.8248 | 115.7639 | 123.5458 | 3.0533 | 123.5962 | 84.8923 | -0.2655 | 123.5458 | 3.0533 | 84.8923 | 115.7639 | 123.5962 | -123.88 | -123.848
3889.7188 | 123.7564 | -61.4273 | 62.1918 | -0.069961 | 0.017733 | 0.017899 | 0.017447 | 0.06388 | -0.0016149 | 0.078622 | -58.3237 | 62.2055 | -61.7249 | -61.6287 | 54.2816 | 23.5245 | 8.0566 | 7.3425 | 62.1597 | -61.7798 | -0.29755 | 0.013733 | 3.1036 | -0.20142 | -7.9102 | -0.35248 | -0.032043 | 3.4012 | 69.4839 | 68.7698 | 115.7089 | 123.6328 | 3.1036 | 123.587 | 84.9518 | -0.35248 | 123.6328 | 3.1036 | 84.9518 | 115.7089 | 123.587 | -123.9166 | -123.9716
3890.7188 | 123.7427 | -61.4639 | 62.1597 | 0.12077 | 0.01816 | 0.0132 | 0.021505 | 0.06623 | -0.0035375 | 0.078195 | -58.4198 | 62.1964 | -61.7386 | -61.4822 | 54.1763 | 23.4375 | 8.2214 | 7.2922 | 62.178 | -61.7432 | -0.27466 | 0.036621 | 3.0441 | -0.018311 | -7.9834 | -0.27924 | 0.018311 | 3.3188 | 69.6854 | 68.7561 | 115.6403 | 123.6603 | 3.0441 | 123.642 | 84.9014 | -0.27924 | 123.6603 | 3.0441 | 84.9014 | 115.6403 | 123.642 | -123.8983 | -123.9029
3891.7188 | 123.7976 | -61.4594 | 62.1689 | 0.14366 | 0.017519 | 0.018327 | 0.013815 | 0.065161 | 9.4068e-05 | 0.083535 | -58.4381 | 62.1872 | -61.7615 | -61.8988 | 53.8788 | 23.2819 | 8.4503 | 7.2693 | 62.1918 | -61.7523 | -0.30212 | 0.018311 | 3.0212 | -0.43945 | -8.2901 | -0.29297 | 0.022888 | 3.3234 | 69.9097 | 68.7286 | 115.3381 | 123.6465 | 3.0212 | 123.6511 | 84.7412 | -0.29297 | 123.6465 | 3.0212 | 84.7412 | 115.3381 | 123.6511 | -123.9304 | -123.9212
3892.7188 | 123.7061 | -61.4456 | 62.1597 | 0.1284 | 0.017306 | 0.011491 | 0.014456 | 0.067725 | -0.0014013 | 0.079049 | -58.4244 | 62.2101 | -61.7615 | -61.6653 | 54.1855 | 23.5794 | 7.5577 | 7.2281 | 62.114 | -61.7935 | -0.31586 | 0.050354 | 3.0212 | -0.21973 | -7.9742 | -0.3479 | -0.045776 | 3.3371 | 69.0033 | 68.6737 | 115.6311 | 123.6557 | 3.0212 | 123.5596 | 85.025 | -0.3479 | 123.6557 | 3.0212 | 85.025 | 115.6311 | 123.5596 | -123.9212 | -123.9532
3893.7188 | 123.8571 | -61.3815 | 62.1506 | 0.04448 | 0.014315 | 0.014482 | 0.0046292 | 0.063666 | 0.00094847 | 0.080331 | -58.4106 | 62.1002 | -61.7432 | -61.6013 | 54.3915 | 23.6435 | 8.0109 | 7.4753 | 62.1597 | -61.6928 | -0.36163 | -0.050354 | 2.9709 | -0.21973 | -7.7591 | -0.31128 | 0.009155 | 3.3325 | 69.3924 | 68.8568 | 115.773 | 123.4818 | 2.9709 | 123.5413 | 85.025 | -0.31128 | 123.4818 | 2.9709 | 85.025 | 115.773 | 123.5413 | -123.8937 | -123.8434
3894.7188 | 123.7061 | -61.4548 | 62.178 | 0.12077 | 0.016238 | 0.016618 | 0.018942 | 0.062384 | -0.00033333 | 0.078622 | -58.3923 | 62.2192 | -61.7432 | -61.6882 | 54.2633 | 23.497 | 8.0841 | 7.3151 | 62.1643 | -61.7844 | -0.28839 | 0.041198 | 3.0624 | -0.23346 | -7.9147 | -0.32959 | -0.013733 | 3.3508 | 69.5389 | 68.7698 | 115.7181 | 123.674 | 3.0624 | 123.6191 | 84.9518 | -0.32959 | 123.674 | 3.0624 | 84.9518 | 115.7181 | 123.6191 | -123.9212 | -123.9624
3895.7188 | 123.7564 | -61.4456 | 62.1552 | -0.0012969 | 0.019656 | 0.017045 | 0.01766 | 0.062171 | -0.0028967 | 0.07969 | -58.3603 | 62.2284 | -61.7477 | -61.6333 | 54.2908 | 23.5245 | 8.0795 | 7.3517 | 62.2147 | -61.7523 | -0.30212 | 0.073243 | 3.0853 | -0.18768 | -7.8644 | -0.3067 | 0.05951 | 3.3875 | 69.5251 | 68.7973 | 115.7364 | 123.674 | 3.0853 | 123.6603 | 84.9701 | -0.3067 | 123.674 | 3.0853 | 84.9701 | 115.7364 | 123.6603 | -123.9029 | -123.9075
3896.7188 | 123.7198 | -61.4319 | 62.1689 | 0.04448 | 0.017733 | 0.014268 | 0.015524 | 0.065589 | -0.00011953 | 0.079263 | -58.3374 | 62.2192 | -61.7477 | -61.6425 | 54.2862 | 23.5794 | 8.0795 | 7.3517 | 62.2055 | -61.7569 | -0.31586 | 0.050354 | 3.0945 | -0.21057 | -7.8827 | -0.32501 | 0.036621 | 3.4103 | 69.5114 | 68.7836 | 115.7181 | 123.6511 | 3.0945 | 123.6374 | 85.0113 | -0.32501 | 123.6511 | 3.0945 | 85.0113 | 115.7181 | 123.6374 | -123.9166 | -123.9258
3897.7188 | 123.7518 | -61.4594 | 62.1185 | 0.43358 | 0.018801 | 0.011918 | 0.015097 | 0.065375 | 0.00073487 | 0.078835 | -58.4015 | 62.1918 | -61.7523 | -61.6791 | 54.2313 | 23.4833 | 8.0521 | 7.3059 | 62.2009 | -61.7661 | -0.29297 | 0.073242 | 3.0579 | -0.21973 | -7.8873 | -0.3067 | 0.082398 | 3.3508 | 69.5114 | 68.7653 | 115.6906 | 123.6511 | 3.0579 | 123.6603 | 84.9426 | -0.3067 | 123.6511 | 3.0579 | 84.9426 | 115.6906 | 123.6603 | -123.8708 | -123.8846
3898.7188 | 123.7839 | -61.441 | 62.1094 | 0.18944 | 0.017733 | 0.014909 | 0.013174 | 0.064093 | 9.4068e-05 | 0.081185 | -58.4015 | 62.178 | -61.734 | -61.6608 | 54.2816 | 23.5016 | 7.9742 | 7.3837 | 62.1643 | -61.7615 | -0.29297 | 0.068665 | 3.0396 | -0.21973 | -7.8278 | -0.32043 | 0.054932 | 3.3325 | 69.4153 | 68.8248 | 115.7227 | 123.6191 | 3.0396 | 123.6053 | 84.9426 | -0.32043 | 123.6191 | 3.0396 | 84.9426 | 115.7227 | 123.6053 | -123.8434 | -123.8708
3899.7188 | 123.7518 | -61.4365 | 62.1506 | 0.10551 | 0.019869 | 0.014054 | 0.01232 | 0.059394 | -0.0018285 | 0.080331 | -58.4335 | 62.2009 | -61.7477 | -61.7477 | 54.245 | 23.584 | 7.9971 | 7.3242 | 62.1918 | -61.7706 | -0.31128 | 0.050354 | 3.0029 | -0.31128 | -7.9056 | -0.33417 | 0.041198 | 3.3142 | 69.4336 | 68.7607 | 115.6815 | 123.6374 | 3.0029 | 123.6282 | 85.0204 | -0.33417 | 123.6374 | 3.0029 | 85.0204 | 115.6815 | 123.6282 | -123.8983 | -123.9212
3900.7188 | 123.7106 | -61.4502 | 62.1643 | 0.15892 | 0.018801 | 0.013627 | 0.012533 | 0.071357 | 0.0015893 | 0.079476 | -58.4427 | 62.1964 | -61.7661 | -61.5784 | 54.6341 | 23.5336 | 8.0292 | 7.4799 | 62.233 | -61.7935 | -0.31586 | 0.032043 | 3.0075 | -0.12817 | -7.5302 | -0.34332 | 0.068664 | 3.3234 | 69.4794 | 68.9301 | 116.0843 | 123.6465 | 3.0075 | 123.6832 | 84.9838 | -0.34332 | 123.6465 | 3.0075 | 84.9838 | 116.0843 | 123.6832 | -123.9304 | -123.9578
3901.7188 | 123.7564 | -61.441 | 62.1964 | 0.11314 | 0.017092 | 0.016618 | 0.013815 | 0.063666 | -0.0011877 | 0.080331 | -58.4518 | 62.2009 | -61.7615 | -61.6196 | 53.952 | 23.1171 | 8.4641 | 7.4799 | 62.1689 | -61.7798 | -0.32043 | 0.004578 | 2.9892 | -0.17853 | -8.2443 | -0.33874 | -0.027466 | 3.3096 | 69.9051 | 68.9209 | 115.3931 | 123.642 | 2.9892 | 123.6099 | 84.5581 | -0.33874 | 123.642 | 2.9892 | 84.5581 | 115.3931 | 123.6099 | -123.9578 | -123.9761
3902.7188 | 123.7564 | -61.4456 | 62.1597 | 0.0063326 | 0.017947 | 0.016831 | 0.013388 | 0.064307 | -0.0022559 | 0.080544 | -58.3923 | 62.2101 | -61.7477 | -61.6745 | 54.3274 | 23.4192 | 8.1116 | 7.3792 | 62.1826 | -61.7386 | -0.30212 | 0.050354 | 3.0533 | -0.22888 | -7.8323 | -0.29297 | 0.022888 | 3.3554 | 69.5572 | 68.8248 | 115.773 | 123.6557 | 3.0533 | 123.6282 | 84.8648 | -0.29297 | 123.6557 | 3.0533 | 84.8648 | 115.773 | 123.6282 | -123.9075 | -123.8983
3903.7188 | 123.8251 | -61.4136 | 62.1414 | 0.18181 | 0.016878 | 0.017259 | 0.011251 | 0.064307 | -0.0011877 | 0.079263 | -58.4015 | 62.114 | -61.7615 | -61.6058 | 54.3869 | 23.4787 | 7.9788 | 7.5897 | 62.1323 | -61.7432 | -0.3479 | -0.027465 | 3.0121 | -0.19226 | -7.7545 | -0.32959 | -0.009155 | 3.36 | 69.3924 | 69.0033 | 115.8005 | 123.5275 | 3.0121 | 123.5458 | 84.8923 | -0.32959 | 123.5275 | 3.0121 | 84.8923 | 115.8005 | 123.5458 | -123.9029 | -123.8846
3904.7188 | 123.7701 | -61.4594 | 62.1552 | 0.16655 | 0.017519 | 0.01555 | 0.012747 | 0.063666 | -0.00033333 | 0.079904 | -58.429 | 62.1918 | -61.7661 | -61.6562 | 54.3137 | 23.4787 | 8.0612 | 7.3837 | 62.1597 | -61.7569 | -0.3067 | 0.036621 | 3.0304 | -0.19684 | -7.8415 | -0.29755 | 0.004578 | 3.3371 | 69.5206 | 68.8431 | 115.773 | 123.6511 | 3.0304 | 123.6191 | 84.9381 | -0.29755 | 123.6511 | 3.0304 | 84.9381 | 115.773 | 123.6191 | -123.9212 | -123.912
3905.7188 | 123.7656 | -61.4548 | 62.1323 | 0.13603 | 0.016665 | 0.018327 | 0.014029 | 0.063452 | 0.00094847 | 0.080758 | -58.4198 | 62.1552 | -61.7432 | -61.6745 | 54.2725 | 23.5565 | 8.1299 | 7.4982 | 62.1597 | -61.7615 | -0.28839 | 0.022888 | 3.035 | -0.21973 | -7.8598 | -0.3067 | 0.027466 | 3.3234 | 69.5847 | 68.9529 | 115.7272 | 123.6099 | 3.035 | 123.6145 | 85.0113 | -0.3067 | 123.6099 | 3.035 | 85.0113 | 115.7272 | 123.6145 | -123.8754 | -123.8937
3906.7188 | 123.7381 | -61.4685 | 62.146 | 0.052109 | 0.018374 | 0.014909 | 0.014242 | 0.063452 | 0.00030767 | 0.078408 | -58.4152 | 62.1826 | -61.7569 | -61.6791 | 54.3045 | 23.5016 | 8.139 | 7.5256 | 62.1735 | -61.7706 | -0.28839 | 0.036621 | 3.0533 | -0.21057 | -7.8415 | -0.30212 | 0.027466 | 3.3417 | 69.6075 | 68.9941 | 115.773 | 123.6511 | 3.0533 | 123.642 | 84.9701 | -0.30212 | 123.6511 | 3.0533 | 84.9701 | 115.773 | 123.642 | -123.9029 | -123.9166
3907.7188 | 123.7518 | -61.441 | 62.1506 | 0.31151 | 0.014101 | 0.015763 | 0.013601 | 0.064093 | 0.00073487 | 0.081185 | -58.4106 | 62.1735 | -61.7432 | -61.6653 | 54.3594 | 23.3505 | 8.1253 | 7.5211 | 62.178 | -61.7569 | -0.30212 | 0.022888 | 3.0304 | -0.2243 | -7.7911 | -0.31586 | 0.027466 | 3.3325 | 69.5663 | 68.9621 | 115.8005 | 123.6145 | 3.0304 | 123.6191 | 84.7916 | -0.31586 | 123.6145 | 3.0304 | 84.7916 | 115.8005 | 123.6191 | -123.8937 | -123.9075
3908.7188 | 123.8342 | -61.4182 | 62.1094 | 0.11314 | 0.016238 | 0.0132 | 0.0093288 | 0.062384 | -0.00033333 | 0.080758 | -58.3511 | 62.0911 | -61.7157 | -61.5967 | 54.4281 | 23.3185 | 8.0017 | 7.6309 | 62.1323 | -61.7065 | -0.29755 | -0.018311 | 3.067 | -0.17853 | -7.6813 | -0.28839 | 0.022888 | 3.3646 | 69.4199 | 69.0491 | 115.8463 | 123.5092 | 3.067 | 123.5504 | 84.7366 | -0.28839 | 123.5092 | 3.067 | 84.7366 | 115.8463 | 123.5504 | -123.8251 | -123.8159
3909.7188 | 123.7335 | -61.4502 | 62.1643 | 0.074997 | 0.015169 | 0.01085 | 0.015738 | 0.063452 | 0.00094847 | 0.080331 | -58.4152 | 62.2284 | -61.7386 | -61.6974 | 54.245 | 23.2361 | 8.2214 | 7.5485 | 62.1506 | -61.7844 | -0.28839 | 0.064087 | 3.035 | -0.24719 | -7.9193 | -0.33417 | -0.013733 | 3.3234 | 69.6716 | 68.9987 | 115.6952 | 123.6786 | 3.035 | 123.6008 | 84.6863 | -0.33417 | 123.6786 | 3.035 | 84.6863 | 115.6952 | 123.6008 | -123.9029 | -123.9487
3910.7188 | 123.761 | -61.4548 | 62.1872 | 0.10551 | 0.01816 | 0.015122 | 0.014456 | 0.063025 | -0.0014013 | 0.080117 | -58.429 | 62.1735 | -61.7477 | -61.6745 | 54.2679 | 23.3368 | 8.1894 | 7.5394 | 62.1918 | -61.7798 | -0.29297 | -0.013733 | 3.0258 | -0.21973 | -7.9193 | -0.32501 | 0.004577 | 3.3188 | 69.6442 | 68.9941 | 115.7227 | 123.6282 | 3.0258 | 123.6465 | 84.7916 | -0.32501 | 123.6282 | 3.0258 | 84.7916 | 115.7227 | 123.6465 | -123.9349 | -123.967
3911.7188 | 123.8342 | -61.4594 | 62.114 | 0.21233 | 0.016024 | 0.011918 | 0.012747 | 0.062812 | 0.0011621 | 0.07969 | -58.4106 | 62.1689 | -61.7569 | -61.6333 | 54.3503 | 23.4375 | 7.9834 | 7.3425 | 62.178 | -61.7523 | -0.29755 | 0.054931 | 3.0487 | -0.17395 | -7.7637 | -0.29297 | 0.064087 | 3.3463 | 69.4427 | 68.8019 | 115.8096 | 123.6282 | 3.0487 | 123.6374 | 84.8969 | -0.29297 | 123.6282 | 3.0487 | 84.8969 | 115.8096 | 123.6374 | -123.8709 | -123.8663
3912.7188 | 123.7747 | -61.4456 | 62.1368 | 0.13603 | 0.018374 | 0.015336 | 0.014029 | 0.064093 | 0.00030767 | 0.079476 | -58.4015 | 62.1597 | -61.7432 | -61.6516 | 54.3228 | 23.4146 | 8.0383 | 7.4203 | 62.1872 | -61.7661 | -0.29755 | 0.022888 | 3.0441 | -0.20599 | -7.814 | -0.32043 | 0.050354 | 3.3417 | 69.4839 | 68.866 | 115.7684 | 123.6053 | 3.0441 | 123.6328 | 84.8602 | -0.32043 | 123.6053 | 3.0441 | 84.8602 | 115.7684 | 123.6328 | -123.88 | -123.9029
3913.7344 | 123.8617 | -61.4044 | 62.1643 | -0.054703 | 0.015383 | 0.011064 | 0.0056972 | 0.062812 | 0.0018031 | 0.080758 | -58.3969 | 62.0819 | -61.702 | -61.5967 | 54.4144 | 23.4879 | 7.6492 | 6.5414 | 62.1689 | -61.6974 | -0.29755 | -0.082398 | 3.0075 | -0.19226 | -7.7499 | -0.29297 | 0.004577 | 3.3051 | 69.0537 | 67.9459 | 115.8188 | 123.4863 | 3.0075 | 123.5733 | 84.8923 | -0.29297 | 123.4863 | 3.0075 | 84.8923 | 115.8188 | 123.5733 | -123.8663 | -123.8617
3914.7188 | 123.8022 | -61.4227 | 62.1552 | 0.15892 | 0.018801 | 0.014695 | 0.014669 | 0.062598 | -0.0011877 | 0.080544 | -58.3832 | 62.1735 | -61.7157 | -61.6287 | 54.3457 | 23.4558 | 7.6309 | 6.3812 | 62.1414 | -61.7569 | -0.29297 | 0.018311 | 3.0395 | -0.20599 | -7.8094 | -0.33417 | -0.013733 | 3.3325 | 69.0536 | 67.804 | 115.7684 | 123.5962 | 3.0395 | 123.5641 | 84.8785 | -0.33417 | 123.5962 | 3.0395 | 84.8785 | 115.7684 | 123.5641 | -123.8708 | -123.912
3915.7188 | 123.7793 | -61.4273 | 62.1414 | 0.17418 | 0.01581 | 0.017259 | 0.015738 | 0.062384 | -0.00011953 | 0.080117 | -58.4427 | 62.1918 | -61.7203 | -61.6379 | 54.3274 | 23.4467 | 7.6263 | 6.4041 | 62.1826 | -61.7523 | -0.29297 | 0.050354 | 2.9846 | -0.21057 | -7.814 | -0.32501 | 0.041199 | 3.2776 | 69.0537 | 67.8314 | 115.7547 | 123.6191 | 2.9846 | 123.6099 | 84.874 | -0.32501 | 123.6191 | 2.9846 | 84.874 | 115.7547 | 123.6099 | -123.8617 | -123.8937
3916.7188 | 123.7335 | -61.4273 | 62.146 | 0.2047 | 0.016878 | 0.013841 | 0.015951 | 0.060889 | 0.00073487 | 0.080972 | -58.4152 | 62.1964 | -61.7935 | -61.7065 | 54.451 | 23.4055 | 8.0933 | 7.5211 | 62.1918 | -61.7661 | -0.36621 | 0.050354 | 3.0121 | -0.27924 | -7.695 | -0.33875 | 0.045776 | 3.3783 | 69.5206 | 68.9484 | 115.8783 | 123.6237 | 3.0121 | 123.6191 | 84.8328 | -0.33875 | 123.6237 | 3.0121 | 84.8328 | 115.8783 | 123.6191 | -123.9395 | -123.912
3917.7188 | 123.7244 | -61.4502 | 62.1689 | 0.13603 | 0.016878 | 0.014695 | 0.011892 | 0.05918 | -0.0020421 | 0.080544 | -58.3786 | 62.178 | -61.7294 | -61.6745 | 54.4098 | 23.3688 | 7.7454 | 6.5872 | 62.2101 | -61.7432 | -0.27924 | 0.009156 | 3.0716 | -0.22431 | -7.7591 | -0.29297 | 0.041199 | 3.3508 | 69.1956 | 68.0374 | 115.86 | 123.6282 | 3.0716 | 123.6603 | 84.819 | -0.29297 | 123.6282 | 3.0716 | 84.819 | 115.86 | 123.6603 | -123.8983 | -123.912
3918.7188 | 123.8113 | -61.4044 | 62.1597 | -0.069961 | 0.014315 | 0.010636 | 0.004202 | 0.059607 | -0.0014013 | 0.079476 | -58.4335 | 62.0819 | -61.7294 | -61.6013 | 54.3823 | 23.5016 | 8.107 | 7.6447 | 62.1826 | -61.702 | -0.32501 | -0.07782 | 2.9709 | -0.19684 | -7.7774 | -0.29755 | 0.022888 | 3.2959 | 69.5114 | 69.0491 | 115.7867 | 123.4863 | 2.9709 | 123.587 | 84.906 | -0.29755 | 123.4863 | 2.9709 | 84.906 | 115.7867 | 123.587 | -123.8892 | -123.8617
3919.7188 | 123.8525 | -61.4182 | 62.1231 | 0.18944 | 0.014742 | 0.013413 | 0.01232 | 0.061743 | -0.0011877 | 0.079263 | -58.3145 | 62.114 | -61.734 | -61.5829 | 54.4373 | 23.4833 | 7.9971 | 7.6126 | 62.1094 | -61.7432 | -0.31586 | -0.009155 | 3.1036 | -0.16479 | -7.6859 | -0.32501 | -0.013733 | 3.4195 | 69.4153 | 69.0308 | 115.8554 | 123.5321 | 3.1036 | 123.5275 | 84.9014 | -0.32501 | 123.5321 | 3.1036 | 84.9014 | 115.8554 | 123.5275 | -123.8571 | -123.8663
3920.7188 | 123.848 | -61.4044 | 62.1414 | 0.15892 | 0.01581 | 0.011277 | 0.0091152 | 0.06153 | 9.4068e-05 | 0.080758 | -58.3511 | 62.1002 | -61.734 | -61.5921 | 54.4281 | 23.5428 | 7.7042 | 6.752 | 62.1094 | -61.734 | -0.32959 | -0.041198 | 3.0533 | -0.18768 | -7.7133 | -0.32959 | -0.032043 | 3.3829 | 69.1086 | 68.1564 | 115.8325 | 123.5046 | 3.0533 | 123.5138 | 84.9472 | -0.32959 | 123.5046 | 3.0533 | 84.9472 | 115.8325 | 123.5138 | -123.8754 | -123.8754
3921.7188 | 123.88 | -61.4136 | 62.146 | 0.16655 | 0.016024 | 0.014909 | 0.013815 | 0.061957 | -0.00076053 | 0.078195 | -58.3466 | 62.1094 | -61.7203 | -61.5646 | 54.4006 | 23.4833 | 7.695 | 6.8161 | 62.1231 | -61.7294 | -0.3067 | -0.036621 | 3.067 | -0.15106 | -7.7454 | -0.31586 | -0.022888 | 3.3737 | 69.1086 | 68.2297 | 115.8142 | 123.5229 | 3.067 | 123.5367 | 84.8969 | -0.31586 | 123.5229 | 3.067 | 84.8969 | 115.8142 | 123.5367 | -123.8663 | -123.8754
3922.7188 | 123.8342 | -61.4182 | 62.1002 | 0.16655 | 0.018587 | 0.013627 | 0.014029 | 0.062812 | 0.0018031 | 0.080331 | -58.3282 | 62.114 | -61.7294 | -61.5738 | 54.4235 | 23.4787 | 8.0429 | 7.6538 | 62.1231 | -61.734 | -0.31128 | 0.013733 | 3.0899 | -0.15564 | -7.6767 | -0.31586 | 0.022888 | 3.4012 | 69.4611 | 69.072 | 115.8417 | 123.5321 | 3.0899 | 123.5413 | 84.8969 | -0.31586 | 123.5321 | 3.0899 | 84.8969 | 115.8417 | 123.5413 | -123.8297 | -123.8342
3923.7344 | 124.0219 | -61.3495 | 62.2009 | -0.16151 | 0.01581 | 0.015763 | 0.0089016 | 0.059821 | -0.00054693 | 0.082681 | -58.3328 | 62.0956 | -61.7065 | -61.496 | 54.5105 | 23.6938 | 8.1207 | 7.7637 | 62.1414 | -61.6928 | -0.35706 | -0.10529 | 3.0167 | -0.14648 | -7.6904 | -0.34332 | -0.05951 | 3.3737 | 69.4702 | 69.1132 | 115.86 | 123.4451 | 3.0167 | 123.4909 | 85.0433 | -0.34332 | 123.4451 | 3.0167 | 85.0433 | 115.86 | 123.4909 | -123.9075 | -123.8937
3924.7188 | 123.8388 | -61.4044 | 62.1368 | 0.24284 | 0.015383 | 0.011491 | 0.015738 | 0.060034 | 9.4068e-05 | 0.077981 | -58.3557 | 62.1185 | -61.734 | -61.5646 | 54.3961 | 23.5336 | 8.0429 | 7.6401 | 62.1277 | -61.7432 | -0.32959 | -0.018311 | 3.0487 | -0.16022 | -7.7408 | -0.33875 | -0.009155 | 3.3783 | 69.4473 | 69.0445 | 115.8005 | 123.5229 | 3.0487 | 123.5321 | 84.938 | -0.33875 | 123.5229 | 3.0487 | 84.938 | 115.8005 | 123.5321 | -123.8708 | -123.88
3925.7188 | 123.8617 | -61.409 | 62.1048 | 0.24284 | 0.016878 | 0.014054 | 0.010824 | 0.063025 | -0.00097413 | 0.07969 | -58.2779 | 62.0728 | -61.7569 | -61.5189 | 54.3823 | 23.4375 | 8.0658 | 7.6767 | 62.0956 | -61.7111 | -0.3479 | -0.032043 | 3.1311 | -0.10986 | -7.7225 | -0.30212 | -0.009155 | 3.479 | 69.4748 | 69.0857 | 115.7913 | 123.4818 | 3.1311 | 123.5046 | 84.8465 | -0.30212 | 123.4818 | 3.1311 | 84.8465 | 115.7913 | 123.5046 | -123.8617 | -123.8159
3926.7188 | 123.8983 | -61.3998 | 62.1048 | 0.23521 | 0.016024 | 0.012773 | 0.01531 | 0.061743 | -0.0011877 | 0.078408 | -58.3328 | 62.0773 | -61.7111 | -61.4868 | 54.3961 | 23.7946 | 8.075 | 7.6447 | 62.1185 | -61.6837 | -0.31128 | -0.027465 | 3.067 | -0.086975 | -7.7087 | -0.28381 | 0.013733 | 3.3783 | 69.4748 | 69.0445 | 115.7959 | 123.4772 | 3.067 | 123.5184 | 85.1944 | -0.28381 | 123.4772 | 3.067 | 85.1944 | 115.7959 | 123.5184 | -123.8159 | -123.7885
3927.7188 | 123.848 | -61.3998 | 62.1506 | 0.24284 | 0.016024 | 0.013413 | 0.013815 | 0.062598 | 0.0035121 | 0.081399 | -58.3099 | 62.1277 | -61.7249 | -61.7157 | 54.6066 | 23.8266 | 7.6996 | 6.9122 | 62.1048 | -61.702 | -0.32501 | -0.022888 | 3.0899 | -0.31586 | -7.5439 | -0.30212 | -0.045777 | 3.4149 | 69.0994 | 68.3121 | 116.0065 | 123.5275 | 3.0899 | 123.5046 | 85.2264 | -0.30212 | 123.5275 | 3.0899 | 85.2264 | 116.0065 | 123.5046 | -123.8754 | -123.8525
3928.7188 | 123.8342 | -61.3815 | 62.1506 | 0.2047 | 0.017733 | 0.014695 | 0.014669 | 0.062812 | -0.00033333 | 0.080758 | -58.2962 | 62.1094 | -61.7386 | -61.5417 | 54.5334 | 23.5382 | 7.5165 | 7.1182 | 62.0728 | -61.7386 | -0.35705 | -0.041199 | 3.0853 | -0.16022 | -7.6172 | -0.35705 | -0.07782 | 3.4424 | 68.898 | 68.4998 | 115.9149 | 123.4909 | 3.0853 | 123.4543 | 84.9197 | -0.35705 | 123.4909 | 3.0853 | 84.9197 | 115.9149 | 123.4543 | -123.8892 | -123.8892
3929.7188 | 123.8205 | -61.4319 | 62.1094 | 0.18944 | 0.015597 | 0.013627 | 0.013174 | 0.061316 | -0.0022559 | 0.077981 | -58.3191 | 62.1185 | -61.7157 | -61.5555 | 54.5975 | 23.7213 | 7.7637 | 6.9077 | 62.114 | -61.7111 | -0.28381 | 0.009155 | 3.1128 | -0.1236 | -7.5119 | -0.27924 | 0.004578 | 3.3966 | 69.1956 | 68.3395 | 116.0294 | 123.5504 | 3.1128 | 123.5458 | 85.1532 | -0.27924 | 123.5504 | 3.1128 | 85.1532 | 116.0294 | 123.5458 | -123.8251 | -123.8205
3930.7188 | 123.793 | -61.441 | 62.1414 | 0.18181 | 0.016878 | 0.014695 | 0.016165 | 0.062171 | -0.0016149 | 0.080117 | -58.3603 | 62.1689 | -61.7523 | -61.6196 | 54.451 | 23.5703 | 7.8644 | 6.839 | 62.1323 | -61.7523 | -0.31128 | 0.027466 | 3.0807 | -0.17853 | -7.6904 | -0.31128 | -0.009155 | 3.392 | 69.3054 | 68.28 | 115.892 | 123.6099 | 3.0807 | 123.5733 | 85.0113 | -0.31128 | 123.6099 | 3.0807 | 85.0113 | 115.892 | 123.5733 | -123.8937 | -123.8937
3931.7188 | 123.8754 | -61.4182 | 62.1323 | 0.18181 | 0.016451 | 0.010209 | 0.012747 | 0.062384 | 0.00052127 | 0.080758 | -58.3054 | 62.1277 | -61.7111 | -61.5509 | 54.4693 | 23.6664 | 7.8003 | 6.871 | 62.1048 | -61.7386 | -0.29297 | -0.004577 | 3.1128 | -0.13275 | -7.663 | -0.32043 | -0.027466 | 3.4058 | 69.2184 | 68.2892 | 115.8875 | 123.5458 | 3.1128 | 123.5229 | 85.0845 | -0.32043 | 123.5458 | 3.1128 | 85.0845 | 115.8875 | 123.5229 | -123.8434 | -123.8708
3932.7188 | 123.8434 | -61.3861 | 62.114 | -0.23781 | 0.015169 | 0.014909 | 0.010824 | 0.062384 | -0.00011953 | 0.081399 | -58.3328 | 62.1048 | -61.7157 | -61.5463 | 54.5059 | 23.5794 | 7.8094 | 6.8939 | 62.1231 | -61.702 | -0.32959 | -0.009156 | 3.0533 | -0.16022 | -7.608 | -0.31586 | 0.009155 | 3.3829 | 69.1956 | 68.28 | 115.892 | 123.4909 | 3.0533 | 123.5092 | 84.9655 | -0.31586 | 123.4909 | 3.0533 | 84.9655 | 115.892 | 123.5092 | -123.8297 | -123.8159
3933.7188 | 123.8709 | -61.3907 | 62.1277 | -0.054703 | 0.013247 | 0.0097818 | 0.0071926 | 0.058966 | -0.00097413 | 0.079049 | -58.3511 | 62.0865 | -61.7065 | -61.5372 | 54.451 | 23.5428 | 7.8644 | 6.958 | 62.1277 | -61.7111 | -0.31586 | -0.041199 | 3.0396 | -0.14648 | -7.6767 | -0.32043 | 0 | 3.3554 | 69.2551 | 68.3487 | 115.8417 | 123.4772 | 3.0396 | 123.5184 | 84.9335 | -0.32043 | 123.4772 | 3.0396 | 84.9335 | 115.8417 | 123.5184 | -123.8342 | -123.8388
3934.7188 | 123.8525 | -61.3953 | 62.1185 | 0.16655 | 0.015597 | 0.012986 | 0.013174 | 0.058966 | -0.00054693 | 0.080972 | -58.287 | 62.0956 | -61.6974 | -61.5784 | 54.4281 | 23.5428 | 7.7637 | 6.9534 | 62.1048 | -61.7203 | -0.30212 | -0.022888 | 3.1082 | -0.18311 | -7.6904 | -0.32501 | -0.013733 | 3.4103 | 69.1589 | 68.3487 | 115.8234 | 123.4909 | 3.1082 | 123.5001 | 84.9381 | -0.32501 | 123.4909 | 3.1082 | 84.9381 | 115.8234 | 123.5001 | -123.8159 | -123.8388
3935.7188 | 123.8342 | -61.4044 | 62.1368 | 0.16655 | 0.015169 | 0.011277 | 0.011679 | 0.05918 | -0.0020421 | 0.079049 | -58.3191 | 62.0819 | -61.7157 | -61.5601 | 54.3823 | 23.4879 | 7.7957 | 6.9168 | 62.1048 | -61.702 | -0.31128 | -0.054932 | 3.0853 | -0.15564 | -7.7545 | -0.29755 | -0.032044 | 3.3966 | 69.2001 | 68.3212 | 115.7867 | 123.4863 | 3.0853 | 123.5092 | 84.8923 | -0.29755 | 123.4863 | 3.0853 | 84.8923 | 115.7867 | 123.5092 | -123.8525 | -123.8388
3936.7188 | 123.8434 | -61.4456 | 62.1368 | 0.23521 | 0.016451 | 0.017686 | 0.016378 | 0.058966 | 9.4068e-05 | 0.081399 | -58.3557 | 62.146 | -61.734 | -61.615 | 54.3732 | 23.5428 | 7.8598 | 6.8939 | 62.1231 | -61.7523 | -0.28839 | 0.009155 | 3.0899 | -0.16937 | -7.7637 | -0.3067 | -0.013733 | 3.3783 | 69.3054 | 68.3395 | 115.8188 | 123.5916 | 3.0899 | 123.5687 | 84.9884 | -0.3067 | 123.5916 | 3.0899 | 84.9884 | 115.8188 | 123.5687 | -123.8708 | -123.8892
3937.7188 | 123.793 | -61.4227 | 62.1552 | 0.18181 | 0.01581 | 0.012986 | 0.014029 | 0.060462 | -0.00054693 | 0.080758 | -58.3694 | 62.1552 | -61.7294 | -61.6104 | 54.3777 | 23.7762 | 7.8781 | 6.8436 | 62.1597 | -61.734 | -0.3067 | 0 | 3.0533 | -0.18768 | -7.7774 | -0.31128 | 0.004578 | 3.36 | 69.3008 | 68.2663 | 115.8005 | 123.5779 | 3.0533 | 123.5825 | 85.199 | -0.31128 | 123.5779 | 3.0533 | 85.199 | 115.8005 | 123.5825 | -123.8846 | -123.8892
3938.7188 | 123.8342 | -61.3953 | 62.1506 | 0.029221 | 0.014742 | 0.0093546 | 0.0071926 | 0.060675 | -0.00076053 | 0.080972 | -58.3878 | 62.0728 | -61.7203 | -61.6013 | 54.4373 | 23.5519 | 7.8781 | 6.9214 | 62.1185 | -61.702 | -0.32501 | -0.07782 | 3.0075 | -0.20599 | -7.7133 | -0.3067 | -0.032044 | 3.3325 | 69.2734 | 68.3167 | 115.8325 | 123.468 | 3.0075 | 123.5138 | 84.9472 | -0.3067 | 123.468 | 3.0075 | 84.9472 | 115.8325 | 123.5138 | -123.8708 | -123.8525
3939.7188 | 123.8709 | -61.4182 | 62.1231 | 0.25047 | 0.016451 | 0.01854 | 0.014029 | 0.061316 | -0.00076053 | 0.079904 | -58.4015 | 62.0956 | -61.7432 | -61.5555 | 54.3961 | 23.6893 | 7.814 | 6.926 | 62.1094 | -61.7111 | -0.32501 | -0.027466 | 3.0167 | -0.13733 | -7.7271 | -0.29297 | -0.013733 | 3.3417 | 69.2322 | 68.3441 | 115.8142 | 123.5138 | 3.0167 | 123.5275 | 85.1074 | -0.29297 | 123.5138 | 3.0167 | 85.1074 | 115.8142 | 123.5275 | -123.8663 | -123.8342
3940.7188 | 123.8571 | -61.3907 | 62.1552 | 0.12077 | 0.017519 | 0.014268 | 0.015738 | 0.060889 | -0.00054693 | 0.078622 | -58.3008 | 62.1094 | -61.7157 | -61.7569 | 54.5425 | 23.735 | 7.7683 | 6.9443 | 62.114 | -61.7065 | -0.32501 | -0.045776 | 3.0899 | -0.36621 | -7.6126 | -0.31586 | -0.041198 | 3.4149 | 69.1589 | 68.335 | 115.9332 | 123.5001 | 3.0899 | 123.5046 | 85.1257 | -0.31586 | 123.5001 | 3.0899 | 85.1257 | 115.9332 | 123.5046 | -123.8708 | -123.8617
3941.7188 | 123.8983 | -61.441 | 62.1231 | 0.18181 | 0.014742 | 0.015336 | 0.014456 | 0.06388 | -0.0018285 | 0.080331 | -58.3008 | 62.114 | -61.7157 | -61.5417 | 54.3961 | 23.5657 | 7.8049 | 6.8939 | 62.0956 | -61.734 | -0.27466 | -0.009155 | 3.1403 | -0.10071 | -7.7271 | -0.29297 | -0.027466 | 3.4149 | 69.2459 | 68.335 | 115.8371 | 123.555 | 3.1403 | 123.5367 | 85.0067 | -0.29297 | 123.555 | 3.1403 | 85.0067 | 115.8371 | 123.5367 | -123.8388 | -123.8571
3942.7188 | 123.8754 | -61.409 | 62.1048 | 0.15892 | 0.017092 | 0.0132 | 0.014883 | 0.06153 | -0.00054693 | 0.079263 | -58.3008 | 62.146 | -61.6882 | -61.5509 | 54.4418 | 23.6389 | 7.8323 | 6.9534 | 62.0911 | -61.7157 | -0.27923 | 0.041199 | 3.1082 | -0.14191 | -7.663 | -0.3067 | -0.013733 | 3.3875 | 69.2413 | 68.3624 | 115.8508 | 123.555 | 3.1082 | 123.5001 | 85.0479 | -0.3067 | 123.555 | 3.1082 | 85.0479 | 115.8508 | 123.5001 | -123.793 | -123.8205
3943.7188 | 123.8113 | -61.3998 | 62.1552 | 0.059738 | 0.01282 | 0.010209 | 0.0076198 | 0.05918 | 0.0011621 | 0.081613 | -58.3786 | 62.059 | -61.7386 | -61.6058 | 54.3777 | 23.4558 | 8.2031 | 7.6126 | 62.1185 | -61.6974 | -0.33874 | -0.09613 | 3.0212 | -0.20599 | -7.7774 | -0.29755 | -0.036621 | 3.36 | 69.603 | 69.0125 | 115.7776 | 123.4589 | 3.0212 | 123.5184 | 84.8557 | -0.29755 | 123.4589 | 3.0212 | 84.8557 | 115.7776 | 123.5184 | -123.8937 | -123.8525
3944.7188 | 123.7701 | -61.4273 | 62.1643 | 0.14366 | 0.017092 | 0.014909 | 0.016165 | 0.060889 | -0.00097413 | 0.079263 | -58.3649 | 62.1597 | -61.7569 | -61.6425 | 54.3365 | 23.4283 | 7.9697 | 6.9031 | 62.1414 | -61.7569 | -0.32959 | -0.004578 | 3.0624 | -0.21515 | -7.8278 | -0.32959 | -0.022889 | 3.392 | 69.397 | 68.3304 | 115.7639 | 123.587 | 3.0624 | 123.5687 | 84.8557 | -0.32959 | 123.587 | 3.0624 | 84.8557 | 115.7639 | 123.5687 | -123.9212 | -123.9212
3945.7188 | 123.8571 | -61.3724 | 62.1414 | 0.23521 | 0.01581 | 0.014268 | 0.014029 | 0.064307 | 0.0018031 | 0.081613 | -58.3054 | 62.1231 | -61.7203 | -61.7523 | 54.4922 | 23.7305 | 7.814 | 7.0358 | 62.1277 | -61.7203 | -0.3479 | -0.01831 | 3.067 | -0.37994 | -7.6492 | -0.3479 | -0.013732 | 3.4149 | 69.1864 | 68.4082 | 115.8646 | 123.4955 | 3.067 | 123.5001 | 85.1028 | -0.3479 | 123.4955 | 3.067 | 85.1028 | 115.8646 | 123.5001 | -123.8617 | -123.8617
3946.7344 | 123.8983 | -61.3953 | 62.1323 | -0.08522 | 0.016878 | 0.01085 | 0.0091152 | 0.060248 | -0.0014013 | 0.080972 | -58.3374 | 62.1094 | -61.7157 | -61.5234 | 54.4601 | 23.6481 | 7.8735 | 7.0908 | 62.1277 | -61.6653 | -0.32043 | -0.022888 | 3.0579 | -0.12817 | -7.6721 | -0.27008 | -0.004577 | 3.3783 | 69.2688 | 68.486 | 115.8554 | 123.5046 | 3.0579 | 123.5229 | 85.0433 | -0.27008 | 123.5046 | 3.0579 | 85.0433 | 115.8554 | 123.5229 | -123.848 | -123.7976
3947.7188 | 123.848 | -61.3998 | 62.1185 | 0.16655 | 0.016024 | 0.011918 | 0.017233 | 0.061316 | -0.0033239 | 0.080758 | -58.3145 | 62.114 | -61.7157 | -61.5601 | 54.4739 | 23.6984 | 7.8278 | 6.9946 | 62.1002 | -61.7203 | -0.31586 | -0.004577 | 3.0853 | -0.16022 | -7.6447 | -0.32043 | -0.01831 | 3.4012 | 69.2276 | 68.3945 | 115.8737 | 123.5138 | 3.0853 | 123.5001 | 85.0983 | -0.32043 | 123.5138 | 3.0853 | 85.0983 | 115.8737 | 123.5001 | -123.8342 | -123.8388
3948.7188 | 123.8388 | -61.4044 | 62.114 | -0.7032 | 0.016878 | 0.012345 | 0.011679 | 0.059607 | 0.00073487 | 0.081185 | -58.3557 | 62.1185 | -61.6837 | -61.5738 | 54.4693 | 23.6801 | 7.8323 | 6.9763 | 62.1094 | -61.7203 | -0.27924 | 0.004577 | 3.0487 | -0.16937 | -7.6447 | -0.31586 | -0.004578 | 3.3279 | 69.2368 | 68.3807 | 115.8737 | 123.5229 | 3.0487 | 123.5138 | 85.0845 | -0.31586 | 123.5229 | 3.0487 | 85.0845 | 115.8737 | 123.5138 | -123.7976 | -123.8342
3949.7188 | 123.8663 | -61.4136 | 62.1231 | 0.15129 | 0.014101 | 0.016831 | 0.014883 | 0.062384 | 0.0018031 | 0.081613 | -58.342 | 62.1277 | -61.7203 | -61.5967 | 54.5105 | 23.7717 | 7.8735 | 6.9855 | 62.1048 | -61.7249 | -0.3067 | 0.004578 | 3.0716 | -0.18311 | -7.6126 | -0.31128 | -0.018311 | 3.3783 | 69.2871 | 68.399 | 115.9241 | 123.5413 | 3.0716 | 123.5184 | 85.1852 | -0.31128 | 123.5413 | 3.0716 | 85.1852 | 115.9241 | 123.5184 | -123.8434 | -123.848
3950.7188 | 123.7656 | -61.441 | 62.1643 | 0.15892 | 0.016665 | 0.017045 | 0.017233 | 0.061743 | -0.00097413 | 0.078622 | -58.3923 | 62.1643 | -61.7477 | -61.6562 | 54.4373 | 23.4558 | 8.0063 | 6.8939 | 62.1368 | -61.7706 | -0.3067 | 0 | 3.0487 | -0.21515 | -7.7271 | -0.32959 | -0.027466 | 3.3554 | 69.4473 | 68.335 | 115.8783 | 123.6053 | 3.0487 | 123.5779 | 84.8969 | -0.32959 | 123.6053 | 3.0487 | 84.8969 | 115.8783 | 123.5779 | -123.912 | -123.9349
3951.7344 | 123.7976 | -61.3861 | 62.1918 | -0.1844 | 0.014529 | 0.01085 | 0.010824 | 0.060675 | -0.00097413 | 0.080758 | -58.3145 | 62.1368 | -61.6745 | -61.5417 | 54.5425 | 23.6343 | 8.0246 | 7.0221 | 62.1735 | -61.6791 | -0.28839 | -0.054931 | 3.0716 | -0.15564 | -7.6492 | -0.29297 | -0.01831 | 3.36 | 69.4107 | 68.4082 | 115.9287 | 123.5229 | 3.0716 | 123.5596 | 85.0204 | -0.29297 | 123.5229 | 3.0716 | 85.0204 | 115.9287 | 123.5596 | -123.8663 | -123.8708
3952.7188 | 123.8846 | -61.4182 | 62.1414 | 0.13603 | 0.01346 | 0.014909 | 0.013174 | 0.063666 | 0.00052127 | 0.077554 | -58.2962 | 62.1094 | -61.7249 | -61.5646 | 54.4968 | 23.6023 | 7.8735 | 6.9901 | 62.0911 | -61.7065 | -0.3067 | -0.032043 | 3.1219 | -0.14648 | -7.6447 | -0.28839 | -0.050354 | 3.4286 | 69.2917 | 68.4082 | 115.9149 | 123.5275 | 3.1219 | 123.5092 | 85.0204 | -0.28839 | 123.5275 | 3.1219 | 85.0204 | 115.9149 | 123.5092 | -123.8663 | -123.848
3953.7188 | 123.7244 | -61.3953 | 62.146 | -0.0089264 | 0.013674 | 0.012132 | 0.0095424 | 0.060889 | -0.0011877 | 0.079904 | -58.3832 | 62.0956 | -61.7203 | -61.6013 | 54.4785 | 23.703 | 7.9376 | 6.9763 | 62.1277 | -61.7111 | -0.32501 | -0.050354 | 3.0121 | -0.20599 | -7.6675 | -0.31586 | -0.01831 | 3.3371 | 69.3329 | 68.3716 | 115.8737 | 123.4909 | 3.0121 | 123.5229 | 85.0983 | -0.31586 | 123.4909 | 3.0121 | 85.0983 | 115.8737 | 123.5229 | -123.8663 | -123.8571
3954.7188 | 123.848 | -61.409 | 62.1231 | 0.30388 | 0.016451 | 0.012559 | 0.016592 | 0.060034 | 0.00073487 | 0.082253 | -58.3328 | 62.114 | -61.7157 | -61.5555 | 54.5013 | 23.703 | 8.0933 | 7.608 | 62.0773 | -61.7386 | -0.3067 | -0.009155 | 3.0762 | -0.14648 | -7.6218 | -0.32959 | -0.045776 | 3.3829 | 69.5023 | 69.017 | 115.9103 | 123.523 | 3.0762 | 123.4863 | 85.112 | -0.32959 | 123.523 | 3.0762 | 85.112 | 115.9103 | 123.4863 | -123.8388 | -123.8617
3955.7188 | 123.8892 | -61.3953 | 62.1414 | 0.2047 | 0.016665 | 0.017472 | 0.014456 | 0.061957 | -0.00097413 | 0.080544 | -58.3237 | 62.1094 | -61.7157 | -61.5738 | 54.451 | 23.6618 | 8.0933 | 7.6172 | 62.1002 | -61.7294 | -0.32043 | -0.032043 | 3.0716 | -0.17853 | -7.6904 | -0.33417 | -0.041198 | 3.392 | 69.4885 | 69.0125 | 115.8463 | 123.5046 | 3.0716 | 123.4955 | 85.0571 | -0.33417 | 123.5046 | 3.0716 | 85.0571 | 115.8463 | 123.4955 | -123.8571 | -123.8708
3956.7188 | 123.8525 | -61.3586 | 62.1323 | 0.28099 | 0.013674 | 0.015336 | 0.0080472 | 0.060462 | -0.00054693 | 0.080972 | -58.255 | 62.0728 | -61.7477 | -61.5005 | 54.5425 | 23.7854 | 8.1711 | 7.7042 | 62.1185 | -61.6699 | -0.3891 | -0.059509 | 3.1036 | -0.14191 | -7.5897 | -0.31128 | -0.013733 | 3.4927 | 69.5297 | 69.0628 | 115.9012 | 123.4314 | 3.1036 | 123.4772 | 85.144 | -0.31128 | 123.4314 | 3.1036 | 85.144 | 115.9012 | 123.4772 | -123.88 | -123.8022
3957.7188 | 123.7427 | -61.4182 | 62.1552 | 0.097885 | 0.015169 | 0.010209 | 0.017019 | 0.06153 | -0.00011953 | 0.079476 | -58.374 | 62.1643 | -61.7523 | -61.647 | 54.364 | 23.6298 | 7.9971 | 6.9443 | 62.1323 | -61.7661 | -0.33417 | 0.009156 | 3.0441 | -0.22888 | -7.7911 | -0.3479 | -0.022888 | 3.3783 | 69.4153 | 68.3624 | 115.7822 | 123.5825 | 3.0441 | 123.5504 | 85.0479 | -0.3479 | 123.5825 | 3.0441 | 85.0479 | 115.7822 | 123.5504 | -123.9075 | -123.9212
3958.7188 | 123.8205 | -61.4136 | 62.1414 | 0.04448 | 0.01282 | 0.0089274 | 0.0084744 | 0.061103 | 0.00073487 | 0.081185 | -58.3878 | 62.0728 | -61.734 | -61.5967 | 54.4418 | 23.6893 | 7.9239 | 6.9992 | 62.1277 | -61.6791 | -0.32044 | -0.068664 | 3.0258 | -0.18311 | -7.6996 | -0.2655 | -0.013732 | 3.3463 | 69.3375 | 68.4128 | 115.8554 | 123.4863 | 3.0258 | 123.5413 | 85.1028 | -0.2655 | 123.4863 | 3.0258 | 85.1028 | 115.8554 | 123.5413 | -123.8754 | -123.8205
3959.7188 | 123.8342 | -61.3953 | 62.1231 | 0.18944 | 0.015383 | 0.012986 | 0.010824 | 0.059821 | -0.0014013 | 0.080758 | -58.3054 | 62.0865 | -61.7111 | -61.5646 | 54.5563 | 23.7259 | 7.8049 | 7.0587 | 62.0819 | -61.7157 | -0.31586 | -0.036621 | 3.0899 | -0.16937 | -7.5668 | -0.32043 | -0.041199 | 3.4058 | 69.2001 | 68.454 | 115.9515 | 123.4818 | 3.0899 | 123.4772 | 85.1212 | -0.32043 | 123.4818 | 3.0899 | 85.1212 | 115.9515 | 123.4772 | -123.8342 | -123.8388
3960.7188 | 123.8571 | -61.4227 | 62.1185 | 0.2047 | 0.016665 | 0.013627 | 0.01232 | 0.060248 | -0.0011877 | 0.081613 | -58.3099 | 62.1002 | -61.7111 | -61.5875 | 54.5975 | 23.8449 | 7.814 | 7.0679 | 62.1094 | -61.7065 | -0.28839 | -0.01831 | 3.1128 | -0.1648 | -7.5211 | -0.28381 | -0.009155 | 3.4012 | 69.2368 | 68.4906 | 116.0202 | 123.5229 | 3.1128 | 123.5321 | 85.2676 | -0.28381 | 123.5229 | 3.1128 | 85.2676 | 116.0202 | 123.5321 | -123.8297 | -123.8251
3961.7344 | 123.761 | -61.4273 | 62.2009 | -0.21492 | 0.015383 | 0.0132 | 0.013601 | 0.058966 | -0.0028967 | 0.07969 | -58.4198 | 62.1552 | -61.7386 | -61.6104 | 54.4785 | 23.7305 | 8.0887 | 6.9809 | 62.1735 | -61.7203 | -0.31128 | -0.045777 | 3.0075 | -0.18311 | -7.7225 | -0.29297 | -0.027466 | 3.3188 | 69.516 | 68.4082 | 115.9058 | 123.5825 | 3.0075 | 123.6008 | 85.1578 | -0.29297 | 123.5825 | 3.0075 | 85.1578 | 115.9058 | 123.6008 | -123.9395 | -123.9212
3962.7188 | 123.8342 | -61.3815 | 62.114 | 0.2581 | 0.014956 | 0.014054 | 0.011892 | 0.058325 | -0.0022559 | 0.08204 | -58.2962 | 62.0819 | -61.7249 | -61.5738 | 54.6707 | 23.7808 | 7.8186 | 7.077 | 62.1002 | -61.6928 | -0.34332 | -0.032044 | 3.0853 | -0.19226 | -7.4432 | -0.31128 | -0.013733 | 3.4286 | 69.2001 | 68.4586 | 116.0522 | 123.4634 | 3.0853 | 123.4818 | 85.1624 | -0.31128 | 123.4634 | 3.0853 | 85.1624 | 116.0522 | 123.4818 | -123.8388 | -123.8068
3963.7188 | 123.8205 | -61.3907 | 62.1872 | -0.16914 | 0.013033 | 0.012773 | 0.010397 | 0.059607 | -0.0022559 | 0.079049 | -58.3054 | 62.1368 | -61.7294 | -61.5509 | 54.5334 | 23.8724 | 7.9605 | 7.0587 | 62.1185 | -61.7111 | -0.33874 | -0.050354 | 3.0853 | -0.16022 | -7.6538 | -0.32043 | -0.068665 | 3.4241 | 69.3512 | 68.4494 | 115.9241 | 123.5275 | 3.0853 | 123.5092 | 85.2631 | -0.32043 | 123.5275 | 3.0853 | 85.2631 | 115.9241 | 123.5092 | -123.9166 | -123.8983
3964.7188 | 123.8434 | -61.4273 | 62.1414 | 0.24284 | 0.014315 | 0.013841 | 0.014456 | 0.060462 | -0.00054693 | 0.080972 | -58.3328 | 62.1094 | -61.7157 | -61.5784 | 54.5013 | 23.7259 | 7.8323 | 6.9901 | 62.1094 | -61.7111 | -0.28839 | -0.032043 | 3.0945 | -0.15106 | -7.6401 | -0.28381 | -0.032043 | 3.3829 | 69.2596 | 68.4174 | 115.9287 | 123.5367 | 3.0945 | 123.5367 | 85.1532 | -0.28381 | 123.5367 | 3.0945 | 85.1532 | 115.9287 | 123.5367 | -123.8571 | -123.8525
3965.7188 | 123.8342 | -61.4044 | 62.0865 | 0.21996 | 0.018374 | 0.0132 | 0.014883 | 0.062171 | 0.0018031 | 0.080544 | -58.3557 | 62.114 | -61.7249 | -61.5875 | 54.4693 | 23.7717 | 7.8552 | 7.0312 | 62.0956 | -61.7249 | -0.32044 | 0.027466 | 3.0487 | -0.18311 | -7.6172 | -0.32044 | 0.009155 | 3.3691 | 69.2596 | 68.4357 | 115.8737 | 123.5184 | 3.0487 | 123.5001 | 85.1761 | -0.32044 | 123.5184 | 3.0487 | 85.1761 | 115.8737 | 123.5001 | -123.8113 | -123.8113
3966.7188 | 123.8159 | -61.4044 | 62.1323 | -0.054703 | 0.011965 | 0.010423 | 0.0093288 | 0.060248 | -0.00033333 | 0.081826 | -58.2321 | 62.1094 | -61.702 | -61.615 | 54.483 | 23.7717 | 7.8873 | 6.9992 | 62.1231 | -61.6745 | -0.29755 | -0.022888 | 3.1723 | -0.21057 | -7.6492 | -0.27008 | -0.009155 | 3.4698 | 69.2917 | 68.4036 | 115.8875 | 123.5138 | 3.1723 | 123.5275 | 85.1761 | -0.27008 | 123.5138 | 3.1723 | 85.1761 | 115.8875 | 123.5275 | -123.8342 | -123.8068
3967.7188 | 123.8342 | -61.409 | 62.1368 | 0.16655 | 0.014101 | 0.017045 | 0.013174 | 0.061103 | -0.0018285 | 0.079476 | -58.3145 | 62.0773 | -61.7203 | -61.5692 | 54.4739 | 23.7671 | 7.8369 | 7.0587 | 62.1277 | -61.6974 | -0.31128 | -0.059509 | 3.0945 | -0.16022 | -7.663 | -0.28839 | -0.009155 | 3.4058 | 69.2459 | 68.4677 | 115.8829 | 123.4863 | 3.0945 | 123.5367 | 85.1761 | -0.28839 | 123.4863 | 3.0945 | 85.1761 | 115.8829 | 123.5367 | -123.8571 | -123.8342
3968.7188 | 123.8571 | -61.4227 | 62.1597 | -0.039444 | 0.01282 | 0.0089274 | 0.0080472 | 0.058539 | -0.0014013 | 0.077767 | -58.342 | 62.0956 | -61.7065 | -61.5555 | 54.4189 | 23.7854 | 7.9056 | 7.0862 | 62.1048 | -61.6699 | -0.28381 | -0.064087 | 3.0807 | -0.13275 | -7.7408 | -0.24719 | -0.054932 | 3.3646 | 69.3283 | 68.5089 | 115.8417 | 123.5184 | 3.0807 | 123.5275 | 85.2081 | -0.24719 | 123.5184 | 3.0807 | 85.2081 | 115.8417 | 123.5275 | -123.8663 | -123.8297
3969.7188 | 123.848 | -61.3907 | 62.1277 | 0.10551 | 0.015597 | 0.017686 | 0.01296 | 0.059607 | 0.00094847 | 0.079263 | -58.2916 | 62.1002 | -61.7203 | -61.5509 | 54.3686 | 23.7946 | 7.8232 | 7.0541 | 62.0911 | -61.7157 | -0.32959 | -0.027466 | 3.0991 | -0.16022 | -7.7591 | -0.32501 | -0.036622 | 3.4286 | 69.2139 | 68.4448 | 115.7593 | 123.4909 | 3.0991 | 123.4818 | 85.1852 | -0.32501 | 123.4909 | 3.0991 | 85.1852 | 115.7593 | 123.4818 | -123.848 | -123.8434
3970.7188 | 123.8754 | -61.409 | 62.114 | 0.029221 | 0.016238 | 0.016404 | 0.01296 | 0.059607 | 0.00030767 | 0.080331 | -58.3054 | 62.0773 | -61.6928 | -61.5463 | 54.4144 | 23.8815 | 7.8186 | 7.0724 | 62.0819 | -61.702 | -0.28381 | -0.036621 | 3.1036 | -0.13733 | -7.6996 | -0.29297 | -0.032044 | 3.3875 | 69.2276 | 68.4814 | 115.8234 | 123.4863 | 3.1036 | 123.4909 | 85.2905 | -0.29297 | 123.4863 | 3.1036 | 85.2905 | 115.8234 | 123.4909 | -123.8068 | -123.8159
3971.7188 | 123.7701 | -61.3815 | 62.1735 | -0.26833 | 0.011965 | 0.012773 | 0.0099698 | 0.058325 | -0.0024695 | 0.07969 | -58.3008 | 62.1094 | -61.6974 | -61.5646 | 54.4739 | 23.8998 | 7.9971 | 7.045 | 62.1689 | -61.6791 | -0.31586 | -0.064087 | 3.0808 | -0.1831 | -7.6996 | -0.29755 | -0.004578 | 3.3966 | 69.3787 | 68.4265 | 115.8554 | 123.4909 | 3.0808 | 123.5504 | 85.2814 | -0.29755 | 123.4909 | 3.0808 | 85.2814 | 115.8554 | 123.5504 | -123.8708 | -123.8525
3972.7188 | 123.8388 | -61.3815 | 62.114 | 0.16655 | 0.017306 | 0.016404 | 0.015097 | 0.060889 | -0.0041785 | 0.07969 | -58.3145 | 62.0911 | -61.734 | -61.5646 | 54.4739 | 23.8037 | 7.8323 | 7.0175 | 62.1094 | -61.7203 | -0.35248 | -0.022889 | 3.067 | -0.1831 | -7.6401 | -0.33874 | -0.004578 | 3.4195 | 69.2139 | 68.399 | 115.8554 | 123.4726 | 3.067 | 123.4909 | 85.1852 | -0.33874 | 123.4726 | 3.067 | 85.1852 | 115.8554 | 123.4909 | -123.848 | -123.8342
3973.7188 | 123.8068 | -61.3998 | 62.1368 | 0.19707 | 0.013247 | 0.013627 | 0.0076198 | 0.060462 | 0.00052127 | 0.079904 | -58.3557 | 62.0865 | -61.7157 | -61.6058 | 54.3961 | 23.8266 | 7.9056 | 7.0038 | 62.146 | -61.6882 | -0.31586 | -0.050354 | 3.0441 | -0.20599 | -7.7408 | -0.28839 | 0.009155 | 3.36 | 69.3054 | 68.4036 | 115.7959 | 123.4863 | 3.0441 | 123.5458 | 85.2264 | -0.28839 | 123.4863 | 3.0441 | 85.2264 | 115.7959 | 123.5458 | -123.8525 | -123.8251
3974.7188 | 123.8388 | -61.409 | 62.114 | 0.15129 | 0.015383 | 0.013413 | 0.012106 | 0.05918 | -0.00011953 | 0.079049 | -58.3054 | 62.0865 | -61.7065 | -61.5738 | 54.4373 | 23.8403 | 7.869 | 7.0358 | 62.0956 | -61.702 | -0.29755 | -0.027466 | 3.1036 | -0.16479 | -7.6767 | -0.29297 | -0.018311 | 3.4012 | 69.278 | 68.4448 | 115.8463 | 123.4955 | 3.1036 | 123.5046 | 85.2493 | -0.29297 | 123.4955 | 3.1036 | 85.2493 | 115.8463 | 123.5046 | -123.8205 | -123.8159
3975.7188 | 123.8525 | -61.4182 | 62.1414 | 0.18944 | 0.01346 | 0.016831 | 0.010611 | 0.061743 | -0.0031103 | 0.079904 | -58.3054 | 62.1002 | -61.7111 | -61.5555 | 54.4647 | 23.8815 | 7.8552 | 7.0404 | 62.0911 | -61.7294 | -0.29297 | -0.041198 | 3.1128 | -0.13733 | -7.6767 | -0.31128 | -0.050354 | 3.4058 | 69.2734 | 68.4586 | 115.8829 | 123.5184 | 3.1128 | 123.5092 | 85.2997 | -0.31128 | 123.5184 | 3.1128 | 85.2997 | 115.8829 | 123.5092 | -123.8525 | -123.8708
3976.7344 | 123.7885 | -61.3724 | 62.1918 | -0.22255 | 0.013888 | 0.011491 | 0.014029 | 0.05918 | -0.00054693 | 0.078622 | -58.3145 | 62.114 | -61.7111 | -61.5189 | 54.4968 | 23.8129 | 7.9926 | 7.1136 | 62.1643 | -61.6974 | -0.33875 | -0.077819 | 3.0579 | -0.14648 | -7.695 | -0.32501 | -0.027465 | 3.3966 | 69.3649 | 68.486 | 115.8691 | 123.4863 | 3.0579 | 123.5367 | 85.1852 | -0.32501 | 123.4863 | 3.0579 | 85.1852 | 115.8691 | 123.5367 | -123.9029 | -123.8892
3977.7188 | 123.8617 | -61.4044 | 62.1094 | -0.024185 | 0.015383 | 0.013841 | 0.015097 | 0.062384 | -0.0022559 | 0.079476 | -58.287 | 62.0865 | -61.6974 | -61.5555 | 54.4922 | 23.7946 | 7.8461 | 7.0724 | 62.1048 | -61.6653 | -0.29297 | -0.022888 | 3.1174 | -0.15106 | -7.6172 | -0.26093 | -0.004578 | 3.4103 | 69.2505 | 68.4769 | 115.8966 | 123.4909 | 3.1174 | 123.5092 | 85.199 | -0.26093 | 123.4909 | 3.1174 | 85.199 | 115.8966 | 123.5092 | -123.8068 | -123.7747
3978.7188 | 123.88 | -61.3724 | 62.146 | -0.10811 | 0.013674 | 0.014695 | 0.0082608 | 0.059607 | -0.0022559 | 0.082253 | -58.3374 | 62.0819 | -61.7157 | -61.5326 | 54.5334 | 23.8449 | 7.8827 | 7.1045 | 62.1277 | -61.6837 | -0.34332 | -0.064087 | 3.035 | -0.16022 | -7.6126 | -0.31128 | -0.01831 | 3.3783 | 69.2551 | 68.4769 | 115.9058 | 123.4543 | 3.035 | 123.5001 | 85.2173 | -0.31128 | 123.4543 | 3.035 | 85.2173 | 115.9058 | 123.5001 | -123.8617 | -123.8297
3979.7188 | 123.8525 | -61.3907 | 62.1368 | 0.21996 | 0.016238 | 0.016191 | 0.016592 | 0.059607 | -0.0014013 | 0.079263 | -58.3099 | 62.1094 | -61.7432 | -61.5601 | 54.5197 | 23.8266 | 7.8506 | 7.0358 | 62.1002 | -61.7157 | -0.35248 | -0.027466 | 3.0807 | -0.16937 | -7.6172 | -0.32501 | -0.036621 | 3.4332 | 69.2413 | 68.4265 | 115.9103 | 123.5001 | 3.0807 | 123.4909 | 85.2173 | -0.32501 | 123.5001 | 3.0807 | 85.2173 | 115.9103 | 123.4909 | -123.88 | -123.8525
3980.7188 | 123.8022 | -61.4044 | 62.1277 | 0.15129 | 0.015383 | 0.010423 | 0.011465 | 0.058753 | 0.00052127 | 0.080117 | -58.3282 | 62.0911 | -61.7477 | -61.5692 | 54.4464 | 23.8312 | 7.8323 | 7.0358 | 62.0865 | -61.6699 | -0.34332 | -0.036622 | 3.0762 | -0.1648 | -7.6813 | -0.2655 | -0.041199 | 3.4195 | 69.2368 | 68.4402 | 115.8508 | 123.4955 | 3.0762 | 123.4909 | 85.2356 | -0.2655 | 123.4955 | 3.0762 | 85.2356 | 115.8508 | 123.4909 | -123.8754 | -123.7976
3981.7344 | 123.6603 | -61.409 | 62.2238 | -0.2607 | 0.016665 | 0.0099954 | 0.014669 | 0.058753 | 9.4068e-05 | 0.080544 | -58.3878 | 62.1872 | -61.7294 | -61.6104 | 54.3915 | 23.6664 | 8.1207 | 7.0221 | 62.1964 | -61.7065 | -0.32043 | -0.036621 | 3.0212 | -0.20142 | -7.8323 | -0.29755 | -0.027466 | 3.3417 | 69.5297 | 68.4311 | 115.8005 | 123.5962 | 3.0212 | 123.6053 | 85.0754 | -0.29755 | 123.5962 | 3.0212 | 85.0754 | 115.8005 | 123.6053 | -123.9532 | -123.9304
3982.7188 | 123.8205 | -61.409 | 62.114 | 0.16655 | 0.016451 | 0.012345 | 0.014242 | 0.060889 | -0.00011953 | 0.078622 | -58.3328 | 62.0819 | -61.7065 | -61.5646 | 54.4922 | 23.8541 | 7.8232 | 7.0221 | 62.0911 | -61.6974 | -0.29755 | -0.032044 | 3.0762 | -0.15564 | -7.6218 | -0.28839 | -0.022889 | 3.3737 | 69.2322 | 68.4311 | 115.9012 | 123.4909 | 3.0762 | 123.5001 | 85.2631 | -0.28839 | 123.4909 | 3.0762 | 85.2631 | 115.9012 | 123.5001 | -123.8205 | -123.8113
3983.7188 | 123.8342 | -61.409 | 62.146 | -0.016556 | 0.014315 | 0.012773 | 0.011465 | 0.059394 | -0.00033333 | 0.080117 | -58.3557 | 62.0865 | -61.7111 | -61.5601 | 54.5105 | 23.9182 | 7.9056 | 7.0587 | 62.114 | -61.6882 | -0.30212 | -0.059509 | 3.0533 | -0.15106 | -7.6355 | -0.27923 | -0.032043 | 3.3554 | 69.3146 | 68.4677 | 115.9195 | 123.4955 | 3.0533 | 123.523 | 85.3271 | -0.27923 | 123.4955 | 3.0533 | 85.3271 | 115.9195 | 123.523 | -123.8571 | -123.8342
3984.7188 | 123.8663 | -61.3907 | 62.114 | 0.16655 | 0.017306 | 0.014054 | 0.01232 | 0.061103 | -0.0024695 | 0.079904 | -58.3099 | 62.1185 | -61.6837 | -61.5509 | 54.4693 | 23.822 | 7.8003 | 7.0404 | 62.0956 | -61.6882 | -0.29297 | 0.004577 | 3.0807 | -0.16022 | -7.6447 | -0.29755 | -0.018311 | 3.3737 | 69.191 | 68.4311 | 115.86 | 123.5092 | 3.0807 | 123.4863 | 85.2127 | -0.29755 | 123.5092 | 3.0807 | 85.2127 | 115.86 | 123.4863 | -123.7976 | -123.8022
3985.7188 | 123.8846 | -61.4136 | 62.1231 | 0.052109 | 0.016238 | 0.011491 | 0.015097 | 0.060462 | -0.00011953 | 0.079476 | -58.2825 | 62.0911 | -61.7203 | -61.5555 | 54.4876 | 23.8312 | 7.8232 | 7.0541 | 62.0956 | -61.7157 | -0.3067 | -0.032044 | 3.1311 | -0.14191 | -7.6355 | -0.30212 | -0.027466 | 3.4378 | 69.2368 | 68.4677 | 115.9012 | 123.5046 | 3.1311 | 123.5092 | 85.2448 | -0.30212 | 123.5046 | 3.1311 | 85.2448 | 115.9012 | 123.5092 | -123.8434 | -123.8388
3986.7344 | 123.7427 | -61.4502 | 62.1643 | 0.021591 | 0.014742 | 0.012345 | 0.018728 | 0.061957 | -0.00054693 | 0.079049 | -58.3603 | 62.1918 | -61.7386 | -61.6516 | 54.3411 | 23.6572 | 8.0017 | 6.8848 | 62.1643 | -61.7752 | -0.28839 | 0.027465 | 3.0899 | -0.20142 | -7.8232 | -0.32501 | 0 | 3.3783 | 69.4519 | 68.335 | 115.7913 | 123.642 | 3.0899 | 123.6145 | 85.1074 | -0.32501 | 123.642 | 3.0899 | 85.1074 | 115.7913 | 123.6145 | -123.9029 | -123.9395
3987.7188 | 123.8159 | -61.409 | 62.1277 | 0.14366 | 0.014315 | 0.013627 | 0.011038 | 0.061743 | -0.0014013 | 0.079263 | -58.3557 | 62.0728 | -61.7477 | -61.5692 | 54.4785 | 24.0051 | 7.8415 | 7.045 | 62.1048 | -61.6699 | -0.33875 | -0.054932 | 3.0533 | -0.16022 | -7.6492 | -0.26093 | -0.022889 | 3.392 | 69.2505 | 68.454 | 115.8875 | 123.4818 | 3.0533 | 123.5138 | 85.4141 | -0.26093 | 123.4818 | 3.0533 | 85.4141 | 115.8875 | 123.5138 | -123.8754 | -123.7976
3988.7344 | 123.8663 | -61.3953 | 62.1735 | 0.13603 | 0.012392 | 0.010636 | 0.011251 | 0.05918 | -0.0018285 | 0.077767 | -58.3099 | 62.0956 | -61.7111 | -61.5051 | 54.5517 | 24.028 | 7.9056 | 7.0908 | 62.1002 | -61.6791 | -0.31586 | -0.07782 | 3.0853 | -0.10986 | -7.6218 | -0.28381 | -0.073242 | 3.4012 | 69.3008 | 68.486 | 115.947 | 123.4909 | 3.0853 | 123.4955 | 85.4233 | -0.28381 | 123.4909 | 3.0853 | 85.4233 | 115.947 | 123.4955 | -123.8846 | -123.8525
3989.7188 | 123.8434 | -61.409 | 62.114 | 0.17418 | 0.014742 | 0.010423 | 0.01232 | 0.060889 | -0.00011953 | 0.081399 | -58.342 | 62.0819 | -61.6791 | -61.5784 | 54.4693 | 23.8586 | 7.8094 | 7.0221 | 62.0865 | -61.7111 | -0.27008 | -0.032044 | 3.067 | -0.16937 | -7.6447 | -0.30212 | -0.027466 | 3.3371 | 69.2184 | 68.4311 | 115.8783 | 123.4909 | 3.067 | 123.4955 | 85.2676 | -0.30212 | 123.4909 | 3.067 | 85.2676 | 115.8783 | 123.4955 | -123.793 | -123.8251
3990.7188 | 123.7976 | -61.409 | 62.1323 | 0.074997 | 0.014742 | 0.014054 | 0.011465 | 0.058539 | -0.00054693 | 0.078835 | -58.3786 | 62.0499 | -61.734 | -61.6058 | 54.4418 | 23.8861 | 7.8644 | 7.0267 | 62.1002 | -61.7065 | -0.32501 | -0.082397 | 3.0304 | -0.19684 | -7.6904 | -0.29755 | -0.032043 | 3.3554 | 69.2734 | 68.4357 | 115.8508 | 123.4589 | 3.0304 | 123.5092 | 85.2951 | -0.29755 | 123.4589 | 3.0304 | 85.2951 | 115.8508 | 123.5092 | -123.8663 | -123.8388
3991.7344 | 123.8342 | -61.409 | 62.1826 | 0.44121 | 0.015169 | 0.011491 | 0.0078336 | 0.058539 | -0.00054693 | 0.080331 | -58.4152 | 62.1185 | -61.702 | -61.5967 | 54.451 | 23.8083 | 7.9102 | 7.0267 | 62.1185 | -61.6974 | -0.29297 | -0.064087 | 2.9938 | -0.18768 | -7.7316 | -0.28839 | -0.064087 | 3.2867 | 69.3192 | 68.4357 | 115.86 | 123.5275 | 2.9938 | 123.5275 | 85.2173 | -0.28839 | 123.5275 | 2.9938 | 85.2173 | 115.86 | 123.5275 | -123.8846 | -123.88
3992.7188 | 123.9395 | -61.4044 | 62.1689 | 0.067368 | 0.01282 | 0.014695 | 0.011038 | 0.060034 | -0.00011953 | 0.080972 | -58.4106 | 62.0636 | -61.7111 | -61.5875 | 54.4601 | 23.8586 | 7.9239 | 7.0541 | 62.1002 | -61.6837 | -0.3067 | -0.10528 | 2.9938 | -0.18311 | -7.7087 | -0.27924 | -0.068664 | 3.3005 | 69.3283 | 68.4586 | 115.8646 | 123.468 | 2.9938 | 123.5046 | 85.2631 | -0.27924 | 123.468 | 2.9938 | 85.2631 | 115.8646 | 123.5046 | -123.88 | -123.8525
3993.7344 | 123.8571 | -61.3907 | 62.1643 | -0.20729 | 0.013033 | 0.012559 | 0.011892 | 0.057257 | -0.00076053 | 0.078408 | -58.3191 | 62.114 | -61.6837 | -61.5143 | 54.57 | 23.8907 | 7.9742 | 7.1365 | 62.1277 | -61.6882 | -0.29297 | -0.050354 | 3.0716 | -0.1236 | -7.5943 | -0.29755 | -0.036621 | 3.3646 | 69.3649 | 68.5272 | 115.9607 | 123.5046 | 3.0716 | 123.5184 | 85.2814 | -0.29755 | 123.5046 | 3.0716 | 85.2814 | 115.9607 | 123.5184 | -123.848 | -123.8525
3994.7188 | 123.8159 | -61.4227 | 62.1323 | 0.14366 | 0.014742 | 0.0093546 | 0.010824 | 0.060462 | -0.0016149 | 0.07969 | -58.3603 | 62.0773 | -61.7249 | -61.5738 | 54.4739 | 23.9685 | 7.869 | 7.0999 | 62.1002 | -61.7111 | -0.30213 | -0.054931 | 3.0624 | -0.15106 | -7.6584 | -0.28839 | -0.032043 | 3.3646 | 69.2917 | 68.5226 | 115.8966 | 123.5001 | 3.0624 | 123.5229 | 85.3912 | -0.28839 | 123.5001 | 3.0624 | 85.3912 | 115.8966 | 123.5229 | -123.8571 | -123.8434
3995.7188 | 123.8022 | -61.409 | 62.1414 | 0.89134 | 0.013033 | 0.011277 | 0.0089016 | 0.05918 | 0.0015893 | 0.078408 | -58.3832 | 62.0956 | -61.702 | -61.5829 | 54.4235 | 23.8953 | 7.9559 | 7.0953 | 62.114 | -61.7111 | -0.29297 | -0.045776 | 3.0258 | -0.17395 | -7.7179 | -0.30212 | -0.027465 | 3.3188 | 69.3649 | 68.5043 | 115.8325 | 123.5046 | 3.0258 | 123.523 | 85.3043 | -0.30212 | 123.5046 | 3.0258 | 85.3043 | 115.8325 | 123.523 | -123.8434 | -123.8525
3996.7344 | 123.8251 | -61.409 | 62.1368 | -0.20729 | 0.013033 | 0.011064 | 0.0095424 | 0.059394 | 0.0015893 | 0.080972 | -58.4152 | 62.0728 | -61.7203 | -61.5784 | 54.5334 | 24.028 | 7.9926 | 7.1182 | 62.1048 | -61.6882 | -0.31128 | -0.064087 | 2.9938 | -0.16937 | -7.6035 | -0.27923 | -0.032044 | 3.3051 | 69.4016 | 68.5272 | 115.9424 | 123.4818 | 2.9938 | 123.5138 | 85.437 | -0.27923 | 123.4818 | 2.9938 | 85.437 | 115.9424 | 123.5138 | -123.8571 | -123.8251
3997.7344 | 123.7656 | -61.409 | 62.1689 | -0.077591 | 0.01816 | 0.015763 | 0.018301 | 0.062171 | -0.0033239 | 0.079476 | -58.3008 | 62.1872 | -61.7249 | -61.5692 | 54.4922 | 23.9456 | 8.0612 | 7.0679 | 62.1368 | -61.7294 | -0.31586 | 0.018311 | 3.1082 | -0.16022 | -7.6767 | -0.32043 | -0.032043 | 3.4241 | 69.4702 | 68.4769 | 115.9012 | 123.5962 | 3.1082 | 123.5458 | 85.3546 | -0.32043 | 123.5962 | 3.1082 | 85.3546 | 115.9012 | 123.5458 | -123.8937 | -123.8983
3998.7344 | 123.8205 | -61.3861 | 62.1872 | -0.16151 | 0.013674 | 0.010423 | 0.0080472 | 0.059821 | 9.4068e-05 | 0.078622 | -58.3328 | 62.1002 | -61.7157 | -61.5234 | 54.5013 | 23.9685 | 8.0292 | 7.164 | 62.1552 | -61.6699 | -0.32959 | -0.086975 | 3.0533 | -0.13733 | -7.6859 | -0.28381 | -0.032044 | 3.3829 | 69.4153 | 68.5501 | 115.8875 | 123.4863 | 3.0533 | 123.5413 | 85.3546 | -0.28381 | 123.4863 | 3.0533 | 85.3546 | 115.8875 | 123.5413 | -123.9029 | -123.8571
3999.7188 | 123.8113 | -61.4044 | 62.1368 | 0.14366 | 0.016878 | 0.0132 | 0.012106 | 0.060248 | -0.00011953 | 0.080544 | -58.3649 | 62.0773 | -61.7203 | -61.6013 | 54.4968 | 23.9594 | 7.8827 | 7.0541 | 62.1002 | -61.6699 | -0.31586 | -0.059509 | 3.0396 | -0.19684 | -7.6401 | -0.2655 | -0.036621 | 3.3554 | 69.2871 | 68.4586 | 115.9012 | 123.4818 | 3.0396 | 123.5046 | 85.3638 | -0.2655 | 123.4818 | 3.0396 | 85.3638 | 115.9012 | 123.5046 | -123.8571 | -123.8068
4000.7188 | 123.8068 | -61.409 | 62.1552 | -0.054703 | 0.013888 | 0.01085 | 0.010183 | 0.059607 | 0.00030767 | 0.07969 | -58.4244 | 62.0911 | -61.7569 | -61.5738 | 54.5242 | 24.0921 | 7.9376 | 7.0999 | 62.1002 | -61.6837 | -0.3479 | -0.064087 | 2.9846 | -0.16479 | -7.6309 | -0.27466 | -0.054931 | 3.3325 | 69.3466 | 68.5089 | 115.9332 | 123.5001 | 2.9846 | 123.5092 | 85.5011 | -0.27466 | 123.5001 | 2.9846 | 85.5011 | 115.9332 | 123.5092 | -123.912 | -123.8388
4001.75 | 123.8754 | -61.3861 | 62.1368 | -0.19203 | 0.011538 | 0.014695 | 0.008688 | 0.058966 | -0.0022559 | 0.078408 | -58.3008 | 62.0865 | -61.6974 | -61.5051 | 54.4647 | 24.3439 | 8.0933 | 6.8069 | 62.1414 | -61.6608 | -0.31128 | -0.050354 | 3.0853 | -0.11902 | -7.6721 | -0.27466 | 0.004577 | 3.3966 | 69.4794 | 68.1931 | 115.8508 | 123.4726 | 3.0853 | 123.5275 | 85.73 | -0.27466 | 123.4726 | 3.0853 | 85.73 | 115.8508 | 123.5275 | -123.8342 | -123.7976
4002.7188 | 123.8342 | -61.409 | 62.1368 | 0.15129 | 0.01282 | 0.013627 | 0.011892 | 0.061743 | -0.00033333 | 0.07969 | -58.3603 | 62.059 | -61.7294 | -61.5555 | 54.4968 | 23.9548 | 7.8918 | 7.0862 | 62.0819 | -61.702 | -0.32043 | -0.07782 | 3.0487 | -0.14648 | -7.6401 | -0.29297 | -0.054932 | 3.3691 | 69.3008 | 68.4952 | 115.9058 | 123.468 | 3.0487 | 123.4909 | 85.3638 | -0.29297 | 123.468 | 3.0487 | 85.3638 | 115.9058 | 123.4909 | -123.8663 | -123.8388
4003.7188 | 123.8205 | -61.4273 | 62.1506 | 0.097885 | 0.012606 | 0.0097818 | 0.0097562 | 0.060248 | -0.0014013 | 0.080117 | -58.4061 | 62.0728 | -61.7203 | -61.5967 | 54.4968 | 24.028 | 8.0658 | 7.4341 | 62.1094 | -61.6928 | -0.29297 | -0.07782 | 3.0212 | -0.16937 | -7.6538 | -0.2655 | -0.041199 | 3.3142 | 69.4931 | 68.8614 | 115.9241 | 123.5001 | 3.0212 | 123.5367 | 85.4553 | -0.2655 | 123.5001 | 3.0212 | 85.4553 | 115.9241 | 123.5367 | -123.8708 | -123.8434
4004.7188 | 123.8983 | -61.4136 | 62.0956 | 0.17418 | 0.013247 | 0.015763 | 0.014883 | 0.061743 | 0.00030767 | 0.079476 | -58.3099 | 62.0773 | -61.7249 | -61.5417 | 54.5288 | 23.996 | 7.9651 | 7.4524 | 62.0819 | -61.7111 | -0.31128 | -0.01831 | 3.1036 | -0.12817 | -7.5668 | -0.29755 | -0.013733 | 3.4149 | 69.3787 | 68.866 | 115.9424 | 123.4909 | 3.1036 | 123.4955 | 85.4095 | -0.29755 | 123.4909 | 3.1036 | 85.4095 | 115.9424 | 123.4955 | -123.8205 | -123.8068
4005.7188 | 123.8846 | -61.3953 | 62.1048 | 0.2581 | 0.015169 | 0.011491 | 0.012533 | 0.059607 | -0.00011953 | 0.079263 | -58.3374 | 62.0865 | -61.7157 | -61.5601 | 54.5197 | 23.8953 | 7.8552 | 7.1045 | 62.0865 | -61.6974 | -0.32043 | -0.01831 | 3.0579 | -0.1648 | -7.5851 | -0.30212 | -0.01831 | 3.3783 | 69.2505 | 68.4998 | 115.9149 | 123.4818 | 3.0579 | 123.4818 | 85.2905 | -0.30212 | 123.4818 | 3.0579 | 85.2905 | 115.9149 | 123.4818 | -123.8205 | -123.8022
4006.7344 | 123.7427 | -61.4639 | 62.1597 | 0.34966 | 0.019228 | 0.014695 | 0.018087 | 0.062812 | -0.00011953 | 0.079263 | -58.4061 | 62.2009 | -61.734 | -61.6425 | 54.5013 | 23.8495 | 8.0109 | 6.9901 | 62.1368 | -61.7432 | -0.27008 | 0.041199 | 3.0579 | -0.17853 | -7.6584 | -0.27924 | -0.022888 | 3.3279 | 69.4748 | 68.454 | 115.9653 | 123.6649 | 3.0579 | 123.6008 | 85.3134 | -0.27924 | 123.6649 | 3.0579 | 85.3134 | 115.9653 | 123.6008 | -123.8937 | -123.9029
4007.7188 | 123.8251 | -61.4136 | 62.1414 | -0.031814 | 0.014529 | 0.010209 | 0.0093288 | 0.060462 | -0.00033333 | 0.079904 | -58.3969 | 62.0911 | -61.7249 | -61.5784 | 54.483 | 23.9227 | 7.9422 | 7.1136 | 62.114 | -61.6928 | -0.31128 | -0.050354 | 3.0167 | -0.1648 | -7.6584 | -0.27924 | -0.027465 | 3.3279 | 69.3558 | 68.5272 | 115.8966 | 123.5046 | 3.0167 | 123.5275 | 85.3363 | -0.27924 | 123.5046 | 3.0167 | 85.3363 | 115.8966 | 123.5275 | -123.8663 | -123.8342
4008.7344 | 123.88 | -61.3907 | 62.1643 | -0.16914 | 0.01346 | 0.012773 | 0.01296 | 0.060248 | -0.0016149 | 0.078835 | -57.9666 | 62.1094 | -61.6928 | -61.5189 | 54.5609 | 23.9182 | 7.9697 | 7.1732 | 62.1185 | -61.6928 | -0.30212 | -0.054932 | 3.4241 | -0.12817 | -7.6035 | -0.30212 | -0.045777 | 3.7262 | 69.3604 | 68.5638 | 115.9515 | 123.5001 | 3.4241 | 123.5092 | 85.3088 | -0.30212 | 123.5001 | 3.4241 | 85.3088 | 115.9515 | 123.5092 | -123.8571 | -123.8571
4009.7188 | 123.8159 | -61.4273 | 62.1368 | 0.66246 | 0.014101 | 0.01555 | 0.0095424 | 0.060034 | -0.0018285 | 0.079476 | -58.3786 | 62.1002 | -61.7249 | -61.5921 | 54.5517 | 23.9044 | 7.9605 | 7.0953 | 62.1002 | -61.6974 | -0.29755 | -0.036621 | 3.0487 | -0.16479 | -7.5851 | -0.27008 | -0.036621 | 3.3463 | 69.3878 | 68.5226 | 115.979 | 123.5275 | 3.0487 | 123.5275 | 85.3317 | -0.27008 | 123.5275 | 3.0487 | 85.3317 | 115.979 | 123.5275 | -123.8617 | -123.8342
4010.7188 | 123.8159 | -61.3907 | 62.1231 | 0.14366 | 0.013674 | 0.014054 | 0.011892 | 0.059821 | -0.00011953 | 0.07969 | -58.342 | 62.0819 | -61.7523 | -61.5738 | 54.538 | 23.9319 | 7.8964 | 7.1548 | 62.0773 | -61.7111 | -0.36163 | -0.041199 | 3.0487 | -0.18311 | -7.5851 | -0.32043 | -0.045776 | 3.4103 | 69.2871 | 68.5455 | 115.9287 | 123.4726 | 3.0487 | 123.468 | 85.3226 | -0.32043 | 123.4726 | 3.0487 | 85.3226 | 115.9287 | 123.468 | -123.8754 | -123.8342
4011.7188 | 123.8892 | -61.3861 | 62.1368 | -0.09285 | 0.014956 | 0.0132 | 0.0082608 | 0.059607 | -0.0018285 | 0.081613 | -58.3511 | 62.0819 | -61.7111 | -61.496 | 54.5563 | 23.941 | 7.9285 | 7.2235 | 62.1048 | -61.6699 | -0.32501 | -0.054932 | 3.035 | -0.10986 | -7.5806 | -0.28381 | -0.032044 | 3.36 | 69.3146 | 68.6096 | 115.9424 | 123.468 | 3.035 | 123.4909 | 85.3271 | -0.28381 | 123.468 | 3.035 | 85.3271 | 115.9424 | 123.4909 | -123.848 | -123.8068
4012.7188 | 123.8663 | -61.3953 | 62.1048 | 0.1284 | 0.014742 | 0.0132 | 0.012106 | 0.057685 | 0.00030767 | 0.078622 | -58.3328 | 62.0773 | -61.7111 | -61.5601 | 54.5563 | 23.877 | 7.8369 | 7.0953 | 62.0682 | -61.7203 | -0.31586 | -0.027465 | 3.0624 | -0.1648 | -7.5485 | -0.32501 | -0.036621 | 3.3783 | 69.2322 | 68.4906 | 115.9515 | 123.4726 | 3.0624 | 123.4634 | 85.2722 | -0.32501 | 123.4726 | 3.0624 | 85.2722 | 115.9515 | 123.4634 | -123.8159 | -123.8251
4013.7188 | 123.8846 | -61.3907 | 62.1185 | 0.17418 | 0.01581 | 0.017045 | 0.014242 | 0.059394 | -0.00076053 | 0.07969 | -58.3374 | 62.0911 | -61.7249 | -61.5463 | 54.5105 | 23.8312 | 7.8232 | 7.0816 | 62.059 | -61.7432 | -0.33417 | -0.027466 | 3.0533 | -0.15564 | -7.608 | -0.35248 | -0.059509 | 3.3875 | 69.2139 | 68.4723 | 115.9012 | 123.4818 | 3.0533 | 123.4497 | 85.2219 | -0.35248 | 123.4818 | 3.0533 | 85.2219 | 115.9012 | 123.4497 | -123.8434 | -123.8617
4014.7188 | 123.8159 | -61.4319 | 62.146 | 0.18944 | 0.015169 | 0.014268 | 0.0099698 | 0.059821 | -0.00033333 | 0.080117 | -58.4244 | 62.0499 | -61.7432 | -61.6058 | 54.4785 | 23.8129 | 7.8918 | 7.0496 | 62.114 | -61.6791 | -0.31128 | -0.09613 | 3.0075 | -0.17395 | -7.6675 | -0.24719 | -0.032043 | 3.3188 | 69.3237 | 68.4814 | 115.9103 | 123.4818 | 3.0075 | 123.5458 | 85.2448 | -0.24719 | 123.4818 | 3.0075 | 85.2448 | 115.9103 | 123.5458 | -123.8892 | -123.8251
4015.7188 | 123.8571 | -61.3998 | 62.1735 | 0.11314 | 0.01346 | 0.012986 | 0.0095424 | 0.057044 | -0.0020421 | 0.078622 | -58.4198 | 62.1002 | -61.6837 | -61.5921 | 54.5563 | 24.0005 | 7.9422 | 7.0587 | 62.0773 | -61.6928 | -0.28381 | -0.073242 | 2.98 | -0.19226 | -7.6172 | -0.29297 | -0.09613 | 3.2639 | 69.342 | 68.4586 | 115.9561 | 123.5001 | 2.98 | 123.4772 | 85.4004 | -0.29297 | 123.5001 | 2.98 | 85.4004 | 115.9561 | 123.4772 | -123.8571 | -123.8663
4016.7188 | 123.8205 | -61.4136 | 62.1552 | -0.024185 | 0.013247 | 0.0085 | 0.0080472 | 0.058539 | -0.00054693 | 0.078195 | -58.4244 | 62.1002 | -61.7386 | -61.5692 | 54.5517 | 23.8449 | 7.9147 | 7.1228 | 62.1231 | -61.6791 | -0.32501 | -0.054931 | 2.9892 | -0.15564 | -7.6035 | -0.2655 | -0.032043 | 3.3142 | 69.3283 | 68.5364 | 115.9653 | 123.5138 | 2.9892 | 123.5367 | 85.2585 | -0.2655 | 123.5138 | 2.9892 | 85.2585 | 115.9653 | 123.5367 | -123.8937 | -123.8342
4017.7188 | 123.8388 | -61.3907 | 62.1506 | 0.11314 | 0.012392 | 0.0076456 | 0.0095424 | 0.058112 | -0.00033333 | 0.079904 | -58.4427 | 62.0682 | -61.7065 | -61.5692 | 54.5883 | 24.0372 | 7.9147 | 7.0908 | 62.1231 | -61.6791 | -0.31586 | -0.082398 | 2.948 | -0.17853 | -7.5623 | -0.28839 | -0.027466 | 3.2639 | 69.3054 | 68.4814 | 115.979 | 123.4589 | 2.948 | 123.5138 | 85.4279 | -0.28839 | 123.4589 | 2.948 | 85.4279 | 115.979 | 123.5138 | -123.8571 | -123.8297
4018.7188 | 123.8251 | -61.3953 | 62.114 | 0.14366 | 0.013888 | 0.0089274 | 0.01296 | 0.060248 | 0.00073487 | 0.079049 | -57.6508 | 62.059 | -61.7523 | -61.5738 | 54.5151 | 23.822 | 7.8186 | 7.077 | 62.0865 | -61.7157 | -0.35706 | -0.054932 | 3.7445 | -0.17853 | -7.5989 | -0.32043 | -0.027466 | 4.1016 | 69.2139 | 68.4723 | 115.9103 | 123.4543 | 3.7445 | 123.4818 | 85.2173 | -0.32043 | 123.4543 | 3.7445 | 85.2173 | 115.9103 | 123.4818 | -123.8663 | -123.8297
4019.7188 | 123.8251 | -61.441 | 62.1506 | 0.082626 | 0.013247 | 0.011064 | 0.0093288 | 0.057898 | 0.00073487 | 0.080972 | -58.4564 | 62.0636 | -61.7249 | -61.5692 | 54.4968 | 23.8586 | 7.9193 | 7.0816 | 62.0956 | -61.6928 | -0.28381 | -0.086975 | 2.9846 | -0.12817 | -7.6538 | -0.25177 | -0.054932 | 3.2684 | 69.3604 | 68.5226 | 115.9378 | 123.5046 | 2.9846 | 123.5367 | 85.2997 | -0.25177 | 123.5046 | 2.9846 | 85.2997 | 115.9378 | 123.5367 | -123.8754 | -123.8434
4020.7344 | 123.7701 | -61.4136 | 62.2101 | -0.5201 | 0.017947 | 0.0132 | 0.015951 | 0.060462 | 0.00094847 | 0.07969 | -58.4335 | 62.1964 | -61.7065 | -61.6058 | 54.483 | 23.79 | 8.0521 | 7.0221 | 62.1735 | -61.7386 | -0.29297 | -0.013733 | 2.98 | -0.19226 | -7.7271 | -0.32501 | -0.036621 | 3.273 | 69.4656 | 68.4357 | 115.8966 | 123.6099 | 2.98 | 123.587 | 85.2036 | -0.32501 | 123.6099 | 2.98 | 85.2036 | 115.8966 | 123.587 | -123.9166 | -123.9487
4021.7188 | 123.8342 | -61.4182 | 62.1872 | 0.10551 | 0.016024 | 0.010423 | 0.010824 | 0.059394 | -0.00054693 | 0.078195 | -58.4244 | 62.0911 | -61.6928 | -61.5784 | 54.5242 | 23.8266 | 7.8873 | 7.0496 | 62.114 | -61.6791 | -0.27466 | -0.096131 | 2.9938 | -0.16022 | -7.663 | -0.26093 | -0.073242 | 3.2684 | 69.3054 | 68.4677 | 115.9424 | 123.5092 | 2.9938 | 123.5321 | 85.2448 | -0.26093 | 123.5092 | 2.9938 | 85.2448 | 115.9424 | 123.5321 | -123.88 | -123.8663
4022.7188 | 123.8434 | -61.3953 | 62.1323 | 0.14366 | 0.014315 | 0.015122 | 0.013388 | 0.061743 | 0.00094847 | 0.079476 | -58.3694 | 62.1002 | -61.7203 | -61.5601 | 54.4922 | 23.8678 | 7.8094 | 7.0953 | 62.1002 | -61.6745 | -0.32501 | -0.032043 | 3.0258 | -0.1648 | -7.6401 | -0.27924 | -0.032043 | 3.3508 | 69.2047 | 68.4906 | 115.8875 | 123.4955 | 3.0258 | 123.4955 | 85.2631 | -0.27924 | 123.4955 | 3.0258 | 85.2631 | 115.8875 | 123.4955 | -123.8525 | -123.8068
4023.7344 | 123.7289 | -61.4182 | 62.2147 | -0.19966 | 0.017092 | 0.013627 | 0.013601 | 0.057685 | -0.00097413 | 0.078195 | -58.4015 | 62.1689 | -61.7203 | -61.6058 | 54.5197 | 23.8541 | 8.0521 | 7.0496 | 62.1552 | -61.702 | -0.30212 | -0.045777 | 3.0167 | -0.18768 | -7.695 | -0.28381 | -0.05951 | 3.3188 | 69.4702 | 68.4677 | 115.9378 | 123.587 | 3.0167 | 123.5733 | 85.2722 | -0.28381 | 123.587 | 3.0167 | 85.2722 | 115.9378 | 123.5733 | -123.9349 | -123.9166
4024.7188 | 123.7839 | -61.4044 | 62.146 | 0.013962 | 0.01282 | 0.01085 | 0.010397 | 0.060034 | -0.0020421 | 0.078622 | -58.4152 | 62.0819 | -61.7203 | -61.5875 | 54.5563 | 23.8861 | 7.9285 | 7.1503 | 62.114 | -61.6699 | -0.31586 | -0.064087 | 2.9892 | -0.18311 | -7.5897 | -0.2655 | -0.032043 | 3.3051 | 69.3329 | 68.5547 | 115.9607 | 123.4863 | 2.9892 | 123.5184 | 85.2905 | -0.2655 | 123.4863 | 2.9892 | 85.2905 | 115.9607 | 123.5184 | -123.8663 | -123.8159
4025.7188 | 123.8892 | -61.4182 | 62.1277 | 1.9442 | 0.016451 | 0.018968 | 0.013174 | 0.060462 | 0.0024439 | 0.081613 | -58.3099 | 62.0819 | -61.7157 | -61.5463 | 54.6295 | 23.8861 | 7.8094 | 7.1136 | 62.059 | -61.6974 | -0.29755 | -0.045777 | 3.1082 | -0.12817 | -7.4982 | -0.27924 | -0.068665 | 3.4058 | 69.2276 | 68.5318 | 116.0477 | 123.5001 | 3.1082 | 123.4772 | 85.3043 | -0.27924 | 123.5001 | 3.1082 | 85.3043 | 116.0477 | 123.4772 | -123.8434 | -123.8251
4026.7344 | 123.8434 | -61.377 | 62.1506 | 0.61668 | 0.015597 | 0.014482 | 0.0097562 | 0.058966 | -0.00033333 | 0.078835 | -58.374 | 62.0911 | -61.7203 | -61.5143 | 54.5746 | 24.0738 | 7.9559 | 7.1823 | 62.1277 | -61.6653 | -0.34332 | -0.05951 | 3.0029 | -0.13733 | -7.576 | -0.28839 | -0.022888 | 3.3463 | 69.3329 | 68.5593 | 115.9515 | 123.468 | 3.0029 | 123.5046 | 85.4507 | -0.28839 | 123.468 | 3.0029 | 85.4507 | 115.9515 | 123.5046 | -123.8708 | -123.8159
4027.7344 | 123.8846 | -61.3861 | 62.146 | -0.062332 | 0.01346 | 0.010209 | 0.0097562 | 0.057685 | -0.0016149 | 0.080331 | -58.3603 | 62.1048 | -61.7065 | -61.5189 | 54.6433 | 23.9456 | 7.8735 | 7.1823 | 62.1002 | -61.6516 | -0.32044 | -0.041199 | 3.0258 | -0.13275 | -7.5027 | -0.2655 | -0.045776 | 3.3463 | 69.2596 | 68.5684 | 116.0294 | 123.4909 | 3.0258 | 123.4863 | 85.3317 | -0.2655 | 123.4909 | 3.0258 | 85.3317 | 116.0294 | 123.4863 | -123.8525 | -123.7976
4028.7188 | 123.8434 | -61.3815 | 62.146 | 0.9829 | 0.016878 | 0.016831 | 0.014669 | 0.060034 | -0.0016149 | 0.07969 | -58.287 | 62.0682 | -61.7203 | -61.5555 | 54.5609 | 23.9594 | 7.814 | 7.1091 | 62.0956 | -61.6653 | -0.33874 | -0.07782 | 3.0945 | -0.17395 | -7.5851 | -0.28381 | -0.050354 | 3.4332 | 69.1956 | 68.4906 | 115.9424 | 123.4497 | 3.0945 | 123.4772 | 85.3409 | -0.28381 | 123.4497 | 3.0945 | 85.3409 | 115.9424 | 123.4772 | -123.8663 | -123.8113
4029.7344 | 123.88 | -61.3907 | 62.1552 | -0.09285 | 0.016024 | 0.0132 | 0.012747 | 0.058753 | -0.0024695 | 0.07734 | -58.3237 | 62.0819 | -61.6974 | -61.4868 | 54.6112 | 24.0509 | 7.8827 | 7.1732 | 62.1231 | -61.7065 | -0.3067 | -0.073242 | 3.067 | -0.09613 | -7.5439 | -0.31586 | -0.032043 | 3.3737 | 69.2734 | 68.5638 | 116.0019 | 123.4726 | 3.067 | 123.5138 | 85.4416 | -0.31586 | 123.4726 | 3.067 | 85.4416 | 116.0019 | 123.5138 | -123.8525 | -123.8617
4030.7188 | 123.8754 | -61.3998 | 62.1185 | 0.18944 | 0.014529 | 0.016191 | 0.014242 | 0.060675 | -0.00076053 | 0.080544 | -58.3557 | 62.0865 | -61.7249 | -61.528 | 54.5471 | 23.909 | 7.5851 | 6.8527 | 62.0773 | -61.7249 | -0.32501 | -0.032043 | 3.0441 | -0.12817 | -7.5714 | -0.32501 | -0.041198 | 3.3691 | 68.985 | 68.2526 | 115.947 | 123.4863 | 3.0441 | 123.4772 | 85.3088 | -0.32501 | 123.4863 | 3.0441 | 85.3088 | 115.947 | 123.4772 | -123.8434 | -123.8434
4031.7188 | 123.8617 | -61.4044 | 62.1323 | 0.10551 | 0.01581 | 0.017686 | 0.013815 | 0.058966 | 9.4068e-05 | 0.080758 | -58.3694 | 62.0911 | -61.6974 | -61.5692 | 54.5517 | 23.9914 | 7.8461 | 7.0679 | 62.1094 | -61.7065 | -0.29297 | -0.041199 | 3.035 | -0.1648 | -7.5806 | -0.30212 | -0.022888 | 3.3279 | 69.2505 | 68.4723 | 115.9561 | 123.4955 | 3.035 | 123.5138 | 85.3958 | -0.30212 | 123.4955 | 3.035 | 85.3958 | 115.9561 | 123.5138 | -123.8297 | -123.8388
4032.7344 | 123.8022 | -61.3998 | 62.0911 | 0.15892 | 0.016665 | 0.01555 | 0.016592 | 0.060889 | -0.0014013 | 0.079049 | -58.3603 | 62.1185 | -61.7249 | -61.5509 | 54.5929 | 24.0921 | 7.8598 | 7.077 | 62.0911 | -61.7249 | -0.32501 | 0.027466 | 3.0396 | -0.15106 | -7.4982 | -0.32501 | 0 | 3.3646 | 69.2596 | 68.4769 | 115.9927 | 123.5184 | 3.0396 | 123.4909 | 85.4919 | -0.32501 | 123.5184 | 3.0396 | 85.4919 | 115.9927 | 123.4909 | -123.8159 | -123.8159
4033.7188 | 123.7701 | -61.4319 | 62.1323 | 0.1284 | 0.016665 | 0.016618 | 0.02001 | 0.062812 | 0.0011621 | 0.079904 | -58.4244 | 62.178 | -61.7386 | -61.647 | 54.4968 | 23.9822 | 7.9605 | 6.9534 | 62.1323 | -61.734 | -0.3067 | 0.045777 | 3.0075 | -0.21515 | -7.6355 | -0.30212 | 0 | 3.3142 | 69.3924 | 68.3853 | 115.9287 | 123.6099 | 3.0075 | 123.5641 | 85.4141 | -0.30212 | 123.6099 | 3.0075 | 85.4141 | 115.9287 | 123.5641 | -123.8708 | -123.8663
4034.7188 | 123.7564 | -61.4182 | 62.1368 | 0.13603 | 0.017092 | 0.017259 | 0.014669 | 0.062598 | -0.00033333 | 0.078408 | -58.4152 | 62.178 | -61.7569 | -61.6287 | 54.4968 | 23.9182 | 8.0109 | 6.9717 | 62.146 | -61.7386 | -0.33875 | 0.041199 | 3.0029 | -0.21057 | -7.6401 | -0.32043 | 0.009155 | 3.3417 | 69.429 | 68.3899 | 115.9149 | 123.5962 | 3.0029 | 123.5641 | 85.3363 | -0.32043 | 123.5962 | 3.0029 | 85.3363 | 115.9149 | 123.5641 | -123.8937 | -123.8754
4035.7344 | 123.8937 | -61.3724 | 62.1277 | -0.26833 | 0.014315 | 0.011064 | 0.0065518 | 0.061957 | -0.00097413 | 0.080117 | -58.3374 | 62.1048 | -61.7157 | -61.5097 | 54.6249 | 24.1241 | 7.9147 | 7.1274 | 62.1368 | -61.6608 | -0.34332 | -0.022889 | 3.035 | -0.13733 | -7.5027 | -0.28839 | 0.009155 | 3.3783 | 69.2871 | 68.4998 | 115.9973 | 123.4772 | 3.035 | 123.5092 | 85.4965 | -0.28839 | 123.4772 | 3.035 | 85.4965 | 115.9973 | 123.5092 | -123.8434 | -123.7885
4036.7188 | 123.8709 | -61.3998 | 62.1185 | 0.21996 | 0.017306 | 0.012345 | 0.013174 | 0.062598 | -0.00076053 | 0.078195 | -58.3557 | 62.0865 | -61.7157 | -61.5738 | 54.5334 | 24.0417 | 7.869 | 7.077 | 62.0911 | -61.7294 | -0.31586 | -0.032043 | 3.0441 | -0.17395 | -7.5851 | -0.32959 | -0.027466 | 3.36 | 69.2688 | 68.4769 | 115.9332 | 123.4863 | 3.0441 | 123.4909 | 85.4416 | -0.32959 | 123.4863 | 3.0441 | 85.4416 | 115.9332 | 123.4909 | -123.8342 | -123.848
4037.7188 | 123.8297 | -61.4182 | 62.146 | -0.039444 | 0.012606 | 0.013841 | 0.0095424 | 0.059607 | -0.00033333 | 0.079476 | -58.4198 | 62.0911 | -61.7386 | -61.5646 | 54.5792 | 24.1516 | 7.933 | 7.0953 | 62.1048 | -61.702 | -0.32043 | -0.054932 | 2.9984 | -0.14648 | -7.5668 | -0.28381 | -0.041199 | 3.3188 | 69.3512 | 68.5135 | 115.9973 | 123.5092 | 2.9984 | 123.5229 | 85.5698 | -0.28381 | 123.5092 | 2.9984 | 85.5698 | 115.9973 | 123.5229 | -123.8846 | -123.848
4038.7344 | 124.0082 | -61.3632 | 62.2192 | -0.16151 | 0.011538 | 0.0080728 | 0.010824 | 0.057257 | -0.0024695 | 0.077126 | -58.342 | 62.0911 | -61.7065 | -61.5097 | 54.6295 | 24.1837 | 7.9193 | 7.1457 | 62.1002 | -61.6653 | -0.34332 | -0.12817 | 3.0212 | -0.14648 | -7.5897 | -0.30212 | -0.11902 | 3.3646 | 69.2825 | 68.5089 | 115.9927 | 123.4543 | 3.0212 | 123.4634 | 85.5469 | -0.30212 | 123.4543 | 3.0212 | 85.5469 | 115.9927 | 123.4634 | -123.9258 | -123.8846
4039.7188 | 123.8571 | -61.3907 | 62.114 | 0.19707 | 0.016238 | 0.016404 | 0.012747 | 0.059607 | -0.00097413 | 0.080758 | -58.3466 | 62.0728 | -61.6974 | -61.5555 | 54.5837 | 24.1058 | 7.7957 | 7.0862 | 62.0728 | -61.6837 | -0.3067 | -0.041199 | 3.0441 | -0.16479 | -7.5302 | -0.29297 | -0.041199 | 3.3508 | 69.1864 | 68.4769 | 115.9744 | 123.4634 | 3.0441 | 123.4634 | 85.4965 | -0.29297 | 123.4634 | 3.0441 | 85.4965 | 115.9744 | 123.4634 | -123.8113 | -123.7976
4040.7188 | 123.8388 | -61.4182 | 62.1323 | 0.12077 | 0.014742 | 0.0132 | 0.01232 | 0.061316 | -0.0014013 | 0.079904 | -58.3649 | 62.0911 | -61.7157 | -61.5463 | 54.5013 | 24.0875 | 7.8415 | 7.0496 | 62.0911 | -61.7111 | -0.29755 | -0.041199 | 3.0533 | -0.12817 | -7.6309 | -0.29297 | -0.041199 | 3.3508 | 69.2596 | 68.4677 | 115.9195 | 123.5092 | 3.0533 | 123.5092 | 85.5057 | -0.29297 | 123.5092 | 3.0533 | 85.5057 | 115.9195 | 123.5092 | -123.848 | -123.8434
4041.7188 | 123.8113 | -61.4182 | 62.1231 | -0.024185 | 0.013247 | 0.014695 | 0.011892 | 0.058325 | -0.0024695 | 0.076699 | -58.4198 | 62.0819 | -61.7386 | -61.5372 | 54.4373 | 23.9868 | 7.9651 | 7.045 | 62.1094 | -61.6974 | -0.32043 | -0.041199 | 2.9984 | -0.11902 | -7.6859 | -0.27924 | -0.013733 | 3.3188 | 69.3832 | 68.4631 | 115.8554 | 123.5001 | 2.9984 | 123.5275 | 85.405 | -0.27924 | 123.5001 | 2.9984 | 85.405 | 115.8554 | 123.5275 | -123.8617 | -123.8205
4042.7344 | 123.8571 | -61.409 | 62.1506 | -0.0089264 | 0.014315 | 0.010636 | 0.0097562 | 0.059821 | 0.0024439 | 0.07969 | -58.4244 | 62.0773 | -61.7294 | -61.5601 | 54.483 | 23.9594 | 7.9376 | 7.077 | 62.1048 | -61.702 | -0.32043 | -0.073242 | 2.9846 | -0.15106 | -7.6675 | -0.29297 | -0.045777 | 3.3051 | 69.3466 | 68.486 | 115.892 | 123.4863 | 2.9846 | 123.5138 | 85.3683 | -0.29297 | 123.4863 | 2.9846 | 85.3683 | 115.892 | 123.5138 | -123.88 | -123.8525
4043.7188 | 123.8617 | -61.409 | 62.1368 | 0.31914 | 0.016238 | 0.0089274 | 0.013815 | 0.06153 | 0.0018031 | 0.078622 | -58.3328 | 62.1002 | -61.7065 | -61.5463 | 54.5288 | 24.1379 | 7.9742 | 7.3837 | 62.0682 | -61.702 | -0.29755 | -0.036621 | 3.0762 | -0.13733 | -7.608 | -0.29297 | -0.068665 | 3.3737 | 69.3832 | 68.7927 | 115.9378 | 123.5092 | 3.0762 | 123.4772 | 85.5469 | -0.29297 | 123.5092 | 3.0762 | 85.5469 | 115.9378 | 123.4772 | -123.8434 | -123.8388
4044.7344 | 123.9899 | -61.3632 | 62.2147 | -0.15388 | 0.013247 | 0.009141 | 0.0099698 | 0.057044 | -0.0014013 | 0.077981 | -58.3374 | 62.0911 | -61.6928 | -61.4822 | 54.5746 | 24.1013 | 8.0887 | 7.4799 | 62.1002 | -61.6653 | -0.32959 | -0.1236 | 3.0258 | -0.11902 | -7.6401 | -0.30212 | -0.11444 | 3.3554 | 69.4519 | 68.8431 | 115.9378 | 123.4543 | 3.0258 | 123.4634 | 85.4645 | -0.30212 | 123.4543 | 3.0258 | 85.4645 | 115.9378 | 123.4634 | -123.9075 | -123.88
4045.7188 | 123.8388 | -61.4136 | 62.1048 | 0.21233 | 0.014529 | 0.021531 | 0.014456 | 0.061743 | -0.00097413 | 0.080331 | -58.5297 | 62.0819 | -61.7386 | -61.5463 | 54.5197 | 24.1287 | 7.9559 | 7.3425 | 62.1002 | -61.7432 | -0.32501 | -0.022888 | 2.8839 | -0.13275 | -7.5851 | -0.32959 | -0.004577 | 3.2089 | 69.3695 | 68.7561 | 115.9332 | 123.4955 | 2.8839 | 123.5138 | 85.5423 | -0.32959 | 123.4955 | 2.8839 | 85.5423 | 115.9332 | 123.5138 | -123.8434 | -123.848
4046.7188 | 123.8388 | -61.4044 | 62.1277 | 0.22758 | 0.017519 | 0.01555 | 0.015097 | 0.062598 | -0.00076053 | 0.081826 | -58.3878 | 62.1094 | -61.7523 | -61.5829 | 54.5425 | 24.0417 | 7.9376 | 7.3151 | 62.0773 | -61.7294 | -0.3479 | -0.018311 | 3.0167 | -0.17853 | -7.5851 | -0.32501 | -0.050354 | 3.3646 | 69.342 | 68.7195 | 115.947 | 123.5138 | 3.0167 | 123.4818 | 85.4462 | -0.32501 | 123.5138 | 3.0167 | 85.4462 | 115.947 | 123.4818 | -123.88 | -123.8571
4047.7344 | 123.7381 | -61.4044 | 62.1918 | -0.14626 | 0.01581 | 0.013841 | 0.011892 | 0.059394 | -0.0014013 | 0.078408 | -58.4335 | 62.1643 | -61.7706 | -61.6196 | 54.4693 | 23.9777 | 8.1802 | 7.2968 | 62.1506 | -61.6837 | -0.36621 | -0.027465 | 2.9709 | -0.21515 | -7.7225 | -0.27924 | -0.041198 | 3.3371 | 69.5847 | 68.7012 | 115.8737 | 123.5687 | 2.9709 | 123.555 | 85.3821 | -0.27924 | 123.5687 | 2.9709 | 85.3821 | 115.8737 | 123.555 | -123.9624 | -123.8754
4048.7344 | 123.6649 | -61.4273 | 62.1735 | -0.10811 | 0.017519 | 0.017045 | 0.017233 | 0.062384 | -0.0024695 | 0.07734 | -58.3328 | 62.2009 | -61.6974 | -61.5692 | 54.5288 | 23.9777 | 8.1573 | 7.3746 | 62.178 | -61.7569 | -0.27008 | 0.027466 | 3.0945 | -0.14191 | -7.6447 | -0.32959 | 0.004578 | 3.3646 | 69.5847 | 68.8019 | 115.9561 | 123.6282 | 3.0945 | 123.6053 | 85.405 | -0.32959 | 123.6282 | 3.0945 | 85.405 | 115.9561 | 123.6053 | -123.8708 | -123.9304
4049.7188 | 123.8068 | -61.4365 | 62.1185 | 0.16655 | 0.016238 | 0.014268 | 0.014242 | 0.063025 | -0.00097413 | 0.080972 | -58.3786 | 62.1094 | -61.7203 | -61.5601 | 54.5197 | 24.0875 | 7.9514 | 7.402 | 62.1002 | -61.7203 | -0.28381 | -0.009155 | 3.0579 | -0.1236 | -7.5989 | -0.28381 | -0.01831 | 3.3417 | 69.3878 | 68.8385 | 115.9561 | 123.5458 | 3.0579 | 123.5367 | 85.524 | -0.28381 | 123.5458 | 3.0579 | 85.524 | 115.9561 | 123.5367 | -123.8388 | -123.8388
4050.7344 | 123.8525 | -61.377 | 62.146 | -0.09285 | 0.013888 | 0.011491 | 0.0065518 | 0.062598 | -0.0018285 | 0.081185 | -58.3832 | 62.0911 | -61.7294 | -61.5143 | 54.5975 | 24.0829 | 7.9971 | 7.4524 | 62.1094 | -61.6379 | -0.35248 | -0.054932 | 2.9938 | -0.13733 | -7.5485 | -0.26093 | -0.036621 | 3.3463 | 69.3741 | 68.8293 | 115.9744 | 123.468 | 2.9938 | 123.4863 | 85.4599 | -0.26093 | 123.468 | 2.9938 | 85.4599 | 115.9744 | 123.4863 | -123.8754 | -123.7839
4051.7188 | 123.8663 | -61.3907 | 62.1231 | 0.13603 | 0.014529 | 0.0082864 | 0.012747 | 0.060462 | -0.0014013 | 0.08204 | -58.3466 | 62.1048 | -61.7386 | -61.5692 | 54.4876 | 24.1058 | 7.8873 | 7.3746 | 62.0911 | -61.6974 | -0.3479 | -0.018311 | 3.0441 | -0.17853 | -7.6355 | -0.3067 | -0.032044 | 3.392 | 69.278 | 68.7653 | 115.8783 | 123.4955 | 3.0441 | 123.4818 | 85.4965 | -0.3067 | 123.4955 | 3.0441 | 85.4965 | 115.8783 | 123.4818 | -123.8617 | -123.8205
4052.7188 | 123.8388 | -61.3861 | 62.1277 | 0.18944 | 0.015169 | 0.013841 | 0.015097 | 0.061103 | 0.00073487 | 0.080758 | -58.374 | 62.1048 | -61.7249 | -61.5646 | 54.5746 | 24.1379 | 7.901 | 7.3883 | 62.0728 | -61.7294 | -0.33875 | -0.022889 | 3.0121 | -0.17853 | -7.5531 | -0.34332 | -0.054932 | 3.3508 | 69.2871 | 68.7744 | 115.9607 | 123.4909 | 3.0121 | 123.4589 | 85.524 | -0.34332 | 123.4909 | 3.0121 | 85.524 | 115.9607 | 123.4589 | -123.8525 | -123.8571
4053.7188 | 123.8297 | -61.4136 | 62.1506 | 0.021591 | 0.015383 | 0.014482 | 0.0074062 | 0.058753 | -0.0037511 | 0.080117 | -58.4198 | 62.0773 | -61.7203 | -61.5921 | 54.4876 | 23.9914 | 7.9971 | 7.3837 | 62.0911 | -61.6882 | -0.3067 | -0.073242 | 2.9938 | -0.17853 | -7.663 | -0.27466 | -0.05951 | 3.3005 | 69.4107 | 68.7973 | 115.9012 | 123.4909 | 2.9938 | 123.5046 | 85.405 | -0.27466 | 123.4909 | 2.9938 | 85.405 | 115.9012 | 123.5046 | -123.8708 | -123.8388
4054.7188 | 123.7839 | -61.4319 | 62.1552 | 0.15129 | 0.016238 | 0.015763 | 0.017447 | 0.060462 | -0.00011953 | 0.078622 | -58.4152 | 62.178 | -61.7798 | -61.6425 | 54.4464 | 23.9456 | 8.0383 | 7.283 | 62.1002 | -61.7661 | -0.3479 | 0.022889 | 3.0167 | -0.21057 | -7.7087 | -0.33417 | -0.054931 | 3.3646 | 69.4702 | 68.7149 | 115.8783 | 123.6099 | 3.0167 | 123.5321 | 85.3775 | -0.33417 | 123.6099 | 3.0167 | 85.3775 | 115.8783 | 123.5321 | -123.9349 | -123.9212
4055.7188 | 123.8709 | -61.4227 | 62.1048 | 1.5246 | 0.014101 | 0.013627 | 0.014669 | 0.06153 | 0.00052127 | 0.079476 | -58.2458 | 62.0636 | -61.7386 | -61.5372 | 54.4968 | 24.0372 | 7.9193 | 7.4112 | 62.0956 | -61.7065 | -0.31586 | -0.041198 | 3.1769 | -0.11444 | -7.608 | -0.28381 | -0.009155 | 3.4927 | 69.342 | 68.8339 | 115.9195 | 123.4863 | 3.1769 | 123.5184 | 85.4599 | -0.28381 | 123.4863 | 3.1769 | 85.4599 | 115.9195 | 123.5184 | -123.8434 | -123.8113
4056.7344 | 123.8571 | -61.3724 | 62.1368 | -0.16914 | 0.014956 | 0.013413 | 0.0095424 | 0.058325 | 0.00030767 | 0.078835 | -58.374 | 62.1048 | -61.7111 | -61.5097 | 54.5654 | 24.1608 | 8.02 | 7.5211 | 62.1094 | -61.6837 | -0.33875 | -0.032044 | 2.9984 | -0.13733 | -7.5714 | -0.31128 | -0.027466 | 3.3371 | 69.3924 | 68.8934 | 115.9378 | 123.4772 | 2.9984 | 123.4818 | 85.5331 | -0.31128 | 123.4772 | 2.9984 | 85.5331 | 115.9378 | 123.4818 | -123.848 | -123.8205
4057.7344 | 123.7747 | -61.3953 | 62.1872 | -0.29121 | 0.01581 | 0.014695 | 0.01296 | 0.060248 | -0.0014013 | 0.079476 | -58.3649 | 62.1323 | -61.702 | -61.5601 | 54.4647 | 24.0189 | 8.107 | 7.3792 | 62.1414 | -61.7294 | -0.3067 | -0.054932 | 3.0304 | -0.1648 | -7.7225 | -0.33417 | -0.045777 | 3.3371 | 69.5023 | 68.7744 | 115.86 | 123.5275 | 3.0304 | 123.5367 | 85.4141 | -0.33417 | 123.5275 | 3.0304 | 85.4141 | 115.86 | 123.5367 | -123.8892 | -123.9166
4058.7188 | 123.8571 | -61.3953 | 62.1368 | 0.25047 | 0.014742 | 0.011491 | 0.017233 | 0.066657 | -0.00076053 | 0.077981 | -58.3511 | 62.1002 | -61.7111 | -61.4182 | 54.5471 | 23.9777 | 7.9834 | 7.4158 | 62.0956 | -61.6974 | -0.31586 | -0.036621 | 3.0441 | -0.022888 | -7.5897 | -0.30212 | -0.041199 | 3.36 | 69.3787 | 68.811 | 115.9424 | 123.4955 | 3.0441 | 123.4909 | 85.3729 | -0.30212 | 123.4955 | 3.0441 | 85.3729 | 115.9424 | 123.4909 | -123.848 | -123.8342
4059.7188 | 123.8251 | -61.4182 | 62.1506 | 0.059738 | 0.014742 | 0.013627 | 0.010397 | 0.05918 | -0.0016149 | 0.077981 | -58.429 | 62.0728 | -61.7203 | -61.6013 | 54.4601 | 24.0463 | 8.0017 | 7.3883 | 62.114 | -61.7065 | -0.30212 | -0.07782 | 2.9892 | -0.1831 | -7.6904 | -0.28839 | -0.036621 | 3.2913 | 69.4199 | 68.8065 | 115.8783 | 123.4909 | 2.9892 | 123.5321 | 85.4645 | -0.28839 | 123.4909 | 2.9892 | 85.4645 | 115.8783 | 123.5321 | -123.8708 | -123.8571
4060.7188 | 123.8754 | -61.4182 | 62.1277 | 0.11314 | 0.016451 | 0.014054 | 0.015738 | 0.059394 | -0.0014013 | 0.079476 | -58.3603 | 62.114 | -61.7294 | -61.702 | 54.2908 | 24.1379 | 8.0338 | 7.3517 | 62.0865 | -61.7157 | -0.31128 | -0.013733 | 3.0579 | -0.28381 | -7.8369 | -0.29755 | -0.041199 | 3.3691 | 69.4519 | 68.7698 | 115.7089 | 123.5321 | 3.0579 | 123.5046 | 85.556 | -0.29755 | 123.5321 | 3.0579 | 85.556 | 115.7089 | 123.5046 | -123.8571 | -123.8434
4061.7344 | 123.7701 | -61.409 | 62.1552 | -0.29121 | 0.01346 | 0.015977 | 0.011892 | 0.060889 | -0.0022559 | 0.080544 | -58.3603 | 62.1048 | -61.6928 | -61.5463 | 54.5059 | 24.0417 | 8.075 | 7.402 | 62.1323 | -61.7111 | -0.28381 | -0.050354 | 3.0487 | -0.13733 | -7.6492 | -0.30212 | -0.022888 | 3.3325 | 69.4839 | 68.811 | 115.9149 | 123.5138 | 3.0487 | 123.5413 | 85.4507 | -0.30212 | 123.5138 | 3.0487 | 85.4507 | 115.9149 | 123.5413 | -123.848 | -123.8663
4062.7188 | 123.8297 | -61.4182 | 62.1231 | 0.17418 | 0.016024 | 0.013841 | 0.016806 | 0.060248 | -0.00097413 | 0.078835 | -58.4152 | 62.1231 | -61.7477 | -61.5967 | 54.4281 | 24.0372 | 7.9285 | 7.3334 | 62.1048 | -61.7294 | -0.32959 | 0 | 3.0029 | -0.17853 | -7.695 | -0.31128 | -0.018311 | 3.3325 | 69.3466 | 68.7515 | 115.8463 | 123.5413 | 3.0029 | 123.5229 | 85.4553 | -0.31128 | 123.5413 | 3.0029 | 85.4553 | 115.8463 | 123.5229 | -123.8709 | -123.8525
4063.7188 | 123.8205 | -61.409 | 62.1094 | 0.15129 | 0.015169 | 0.011918 | 0.011251 | 0.060248 | -0.00097413 | 0.079049 | -58.4015 | 62.1048 | -61.702 | -61.5738 | 54.5013 | 24.1013 | 7.8735 | 7.3517 | 62.0682 | -61.7203 | -0.29297 | -0.004578 | 3.0075 | -0.16479 | -7.608 | -0.31128 | -0.041199 | 3.3005 | 69.2825 | 68.7607 | 115.9103 | 123.5138 | 3.0075 | 123.4772 | 85.5103 | -0.31128 | 123.5138 | 3.0075 | 85.5103 | 115.9103 | 123.4772 | -123.8113 | -123.8297
4064.7188 | 123.88 | -61.3907 | 62.1368 | -0.039444 | 0.014529 | 0.011918 | 0.0074062 | 0.058112 | 9.4068e-05 | 0.080117 | -58.4152 | 62.0773 | -61.734 | -61.5555 | 54.5151 | 24.1745 | 8.0063 | 7.4066 | 62.0956 | -61.6974 | -0.34332 | -0.059509 | 2.9755 | -0.16479 | -7.6218 | -0.3067 | -0.041199 | 3.3188 | 69.397 | 68.7973 | 115.9058 | 123.468 | 2.9755 | 123.4863 | 85.5652 | -0.3067 | 123.468 | 2.9755 | 85.5652 | 115.9058 | 123.4863 | -123.8708 | -123.8342
4065.7188 | 123.88 | -61.409 | 62.1231 | 0.15129 | 0.017519 | 0.011277 | 0.013388 | 0.05918 | 0.0013757 | 0.080544 | -58.3694 | 62.0682 | -61.7157 | -61.5601 | 54.5151 | 24.2111 | 7.9056 | 7.3792 | 62.059 | -61.734 | -0.3067 | -0.054932 | 3.0396 | -0.15106 | -7.608 | -0.32501 | -0.064087 | 3.3463 | 69.3146 | 68.7881 | 115.9241 | 123.4772 | 3.0396 | 123.468 | 85.6201 | -0.32501 | 123.4772 | 3.0396 | 85.6201 | 115.9241 | 123.468 | -123.8388 | -123.8571
4066.7188 | 123.8754 | -61.3953 | 62.146 | -0.054703 | 0.014529 | 0.0099954 | 0.008688 | 0.05918 | -0.0011877 | 0.077767 | -58.429 | 62.0819 | -61.6974 | -61.5646 | 54.4968 | 24.1379 | 8.0063 | 7.4112 | 62.1277 | -61.6882 | -0.30212 | -0.064087 | 2.9663 | -0.16937 | -7.6492 | -0.29297 | -0.01831 | 3.2684 | 69.4016 | 68.8065 | 115.892 | 123.4772 | 2.9663 | 123.5229 | 85.5331 | -0.29297 | 123.4772 | 2.9663 | 85.5331 | 115.892 | 123.5229 | -123.8434 | -123.8342
4067.7188 | 123.7885 | -61.4136 | 62.1323 | 0.18944 | 0.011324 | 0.016191 | 0.0080472 | 0.058325 | 0.00073487 | 0.080331 | -58.4473 | 62.1002 | -61.7386 | -61.6013 | 54.3961 | 24.0601 | 7.9651 | 7.338 | 62.1002 | -61.7157 | -0.32501 | -0.032043 | 2.9663 | -0.18768 | -7.7362 | -0.30212 | -0.032043 | 3.2913 | 69.3787 | 68.7515 | 115.8096 | 123.5138 | 2.9663 | 123.5138 | 85.4736 | -0.30212 | 123.5138 | 2.9663 | 85.4736 | 115.8096 | 123.5138 | -123.8708 | -123.848
4068.7188 | 123.8434 | -61.4044 | 62.1048 | 0.15129 | 0.01282 | 0.013627 | 0.015524 | 0.060462 | -0.0024695 | 0.080117 | -58.374 | 62.0819 | -61.7157 | -61.5463 | 54.4739 | 24.2111 | 7.6492 | 7.1915 | 62.0453 | -61.7386 | -0.31128 | -0.022888 | 3.0304 | -0.14191 | -7.6309 | -0.33417 | -0.059509 | 3.3417 | 69.0537 | 68.5959 | 115.8783 | 123.4863 | 3.0304 | 123.4497 | 85.6155 | -0.33417 | 123.4863 | 3.0304 | 85.6155 | 115.8783 | 123.4497 | -123.8205 | -123.8434
4069.7188 | 123.8937 | -61.3998 | 62.1414 | -0.08522 | 0.012606 | 0.0085 | 0.0097562 | 0.059394 | 9.4068e-05 | 0.07734 | -58.3649 | 62.0911 | -61.6974 | -61.5326 | 54.5059 | 24.2844 | 7.9697 | 7.4707 | 62.114 | -61.6791 | -0.29755 | -0.050354 | 3.035 | -0.13275 | -7.6355 | -0.27924 | -0.027465 | 3.3325 | 69.3695 | 68.8705 | 115.9058 | 123.4909 | 3.035 | 123.5138 | 85.6842 | -0.27924 | 123.4909 | 3.035 | 85.6842 | 115.9058 | 123.5138 | -123.8388 | -123.8205
4070.7188 | 123.8388 | -61.4044 | 62.146 | 0.18181 | 0.015169 | 0.014909 | 0.0099698 | 0.060675 | -0.00033333 | 0.078835 | -58.429 | 62.059 | -61.7477 | -61.5967 | 54.4418 | 24.234 | 7.9422 | 7.3334 | 62.0956 | -61.702 | -0.34332 | -0.086975 | 2.9755 | -0.19226 | -7.7042 | -0.29755 | -0.050354 | 3.3188 | 69.3466 | 68.7378 | 115.8463 | 123.4634 | 2.9755 | 123.5001 | 85.6384 | -0.29755 | 123.4634 | 2.9755 | 85.6384 | 115.8463 | 123.5001 | -123.8937 | -123.848
4071.7344 | 123.761 | -61.4273 | 62.178 | -0.26833 | 0.015169 | 0.011704 | 0.011892 | 0.058325 | -0.00076053 | 0.078835 | -58.4335 | 62.1735 | -61.734 | -61.6058 | 54.483 | 24.1653 | 8.1573 | 7.3746 | 62.1826 | -61.7203 | -0.3067 | -0.004578 | 2.9938 | -0.17853 | -7.695 | -0.29297 | 0.004577 | 3.3005 | 69.5847 | 68.8019 | 115.9103 | 123.6008 | 2.9938 | 123.6099 | 85.5927 | -0.29297 | 123.6008 | 2.9938 | 85.5927 | 115.9103 | 123.6099 | -123.912 | -123.8983
4072.7188 | 123.8525 | -61.4319 | 62.1597 | -0.0012969 | 0.014101 | 0.012773 | 0.0095424 | 0.05918 | -0.00054693 | 0.080758 | -58.4427 | 62.0911 | -61.7203 | -61.5921 | 54.5013 | 24.1699 | 8.02 | 7.4203 | 62.1185 | -61.7065 | -0.28839 | -0.068665 | 2.9892 | -0.16022 | -7.6584 | -0.27466 | -0.041199 | 3.2776 | 69.4519 | 68.8522 | 115.9332 | 123.5229 | 2.9892 | 123.5504 | 85.6018 | -0.27466 | 123.5229 | 2.9892 | 85.6018 | 115.9332 | 123.5504 | -123.88 | -123.8663
4073.7188 | 123.8205 | -61.3998 | 62.1094 | 0.090256 | 0.013888 | 0.014268 | 0.013174 | 0.057471 | 0.00073487 | 0.079904 | -58.3969 | 62.0728 | -61.7477 | -61.5829 | 54.4601 | 24.115 | 7.933 | 7.3471 | 62.0773 | -61.7203 | -0.3479 | -0.036621 | 3.0029 | -0.18311 | -7.6492 | -0.32043 | -0.032043 | 3.3508 | 69.3329 | 68.7469 | 115.86 | 123.4726 | 3.0029 | 123.4772 | 85.5148 | -0.32043 | 123.4726 | 3.0029 | 85.5148 | 115.86 | 123.4772 | -123.8571 | -123.8297
4074.7188 | 123.8159 | -61.377 | 62.1872 | -0.08522 | 0.012606 | 0.010636 | 0.0099698 | 0.05683 | 0.0024439 | 0.077554 | -58.3466 | 62.0819 | -61.702 | -61.5005 | 54.538 | 24.1974 | 7.9971 | 7.4844 | 62.114 | -61.6699 | -0.32501 | -0.10529 | 3.0304 | -0.1236 | -7.6492 | -0.29297 | -0.073242 | 3.3554 | 69.3741 | 68.8614 | 115.9149 | 123.4589 | 3.0304 | 123.4909 | 85.5743 | -0.29297 | 123.4589 | 3.0304 | 85.5743 | 115.9149 | 123.4909 | -123.8892 | -123.8571
4075.7188 | 123.8297 | -61.4227 | 62.146 | 0.17418 | 0.014956 | 0.014482 | 0.011251 | 0.059607 | -0.00076053 | 0.07969 | -58.3923 | 62.0499 | -61.7386 | -61.5784 | 54.4785 | 24.1379 | 7.9468 | 7.402 | 62.0819 | -61.702 | -0.31586 | -0.09613 | 3.0304 | -0.15564 | -7.6675 | -0.27924 | -0.064087 | 3.3463 | 69.3695 | 68.8248 | 115.9012 | 123.4726 | 3.0304 | 123.5046 | 85.5606 | -0.27924 | 123.4726 | 3.0304 | 85.5606 | 115.9012 | 123.5046 | -123.8846 | -123.848
4076.7188 | 123.8205 | -61.4182 | 62.1277 | 0.059738 | 0.015597 | 0.012345 | 0.0095424 | 0.060675 | -0.0014013 | 0.080758 | -58.4473 | 62.0773 | -61.7111 | -61.6058 | 54.5105 | 24.1013 | 7.9926 | 7.3975 | 62.0865 | -61.6837 | -0.29297 | -0.050354 | 2.9709 | -0.18768 | -7.6172 | -0.2655 | -0.041199 | 3.2639 | 69.4107 | 68.8156 | 115.9287 | 123.4955 | 2.9709 | 123.5046 | 85.5194 | -0.2655 | 123.4955 | 2.9709 | 85.5194 | 115.9287 | 123.5046 | -123.8388 | -123.8113
4077.7188 | 123.793 | -61.409 | 62.1414 | 0.15892 | 0.01581 | 0.014695 | 0.0095424 | 0.05918 | 0.0013757 | 0.079904 | -58.4335 | 62.0682 | -61.734 | -61.6013 | 54.4739 | 24.1882 | 7.9834 | 7.3746 | 62.1094 | -61.7294 | -0.32501 | -0.073242 | 2.9755 | -0.19226 | -7.6675 | -0.32043 | -0.032043 | 3.3005 | 69.3924 | 68.7836 | 115.8829 | 123.4772 | 2.9755 | 123.5184 | 85.5972 | -0.32043 | 123.4772 | 2.9755 | 85.5972 | 115.8829 | 123.5184 | -123.8754 | -123.8708
4078.7188 | 123.8297 | -61.4182 | 62.1414 | 0.074997 | 0.013033 | 0.014054 | 0.011038 | 0.06153 | -0.00076053 | 0.07969 | -58.429 | 62.0636 | -61.7432 | -61.5967 | 54.5105 | 24.1241 | 7.9742 | 7.3563 | 62.0865 | -61.6837 | -0.32501 | -0.077819 | 2.9892 | -0.17853 | -7.6309 | -0.2655 | -0.054931 | 3.3142 | 69.3924 | 68.7744 | 115.9287 | 123.4818 | 2.9892 | 123.5046 | 85.5423 | -0.2655 | 123.4818 | 2.9892 | 85.5423 | 115.9287 | 123.5046 | -123.8846 | -123.8251
4079.7344 | 123.8205 | -61.3861 | 62.1597 | -0.23781 | 0.014315 | 0.009141 | 0.0095424 | 0.057898 | -0.0024695 | 0.079476 | -58.3603 | 62.0956 | -61.6974 | -61.528 | 54.57 | 24.1974 | 8.0658 | 7.4707 | 62.1323 | -61.6882 | -0.31128 | -0.064087 | 3.0258 | -0.14191 | -7.5897 | -0.30212 | -0.027466 | 3.3371 | 69.4519 | 68.8568 | 115.9561 | 123.4818 | 3.0258 | 123.5184 | 85.5835 | -0.30212 | 123.4818 | 3.0258 | 85.5835 | 115.9561 | 123.5184 | -123.8571 | -123.848
4080.7188 | 123.848 | -61.3998 | 62.146 | -0.031814 | 0.013888 | 0.017259 | 0.0097562 | 0.059394 | -0.00076053 | 0.07969 | -58.429 | 62.0865 | -61.7249 | -61.5646 | 54.5654 | 24.2157 | 8.0109 | 7.4203 | 62.1231 | -61.6745 | -0.32501 | -0.059509 | 2.9709 | -0.16479 | -7.5806 | -0.27466 | -0.022888 | 3.2959 | 69.4107 | 68.8202 | 115.9653 | 123.4863 | 2.9709 | 123.5229 | 85.6155 | -0.27466 | 123.4863 | 2.9709 | 85.6155 | 115.9653 | 123.5229 | -123.8708 | -123.8205
4081.7188 | 123.8617 | -61.4136 | 62.1735 | -0.069961 | 0.013247 | 0.014909 | 0.0089016 | 0.059607 | -0.00011953 | 0.081613 | -58.4473 | 62.0773 | -61.7157 | -61.5601 | 54.5654 | 24.2249 | 8.0154 | 7.3929 | 62.0911 | -61.6699 | -0.30212 | -0.09613 | 2.9663 | -0.14649 | -7.608 | -0.25635 | -0.082398 | 3.2684 | 69.429 | 68.8065 | 115.979 | 123.4909 | 2.9663 | 123.5046 | 85.6384 | -0.25635 | 123.4909 | 2.9663 | 85.6384 | 115.979 | 123.5046 | -123.8892 | -123.8434
4082.7188 | 123.8068 | -61.4182 | 62.1368 | 0.1284 | 0.013674 | 0.014909 | 0.011038 | 0.057685 | 0.0022303 | 0.079263 | -58.3969 | 62.0499 | -61.7294 | -61.5921 | 54.5609 | 24.2294 | 7.9376 | 7.3608 | 62.0773 | -61.7065 | -0.31128 | -0.086975 | 3.0212 | -0.17395 | -7.576 | -0.28839 | -0.059509 | 3.3325 | 69.3558 | 68.779 | 115.979 | 123.468 | 3.0212 | 123.4955 | 85.6476 | -0.28839 | 123.468 | 3.0212 | 85.6476 | 115.979 | 123.4955 | -123.8663 | -123.8434
4083.7188 | 123.7885 | -61.4182 | 62.1368 | 0.04448 | 0.014101 | 0.012132 | 0.0091152 | 0.057898 | 0.0011621 | 0.078835 | -58.4427 | 62.0819 | -61.7294 | -61.5875 | 54.5471 | 24.1837 | 7.9971 | 7.3883 | 62.0819 | -61.702 | -0.31128 | -0.054932 | 2.9755 | -0.16937 | -7.5897 | -0.28381 | -0.054932 | 3.2867 | 69.4153 | 68.8065 | 115.9653 | 123.5001 | 2.9755 | 123.5001 | 85.6018 | -0.28381 | 123.5001 | 2.9755 | 85.6018 | 115.9653 | 123.5001 | -123.8663 | -123.8388
4084.7188 | 123.848 | -61.377 | 62.1414 | -0.10811 | 0.011751 | 0.010423 | 0.0065518 | 0.059607 | -0.0018285 | 0.077554 | -58.4061 | 62.0682 | -61.7249 | -61.5326 | 54.5563 | 24.1791 | 7.9559 | 7.4387 | 62.1002 | -61.7111 | -0.3479 | -0.073242 | 2.9709 | -0.15564 | -7.5851 | -0.33417 | -0.041198 | 3.3188 | 69.3329 | 68.8156 | 115.9332 | 123.4451 | 2.9709 | 123.4772 | 85.556 | -0.33417 | 123.4451 | 2.9709 | 85.556 | 115.9332 | 123.4772 | -123.8663 | -123.8525
4085.7188 | 123.8113 | -61.4044 | 62.1231 | 0.12077 | 0.016024 | 0.011491 | 0.0076198 | 0.058539 | -0.00011953 | 0.07969 | -58.4427 | 62.0773 | -61.7249 | -61.6013 | 54.57 | 24.147 | 7.9651 | 7.3746 | 62.1002 | -61.6882 | -0.32044 | -0.045776 | 2.9617 | -0.19684 | -7.5531 | -0.28381 | -0.022888 | 3.2822 | 69.3695 | 68.779 | 115.9744 | 123.4818 | 2.9617 | 123.5046 | 85.5515 | -0.28381 | 123.4818 | 2.9617 | 85.5515 | 115.9744 | 123.5046 | -123.848 | -123.8113
4086.7188 | 123.8709 | -61.3861 | 62.1277 | 0.013962 | 0.014742 | 0.014695 | 0.0082608 | 0.059394 | 9.4068e-05 | 0.080331 | -58.4152 | 62.0682 | -61.7432 | -61.5601 | 54.6204 | 24.234 | 7.9651 | 7.4203 | 62.0911 | -61.6928 | -0.35706 | -0.05951 | 2.9709 | -0.17395 | -7.5073 | -0.3067 | -0.036622 | 3.3279 | 69.3512 | 68.8065 | 116.0065 | 123.4543 | 2.9709 | 123.4772 | 85.6201 | -0.3067 | 123.4543 | 2.9709 | 85.6201 | 116.0065 | 123.4772 | -123.8708 | -123.8205
4087.7188 | 123.8159 | -61.409 | 62.1414 | -0.024185 | 0.01346 | 0.014695 | 0.0076198 | 0.057471 | 0.0020167 | 0.079476 | -58.4427 | 62.0728 | -61.7111 | -61.5738 | 54.6066 | 24.3896 | 7.8644 | 7.3151 | 62.1002 | -61.6837 | -0.30212 | -0.068664 | 2.9663 | -0.16479 | -7.5348 | -0.27466 | -0.041198 | 3.2684 | 69.2734 | 68.7241 | 116.0156 | 123.4818 | 2.9663 | 123.5092 | 85.7986 | -0.27466 | 123.4818 | 2.9663 | 85.7986 | 116.0156 | 123.5092 | -123.8525 | -123.8251
4088.7188 | 123.8388 | -61.3998 | 62.146 | -0.0012969 | 0.013888 | 0.011704 | 0.008688 | 0.057685 | -0.00054693 | 0.080972 | -58.4198 | 62.0865 | -61.7157 | -61.5738 | 54.6387 | 24.2523 | 7.9697 | 7.3883 | 62.1048 | -61.6745 | -0.31586 | -0.059509 | 2.98 | -0.17395 | -7.5073 | -0.27466 | -0.041199 | 3.2959 | 69.3695 | 68.7881 | 116.0385 | 123.4863 | 2.98 | 123.5046 | 85.6522 | -0.27466 | 123.4863 | 2.98 | 85.6522 | 116.0385 | 123.5046 | -123.8617 | -123.8205
4089.7188 | 123.8892 | -61.3953 | 62.1277 | -0.047073 | 0.013247 | 0.0132 | 0.010397 | 0.058325 | 0.0015893 | 0.077767 | -58.3878 | 62.0819 | -61.7065 | -61.5143 | 54.6204 | 24.3164 | 7.9376 | 7.4295 | 62.1002 | -61.6837 | -0.31128 | -0.045777 | 3.0075 | -0.11902 | -7.5073 | -0.28839 | -0.027466 | 3.3188 | 69.3329 | 68.8248 | 116.0156 | 123.4772 | 3.0075 | 123.4955 | 85.7117 | -0.28839 | 123.4772 | 3.0075 | 85.7117 | 116.0156 | 123.4955 | -123.8342 | -123.8113
4090.7188 | 123.848 | -61.3907 | 62.1323 | 0.96764 | 0.015169 | 0.013841 | 0.01232 | 0.060248 | 0.0020167 | 0.078622 | -58.2504 | 62.0728 | -61.7111 | -61.5234 | 54.6387 | 24.2523 | 7.8735 | 7.3792 | 62.0773 | -61.7065 | -0.32043 | -0.059509 | 3.1403 | -0.13275 | -7.4936 | -0.31586 | -0.054931 | 3.4607 | 69.2642 | 68.7698 | 116.0294 | 123.4634 | 3.1403 | 123.468 | 85.643 | -0.31586 | 123.4634 | 3.1403 | 85.643 | 116.0294 | 123.468 | -123.8434 | -123.8388
4091.7188 | 123.9029 | -61.4044 | 62.146 | -0.15388 | 0.014742 | 0.011918 | 0.008688 | 0.060248 | -0.00054693 | 0.078835 | -58.3694 | 62.0636 | -61.7111 | -61.5005 | 54.6661 | 24.3118 | 7.9651 | 7.5119 | 62.1094 | -61.6653 | -0.3067 | -0.082397 | 3.035 | -0.09613 | -7.4799 | -0.26093 | -0.036621 | 3.3417 | 69.3695 | 68.9163 | 116.0706 | 123.468 | 3.035 | 123.5138 | 85.7162 | -0.26093 | 123.468 | 3.035 | 85.7162 | 116.0706 | 123.5138 | -123.8571 | -123.8113
4092.7188 | 123.8388 | -61.377 | 62.1506 | -0.031814 | 0.012606 | 0.012132 | 0.0078336 | 0.057257 | 0.0020167 | 0.079263 | -58.4244 | 62.0773 | -61.734 | -61.5555 | 54.6249 | 24.3027 | 7.9376 | 7.4158 | 62.0956 | -61.6745 | -0.35706 | -0.073242 | 2.9526 | -0.17853 | -7.5256 | -0.29755 | -0.054932 | 3.3096 | 69.3146 | 68.7927 | 116.0019 | 123.4543 | 2.9526 | 123.4726 | 85.6796 | -0.29755 | 123.4543 | 2.9526 | 85.6796 | 116.0019 | 123.4726 | -123.8846 | -123.8251
4093.7188 | 123.793 | -61.4182 | 62.1597 | 0.04448 | 0.01282 | 0.016191 | 0.0080472 | 0.056189 | -0.00076053 | 0.080544 | -58.461 | 62.0819 | -61.734 | -61.6516 | 54.6066 | 24.2386 | 7.9834 | 7.3425 | 62.0911 | -61.6608 | -0.31586 | -0.07782 | 2.9572 | -0.23346 | -7.5531 | -0.24262 | -0.068665 | 3.273 | 69.4016 | 68.7607 | 116.0248 | 123.5001 | 2.9572 | 123.5092 | 85.6567 | -0.24262 | 123.5001 | 2.9572 | 85.6567 | 116.0248 | 123.5092 | -123.8937 | -123.8205
4094.7188 | 123.7335 | -61.4273 | 62.1826 | -0.26833 | 0.014956 | 0.011277 | 0.013388 | 0.058539 | -0.0014013 | 0.080758 | -58.4381 | 62.1689 | -61.7203 | -61.6241 | 54.332 | 24.0234 | 8.2169 | 7.2647 | 62.1368 | -61.7111 | -0.29297 | -0.013733 | 2.9892 | -0.19684 | -7.8506 | -0.28381 | -0.045776 | 3.2822 | 69.6442 | 68.692 | 115.7593 | 123.5962 | 2.9892 | 123.5641 | 85.4507 | -0.28381 | 123.5962 | 2.9892 | 85.4507 | 115.7593 | 123.5641 | -123.9029 | -123.8937
4095.7188 | 123.8297 | -61.3953 | 62.114 | 0.11314 | 0.014742 | 0.011491 | 0.0089016 | 0.060034 | -0.00054693 | 0.076699 | -58.4335 | 62.0728 | -61.7432 | -61.5829 | 54.6021 | 24.234 | 7.9468 | 7.3517 | 62.0865 | -61.7065 | -0.3479 | -0.041199 | 2.9617 | -0.18768 | -7.5119 | -0.31128 | -0.027466 | 3.3096 | 69.342 | 68.7469 | 115.9973 | 123.468 | 2.9617 | 123.4818 | 85.6293 | -0.31128 | 123.468 | 2.9617 | 85.6293 | 115.9973 | 123.4818 | -123.8571 | -123.8205
4096.7188 | 123.8159 | -61.3953 | 62.146 | -0.069961 | 0.014529 | 0.01085 | 0.0099698 | 0.058966 | -0.00076053 | 0.080331 | -58.4656 | 62.0865 | -61.7294 | -61.5829 | 54.5929 | 24.2706 | 7.9834 | 7.3563 | 62.0956 | -61.6928 | -0.33417 | -0.059509 | 2.9297 | -0.18768 | -7.5531 | -0.29755 | -0.050354 | 3.2639 | 69.3787 | 68.7515 | 115.9882 | 123.4818 | 2.9297 | 123.4909 | 85.6659 | -0.29755 | 123.4818 | 2.9297 | 85.6659 | 115.9882 | 123.4909 | -123.8754 | -123.8388
4097.7188 | 123.8388 | -61.3907 | 62.1231 | 0.18944 | 0.015383 | 0.012132 | 0.013174 | 0.059394 | 0.0020167 | 0.07969 | -58.3923 | 62.0956 | -61.7249 | -61.5829 | 54.6021 | 24.3759 | 7.8598 | 7.3929 | 62.0636 | -61.6974 | -0.33417 | -0.027466 | 2.9984 | -0.19226 | -7.5211 | -0.3067 | -0.059509 | 3.3325 | 69.2505 | 68.7836 | 115.9927 | 123.4863 | 2.9984 | 123.4543 | 85.7666 | -0.3067 | 123.4863 | 2.9984 | 85.7666 | 115.9927 | 123.4543 | -123.848 | -123.8205
4098.7188 | 123.7976 | -61.3953 | 62.146 | 0.19707 | 0.013674 | 0.0132 | 0.0093288 | 0.059821 | -0.0018285 | 0.079049 | -58.4518 | 62.0728 | -61.734 | -61.6013 | 54.5563 | 24.2203 | 7.9742 | 7.3288 | 62.1002 | -61.6837 | -0.33875 | -0.073242 | 2.9434 | -0.20599 | -7.5897 | -0.28839 | -0.045776 | 3.2822 | 69.3695 | 68.7241 | 115.9515 | 123.468 | 2.9434 | 123.4955 | 85.6155 | -0.28839 | 123.468 | 2.9434 | 85.6155 | 115.9515 | 123.4955 | -123.88 | -123.8297
4099.7188 | 123.8663 | -61.3907 | 62.1185 | -0.17677 | 0.013674 | 0.009141 | 0.0095424 | 0.059607 | 0.0045801 | 0.077981 | -58.3603 | 62.1002 | -61.6928 | -61.441 | 54.6341 | 24.2157 | 8.0109 | 7.489 | 62.0728 | -61.6699 | -0.30212 | -0.01831 | 3.0304 | -0.050354 | -7.4844 | -0.27924 | -0.045776 | 3.3325 | 69.4016 | 68.8797 | 116.0248 | 123.4909 | 3.0304 | 123.4634 | 85.6064 | -0.27924 | 123.4909 | 3.0304 | 85.6064 | 116.0248 | 123.4634 | -123.8113 | -123.7885
4100.7188 | 123.8113 | -61.4227 | 62.1506 | 0.0063326 | 0.013674 | 0.0097818 | 0.0076198 | 0.05918 | 0.00030767 | 0.081399 | -58.4427 | 62.0865 | -61.7249 | -61.5784 | 54.57 | 24.2432 | 7.9834 | 7.3746 | 62.1002 | -61.6837 | -0.30213 | -0.064087 | 2.98 | -0.15564 | -7.5806 | -0.26093 | -0.050354 | 3.2822 | 69.4061 | 68.7973 | 115.9927 | 123.5092 | 2.98 | 123.5229 | 85.6659 | -0.26093 | 123.5092 | 2.98 | 85.6659 | 115.9927 | 123.5229 | -123.8754 | -123.8342
4101.7188 | 123.7106 | -61.3586 | 62.2147 | -0.13863 | 0.014529 | 0.014054 | 0.010397 | 0.058325 | 0.0018031 | 0.079049 | -58.3603 | 62.0911 | -61.6974 | -61.4777 | 54.6478 | 24.2661 | 7.9971 | 7.5027 | 62.1231 | -61.6608 | -0.33874 | -0.1236 | 2.9984 | -0.11902 | -7.5668 | -0.30212 | -0.091553 | 3.3371 | 69.3558 | 68.8614 | 116.0065 | 123.4497 | 2.9984 | 123.4818 | 85.6247 | -0.30212 | 123.4497 | 2.9984 | 85.6247 | 116.0065 | 123.4818 | -123.912 | -123.8754
4102.7188 | 123.8205 | -61.4136 | 62.146 | 0.090256 | 0.016665 | 0.0097818 | 0.0091152 | 0.058753 | 0.00030767 | 0.075845 | -58.4381 | 62.0682 | -61.7432 | -61.6013 | 54.5471 | 24.234 | 7.9697 | 7.3334 | 62.059 | -61.6928 | -0.32959 | -0.07782 | 2.9755 | -0.18768 | -7.5989 | -0.27924 | -0.086975 | 3.3051 | 69.3832 | 68.7469 | 115.9607 | 123.4818 | 2.9755 | 123.4726 | 85.6476 | -0.27924 | 123.4818 | 2.9755 | 85.6476 | 115.9607 | 123.4726 | -123.8892 | -123.8388
4103.7188 | 123.8846 | -61.3953 | 62.1231 | 0.13603 | 0.015597 | 0.011491 | 0.014456 | 0.061103 | 0.0018031 | 0.077981 | -58.3649 | 62.0911 | -61.7523 | -61.5692 | 54.3365 | 24.1196 | 8.1436 | 7.457 | 62.0544 | -61.6974 | -0.35706 | -0.032044 | 3.0304 | -0.17395 | -7.7866 | -0.30212 | -0.068665 | 3.3875 | 69.5389 | 68.8522 | 115.7318 | 123.4863 | 3.0304 | 123.4497 | 85.5148 | -0.30212 | 123.4863 | 3.0304 | 85.5148 | 115.7318 | 123.4497 | -123.8754 | -123.8205
4104.7344 | 123.8663 | -61.3907 | 62.1277 | -0.19203 | 0.01346 | 0.0050822 | 0.0089016 | 0.060462 | 0.0018031 | 0.078622 | -58.0902 | 62.1506 | -61.6699 | -61.4822 | 54.6753 | 24.2661 | 7.9788 | 7.5119 | 62.1094 | -61.6562 | -0.27924 | 0.022888 | 3.3005 | -0.091553 | -7.4524 | -0.2655 | -0.018311 | 3.5797 | 69.3695 | 68.9026 | 116.066 | 123.5413 | 3.3005 | 123.5001 | 85.6567 | -0.2655 | 123.5413 | 3.3005 | 85.6567 | 116.066 | 123.5001 | -123.7976 | -123.7839
4105.7188 | 123.8388 | -61.3998 | 62.146 | -0.031814 | 0.014742 | 0.010636 | 0.0074062 | 0.05683 | 0.00030767 | 0.078622 | -58.4518 | 62.0956 | -61.734 | -61.5601 | 54.6204 | 24.234 | 8.0063 | 7.3929 | 62.1048 | -61.6653 | -0.33417 | -0.050354 | 2.948 | -0.16022 | -7.5256 | -0.2655 | -0.041199 | 3.2822 | 69.4061 | 68.7927 | 116.0202 | 123.4955 | 2.948 | 123.5046 | 85.6338 | -0.2655 | 123.4955 | 2.948 | 85.6338 | 116.0202 | 123.5046 | -123.88 | -123.8113
4106.7188 | 123.848 | -61.409 | 62.1552 | -0.131 | 0.01282 | 0.012986 | 0.0089016 | 0.057898 | 0.00030767 | 0.078835 | -58.4061 | 62.0636 | -61.734 | -61.5234 | 54.6524 | 24.2523 | 7.9651 | 7.4753 | 62.0682 | -61.6837 | -0.32501 | -0.091552 | 3.0029 | -0.11444 | -7.5027 | -0.27466 | -0.086975 | 3.3279 | 69.3741 | 68.8843 | 116.0614 | 123.4726 | 3.0029 | 123.4772 | 85.6613 | -0.27466 | 123.4726 | 3.0029 | 85.6613 | 116.0614 | 123.4772 | -123.8892 | -123.8388
4107.7188 | 123.8297 | -61.4227 | 62.1368 | -0.039444 | 0.015383 | 0.012345 | 0.0099698 | 0.059394 | 0.0011621 | 0.079476 | -58.4427 | 62.059 | -61.7203 | -61.6013 | 54.4785 | 24.1333 | 7.9697 | 7.3563 | 62.1048 | -61.6928 | -0.29755 | -0.07782 | 2.98 | -0.17853 | -7.6584 | -0.27008 | -0.032044 | 3.2776 | 69.3924 | 68.779 | 115.9012 | 123.4818 | 2.98 | 123.5275 | 85.556 | -0.27008 | 123.4818 | 2.98 | 85.556 | 115.9012 | 123.5275 | -123.8571 | -123.8297
4108.7188 | 123.7976 | -61.4136 | 62.1552 | 0.04448 | 0.014101 | 0.014909 | 0.0089016 | 0.060248 | 0.00052127 | 0.079904 | -58.4427 | 62.0911 | -61.7111 | -61.6013 | 54.5425 | 24.1791 | 8.0246 | 7.4432 | 62.0865 | -61.7065 | -0.29755 | -0.064087 | 2.9709 | -0.18768 | -7.6126 | -0.29297 | -0.068664 | 3.2684 | 69.4382 | 68.8568 | 115.9561 | 123.5046 | 2.9709 | 123.5001 | 85.5927 | -0.29297 | 123.5046 | 2.9709 | 85.5927 | 115.9561 | 123.5001 | -123.8663 | -123.8617
4109.7188 | 123.7335 | -61.4136 | 62.1872 | -0.17677 | 0.015597 | 0.014695 | 0.01232 | 0.057685 | 0.0011621 | 0.078835 | -58.4518 | 62.146 | -61.7432 | -61.5921 | 54.4052 | 24.0417 | 8.1757 | 7.4203 | 62.1643 | -61.7065 | -0.32959 | -0.041199 | 2.9617 | -0.17853 | -7.782 | -0.29297 | -0.022888 | 3.2913 | 69.5892 | 68.8339 | 115.8188 | 123.5596 | 2.9617 | 123.5779 | 85.4553 | -0.29297 | 123.5596 | 2.9617 | 85.4553 | 115.8188 | 123.5779 | -123.9304 | -123.8937
4110.7188 | 123.8434 | -61.3953 | 62.114 | 0.2047 | 0.015383 | 0.011064 | 0.01296 | 0.05918 | -0.00033333 | 0.079904 | -58.3878 | 62.0865 | -61.7386 | -61.5646 | 54.4968 | 24.2294 | 7.8735 | 7.4844 | 62.0773 | -61.6791 | -0.34332 | -0.027466 | 3.0075 | -0.16937 | -7.6172 | -0.28381 | -0.036621 | 3.3508 | 69.2688 | 68.8797 | 115.892 | 123.4818 | 3.0075 | 123.4726 | 85.6247 | -0.28381 | 123.4818 | 3.0075 | 85.6247 | 115.892 | 123.4726 | -123.8525 | -123.793
4111.7188 | 123.8709 | -61.409 | 62.1323 | -0.09285 | 0.015383 | 0.014268 | 0.0076198 | 0.058539 | 0.00030767 | 0.080544 | -58.4473 | 62.0682 | -61.7157 | -61.5417 | 54.5517 | 24.2752 | 7.9926 | 7.4982 | 62.1048 | -61.6653 | -0.3067 | -0.064087 | 2.9617 | -0.13275 | -7.5806 | -0.25635 | -0.027466 | 3.2684 | 69.4016 | 68.9072 | 115.9607 | 123.4772 | 2.9617 | 123.5138 | 85.6842 | -0.25635 | 123.4772 | 2.9617 | 85.6842 | 115.9607 | 123.5138 | -123.848 | -123.7976
4112.7188 | 123.8205 | -61.409 | 62.1323 | -0.0089264 | 0.015597 | 0.0095682 | 0.0082608 | 0.060034 | 0.0013757 | 0.079904 | -58.4106 | 62.0956 | -61.734 | -61.5875 | 54.5242 | 24.1974 | 8.0017 | 7.4387 | 62.0956 | -61.6928 | -0.32501 | -0.036621 | 2.9984 | -0.17853 | -7.608 | -0.28381 | -0.036621 | 3.3234 | 69.4107 | 68.8477 | 115.9332 | 123.5046 | 2.9984 | 123.5046 | 85.6064 | -0.28381 | 123.5046 | 2.9984 | 85.6064 | 115.9332 | 123.5046 | -123.8663 | -123.8251
4113.7188 | 123.7976 | -61.4227 | 62.1231 | 0.082626 | 0.013033 | 0.011918 | 0.0093288 | 0.06153 | 0.0020167 | 0.080331 | -58.4473 | 62.0956 | -61.7157 | -61.5967 | 54.4647 | 24.2249 | 8.0612 | 7.457 | 62.0911 | -61.6974 | -0.29297 | -0.027466 | 2.9755 | -0.17395 | -7.6584 | -0.27466 | -0.032044 | 3.2684 | 69.4839 | 68.8797 | 115.8875 | 123.5184 | 2.9755 | 123.5138 | 85.6476 | -0.27466 | 123.5184 | 2.9755 | 85.6476 | 115.8875 | 123.5138 | -123.8388 | -123.8205
4114.7188 | 123.8754 | -61.3861 | 62.1094 | -0.09285 | 0.01581 | 0.01085 | 0.0091152 | 0.05683 | -0.0011877 | 0.081399 | -58.374 | 62.0911 | -61.7249 | -61.5189 | 54.6295 | 24.3164 | 7.9971 | 7.5348 | 62.0682 | -61.6699 | -0.33875 | -0.018311 | 3.0121 | -0.13275 | -7.4799 | -0.28381 | -0.041199 | 3.3508 | 69.3832 | 68.9209 | 116.0156 | 123.4772 | 3.0121 | 123.4543 | 85.7025 | -0.28381 | 123.4772 | 3.0121 | 85.7025 | 116.0156 | 123.4543 | -123.8342 | -123.7793
4115.7188 | 123.8159 | -61.4136 | 62.146 | 0.097885 | 0.012179 | 0.01085 | 0.0095424 | 0.058753 | 0.00052127 | 0.080758 | -58.4518 | 62.0636 | -61.7157 | -61.6013 | 54.5151 | 24.2157 | 8.0292 | 7.4203 | 62.0819 | -61.6882 | -0.30212 | -0.082397 | 2.9617 | -0.18768 | -7.6309 | -0.27466 | -0.064087 | 3.2639 | 69.4427 | 68.8339 | 115.9287 | 123.4772 | 2.9617 | 123.4955 | 85.6293 | -0.27466 | 123.4772 | 2.9617 | 85.6293 | 115.9287 | 123.4955 | -123.8617 | -123.8342
4116.7188 | 123.8617 | -61.3724 | 62.1552 | -3.7702 | 0.013033 | 0.013841 | 0.011892 | 0.058112 | -0.0016149 | 0.079904 | -58.5754 | 62.0911 | -61.6974 | -61.5417 | 54.5288 | 24.2752 | 8.1161 | 7.5668 | 62.0819 | -61.6745 | -0.32501 | -0.064087 | 2.7969 | -0.16937 | -7.6263 | -0.30213 | -0.073242 | 3.1219 | 69.4885 | 68.9392 | 115.9012 | 123.4634 | 2.7969 | 123.4543 | 85.6476 | -0.30213 | 123.4634 | 2.7969 | 85.6476 | 115.9012 | 123.4543 | -123.8525 | -123.8297
4117.7188 | 123.8617 | -61.3724 | 62.146 | -3.4803 | 0.019228 | 0.014909 | 0.01232 | 0.058325 | -0.00033333 | 0.077126 | -58.429 | 62.1185 | -61.7111 | -61.5143 | 54.6112 | 24.3301 | 8.107 | 7.5668 | 62.1231 | -61.6653 | -0.33875 | -0.027466 | 2.9434 | -0.14191 | -7.5348 | -0.29297 | -0.022888 | 3.2822 | 69.4794 | 68.9392 | 115.9836 | 123.4909 | 2.9434 | 123.4955 | 85.7025 | -0.29297 | 123.4909 | 2.9434 | 85.7025 | 115.9836 | 123.4955 | -123.8571 | -123.8113
4118.7344 | 123.7198 | -61.409 | 62.1872 | -0.23781 | 0.016024 | 0.011918 | 0.01232 | 0.060248 | 0.0011621 | 0.078835 | -58.461 | 62.1735 | -61.7249 | -61.6013 | 54.6249 | 24.2386 | 8.2031 | 7.4158 | 62.1597 | -61.7203 | -0.31586 | -0.013733 | 2.948 | -0.19226 | -7.5623 | -0.31128 | -0.027466 | 3.2639 | 69.6121 | 68.8248 | 116.0339 | 123.5825 | 2.948 | 123.5687 | 85.6476 | -0.31128 | 123.5825 | 2.948 | 85.6476 | 116.0339 | 123.5687 | -123.912 | -123.9075
4119.7188 | 123.8617 | -61.3861 | 62.1597 | -1.6035 | 0.010897 | 0.01085 | 0.0091152 | 0.060675 | 9.4068e-05 | 0.078408 | -58.3466 | 62.1506 | -61.6837 | -61.496 | 54.6661 | 24.3118 | 8.0383 | 7.5256 | 62.114 | -61.6379 | -0.29755 | -0.009155 | 3.0395 | -0.10986 | -7.4936 | -0.25177 | -0.045776 | 3.3371 | 69.4244 | 68.9117 | 116.0522 | 123.5367 | 3.0395 | 123.5001 | 85.6979 | -0.25177 | 123.5367 | 3.0395 | 85.6979 | 116.0522 | 123.5001 | -123.8434 | -123.7976
4120.7188 | 123.7885 | -61.4182 | 62.1323 | 0.04448 | 0.01346 | 0.0097818 | 0.0076198 | 0.060462 | -0.00054693 | 0.077554 | -58.4839 | 62.0773 | -61.7157 | -61.5921 | 54.4052 | 24.2569 | 8.0063 | 7.4203 | 62.0819 | -61.6791 | -0.29755 | -0.054931 | 2.9343 | -0.17395 | -7.7271 | -0.26093 | -0.050354 | 3.2318 | 69.4244 | 68.8385 | 115.8234 | 123.4955 | 2.9343 | 123.5001 | 85.675 | -0.26093 | 123.4955 | 2.9343 | 85.675 | 115.8234 | 123.5001 | -123.848 | -123.8113
4121.7344 | 123.7473 | -61.4365 | 62.2147 | -0.10811 | 0.016665 | 0.0097818 | 0.010397 | 0.060675 | -0.00076053 | 0.079904 | -58.4244 | 62.1414 | -61.7065 | -61.5921 | 54.5242 | 24.2065 | 8.2123 | 7.4295 | 62.1368 | -61.7294 | -0.27008 | -0.073243 | 3.0121 | -0.15564 | -7.6904 | -0.29297 | -0.07782 | 3.2822 | 69.6487 | 68.866 | 115.9607 | 123.5779 | 3.0121 | 123.5733 | 85.643 | -0.29297 | 123.5779 | 3.0121 | 85.643 | 115.9607 | 123.5733 | -123.9212 | -123.9441
4122.7188 | 123.8159 | -61.3907 | 62.1506 | 0.090256 | 0.012606 | 0.011918 | 0.0099698 | 0.059394 | -0.0011877 | 0.079476 | -58.4564 | 62.0728 | -61.7523 | -61.5875 | 54.5425 | 24.3347 | 8.107 | 7.3517 | 62.114 | -61.6379 | -0.36163 | -0.07782 | 2.9343 | -0.19684 | -7.608 | -0.24719 | -0.036621 | 3.2959 | 69.4977 | 68.7424 | 115.9332 | 123.4634 | 2.9343 | 123.5046 | 85.7254 | -0.24719 | 123.4634 | 2.9343 | 85.7254 | 115.9332 | 123.5046 | -123.9029 | -123.7885
4123.7344 | 123.761 | -61.4227 | 62.1964 | -0.077591 | 0.016238 | 0.013841 | 0.017447 | 0.059607 | -0.00011953 | 0.07734 | -58.3969 | 62.1826 | -61.7157 | -61.5463 | 54.4968 | 24.1974 | 8.1161 | 7.4432 | 62.1414 | -61.7249 | -0.29297 | -0.013733 | 3.0258 | -0.1236 | -7.6996 | -0.30213 | -0.054932 | 3.3188 | 69.5389 | 68.866 | 115.9195 | 123.6053 | 3.0258 | 123.5641 | 85.6201 | -0.30213 | 123.6053 | 3.0258 | 85.6201 | 115.9195 | 123.5641 | -123.912 | -123.9212
4124.7188 | 123.8342 | -61.4136 | 62.146 | 0.013962 | 0.012606 | 0.011491 | 0.008688 | 0.059821 | 0.00052127 | 0.079476 | -58.4427 | 62.0865 | -61.7249 | -61.5784 | 54.5975 | 24.1928 | 8.0521 | 7.4615 | 62.114 | -61.6653 | -0.31128 | -0.059509 | 2.9709 | -0.1648 | -7.5485 | -0.25177 | -0.032043 | 3.2822 | 69.4656 | 68.8751 | 116.011 | 123.5001 | 2.9709 | 123.5275 | 85.6064 | -0.25177 | 123.5001 | 2.9709 | 85.6064 | 116.011 | 123.5275 | -123.8708 | -123.8113
4125.7188 | 123.8297 | -61.4273 | 62.146 | 0.097885 | 0.016238 | 0.010209 | 0.0099698 | 0.058539 | 0.0018031 | 0.079476 | -58.4518 | 62.0819 | -61.7569 | -61.5921 | 54.4968 | 24.0463 | 8.0795 | 7.4524 | 62.0773 | -61.6928 | -0.32959 | -0.064087 | 2.9755 | -0.16479 | -7.6492 | -0.2655 | -0.068664 | 3.3051 | 69.5068 | 68.8797 | 115.9241 | 123.5092 | 2.9755 | 123.5046 | 85.4736 | -0.2655 | 123.5092 | 2.9755 | 85.4736 | 115.9241 | 123.5046 | -123.9029 | -123.8388
4126.7188 | 124.0173 | -61.3815 | 62.2147 | -0.16151 | 0.013247 | 0.011918 | 0.010397 | 0.057898 | -0.00033333 | 0.080972 | -58.3694 | 62.0911 | -61.7065 | -61.5005 | 54.5883 | 24.115 | 8.0017 | 7.5302 | 62.114 | -61.6379 | -0.32501 | -0.1236 | 3.0121 | -0.11902 | -7.6263 | -0.25635 | -0.10071 | 3.3371 | 69.3832 | 68.9117 | 115.9698 | 123.4726 | 3.0121 | 123.4955 | 85.4965 | -0.25635 | 123.4726 | 3.0121 | 85.4965 | 115.9698 | 123.4955 | -123.9212 | -123.8525
4127.7188 | 123.8434 | -61.3998 | 62.1689 | 0.28862 | 0.011538 | 0.013413 | 0.010397 | 0.059821 | 0.0011621 | 0.078835 | -58.4702 | 62.0911 | -61.7203 | -61.5921 | 54.5197 | 24.1196 | 8.0154 | 7.4341 | 62.0773 | -61.6745 | -0.32043 | -0.07782 | 2.9297 | -0.19226 | -7.6492 | -0.27466 | -0.091552 | 3.2501 | 69.4153 | 68.8339 | 115.9195 | 123.4909 | 2.9297 | 123.4772 | 85.5194 | -0.27466 | 123.4909 | 2.9297 | 85.5194 | 115.9195 | 123.4772 | -123.8892 | -123.8434
4128.7344 | 123.7427 | -61.4227 | 62.1735 | -0.0089264 | 0.01816 | 0.013627 | 0.017874 | 0.060889 | -0.00033333 | 0.077981 | -58.3832 | 62.1735 | -61.7111 | -61.5784 | 54.5013 | 24.0051 | 8.0978 | 7.37 | 62.1323 | -61.7432 | -0.28839 | 0 | 3.0395 | -0.15564 | -7.6721 | -0.32044 | -0.041199 | 3.3279 | 69.5206 | 68.7927 | 115.9241 | 123.5962 | 3.0395 | 123.555 | 85.4279 | -0.32044 | 123.5962 | 3.0395 | 85.4279 | 115.9241 | 123.555 | -123.8846 | -123.9166
4129.7188 | 123.8571 | -61.3724 | 62.1368 | -1.5348 | 0.013674 | 0.0076456 | 0.0071926 | 0.05918 | -0.00033333 | 0.078622 | -58.461 | 62.1002 | -61.7157 | -61.5143 | 54.5563 | 24.0921 | 8.0017 | 7.5119 | 62.1323 | -61.6608 | -0.34332 | -0.036621 | 2.9114 | -0.14191 | -7.5806 | -0.28839 | -0.004578 | 3.2547 | 69.3741 | 68.8843 | 115.9286 | 123.4726 | 2.9114 | 123.5046 | 85.4645 | -0.28839 | 123.4726 | 2.9114 | 85.4645 | 115.9286 | 123.5046 | -123.8525 | -123.7976
4130.7188 | 123.8113 | -61.409 | 62.1323 | 0.03685 | 0.014101 | 0.012986 | 0.0093288 | 0.057471 | -0.00011953 | 0.078835 | -58.4198 | 62.0361 | -61.7523 | -61.6104 | 54.4876 | 23.9182 | 7.9971 | 7.4112 | 62.0728 | -61.6791 | -0.34332 | -0.09613 | 2.9892 | -0.20142 | -7.6447 | -0.27008 | -0.059509 | 3.3325 | 69.4061 | 68.8202 | 115.8966 | 123.4451 | 2.9892 | 123.4818 | 85.3271 | -0.27008 | 123.4451 | 2.9892 | 85.3271 | 115.8966 | 123.4818 | -123.8846 | -123.8113
4131.7188 | 123.8205 | -61.3953 | 62.1689 | -0.19966 | 0.016665 | 0.0095682 | 0.010611 | 0.057898 | 9.4068e-05 | 0.079904 | -58.3511 | 62.1185 | -61.702 | -61.5234 | 54.5517 | 24.0509 | 8.075 | 7.4753 | 62.1002 | -61.6837 | -0.3067 | -0.050354 | 3.0441 | -0.12817 | -7.6172 | -0.28839 | -0.068664 | 3.3508 | 69.4702 | 68.8705 | 115.947 | 123.5138 | 3.0441 | 123.4955 | 85.4462 | -0.28839 | 123.5138 | 3.0441 | 85.4462 | 115.947 | 123.4955 | -123.8708 | -123.8525
4132.7188 | 123.8388 | -61.3998 | 62.1597 | -0.016556 | 0.01346 | 0.0093546 | 0.0082608 | 0.059394 | -0.00054693 | 0.079904 | -58.4473 | 62.0728 | -61.734 | -61.5875 | 54.5242 | 24.0601 | 8.0154 | 7.4341 | 62.114 | -61.6745 | -0.33417 | -0.086975 | 2.9526 | -0.18768 | -7.6355 | -0.27466 | -0.045776 | 3.2867 | 69.4153 | 68.8339 | 115.9241 | 123.4726 | 2.9526 | 123.5138 | 85.4599 | -0.27466 | 123.4726 | 2.9526 | 85.4599 | 115.9241 | 123.5138 | -123.8937 | -123.8342
4133.7188 | 123.6694 | -61.4044 | 62.1643 | -0.069961 | 0.015597 | 0.0132 | 0.017447 | 0.059394 | -0.0020421 | 0.078835 | -58.3923 | 62.114 | -61.7203 | -61.5646 | 54.4739 | 24.0143 | 8.0658 | 7.3792 | 62.1368 | -61.7111 | -0.31586 | -0.050354 | 3.0121 | -0.16022 | -7.6904 | -0.3067 | -0.027466 | 3.3279 | 69.4702 | 68.7836 | 115.8783 | 123.5184 | 3.0121 | 123.5413 | 85.4187 | -0.3067 | 123.5184 | 3.0121 | 85.4187 | 115.8783 | 123.5413 | -123.8846 | -123.8754
4134.7344 | 123.7381 | -61.4136 | 62.1918 | -0.19203 | 0.01346 | 0.014695 | 0.01296 | 0.060034 | -0.00033333 | 0.077981 | -58.4518 | 62.178 | -61.7432 | -61.6241 | 54.4693 | 23.9227 | 8.1802 | 7.37 | 62.1872 | -61.7157 | -0.32959 | -0.013732 | 2.9617 | -0.21057 | -7.7225 | -0.30212 | -0.004577 | 3.2913 | 69.5938 | 68.7836 | 115.8829 | 123.5916 | 2.9617 | 123.6008 | 85.3363 | -0.30212 | 123.5916 | 2.9617 | 85.3363 | 115.8829 | 123.6008 | -123.9349 | -123.9075
4135.7188 | 123.8113 | -61.4227 | 62.1689 | -0.062332 | 0.01346 | 0.012986 | 0.0099698 | 0.060675 | 0.00030767 | 0.082894 | -58.429 | 62.0773 | -61.7157 | -61.615 | 54.5197 | 23.9365 | 7.8735 | 6.9809 | 62.1277 | -61.647 | -0.29297 | -0.091552 | 2.9938 | -0.19226 | -7.6492 | -0.22431 | -0.041198 | 3.2867 | 69.2963 | 68.4036 | 115.9424 | 123.5001 | 2.9938 | 123.5504 | 85.3592 | -0.22431 | 123.5001 | 2.9938 | 85.3592 | 115.9424 | 123.5504 | -123.8846 | -123.8159
4136.7188 | 123.88 | -61.3724 | 62.1597 | -0.08522 | 0.013888 | 0.01085 | 0.0099698 | 0.060248 | -0.00054693 | 0.07969 | -58.3923 | 62.0865 | -61.6974 | -61.5005 | 54.5563 | 23.9777 | 7.8461 | 7.1182 | 62.1094 | -61.6653 | -0.32501 | -0.073242 | 2.98 | -0.12817 | -7.6035 | -0.29297 | -0.050354 | 3.3051 | 69.2184 | 68.4906 | 115.9286 | 123.4589 | 2.98 | 123.4818 | 85.35 | -0.29297 | 123.4589 | 2.98 | 85.35 | 115.9286 | 123.4818 | -123.8571 | -123.8251
4137.7188 | 123.8846 | -61.4044 | 62.1414 | -0.14626 | 0.012392 | 0.010209 | 0.0091152 | 0.057685 | -0.00076053 | 0.08204 | -58.3832 | 62.0819 | -61.7432 | -61.5417 | 54.5883 | 24.0051 | 7.9422 | 7.3471 | 62.1094 | -61.6837 | -0.33875 | -0.059509 | 3.0212 | -0.13733 | -7.5531 | -0.27924 | -0.032043 | 3.36 | 69.3466 | 68.7515 | 115.9927 | 123.4863 | 3.0212 | 123.5138 | 85.4095 | -0.27924 | 123.4863 | 3.0212 | 85.4095 | 115.9927 | 123.5138 | -123.8846 | -123.8251
4138.7188 | 123.8892 | -61.3861 | 62.1506 | -0.10048 | 0.014101 | 0.012986 | 0.0084744 | 0.058753 | 0.00073487 | 0.078622 | -58.3923 | 62.0544 | -61.702 | -61.528 | 54.5197 | 23.9273 | 7.9514 | 7.3425 | 62.1185 | -61.6653 | -0.31586 | -0.096131 | 2.9938 | -0.14191 | -7.6309 | -0.27924 | -0.032044 | 3.3096 | 69.3375 | 68.7286 | 115.9058 | 123.4406 | 2.9938 | 123.5046 | 85.3134 | -0.27924 | 123.4406 | 2.9938 | 85.3134 | 115.9058 | 123.5046 | -123.8525 | -123.8159
4139.7188 | 123.8983 | -61.3586 | 62.146 | -0.16914 | 0.014529 | 0.012773 | 0.0095424 | 0.057257 | 0.00094847 | 0.077767 | -58.3557 | 62.0865 | -61.6974 | -61.5051 | 54.5883 | 24.0921 | 7.9926 | 7.3792 | 62.1231 | -61.6608 | -0.33874 | -0.059509 | 3.0029 | -0.14648 | -7.5577 | -0.30212 | -0.022888 | 3.3417 | 69.3512 | 68.7378 | 115.947 | 123.4451 | 3.0029 | 123.4818 | 85.4507 | -0.30212 | 123.4451 | 3.0029 | 85.4507 | 115.947 | 123.4818 | -123.8434 | -123.8068
4140.7188 | 123.848 | -61.3907 | 62.178 | -0.077591 | 0.015169 | 0.0095682 | 0.008688 | 0.060462 | -0.0011877 | 0.078835 | -58.3969 | 62.0773 | -61.7111 | -61.5417 | 54.5471 | 23.9502 | 8.0704 | 7.5027 | 62.114 | -61.6745 | -0.32043 | -0.10071 | 2.9938 | -0.15106 | -7.6309 | -0.28381 | -0.064087 | 3.3142 | 69.4611 | 68.8934 | 115.9378 | 123.468 | 2.9938 | 123.5046 | 85.3409 | -0.28381 | 123.468 | 2.9938 | 85.3409 | 115.9378 | 123.5046 | -123.8892 | -123.8525
4141.7188 | 123.8663 | -61.3953 | 62.1552 | -0.55061 | 0.014315 | 0.0089274 | 0.0099698 | 0.057685 | 0.00073487 | 0.078835 | -58.3191 | 62.0911 | -61.6974 | -61.5005 | 54.5975 | 23.9822 | 7.988 | 7.3425 | 62.1048 | -61.6745 | -0.30212 | -0.064087 | 3.0762 | -0.10529 | -7.5577 | -0.27924 | -0.050354 | 3.3783 | 69.3832 | 68.7378 | 115.9927 | 123.4863 | 3.0762 | 123.5001 | 85.3775 | -0.27924 | 123.4863 | 3.0762 | 85.3775 | 115.9927 | 123.5001 | -123.8525 | -123.8297
4142.7188 | 123.8022 | -61.3998 | 62.1414 | -0.016556 | 0.015597 | 0.010209 | 0.0076198 | 0.05918 | -0.00097413 | 0.080758 | -58.3923 | 62.0773 | -61.7203 | -61.4594 | 54.4418 | 24.0097 | 7.901 | 6.9534 | 62.1002 | -61.6791 | -0.32043 | -0.064086 | 3.0075 | -0.05951 | -7.6996 | -0.27924 | -0.041198 | 3.3279 | 69.3008 | 68.3533 | 115.8417 | 123.4772 | 3.0075 | 123.5001 | 85.4095 | -0.27924 | 123.4772 | 3.0075 | 85.4095 | 115.8417 | 123.5001 | -123.8617 | -123.8205
4143.7188 | 123.8342 | -61.3861 | 62.1414 | 0.067368 | 0.014956 | 0.0078592 | 0.0074062 | 0.057898 | -0.00054693 | 0.079049 | -58.4244 | 62.0682 | -61.7294 | -61.5692 | 54.4373 | 23.7991 | 8.107 | 6.9534 | 62.1231 | -61.6653 | -0.34332 | -0.073242 | 2.9617 | -0.18311 | -7.7042 | -0.27924 | -0.01831 | 3.3051 | 69.4931 | 68.3395 | 115.8234 | 123.4543 | 2.9617 | 123.5092 | 85.1852 | -0.27924 | 123.4543 | 2.9617 | 85.1852 | 115.8234 | 123.5092 | -123.8708 | -123.8068
4144.7188 | 123.7885 | -61.3907 | 62.1597 | 0.013962 | 0.013247 | 0.013841 | 0.010397 | 0.058753 | -0.00033333 | 0.080331 | -58.4106 | 62.0728 | -61.7203 | -61.5738 | 54.4876 | 23.9227 | 7.901 | 6.958 | 62.1094 | -61.647 | -0.32959 | -0.086975 | 2.98 | -0.18311 | -7.6721 | -0.25635 | -0.050354 | 3.3096 | 69.2917 | 68.3487 | 115.8783 | 123.4634 | 2.98 | 123.5001 | 85.3134 | -0.25635 | 123.4634 | 2.98 | 85.3134 | 115.8783 | 123.5001 | -123.88 | -123.8068
4145.7188 | 123.8388 | -61.4182 | 62.114 | 0.013962 | 0.012606 | 0.011918 | 0.0082608 | 0.060034 | 0.0020167 | 0.079904 | -58.4152 | 62.0956 | -61.7249 | -61.5692 | 54.4601 | 23.7946 | 8.0933 | 7.4615 | 62.1231 | -61.6745 | -0.3067 | -0.018311 | 3.0029 | -0.15106 | -7.6538 | -0.25635 | 0.009155 | 3.3096 | 69.5114 | 68.8797 | 115.8783 | 123.5138 | 3.0029 | 123.5413 | 85.2127 | -0.25635 | 123.5138 | 3.0029 | 85.2127 | 115.8783 | 123.5413 | -123.8388 | -123.7885
4146.7188 | 123.7473 | -61.3678 | 62.1414 | -0.14626 | 0.014956 | 0.011491 | 0.0093288 | 0.060889 | -0.0014013 | 0.077981 | -58.3328 | 62.0911 | -61.7065 | -61.4868 | 54.5929 | 24.0738 | 8.0795 | 7.9697 | 62.1185 | -61.6379 | -0.33875 | -0.050354 | 3.035 | -0.11902 | -7.5485 | -0.27008 | -0.022888 | 3.3737 | 69.4473 | 69.3375 | 115.9607 | 123.4589 | 3.035 | 123.4863 | 85.4416 | -0.27008 | 123.4589 | 3.035 | 85.4416 | 115.9607 | 123.4863 | -123.848 | -123.7793
4147.7188 | 123.8297 | -61.4182 | 62.1506 | 0.067368 | 0.014101 | 0.0063638 | 0.0080472 | 0.057257 | -0.0014013 | 0.07969 | -58.4335 | 62.0728 | -61.7294 | -61.5509 | 54.4693 | 23.8724 | 8.107 | 7.457 | 62.0956 | -61.6882 | -0.31128 | -0.07782 | 2.9846 | -0.13275 | -7.6813 | -0.27008 | -0.054932 | 3.2959 | 69.5251 | 68.8751 | 115.8875 | 123.4909 | 2.9846 | 123.5138 | 85.2905 | -0.27008 | 123.4909 | 2.9846 | 85.2905 | 115.8875 | 123.5138 | -123.88 | -123.8388
4148.7188 | 123.8754 | -61.4044 | 62.1552 | -0.12337 | 0.01282 | 0.012345 | 0.0093288 | 0.059607 | 0.0024439 | 0.078622 | -58.3786 | 62.0773 | -61.7203 | -61.5189 | 54.5334 | 23.941 | 8.0154 | 7.4844 | 62.1048 | -61.6699 | -0.31586 | -0.077819 | 3.0258 | -0.11444 | -7.6218 | -0.2655 | -0.050354 | 3.3417 | 69.4199 | 68.8889 | 115.9378 | 123.4818 | 3.0258 | 123.5092 | 85.3455 | -0.2655 | 123.4818 | 3.0258 | 85.3455 | 115.9378 | 123.5092 | -123.8754 | -123.8251
4149.7188 | 123.8022 | -61.4044 | 62.1826 | -0.14626 | 0.014529 | 0.012986 | 0.018301 | 0.063666 | -0.00076053 | 0.078835 | -58.374 | 62.178 | -61.702 | -61.5417 | 54.5288 | 23.9777 | 8.139 | 7.4158 | 62.1643 | -61.6699 | -0.29755 | -0.004577 | 3.0304 | -0.13733 | -7.6538 | -0.2655 | -0.01831 | 3.3279 | 69.5435 | 68.8202 | 115.9332 | 123.5825 | 3.0304 | 123.5687 | 85.3821 | -0.2655 | 123.5825 | 3.0304 | 85.3821 | 115.9332 | 123.5687 | -123.8846 | -123.8525
4150.7188 | 123.7976 | -61.3907 | 62.1414 | -0.24544 | 0.013888 | 0.011491 | 0.0061246 | 0.061316 | -0.0020421 | 0.079476 | -58.4518 | 62.0682 | -61.7386 | -61.5784 | 54.5334 | 24.0372 | 7.9056 | 7.0312 | 62.1323 | -61.6562 | -0.3479 | -0.073242 | 2.9388 | -0.18768 | -7.608 | -0.2655 | -0.009155 | 3.2867 | 69.2963 | 68.4219 | 115.9241 | 123.4589 | 2.9388 | 123.5229 | 85.4279 | -0.2655 | 123.4589 | 2.9388 | 85.4279 | 115.9241 | 123.5229 | -123.88 | -123.7976
4151.7188 | 123.8205 | -61.3724 | 62.146 | -0.3141 | 0.01282 | 0.013627 | 0.0082608 | 0.05918 | 9.4068e-05 | 0.077554 | -58.3511 | 62.0819 | -61.6882 | -61.5097 | 54.5471 | 24.0601 | 7.8735 | 7.0724 | 62.1323 | -61.6608 | -0.31586 | -0.064087 | 3.0212 | -0.13733 | -7.5989 | -0.28839 | -0.013733 | 3.3371 | 69.2459 | 68.4448 | 115.9195 | 123.4543 | 3.0212 | 123.5046 | 85.4324 | -0.28839 | 123.4543 | 3.0212 | 85.4324 | 115.9195 | 123.5046 | -123.8342 | -123.8068
4152.7188 | 123.8159 | -61.4227 | 62.1643 | -0.39803 | 0.014101 | 0.012986 | 0.010183 | 0.058753 | -0.00076053 | 0.079904 | -58.4518 | 62.0773 | -61.7203 | -61.5738 | 54.4785 | 24.0463 | 7.8735 | 7.0038 | 62.114 | -61.6928 | -0.29755 | -0.086975 | 2.9709 | -0.15106 | -7.6859 | -0.27008 | -0.050354 | 3.2684 | 69.2963 | 68.4265 | 115.9012 | 123.5001 | 2.9709 | 123.5367 | 85.4691 | -0.27008 | 123.5001 | 2.9709 | 85.4691 | 115.9012 | 123.5367 | -123.8846 | -123.8571
4153.7188 | 123.8754 | -61.409 | 62.1506 | -0.08522 | 0.014529 | 0.0078592 | 0.0067654 | 0.058539 | 0.00030767 | 0.079049 | -58.3786 | 62.0865 | -61.6974 | -61.5326 | 54.538 | 24.2111 | 7.8003 | 7.0175 | 62.1048 | -61.6745 | -0.28839 | -0.064087 | 3.0304 | -0.1236 | -7.6126 | -0.2655 | -0.045777 | 3.3188 | 69.2093 | 68.4265 | 115.947 | 123.4955 | 3.0304 | 123.5138 | 85.6201 | -0.2655 | 123.4955 | 3.0304 | 85.6201 | 115.947 | 123.5138 | -123.848 | -123.8251
4154.7188 | 123.8388 | -61.377 | 62.178 | 0.013962 | 0.013674 | 0.011918 | 0.011038 | 0.058753 | -0.00011953 | 0.078622 | -58.3237 | 62.0865 | -61.6837 | -61.5097 | 54.5609 | 24.2798 | 7.8918 | 7.0816 | 62.0865 | -61.6562 | -0.3067 | -0.091553 | 3.0533 | -0.13275 | -7.6172 | -0.27924 | -0.091553 | 3.36 | 69.2688 | 68.4586 | 115.9378 | 123.4634 | 3.0533 | 123.4634 | 85.6567 | -0.27924 | 123.4634 | 3.0533 | 85.6567 | 115.9378 | 123.4634 | -123.8617 | -123.8342
4155.7188 | 123.8663 | -61.3953 | 62.1506 | -0.0012969 | 0.01282 | 0.010423 | 0.0078336 | 0.059394 | -0.00011953 | 0.079476 | -58.4061 | 62.0728 | -61.7111 | -61.5646 | 54.5517 | 24.2523 | 7.8278 | 7.0679 | 62.1048 | -61.6745 | -0.31586 | -0.07782 | 2.9892 | -0.16937 | -7.5989 | -0.27924 | -0.045777 | 3.3051 | 69.223 | 68.4631 | 115.947 | 123.468 | 2.9892 | 123.5001 | 85.6476 | -0.27924 | 123.468 | 2.9892 | 85.6476 | 115.947 | 123.5001 | -123.8617 | -123.8251
4156.7188 | 123.7427 | -61.4273 | 62.1689 | -0.24544 | 0.012179 | 0.012132 | 0.012747 | 0.057257 | 0.0015893 | 0.077767 | -58.4335 | 62.1323 | -61.7203 | -61.5967 | 54.4556 | 24.115 | 8.0338 | 7.0129 | 62.1643 | -61.6882 | -0.29297 | -0.036621 | 2.9938 | -0.16937 | -7.7133 | -0.26093 | -0.004577 | 3.2867 | 69.4611 | 68.4402 | 115.8829 | 123.5596 | 2.9938 | 123.5916 | 85.5423 | -0.26093 | 123.5596 | 2.9938 | 85.5423 | 115.8829 | 123.5916 | -123.8892 | -123.8571
4157.7188 | 123.8617 | -61.3998 | 62.1368 | -0.24544 | 0.013247 | 0.0063638 | 0.0031338 | 0.053839 | 0.0011621 | 0.081399 | -58.3466 | 62.1048 | -61.6837 | -61.6516 | 54.657 | 24.3805 | 7.8049 | 7.3608 | 62.1002 | -61.6516 | -0.28381 | -0.032044 | 3.0533 | -0.25177 | -7.4799 | -0.25177 | -0.036621 | 3.3371 | 69.2047 | 68.7607 | 116.0568 | 123.5046 | 3.0533 | 123.5001 | 85.7803 | -0.25177 | 123.5046 | 3.0533 | 85.7803 | 116.0568 | 123.5001 | -123.8205 | -123.7885
4158.7188 | 123.8113 | -61.3907 | 62.1506 | -0.031814 | 0.014529 | 0.012773 | 0.0097562 | 0.056189 | 0.0020167 | 0.080331 | -58.4198 | 62.0819 | -61.7249 | -61.5921 | 54.4464 | 24.2889 | 7.9422 | 7.2739 | 62.0819 | -61.6974 | -0.33417 | -0.068665 | 2.9709 | -0.20142 | -7.7042 | -0.3067 | -0.068665 | 3.3051 | 69.3329 | 68.6646 | 115.8371 | 123.4726 | 2.9709 | 123.4726 | 85.6796 | -0.3067 | 123.4726 | 2.9709 | 85.6796 | 115.8371 | 123.4726 | -123.8754 | -123.848
4159.7188 | 123.8388 | -61.3815 | 62.1689 | -0.21492 | 0.01346 | 0.012345 | 0.011679 | 0.059394 | -0.00076053 | 0.078195 | -58.3374 | 62.0911 | -61.6928 | -61.5189 | 54.5013 | 24.1974 | 8.02 | 7.4295 | 62.114 | -61.6653 | -0.31128 | -0.07782 | 3.0441 | -0.13733 | -7.6675 | -0.28381 | -0.054931 | 3.3554 | 69.4016 | 68.811 | 115.8829 | 123.4726 | 3.0441 | 123.4955 | 85.5789 | -0.28381 | 123.4726 | 3.0441 | 85.5789 | 115.8829 | 123.4955 | -123.8617 | -123.8342
4160.7188 | 123.8342 | -61.3907 | 62.146 | -0.054703 | 0.012179 | 0.009141 | 0.0078336 | 0.058753 | 0.00073487 | 0.079476 | -58.4015 | 62.0728 | -61.7111 | -61.5372 | 54.4601 | 24.2477 | 7.9971 | 7.4432 | 62.1002 | -61.6562 | -0.32043 | -0.073242 | 2.9892 | -0.14648 | -7.6859 | -0.2655 | -0.045776 | 3.3096 | 69.3878 | 68.8339 | 115.8508 | 123.4634 | 2.9892 | 123.4909 | 85.6384 | -0.2655 | 123.4634 | 2.9892 | 85.6384 | 115.8508 | 123.4909 | -123.8571 | -123.8022
4161.7188 | 123.8342 | -61.4227 | 62.1689 | -0.25307 | 0.013033 | 0.0085 | 0.010397 | 0.057685 | 0.0018031 | 0.079904 | -58.3649 | 62.0956 | -61.7065 | -61.5234 | 54.4647 | 24.2065 | 8.1207 | 7.4432 | 62.1414 | -61.6928 | -0.28381 | -0.073242 | 3.0579 | -0.10071 | -7.7042 | -0.27008 | -0.027466 | 3.3417 | 69.5435 | 68.866 | 115.8875 | 123.5184 | 3.0579 | 123.5641 | 85.6293 | -0.27008 | 123.5184 | 3.0579 | 85.6293 | 115.8875 | 123.5641 | -123.8754 | -123.8617
4162.7188 | 123.8892 | -61.3724 | 62.1414 | -0.23018 | 0.014742 | 0.005723 | 0.0095424 | 0.057898 | -0.0058875 | 0.079049 | -58.3191 | 62.0773 | -61.6928 | -61.2946 | 54.2175 | 24.0189 | 8.194 | 7.457 | 62.0911 | -61.6653 | -0.32044 | -0.064086 | 3.0533 | 0.077819 | -7.9239 | -0.29297 | -0.050354 | 3.3737 | 69.5663 | 68.8293 | 115.5899 | 123.4497 | 3.0533 | 123.4634 | 85.3912 | -0.29297 | 123.4497 | 3.0533 | 85.3912 | 115.5899 | 123.4634 | -123.8342 | -123.8068
4163.7188 | 123.8205 | -61.4273 | 62.1506 | -0.054703 | 0.014956 | 0.007432 | 0.0091152 | 0.058325 | 0.0028711 | 0.080758 | -58.4381 | 62.059 | -61.7249 | -61.5784 | 54.4968 | 24.2844 | 8.0566 | 7.4112 | 62.1231 | -61.647 | -0.29755 | -0.091553 | 2.9892 | -0.15106 | -7.6538 | -0.21973 | -0.027466 | 3.2867 | 69.4839 | 68.8385 | 115.9241 | 123.4863 | 2.9892 | 123.5504 | 85.7117 | -0.21973 | 123.4863 | 2.9892 | 85.7117 | 115.9241 | 123.5504 | -123.8754 | -123.7976
4164.7188 | 123.793 | -61.3953 | 62.1918 | -0.21492 | 0.015383 | 0.011064 | 0.011465 | 0.058539 | 0.0018031 | 0.078408 | -58.3557 | 62.1185 | -61.7065 | -61.5417 | 54.5242 | 24.2661 | 8.2031 | 7.4661 | 62.146 | -61.6882 | -0.31128 | -0.073242 | 3.0396 | -0.14648 | -7.6675 | -0.29297 | -0.045776 | 3.3508 | 69.5984 | 68.8614 | 115.9195 | 123.5138 | 3.0396 | 123.5413 | 85.6613 | -0.29297 | 123.5138 | 3.0396 | 85.6613 | 115.9195 | 123.5413 | -123.8983 | -123.88
4165.7188 | 123.793 | -61.4273 | 62.1506 | 0.03685 | 0.013033 | 0.011064 | 0.0054836 | 0.058539 | 0.00094847 | 0.079904 | -58.4335 | 62.059 | -61.7294 | -61.5692 | 54.4785 | 24.2706 | 8.1619 | 7.3929 | 62.0819 | -61.6974 | -0.30212 | -0.091553 | 2.9938 | -0.14191 | -7.6721 | -0.27008 | -0.068665 | 3.2959 | 69.5892 | 68.8202 | 115.9058 | 123.4863 | 2.9938 | 123.5092 | 85.6979 | -0.27008 | 123.4863 | 2.9938 | 85.6979 | 115.9058 | 123.5092 | -123.88 | -123.848
4166.7188 | 123.7885 | -61.409 | 62.1689 | 0.013962 | 0.017306 | 0.014695 | 0.019369 | 0.061743 | -0.0026831 | 0.079904 | -58.461 | 62.1094 | -61.7569 | -61.5875 | 54.4327 | 24.2661 | 8.1573 | 7.402 | 62.1323 | -61.7111 | -0.3479 | -0.059509 | 2.948 | -0.17853 | -7.7362 | -0.30212 | -0.036621 | 3.2959 | 69.5663 | 68.811 | 115.8417 | 123.5184 | 2.948 | 123.5413 | 85.675 | -0.30212 | 123.5184 | 2.948 | 85.675 | 115.8417 | 123.5413 | -123.9258 | -123.88
4167.7188 | 123.8159 | -61.4182 | 62.1414 | 0.029221 | 0.013247 | 0.015122 | 0.0065518 | 0.060675 | 0.0015893 | 0.080972 | -58.429 | 62.0865 | -61.7065 | -61.5738 | 54.4601 | 24.2798 | 8.1024 | 7.4203 | 62.1048 | -61.6608 | -0.28839 | -0.054931 | 2.9892 | -0.15564 | -7.6813 | -0.24262 | -0.036621 | 3.2776 | 69.5206 | 68.8385 | 115.8783 | 123.5046 | 2.9892 | 123.5229 | 85.6979 | -0.24262 | 123.5046 | 2.9892 | 85.6979 | 115.8783 | 123.5229 | -123.848 | -123.8022
4168.7188 | 123.8297 | -61.4182 | 62.1323 | -0.19966 | 0.015383 | 0.011064 | 0.0067654 | 0.059607 | 0.00030767 | 0.07969 | -58.4061 | 62.1002 | -61.7294 | -61.5921 | 54.4556 | 24.1974 | 8.0338 | 7.4203 | 62.1048 | -61.6974 | -0.31128 | -0.032043 | 3.0121 | -0.17395 | -7.6767 | -0.27924 | -0.027466 | 3.3234 | 69.4519 | 68.8385 | 115.8737 | 123.5184 | 3.0121 | 123.5229 | 85.6155 | -0.27924 | 123.5184 | 3.0121 | 85.6155 | 115.8737 | 123.5229 | -123.8617 | -123.8297
4169.7344 | 123.7289 | -61.4227 | 62.178 | -0.14626 | 0.017519 | 0.012132 | 0.011892 | 0.059821 | 0.00052127 | 0.077554 | -58.4427 | 62.1506 | -61.7111 | -61.5921 | 54.4418 | 24.1974 | 8.2489 | 7.3792 | 62.1277 | -61.7065 | -0.28839 | -0.027466 | 2.98 | -0.16937 | -7.7362 | -0.28381 | -0.050354 | 3.2684 | 69.6716 | 68.8019 | 115.8646 | 123.5733 | 2.98 | 123.5504 | 85.6201 | -0.28381 | 123.5733 | 2.98 | 85.6201 | 115.8646 | 123.5504 | -123.8892 | -123.8846
4170.7188 | 123.848 | -61.3998 | 62.1552 | -0.0089264 | 0.014101 | 0.010209 | 0.0082608 | 0.058112 | -0.00033333 | 0.079263 | -58.3969 | 62.0819 | -61.734 | -61.5692 | 54.5242 | 24.2844 | 8.0887 | 7.4661 | 62.1048 | -61.6882 | -0.33417 | -0.073242 | 3.0029 | -0.16937 | -7.6309 | -0.28839 | -0.050354 | 3.3371 | 69.4885 | 68.866 | 115.9241 | 123.4818 | 3.0029 | 123.5046 | 85.6842 | -0.28839 | 123.4818 | 3.0029 | 85.6842 | 115.9241 | 123.5046 | -123.8892 | -123.8434
4171.7188 | 123.7564 | -61.4136 | 62.1643 | -0.13863 | 0.01346 | 0.011918 | 0.01766 | 0.060462 | -0.00076053 | 0.077554 | -58.3099 | 62.146 | -61.7432 | -61.5509 | 54.5105 | 24.2432 | 8.1894 | 7.4387 | 62.1323 | -61.6974 | -0.32959 | -0.018311 | 3.1036 | -0.13733 | -7.6538 | -0.28381 | -0.032044 | 3.4332 | 69.603 | 68.8522 | 115.9241 | 123.5596 | 3.1036 | 123.5458 | 85.6567 | -0.28381 | 123.5596 | 3.1036 | 85.6567 | 115.9241 | 123.5458 | -123.9075 | -123.8617
4172.7188 | 123.8022 | -61.3953 | 62.1094 | 0.13603 | 0.012179 | 0.0097818 | 0.0080472 | 0.061103 | 0.0011621 | 0.079476 | -58.3878 | 62.0773 | -61.734 | -61.6013 | 54.5242 | 24.3256 | 8.0521 | 7.4341 | 62.1048 | -61.6791 | -0.33875 | -0.032043 | 3.0075 | -0.20599 | -7.5851 | -0.28381 | -0.004578 | 3.3463 | 69.4473 | 68.8293 | 115.9195 | 123.4726 | 3.0075 | 123.5001 | 85.7208 | -0.28381 | 123.4726 | 3.0075 | 85.7208 | 115.9195 | 123.5001 | -123.8434 | -123.7885
4173.7188 | 123.8068 | -61.4182 | 62.1506 | 0.03685 | 0.015597 | 0.013841 | 0.0099698 | 0.060675 | -0.0014013 | 0.079049 | -58.3878 | 62.0682 | -61.7203 | -61.6104 | 54.5609 | 24.2981 | 8.1116 | 7.4707 | 62.1002 | -61.6928 | -0.30212 | -0.082398 | 3.0304 | -0.19226 | -7.5897 | -0.27466 | -0.050354 | 3.3325 | 69.5297 | 68.8889 | 115.979 | 123.4863 | 3.0304 | 123.5184 | 85.7162 | -0.27466 | 123.4863 | 3.0304 | 85.7162 | 115.979 | 123.5184 | -123.8708 | -123.8434
4174.7344 | 123.761 | -61.4227 | 62.1643 | -0.25307 | 0.015383 | 0.0099954 | 0.010824 | 0.059821 | -0.00076053 | 0.077767 | -58.342 | 62.1323 | -61.6974 | -61.5601 | 54.5013 | 24.2844 | 8.2489 | 7.4936 | 62.1414 | -61.7111 | -0.27466 | -0.032044 | 3.0807 | -0.13733 | -7.663 | -0.28839 | -0.022889 | 3.3554 | 69.6716 | 68.9163 | 115.9241 | 123.555 | 3.0807 | 123.5641 | 85.7071 | -0.28839 | 123.555 | 3.0807 | 85.7071 | 115.9241 | 123.5641 | -123.8617 | -123.8754
4175.7188 | 123.8297 | -61.3953 | 62.1643 | -0.08522 | 0.014742 | 0.0089274 | 0.0078336 | 0.059821 | 0.00030767 | 0.076913 | -58.3969 | 62.0682 | -61.7203 | -61.5601 | 54.5242 | 24.353 | 8.0887 | 7.5165 | 62.0911 | -61.6562 | -0.32501 | -0.096131 | 2.9984 | -0.1648 | -7.6401 | -0.26093 | -0.073243 | 3.3234 | 69.4839 | 68.9117 | 115.9195 | 123.4634 | 2.9984 | 123.4863 | 85.7483 | -0.26093 | 123.4634 | 2.9984 | 85.7483 | 115.9195 | 123.4863 | -123.8846 | -123.8205
4176.7188 | 123.7885 | -61.4136 | 62.1735 | -0.23781 | 0.015169 | 0.0132 | 0.017019 | 0.060462 | -0.0011877 | 0.078408 | -58.3191 | 62.1414 | -61.734 | -61.5784 | 54.4373 | 24.2157 | 8.2031 | 7.4524 | 62.1323 | -61.7065 | -0.32044 | -0.032044 | 3.0945 | -0.1648 | -7.7362 | -0.29297 | -0.041199 | 3.4149 | 69.6167 | 68.866 | 115.8508 | 123.555 | 3.0945 | 123.5458 | 85.6293 | -0.29297 | 123.555 | 3.0945 | 85.6293 | 115.8508 | 123.5458 | -123.9075 | -123.88
4177.7344 | 123.7747 | -61.3998 | 62.1689 | -0.10811 | 0.01581 | 0.013841 | 0.013815 | 0.059821 | -0.0020421 | 0.081185 | -58.3328 | 62.1368 | -61.7523 | -61.5646 | 54.5105 | 24.2844 | 8.1802 | 7.4615 | 62.146 | -61.6837 | -0.35248 | -0.032043 | 3.067 | -0.16479 | -7.6584 | -0.28381 | -0.022888 | 3.4195 | 69.5801 | 68.8614 | 115.9103 | 123.5367 | 3.067 | 123.5458 | 85.6842 | -0.28381 | 123.5367 | 3.067 | 85.6842 | 115.9103 | 123.5458 | -123.9212 | -123.8525
4178.7188 | 123.8617 | -61.4182 | 62.1368 | -0.0012969 | 0.015597 | 0.011918 | 0.0074062 | 0.060889 | 0.0020167 | 0.078835 | -58.3694 | 62.0865 | -61.7157 | -61.5875 | 54.5288 | 24.2981 | 8.107 | 7.489 | 62.1323 | -61.6928 | -0.29755 | -0.050354 | 3.0487 | -0.16937 | -7.608 | -0.27466 | -0.004578 | 3.3463 | 69.5251 | 68.9072 | 115.947 | 123.5046 | 3.0487 | 123.5504 | 85.7162 | -0.27466 | 123.5046 | 3.0487 | 85.7162 | 115.947 | 123.5504 | -123.8525 | -123.8297
4179.7188 | 123.8709 | -61.3861 | 62.1506 | -0.047073 | 0.01282 | 0.013627 | 0.0097562 | 0.058753 | 0.00030767 | 0.080117 | -58.3328 | 62.059 | -61.7065 | -61.5417 | 54.6387 | 24.2935 | 8.1116 | 7.5485 | 62.1094 | -61.6928 | -0.32044 | -0.091553 | 3.0533 | -0.15564 | -7.5119 | -0.3067 | -0.041199 | 3.3737 | 69.4977 | 68.9346 | 116.0248 | 123.4451 | 3.0533 | 123.4955 | 85.6796 | -0.3067 | 123.4451 | 3.0533 | 85.6796 | 116.0248 | 123.4955 | -123.8571 | -123.8434
4180.7188 | 123.8205 | -61.4136 | 62.1094 | 0.074997 | 0.015597 | 0.0070048 | 0.011679 | 0.058966 | -0.0020421 | 0.078195 | -58.3374 | 62.0453 | -61.7432 | -61.5829 | 54.5059 | 24.3027 | 8.0109 | 7.4478 | 62.0728 | -61.6928 | -0.32959 | -0.064087 | 3.0762 | -0.16937 | -7.6035 | -0.27924 | -0.036621 | 3.4058 | 69.4244 | 68.8614 | 115.9195 | 123.4589 | 3.0762 | 123.4863 | 85.7162 | -0.27924 | 123.4589 | 3.0762 | 85.7162 | 115.9195 | 123.4863 | -123.8525 | -123.8022
4181.7188 | 123.7793 | -61.4273 | 62.178 | -0.1844 | 0.012392 | 0.011918 | 0.014242 | 0.058325 | -0.00054693 | 0.079904 | -58.3649 | 62.1368 | -61.7386 | -61.5875 | 54.4922 | 24.2203 | 8.2581 | 7.4524 | 62.1552 | -61.702 | -0.31128 | -0.041199 | 3.0624 | -0.16022 | -7.6859 | -0.27466 | -0.022889 | 3.3737 | 69.6854 | 68.8797 | 115.9195 | 123.5641 | 3.0624 | 123.5825 | 85.6476 | -0.27466 | 123.5641 | 3.0624 | 85.6476 | 115.9195 | 123.5825 | -123.9166 | -123.88
4182.7188 | 123.8434 | -61.3907 | 62.1231 | -0.11574 | 0.014742 | 0.012986 | 0.0080472 | 0.05918 | -0.00054693 | 0.079049 | -58.0536 | 62.0682 | -61.6791 | -61.5051 | 54.5563 | 24.3484 | 8.02 | 7.5348 | 62.1048 | -61.6562 | -0.28839 | -0.054932 | 3.3371 | -0.11444 | -7.5668 | -0.2655 | -0.018311 | 3.6255 | 69.4107 | 68.9255 | 115.947 | 123.4589 | 3.3371 | 123.4955 | 85.7391 | -0.2655 | 123.4589 | 3.3371 | 85.7391 | 115.947 | 123.4955 | -123.8022 | -123.7793
4183.7188 | 123.8159 | -61.4227 | 62.1552 | 0.090256 | 0.013674 | 0.0093546 | 0.0071926 | 0.058325 | 9.4068e-05 | 0.080758 | -58.3694 | 62.0682 | -61.7249 | -61.6013 | 54.483 | 24.3164 | 8.1665 | 7.663 | 62.1506 | -61.6562 | -0.30213 | -0.086975 | 3.0533 | -0.17853 | -7.6721 | -0.23346 | -0.004577 | 3.3554 | 69.5892 | 69.0857 | 115.9058 | 123.4909 | 3.0533 | 123.5733 | 85.7391 | -0.23346 | 123.4909 | 3.0533 | 85.7391 | 115.9058 | 123.5733 | -123.88 | -123.8113
4184.7344 | 123.7656 | -61.4227 | 62.1964 | -0.17677 | 0.016878 | 0.011491 | 0.012747 | 0.05918 | -0.0020421 | 0.077554 | -58.3649 | 62.1597 | -61.734 | -61.5829 | 54.4556 | 24.3256 | 8.2306 | 7.3883 | 62.1826 | -61.7386 | -0.31128 | -0.036621 | 3.0579 | -0.16022 | -7.7408 | -0.31586 | -0.013733 | 3.3691 | 69.6533 | 68.811 | 115.8783 | 123.5825 | 3.0579 | 123.6053 | 85.7483 | -0.31586 | 123.5825 | 3.0579 | 85.7483 | 115.8783 | 123.6053 | -123.9304 | -123.9349
4185.7188 | 123.8342 | -61.3998 | 62.1506 | 0.04448 | 0.012392 | 0.0132 | 0.0061246 | 0.057685 | -0.00054693 | 0.078622 | -58.3878 | 62.059 | -61.7386 | -61.5784 | 54.5837 | 24.4034 | 8.0704 | 7.4432 | 62.1002 | -61.6699 | -0.33874 | -0.091553 | 3.0121 | -0.17853 | -7.5668 | -0.27008 | -0.050354 | 3.3508 | 69.4702 | 68.8431 | 115.9836 | 123.4589 | 3.0121 | 123.5001 | 85.8032 | -0.27008 | 123.4589 | 3.0121 | 85.8032 | 115.9836 | 123.5001 | -123.8892 | -123.8205
4186.7188 | 123.8022 | -61.3998 | 62.1689 | -0.1844 | 0.014742 | 0.014909 | 0.010611 | 0.05918 | -0.00076053 | 0.078195 | -58.2413 | 62.1002 | -61.7249 | -61.5555 | 54.5288 | 24.3988 | 8.1665 | 7.4753 | 62.1368 | -61.6974 | -0.32501 | -0.068664 | 3.1586 | -0.15564 | -7.6401 | -0.29755 | -0.032043 | 3.4836 | 69.5663 | 68.8751 | 115.9287 | 123.5001 | 3.1586 | 123.5367 | 85.7986 | -0.29755 | 123.5001 | 3.1586 | 85.7986 | 115.9287 | 123.5367 | -123.8937 | -123.8663
4187.7188 | 123.7976 | -61.4365 | 62.1368 | 0.16655 | 0.013674 | 0.012132 | 0.012533 | 0.059394 | -0.00097413 | 0.07969 | -58.2825 | 62.059 | -61.7569 | -61.615 | 54.5242 | 24.3851 | 8.0566 | 7.4387 | 62.0773 | -61.6928 | -0.32044 | -0.07782 | 3.154 | -0.17853 | -7.6126 | -0.25635 | -0.059509 | 3.4744 | 69.4931 | 68.8751 | 115.9607 | 123.4955 | 3.154 | 123.5138 | 85.8215 | -0.25635 | 123.4955 | 3.154 | 85.8215 | 115.9607 | 123.5138 | -123.8937 | -123.8297
4188.7188 | 123.9258 | -61.3998 | 62.1414 | 0.052109 | 0.014315 | 0.011704 | 0.0089016 | 0.058753 | -0.00054693 | 0.077981 | -58.2779 | 62.0728 | -61.7432 | -61.6013 | 54.5242 | 24.3484 | 8.0658 | 7.4295 | 62.0773 | -61.647 | -0.34332 | -0.068664 | 3.1219 | -0.20142 | -7.6172 | -0.24719 | -0.064086 | 3.4653 | 69.4656 | 68.8293 | 115.9241 | 123.4726 | 3.1219 | 123.4772 | 85.7483 | -0.24719 | 123.4726 | 3.1219 | 85.7483 | 115.9241 | 123.4772 | -123.8846 | -123.7885
4189.7344 | 123.7473 | -61.441 | 62.1826 | -0.24544 | 0.017306 | 0.012559 | 0.014669 | 0.057257 | -0.0011877 | 0.078622 | -58.2916 | 62.146 | -61.734 | -61.4594 | 54.2999 | 24.1287 | 8.2672 | 7.4158 | 62.1552 | -61.7432 | -0.29297 | -0.036621 | 3.1494 | -0.018311 | -7.8827 | -0.30212 | -0.027466 | 3.4424 | 69.7083 | 68.8568 | 115.741 | 123.587 | 3.1494 | 123.5962 | 85.5698 | -0.30212 | 123.587 | 3.1494 | 85.5698 | 115.741 | 123.5962 | -123.9166 | -123.9258
4190.7188 | 123.793 | -61.3861 | 62.1277 | -0.61928 | 0.016665 | 0.009141 | 0.0084744 | 0.059394 | 0.00073487 | 0.079904 | -58.3603 | 62.0773 | -61.7157 | -61.5921 | 54.451 | 24.2889 | 8.0658 | 7.457 | 62.1048 | -61.6745 | -0.32959 | -0.050354 | 3.0258 | -0.20599 | -7.6767 | -0.28839 | -0.022889 | 3.3554 | 69.4519 | 68.8431 | 115.8371 | 123.4634 | 3.0258 | 123.4909 | 85.675 | -0.28839 | 123.4634 | 3.0258 | 85.675 | 115.8371 | 123.4909 | -123.8434 | -123.8022
4191.7188 | 123.8022 | -61.4136 | 62.146 | -0.039444 | 0.012606 | 0.012986 | 0.0095424 | 0.061957 | 0.0018031 | 0.079904 | -58.3466 | 62.0865 | -61.702 | -61.5738 | 54.4556 | 24.3118 | 8.0566 | 7.4341 | 62.1048 | -61.6837 | -0.28839 | -0.059509 | 3.067 | -0.16022 | -7.6904 | -0.27008 | -0.041199 | 3.3554 | 69.4702 | 68.8477 | 115.8691 | 123.5001 | 3.067 | 123.5184 | 85.7254 | -0.27008 | 123.5001 | 3.067 | 85.7254 | 115.8691 | 123.5184 | -123.848 | -123.8297
4192.7188 | 123.8297 | -61.4044 | 62.114 | 0.10551 | 0.015383 | 0.014909 | 0.0089016 | 0.058753 | 0.0018031 | 0.07969 | -58.342 | 62.0499 | -61.7477 | -61.6058 | 54.4006 | 24.234 | 8.0017 | 7.4432 | 62.0773 | -61.7203 | -0.34332 | -0.064087 | 3.0624 | -0.20142 | -7.7133 | -0.31586 | -0.036621 | 3.4058 | 69.4061 | 68.8477 | 115.8051 | 123.4543 | 3.0624 | 123.4818 | 85.6384 | -0.31586 | 123.4543 | 3.0624 | 85.6384 | 115.8051 | 123.4818 | -123.8617 | -123.8342
4193.7188 | 123.8342 | -61.409 | 62.1094 | -0.17677 | 0.015169 | 0.015977 | 0.010824 | 0.060462 | 0.00073487 | 0.079476 | -58.3511 | 62.0682 | -61.7386 | -61.5509 | 54.4235 | 24.1928 | 8.0063 | 7.4936 | 62.0865 | -61.702 | -0.32959 | -0.041199 | 3.0579 | -0.14191 | -7.6859 | -0.29297 | -0.022888 | 3.3875 | 69.4153 | 68.9026 | 115.8325 | 123.4772 | 3.0579 | 123.4955 | 85.6018 | -0.29297 | 123.4772 | 3.0579 | 85.6018 | 115.8325 | 123.4955 | -123.848 | -123.8113
4194.7344 | 123.7701 | -61.4136 | 62.1872 | -0.22255 | 0.013674 | 0.0097818 | 0.01296 | 0.059821 | -0.0016149 | 0.079263 | -58.3374 | 62.1231 | -61.702 | -61.5601 | 54.4922 | 24.1974 | 8.1757 | 7.4615 | 62.1506 | -61.6791 | -0.28839 | -0.064087 | 3.0762 | -0.14649 | -7.695 | -0.2655 | -0.036621 | 3.3646 | 69.5892 | 68.8751 | 115.9058 | 123.5367 | 3.0762 | 123.5641 | 85.611 | -0.2655 | 123.5367 | 3.0762 | 85.611 | 115.9058 | 123.5641 | -123.8892 | -123.8663
4195.7188 | 123.8068 | -61.3861 | 62.1597 | 0.029221 | 0.011538 | 0.010209 | 0.0097562 | 0.058325 | -0.0022559 | 0.07969 | -58.493 | 62.0819 | -61.6974 | -61.6013 | 54.4373 | 24.1837 | 8.0246 | 7.4112 | 62.1048 | -61.6837 | -0.31128 | -0.07782 | 2.8931 | -0.21515 | -7.7225 | -0.29755 | -0.054932 | 3.2043 | 69.4107 | 68.7973 | 115.8234 | 123.468 | 2.8931 | 123.4909 | 85.5698 | -0.29755 | 123.468 | 2.8931 | 85.5698 | 115.8234 | 123.4909 | -123.8571 | -123.8434
4196.7188 | 123.8388 | -61.3953 | 62.146 | -0.0089264 | 0.014315 | 0.012986 | 0.0089016 | 0.058539 | 0.00094847 | 0.079049 | -58.3832 | 62.0819 | -61.7386 | -61.5738 | 54.4601 | 24.2661 | 8.0429 | 7.457 | 62.0865 | -61.6974 | -0.34332 | -0.064087 | 3.0121 | -0.17853 | -7.6859 | -0.30212 | -0.059509 | 3.3554 | 69.4382 | 68.8522 | 115.8554 | 123.4772 | 3.0121 | 123.4818 | 85.6613 | -0.30212 | 123.4772 | 3.0121 | 85.6613 | 115.8554 | 123.4818 | -123.8846 | -123.8434
4197.7188 | 123.8434 | -61.4136 | 62.1552 | 0.03685 | 0.014315 | 0.011704 | 0.010183 | 0.058112 | 0.00030767 | 0.078195 | -58.4198 | 62.0819 | -61.7615 | -61.5784 | 54.3228 | 24.2294 | 8.1528 | 7.4844 | 62.0728 | -61.702 | -0.3479 | -0.073242 | 2.9938 | -0.1648 | -7.8323 | -0.28839 | -0.082397 | 3.3417 | 69.5663 | 68.898 | 115.7364 | 123.4955 | 2.9938 | 123.4863 | 85.643 | -0.28839 | 123.4955 | 2.9938 | 85.643 | 115.7364 | 123.4863 | -123.9166 | -123.8571
4198.7188 | 123.8297 | -61.4044 | 62.1231 | 0.1284 | 0.011965 | 0.015763 | 0.0095424 | 0.058325 | -0.0011877 | 0.080331 | -58.3878 | 62.0911 | -61.7294 | -61.5921 | 54.3961 | 24.2523 | 8.0475 | 7.4478 | 62.1002 | -61.7203 | -0.32501 | -0.032044 | 3.0167 | -0.18768 | -7.7271 | -0.31586 | -0.022888 | 3.3417 | 69.4519 | 68.8522 | 115.8005 | 123.4955 | 3.0167 | 123.5046 | 85.6567 | -0.31586 | 123.4955 | 3.0167 | 85.6567 | 115.8005 | 123.5046 | -123.8525 | -123.8434
4199.7188 | 123.7473 | -61.4182 | 62.1597 | -0.29121 | 0.01282 | 0.011491 | 0.01531 | 0.05918 | -0.0026831 | 0.079904 | -58.5205 | 62.1414 | -61.7294 | -61.6333 | 54.3137 | 24.1653 | 8.1848 | 7.3654 | 62.1872 | -61.7294 | -0.31128 | -0.018311 | 2.8976 | -0.21515 | -7.8461 | -0.31128 | 0.027466 | 3.2089 | 69.603 | 68.7836 | 115.7318 | 123.5596 | 2.8976 | 123.6053 | 85.5835 | -0.31128 | 123.5596 | 2.8976 | 85.5835 | 115.7318 | 123.6053 | -123.8892 | -123.8892
4200.7188 | 123.8342 | -61.3998 | 62.1506 | 0.17418 | 0.014956 | 0.016618 | 0.017233 | 0.060034 | 0.00052127 | 0.078622 | -58.3191 | 62.0773 | -61.7111 | -61.5555 | 54.3869 | 24.2935 | 7.9285 | 7.457 | 62.0819 | -61.7065 | -0.31128 | -0.073242 | 3.0807 | -0.15564 | -7.7637 | -0.3067 | -0.068665 | 3.392 | 69.3283 | 68.8568 | 115.7867 | 123.4772 | 3.0807 | 123.4818 | 85.6934 | -0.3067 | 123.4772 | 3.0807 | 85.6934 | 115.7867 | 123.4818 | -123.8617 | -123.8571
4201.7188 | 123.8205 | -61.3998 | 62.1094 | 0.12077 | 0.014101 | 0.011064 | 0.010397 | 0.060034 | 0.0011621 | 0.080117 | -58.3603 | 62.059 | -61.7157 | -61.5646 | 54.4052 | 24.3118 | 7.9697 | 7.4203 | 62.0956 | -61.6837 | -0.31586 | -0.050354 | 3.0396 | -0.16479 | -7.7042 | -0.28381 | -0.013733 | 3.3554 | 69.3695 | 68.8202 | 115.8051 | 123.4589 | 3.0396 | 123.4955 | 85.7117 | -0.28381 | 123.4589 | 3.0396 | 85.7117 | 115.8051 | 123.4955 | -123.8251 | -123.793
4202.7188 | 123.8022 | -61.3907 | 62.1368 | 0.10551 | 0.015597 | 0.013627 | 0.011465 | 0.060248 | 0.00030767 | 0.079049 | -58.3649 | 62.0682 | -61.734 | -61.5601 | 54.4098 | 24.3118 | 7.9742 | 7.4295 | 62.0636 | -61.7065 | -0.34332 | -0.068665 | 3.0258 | -0.16937 | -7.7271 | -0.31586 | -0.073242 | 3.3691 | 69.3649 | 68.8202 | 115.8005 | 123.4589 | 3.0258 | 123.4543 | 85.7025 | -0.31586 | 123.4589 | 3.0258 | 85.7025 | 115.8005 | 123.4543 | -123.8708 | -123.8434
4203.7188 | 123.8571 | -61.409 | 62.1048 | 0.15129 | 0.014315 | 0.015763 | 0.011679 | 0.060889 | 0.0028711 | 0.080972 | -58.342 | 62.0728 | -61.7111 | -61.5646 | 54.4189 | 24.2294 | 7.9788 | 7.4615 | 62.1002 | -61.6974 | -0.30212 | -0.032043 | 3.067 | -0.15564 | -7.6859 | -0.28839 | -0.004577 | 3.3691 | 69.3878 | 68.8705 | 115.8279 | 123.4818 | 3.067 | 123.5092 | 85.6384 | -0.28839 | 123.4818 | 3.067 | 85.6384 | 115.8279 | 123.5092 | -123.8159 | -123.8022
4204.7344 | 123.7793 | -61.409 | 62.1597 | -0.19203 | 0.015383 | 0.015122 | 0.018301 | 0.060462 | -0.00054693 | 0.077554 | -58.3374 | 62.178 | -61.7157 | -61.5692 | 54.4556 | 24.2706 | 8.1345 | 7.4158 | 62.146 | -61.7294 | -0.3067 | 0.018311 | 3.0716 | -0.16022 | -7.7042 | -0.32043 | -0.013733 | 3.3783 | 69.5435 | 68.8248 | 115.8646 | 123.587 | 3.0716 | 123.555 | 85.6796 | -0.32043 | 123.587 | 3.0716 | 85.6796 | 115.8646 | 123.555 | -123.8754 | -123.8892
4205.7188 | 123.848 | -61.4044 | 62.0865 | 1.4941 | 0.014742 | 0.014695 | 0.011892 | 0.062171 | -0.00054693 | 0.078195 | -58.1955 | 62.0911 | -61.7065 | -61.5326 | 54.4647 | 24.3164 | 7.9742 | 7.4799 | 62.0728 | -61.734 | -0.30212 | 0.004577 | 3.2089 | -0.12817 | -7.6218 | -0.32959 | -0.013733 | 3.511 | 69.3787 | 68.8843 | 115.8691 | 123.4955 | 3.2089 | 123.4772 | 85.7208 | -0.32959 | 123.4955 | 3.2089 | 85.7208 | 115.8691 | 123.4772 | -123.793 | -123.8205
4206.7188 | 123.8251 | -61.4182 | 62.1231 | 0.15892 | 0.013674 | 0.016404 | 0.011679 | 0.061743 | 0.00030767 | 0.077767 | -58.3557 | 62.0773 | -61.7249 | -61.5829 | 54.4373 | 24.3393 | 8.02 | 7.4524 | 62.1323 | -61.7203 | -0.3067 | -0.045776 | 3.0624 | -0.16479 | -7.6859 | -0.30212 | 0.009155 | 3.3691 | 69.4382 | 68.8705 | 115.8554 | 123.4955 | 3.0624 | 123.5504 | 85.7574 | -0.30212 | 123.4955 | 3.0624 | 85.7574 | 115.8554 | 123.5504 | -123.848 | -123.8434
4207.7188 | 123.8068 | -61.441 | 62.1002 | 0.23521 | 0.016878 | 0.019395 | 0.015951 | 0.060034 | -0.00011953 | 0.079904 | -58.4015 | 62.1368 | -61.7752 | -61.6058 | 54.4052 | 24.321 | 8.075 | 7.3929 | 62.1002 | -61.7432 | -0.33417 | 0.036621 | 3.0396 | -0.16479 | -7.695 | -0.30212 | 0 | 3.3737 | 69.516 | 68.8339 | 115.8463 | 123.5779 | 3.0396 | 123.5413 | 85.762 | -0.30212 | 123.5779 | 3.0396 | 85.762 | 115.8463 | 123.5413 | -123.8754 | -123.8434
4208.7188 | 123.848 | -61.409 | 62.0956 | 0.28862 | 0.016878 | 0.014268 | 0.014883 | 0.062384 | -0.00076053 | 0.080117 | -58.3328 | 62.1002 | -61.7432 | -61.5738 | 54.4235 | 24.3622 | 8.0246 | 7.4615 | 62.0728 | -61.7157 | -0.33417 | 0.004578 | 3.0762 | -0.16479 | -7.6721 | -0.3067 | -0.022888 | 3.4103 | 69.4336 | 68.8705 | 115.8325 | 123.5092 | 3.0762 | 123.4818 | 85.7712 | -0.3067 | 123.5092 | 3.0762 | 85.7712 | 115.8325 | 123.4818 | -123.8388 | -123.8113
4209.7344 | 123.7701 | -61.4502 | 62.1643 | -0.10048 | 0.019228 | 0.0132 | 0.017019 | 0.063239 | 0.0032983 | 0.079049 | -58.3374 | 62.1964 | -61.7203 | -61.6333 | 54.538 | 24.2752 | 8.194 | 7.4753 | 62.1597 | -61.7249 | -0.27008 | 0.032043 | 3.1128 | -0.18311 | -7.6263 | -0.27466 | -0.004578 | 3.3829 | 69.6442 | 68.9255 | 115.9882 | 123.6465 | 3.1128 | 123.6099 | 85.7254 | -0.27466 | 123.6465 | 3.1128 | 85.7254 | 115.9882 | 123.6099 | -123.8846 | -123.8892
4210.7188 | 123.8342 | -61.4136 | 62.1094 | 0.2047 | 0.015169 | 0.014268 | 0.014456 | 0.061743 | -0.00033333 | 0.078408 | -58.342 | 62.1094 | -61.7157 | -61.5509 | 54.4327 | 24.4492 | 7.6675 | 7.3563 | 62.0544 | -61.7111 | -0.30212 | 0 | 3.0716 | -0.13733 | -7.6767 | -0.29755 | -0.054932 | 3.3737 | 69.0811 | 68.7698 | 115.8463 | 123.5229 | 3.0716 | 123.468 | 85.8627 | -0.29755 | 123.5229 | 3.0716 | 85.8627 | 115.8463 | 123.468 | -123.8251 | -123.8205
4211.7188 | 123.8571 | -61.4136 | 62.1094 | 0.17418 | 0.016665 | 0.014268 | 0.011251 | 0.062598 | 0.00052127 | 0.077981 | -58.3466 | 62.0956 | -61.734 | -61.5738 | 54.451 | 24.2661 | 8.0017 | 7.4615 | 62.0773 | -61.7203 | -0.32044 | -0.013733 | 3.067 | -0.16022 | -7.6584 | -0.3067 | -0.032043 | 3.3875 | 69.4153 | 68.8751 | 115.8646 | 123.5092 | 3.067 | 123.4909 | 85.6796 | -0.3067 | 123.5092 | 3.067 | 85.6796 | 115.8646 | 123.4909 | -123.8434 | -123.8297
4212.7188 | 123.8388 | -61.409 | 62.1048 | 0.15129 | 0.016238 | 0.012559 | 0.01531 | 0.06153 | -0.00033333 | 0.080972 | -58.342 | 62.1323 | -61.734 | -61.5692 | 54.3823 | 24.3347 | 8.0246 | 7.4432 | 62.0819 | -61.734 | -0.32501 | 0.027466 | 3.067 | -0.16022 | -7.7225 | -0.32501 | -0.022888 | 3.392 | 69.4336 | 68.8522 | 115.7913 | 123.5413 | 3.067 | 123.4909 | 85.7437 | -0.32501 | 123.5413 | 3.067 | 85.7437 | 115.7913 | 123.4909 | -123.8388 | -123.8388
4213.7188 | 123.8251 | -61.409 | 62.0956 | 0.24284 | 0.018374 | 0.012773 | 0.008688 | 0.060675 | 0.00073487 | 0.079049 | -58.2138 | 62.0911 | -61.7523 | -61.5189 | 54.4464 | 24.3484 | 8.0383 | 7.5394 | 62.1002 | -61.7203 | -0.34332 | -0.004578 | 3.1952 | -0.10986 | -7.6492 | -0.31128 | 0.004578 | 3.5385 | 69.4473 | 68.9484 | 115.8554 | 123.5001 | 3.1952 | 123.5092 | 85.7574 | -0.31128 | 123.5001 | 3.1952 | 85.7574 | 115.8554 | 123.5092 | -123.848 | -123.8159
4214.7344 | 123.8251 | -61.3998 | 62.114 | -0.047073 | 0.012606 | 0.015977 | 0.0067654 | 0.060248 | 0.00094847 | 0.080331 | -58.3969 | 62.0682 | -61.7386 | -61.5646 | 54.4052 | 24.2706 | 8.1345 | 7.4982 | 62.1185 | -61.6791 | -0.33874 | -0.045777 | 3.0029 | -0.16479 | -7.7087 | -0.27924 | 0.004577 | 3.3417 | 69.5343 | 68.898 | 115.8051 | 123.468 | 3.0029 | 123.5184 | 85.6705 | -0.27924 | 123.468 | 3.0029 | 85.6705 | 115.8051 | 123.5184 | -123.8525 | -123.793
4215.7188 | 123.8113 | -61.4227 | 62.1185 | -0.016556 | 0.015597 | 0.010636 | 0.012106 | 0.060675 | -0.0014013 | 0.080117 | -58.3969 | 62.1185 | -61.7111 | -61.6104 | 54.7165 | 24.408 | 7.9742 | 7.489 | 62.1231 | -61.7249 | -0.28839 | 0 | 3.0258 | -0.18768 | -7.402 | -0.30213 | 0.004578 | 3.3142 | 69.397 | 68.9117 | 116.1392 | 123.5413 | 3.0258 | 123.5458 | 85.8307 | -0.30213 | 123.5413 | 3.0258 | 85.8307 | 116.1392 | 123.5458 | -123.8297 | -123.8434
4216.7188 | 123.8388 | -61.4227 | 62.1185 | 0.18944 | 0.017947 | 0.013413 | 0.015738 | 0.059821 | 0.00030767 | 0.080117 | -58.3374 | 62.1094 | -61.7569 | -61.5509 | 54.4556 | 24.2981 | 8.0429 | 7.4615 | 62.0728 | -61.7111 | -0.33417 | -0.009155 | 3.0853 | -0.12817 | -7.663 | -0.28839 | -0.045776 | 3.4195 | 69.4656 | 68.8843 | 115.8783 | 123.5321 | 3.0853 | 123.4955 | 85.7208 | -0.28839 | 123.5321 | 3.0853 | 85.7208 | 115.8783 | 123.4955 | -123.8754 | -123.8297
4217.7188 | 123.8434 | -61.377 | 62.1323 | 0.23521 | 0.016451 | 0.012132 | 0.015951 | 0.060675 | 0.00073487 | 0.079476 | -58.3511 | 62.114 | -61.7477 | -61.5646 | 54.3594 | 24.2111 | 8.0063 | 7.4432 | 62.0956 | -61.7294 | -0.37079 | -0.01831 | 3.0258 | -0.18768 | -7.7728 | -0.35248 | -0.036621 | 3.3966 | 69.3832 | 68.8202 | 115.7364 | 123.4909 | 3.0258 | 123.4726 | 85.5881 | -0.35248 | 123.4909 | 3.0258 | 85.5881 | 115.7364 | 123.4726 | -123.88 | -123.8617
4218.7188 | 123.8251 | -61.3861 | 62.1185 | 0.19707 | 0.014529 | 0.016191 | 0.014883 | 0.060034 | -0.00054693 | 0.076486 | -58.3511 | 62.1506 | -61.734 | -61.5875 | 54.3823 | 24.1745 | 7.9285 | 7.3471 | 62.0819 | -61.7294 | -0.3479 | 0.032044 | 3.035 | -0.20142 | -7.7362 | -0.34332 | -0.036621 | 3.3829 | 69.3146 | 68.7332 | 115.7684 | 123.5367 | 3.035 | 123.468 | 85.5606 | -0.34332 | 123.5367 | 3.035 | 85.5606 | 115.7684 | 123.468 | -123.8525 | -123.848
4219.7344 | 123.7976 | -61.3907 | 62.1735 | -0.24544 | 0.013674 | 0.011277 | 0.010183 | 0.059394 | -0.0014013 | 0.080117 | -58.3511 | 62.1048 | -61.6928 | -61.5417 | 54.4327 | 24.2249 | 8.1619 | 7.4478 | 62.1735 | -61.6974 | -0.30212 | -0.068665 | 3.0396 | -0.15106 | -7.7408 | -0.3067 | 0 | 3.3417 | 69.5526 | 68.8385 | 115.8234 | 123.4955 | 3.0396 | 123.5641 | 85.6155 | -0.3067 | 123.4955 | 3.0396 | 85.6155 | 115.8234 | 123.5641 | -123.8663 | -123.8708
4220.7188 | 123.7335 | -61.4456 | 62.1414 | -0.23018 | 0.016024 | 0.015336 | 0.01766 | 0.060462 | 0.0015893 | 0.079263 | -58.4015 | 62.1872 | -61.7523 | -61.6608 | 54.3686 | 24.1882 | 8.1253 | 7.2922 | 62.1368 | -61.7569 | -0.3067 | 0.045777 | 3.0441 | -0.21515 | -7.7728 | -0.31128 | -0.004577 | 3.3508 | 69.5709 | 68.7378 | 115.8142 | 123.6328 | 3.0441 | 123.5825 | 85.6338 | -0.31128 | 123.6328 | 3.0441 | 85.6338 | 115.8142 | 123.5825 | -123.8937 | -123.8983
4221.7188 | 123.7335 | -61.4456 | 62.146 | 0.26573 | 0.017519 | 0.011491 | 0.015097 | 0.060675 | 0.00094847 | 0.081185 | -58.429 | 62.2055 | -61.7432 | -61.6653 | 54.3365 | 24.1379 | 8.1482 | 7.2922 | 62.1414 | -61.7569 | -0.29755 | 0.059509 | 3.0167 | -0.21973 | -7.8094 | -0.31128 | -0.004578 | 3.3142 | 69.5938 | 68.7378 | 115.7822 | 123.6511 | 3.0167 | 123.587 | 85.5835 | -0.31128 | 123.6511 | 3.0167 | 85.5835 | 115.7822 | 123.587 | -123.8892 | -123.9029
4222.7188 | 123.8297 | -61.3953 | 62.1094 | 0.2047 | 0.016665 | 0.016618 | 0.014029 | 0.062598 | 0.0015893 | 0.080544 | -58.3466 | 62.1048 | -61.7386 | -61.5738 | 54.4281 | 24.1699 | 8.02 | 7.4478 | 62.0911 | -61.7386 | -0.34332 | -0.004578 | 3.0487 | -0.17853 | -7.6813 | -0.34332 | -0.018311 | 3.392 | 69.4153 | 68.8431 | 115.8234 | 123.5001 | 3.0487 | 123.4863 | 85.5652 | -0.34332 | 123.5001 | 3.0487 | 85.5652 | 115.8234 | 123.4863 | -123.848 | -123.848
4223.7188 | 123.8388 | -61.4044 | 62.1094 | 0.21996 | 0.016451 | 0.013841 | 0.013174 | 0.063452 | -0.00054693 | 0.078835 | -58.3694 | 62.1506 | -61.7432 | -61.5875 | 54.451 | 24.2432 | 7.9971 | 7.4249 | 62.0728 | -61.7523 | -0.33875 | 0.041199 | 3.035 | -0.18311 | -7.6584 | -0.3479 | -0.036621 | 3.3737 | 69.4016 | 68.8293 | 115.8554 | 123.555 | 3.035 | 123.4772 | 85.6476 | -0.3479 | 123.555 | 3.035 | 85.6476 | 115.8554 | 123.4772 | -123.8525 | -123.8617
4224.7188 | 123.8159 | -61.4044 | 62.114 | 0.059738 | 0.013247 | 0.010636 | 0.010824 | 0.061316 | -0.00054693 | 0.080331 | -58.4198 | 62.1002 | -61.6882 | -61.6241 | 54.5242 | 24.1882 | 8.0521 | 7.3929 | 62.1323 | -61.6882 | -0.28381 | -0.013733 | 2.9846 | -0.21973 | -7.5897 | -0.28381 | 0.01831 | 3.2684 | 69.4565 | 68.7973 | 115.9287 | 123.5046 | 2.9846 | 123.5367 | 85.5927 | -0.28381 | 123.5046 | 2.9846 | 85.5927 | 115.9287 | 123.5367 | -123.8022 | -123.8022
4225.7188 | 123.8113 | -61.4365 | 62.114 | 0.16655 | 0.017947 | 0.012345 | 0.017447 | 0.062384 | -0.00033333 | 0.077126 | -58.3694 | 62.1552 | -61.7477 | -61.6104 | 54.4144 | 24.1013 | 8.0566 | 7.3654 | 62.1277 | -61.7477 | -0.31128 | 0.041198 | 3.067 | -0.17395 | -7.6996 | -0.31128 | 0.013733 | 3.3783 | 69.4931 | 68.8019 | 115.8508 | 123.5916 | 3.067 | 123.5641 | 85.5377 | -0.31128 | 123.5916 | 3.067 | 85.5377 | 115.8508 | 123.5641 | -123.8617 | -123.8617
4226.7188 | 123.7747 | -61.4273 | 62.114 | 0.21233 | 0.016451 | 0.013413 | 0.014456 | 0.060675 | -0.0014013 | 0.07969 | -58.3878 | 62.1506 | -61.7477 | -61.6241 | 54.4098 | 24.0829 | 8.0704 | 7.3196 | 62.1414 | -61.7294 | -0.32044 | 0.036621 | 3.0396 | -0.19684 | -7.7042 | -0.30212 | 0.027465 | 3.36 | 69.4977 | 68.7469 | 115.8371 | 123.5779 | 3.0396 | 123.5687 | 85.5103 | -0.30212 | 123.5779 | 3.0396 | 85.5103 | 115.8371 | 123.5687 | -123.8617 | -123.8434
4227.7188 | 123.7564 | -61.4639 | 62.1368 | 0.12077 | 0.018374 | 0.0132 | 0.018087 | 0.05918 | -0.0011877 | 0.07969 | -58.3923 | 62.1735 | -61.7661 | -61.6974 | 54.4876 | 24.0555 | 8.0887 | 7.3013 | 62.146 | -61.7477 | -0.30212 | 0.036621 | 3.0716 | -0.23346 | -7.6492 | -0.28381 | 0.009155 | 3.3737 | 69.5526 | 68.7653 | 115.9515 | 123.6374 | 3.0716 | 123.6099 | 85.5194 | -0.28381 | 123.6374 | 3.0716 | 85.5194 | 115.9515 | 123.6099 | -123.9029 | -123.8846
4228.7188 | 123.7152 | -61.4502 | 62.1552 | 0.14366 | 0.019656 | 0.014054 | 0.014669 | 0.062384 | 0.0020167 | 0.082467 | -58.4198 | 62.2055 | -61.7386 | -61.9583 | 54.3686 | 24.3942 | 8.1161 | 7.2556 | 62.1826 | -61.734 | -0.28839 | 0.050354 | 3.0304 | -0.50812 | -7.7866 | -0.28381 | 0.027466 | 3.3188 | 69.5663 | 68.7057 | 115.8188 | 123.6557 | 3.0304 | 123.6328 | 85.8444 | -0.28381 | 123.6557 | 3.0304 | 85.8444 | 115.8188 | 123.6328 | -123.8937 | -123.8892
4229.7188 | 123.7839 | -61.3998 | 62.1368 | 0.04448 | 0.01282 | 0.012345 | 0.0050564 | 0.064093 | -0.00054693 | 0.079476 | -58.3969 | 62.0499 | -61.7432 | -61.6196 | 54.4418 | 24.115 | 8.0475 | 7.402 | 62.114 | -61.7111 | -0.34332 | -0.086975 | 3.0029 | -0.21973 | -7.695 | -0.31128 | -0.022888 | 3.3463 | 69.4473 | 68.8019 | 115.8417 | 123.4497 | 3.0029 | 123.5138 | 85.5148 | -0.31128 | 123.4497 | 3.0029 | 85.5148 | 115.8417 | 123.5138 | -123.88 | -123.848
4230.7188 | 123.8571 | -61.4227 | 62.1414 | 0.18181 | 0.015169 | 0.016831 | 0.014456 | 0.062384 | -0.00054693 | 0.079476 | -58.3694 | 62.1277 | -61.7569 | -61.6013 | 54.4464 | 24.0829 | 7.988 | 7.3746 | 62.146 | -61.734 | -0.33417 | -0.013732 | 3.0533 | -0.17853 | -7.695 | -0.31128 | 0.004578 | 3.3875 | 69.4107 | 68.7973 | 115.8691 | 123.5504 | 3.0533 | 123.5687 | 85.5057 | -0.31128 | 123.5504 | 3.0533 | 85.5057 | 115.8691 | 123.5687 | -123.8983 | -123.8754
4231.7188 | 123.8022 | -61.4319 | 62.1231 | 0.18944 | 0.016451 | 0.01555 | 0.015097 | 0.062598 | 0.00030767 | 0.07969 | -58.3557 | 62.1552 | -61.734 | -61.615 | 54.4098 | 24.1562 | 7.988 | 7.3242 | 62.1094 | -61.7523 | -0.30212 | 0.032043 | 3.0762 | -0.1831 | -7.7133 | -0.32043 | -0.013733 | 3.3783 | 69.4199 | 68.7561 | 115.8417 | 123.587 | 3.0762 | 123.5413 | 85.5881 | -0.32043 | 123.587 | 3.0762 | 85.5881 | 115.8417 | 123.5413 | -123.8571 | -123.8754
4232.7188 | 123.8113 | -61.4319 | 62.1277 | 0.18181 | 0.014742 | 0.011491 | 0.012747 | 0.060675 | 0.00030767 | 0.079263 | -58.3878 | 62.1689 | -61.7844 | -61.615 | 54.4281 | 24.1745 | 8.0154 | 7.3425 | 62.1185 | -61.7752 | -0.35248 | 0.041198 | 3.0441 | -0.1831 | -7.6996 | -0.34332 | -0.009156 | 3.3966 | 69.4473 | 68.7744 | 115.86 | 123.6008 | 3.0441 | 123.5504 | 85.6064 | -0.34332 | 123.6008 | 3.0441 | 85.6064 | 115.86 | 123.5504 | -123.912 | -123.9029
4233.7188 | 123.7885 | -61.4456 | 62.1094 | 0.15892 | 0.017306 | 0.012986 | 0.014029 | 0.062598 | 9.4068e-05 | 0.077981 | -58.3786 | 62.1689 | -61.7569 | -61.6287 | 54.4052 | 24.1241 | 8.0154 | 7.3517 | 62.1368 | -61.7523 | -0.31128 | 0.059509 | 3.067 | -0.1831 | -7.7042 | -0.3067 | 0.027466 | 3.3783 | 69.4611 | 68.7973 | 115.8508 | 123.6145 | 3.067 | 123.5825 | 85.5698 | -0.3067 | 123.6145 | 3.067 | 85.5698 | 115.8508 | 123.5825 | -123.8663 | -123.8617
4234.7188 | 123.7839 | -61.4365 | 62.1368 | 0.2047 | 0.017519 | 0.015763 | 0.013388 | 0.06153 | 0.00073487 | 0.080331 | -58.4015 | 62.1414 | -61.7569 | -61.6425 | 54.3686 | 24.1196 | 8.0521 | 7.3288 | 62.1277 | -61.7432 | -0.32044 | 0.004577 | 3.035 | -0.20599 | -7.7682 | -0.3067 | -0.009155 | 3.3554 | 69.4885 | 68.7653 | 115.8051 | 123.5779 | 3.035 | 123.5641 | 85.556 | -0.3067 | 123.5779 | 3.035 | 85.556 | 115.8051 | 123.5641 | -123.8937 | -123.88
4235.7188 | 123.7289 | -61.4594 | 62.1414 | 2.6232 | 0.01816 | 0.0093546 | 0.012533 | 0.063452 | 0.0018031 | 0.080972 | -58.1497 | 62.146 | -61.7569 | -61.6379 | 54.3503 | 24.1745 | 8.1711 | 7.3059 | 62.1368 | -61.7706 | -0.29755 | 0.004578 | 3.3096 | -0.17853 | -7.7911 | -0.31128 | -0.004577 | 3.6072 | 69.6304 | 68.7653 | 115.8096 | 123.6053 | 3.3096 | 123.5962 | 85.6339 | -0.31128 | 123.6053 | 3.3096 | 85.6339 | 115.8096 | 123.5962 | -123.8983 | -123.912
4236.7188 | 123.8342 | -61.3998 | 62.1002 | 0.13603 | 0.018374 | 0.016618 | 0.01296 | 0.063452 | -0.0011877 | 0.077767 | -58.3466 | 62.1048 | -61.7569 | -61.5692 | 54.4556 | 24.3439 | 7.988 | 7.4249 | 62.1048 | -61.7065 | -0.35706 | 0.004577 | 3.0533 | -0.16937 | -7.6447 | -0.3067 | 0.004577 | 3.4103 | 69.3878 | 68.8248 | 115.8554 | 123.5046 | 3.0533 | 123.5046 | 85.7437 | -0.3067 | 123.5046 | 3.0533 | 85.7437 | 115.8554 | 123.5046 | -123.8571 | -123.8068
4237.7188 | 123.8159 | -61.4182 | 62.114 | 0.2047 | 0.01581 | 0.0132 | 0.01296 | 0.063025 | -0.0026831 | 0.079476 | -58.3374 | 62.1414 | -61.7294 | -61.5738 | 54.5105 | 24.2752 | 7.9193 | 7.3654 | 62.1002 | -61.6974 | -0.31128 | 0.027465 | 3.0808 | -0.15564 | -7.6035 | -0.27924 | -0.013733 | 3.392 | 69.3375 | 68.7836 | 115.9287 | 123.5596 | 3.0808 | 123.5184 | 85.6934 | -0.27924 | 123.5596 | 3.0808 | 85.6934 | 115.9287 | 123.5184 | -123.8434 | -123.8113
4238.7188 | 123.8388 | -61.4136 | 62.1323 | 0.21233 | 0.014101 | 0.011277 | 0.012747 | 0.064521 | -0.00011953 | 0.079904 | -58.3786 | 62.1414 | -61.7432 | -61.5875 | 54.4739 | 24.2477 | 7.9834 | 7.3654 | 62.1002 | -61.7523 | -0.32959 | 0.009155 | 3.035 | -0.17395 | -7.6584 | -0.33875 | -0.032043 | 3.3646 | 69.397 | 68.779 | 115.8875 | 123.555 | 3.035 | 123.5138 | 85.6613 | -0.33875 | 123.555 | 3.035 | 85.6613 | 115.8875 | 123.5138 | -123.8754 | -123.8846
4239.7188 | 123.8342 | -61.4273 | 62.1323 | -0.19966 | 0.01282 | 0.013413 | 0.0089016 | 0.060675 | 0.0011621 | 0.080972 | -58.4473 | 62.1048 | -61.7249 | -61.6241 | 54.5059 | 24.3118 | 8.0338 | 7.3883 | 62.1185 | -61.6882 | -0.29755 | -0.027466 | 2.98 | -0.19684 | -7.6263 | -0.26093 | -0.013733 | 3.2776 | 69.4611 | 68.8156 | 115.9332 | 123.5321 | 2.98 | 123.5458 | 85.7391 | -0.26093 | 123.5321 | 2.98 | 85.7391 | 115.9332 | 123.5458 | -123.8571 | -123.8205
4240.7188 | 123.8159 | -61.4273 | 62.1277 | 0.18181 | 0.016238 | 0.01085 | 0.016806 | 0.061743 | -0.00054693 | 0.080117 | -58.374 | 62.146 | -61.7477 | -61.6241 | 54.4556 | 24.2432 | 7.9834 | 7.338 | 62.0773 | -61.7798 | -0.32044 | 0.01831 | 3.0533 | -0.19684 | -7.6721 | -0.35248 | -0.050354 | 3.3737 | 69.4107 | 68.7653 | 115.8829 | 123.5733 | 3.0533 | 123.5046 | 85.6705 | -0.35248 | 123.5733 | 3.0533 | 85.6705 | 115.8829 | 123.5046 | -123.8754 | -123.9075
4241.7188 | 123.7381 | -61.441 | 62.1323 | -0.23781 | 0.018587 | 0.012986 | 0.014242 | 0.060034 | -0.00054693 | 0.080331 | -58.3923 | 62.2009 | -61.7477 | -61.6653 | 54.4098 | 24.1562 | 8.1345 | 7.2922 | 62.1552 | -61.7661 | -0.3067 | 0.068665 | 3.0487 | -0.2243 | -7.7225 | -0.32501 | 0.022888 | 3.3554 | 69.5755 | 68.7332 | 115.8508 | 123.642 | 3.0487 | 123.5962 | 85.5972 | -0.32501 | 123.642 | 3.0487 | 85.5972 | 115.8508 | 123.5962 | -123.88 | -123.8983
4242.7188 | 123.7518 | -61.441 | 62.1552 | 1.2576 | 0.019656 | 0.013841 | 0.015738 | 0.063025 | 0.00073487 | 0.080331 | -58.2962 | 62.2009 | -61.7661 | -61.6562 | 54.4464 | 24.1699 | 8.0795 | 7.2556 | 62.146 | -61.7706 | -0.32501 | 0.045777 | 3.1448 | -0.21515 | -7.7087 | -0.32959 | -0.009155 | 3.4698 | 69.5206 | 68.6966 | 115.8875 | 123.642 | 3.1448 | 123.587 | 85.611 | -0.32959 | 123.642 | 3.1448 | 85.611 | 115.8875 | 123.587 | -123.9212 | -123.9258
4243.7188 | 123.8434 | -61.4182 | 62.1094 | 0.26573 | 0.016665 | 0.012986 | 0.015524 | 0.06388 | 0.00030767 | 0.077767 | -58.3557 | 62.114 | -61.7569 | -61.5738 | 54.4739 | 24.2569 | 7.9605 | 7.3883 | 62.1002 | -61.734 | -0.33875 | 0.004578 | 3.0624 | -0.15564 | -7.6355 | -0.31586 | -0.009155 | 3.4012 | 69.3787 | 68.8065 | 115.892 | 123.5321 | 3.0624 | 123.5184 | 85.675 | -0.31586 | 123.5321 | 3.0624 | 85.675 | 115.892 | 123.5184 | -123.8663 | -123.8434
4244.7188 | 123.8617 | -61.4227 | 62.1094 | 0.21233 | 0.017733 | 0.013413 | 0.014456 | 0.063239 | -0.0014013 | 0.078622 | -58.3466 | 62.1185 | -61.7569 | -61.5784 | 54.4922 | 24.2752 | 7.9422 | 7.3654 | 62.114 | -61.7477 | -0.33417 | 0.009155 | 3.0762 | -0.15564 | -7.6172 | -0.32501 | 0.004578 | 3.4103 | 69.3649 | 68.7881 | 115.9149 | 123.5413 | 3.0762 | 123.5367 | 85.6979 | -0.32501 | 123.5413 | 3.0762 | 85.6979 | 115.9149 | 123.5367 | -123.8663 | -123.8571
4245.7188 | 123.8251 | -61.4182 | 62.1185 | 0.22758 | 0.017733 | 0.015122 | 0.014242 | 0.061957 | 0.0013757 | 0.079904 | -58.3374 | 62.1277 | -61.7432 | -61.5875 | 54.483 | 24.2386 | 7.9742 | 7.37 | 62.1185 | -61.7294 | -0.32501 | 0.009156 | 3.0808 | -0.16937 | -7.6355 | -0.31128 | 0 | 3.4058 | 69.3924 | 68.7881 | 115.9012 | 123.5458 | 3.0808 | 123.5367 | 85.6567 | -0.31128 | 123.5458 | 3.0808 | 85.6567 | 115.9012 | 123.5367 | -123.8617 | -123.848
4246.7188 | 123.8205 | -61.409 | 62.1048 | 0.22758 | 0.017092 | 0.014482 | 0.014029 | 0.064307 | -0.00033333 | 0.080117 | -58.3557 | 62.1368 | -61.7477 | -61.5921 | 54.483 | 24.353 | 7.9834 | 7.37 | 62.1323 | -61.7523 | -0.33875 | 0.032044 | 3.0533 | -0.1831 | -7.6218 | -0.34332 | 0.027466 | 3.392 | 69.3924 | 68.779 | 115.892 | 123.5458 | 3.0533 | 123.5413 | 85.762 | -0.34332 | 123.5458 | 3.0533 | 85.762 | 115.892 | 123.5413 | -123.8525 | -123.8571
4247.7188 | 123.8205 | -61.4319 | 62.1323 | 0.2047 | 0.016878 | 0.016191 | 0.014669 | 0.062598 | 0.0022303 | 0.078195 | -58.3878 | 62.1368 | -61.7386 | -61.615 | 54.4601 | 24.2798 | 8.0154 | 7.3334 | 62.1277 | -61.7615 | -0.3067 | 0.004578 | 3.0441 | -0.1831 | -7.6721 | -0.32959 | -0.004577 | 3.3508 | 69.4473 | 68.7653 | 115.892 | 123.5687 | 3.0441 | 123.5596 | 85.7117 | -0.32959 | 123.5687 | 3.0441 | 85.7117 | 115.892 | 123.5596 | -123.8708 | -123.8937
4248.7188 | 123.7564 | -61.4548 | 62.146 | 1.1736 | 0.016238 | 0.013413 | 0.012747 | 0.062171 | -0.0011877 | 0.078835 | -58.2962 | 62.1597 | -61.7661 | -61.6699 | 54.3915 | 24.2432 | 8.0887 | 7.2372 | 62.1506 | -61.7844 | -0.31128 | 0.013733 | 3.1586 | -0.21515 | -7.7545 | -0.32959 | 0.004578 | 3.4698 | 69.5435 | 68.692 | 115.8463 | 123.6145 | 3.1586 | 123.6053 | 85.6979 | -0.32959 | 123.6145 | 3.1586 | 85.6979 | 115.8463 | 123.6053 | -123.912 | -123.9304
4249.7188 | 123.8113 | -61.409 | 62.1002 | 0.14366 | 0.015383 | 0.011918 | 0.0071926 | 0.061316 | -0.0011877 | 0.080972 | -58.3557 | 62.0682 | -61.7569 | -61.6013 | 54.5013 | 24.2844 | 7.9697 | 7.3608 | 62.1002 | -61.6837 | -0.3479 | -0.032044 | 3.0533 | -0.19226 | -7.5989 | -0.27466 | 0 | 3.4012 | 69.3787 | 68.7698 | 115.9103 | 123.4772 | 3.0533 | 123.5092 | 85.6934 | -0.27466 | 123.4772 | 3.0533 | 85.6934 | 115.9103 | 123.5092 | -123.8571 | -123.7839
4250.7188 | 123.8709 | -61.409 | 62.1002 | 0.22758 | 0.016878 | 0.015977 | 0.014669 | 0.061103 | 0.0011621 | 0.079049 | -58.342 | 62.1368 | -61.7249 | -61.5875 | 54.5654 | 24.3439 | 7.9559 | 7.3837 | 62.0911 | -61.7523 | -0.31586 | 0.036621 | 3.067 | -0.17853 | -7.5348 | -0.34332 | -0.009156 | 3.3829 | 69.3649 | 68.7927 | 115.9744 | 123.5458 | 3.067 | 123.5001 | 85.7529 | -0.34332 | 123.5458 | 3.067 | 85.7529 | 115.9744 | 123.5001 | -123.8251 | -123.8525
4251.7188 | 123.8388 | -61.4227 | 62.0865 | 0.19707 | 0.017947 | 0.020463 | 0.012747 | 0.062171 | -0.00011953 | 0.078835 | -58.3603 | 62.1277 | -61.7523 | -61.6013 | 54.4785 | 24.3668 | 7.9742 | 7.3425 | 62.114 | -61.7661 | -0.32959 | 0.041199 | 3.0624 | -0.17853 | -7.608 | -0.34332 | 0.027466 | 3.392 | 69.397 | 68.7653 | 115.9012 | 123.5504 | 3.0624 | 123.5367 | 85.7895 | -0.34332 | 123.5504 | 3.0624 | 85.7895 | 115.9012 | 123.5367 | -123.8388 | -123.8525
4252.7188 | 123.7976 | -61.4365 | 62.1231 | 0.18181 | 0.017519 | 0.014909 | 0.015524 | 0.062812 | 0.00094847 | 0.081826 | -58.3832 | 62.178 | -61.7477 | -61.6196 | 54.4739 | 24.3622 | 7.9468 | 7.3242 | 62.114 | -61.7523 | -0.31128 | 0.054932 | 3.0533 | -0.18311 | -7.6492 | -0.31586 | -0.009155 | 3.3646 | 69.3832 | 68.7607 | 115.9103 | 123.6145 | 3.0533 | 123.5504 | 85.7986 | -0.31586 | 123.6145 | 3.0533 | 85.7986 | 115.9103 | 123.5504 | -123.8709 | -123.8754
4253.7188 | 123.8022 | -61.4502 | 62.1552 | 0.18944 | 0.016878 | 0.015122 | 0.01531 | 0.061103 | 0.0030847 | 0.07969 | -58.4015 | 62.1643 | -61.7386 | -61.6287 | 54.4373 | 24.2203 | 8.0154 | 7.2968 | 62.1414 | -61.7569 | -0.28839 | 0.009156 | 3.0487 | -0.17853 | -7.7179 | -0.3067 | -0.013733 | 3.3371 | 69.4656 | 68.7469 | 115.8875 | 123.6145 | 3.0487 | 123.5916 | 85.6705 | -0.3067 | 123.6145 | 3.0487 | 85.6705 | 115.8875 | 123.5916 | -123.8937 | -123.912
4254.7188 | 123.7656 | -61.441 | 62.1185 | 0.16655 | 0.02051 | 0.016831 | 0.015097 | 0.061957 | 0.0015893 | 0.078835 | -58.374 | 62.178 | -61.7432 | -61.6653 | 54.4144 | 24.202 | 8.0154 | 7.2281 | 62.1506 | -61.7798 | -0.30212 | 0.05951 | 3.067 | -0.2243 | -7.7042 | -0.33874 | 0.032044 | 3.3691 | 69.4565 | 68.6691 | 115.8554 | 123.6191 | 3.067 | 123.5916 | 85.643 | -0.33874 | 123.6191 | 3.067 | 85.643 | 115.8554 | 123.5916 | -123.8617 | -123.8983
4255.7188 | 123.5733 | -61.4548 | 62.0956 | 0.097885 | 0.017733 | 0.013413 | 0.017447 | 0.061957 | 0.0015893 | 0.080544 | -58.4015 | 62.2055 | -61.7661 | -61.6745 | 54.4235 | 24.1425 | 8.0566 | 7.2281 | 62.1597 | -61.7798 | -0.31128 | 0.10986 | 3.0533 | -0.21973 | -7.6721 | -0.32501 | 0.064087 | 3.3646 | 69.5114 | 68.6829 | 115.8783 | 123.6603 | 3.0533 | 123.6145 | 85.5972 | -0.32501 | 123.6603 | 3.0533 | 85.5972 | 115.8783 | 123.6145 | -123.8617 | -123.8754
4256.7188 | 123.6969 | -61.441 | 62.1323 | 0.10551 | 0.018374 | 0.018113 | 0.014456 | 0.061743 | 0.00052127 | 0.080331 | -58.3511 | 62.1918 | -61.7386 | -61.6974 | 54.4052 | 24.1608 | 8.107 | 7.2281 | 62.1552 | -61.7706 | -0.29755 | 0.059509 | 3.0899 | -0.25635 | -7.7271 | -0.32959 | 0.022888 | 3.3875 | 69.548 | 68.6691 | 115.8463 | 123.6328 | 3.0899 | 123.5962 | 85.6018 | -0.32959 | 123.6328 | 3.0899 | 85.6018 | 115.8463 | 123.5962 | -123.8708 | -123.9029
4257.7188 | 123.7885 | -61.4365 | 62.1368 | 0.15892 | 0.016024 | 0.01555 | 0.012533 | 0.063666 | 0.0015893 | 0.078622 | -58.3649 | 62.1735 | -61.7569 | -61.6241 | 54.4647 | 24.147 | 8.0109 | 7.2739 | 62.1414 | -61.7844 | -0.32044 | 0.036621 | 3.0716 | -0.18768 | -7.6721 | -0.3479 | 0.004577 | 3.392 | 69.4473 | 68.7103 | 115.9012 | 123.6099 | 3.0716 | 123.5779 | 85.5835 | -0.3479 | 123.6099 | 3.0716 | 85.5835 | 115.9012 | 123.5779 | -123.8937 | -123.9212
4258.7188 | 123.7381 | -61.4319 | 62.1185 | 0.14366 | 0.017306 | 0.015763 | 0.01232 | 0.06388 | 0.0011621 | 0.080972 | -58.3603 | 62.1964 | -61.7294 | -61.647 | 54.3823 | 24.1837 | 8.0658 | 7.2876 | 62.1689 | -61.7661 | -0.29755 | 0.07782 | 3.0716 | -0.21515 | -7.7362 | -0.33417 | 0.050354 | 3.3691 | 69.4977 | 68.7195 | 115.8142 | 123.6282 | 3.0716 | 123.6008 | 85.6155 | -0.33417 | 123.6282 | 3.0716 | 85.6155 | 115.8142 | 123.6008 | -123.848 | -123.8846
4259.7188 | 123.8434 | -61.4136 | 62.1185 | 0.14366 | 0.017306 | 0.0097818 | 0.010183 | 0.063452 | 0.0028711 | 0.081826 | -58.3191 | 62.0819 | -61.734 | -61.5967 | 54.5242 | 24.321 | 7.9102 | 7.3654 | 62.1368 | -61.7249 | -0.32044 | -0.036621 | 3.0945 | -0.18311 | -7.5943 | -0.31128 | 0.018311 | 3.4149 | 69.3237 | 68.779 | 115.9378 | 123.4955 | 3.0945 | 123.5504 | 85.7346 | -0.31128 | 123.4955 | 3.0945 | 85.7346 | 115.9378 | 123.5504 | -123.8525 | -123.8434
4260.7188 | 123.7335 | -61.4319 | 62.1368 | 0.38017 | 0.01581 | 0.012773 | 0.015524 | 0.061743 | -0.00011953 | 0.080117 | -58.3237 | 62.178 | -61.7477 | -61.6837 | 54.4052 | 24.1928 | 8.0841 | 7.2556 | 62.1506 | -61.7798 | -0.31586 | 0.041199 | 3.1082 | -0.25177 | -7.7316 | -0.3479 | 0.013733 | 3.4241 | 69.516 | 68.6874 | 115.8371 | 123.6099 | 3.1082 | 123.5825 | 85.6247 | -0.3479 | 123.6099 | 3.1082 | 85.6247 | 115.8371 | 123.5825 | -123.8846 | -123.9166
4261.7188 | 123.7244 | -61.4548 | 62.146 | 1.4101 | 0.017947 | 0.0095682 | 0.014456 | 0.06388 | 0.0013757 | 0.078622 | -58.1039 | 62.1826 | -61.7432 | -61.615 | 54.4052 | 24.1562 | 8.0841 | 7.2647 | 62.1552 | -61.7523 | -0.28839 | 0.036621 | 3.3508 | -0.16022 | -7.7408 | -0.29755 | 0.009155 | 3.6392 | 69.5389 | 68.7195 | 115.86 | 123.6374 | 3.3508 | 123.6099 | 85.611 | -0.29755 | 123.6374 | 3.3508 | 85.611 | 115.86 | 123.6099 | -123.8892 | -123.8983
4262.7188 | 123.7106 | -61.4227 | 62.1552 | 0.059738 | 0.017733 | 0.012986 | 0.016378 | 0.064521 | 0.0011621 | 0.078408 | -58.3466 | 62.1918 | -61.7203 | -61.6699 | 54.3594 | 24.1928 | 8.1253 | 7.3105 | 62.1414 | -61.7752 | -0.29755 | 0.036621 | 3.0762 | -0.24719 | -7.7957 | -0.35248 | -0.013733 | 3.3737 | 69.548 | 68.7332 | 115.7822 | 123.6145 | 3.0762 | 123.5641 | 85.6155 | -0.35248 | 123.6145 | 3.0762 | 85.6155 | 115.7822 | 123.5641 | -123.8754 | -123.9304
4263.7188 | 123.7518 | -61.4548 | 62.1506 | 0.03685 | 0.016238 | 0.012132 | 0.014456 | 0.062384 | -0.00054693 | 0.079476 | -58.3328 | 62.178 | -61.7569 | -61.6516 | 54.4098 | 24.1333 | 8.1665 | 7.3425 | 62.1918 | -61.7615 | -0.30212 | 0.027466 | 3.1219 | -0.19684 | -7.7408 | -0.3067 | 0.041198 | 3.4241 | 69.6213 | 68.7973 | 115.8646 | 123.6328 | 3.1219 | 123.6465 | 85.5881 | -0.3067 | 123.6328 | 3.1219 | 85.5881 | 115.8646 | 123.6465 | -123.9075 | -123.912
4264.7188 | 123.8434 | -61.409 | 62.1368 | 0.10551 | 0.014315 | 0.0093546 | 0.0054836 | 0.063025 | -0.00097413 | 0.07969 | -58.3145 | 62.0544 | -61.7386 | -61.5738 | 54.4601 | 24.3027 | 7.9651 | 7.4249 | 62.1002 | -61.7111 | -0.32959 | -0.082398 | 3.0945 | -0.16479 | -7.6767 | -0.30212 | -0.036621 | 3.4241 | 69.3741 | 68.8339 | 115.8691 | 123.4634 | 3.0945 | 123.5092 | 85.7117 | -0.30212 | 123.4634 | 3.0945 | 85.7117 | 115.8691 | 123.5092 | -123.8754 | -123.848
4265.7188 | 123.7473 | -61.4548 | 62.1689 | -0.8329 | 0.016024 | 0.012345 | 0.014029 | 0.061743 | 0.0015893 | 0.080972 | -58.4656 | 62.1826 | -61.7432 | -61.6882 | 54.3594 | 24.2386 | 8.0933 | 7.3151 | 62.1368 | -61.7889 | -0.28839 | 0.013733 | 2.9892 | -0.23346 | -7.8094 | -0.33417 | -0.032043 | 3.2776 | 69.548 | 68.7698 | 115.8142 | 123.6374 | 2.9892 | 123.5916 | 85.6934 | -0.33417 | 123.6374 | 2.9892 | 85.6934 | 115.8142 | 123.5916 | -123.912 | -123.9578
4266.7188 | 123.7518 | -61.4731 | 62.1323 | -0.0012969 | 0.016665 | 0.0132 | 0.014883 | 0.064521 | -0.00097413 | 0.080758 | -58.1543 | 62.2101 | -61.7432 | -61.6425 | 54.3365 | 24.0555 | 8.1207 | 7.2922 | 62.1506 | -61.7889 | -0.27008 | 0.07782 | 3.3188 | -0.16937 | -7.7957 | -0.31586 | 0.018311 | 3.5889 | 69.5938 | 68.7653 | 115.8096 | 123.6832 | 3.3188 | 123.6237 | 85.5286 | -0.31586 | 123.6832 | 3.3188 | 85.5286 | 115.8096 | 123.6237 | -123.8754 | -123.9212
4267.7188 | 123.7106 | -61.4594 | 62.1552 | 0.15892 | 0.02051 | 0.016831 | 0.013601 | 0.057471 | 9.4068e-05 | 0.081185 | -58.3511 | 62.1735 | -61.7569 | -61.7111 | 54.4052 | 24.2569 | 8.0566 | 7.2922 | 62.1597 | -61.7981 | -0.29755 | 0.018311 | 3.1082 | -0.25177 | -7.7499 | -0.33875 | 0.004578 | 3.4058 | 69.516 | 68.7515 | 115.8646 | 123.6328 | 3.1082 | 123.6191 | 85.7162 | -0.33875 | 123.6328 | 3.1082 | 85.7162 | 115.8646 | 123.6191 | -123.912 | -123.9532
4268.7188 | 123.7198 | -61.441 | 62.1735 | 0.14366 | 0.019228 | 0.015977 | 0.015951 | 0.062384 | 0.0022303 | 0.077554 | -58.374 | 62.1964 | -61.7661 | -61.8851 | 54.6616 | 24.3484 | 8.0292 | 7.3654 | 62.1414 | -61.7752 | -0.32501 | 0.022888 | 3.067 | -0.44403 | -7.5119 | -0.33417 | -0.032044 | 3.392 | 69.4702 | 68.8065 | 116.1026 | 123.6374 | 3.067 | 123.5825 | 85.7895 | -0.33417 | 123.6374 | 3.067 | 85.7895 | 116.1026 | 123.5825 | -123.9395 | -123.9487
4269.7188 | 123.7335 | -61.4273 | 62.146 | 0.029221 | 0.018587 | 0.012986 | 0.014456 | 0.064948 | -0.0026831 | 0.080972 | -58.3099 | 62.2055 | -61.7523 | -61.6653 | 54.3228 | 24.0005 | 8.1482 | 7.3105 | 62.1918 | -61.7569 | -0.32501 | 0.059509 | 3.1174 | -0.23804 | -7.8232 | -0.32959 | 0.045776 | 3.4424 | 69.5755 | 68.7378 | 115.7501 | 123.6328 | 3.1174 | 123.6191 | 85.4279 | -0.32959 | 123.6328 | 3.1174 | 85.4279 | 115.7501 | 123.6191 | -123.8983 | -123.9029
4270.7188 | 123.7381 | -61.4365 | 62.1506 | 0.067368 | 0.016451 | 0.012559 | 0.015524 | 0.062812 | -0.0016149 | 0.07969 | -58.3099 | 62.1964 | -61.7706 | -61.6425 | 54.3915 | 24.1241 | 8.1894 | 7.3471 | 62.1826 | -61.7706 | -0.33417 | 0.045776 | 3.1265 | -0.20599 | -7.7591 | -0.33417 | 0.032043 | 3.4607 | 69.6259 | 68.7836 | 115.8279 | 123.6328 | 3.1265 | 123.6191 | 85.5606 | -0.33417 | 123.6328 | 3.1265 | 85.5606 | 115.8279 | 123.6191 | -123.9212 | -123.9212
4271.7188 | 123.7518 | -61.441 | 62.1368 | 0.12077 | 0.017733 | 0.014909 | 0.013601 | 0.063025 | -0.00033333 | 0.081613 | -58.3603 | 62.1872 | -61.7661 | -61.6745 | 54.277 | 24.0921 | 8.1665 | 7.338 | 62.1735 | -61.7569 | -0.32501 | 0.050354 | 3.0807 | -0.23346 | -7.8598 | -0.31586 | 0.036621 | 3.4058 | 69.6075 | 68.779 | 115.7181 | 123.6282 | 3.0807 | 123.6145 | 85.5331 | -0.31586 | 123.6282 | 3.0807 | 85.5331 | 115.7181 | 123.6145 | -123.9029 | -123.8937
4272.7188 | 123.7701 | -61.4685 | 62.1323 | 0.34203 | 0.017947 | 0.014695 | 0.012747 | 0.063452 | 0.0020167 | 0.080331 | -58.3557 | 62.1964 | -61.7569 | -61.6745 | 54.2816 | 24.1196 | 8.1665 | 7.3563 | 62.1368 | -61.8027 | -0.28839 | 0.064087 | 3.1128 | -0.20599 | -7.8506 | -0.33417 | 0.004578 | 3.4012 | 69.635 | 68.8248 | 115.7501 | 123.6649 | 3.1128 | 123.6053 | 85.5881 | -0.33417 | 123.6649 | 3.1128 | 85.5881 | 115.7501 | 123.6053 | -123.8892 | -123.9349
4273.7188 | 123.7427 | -61.4502 | 62.1506 | -0.054703 | 0.017519 | 0.015977 | 0.012106 | 0.064734 | 0.0018031 | 0.080544 | -58.3557 | 62.2055 | -61.7477 | -61.6928 | 54.3823 | 24.2249 | 8.1757 | 7.3242 | 62.1964 | -61.7615 | -0.29755 | 0.054931 | 3.0945 | -0.24262 | -7.7683 | -0.31128 | 0.045776 | 3.392 | 69.6259 | 68.7744 | 115.8325 | 123.6557 | 3.0945 | 123.6465 | 85.675 | -0.31128 | 123.6557 | 3.0945 | 85.675 | 115.8325 | 123.6465 | -123.8983 | -123.912
4274.7188 | 123.8846 | -61.3907 | 62.1002 | 0.15129 | 0.01581 | 0.015122 | 0.0089016 | 0.061957 | -0.00076053 | 0.080544 | -58.287 | 62.146 | -61.7523 | -61.5875 | 54.3961 | 24.202 | 8.0246 | 7.4387 | 62.1094 | -61.734 | -0.36163 | 0.045776 | 3.1036 | -0.19684 | -7.7042 | -0.34332 | 0.009155 | 3.4653 | 69.4153 | 68.8293 | 115.7867 | 123.5367 | 3.1036 | 123.5001 | 85.5927 | -0.34332 | 123.5367 | 3.1036 | 85.5927 | 115.7867 | 123.5001 | -123.8525 | -123.8342
4275.7188 | 123.7335 | -61.4594 | 62.1277 | -3.2056 | 0.018587 | 0.017045 | 0.014883 | 0.063666 | -0.00054693 | 0.078195 | -58.3923 | 62.1964 | -61.7615 | -61.6928 | 54.2816 | 24.0738 | 8.1985 | 7.3013 | 62.178 | -61.7798 | -0.30212 | 0.068664 | 3.067 | -0.23346 | -7.8461 | -0.32043 | 0.050354 | 3.3691 | 69.6579 | 68.7607 | 115.741 | 123.6557 | 3.067 | 123.6374 | 85.5331 | -0.32043 | 123.6557 | 3.067 | 85.5331 | 115.741 | 123.6374 | -123.8892 | -123.9075
4276.7188 | 123.7061 | -61.4594 | 62.1597 | 0.097885 | 0.016024 | 0.016191 | 0.015738 | 0.065802 | -0.00097413 | 0.080331 | -58.3328 | 62.1826 | -61.7523 | -61.6699 | 54.2633 | 24.1882 | 8.3084 | 7.3471 | 62.178 | -61.7798 | -0.29297 | 0.022888 | 3.1265 | -0.21057 | -7.8964 | -0.32043 | 0.018311 | 3.4195 | 69.7678 | 68.8065 | 115.7227 | 123.642 | 3.1265 | 123.6374 | 85.6476 | -0.32043 | 123.642 | 3.1265 | 85.6476 | 115.7227 | 123.6374 | -123.912 | -123.9395
4277.7188 | 123.761 | -61.4502 | 62.114 | 0.12077 | 0.016665 | 0.015977 | 0.012106 | 0.061103 | 0.00030767 | 0.077554 | -58.3282 | 62.1643 | -61.7477 | -61.6562 | 54.2953 | 24.1974 | 8.1619 | 7.37 | 62.1597 | -61.7661 | -0.29755 | 0.050354 | 3.1219 | -0.20599 | -7.8186 | -0.31586 | 0.045776 | 3.4195 | 69.6121 | 68.8202 | 115.7455 | 123.6145 | 3.1219 | 123.6099 | 85.6476 | -0.31586 | 123.6145 | 3.1219 | 85.6476 | 115.7455 | 123.6099 | -123.8617 | -123.88
4278.7188 | 123.7518 | -61.4639 | 62.1185 | 0.13603 | 0.019228 | 0.013413 | 0.012747 | 0.064948 | -0.00011953 | 0.080758 | -58.3466 | 62.146 | -61.7477 | -61.6699 | 54.2633 | 24.0967 | 8.1207 | 7.338 | 62.1643 | -61.7752 | -0.28381 | 0.027466 | 3.1174 | -0.20599 | -7.8552 | -0.31128 | 0.045777 | 3.4012 | 69.5847 | 68.8019 | 115.7272 | 123.6099 | 3.1174 | 123.6282 | 85.5606 | -0.31128 | 123.6099 | 3.1174 | 85.5606 | 115.7272 | 123.6282 | -123.8663 | -123.8937
4279.7188 | 123.8571 | -61.409 | 62.1002 | 0.11314 | 0.015383 | 0.015122 | 0.0065518 | 0.061957 | 0.0015893 | 0.080758 | -58.3099 | 62.0865 | -61.7432 | -61.6058 | 54.3869 | 24.2981 | 7.9651 | 7.3929 | 62.1277 | -61.7249 | -0.33417 | -0.013733 | 3.0991 | -0.19684 | -7.7133 | -0.31586 | 0.027466 | 3.4332 | 69.3741 | 68.8019 | 115.7959 | 123.4955 | 3.0991 | 123.5367 | 85.7071 | -0.31586 | 123.4955 | 3.0991 | 85.7071 | 115.7959 | 123.5367 | -123.8434 | -123.8251
4280.7188 | 123.7427 | -61.4456 | 62.1689 | 0.14366 | 0.017092 | 0.013627 | 0.014456 | 0.060462 | 0.00030767 | 0.081185 | -58.3145 | 62.1735 | -61.7477 | -61.6562 | 54.2862 | 24.1013 | 8.1161 | 7.2968 | 62.1597 | -61.7523 | -0.30212 | 0.004578 | 3.1311 | -0.21057 | -7.8827 | -0.3067 | -0.009155 | 3.4332 | 69.5618 | 68.7424 | 115.7318 | 123.6191 | 3.1311 | 123.6053 | 85.5469 | -0.3067 | 123.6191 | 3.1311 | 85.5469 | 115.7318 | 123.6053 | -123.9166 | -123.9212
4281.7188 | 123.7518 | -61.4319 | 62.1368 | 0.2047 | 0.017733 | 0.016404 | 0.013815 | 0.064093 | -0.00076053 | 0.081185 | -58.3694 | 62.1689 | -61.7523 | -61.6791 | 54.3182 | 24.1837 | 8.1161 | 7.3196 | 62.178 | -61.7615 | -0.32043 | 0.032043 | 3.0624 | -0.24719 | -7.8186 | -0.32959 | 0.041199 | 3.3829 | 69.548 | 68.7515 | 115.7501 | 123.6008 | 3.0624 | 123.6099 | 85.6155 | -0.32959 | 123.6008 | 3.0624 | 85.6155 | 115.7501 | 123.6099 | -123.8892 | -123.8983
4282.7188 | 123.7518 | -61.4273 | 62.1368 | 0.029221 | 0.019869 | 0.016831 | 0.013388 | 0.063452 | -0.0014013 | 0.080117 | -58.3603 | 62.1689 | -61.7569 | -61.6562 | 54.3274 | 24.3027 | 8.1299 | 7.3517 | 62.146 | -61.7844 | -0.32959 | 0.032043 | 3.067 | -0.22888 | -7.8094 | -0.35706 | 0.009155 | 3.3966 | 69.5572 | 68.779 | 115.7547 | 123.5962 | 3.067 | 123.5733 | 85.73 | -0.35706 | 123.5962 | 3.067 | 85.73 | 115.7547 | 123.5733 | -123.8937 | -123.9212
4283.7188 | 123.7289 | -61.4365 | 62.1368 | 0.021591 | 0.016665 | 0.014695 | 0.014669 | 0.062598 | -0.00033333 | 0.07969 | -58.3694 | 62.2147 | -61.7523 | -61.7065 | 54.3365 | 24.2981 | 8.139 | 7.283 | 62.1826 | -61.7935 | -0.31586 | 0.07782 | 3.067 | -0.27008 | -7.8003 | -0.35706 | 0.045776 | 3.3829 | 69.5755 | 68.7195 | 115.773 | 123.6511 | 3.067 | 123.6191 | 85.7346 | -0.35706 | 123.6511 | 3.067 | 85.7346 | 115.773 | 123.6191 | -123.8892 | -123.9304
4284.7188 | 123.793 | -61.4136 | 62.114 | 0.2047 | 0.015597 | 0.012773 | 0.0050564 | 0.061957 | -0.00097413 | 0.07969 | -58.3145 | 62.0682 | -61.7569 | -61.6287 | 54.4098 | 24.4766 | 8.0383 | 7.4249 | 62.1277 | -61.702 | -0.34332 | -0.045777 | 3.0991 | -0.21515 | -7.7042 | -0.28839 | 0.013733 | 3.4424 | 69.4519 | 68.8385 | 115.8234 | 123.4818 | 3.0991 | 123.5413 | 85.8902 | -0.28839 | 123.4818 | 3.0991 | 85.8902 | 115.8234 | 123.5413 | -123.8709 | -123.8159
4285.7188 | 123.8068 | -61.4273 | 62.1094 | 0.19707 | 0.01581 | 0.014268 | 0.013601 | 0.061743 | 0.0015893 | 0.080758 | -58.3282 | 62.146 | -61.7294 | -61.6379 | 54.3594 | 24.4125 | 8.0704 | 7.338 | 62.1277 | -61.7569 | -0.30212 | 0.036621 | 3.0991 | -0.21057 | -7.7499 | -0.32959 | 0.018311 | 3.4012 | 69.4977 | 68.7653 | 115.7867 | 123.5733 | 3.0991 | 123.555 | 85.8398 | -0.32959 | 123.5733 | 3.0991 | 85.8398 | 115.7867 | 123.555 | -123.8388 | -123.8663
4286.7188 | 123.7564 | -61.4227 | 62.1185 | 0.18181 | 0.017306 | 0.014695 | 0.01232 | 0.06388 | 0.0015893 | 0.080758 | -58.3282 | 62.1506 | -61.7523 | -61.6562 | 54.332 | 24.4125 | 8.0933 | 7.3517 | 62.1323 | -61.7615 | -0.32959 | 0.032044 | 3.0945 | -0.23346 | -7.7866 | -0.33875 | 0.013733 | 3.4241 | 69.516 | 68.7744 | 115.7547 | 123.5733 | 3.0945 | 123.555 | 85.8353 | -0.33875 | 123.5733 | 3.0945 | 85.8353 | 115.7547 | 123.555 | -123.8708 | -123.88
4287.7188 | 123.7793 | -61.4548 | 62.1414 | 0.18944 | 0.016024 | 0.014268 | 0.015097 | 0.064093 | -0.0011877 | 0.078622 | -58.3374 | 62.1552 | -61.7661 | -61.647 | 54.3915 | 24.321 | 8.0658 | 7.3288 | 62.1414 | -61.7798 | -0.31128 | 0.013733 | 3.1174 | -0.19226 | -7.7499 | -0.32501 | 0 | 3.4287 | 69.5206 | 68.7836 | 115.8463 | 123.6099 | 3.1174 | 123.5962 | 85.7758 | -0.32501 | 123.6099 | 3.1174 | 85.7758 | 115.8463 | 123.5962 | -123.9075 | -123.9212
4288.7188 | 123.7473 | -61.4502 | 62.1368 | 0.074997 | 0.018801 | 0.012559 | 0.014029 | 0.060248 | 0.00030767 | 0.079263 | -58.3603 | 62.1689 | -61.734 | -61.6608 | 54.3823 | 24.3027 | 8.1299 | 7.3517 | 62.1368 | -61.7844 | -0.28381 | 0.032043 | 3.0899 | -0.21057 | -7.7545 | -0.33417 | 0 | 3.3737 | 69.5801 | 68.8019 | 115.8325 | 123.6191 | 3.0899 | 123.587 | 85.7529 | -0.33417 | 123.6191 | 3.0899 | 85.7529 | 115.8325 | 123.587 | -123.8708 | -123.9212
4289.7188 | 123.7427 | -61.441 | 62.1231 | 0.16655 | 0.018587 | 0.012345 | 0.014242 | 0.061957 | -0.00011953 | 0.07969 | -58.3511 | 62.1872 | -61.7569 | -61.6791 | 54.3686 | 24.353 | 8.1436 | 7.3425 | 62.1506 | -61.7661 | -0.31586 | 0.064087 | 3.0899 | -0.23804 | -7.7545 | -0.32501 | 0.027466 | 3.4058 | 69.5847 | 68.7836 | 115.8096 | 123.6282 | 3.0899 | 123.5916 | 85.7941 | -0.32501 | 123.6282 | 3.0899 | 85.7941 | 115.8096 | 123.5916 | -123.88 | -123.8892
4290.7344 | 123.8617 | -61.3541 | 62.1368 | -0.09285 | 0.0098287 | 0.013413 | 0.0071926 | 0.06153 | 0.00073487 | 0.079263 | -58.2962 | 62.0865 | -61.7111 | -61.5509 | 54.4922 | 24.5041 | 8.0338 | 7.5302 | 62.1323 | -61.6699 | -0.35706 | -0.050354 | 3.0579 | -0.19684 | -7.6447 | -0.31586 | -0.004578 | 3.4149 | 69.3878 | 68.8843 | 115.8463 | 123.4406 | 3.0579 | 123.4863 | 85.8582 | -0.31586 | 123.4406 | 3.0579 | 85.8582 | 115.8463 | 123.4863 | -123.848 | -123.8068
4291.7188 | 123.8113 | -61.4502 | 62.114 | 0.18181 | 0.017306 | 0.013627 | 0.015738 | 0.061957 | 0.0013757 | 0.07969 | -58.3374 | 62.1597 | -61.7386 | -61.6241 | 54.3915 | 24.4263 | 7.9788 | 7.3517 | 62.1277 | -61.7569 | -0.28839 | 0.045776 | 3.1128 | -0.17395 | -7.7225 | -0.3067 | 0.013733 | 3.4012 | 69.429 | 68.8019 | 115.8417 | 123.6099 | 3.1128 | 123.5779 | 85.8765 | -0.3067 | 123.6099 | 3.1128 | 85.8765 | 115.8417 | 123.5779 | -123.8525 | -123.8709
4292.7188 | 123.793 | -61.4548 | 62.1368 | 0.25047 | 0.016665 | 0.015763 | 0.015738 | 0.061743 | 0.0011621 | 0.078835 | -58.3511 | 62.1414 | -61.7706 | -61.6287 | 54.4006 | 24.3805 | 8.0063 | 7.3517 | 62.1277 | -61.7569 | -0.31586 | 0.004577 | 3.1036 | -0.17395 | -7.7362 | -0.30212 | -0.009155 | 3.4195 | 69.4611 | 68.8065 | 115.8554 | 123.5962 | 3.1036 | 123.5825 | 85.8353 | -0.30212 | 123.5962 | 3.1036 | 85.8353 | 115.8554 | 123.5825 | -123.9075 | -123.8937
4293.7188 | 123.7518 | -61.4182 | 62.1368 | 0.16655 | 0.01816 | 0.017899 | 0.011679 | 0.063025 | -0.00033333 | 0.080117 | -58.3466 | 62.1552 | -61.734 | -61.6333 | 54.4144 | 24.2889 | 8.0292 | 7.3334 | 62.1597 | -61.7432 | -0.31586 | 0.01831 | 3.0716 | -0.21515 | -7.7225 | -0.32501 | 0.022888 | 3.3875 | 69.4473 | 68.7515 | 115.8325 | 123.5733 | 3.0716 | 123.5779 | 85.7071 | -0.32501 | 123.5733 | 3.0716 | 85.7071 | 115.8325 | 123.5779 | -123.8708 | -123.88
4294.7188 | 123.7976 | -61.4182 | 62.1094 | 0.18181 | 0.013888 | 0.012773 | 0.0076198 | 0.062384 | 0.00052127 | 0.079263 | -58.3237 | 62.0819 | -61.7386 | -61.6241 | 54.4556 | 24.3576 | 7.988 | 7.3975 | 62.1185 | -61.7386 | -0.32043 | -0.027466 | 3.0945 | -0.20599 | -7.6538 | -0.32043 | 0.009155 | 3.4149 | 69.4061 | 68.8156 | 115.8737 | 123.5001 | 3.0945 | 123.5367 | 85.7758 | -0.32043 | 123.5001 | 3.0945 | 85.7758 | 115.8737 | 123.5367 | -123.848 | -123.848
4295.7344 | 123.8663 | -61.3678 | 62.1185 | -0.062332 | 0.013674 | 0.011704 | 0.0074062 | 0.059394 | 0.00052127 | 0.078622 | -58.3557 | 62.1048 | -61.7111 | -61.5646 | 54.5288 | 24.4171 | 8.0475 | 7.4753 | 62.1368 | -61.7111 | -0.34332 | -0.013733 | 3.0121 | -0.19684 | -7.5897 | -0.34332 | 0.018311 | 3.3554 | 69.4153 | 68.8431 | 115.8966 | 123.4726 | 3.0121 | 123.5046 | 85.7849 | -0.34332 | 123.4726 | 3.0121 | 85.7849 | 115.8966 | 123.5046 | -123.8297 | -123.8297
4296.7188 | 123.7747 | -61.4548 | 62.1414 | 0.082626 | 0.016878 | 0.01555 | 0.016378 | 0.061316 | 0.0018031 | 0.080117 | -58.3694 | 62.178 | -61.7432 | -61.6608 | 54.4006 | 24.2935 | 8.1253 | 7.3425 | 62.1323 | -61.7844 | -0.28839 | 0.036622 | 3.0853 | -0.20599 | -7.7408 | -0.32959 | -0.009155 | 3.3737 | 69.5801 | 68.7973 | 115.8554 | 123.6328 | 3.0853 | 123.587 | 85.7483 | -0.32959 | 123.6328 | 3.0853 | 85.7483 | 115.8554 | 123.587 | -123.8846 | -123.9258
4297.7188 | 123.7198 | -61.4227 | 62.178 | 0.19707 | 0.015597 | 0.01854 | 0.016165 | 0.060248 | 0.0024439 | 0.079263 | -58.3923 | 62.1872 | -61.7661 | -61.6562 | 54.3503 | 23.9777 | 8.0887 | 7.6813 | 62.114 | -61.8027 | -0.34332 | 0.009155 | 3.0304 | -0.23346 | -7.8278 | -0.37994 | -0.064087 | 3.3737 | 69.5114 | 69.104 | 115.773 | 123.6099 | 3.0304 | 123.5367 | 85.4004 | -0.37994 | 123.6099 | 3.0304 | 85.4004 | 115.773 | 123.5367 | -123.9441 | -123.9807
4298.7188 | 123.8571 | -61.4319 | 62.1277 | 0.26573 | 0.016024 | 0.012132 | 0.012106 | 0.062812 | 0.00073487 | 0.079476 | -58.3466 | 62.1368 | -61.7294 | -61.5967 | 54.5197 | 24.3668 | 7.9926 | 7.402 | 62.1048 | -61.7569 | -0.29755 | 0.009155 | 3.0853 | -0.16479 | -7.608 | -0.32501 | -0.022889 | 3.3829 | 69.4244 | 68.8339 | 115.9515 | 123.5687 | 3.0853 | 123.5367 | 85.7986 | -0.32501 | 123.5687 | 3.0853 | 85.7986 | 115.9515 | 123.5367 | -123.8571 | -123.8846
4299.7188 | 123.8022 | -61.4136 | 62.1323 | 0.029221 | 0.014956 | 0.0072184 | 0.006979 | 0.059394 | 0.0020167 | 0.079904 | -58.1772 | 62.1185 | -61.7157 | -61.6058 | 54.538 | 24.3805 | 8.075 | 7.4432 | 62.1185 | -61.702 | -0.30212 | -0.013733 | 3.2364 | -0.19226 | -7.5943 | -0.28839 | -0.013733 | 3.5385 | 69.4885 | 68.8568 | 115.9515 | 123.5321 | 3.2364 | 123.5321 | 85.7941 | -0.28839 | 123.5321 | 3.2364 | 85.7941 | 115.9515 | 123.5321 | -123.848 | -123.8342
4300.7344 | 123.8388 | -61.377 | 62.1597 | -0.50484 | 0.013888 | 0.011704 | 0.010824 | 0.060034 | 9.4068e-05 | 0.078622 | -58.5342 | 62.1094 | -61.7111 | -61.5784 | 54.5746 | 24.527 | 8.0475 | 7.5256 | 62.1231 | -61.7065 | -0.33417 | -0.050354 | 2.8427 | -0.20142 | -7.5851 | -0.32959 | -0.036621 | 3.1769 | 69.4244 | 68.9026 | 115.9515 | 123.4863 | 2.8427 | 123.5001 | 85.9039 | -0.32959 | 123.4863 | 2.8427 | 85.9039 | 115.9515 | 123.5001 | -123.8708 | -123.8663
4301.7188 | 123.793 | -61.4182 | 62.114 | 0.22758 | 0.017519 | 0.014054 | 0.017874 | 0.058966 | -0.0020421 | 0.079049 | -58.3511 | 62.1368 | -61.7523 | -61.6287 | 54.4052 | 24.4034 | 8.0017 | 7.3837 | 62.1368 | -61.7615 | -0.33417 | 0.022888 | 3.067 | -0.21057 | -7.7087 | -0.34332 | 0.022888 | 3.4012 | 69.4199 | 68.8019 | 115.8234 | 123.555 | 3.067 | 123.555 | 85.8215 | -0.34332 | 123.555 | 3.067 | 85.8215 | 115.8234 | 123.555 | -123.8663 | -123.8754
4302.7188 | 123.8022 | -61.441 | 62.114 | 0.18944 | 0.016238 | 0.012132 | 0.013174 | 0.06388 | 0.00073487 | 0.077767 | -58.3511 | 62.1689 | -61.7615 | -61.6241 | 54.3961 | 24.2706 | 8.0566 | 7.3746 | 62.1277 | -61.7477 | -0.32043 | 0.054931 | 3.0899 | -0.18311 | -7.7179 | -0.3067 | 0.013733 | 3.4103 | 69.4977 | 68.8156 | 115.8371 | 123.6099 | 3.0899 | 123.5687 | 85.7117 | -0.3067 | 123.6099 | 3.0899 | 85.7117 | 115.8371 | 123.5687 | -123.8754 | -123.8617
4303.7188 | 123.7473 | -61.4227 | 62.146 | 2.7071 | 0.016024 | 0.01085 | 0.013601 | 0.062384 | 0.00073487 | 0.080972 | -58.0994 | 62.1597 | -61.7752 | -61.6287 | 54.451 | 24.3118 | 8.1299 | 7.338 | 62.1506 | -61.7798 | -0.35248 | 0.013733 | 3.3234 | -0.20599 | -7.695 | -0.35706 | 0.004578 | 3.6758 | 69.5526 | 68.7607 | 115.8737 | 123.5825 | 3.3234 | 123.5733 | 85.7346 | -0.35706 | 123.5825 | 3.3234 | 85.7346 | 115.8737 | 123.5733 | -123.9212 | -123.9258
4304.7188 | 123.8297 | -61.4273 | 62.1185 | 0.18181 | 0.013888 | 0.013627 | 0.0084744 | 0.061743 | 0.0013757 | 0.080544 | -58.342 | 62.0728 | -61.7569 | -61.5967 | 54.4739 | 24.4354 | 7.9742 | 7.4203 | 62.1048 | -61.7065 | -0.32959 | -0.045776 | 3.0853 | -0.16937 | -7.6447 | -0.27924 | -0.013733 | 3.4149 | 69.4016 | 68.8477 | 115.9012 | 123.5001 | 3.0853 | 123.5321 | 85.8627 | -0.27924 | 123.5001 | 3.0853 | 85.8627 | 115.9012 | 123.5321 | -123.8754 | -123.8251
4305.7188 | 123.8434 | -61.3998 | 62.0819 | 0.16655 | 0.014956 | 0.014695 | 0.014242 | 0.064734 | -0.0028967 | 0.076699 | -58.3008 | 62.1094 | -61.7203 | -61.5555 | 54.4693 | 24.3393 | 7.9697 | 7.4295 | 62.1368 | -61.734 | -0.32043 | 0.027466 | 3.0991 | -0.15564 | -7.6126 | -0.33417 | 0.054932 | 3.4195 | 69.3695 | 68.8293 | 115.8691 | 123.5092 | 3.0991 | 123.5367 | 85.7391 | -0.33417 | 123.5092 | 3.0991 | 85.7391 | 115.8691 | 123.5367 | -123.8022 | -123.8159
4306.7188 | 123.848 | -61.4227 | 62.114 | 0.22758 | 0.016238 | 0.011704 | 0.016165 | 0.063452 | -0.00097413 | 0.080117 | -58.3237 | 62.1414 | -61.7386 | -61.5967 | 54.4556 | 24.408 | 7.9651 | 7.402 | 62.114 | -61.7432 | -0.31586 | 0.027465 | 3.0991 | -0.17395 | -7.6584 | -0.32044 | 0 | 3.4149 | 69.3878 | 68.8248 | 115.8783 | 123.5641 | 3.0991 | 123.5367 | 85.8307 | -0.32044 | 123.5641 | 3.0991 | 85.8307 | 115.8783 | 123.5367 | -123.8525 | -123.8571
4307.7188 | 123.8159 | -61.3998 | 62.1185 | 0.17418 | 0.016024 | 0.014909 | 0.013174 | 0.061316 | -0.00054693 | 0.079263 | -58.3374 | 62.1185 | -61.7294 | -61.5875 | 54.538 | 24.4034 | 7.8918 | 7.3563 | 62.0819 | -61.7386 | -0.32959 | 0 | 3.0624 | -0.18768 | -7.5806 | -0.33874 | -0.036621 | 3.392 | 69.2917 | 68.7561 | 115.9378 | 123.5184 | 3.0624 | 123.4818 | 85.8032 | -0.33874 | 123.5184 | 3.0624 | 85.8032 | 115.9378 | 123.4818 | -123.848 | -123.8571
4308.7188 | 123.848 | -61.409 | 62.1002 | 0.15129 | 0.016024 | 0.0132 | 0.015524 | 0.060462 | -0.00054693 | 0.079476 | -58.342 | 62.1277 | -61.7477 | -61.5967 | 54.4098 | 24.2157 | 7.9468 | 7.4066 | 62.0911 | -61.7432 | -0.33875 | 0.027466 | 3.067 | -0.18768 | -7.6904 | -0.33417 | -0.009156 | 3.4058 | 69.3558 | 68.8156 | 115.8188 | 123.5367 | 3.067 | 123.5001 | 85.6247 | -0.33417 | 123.5367 | 3.067 | 85.6247 | 115.8188 | 123.5001 | -123.848 | -123.8434
4309.7188 | 123.8205 | -61.4319 | 62.0819 | 0.1284 | 0.016878 | 0.017259 | 0.008688 | 0.06153 | -0.0014013 | 0.080544 | -58.3374 | 62.0819 | -61.7477 | -61.5829 | 54.5059 | 24.3347 | 7.901 | 7.4249 | 62.0773 | -61.6974 | -0.31586 | 0 | 3.0945 | -0.15106 | -7.576 | -0.2655 | -0.004577 | 3.4103 | 69.3329 | 68.8568 | 115.9378 | 123.5138 | 3.0945 | 123.5092 | 85.7666 | -0.2655 | 123.5138 | 3.0945 | 85.7666 | 115.9378 | 123.5092 | -123.8297 | -123.7793
4310.7188 | 123.7518 | -61.4594 | 62.1552 | 0.22758 | 0.018587 | 0.013413 | 0.015951 | 0.060034 | -0.00097413 | 0.078195 | -58.3786 | 62.1735 | -61.7523 | -61.647 | 54.4144 | 24.2661 | 8.0246 | 7.2876 | 62.1277 | -61.734 | -0.29297 | 0.018311 | 3.0807 | -0.18768 | -7.7408 | -0.27466 | -0.027465 | 3.3737 | 69.4839 | 68.7469 | 115.8737 | 123.6328 | 3.0807 | 123.587 | 85.7254 | -0.27466 | 123.6328 | 3.0807 | 85.7254 | 115.8737 | 123.587 | -123.9075 | -123.8892
4311.7188 | 123.7289 | -61.4502 | 62.1414 | 0.14366 | 0.016024 | 0.014054 | 0.015951 | 0.060034 | 0.00030767 | 0.081826 | -58.3649 | 62.1643 | -61.7432 | -61.6653 | 54.4235 | 24.2889 | 8.0338 | 7.3059 | 62.1323 | -61.7752 | -0.29297 | 0.022889 | 3.0853 | -0.21515 | -7.7179 | -0.32501 | -0.009155 | 3.3783 | 69.4839 | 68.7561 | 115.8737 | 123.6145 | 3.0853 | 123.5825 | 85.7391 | -0.32501 | 123.6145 | 3.0853 | 85.7391 | 115.8737 | 123.5825 | -123.8846 | -123.9166
4312.7188 | 123.9075 | -61.4365 | 62.114 | 0.22758 | 0.015383 | 0.017045 | 0.014456 | 0.06153 | 0.0015893 | 0.079049 | -58.3145 | 62.114 | -61.7432 | -61.5601 | 54.5334 | 24.2523 | 7.869 | 7.3471 | 62.0728 | -61.7569 | -0.3067 | 0 | 3.1219 | -0.1236 | -7.5806 | -0.32044 | -0.041199 | 3.4286 | 69.3054 | 68.7836 | 115.9698 | 123.5504 | 3.1219 | 123.5092 | 85.6888 | -0.32044 | 123.5504 | 3.1219 | 85.6888 | 115.9698 | 123.5092 | -123.8571 | -123.8709
4313.7188 | 123.8617 | -61.3953 | 62.0728 | 0.16655 | 0.016238 | 0.013413 | 0.012533 | 0.060675 | 9.4068e-05 | 0.079904 | -58.287 | 62.0956 | -61.7203 | -61.5738 | 54.5425 | 24.3484 | 7.8598 | 7.4249 | 62.0819 | -61.7249 | -0.32501 | 0.022888 | 3.1082 | -0.17853 | -7.5302 | -0.32959 | 0.009155 | 3.4332 | 69.2551 | 68.8202 | 115.9378 | 123.4909 | 3.1082 | 123.4772 | 85.7437 | -0.32959 | 123.4909 | 3.1082 | 85.7437 | 115.9378 | 123.4772 | -123.793 | -123.7976
4314.7188 | 123.8342 | -61.409 | 62.1414 | 0.0063326 | 0.014529 | 0.011918 | 0.006979 | 0.060675 | 0.00052127 | 0.081185 | -58.3603 | 62.0865 | -61.7249 | -61.5784 | 54.483 | 24.2615 | 7.9926 | 7.4432 | 62.1323 | -61.702 | -0.31586 | -0.054931 | 3.0487 | -0.16937 | -7.6584 | -0.29297 | -0.009155 | 3.3646 | 69.4016 | 68.8522 | 115.892 | 123.4955 | 3.0487 | 123.5413 | 85.6705 | -0.29297 | 123.4955 | 3.0487 | 85.6705 | 115.892 | 123.5413 | -123.8663 | -123.8434
4315.7188 | 123.8251 | -61.3953 | 62.1002 | 0.18181 | 0.014315 | 0.010209 | 0.01232 | 0.060675 | 0.00094847 | 0.078835 | -58.2962 | 62.1231 | -61.7249 | -61.5738 | 54.4922 | 24.3851 | 7.8873 | 7.4341 | 62.0819 | -61.734 | -0.32959 | 0.022888 | 3.0991 | -0.17853 | -7.608 | -0.33875 | -0.018311 | 3.4286 | 69.2825 | 68.8293 | 115.8875 | 123.5184 | 3.0991 | 123.4772 | 85.7803 | -0.33875 | 123.5184 | 3.0991 | 85.7803 | 115.8875 | 123.4772 | -123.8251 | -123.8342
4316.7188 | 123.8525 | -61.4182 | 62.1185 | 0.2581 | 0.016238 | 0.011064 | 0.014669 | 0.061316 | 0.0011621 | 0.077981 | -58.3099 | 62.146 | -61.7203 | -61.5738 | 54.4464 | 24.321 | 7.8964 | 7.4432 | 62.0956 | -61.702 | -0.30212 | 0.027466 | 3.1082 | -0.15564 | -7.6721 | -0.28381 | -0.022888 | 3.4103 | 69.3146 | 68.8614 | 115.8646 | 123.5641 | 3.1082 | 123.5138 | 85.7391 | -0.28381 | 123.5641 | 3.1082 | 85.7391 | 115.8646 | 123.5138 | -123.8388 | -123.8205
4317.7188 | 123.7701 | -61.4273 | 62.1414 | 0.14366 | 0.01581 | 0.014909 | 0.018301 | 0.06153 | -0.0011877 | 0.080544 | -58.374 | 62.1689 | -61.7432 | -61.6379 | 54.4144 | 24.1653 | 7.9971 | 7.3196 | 62.1323 | -61.7706 | -0.31586 | 0.027466 | 3.0533 | -0.21057 | -7.727 | -0.34332 | -0.009155 | 3.3691 | 69.4244 | 68.7469 | 115.8417 | 123.5962 | 3.0533 | 123.5596 | 85.5927 | -0.34332 | 123.5962 | 3.0533 | 85.5927 | 115.8417 | 123.5596 | -123.8846 | -123.912
4318.7188 | 123.7427 | -61.4502 | 62.1368 | 0.21233 | 0.01816 | 0.013627 | 0.014883 | 0.063025 | -0.0022559 | 0.077981 | -58.374 | 62.178 | -61.7477 | -61.647 | 54.4281 | 24.1562 | 8.0429 | 7.3288 | 62.1506 | -61.7432 | -0.29755 | 0.041199 | 3.0762 | -0.19684 | -7.7087 | -0.29297 | 0.013733 | 3.3737 | 69.4931 | 68.779 | 115.8783 | 123.6282 | 3.0762 | 123.6008 | 85.6064 | -0.29297 | 123.6282 | 3.0762 | 85.6064 | 115.8783 | 123.6008 | -123.8846 | -123.88
4319.7188 | 123.8663 | -61.4319 | 62.1002 | 0.2047 | 0.014956 | 0.017045 | 0.011465 | 0.062812 | 0.00073487 | 0.07969 | -58.2825 | 62.0865 | -61.7477 | -61.5692 | 54.5425 | 24.2477 | 7.8873 | 7.4341 | 62.0911 | -61.7065 | -0.31586 | -0.013733 | 3.1494 | -0.13733 | -7.5577 | -0.27466 | -0.009156 | 3.4653 | 69.3192 | 68.866 | 115.9744 | 123.5184 | 3.1494 | 123.5229 | 85.6796 | -0.27466 | 123.5184 | 3.1494 | 85.6796 | 115.9744 | 123.5229 | -123.848 | -123.8068
4320.7188 | 123.8709 | -61.4136 | 62.0956 | 0.16655 | 0.01581 | 0.013841 | 0.011679 | 0.064093 | 9.4068e-05 | 0.081185 | -58.3008 | 62.114 | -61.7386 | -61.5463 | 54.5242 | 24.3118 | 7.901 | 7.4295 | 62.0911 | -61.7249 | -0.32501 | 0.018311 | 3.1128 | -0.13275 | -7.5714 | -0.31128 | -0.004578 | 3.4378 | 69.3146 | 68.8431 | 115.9378 | 123.5275 | 3.1128 | 123.5046 | 85.7254 | -0.31128 | 123.5275 | 3.1128 | 85.7254 | 115.9378 | 123.5046 | -123.8342 | -123.8205
4321.7188 | 123.8159 | -61.4182 | 62.0911 | 0.11314 | 0.01581 | 0.016404 | 0.014242 | 0.063452 | 0.00094847 | 0.078408 | -58.3054 | 62.1185 | -61.7203 | -61.5555 | 54.5013 | 24.3256 | 7.9285 | 7.4524 | 62.0865 | -61.7249 | -0.30212 | 0.027466 | 3.1128 | -0.13733 | -7.5897 | -0.3067 | -0.004577 | 3.4149 | 69.3466 | 68.8705 | 115.9195 | 123.5367 | 3.1128 | 123.5046 | 85.7437 | -0.3067 | 123.5367 | 3.1128 | 85.7437 | 115.9195 | 123.5046 | -123.8113 | -123.8159
4322.7188 | 123.8251 | -61.409 | 62.1231 | 0.2047 | 0.016878 | 0.012773 | 0.011892 | 0.060889 | 0.0020167 | 0.08204 | -58.3282 | 62.1368 | -61.7294 | -61.5738 | 54.4601 | 24.3301 | 7.9193 | 7.4615 | 62.0773 | -61.7523 | -0.32043 | 0.013733 | 3.0808 | -0.16479 | -7.663 | -0.34332 | -0.045776 | 3.4012 | 69.3283 | 68.8705 | 115.8691 | 123.5458 | 3.0808 | 123.4863 | 85.7391 | -0.34332 | 123.5458 | 3.0808 | 85.7391 | 115.8691 | 123.4863 | -123.8525 | -123.8754
4323.7188 | 123.8617 | -61.4182 | 62.1231 | 0.15892 | 0.016238 | 0.014695 | 0.015524 | 0.060889 | 0.00052127 | 0.079263 | -58.3328 | 62.1506 | -61.7752 | -61.6013 | 54.4281 | 24.2203 | 7.9422 | 7.4203 | 62.1231 | -61.7569 | -0.35706 | 0.027466 | 3.0853 | -0.1831 | -7.695 | -0.33875 | 0 | 3.4424 | 69.3604 | 68.8385 | 115.8463 | 123.5687 | 3.0853 | 123.5413 | 85.6384 | -0.33875 | 123.5687 | 3.0853 | 85.6384 | 115.8463 | 123.5413 | -123.8983 | -123.88
4324.7188 | 123.7564 | -61.3495 | 62.1918 | -0.11574 | 0.01346 | 0.010423 | 0.0078336 | 0.05918 | 9.4068e-05 | 0.07969 | -58.2687 | 62.0865 | -61.702 | -61.5097 | 54.5563 | 24.2889 | 7.9971 | 7.5439 | 62.114 | -61.6837 | -0.35248 | -0.10529 | 3.0807 | -0.16022 | -7.6355 | -0.33417 | -0.077819 | 3.4332 | 69.3466 | 68.8934 | 115.9058 | 123.436 | 3.0807 | 123.4634 | 85.6384 | -0.33417 | 123.436 | 3.0807 | 85.6384 | 115.9058 | 123.4634 | -123.8937 | -123.8754
4325.7188 | 123.7061 | -61.4227 | 62.1597 | 0.1284 | 0.016024 | 0.011277 | 0.017447 | 0.062812 | 0.00073487 | 0.07734 | -58.4885 | 62.1506 | -61.7661 | -61.6104 | 54.3137 | 24.0738 | 8.139 | 7.3196 | 62.1643 | -61.7798 | -0.34332 | -0.009155 | 2.9343 | -0.18768 | -7.8461 | -0.35706 | 0.004578 | 3.2776 | 69.5618 | 68.7424 | 115.7364 | 123.5733 | 2.9343 | 123.587 | 85.4965 | -0.35706 | 123.5733 | 2.9343 | 85.4965 | 115.7364 | 123.587 | -123.9258 | -123.9395
4326.7188 | 123.8617 | -61.4044 | 62.1185 | 0.25047 | 0.015383 | 0.015763 | 0.014242 | 0.064093 | 0.00094847 | 0.07969 | -58.3054 | 62.1414 | -61.7294 | -61.6104 | 54.451 | 24.2844 | 7.9102 | 7.4203 | 62.1185 | -61.7111 | -0.32501 | 0.022888 | 3.0991 | -0.20599 | -7.6675 | -0.3067 | 0 | 3.4241 | 69.3146 | 68.8248 | 115.8554 | 123.5458 | 3.0991 | 123.5229 | 85.6888 | -0.3067 | 123.5458 | 3.0991 | 85.6888 | 115.8554 | 123.5229 | -123.848 | -123.8297
4327.7188 | 123.8159 | -61.4136 | 62.1002 | 0.17418 | 0.016878 | 0.011704 | 0.014029 | 0.063666 | -0.00011953 | 0.078195 | -58.3374 | 62.1414 | -61.7294 | -61.5967 | 54.4556 | 24.2203 | 7.9239 | 7.4249 | 62.0956 | -61.7249 | -0.31586 | 0.041198 | 3.0762 | -0.18311 | -7.6447 | -0.31128 | -0.004578 | 3.392 | 69.3375 | 68.8385 | 115.8691 | 123.555 | 3.0762 | 123.5092 | 85.6338 | -0.31128 | 123.555 | 3.0762 | 85.6338 | 115.8691 | 123.5092 | -123.8297 | -123.8251
4328.7188 | 123.8251 | -61.4044 | 62.1048 | 0.17418 | 0.017519 | 0.016618 | 0.014242 | 0.061743 | -0.00097413 | 0.07969 | -58.3374 | 62.146 | -61.7386 | -61.6241 | 54.4739 | 24.2935 | 7.9742 | 7.4203 | 62.1048 | -61.7523 | -0.33417 | 0.041199 | 3.067 | -0.21973 | -7.6309 | -0.3479 | 0 | 3.4012 | 69.3787 | 68.8248 | 115.8783 | 123.5504 | 3.067 | 123.5092 | 85.6979 | -0.3479 | 123.5504 | 3.067 | 85.6979 | 115.8783 | 123.5092 | -123.8434 | -123.8571
4329.7188 | 123.7976 | -61.3724 | 62.2101 | -0.16914 | 0.012179 | 0.012345 | 0.005911 | 0.063239 | 0.0026575 | 0.080544 | -58.2825 | 62.0773 | -61.7065 | -61.5097 | 54.6066 | 24.3393 | 7.9742 | 7.5623 | 62.1414 | -61.6608 | -0.33417 | -0.13275 | 3.0899 | -0.13733 | -7.6035 | -0.28839 | -0.068665 | 3.4241 | 69.3466 | 68.9346 | 115.979 | 123.4497 | 3.0899 | 123.5138 | 85.7117 | -0.28839 | 123.4497 | 3.0899 | 85.7117 | 115.979 | 123.5138 | -123.9166 | -123.8708
4330.7188 | 123.7701 | -61.4365 | 62.146 | 0.16655 | 0.014742 | 0.014909 | 0.016378 | 0.061316 | 9.4068e-05 | 0.078835 | -58.3557 | 62.1735 | -61.7294 | -61.6241 | 54.4373 | 24.2981 | 7.9605 | 7.338 | 62.1414 | -61.7386 | -0.29297 | 0.027466 | 3.0807 | -0.18768 | -7.7087 | -0.30212 | -0.004578 | 3.3737 | 69.397 | 68.7744 | 115.8737 | 123.6099 | 3.0807 | 123.5779 | 85.7346 | -0.30212 | 123.6099 | 3.0807 | 85.7346 | 115.8737 | 123.5779 | -123.8754 | -123.8846
4331.7188 | 123.7106 | -61.4594 | 62.1506 | 0.19707 | 0.016878 | 0.016618 | 0.016592 | 0.058325 | 0.0011621 | 0.078835 | -58.3878 | 62.178 | -61.7661 | -61.7065 | 54.5013 | 24.3027 | 7.9926 | 7.3288 | 62.1597 | -61.7661 | -0.3067 | 0.027466 | 3.0716 | -0.24719 | -7.6492 | -0.3067 | 0.009155 | 3.3783 | 69.4519 | 68.7881 | 115.9607 | 123.6374 | 3.0716 | 123.6191 | 85.762 | -0.3067 | 123.6374 | 3.0716 | 85.762 | 115.9607 | 123.6191 | -123.9166 | -123.9166
4332.7188 | 123.7335 | -61.4502 | 62.1643 | 0.13603 | 0.016451 | 0.014909 | 0.018301 | 0.062171 | 0.00052127 | 0.079904 | -58.4015 | 62.1826 | -61.7615 | -61.9904 | 54.1351 | 24.2935 | 8.2123 | 7.2327 | 62.146 | -61.7432 | -0.31128 | 0.01831 | 3.0487 | -0.54016 | -8.0292 | -0.29297 | -0.018311 | 3.36 | 69.6625 | 68.6829 | 115.5853 | 123.6328 | 3.0487 | 123.5962 | 85.7437 | -0.29297 | 123.6328 | 3.0487 | 85.7437 | 115.5853 | 123.5962 | -123.9258 | -123.9075
4333.7188 | 123.8251 | -61.3953 | 62.114 | 0.18944 | 0.017519 | 0.015122 | 0.013174 | 0.063666 | -0.00097413 | 0.080331 | -58.3511 | 62.1323 | -61.7386 | -61.5921 | 54.5288 | 24.234 | 7.8873 | 7.4158 | 62.1231 | -61.7294 | -0.34332 | 0.01831 | 3.0441 | -0.19684 | -7.5851 | -0.33417 | 0.009155 | 3.3875 | 69.2825 | 68.811 | 115.9241 | 123.5275 | 3.0441 | 123.5184 | 85.6293 | -0.33417 | 123.5275 | 3.0441 | 85.6293 | 115.9241 | 123.5184 | -123.8525 | -123.8434
4334.7188 | 123.8113 | -61.4136 | 62.114 | 0.15129 | 0.014956 | 0.016831 | 0.014029 | 0.062171 | 0.00073487 | 0.079904 | -58.3282 | 62.1506 | -61.7249 | -61.5921 | 54.5151 | 24.234 | 7.9285 | 7.3792 | 62.1185 | -61.7477 | -0.31128 | 0.036621 | 3.0853 | -0.17853 | -7.5989 | -0.33417 | 0.004577 | 3.3966 | 69.342 | 68.7927 | 115.9287 | 123.5641 | 3.0853 | 123.5321 | 85.6476 | -0.33417 | 123.5641 | 3.0853 | 85.6476 | 115.9287 | 123.5321 | -123.8388 | -123.8617
4335.7188 | 123.8068 | -61.4227 | 62.1185 | 0.23521 | 0.014529 | 0.0099954 | 0.01232 | 0.063452 | -0.0022559 | 0.080331 | -58.3328 | 62.1506 | -61.7294 | -61.615 | 54.5242 | 24.2569 | 7.9239 | 7.4295 | 62.1094 | -61.7523 | -0.3067 | 0.032044 | 3.0899 | -0.19226 | -7.5943 | -0.32959 | -0.009155 | 3.3966 | 69.3466 | 68.8522 | 115.947 | 123.5733 | 3.0899 | 123.5321 | 85.6796 | -0.32959 | 123.5733 | 3.0899 | 85.6796 | 115.947 | 123.5321 | -123.848 | -123.8708
4336.7188 | 123.8434 | -61.4136 | 62.1185 | 0.25047 | 0.016024 | 0.017686 | 0.013388 | 0.063452 | 0.00094847 | 0.078195 | -58.3328 | 62.1277 | -61.7523 | -61.615 | 54.483 | 24.2935 | 7.9056 | 7.3929 | 62.1277 | -61.7844 | -0.33875 | 0.009156 | 3.0807 | -0.20142 | -7.6355 | -0.37079 | 0.009156 | 3.4195 | 69.3192 | 68.8065 | 115.8966 | 123.5413 | 3.0807 | 123.5413 | 85.7071 | -0.37079 | 123.5413 | 3.0807 | 85.7071 | 115.8966 | 123.5413 | -123.8708 | -123.9029
4337.7188 | 123.7885 | -61.4273 | 62.1048 | 0.17418 | 0.01581 | 0.012559 | 0.014669 | 0.06153 | 0.0013757 | 0.081613 | -58.3374 | 62.1414 | -61.7203 | -61.6104 | 54.3961 | 24.1653 | 7.9056 | 7.3563 | 62.1277 | -61.7844 | -0.29297 | 0.036621 | 3.0899 | -0.18311 | -7.7087 | -0.35706 | 0.022889 | 3.3829 | 69.3329 | 68.7836 | 115.8234 | 123.5687 | 3.0899 | 123.555 | 85.5927 | -0.35706 | 123.5687 | 3.0899 | 85.5927 | 115.8234 | 123.555 | -123.8251 | -123.8892
4338.7188 | 123.7381 | -61.4594 | 62.1506 | 0.54802 | 0.01816 | 0.013841 | 0.013815 | 0.064093 | 0.00030767 | 0.079049 | -58.3282 | 62.1689 | -61.7523 | -61.6791 | 54.364 | 24.2249 | 8.0429 | 7.3425 | 62.1323 | -61.7615 | -0.29297 | 0.01831 | 3.1311 | -0.21973 | -7.7866 | -0.30212 | -0.018311 | 3.4241 | 69.5023 | 68.8019 | 115.8234 | 123.6282 | 3.1311 | 123.5916 | 85.6842 | -0.30212 | 123.6282 | 3.1311 | 85.6842 | 115.8234 | 123.5916 | -123.9029 | -123.912
4339.7188 | 123.8434 | -61.4044 | 62.1048 | 0.21233 | 0.01346 | 0.014909 | 0.010611 | 0.062171 | -0.00076053 | 0.078835 | -58.2779 | 62.0682 | -61.734 | -61.5829 | 54.4693 | 24.3713 | 7.869 | 7.4341 | 62.1002 | -61.7157 | -0.32959 | -0.036621 | 3.1265 | -0.17853 | -7.6355 | -0.31128 | -0.004577 | 3.4561 | 69.2734 | 68.8385 | 115.8737 | 123.4726 | 3.1265 | 123.5046 | 85.7758 | -0.31128 | 123.4726 | 3.1265 | 85.7758 | 115.8737 | 123.5046 | -123.8388 | -123.8205
4340.7188 | 123.8297 | -61.4044 | 62.0956 | 0.22758 | 0.012606 | 0.014268 | 0.012106 | 0.063025 | 0.00094847 | 0.080544 | -58.287 | 62.1048 | -61.7386 | -61.5601 | 54.4464 | 24.4263 | 7.869 | 7.4432 | 62.1002 | -61.7249 | -0.33417 | 0.009155 | 3.1174 | -0.15564 | -7.6492 | -0.32044 | 0.004578 | 3.4515 | 69.2734 | 68.8477 | 115.8508 | 123.5092 | 3.1174 | 123.5046 | 85.8307 | -0.32044 | 123.5092 | 3.1174 | 85.8307 | 115.8508 | 123.5046 | -123.8342 | -123.8205
4341.7188 | 123.8571 | -61.3953 | 62.1002 | 0.15129 | 0.017092 | 0.017259 | 0.01531 | 0.063239 | 0.00073487 | 0.082894 | -58.2962 | 62.1048 | -61.7111 | -61.5692 | 54.4556 | 24.234 | 7.8552 | 7.457 | 62.0956 | -61.7249 | -0.31586 | 0.004577 | 3.0991 | -0.17395 | -7.6447 | -0.32959 | -0.004578 | 3.4149 | 69.2505 | 68.8522 | 115.8508 | 123.5001 | 3.0991 | 123.4909 | 85.6293 | -0.32959 | 123.5001 | 3.0991 | 85.6293 | 115.8508 | 123.4909 | -123.8113 | -123.8251
4342.7188 | 123.8525 | -61.3953 | 62.1231 | 0.074997 | 0.017519 | 0.013627 | 0.01296 | 0.062598 | 0.0011621 | 0.080972 | -58.3328 | 62.1277 | -61.7523 | -61.5829 | 54.4098 | 24.1882 | 7.8415 | 7.4432 | 62.0865 | -61.7203 | -0.35706 | 0.004578 | 3.0624 | -0.18768 | -7.7133 | -0.32501 | -0.036621 | 3.4195 | 69.2368 | 68.8385 | 115.8051 | 123.5229 | 3.0624 | 123.4818 | 85.5835 | -0.32501 | 123.5229 | 3.0624 | 85.5835 | 115.8051 | 123.4818 | -123.8754 | -123.8434
4343.7188 | 123.8297 | -61.3953 | 62.1231 | 0.18944 | 0.016878 | 0.012773 | 0.012747 | 0.06153 | 0.00030767 | 0.080972 | -58.287 | 62.1506 | -61.734 | -61.5555 | 54.4739 | 24.1974 | 7.8735 | 7.4478 | 62.1048 | -61.7294 | -0.33875 | 0.027466 | 3.1082 | -0.16022 | -7.6492 | -0.33417 | -0.018311 | 3.447 | 69.2688 | 68.8431 | 115.8691 | 123.5458 | 3.1082 | 123.5001 | 85.5927 | -0.33417 | 123.5458 | 3.1082 | 85.5927 | 115.8691 | 123.5001 | -123.8571 | -123.8525
4344.7188 | 123.7976 | -61.4182 | 62.1368 | 0.059738 | 0.013888 | 0.013627 | 0.0056972 | 0.06153 | 0.0013757 | 0.078835 | -58.3511 | 62.0956 | -61.7203 | -61.6058 | 54.4601 | 24.1425 | 7.9514 | 7.4478 | 62.1231 | -61.7157 | -0.30212 | -0.041199 | 3.067 | -0.18768 | -7.6767 | -0.29755 | -0.013733 | 3.3691 | 69.3695 | 68.866 | 115.8783 | 123.5138 | 3.067 | 123.5413 | 85.5606 | -0.29755 | 123.5138 | 3.067 | 85.5606 | 115.8783 | 123.5413 | -123.8571 | -123.8525
4345.7188 | 123.7564 | -61.4365 | 62.1414 | 0.090256 | 0.018801 | 0.010636 | 0.015738 | 0.060248 | 9.4068e-05 | 0.079263 | -58.3603 | 62.1735 | -61.7569 | -61.6516 | 54.3823 | 24.0921 | 7.9376 | 7.3471 | 62.1277 | -61.7798 | -0.32044 | 0.032044 | 3.0762 | -0.21515 | -7.7591 | -0.34332 | -0.013732 | 3.3966 | 69.3741 | 68.7836 | 115.8188 | 123.6099 | 3.0762 | 123.5641 | 85.5286 | -0.34332 | 123.6099 | 3.0762 | 85.5286 | 115.8188 | 123.5641 | -123.8983 | -123.9212
4346.7188 | 123.7518 | -61.4365 | 62.1231 | 0.12077 | 0.016451 | 0.014268 | 0.015524 | 0.063025 | 0.0013757 | 0.079049 | -58.3374 | 62.1597 | -61.7477 | -61.647 | 54.3686 | 24.0784 | 7.9742 | 7.3471 | 62.1506 | -61.7615 | -0.31128 | 0.036621 | 3.0991 | -0.21057 | -7.7545 | -0.32501 | 0.027466 | 3.4103 | 69.4107 | 68.7836 | 115.8051 | 123.5962 | 3.0991 | 123.587 | 85.5148 | -0.32501 | 123.5962 | 3.0991 | 85.5148 | 115.8051 | 123.587 | -123.8709 | -123.8846
4347.7188 | 123.88 | -61.441 | 62.1277 | 0.15129 | 0.016238 | 0.015763 | 0.014456 | 0.064948 | -0.0011877 | 0.078622 | -58.2779 | 62.1048 | -61.7157 | -61.4594 | 54.4785 | 24.202 | 7.9193 | 7.457 | 62.114 | -61.7157 | -0.27466 | -0.022889 | 3.1631 | -0.018311 | -7.6492 | -0.27466 | -0.013733 | 3.4378 | 69.3604 | 68.898 | 115.9195 | 123.5458 | 3.1631 | 123.555 | 85.643 | -0.27466 | 123.5458 | 3.1631 | 85.643 | 115.9195 | 123.555 | -123.8434 | -123.8434
4348.7188 | 123.8342 | -61.3998 | 62.1094 | 0.18181 | 0.017092 | 0.014695 | 0.012747 | 0.060248 | -0.0011877 | 0.078622 | -58.2779 | 62.1002 | -61.7203 | -61.6379 | 54.689 | 24.4217 | 7.7957 | 7.5073 | 62.1048 | -61.6882 | -0.32043 | -0.009155 | 3.1219 | -0.23804 | -7.4203 | -0.28839 | -0.004578 | 3.4424 | 69.1956 | 68.9072 | 116.0889 | 123.5001 | 3.1219 | 123.5046 | 85.8215 | -0.28839 | 123.5001 | 3.1219 | 85.8215 | 116.0889 | 123.5046 | -123.8297 | -123.7976
4349.7188 | 123.8205 | -61.4136 | 62.1506 | -0.047073 | 0.013033 | 0.011918 | 0.0074062 | 0.059394 | -0.00054693 | 0.08204 | -58.3374 | 62.0728 | -61.7157 | -61.5601 | 54.5288 | 24.2752 | 7.9193 | 7.5073 | 62.1231 | -61.6928 | -0.30212 | -0.07782 | 3.0762 | -0.14649 | -7.6218 | -0.27924 | -0.027466 | 3.3783 | 69.3329 | 68.9209 | 115.9424 | 123.4863 | 3.0762 | 123.5367 | 85.6888 | -0.27924 | 123.4863 | 3.0762 | 85.6888 | 115.9424 | 123.5367 | -123.8663 | -123.8434
4350.7188 | 123.9212 | -61.3998 | 62.1048 | 0.22758 | 0.017306 | 0.013627 | 0.014669 | 0.058325 | -0.0014013 | 0.079263 | -58.2504 | 62.0956 | -61.6837 | -61.5601 | 54.5242 | 24.1745 | 7.7133 | 7.2327 | 62.059 | -61.7615 | -0.28381 | -0.009155 | 3.1494 | -0.16022 | -7.5806 | -0.36163 | -0.045776 | 3.4332 | 69.1132 | 68.6325 | 115.9241 | 123.4955 | 3.1494 | 123.4589 | 85.5743 | -0.36163 | 123.4955 | 3.1494 | 85.5743 | 115.9241 | 123.4589 | -123.7885 | -123.8663
4351.7188 | 123.7885 | -61.4319 | 62.0773 | 0.15892 | 0.014742 | 0.015977 | 0.012533 | 0.061103 | -0.0011877 | 0.079904 | -58.2413 | 62.1185 | -61.702 | -61.5646 | 54.5197 | 24.2798 | 7.8232 | 7.4707 | 62.1002 | -61.734 | -0.27008 | 0.041198 | 3.1906 | -0.13275 | -7.5577 | -0.30212 | 0.022888 | 3.4607 | 69.2551 | 68.9026 | 115.9515 | 123.5504 | 3.1906 | 123.5321 | 85.7117 | -0.30212 | 123.5504 | 3.1906 | 85.7117 | 115.9515 | 123.5321 | -123.7793 | -123.8113
4352.7188 | 123.793 | -61.4365 | 62.0911 | 0.18944 | 0.016451 | 0.011277 | 0.014242 | 0.059607 | -0.00011953 | 0.080972 | -58.3237 | 62.1506 | -61.7523 | -61.6333 | 54.451 | 24.1241 | 7.9239 | 7.4753 | 62.1277 | -61.7615 | -0.31586 | 0.05951 | 3.1128 | -0.19684 | -7.6401 | -0.32501 | 0.036622 | 3.4286 | 69.3604 | 68.9117 | 115.8875 | 123.587 | 3.1128 | 123.5641 | 85.5606 | -0.32501 | 123.587 | 3.1128 | 85.5606 | 115.8875 | 123.5641 | -123.8434 | -123.8525
4353.7188 | 123.7564 | -61.4182 | 62.1368 | 0.15129 | 0.017306 | 0.0099954 | 0.016378 | 0.062598 | 0.0011621 | 0.078622 | -58.3008 | 62.1323 | -61.7615 | -61.615 | 54.4647 | 24.1196 | 7.9193 | 7.3792 | 62.1277 | -61.7615 | -0.34332 | -0.004578 | 3.1174 | -0.19684 | -7.6721 | -0.34332 | -0.009155 | 3.4607 | 69.3375 | 68.7973 | 115.8829 | 123.5504 | 3.1174 | 123.5458 | 85.5377 | -0.34332 | 123.5504 | 3.1174 | 85.5377 | 115.8829 | 123.5458 | -123.8983 | -123.8983
4354.7188 | 123.8251 | -61.4182 | 62.1231 | 0.029221 | 0.013247 | 0.013627 | 0.0076198 | 0.06153 | 0.00052127 | 0.079904 | -58.2916 | 62.0819 | -61.734 | -61.5967 | 54.5517 | 24.3851 | 8.0246 | 7.5302 | 62.0956 | -61.6974 | -0.31586 | -0.041199 | 3.1265 | -0.17853 | -7.5714 | -0.27924 | -0.027466 | 3.4424 | 69.4427 | 68.9484 | 115.9698 | 123.5001 | 3.1265 | 123.5138 | 85.8032 | -0.27924 | 123.5001 | 3.1265 | 85.8032 | 115.9698 | 123.5138 | -123.8571 | -123.8205
4355.7188 | 123.8342 | -61.3678 | 62.1048 | -1.573 | 0.01581 | 0.016404 | 0.01296 | 0.060034 | -0.0011877 | 0.077767 | -58.2962 | 62.1002 | -61.6928 | -61.5692 | 54.5563 | 24.2798 | 7.5027 | 7.402 | 62.0728 | -61.6974 | -0.32501 | -0.004577 | 3.0716 | -0.20142 | -7.5485 | -0.32959 | -0.032043 | 3.3966 | 68.8705 | 68.7698 | 115.9241 | 123.468 | 3.0716 | 123.4406 | 85.6476 | -0.32959 | 123.468 | 3.0716 | 85.6476 | 115.9241 | 123.4406 | -123.7976 | -123.8022
4356.7188 | 123.8617 | -61.4136 | 62.1094 | 0.21996 | 0.016665 | 0.014695 | 0.01531 | 0.061957 | 0.0015893 | 0.080117 | -58.4152 | 62.0773 | -61.7432 | -61.5463 | 54.5471 | 24.2706 | 7.5348 | 7.3654 | 62.0728 | -61.7157 | -0.32959 | -0.032043 | 2.9984 | -0.13275 | -7.5623 | -0.30212 | -0.036621 | 3.3279 | 68.9484 | 68.779 | 115.9607 | 123.4909 | 2.9984 | 123.4863 | 85.6842 | -0.30212 | 123.4909 | 2.9984 | 85.6842 | 115.9607 | 123.4863 | -123.8525 | -123.8251
4357.7188 | 123.8525 | -61.3678 | 62.1231 | 0.18181 | 0.016665 | 0.013841 | 0.014029 | 0.06153 | 0.00052127 | 0.076913 | -58.2504 | 62.1185 | -61.7157 | -61.4136 | 54.7028 | 24.472 | 7.4615 | 7.3929 | 62.0956 | -61.7157 | -0.3479 | -0.004578 | 3.1174 | -0.045776 | -7.4203 | -0.3479 | -0.027466 | 3.4653 | 68.8293 | 68.7607 | 116.0706 | 123.4863 | 3.1174 | 123.4634 | 85.8398 | -0.3479 | 123.4863 | 3.1174 | 85.8398 | 116.0706 | 123.4634 | -123.8388 | -123.8388
4358.7188 | 123.8297 | -61.3724 | 62.1277 | 0.17418 | 0.014956 | 0.016404 | 0.013174 | 0.061316 | 0.00030767 | 0.080758 | -58.2458 | 62.0956 | -61.7249 | -61.5646 | 54.5151 | 24.1974 | 7.6721 | 7.5439 | 62.0865 | -61.7294 | -0.35248 | -0.032044 | 3.1265 | -0.19226 | -7.6126 | -0.35706 | -0.041199 | 3.479 | 69.0445 | 68.9163 | 115.8875 | 123.468 | 3.1265 | 123.4589 | 85.5698 | -0.35706 | 123.468 | 3.1265 | 85.5698 | 115.8875 | 123.4589 | -123.8525 | -123.8571
4359.7188 | 123.8113 | -61.4273 | 62.1094 | 0.059738 | 0.011751 | 0.0132 | 0.0071926 | 0.058539 | -0.0022559 | 0.08204 | -58.3374 | 62.0819 | -61.7569 | -61.5097 | 54.4373 | 24.3118 | 7.8873 | 7.4661 | 62.1094 | -61.6928 | -0.32959 | -0.027466 | 3.0899 | -0.082398 | -7.6721 | -0.2655 | 0 | 3.4195 | 69.3146 | 68.8934 | 115.8646 | 123.5092 | 3.0899 | 123.5367 | 85.7391 | -0.2655 | 123.5092 | 3.0899 | 85.7391 | 115.8646 | 123.5367 | -123.8663 | -123.8022
4360.7188 | 123.8617 | -61.4044 | 62.1094 | 0.18181 | 0.014529 | 0.015122 | 0.013815 | 0.060034 | -0.00033333 | 0.080544 | -58.2504 | 62.0956 | -61.7203 | -61.5463 | 54.6249 | 24.4537 | 7.402 | 7.3151 | 62.0728 | -61.7111 | -0.31586 | -0.013733 | 3.154 | -0.14191 | -7.4844 | -0.3067 | -0.036621 | 3.4698 | 68.8065 | 68.7195 | 116.0294 | 123.5001 | 3.154 | 123.4772 | 85.8582 | -0.3067 | 123.5001 | 3.154 | 85.8582 | 116.0294 | 123.4772 | -123.8297 | -123.8205
4361.7188 | 123.8297 | -61.3861 | 62.1094 | -0.09285 | 0.01581 | 0.013413 | 0.013388 | 0.061103 | 0.0015893 | 0.080544 | -58.2733 | 62.0956 | -61.7386 | -61.5417 | 54.5334 | 24.3027 | 6.9809 | 7.196 | 62.0956 | -61.7065 | -0.35248 | -0.013733 | 3.1128 | -0.15564 | -7.576 | -0.32044 | -0.013733 | 3.4653 | 68.367 | 68.5822 | 115.9195 | 123.4818 | 3.1128 | 123.4818 | 85.6888 | -0.32044 | 123.4818 | 3.1128 | 85.6888 | 115.9195 | 123.4818 | -123.848 | -123.8159
4362.7188 | 123.8663 | -61.4044 | 62.1277 | -0.20729 | 0.016665 | 0.01085 | 0.014669 | 0.059607 | 0.00094847 | 0.080758 | -58.2733 | 62.0865 | -61.7157 | -61.5692 | 54.538 | 24.2935 | 7.0267 | 7.2189 | 62.1002 | -61.7157 | -0.31128 | -0.041199 | 3.1311 | -0.1648 | -7.5897 | -0.31128 | -0.027466 | 3.4424 | 68.4311 | 68.6234 | 115.9424 | 123.4909 | 3.1311 | 123.5046 | 85.6979 | -0.31128 | 123.4909 | 3.1311 | 85.6979 | 115.9424 | 123.5046 | -123.8434 | -123.8434
4363.7188 | 123.8342 | -61.4044 | 62.1094 | -1.1228 | 0.014529 | 0.014054 | 0.01296 | 0.059607 | -0.00076053 | 0.080758 | -58.3099 | 62.0956 | -61.7065 | -61.5784 | 54.6112 | 24.3439 | 7.3929 | 7.338 | 62.0773 | -61.7065 | -0.30212 | -0.013733 | 3.0945 | -0.17395 | -7.4982 | -0.30212 | -0.032043 | 3.3966 | 68.7973 | 68.7424 | 116.0156 | 123.5001 | 3.0945 | 123.4818 | 85.7483 | -0.30212 | 123.5001 | 3.0945 | 85.7483 | 116.0156 | 123.4818 | -123.8159 | -123.8159
4364.7188 | 123.8388 | -61.4136 | 62.1414 | -0.062332 | 0.012606 | 0.011491 | 0.010824 | 0.058325 | 9.4068e-05 | 0.079476 | -58.2825 | 62.0819 | -61.7111 | -61.5417 | 54.6478 | 24.3622 | 7.4982 | 7.3746 | 62.114 | -61.6928 | -0.29755 | -0.059509 | 3.1311 | -0.12817 | -7.4936 | -0.27924 | -0.027465 | 3.4286 | 68.9117 | 68.7881 | 116.0614 | 123.4955 | 3.1311 | 123.5275 | 85.7758 | -0.27924 | 123.4955 | 3.1311 | 85.7758 | 116.0614 | 123.5275 | -123.8525 | -123.8342
4365.7188 | 123.8571 | -61.3907 | 62.114 | 0.18181 | 0.013033 | 0.0132 | 0.011251 | 0.060675 | -0.00054693 | 0.078195 | -58.1223 | 62.0911 | -61.7249 | -61.4822 | 54.5837 | 24.2706 | 7.2739 | 7.3105 | 62.0773 | -61.7111 | -0.33417 | -0.022889 | 3.2684 | -0.091553 | -7.5302 | -0.32043 | -0.036621 | 3.6026 | 68.6646 | 68.7012 | 115.9744 | 123.4818 | 3.2684 | 123.468 | 85.6613 | -0.32043 | 123.4818 | 3.2684 | 85.6613 | 115.9744 | 123.468 | -123.8388 | -123.8251
4366.7188 | 123.8297 | -61.3998 | 62.114 | 0.2581 | 0.013033 | 0.015122 | 0.01766 | 0.060462 | -0.0018285 | 0.079904 | -58.2687 | 62.1185 | -61.7111 | -61.5646 | 54.6021 | 24.3896 | 7.2784 | 7.2464 | 62.0865 | -61.702 | -0.31128 | 0.004577 | 3.1311 | -0.16479 | -7.5119 | -0.30212 | -0.027466 | 3.4424 | 68.6783 | 68.6462 | 116.0019 | 123.5184 | 3.1311 | 123.4863 | 85.7895 | -0.30212 | 123.5184 | 3.1311 | 85.7895 | 116.0019 | 123.4863 | -123.8251 | -123.8159
4367.7188 | 123.8434 | -61.3953 | 62.0865 | 0.2047 | 0.013888 | 0.014268 | 0.014669 | 0.061957 | 0.00030767 | 0.079904 | -58.2275 | 62.1048 | -61.734 | -61.3998 | 54.7394 | 24.44 | 7.3242 | 7.3746 | 62.0773 | -61.702 | -0.33875 | 0.01831 | 3.1677 | -0.004577 | -7.3471 | -0.3067 | -0.009155 | 3.5065 | 68.7195 | 68.7698 | 116.1346 | 123.5001 | 3.1677 | 123.4726 | 85.8353 | -0.3067 | 123.5001 | 3.1677 | 85.8353 | 116.1346 | 123.4726 | -123.8205 | -123.7885
4368.7188 | 123.8434 | -61.3998 | 62.1277 | 0.14366 | 0.012179 | 0.015336 | 0.012533 | 0.05918 | -0.00033333 | 0.078408 | -58.2596 | 62.0911 | -61.7294 | -61.5875 | 54.6295 | 24.2569 | 7.3746 | 7.3334 | 62.0728 | -61.6882 | -0.32959 | -0.036622 | 3.1403 | -0.18768 | -7.4982 | -0.28839 | -0.054932 | 3.4698 | 68.7744 | 68.7332 | 116.0294 | 123.4909 | 3.1403 | 123.4726 | 85.6567 | -0.28839 | 123.4909 | 3.1403 | 85.6567 | 116.0294 | 123.4726 | -123.8571 | -123.8159
4369.7344 | 123.8709 | -61.3724 | 62.1506 | -0.19203 | 0.01346 | 0.010423 | 0.011251 | 0.05918 | -0.0018285 | 0.078622 | -58.1863 | 62.0819 | -61.7111 | -61.5005 | 54.6799 | 24.2752 | 7.4799 | 7.4341 | 62.1368 | -61.6928 | -0.33875 | -0.068665 | 3.186 | -0.12817 | -7.4707 | -0.32044 | -0.013733 | 3.5248 | 68.8522 | 68.8065 | 116.0522 | 123.4543 | 3.186 | 123.5092 | 85.6476 | -0.32044 | 123.4543 | 3.186 | 85.6476 | 116.0522 | 123.5092 | -123.8617 | -123.8434
4370.7188 | 123.8571 | -61.4044 | 62.1231 | 0.1284 | 0.018801 | 0.01555 | 0.014669 | 0.060675 | -0.00011953 | 0.080544 | -58.2458 | 62.0773 | -61.7157 | -61.5601 | 54.6066 | 24.408 | 7.283 | 7.3105 | 62.1002 | -61.6928 | -0.31128 | -0.045776 | 3.1586 | -0.15564 | -7.5165 | -0.28839 | -0.022888 | 3.4698 | 68.6874 | 68.7149 | 116.011 | 123.4818 | 3.1586 | 123.5046 | 85.8124 | -0.28839 | 123.4818 | 3.1586 | 85.8124 | 116.011 | 123.5046 | -123.8388 | -123.8159
4371.7344 | 123.7335 | -61.409 | 62.1872 | -0.29121 | 0.014956 | 0.013413 | 0.014029 | 0.058112 | -0.00011953 | 0.079049 | -58.2779 | 62.178 | -61.7203 | -61.5921 | 54.5837 | 24.2981 | 7.5211 | 7.2601 | 62.1826 | -61.734 | -0.31128 | -0.009155 | 3.1311 | -0.1831 | -7.6035 | -0.32501 | -0.004578 | 3.4424 | 68.9301 | 68.6691 | 115.9927 | 123.587 | 3.1311 | 123.5916 | 85.7071 | -0.32501 | 123.587 | 3.1311 | 85.7071 | 115.9927 | 123.5916 | -123.9075 | -123.9212
4372.7188 | 123.8342 | -61.4136 | 62.1185 | 0.13603 | 0.013888 | 0.014909 | 0.012533 | 0.060675 | -0.0014013 | 0.078622 | -58.2413 | 62.0865 | -61.7065 | -61.5555 | 54.6204 | 24.3942 | 7.3425 | 7.3151 | 62.1185 | -61.6974 | -0.29297 | -0.032043 | 3.1723 | -0.14191 | -7.4982 | -0.28381 | 0 | 3.4653 | 68.7561 | 68.7286 | 116.0339 | 123.5001 | 3.1723 | 123.5321 | 85.8078 | -0.28381 | 123.5001 | 3.1723 | 85.8078 | 116.0339 | 123.5321 | -123.8251 | -123.8159
4373.7188 | 123.8434 | -61.4182 | 62.1277 | 0.2047 | 0.01346 | 0.014695 | 0.015951 | 0.061957 | -0.0014013 | 0.079476 | -58.2596 | 62.1002 | -61.7249 | -61.5555 | 54.6661 | 24.3851 | 7.3242 | 7.3105 | 62.0911 | -61.7111 | -0.3067 | -0.027466 | 3.1586 | -0.13733 | -7.4615 | -0.29297 | -0.036622 | 3.4653 | 68.7424 | 68.7286 | 116.0843 | 123.5184 | 3.1586 | 123.5092 | 85.8032 | -0.29297 | 123.5184 | 3.1586 | 85.8032 | 116.0843 | 123.5092 | -123.8525 | -123.8388
4374.7188 | 123.8709 | -61.3998 | 62.1002 | 0.14366 | 0.013033 | 0.010636 | 0.015738 | 0.060462 | -0.00076053 | 0.077981 | -58.2596 | 62.059 | -61.7432 | -61.5417 | 54.5929 | 24.3988 | 7.3608 | 7.3288 | 62.0911 | -61.6882 | -0.34332 | -0.041199 | 3.1403 | -0.14191 | -7.5073 | -0.28839 | -0.009156 | 3.4836 | 68.7607 | 68.7286 | 115.9927 | 123.4589 | 3.1403 | 123.4909 | 85.7986 | -0.28839 | 123.4589 | 3.1403 | 85.7986 | 115.9927 | 123.4909 | -123.8434 | -123.7885
4375.7188 | 123.793 | -61.409 | 62.1368 | 0.17418 | 0.017092 | 0.012132 | 0.011251 | 0.059394 | -0.00033333 | 0.07969 | -58.3008 | 62.0773 | -61.734 | -61.5875 | 54.6204 | 24.4171 | 7.3334 | 7.2968 | 62.0728 | -61.6882 | -0.32501 | -0.059509 | 3.1082 | -0.17853 | -7.5165 | -0.27923 | -0.064087 | 3.4332 | 68.7424 | 68.7057 | 116.0294 | 123.4863 | 3.1082 | 123.4818 | 85.8261 | -0.27923 | 123.4863 | 3.1082 | 85.8261 | 116.0294 | 123.4818 | -123.8708 | -123.8251
4376.7344 | 123.7747 | -61.3861 | 62.1826 | -0.22255 | 0.013674 | 0.010209 | 0.012106 | 0.057898 | -0.0011877 | 0.076699 | -58.2916 | 62.1414 | -61.7111 | -61.5646 | 54.6112 | 23.7625 | 7.5897 | 7.338 | 62.1597 | -61.702 | -0.32501 | -0.041199 | 3.0945 | -0.17853 | -7.5714 | -0.31586 | -0.022888 | 3.4195 | 68.9758 | 68.7241 | 115.9973 | 123.5275 | 3.0945 | 123.5458 | 85.1486 | -0.31586 | 123.5275 | 3.0945 | 85.1486 | 115.9973 | 123.5458 | -123.8937 | -123.8846
4377.7188 | 123.793 | -61.3953 | 62.1277 | 0.18944 | 0.015597 | 0.0089274 | 0.012747 | 0.057685 | -0.0020421 | 0.07734 | -58.287 | 62.0865 | -61.7111 | -61.5509 | 54.5746 | 23.8037 | 7.283 | 7.3425 | 62.1002 | -61.6837 | -0.31586 | -0.041199 | 3.1082 | -0.15564 | -7.5531 | -0.28839 | -0.027466 | 3.4241 | 68.6783 | 68.7378 | 115.9698 | 123.4818 | 3.1082 | 123.4955 | 85.199 | -0.28839 | 123.4818 | 3.1082 | 85.199 | 115.9698 | 123.4955 | -123.8388 | -123.8113
4378.7188 | 123.8022 | -61.4044 | 62.0911 | 0.15892 | 0.013033 | 0.011918 | 0.011038 | 0.058112 | 0.00052127 | 0.079904 | -58.3374 | 62.059 | -61.7477 | -61.5463 | 54.5746 | 24.3805 | 7.3471 | 7.3792 | 62.1048 | -61.7065 | -0.34332 | -0.032043 | 3.067 | -0.14191 | -7.5165 | -0.30212 | 0.013733 | 3.4103 | 68.7515 | 68.7836 | 115.979 | 123.4634 | 3.067 | 123.5092 | 85.7849 | -0.30212 | 123.4634 | 3.067 | 85.7849 | 115.979 | 123.5092 | -123.8388 | -123.7976
4379.7188 | 123.7106 | -61.4136 | 62.1826 | -0.27596 | 0.014956 | 0.0097818 | 0.01296 | 0.058539 | -0.0022559 | 0.07734 | -58.3328 | 62.1414 | -61.7432 | -61.5646 | 54.6066 | 24.4354 | 7.8598 | 7.4432 | 62.1552 | -61.6837 | -0.32959 | -0.041199 | 3.0807 | -0.15106 | -7.576 | -0.27008 | -0.027466 | 3.4103 | 69.2734 | 68.8568 | 116.0202 | 123.555 | 3.0807 | 123.5687 | 85.849 | -0.27008 | 123.555 | 3.0807 | 85.849 | 116.0202 | 123.5687 | -123.9258 | -123.8663
4380.7188 | 123.9395 | -61.3953 | 62.0819 | 0.17418 | 0.015383 | 0.011918 | 0.014029 | 0.061743 | -0.00097413 | 0.078835 | -58.2642 | 62.059 | -61.7157 | -61.5555 | 54.6021 | 24.4766 | 7.6813 | 7.5027 | 62.1002 | -61.702 | -0.32043 | -0.022888 | 3.1311 | -0.16022 | -7.4799 | -0.3067 | 0.018311 | 3.4515 | 69.0765 | 68.898 | 115.9973 | 123.4543 | 3.1311 | 123.4955 | 85.8719 | -0.3067 | 123.4543 | 3.1311 | 85.8719 | 115.9973 | 123.4955 | -123.7976 | -123.7839
4381.7344 | 123.8068 | -61.3998 | 62.1689 | -0.22255 | 0.014101 | 0.012773 | 0.010824 | 0.059607 | -0.00097413 | 0.079476 | -58.2733 | 62.1185 | -61.6974 | -61.5234 | 54.6112 | 23.8495 | 8.2352 | 7.7225 | 62.1185 | -61.702 | -0.29755 | -0.050354 | 3.1265 | -0.1236 | -7.5577 | -0.30212 | -0.050354 | 3.4241 | 69.635 | 69.1223 | 116.011 | 123.5184 | 3.1265 | 123.5184 | 85.2493 | -0.30212 | 123.5184 | 3.1265 | 85.2493 | 116.011 | 123.5184 | -123.8663 | -123.8708
4382.7188 | 123.8159 | -61.4136 | 62.1277 | 0.21233 | 0.012392 | 0.012132 | 0.011892 | 0.058539 | 0.00073487 | 0.077981 | -58.3145 | 62.0544 | -61.7432 | -61.5784 | 54.6158 | 23.735 | 7.5165 | 7.4066 | 62.114 | -61.6791 | -0.32959 | -0.073243 | 3.0991 | -0.1648 | -7.5119 | -0.2655 | -0.013733 | 3.4286 | 68.9301 | 68.8202 | 116.0294 | 123.468 | 3.0991 | 123.5275 | 85.1486 | -0.2655 | 123.468 | 3.0991 | 85.1486 | 116.0294 | 123.5275 | -123.8708 | -123.8068
4383.7188 | 123.8022 | -61.3861 | 62.146 | 0.19707 | 0.014315 | 0.01555 | 0.0095424 | 0.059394 | -0.0016149 | 0.079904 | -58.3054 | 62.0682 | -61.7111 | -61.5646 | 54.5883 | 23.6801 | 7.4524 | 7.3746 | 62.1002 | -61.6837 | -0.32501 | -0.07782 | 3.0807 | -0.17853 | -7.5577 | -0.29755 | -0.045776 | 3.4058 | 68.8385 | 68.7607 | 115.9744 | 123.4543 | 3.0807 | 123.4863 | 85.0662 | -0.29755 | 123.4543 | 3.0807 | 85.0662 | 115.9744 | 123.4863 | -123.8571 | -123.8297
4384.7188 | 123.8342 | -61.4136 | 62.1277 | 0.15892 | 0.016024 | 0.01085 | 0.010611 | 0.060248 | 0.0020167 | 0.080544 | -58.2733 | 62.0819 | -61.734 | -61.5692 | 54.5746 | 23.7213 | 7.8552 | 7.5302 | 62.0773 | -61.702 | -0.32044 | -0.045777 | 3.1403 | -0.15564 | -7.5531 | -0.28839 | -0.050354 | 3.4607 | 69.2688 | 68.9438 | 115.9882 | 123.4955 | 3.1403 | 123.4909 | 85.1349 | -0.28839 | 123.4955 | 3.1403 | 85.1349 | 115.9882 | 123.4909 | -123.8617 | -123.8297
4385.7188 | 123.8297 | -61.3953 | 62.1094 | 0.1284 | 0.014529 | 0.0078592 | 0.011679 | 0.057685 | 9.4068e-05 | 0.080331 | -58.3145 | 62.0865 | -61.7249 | -61.5738 | 54.57 | 23.7167 | 7.7774 | 7.5165 | 62.0819 | -61.702 | -0.32959 | -0.022888 | 3.0807 | -0.17853 | -7.5394 | -0.3067 | -0.027466 | 3.4103 | 69.1727 | 68.9117 | 115.9653 | 123.4818 | 3.0807 | 123.4772 | 85.112 | -0.3067 | 123.4818 | 3.0807 | 85.112 | 115.9653 | 123.4772 | -123.8342 | -123.8113
4386.7344 | 123.761 | -61.3907 | 62.1735 | -0.21492 | 0.014315 | 0.012132 | 0.011679 | 0.058325 | -0.00011953 | 0.077767 | -58.287 | 62.146 | -61.702 | -61.5326 | 54.5746 | 23.8129 | 7.7179 | 7.4432 | 62.1506 | -61.6974 | -0.31128 | -0.027466 | 3.1036 | -0.14191 | -7.5989 | -0.3067 | -0.022888 | 3.4149 | 69.1086 | 68.8339 | 115.9653 | 123.5367 | 3.1036 | 123.5413 | 85.2036 | -0.3067 | 123.5367 | 3.1036 | 85.2036 | 115.9653 | 123.5413 | -123.8754 | -123.8708
4387.7188 | 123.9395 | -61.4044 | 62.1323 | 0.14366 | 0.016665 | 0.014054 | 0.014242 | 0.062384 | 0.00052127 | 0.079904 | -58.2687 | 62.0773 | -61.7294 | -61.528 | 54.6249 | 23.8586 | 7.196 | 7.1365 | 62.1002 | -61.702 | -0.32501 | -0.054931 | 3.1357 | -0.1236 | -7.5073 | -0.29755 | -0.032043 | 3.4607 | 68.6005 | 68.541 | 116.0294 | 123.4818 | 3.1357 | 123.5046 | 85.2631 | -0.29755 | 123.4818 | 3.1357 | 85.2631 | 116.0294 | 123.5046 | -123.8617 | -123.8342
4388.7188 | 123.8251 | -61.3815 | 62.1185 | 0.21996 | 0.012606 | 0.012132 | 0.014242 | 0.060462 | -0.0011877 | 0.080758 | -58.2916 | 62.0682 | -61.7065 | -61.5692 | 54.6021 | 23.8632 | 7.3151 | 7.3471 | 62.1002 | -61.6928 | -0.32501 | -0.050354 | 3.0899 | -0.18768 | -7.5165 | -0.31128 | -0.01831 | 3.4149 | 68.6966 | 68.7286 | 115.9836 | 123.4497 | 3.0899 | 123.4818 | 85.2448 | -0.31128 | 123.4497 | 3.0899 | 85.2448 | 115.9836 | 123.4818 | -123.8251 | -123.8113
4389.7188 | 123.8388 | -61.3495 | 62.1506 | -0.16914 | 0.010683 | 0.0097818 | 0.0078336 | 0.05918 | 0.00052127 | 0.082467 | -58.2687 | 62.0911 | -61.6974 | -61.6974 | 54.6936 | 23.9914 | 7.1869 | 7.4661 | 62.1094 | -61.6745 | -0.3479 | -0.05951 | 3.0807 | -0.3479 | -7.457 | -0.32501 | -0.041199 | 3.4286 | 68.5364 | 68.8156 | 116.0431 | 123.4406 | 3.0807 | 123.4589 | 85.3409 | -0.32501 | 123.4406 | 3.0807 | 85.3409 | 116.0431 | 123.4589 | -123.848 | -123.8251
4390.7188 | 123.8159 | -61.3953 | 62.1231 | 0.17418 | 0.011965 | 0.0087138 | 0.008688 | 0.059607 | -0.00054693 | 0.080972 | -58.3099 | 62.0544 | -61.702 | -61.5875 | 54.57 | 23.9044 | 8.1985 | 7.6675 | 62.0773 | -61.6974 | -0.3067 | -0.068665 | 3.0853 | -0.19226 | -7.5531 | -0.30212 | -0.045776 | 3.392 | 69.5938 | 69.0628 | 115.9653 | 123.4497 | 3.0853 | 123.4726 | 85.2997 | -0.30212 | 123.4497 | 3.0853 | 85.2997 | 115.9653 | 123.4726 | -123.8251 | -123.8205
4391.7188 | 123.7976 | -61.377 | 62.146 | 0.18944 | 0.012606 | 0.011918 | 0.011679 | 0.060462 | -0.0011877 | 0.080544 | -58.3008 | 62.0682 | -61.7249 | -61.5829 | 54.5471 | 23.8815 | 8.0292 | 7.6172 | 62.1002 | -61.702 | -0.3479 | -0.07782 | 3.0762 | -0.20599 | -7.5989 | -0.32501 | -0.045776 | 3.4241 | 69.4061 | 68.9941 | 115.9241 | 123.4451 | 3.0762 | 123.4772 | 85.2585 | -0.32501 | 123.4451 | 3.0762 | 85.2585 | 115.9241 | 123.4772 | -123.8708 | -123.848
4392.7188 | 123.8022 | -61.3953 | 62.1368 | 0.10551 | 0.014529 | 0.010636 | 0.010611 | 0.059394 | -0.0028967 | 0.079049 | -58.3008 | 62.0682 | -61.734 | -61.5692 | 54.5746 | 23.9136 | 7.7362 | 7.5119 | 62.114 | -61.7157 | -0.33875 | -0.068665 | 3.0945 | -0.17395 | -7.5623 | -0.32043 | -0.022888 | 3.4332 | 69.1315 | 68.9072 | 115.9698 | 123.4634 | 3.0945 | 123.5092 | 85.3088 | -0.32043 | 123.4634 | 3.0945 | 85.3088 | 115.9698 | 123.5092 | -123.8708 | -123.8525
4393.7188 | 123.8525 | -61.3815 | 62.1002 | 0.21996 | 0.015169 | 0.013841 | 0.012533 | 0.057898 | -0.0020421 | 0.080758 | -58.3099 | 62.059 | -61.7157 | -61.5646 | 54.6021 | 23.9777 | 7.7087 | 7.5531 | 62.0682 | -61.6974 | -0.33417 | -0.041199 | 3.0716 | -0.1831 | -7.4982 | -0.31586 | -0.032044 | 3.4058 | 69.0903 | 68.9346 | 115.9836 | 123.4406 | 3.0716 | 123.4497 | 85.3592 | -0.31586 | 123.4406 | 3.0716 | 85.3592 | 115.9836 | 123.4497 | -123.8159 | -123.7976
4394.7188 | 123.8022 | -61.4044 | 62.1048 | 0.2047 | 0.01282 | 0.013841 | 0.011465 | 0.060889 | -0.0011877 | 0.079476 | -58.3328 | 62.059 | -61.7157 | -61.5555 | 54.6387 | 23.9044 | 7.7957 | 7.5668 | 62.0911 | -61.702 | -0.31128 | -0.045776 | 3.0716 | -0.15106 | -7.4661 | -0.29755 | -0.013733 | 3.3829 | 69.2001 | 68.9713 | 116.0431 | 123.4634 | 3.0716 | 123.4955 | 85.3088 | -0.29755 | 123.4634 | 3.0716 | 85.3088 | 116.0431 | 123.4955 | -123.8205 | -123.8068
4395.7188 | 123.7793 | -61.409 | 62.1048 | 0.17418 | 0.016238 | 0.011491 | 0.011465 | 0.060462 | 0.00073487 | 0.080331 | -58.3603 | 62.0773 | -61.7294 | -61.6104 | 54.5975 | 23.8403 | 7.8232 | 7.4982 | 62.1094 | -61.6928 | -0.32043 | -0.027465 | 3.0487 | -0.20142 | -7.5073 | -0.28381 | 0.004578 | 3.3691 | 69.2322 | 68.9072 | 116.0065 | 123.4863 | 3.0487 | 123.5184 | 85.2493 | -0.28381 | 123.4863 | 3.0487 | 85.2493 | 116.0065 | 123.5184 | -123.8342 | -123.7976
4396.7188 | 123.7885 | -61.4182 | 62.1048 | 0.2047 | 0.011751 | 0.011277 | 0.011251 | 0.059607 | -0.00076053 | 0.081185 | -58.3603 | 62.059 | -61.7432 | -61.5967 | 54.57 | 24.4675 | 7.901 | 7.5485 | 62.0636 | -61.734 | -0.32501 | -0.045776 | 3.0579 | -0.17853 | -7.5348 | -0.31586 | -0.041198 | 3.3829 | 69.3192 | 68.9667 | 115.9882 | 123.4772 | 3.0579 | 123.4818 | 85.8856 | -0.31586 | 123.4772 | 3.0579 | 85.8856 | 115.9882 | 123.4818 | -123.848 | -123.8388
4397.7188 | 123.7839 | -61.3907 | 62.1048 | 0.097885 | 0.013033 | 0.010636 | 0.011465 | 0.060462 | -0.0020421 | 0.078195 | -58.3237 | 62.059 | -61.7203 | -61.6013 | 54.5792 | 24.5178 | 7.9056 | 7.5714 | 62.0819 | -61.6928 | -0.32959 | -0.045776 | 3.067 | -0.21057 | -7.5256 | -0.30212 | -0.022888 | 3.3966 | 69.2963 | 68.9621 | 115.9698 | 123.4497 | 3.067 | 123.4726 | 85.9085 | -0.30212 | 123.4497 | 3.067 | 85.9085 | 115.9698 | 123.4726 | -123.8251 | -123.7976
4398.7188 | 123.8159 | -61.4044 | 62.1323 | 0.15129 | 0.015169 | 0.013627 | 0.013174 | 0.058966 | 0.00073487 | 0.079476 | -58.3374 | 62.0636 | -61.7203 | -61.5692 | 54.5837 | 24.4446 | 7.3563 | 7.3654 | 62.0773 | -61.6928 | -0.31586 | -0.068664 | 3.067 | -0.1648 | -7.5485 | -0.28839 | -0.054931 | 3.3829 | 68.7607 | 68.7698 | 115.9882 | 123.468 | 3.067 | 123.4818 | 85.849 | -0.28839 | 123.468 | 3.067 | 85.849 | 115.9882 | 123.4818 | -123.8525 | -123.8251
4399.7188 | 123.88 | -61.3998 | 62.1094 | -0.016556 | 0.015383 | 0.011918 | 0.0099698 | 0.058325 | -0.00054693 | 0.079476 | -58.2962 | 62.0911 | -61.7249 | -61.4914 | 54.657 | 24.5911 | 7.8873 | 7.6447 | 62.1002 | -61.6791 | -0.32501 | -0.018311 | 3.1036 | -0.091553 | -7.4524 | -0.27924 | -0.009155 | 3.4286 | 69.2871 | 69.0445 | 116.0568 | 123.4909 | 3.1036 | 123.5001 | 85.9909 | -0.27924 | 123.4909 | 3.1036 | 85.9909 | 116.0568 | 123.5001 | -123.8342 | -123.7885
4400.7188 | 123.8571 | -61.4319 | 62.0911 | 0.18181 | 0.01346 | 0.015122 | 0.014242 | 0.060889 | -0.00011953 | 0.080117 | -58.3282 | 62.0819 | -61.7432 | -61.5417 | 54.6387 | 24.5453 | 7.7362 | 7.5211 | 62.0773 | -61.7065 | -0.31128 | -0.009155 | 3.1036 | -0.10986 | -7.4524 | -0.27466 | -0.013732 | 3.4149 | 69.1681 | 68.9529 | 116.0706 | 123.5138 | 3.1036 | 123.5092 | 85.9772 | -0.27466 | 123.5138 | 3.1036 | 85.9772 | 116.0706 | 123.5092 | -123.8342 | -123.7976
4401.7188 | 123.8571 | -61.4182 | 62.1002 | 0.21996 | 0.016451 | 0.011491 | 0.014669 | 0.060248 | 0.00073487 | 0.079904 | -58.3054 | 62.059 | -61.7203 | -61.5463 | 54.6249 | 24.5041 | 7.338 | 7.3471 | 62.0728 | -61.6837 | -0.30212 | -0.041199 | 3.1128 | -0.12817 | -7.4753 | -0.2655 | -0.027466 | 3.4149 | 68.7561 | 68.7653 | 116.0431 | 123.4772 | 3.1128 | 123.4909 | 85.9222 | -0.2655 | 123.4772 | 3.1128 | 85.9222 | 116.0431 | 123.4909 | -123.8205 | -123.7839
4402.7188 | 123.8159 | -61.4182 | 62.1231 | 0.090256 | 0.015597 | 0.015122 | 0.012747 | 0.058966 | -0.00033333 | 0.082467 | -58.3328 | 62.0728 | -61.7111 | -61.5921 | 54.5883 | 24.5041 | 7.4615 | 7.3608 | 62.0819 | -61.6837 | -0.29297 | -0.050354 | 3.0853 | -0.17395 | -7.5348 | -0.2655 | -0.041199 | 3.3783 | 68.8797 | 68.779 | 116.0065 | 123.4909 | 3.0853 | 123.5001 | 85.9222 | -0.2655 | 123.4909 | 3.0853 | 85.9222 | 116.0065 | 123.5001 | -123.8342 | -123.8068
4403.7188 | 123.8068 | -61.3998 | 62.1094 | 0.15129 | 0.014742 | 0.013841 | 0.012533 | 0.060675 | 9.4068e-05 | 0.078622 | -58.3374 | 62.0911 | -61.7386 | -61.5646 | 54.6112 | 24.5316 | 7.9422 | 7.5531 | 62.0819 | -61.702 | -0.33874 | -0.018311 | 3.0624 | -0.16479 | -7.4982 | -0.30212 | -0.027466 | 3.4012 | 69.342 | 68.9529 | 116.011 | 123.4909 | 3.0624 | 123.4818 | 85.9314 | -0.30212 | 123.4909 | 3.0624 | 85.9314 | 116.011 | 123.4818 | -123.848 | -123.8113
4404.7188 | 123.8754 | -61.3586 | 62.1323 | -0.09285 | 0.013247 | 0.0099954 | 0.0080472 | 0.058112 | -0.00054693 | 0.079263 | -58.3145 | 62.0544 | -61.7249 | -61.5143 | 54.6295 | 24.614 | 7.9514 | 7.6263 | 62.114 | -61.6562 | -0.36621 | -0.07782 | 3.0441 | -0.15564 | -7.5027 | -0.29755 | -0.01831 | 3.4103 | 69.31 | 68.985 | 115.9882 | 123.4131 | 3.0441 | 123.4726 | 85.9726 | -0.29755 | 123.4131 | 3.0441 | 85.9726 | 115.9882 | 123.4726 | -123.8571 | -123.7885
4405.7188 | 123.8388 | -61.4136 | 62.1094 | 0.17418 | 0.016238 | 0.015763 | 0.014242 | 0.06153 | -0.00054693 | 0.076486 | -58.3145 | 62.0682 | -61.7203 | -61.5509 | 54.57 | 24.5819 | 7.9376 | 7.5943 | 62.1048 | -61.7111 | -0.3067 | -0.041199 | 3.0991 | -0.13733 | -7.5394 | -0.29755 | -0.004578 | 3.4058 | 69.3512 | 69.0079 | 115.9836 | 123.4818 | 3.0991 | 123.5184 | 85.9955 | -0.29755 | 123.4818 | 3.0991 | 85.9955 | 115.9836 | 123.5184 | -123.8297 | -123.8205
4406.7188 | 123.8342 | -61.4044 | 62.114 | 0.73875 | 0.01581 | 0.015977 | 0.014029 | 0.059607 | -0.0016149 | 0.07969 | -58.2825 | 62.0773 | -61.7203 | -61.5555 | 54.6204 | 24.5132 | 7.4661 | 7.4203 | 62.0911 | -61.7157 | -0.31586 | -0.036621 | 3.1219 | -0.15106 | -7.4936 | -0.31128 | -0.022889 | 3.4378 | 68.8705 | 68.8248 | 116.0248 | 123.4818 | 3.1219 | 123.4955 | 85.9177 | -0.31128 | 123.4818 | 3.1219 | 85.9177 | 116.0248 | 123.4955 | -123.8342 | -123.8297
4407.7188 | 123.8388 | -61.3998 | 62.1094 | 0.16655 | 0.016878 | 0.015336 | 0.014456 | 0.060034 | -0.0011877 | 0.077126 | -58.3466 | 62.1094 | -61.7477 | -61.5601 | 54.57 | 24.4629 | 7.5623 | 7.402 | 62.0911 | -61.6928 | -0.3479 | 0 | 3.0533 | -0.16022 | -7.5394 | -0.29297 | -0.018311 | 3.4012 | 68.9621 | 68.8019 | 115.9698 | 123.5092 | 3.0533 | 123.4909 | 85.8627 | -0.29297 | 123.5092 | 3.0533 | 85.8627 | 115.9698 | 123.4909 | -123.8571 | -123.8022
4408.7188 | 123.7976 | -61.4182 | 62.0911 | 0.19707 | 0.014101 | 0.013841 | 0.015738 | 0.061957 | -0.00033333 | 0.07969 | -58.3557 | 62.1323 | -61.7432 | -61.5829 | 54.5929 | 24.5407 | 7.9147 | 7.5073 | 62.1002 | -61.7249 | -0.32501 | 0.041199 | 3.0624 | -0.16479 | -7.4982 | -0.3067 | 0.009156 | 3.3875 | 69.3329 | 68.9255 | 116.011 | 123.5504 | 3.0624 | 123.5184 | 85.9589 | -0.3067 | 123.5504 | 3.0624 | 85.9589 | 116.011 | 123.5184 | -123.8342 | -123.8159
4409.7344 | 123.8709 | -61.4044 | 62.1231 | -0.19966 | 0.016024 | 0.0095682 | 0.0084744 | 0.060248 | 0.00094847 | 0.079049 | -58.3282 | 62.0956 | -61.7249 | -61.5234 | 54.6799 | 24.6277 | 7.9651 | 7.6492 | 62.0956 | -61.6837 | -0.32044 | -0.027466 | 3.0762 | -0.11902 | -7.4432 | -0.27924 | -0.027466 | 3.3966 | 69.3695 | 69.0537 | 116.0843 | 123.5001 | 3.0762 | 123.5001 | 86.0321 | -0.27924 | 123.5001 | 3.0762 | 86.0321 | 116.0843 | 123.5001 | -123.848 | -123.8068
4410.7188 | 123.8342 | -61.4044 | 62.1048 | -0.11574 | 0.016451 | 0.0132 | 0.013174 | 0.060889 | -0.0020421 | 0.078195 | -58.342 | 62.059 | -61.702 | -61.5601 | 54.6021 | 24.6414 | 7.9102 | 7.576 | 62.0819 | -61.7203 | -0.29755 | -0.045776 | 3.0624 | -0.15564 | -7.5027 | -0.31586 | -0.022888 | 3.36 | 69.3146 | 68.9804 | 116.0065 | 123.4634 | 3.0624 | 123.4863 | 86.0458 | -0.31586 | 123.4634 | 3.0624 | 86.0458 | 116.0065 | 123.4863 | -123.8068 | -123.8251
4411.7188 | 123.8159 | -61.4227 | 62.1094 | 0.18944 | 0.016878 | 0.010636 | 0.01232 | 0.058753 | 0.0022303 | 0.083749 | -58.3466 | 62.0728 | -61.7249 | -61.5967 | 54.5975 | 24.5682 | 7.9193 | 7.5439 | 62.0728 | -61.7203 | -0.30213 | -0.036621 | 3.0762 | -0.17395 | -7.5119 | -0.29755 | -0.036621 | 3.3783 | 69.342 | 68.9667 | 116.0202 | 123.4955 | 3.0762 | 123.4955 | 85.9909 | -0.29755 | 123.4955 | 3.0762 | 85.9909 | 116.0202 | 123.4955 | -123.8342 | -123.8297
4412.7188 | 123.8617 | -61.3998 | 62.1002 | 0.21996 | 0.016024 | 0.014482 | 0.01296 | 0.062812 | 0.0020167 | 0.078835 | -58.3145 | 62.1002 | -61.7065 | -61.4639 | 54.776 | 24.7055 | 7.9102 | 7.6447 | 62.0773 | -61.7065 | -0.3067 | 0 | 3.0853 | -0.064087 | -7.3242 | -0.3067 | -0.022888 | 3.392 | 69.31 | 69.0445 | 116.1758 | 123.5001 | 3.0853 | 123.4772 | 86.1053 | -0.3067 | 123.5001 | 3.0853 | 86.1053 | 116.1758 | 123.4772 | -123.8068 | -123.8068
4413.7188 | 123.8068 | -61.4365 | 62.0728 | 0.15129 | 0.014315 | 0.011704 | 0.015524 | 0.062812 | 9.4068e-05 | 0.077981 | -58.2962 | 62.114 | -61.7386 | -61.5509 | 54.6661 | 24.5956 | 7.9285 | 7.5714 | 62.0728 | -61.6974 | -0.30212 | 0.041199 | 3.1403 | -0.11444 | -7.4066 | -0.26093 | 0 | 3.4424 | 69.3649 | 69.0079 | 116.1026 | 123.5504 | 3.1403 | 123.5092 | 86.0321 | -0.26093 | 123.5504 | 3.1403 | 86.0321 | 116.1026 | 123.5092 | -123.8113 | -123.7701
4414.7188 | 123.8388 | -61.3861 | 62.146 | -0.26833 | 0.014956 | 0.011491 | 0.011465 | 0.058753 | -0.00033333 | 0.078835 | -58.3145 | 62.0728 | -61.7249 | -61.5234 | 54.7668 | 24.6552 | 8.0475 | 7.6447 | 62.1277 | -61.6425 | -0.33875 | -0.073242 | 3.0716 | -0.13733 | -7.3791 | -0.25635 | -0.01831 | 3.4103 | 69.4336 | 69.0308 | 116.153 | 123.4589 | 3.0716 | 123.5138 | 86.0413 | -0.25635 | 123.4589 | 3.0716 | 86.0413 | 116.153 | 123.5138 | -123.8708 | -123.7885
4415.7188 | 123.7839 | -61.3861 | 62.1048 | 0.13603 | 0.017947 | 0.015122 | 0.016592 | 0.060675 | -0.0011877 | 0.079049 | -58.374 | 62.1506 | -61.7477 | -61.6287 | 54.5197 | 24.4812 | 7.6126 | 7.3288 | 62.1277 | -61.7294 | -0.36163 | 0.045777 | 3.0121 | -0.24262 | -7.5851 | -0.34332 | 0.022889 | 3.3737 | 68.9987 | 68.7149 | 115.9058 | 123.5367 | 3.0121 | 123.5138 | 85.8673 | -0.34332 | 123.5367 | 3.0121 | 85.8673 | 115.9058 | 123.5138 | -123.8525 | -123.8342
4416.7188 | 123.848 | -61.4227 | 62.0956 | 0.17418 | 0.017092 | 0.015122 | 0.01531 | 0.060248 | -0.00011953 | 0.079904 | -58.4427 | 62.0728 | -61.7386 | -61.5692 | 54.6341 | 24.6552 | 7.4524 | 7.3883 | 62.1048 | -61.6928 | -0.31586 | -0.022888 | 2.98 | -0.14649 | -7.4615 | -0.27008 | 0.009155 | 3.2959 | 68.8751 | 68.811 | 116.0568 | 123.4955 | 2.98 | 123.5275 | 86.0779 | -0.27008 | 123.4955 | 2.98 | 86.0779 | 116.0568 | 123.5275 | -123.8342 | -123.7885
4417.7188 | 123.8342 | -61.3953 | 62.1094 | 0.2047 | 0.01816 | 0.011277 | 0.013601 | 0.061743 | 9.4068e-05 | 0.080758 | -58.2916 | 62.0956 | -61.7294 | -61.4777 | 54.8172 | 24.7192 | 7.4341 | 7.4661 | 62.0865 | -61.7111 | -0.33417 | -0.013733 | 3.1036 | -0.082397 | -7.2922 | -0.31586 | -0.022888 | 3.4378 | 68.8293 | 68.8614 | 116.2125 | 123.4909 | 3.1036 | 123.4818 | 86.1145 | -0.31586 | 123.4909 | 3.1036 | 86.1145 | 116.2125 | 123.4818 | -123.8388 | -123.8205
4418.7188 | 123.88 | -61.4044 | 62.1231 | 0.19707 | 0.014529 | 0.013841 | 0.013815 | 0.059821 | -0.00097413 | 0.079049 | -58.287 | 62.1048 | -61.7203 | -61.5646 | 54.5517 | 24.5773 | 7.3471 | 7.196 | 62.0499 | -61.7432 | -0.31586 | -0.018311 | 3.1174 | -0.16022 | -7.5714 | -0.33875 | -0.073242 | 3.4332 | 68.7515 | 68.6005 | 115.9561 | 123.5092 | 3.1174 | 123.4543 | 85.9818 | -0.33875 | 123.5092 | 3.1174 | 85.9818 | 115.9561 | 123.4543 | -123.8434 | -123.8663
4419.7344 | 123.8297 | -61.3907 | 62.1643 | -0.21492 | 0.01282 | 0.010423 | 0.0099698 | 0.058325 | -0.0014013 | 0.080331 | -58.2962 | 62.1277 | -61.702 | -61.528 | 54.5929 | 24.5773 | 7.7179 | 7.4661 | 62.146 | -61.6699 | -0.31128 | -0.036621 | 3.0945 | -0.13733 | -7.5714 | -0.27924 | -0.018311 | 3.4058 | 69.1086 | 68.8568 | 115.9836 | 123.5184 | 3.0945 | 123.5367 | 85.968 | -0.27924 | 123.5184 | 3.0945 | 85.968 | 115.9836 | 123.5367 | -123.8663 | -123.8342
4420.7188 | 123.8663 | -61.3953 | 62.114 | 0.052109 | 0.017306 | 0.013413 | 0.015738 | 0.060889 | -0.0026831 | 0.079263 | -58.3008 | 62.1185 | -61.7157 | -61.5738 | 54.6021 | 24.5728 | 7.6584 | 7.4478 | 62.0728 | -61.7111 | -0.32043 | 0.004577 | 3.0945 | -0.17853 | -7.5119 | -0.31586 | -0.041199 | 3.4149 | 69.0537 | 68.8431 | 115.9973 | 123.5138 | 3.0945 | 123.468 | 85.968 | -0.31586 | 123.5138 | 3.0945 | 85.968 | 115.9973 | 123.468 | -123.8297 | -123.8251
4421.7188 | 123.7656 | -61.441 | 62.1277 | 0.16655 | 0.017306 | 0.0132 | 0.018301 | 0.062812 | -0.0011877 | 0.078835 | -58.3466 | 62.1368 | -61.7523 | -61.647 | 54.5654 | 24.4995 | 7.6721 | 7.3425 | 62.1506 | -61.7523 | -0.31128 | 0.009155 | 3.0945 | -0.20599 | -7.5623 | -0.31128 | 0.022888 | 3.4058 | 69.1132 | 68.7836 | 116.0065 | 123.5779 | 3.0945 | 123.5916 | 85.9406 | -0.31128 | 123.5779 | 3.0945 | 85.9406 | 116.0065 | 123.5916 | -123.88 | -123.88
4422.7188 | 123.7518 | -61.4365 | 62.1552 | 0.12077 | 0.016451 | 0.01085 | 0.014456 | 0.061103 | -0.0020421 | 0.079263 | -58.3878 | 62.1643 | -61.7249 | -61.6562 | 54.5517 | 24.5041 | 7.6859 | 7.3654 | 62.146 | -61.7615 | -0.28839 | 0.009156 | 3.0487 | -0.21973 | -7.6035 | -0.32501 | -0.009155 | 3.3371 | 69.1223 | 68.8019 | 115.9882 | 123.6008 | 3.0487 | 123.5825 | 85.9406 | -0.32501 | 123.6008 | 3.0487 | 85.9406 | 115.9882 | 123.5825 | -123.88 | -123.9166
4423.7188 | 123.8068 | -61.3724 | 62.1094 | 0.14366 | 0.01581 | 0.012559 | 0.0093288 | 0.060462 | 0.00052127 | 0.081185 | -58.374 | 62.0682 | -61.7386 | -61.6196 | 54.6066 | 24.559 | 7.6263 | 7.4249 | 62.1002 | -61.6837 | -0.36621 | -0.041199 | 2.9984 | -0.24719 | -7.5027 | -0.31128 | -0.009155 | 3.3646 | 68.9987 | 68.7973 | 115.979 | 123.4406 | 2.9984 | 123.4726 | 85.9314 | -0.31128 | 123.4406 | 2.9984 | 85.9314 | 115.979 | 123.4726 | -123.848 | -123.793
4424.7188 | 123.8388 | -61.4044 | 62.1277 | -0.031814 | 0.012392 | 0.0061502 | 0.0082608 | 0.057898 | 0.0026575 | 0.077554 | -58.3282 | 62.0636 | -61.7111 | -61.5646 | 54.6204 | 24.0326 | 7.9514 | 7.5851 | 62.1185 | -61.6745 | -0.3067 | -0.064087 | 3.0762 | -0.16022 | -7.5073 | -0.27008 | -0.009156 | 3.3829 | 69.3558 | 68.9896 | 116.0248 | 123.468 | 3.0762 | 123.5229 | 85.437 | -0.27008 | 123.468 | 3.0762 | 85.437 | 116.0248 | 123.5229 | -123.8388 | -123.8022
4425.7188 | 123.8983 | -61.4273 | 62.1231 | 0.14366 | 0.014101 | 0.015122 | 0.013815 | 0.058539 | -0.00011953 | 0.080117 | -58.2825 | 62.0956 | -61.702 | -61.5738 | 54.5792 | 24.0234 | 7.8873 | 7.5623 | 62.0773 | -61.7294 | -0.27466 | -0.027466 | 3.1448 | -0.14648 | -7.5439 | -0.30212 | -0.045776 | 3.4195 | 69.3146 | 68.9896 | 116.0065 | 123.5229 | 3.1448 | 123.5046 | 85.4507 | -0.30212 | 123.5229 | 3.1448 | 85.4507 | 116.0065 | 123.5046 | -123.8251 | -123.8525
4426.7188 | 123.848 | -61.4273 | 62.0956 | 0.15129 | 0.013674 | 0.017472 | 0.016165 | 0.062384 | -0.0022559 | 0.079476 | -58.3054 | 62.1048 | -61.702 | -61.5463 | 54.5883 | 24.0692 | 7.8644 | 7.5577 | 62.0636 | -61.7203 | -0.27466 | 0.009155 | 3.1219 | -0.11902 | -7.5073 | -0.29297 | -0.032043 | 3.3966 | 69.2917 | 68.985 | 116.0156 | 123.5321 | 3.1219 | 123.4909 | 85.4965 | -0.29297 | 123.5321 | 3.1219 | 85.4965 | 116.0156 | 123.4909 | -123.7976 | -123.8159
4427.7188 | 123.7839 | -61.3998 | 62.1597 | 0.0063326 | 0.01282 | 0.010423 | 0.010183 | 0.060462 | 0.00073487 | 0.079049 | -58.3603 | 62.0865 | -61.7294 | -61.5967 | 54.6341 | 24.1379 | 8.0063 | 7.5577 | 62.1048 | -61.7065 | -0.32959 | -0.073242 | 3.0396 | -0.19684 | -7.5256 | -0.3067 | -0.054932 | 3.3691 | 69.4061 | 68.9575 | 116.0339 | 123.4863 | 3.0396 | 123.5046 | 85.5377 | -0.3067 | 123.4863 | 3.0396 | 85.5377 | 116.0339 | 123.5046 | -123.8892 | -123.8663
4428.7188 | 123.7701 | -61.4273 | 62.1368 | 0.14366 | 0.018587 | 0.013627 | 0.018301 | 0.061743 | -0.0016149 | 0.080544 | -58.374 | 62.146 | -61.7615 | -61.647 | 54.5197 | 24.0875 | 8.0658 | 7.489 | 62.1277 | -61.7523 | -0.33417 | 0.009155 | 3.0533 | -0.21973 | -7.6172 | -0.32501 | -0.009155 | 3.3875 | 69.4931 | 68.9163 | 115.947 | 123.5733 | 3.0533 | 123.555 | 85.5148 | -0.32501 | 123.5733 | 3.0533 | 85.5148 | 115.947 | 123.555 | -123.8983 | -123.8892
4429.7344 | 123.8205 | -61.3724 | 62.1414 | -0.27596 | 0.014529 | 0.011491 | 0.0093288 | 0.059394 | -0.0024695 | 0.079476 | -58.2779 | 62.0956 | -61.7157 | -61.5463 | 54.6616 | 24.2157 | 8.0566 | 7.6675 | 62.1368 | -61.6745 | -0.34332 | -0.045776 | 3.0945 | -0.17395 | -7.4799 | -0.30213 | -0.004577 | 3.4378 | 69.429 | 69.0399 | 116.0339 | 123.468 | 3.0945 | 123.5092 | 85.5881 | -0.30213 | 123.468 | 3.0945 | 85.5881 | 116.0339 | 123.5092 | -123.8571 | -123.8159
4430.7188 | 123.8159 | -61.3907 | 62.114 | 0.15129 | 0.013888 | 0.018327 | 0.015097 | 0.060462 | 0.0013757 | 0.078622 | -58.2779 | 62.0956 | -61.7203 | -61.5601 | 54.6204 | 24.3713 | 7.6584 | 7.7133 | 62.0636 | -61.7432 | -0.32959 | -0.018311 | 3.1128 | -0.16937 | -7.4936 | -0.35248 | -0.050354 | 3.4424 | 69.0491 | 69.104 | 116.011 | 123.4863 | 3.1128 | 123.4543 | 85.762 | -0.35248 | 123.4863 | 3.1128 | 85.762 | 116.011 | 123.4543 | -123.8342 | -123.8571
4431.7188 | 123.8251 | -61.409 | 62.1048 | 0.2047 | 0.016878 | 0.015763 | 0.015524 | 0.061743 | -0.00054693 | 0.079049 | -58.3008 | 62.0956 | -61.7203 | -61.5692 | 54.6524 | 24.3713 | 7.9697 | 7.608 | 62.0865 | -61.7249 | -0.31128 | -0.009155 | 3.1082 | -0.16022 | -7.4524 | -0.31586 | -0.01831 | 3.4195 | 69.3787 | 69.017 | 116.0614 | 123.5046 | 3.1082 | 123.4955 | 85.7803 | -0.31586 | 123.5046 | 3.1082 | 85.7803 | 116.0614 | 123.4955 | -123.8251 | -123.8297
4432.7188 | 123.8388 | -61.3907 | 62.0865 | 0.074997 | 0.016878 | 0.014054 | 0.014883 | 0.062171 | -0.00033333 | 0.078622 | -58.342 | 62.1185 | -61.7203 | -61.5738 | 54.6295 | 24.3576 | 7.9422 | 7.5851 | 62.0865 | -61.734 | -0.32959 | 0.032043 | 3.0487 | -0.18311 | -7.457 | -0.34332 | 0 | 3.3783 | 69.3329 | 68.9758 | 116.0202 | 123.5092 | 3.0487 | 123.4772 | 85.7483 | -0.34332 | 123.5092 | 3.0487 | 85.7483 | 116.0202 | 123.4772 | -123.8068 | -123.8205
4433.7188 | 123.8617 | -61.4136 | 62.0911 | 0.2047 | 0.01581 | 0.014054 | 0.016378 | 0.061316 | 0.00073487 | 0.080758 | -58.3557 | 62.1185 | -61.7294 | -61.5646 | 54.5609 | 24.5865 | 7.9514 | 7.5668 | 62.0819 | -61.7477 | -0.31586 | 0.027466 | 3.0579 | -0.15106 | -7.5302 | -0.33417 | -0.009155 | 3.3737 | 69.3649 | 68.9804 | 115.9744 | 123.5321 | 3.0579 | 123.4955 | 86.0001 | -0.33417 | 123.5321 | 3.0579 | 86.0001 | 115.9744 | 123.4955 | -123.8205 | -123.8388
4434.7188 | 123.8251 | -61.4182 | 62.0956 | 0.18944 | 0.014742 | 0.0132 | 0.014883 | 0.063452 | 0.00030767 | 0.078408 | -58.3466 | 62.1414 | -61.7615 | -61.6104 | 54.6158 | 24.5773 | 7.9788 | 7.5394 | 62.1185 | -61.7523 | -0.34332 | 0.045776 | 3.0716 | -0.19226 | -7.4799 | -0.33417 | 0.022888 | 3.4149 | 69.397 | 68.9575 | 116.0339 | 123.5596 | 3.0716 | 123.5367 | 85.9955 | -0.33417 | 123.5596 | 3.0716 | 85.9955 | 116.0339 | 123.5367 | -123.8571 | -123.848
4435.7188 | 123.7701 | -61.4273 | 62.1185 | 0.21233 | 0.016451 | 0.016618 | 0.015524 | 0.062598 | -0.0028967 | 0.080117 | -58.3603 | 62.1506 | -61.7432 | -61.6104 | 54.5563 | 24.0555 | 7.9834 | 7.4936 | 62.1002 | -61.7477 | -0.31586 | 0.032044 | 3.067 | -0.18311 | -7.5623 | -0.32044 | -0.01831 | 3.3829 | 69.4107 | 68.9209 | 115.9836 | 123.5779 | 3.067 | 123.5275 | 85.4828 | -0.32044 | 123.5779 | 3.067 | 85.4828 | 115.9836 | 123.5275 | -123.8617 | -123.8663
4436.7188 | 123.7656 | -61.4456 | 62.1368 | 0.15892 | 0.016665 | 0.014695 | 0.013601 | 0.061957 | 9.4068e-05 | 0.079263 | -58.3649 | 62.1552 | -61.7523 | -61.6425 | 54.5105 | 24.115 | 8.0154 | 7.4615 | 62.1231 | -61.7432 | -0.3067 | 0.01831 | 3.0808 | -0.19684 | -7.6263 | -0.29755 | -0.013733 | 3.3875 | 69.4611 | 68.9072 | 115.9561 | 123.6008 | 3.0808 | 123.5687 | 85.5606 | -0.29755 | 123.6008 | 3.0808 | 85.5606 | 115.9561 | 123.5687 | -123.8892 | -123.88
4437.7188 | 123.848 | -61.3861 | 62.1094 | 0.18181 | 0.017092 | 0.013413 | 0.013388 | 0.064093 | 0.00094847 | 0.079476 | -58.3099 | 62.1094 | -61.7294 | -61.5189 | 54.57 | 24.3256 | 7.8964 | 7.5394 | 62.114 | -61.702 | -0.34332 | 0 | 3.0762 | -0.13275 | -7.5394 | -0.31586 | 0.004578 | 3.4195 | 69.2825 | 68.9255 | 115.9561 | 123.4955 | 3.0762 | 123.5001 | 85.7117 | -0.31586 | 123.4955 | 3.0762 | 85.7117 | 115.9561 | 123.5001 | -123.8388 | -123.8113
4438.7188 | 123.9578 | -61.409 | 62.1002 | 0.22758 | 0.016878 | 0.015763 | 0.013601 | 0.062171 | -0.00033333 | 0.079476 | -58.3054 | 62.0956 | -61.7477 | -61.5692 | 54.6295 | 24.3484 | 7.8918 | 7.4066 | 62.0728 | -61.734 | -0.33875 | -0.004578 | 3.1036 | -0.16022 | -7.4707 | -0.32501 | -0.027466 | 3.4424 | 69.3008 | 68.8156 | 116.0385 | 123.5046 | 3.1036 | 123.4818 | 85.7574 | -0.32501 | 123.5046 | 3.1036 | 85.7574 | 116.0385 | 123.4818 | -123.848 | -123.8342
4439.7188 | 123.8434 | -61.3861 | 62.0956 | 0.1284 | 0.016238 | 0.015122 | 0.014669 | 0.060675 | -0.0016149 | 0.080117 | -58.3282 | 62.1048 | -61.7523 | -61.5738 | 54.5883 | 24.2935 | 7.9742 | 7.5851 | 62.0865 | -61.7157 | -0.36621 | 0.009155 | 3.0579 | -0.18768 | -7.5073 | -0.32959 | -0.009155 | 3.4241 | 69.3604 | 68.9713 | 115.9744 | 123.4909 | 3.0579 | 123.4726 | 85.6796 | -0.32959 | 123.4909 | 3.0579 | 85.6796 | 115.9744 | 123.4726 | -123.848 | -123.8113
4440.7188 | 123.7656 | -61.4365 | 62.1231 | 0.16655 | 0.016024 | 0.014054 | 0.014242 | 0.06153 | 0.00073487 | 0.080544 | -58.3878 | 62.1597 | -61.7569 | -61.6425 | 54.5242 | 24.0372 | 8.107 | 7.4936 | 62.1368 | -61.7432 | -0.32044 | 0.036621 | 3.0487 | -0.20599 | -7.5989 | -0.3067 | 0.013733 | 3.3691 | 69.5435 | 68.9301 | 115.9607 | 123.5962 | 3.0487 | 123.5733 | 85.4736 | -0.3067 | 123.5962 | 3.0487 | 85.4736 | 115.9607 | 123.5733 | -123.88 | -123.8663
4441.7188 | 123.761 | -61.4136 | 62.1368 | 0.16655 | 0.017519 | 0.01555 | 0.016165 | 0.060675 | -0.0020421 | 0.078622 | -58.374 | 62.1597 | -61.7523 | -61.647 | 54.5105 | 24.0692 | 8.2077 | 7.5165 | 62.1552 | -61.7477 | -0.33875 | 0.022888 | 3.0396 | -0.23346 | -7.6263 | -0.33417 | 0.01831 | 3.3783 | 69.6213 | 68.9301 | 115.9241 | 123.5733 | 3.0396 | 123.5687 | 85.4828 | -0.33417 | 123.5733 | 3.0396 | 85.4828 | 115.9241 | 123.5687 | -123.8892 | -123.8846
4442.7188 | 123.6923 | -61.4319 | 62.1414 | 0.074997 | 0.016665 | 0.0132 | 0.01531 | 0.063452 | 0.00030767 | 0.079476 | -58.3923 | 62.2192 | -61.7477 | -61.6882 | 54.4601 | 23.9914 | 8.3176 | 7.489 | 62.1597 | -61.7706 | -0.31586 | 0.07782 | 3.0396 | -0.25635 | -7.6813 | -0.33874 | 0.018311 | 3.3554 | 69.7495 | 68.9209 | 115.892 | 123.6511 | 3.0396 | 123.5916 | 85.4233 | -0.33874 | 123.6511 | 3.0396 | 85.4233 | 115.892 | 123.5916 | -123.8892 | -123.912
4443.7188 | 123.8617 | -61.3861 | 62.0956 | 0.21233 | 0.017092 | 0.010636 | 0.013174 | 0.063452 | 0.00052127 | 0.078622 | -58.3191 | 62.0819 | -61.7157 | -61.5646 | 54.5654 | 24.1974 | 8.0704 | 7.6126 | 62.1094 | -61.734 | -0.32959 | -0.013733 | 3.067 | -0.17853 | -7.5302 | -0.3479 | 0.013733 | 3.3966 | 69.4565 | 68.9987 | 115.9515 | 123.468 | 3.067 | 123.4955 | 85.5835 | -0.3479 | 123.468 | 3.067 | 85.5835 | 115.9515 | 123.4955 | -123.8113 | -123.8297
4444.7188 | 123.8022 | -61.409 | 62.114 | 0.12077 | 0.01282 | 0.0078592 | 0.0093288 | 0.062812 | -0.0016149 | 0.08204 | -58.3557 | 62.0544 | -61.7523 | -61.6058 | 54.5425 | 24.1287 | 8.1207 | 7.5943 | 62.0865 | -61.7157 | -0.34332 | -0.05951 | 3.0533 | -0.19684 | -7.5714 | -0.3067 | -0.027466 | 3.3966 | 69.5297 | 69.0033 | 115.9515 | 123.4634 | 3.0533 | 123.4955 | 85.5377 | -0.3067 | 123.4634 | 3.0533 | 85.5377 | 115.9515 | 123.4955 | -123.8663 | -123.8297
4445.7188 | 123.7289 | -61.4548 | 62.1185 | 0.097885 | 0.01816 | 0.014054 | 0.014242 | 0.063452 | -0.00097413 | 0.079049 | -58.3649 | 62.1689 | -61.7294 | -61.6562 | 54.4785 | 24.1013 | 8.2031 | 7.5027 | 62.146 | -61.7798 | -0.27466 | 0.050354 | 3.0899 | -0.20142 | -7.6401 | -0.32501 | 0.027466 | 3.3646 | 69.6579 | 68.9575 | 115.9332 | 123.6237 | 3.0899 | 123.6008 | 85.556 | -0.32501 | 123.6237 | 3.0899 | 85.556 | 115.9332 | 123.6008 | -123.848 | -123.8983
4446.7188 | 123.7381 | -61.4731 | 62.1277 | 0.021591 | 0.019015 | 0.014054 | 0.015951 | 0.063239 | -0.00097413 | 0.080758 | -58.3923 | 62.1735 | -61.7569 | -61.6425 | 54.4968 | 24.1104 | 8.3908 | 7.5531 | 62.1323 | -61.7569 | -0.28381 | 0.045776 | 3.0807 | -0.16937 | -7.6309 | -0.28381 | 0.004577 | 3.3646 | 69.8639 | 69.0262 | 115.9698 | 123.6465 | 3.0807 | 123.6053 | 85.5835 | -0.28381 | 123.6465 | 3.0807 | 85.5835 | 115.9698 | 123.6053 | -123.8846 | -123.8846
4447.7188 | 123.761 | -61.4227 | 62.1323 | 0.15129 | 0.017519 | 0.012345 | 0.015097 | 0.062171 | -0.0026831 | 0.080544 | -58.3786 | 62.1918 | -61.7477 | -61.6562 | 54.5471 | 24.1928 | 8.3771 | 7.5439 | 62.1689 | -61.7569 | -0.32501 | 0.059509 | 3.0441 | -0.23346 | -7.5851 | -0.33417 | 0.036621 | 3.3691 | 69.7998 | 68.9667 | 115.9698 | 123.6145 | 3.0441 | 123.5916 | 85.6155 | -0.33417 | 123.6145 | 3.0441 | 85.6155 | 115.9698 | 123.5916 | -123.88 | -123.8892
4448.7188 | 123.7198 | -61.4456 | 62.1185 | 0.15129 | 0.015169 | 0.022172 | 0.015738 | 0.065161 | 0.00094847 | 0.07969 | -58.5434 | 62.1552 | -61.7752 | -61.6379 | 54.483 | 24.1699 | 8.4641 | 7.5348 | 62.1735 | -61.7569 | -0.32959 | 0.036621 | 2.9022 | -0.19226 | -7.6355 | -0.31128 | 0.054932 | 3.2318 | 69.9097 | 68.9804 | 115.9287 | 123.6008 | 2.9022 | 123.6191 | 85.6155 | -0.31128 | 123.6008 | 2.9022 | 85.6155 | 115.9287 | 123.6191 | -123.8937 | -123.8754
4449.7188 | 123.8434 | -61.4044 | 62.0911 | 0.19707 | 0.014315 | 0.012986 | 0.015097 | 0.063666 | 0.00030767 | 0.081185 | -58.3603 | 62.1185 | -61.7432 | -61.5921 | 54.5837 | 24.2432 | 8.2214 | 7.6584 | 62.1048 | -61.702 | -0.33875 | 0.027466 | 3.0441 | -0.18768 | -7.5073 | -0.29755 | 0.013733 | 3.3829 | 69.6259 | 69.0628 | 115.9882 | 123.5229 | 3.0441 | 123.5092 | 85.6476 | -0.29755 | 123.5229 | 3.0441 | 85.6476 | 115.9882 | 123.5092 | -123.8342 | -123.793
4450.7188 | 123.7106 | -61.4365 | 62.1048 | 0.0063326 | 0.018374 | 0.017899 | 0.014242 | 0.063239 | 0.00030767 | 0.080758 | -58.4015 | 62.1689 | -61.7661 | -61.6928 | 54.4876 | 24.1745 | 8.432 | 7.5439 | 62.1643 | -61.7798 | -0.32959 | 0.064087 | 3.035 | -0.25635 | -7.6172 | -0.34332 | 0.05951 | 3.3646 | 69.8685 | 68.9804 | 115.9241 | 123.6053 | 3.035 | 123.6008 | 85.611 | -0.34332 | 123.6053 | 3.035 | 85.611 | 115.9241 | 123.6008 | -123.8708 | -123.8846
4451.7188 | 123.8159 | -61.4456 | 62.0911 | 0.16655 | 0.015383 | 0.015122 | 0.011892 | 0.063239 | -0.00011953 | 0.080544 | -58.3694 | 62.1368 | -61.7706 | -61.647 | 54.5563 | 24.2249 | 8.2535 | 7.608 | 62.1368 | -61.7294 | -0.32501 | 0.045777 | 3.0762 | -0.20142 | -7.5348 | -0.28381 | 0.045777 | 3.4012 | 69.6991 | 69.0537 | 116.0019 | 123.5825 | 3.0762 | 123.5825 | 85.6705 | -0.28381 | 123.5825 | 3.0762 | 85.6705 | 116.0019 | 123.5825 | -123.8617 | -123.8205
4452.7344 | 123.8434 | -61.3907 | 62.1414 | -0.062332 | 0.014529 | 0.017259 | 0.005911 | 0.060675 | 0.00030767 | 0.079476 | -58.3603 | 62.059 | -61.7203 | -61.5555 | 54.6707 | 24.3576 | 8.0841 | 7.6904 | 62.1323 | -61.6608 | -0.32959 | -0.082397 | 3.0304 | -0.16479 | -7.4707 | -0.27008 | -0.009155 | 3.36 | 69.4748 | 69.0811 | 116.0614 | 123.4497 | 3.0304 | 123.5229 | 85.7483 | -0.27008 | 123.4497 | 3.0304 | 85.7483 | 116.0614 | 123.5229 | -123.8617 | -123.8022
4453.7188 | 123.7427 | -61.4502 | 62.146 | 0.15129 | 0.017947 | 0.014909 | 0.016592 | 0.063452 | 0.0022303 | 0.076699 | -58.3878 | 62.1964 | -61.7569 | -61.4227 | 54.7256 | 24.1653 | 8.2626 | 7.663 | 62.178 | -61.7706 | -0.3067 | 0.050354 | 3.0624 | 0.027466 | -7.4203 | -0.32043 | 0.032044 | 3.3691 | 69.7128 | 69.1132 | 116.1758 | 123.6465 | 3.0624 | 123.6282 | 85.6155 | -0.32043 | 123.6465 | 3.0624 | 85.6155 | 116.1758 | 123.6282 | -123.9029 | -123.9166
4454.7188 | 123.8113 | -61.3998 | 62.1277 | -0.054703 | 0.011751 | 0.0087138 | 0.00527 | 0.061316 | -0.00097413 | 0.077767 | -58.3649 | 62.0865 | -61.734 | -61.5646 | 54.6341 | 24.2981 | 8.1116 | 7.6492 | 62.1323 | -61.7157 | -0.33417 | -0.041199 | 3.035 | -0.16479 | -7.4936 | -0.31586 | 0.004577 | 3.3691 | 69.5114 | 69.0491 | 116.0339 | 123.4863 | 3.035 | 123.5321 | 85.6979 | -0.31586 | 123.4863 | 3.035 | 85.6979 | 116.0339 | 123.5321 | -123.8617 | -123.8434
4455.7188 | 123.6969 | -61.4594 | 62.1597 | 0.11314 | 0.017947 | 0.013841 | 0.015951 | 0.061316 | 0.00052127 | 0.078622 | -58.3969 | 62.2055 | -61.7294 | -61.6837 | 54.4739 | 24.1882 | 8.2535 | 7.489 | 62.1277 | -61.7935 | -0.27008 | 0.045776 | 3.0624 | -0.2243 | -7.6859 | -0.33417 | -0.032043 | 3.3325 | 69.7128 | 68.9484 | 115.9332 | 123.6649 | 3.0624 | 123.587 | 85.6476 | -0.33417 | 123.6649 | 3.0624 | 85.6476 | 115.9332 | 123.587 | -123.8892 | -123.9532
4456.7188 | 123.7335 | -61.4456 | 62.1506 | -0.016556 | 0.017092 | 0.014695 | 0.017447 | 0.063025 | -0.0011877 | 0.076486 | -58.3282 | 62.1872 | -61.7203 | -61.615 | 54.5013 | 24.2111 | 8.2123 | 7.5668 | 62.1735 | -61.7706 | -0.27466 | 0.036621 | 3.1174 | -0.16937 | -7.6492 | -0.32501 | 0.022888 | 3.392 | 69.6579 | 69.0125 | 115.947 | 123.6328 | 3.1174 | 123.6191 | 85.6567 | -0.32501 | 123.6328 | 3.1174 | 85.6567 | 115.947 | 123.6191 | -123.8708 | -123.9212
4457.7344 | 123.8663 | -61.3907 | 62.1185 | -0.047073 | 0.012179 | 0.011491 | 0.0054836 | 0.061957 | -0.00076053 | 0.079263 | -58.3694 | 62.0865 | -61.7249 | -61.5692 | 54.6158 | 24.3118 | 8.1345 | 7.6721 | 62.146 | -61.6791 | -0.33417 | -0.032043 | 3.0212 | -0.17853 | -7.5027 | -0.28839 | 0.027466 | 3.3554 | 69.5251 | 69.0628 | 116.0065 | 123.4772 | 3.0212 | 123.5367 | 85.7025 | -0.28839 | 123.4772 | 3.0212 | 85.7025 | 116.0065 | 123.5367 | -123.8434 | -123.7976
4458.7188 | 123.6923 | -61.4777 | 62.1506 | 0.067368 | 0.019656 | 0.016404 | 0.014883 | 0.062384 | 0.00073487 | 0.078408 | -58.3832 | 62.2009 | -61.7386 | -61.6974 | 54.4739 | 24.1837 | 8.2718 | 7.5302 | 62.1414 | -61.7889 | -0.26093 | 0.050354 | 3.0945 | -0.21973 | -7.6767 | -0.31128 | -0.009156 | 3.3554 | 69.7495 | 69.0079 | 115.9515 | 123.6786 | 3.0945 | 123.6191 | 85.6613 | -0.31128 | 123.6786 | 3.0945 | 85.6613 | 115.9515 | 123.6191 | -123.8892 | -123.9395
4459.7344 | 123.7793 | -61.3953 | 62.1048 | 0.15129 | 0.015597 | 0.012132 | 0.0074062 | 0.061316 | -0.00033333 | 0.080117 | -58.3603 | 62.0728 | -61.7432 | -61.6104 | 54.5288 | 24.2294 | 8.0978 | 7.6035 | 62.1185 | -61.7249 | -0.3479 | -0.032043 | 3.035 | -0.21515 | -7.576 | -0.32959 | 0.013733 | 3.3829 | 69.4931 | 68.9987 | 115.9241 | 123.468 | 3.035 | 123.5138 | 85.6247 | -0.32959 | 123.468 | 3.035 | 85.6247 | 115.9241 | 123.5138 | -123.848 | -123.8297
4460.7188 | 123.7106 | -61.4548 | 62.1689 | 0.074997 | 0.016024 | 0.013841 | 0.017447 | 0.06153 | 9.4068e-05 | 0.078622 | -58.3511 | 62.1826 | -61.7432 | -61.6791 | 54.451 | 24.1379 | 8.2031 | 7.4799 | 62.178 | -61.7752 | -0.28839 | 0.013733 | 3.1036 | -0.2243 | -7.7179 | -0.32043 | 0.009156 | 3.392 | 69.6579 | 68.9346 | 115.9058 | 123.6374 | 3.1036 | 123.6328 | 85.5927 | -0.32043 | 123.6374 | 3.1036 | 85.5927 | 115.9058 | 123.6328 | -123.912 | -123.9441
4461.7188 | 123.7198 | -61.4456 | 62.1323 | 0.021591 | 0.017947 | 0.014909 | 0.01766 | 0.063452 | -0.00033333 | 0.077981 | -58.3054 | 62.1918 | -61.7615 | -61.647 | 54.4968 | 24.202 | 8.226 | 7.5485 | 62.1735 | -61.7523 | -0.31586 | 0.059509 | 3.1403 | -0.20142 | -7.6355 | -0.3067 | 0.041199 | 3.4561 | 69.6716 | 68.9941 | 115.9424 | 123.6374 | 3.1403 | 123.6191 | 85.6476 | -0.3067 | 123.6374 | 3.1403 | 85.6476 | 115.9424 | 123.6191 | -123.8937 | -123.8846
4462.7344 | 123.8113 | -61.4136 | 62.1002 | 0.013962 | 0.013033 | 0.0078592 | 0.0046292 | 0.062812 | 0.0011621 | 0.080117 | -58.342 | 62.0773 | -61.7477 | -61.5784 | 54.5609 | 24.2386 | 8.2352 | 7.663 | 62.1231 | -61.7111 | -0.33417 | -0.022888 | 3.0716 | -0.1648 | -7.5394 | -0.29755 | 0.022888 | 3.4058 | 69.6487 | 69.0765 | 115.9744 | 123.4909 | 3.0716 | 123.5367 | 85.6522 | -0.29755 | 123.4909 | 3.0716 | 85.6522 | 115.9744 | 123.5367 | -123.848 | -123.8113
4463.7188 | 123.7564 | -61.4365 | 62.1689 | -0.047073 | 0.017092 | 0.016404 | 0.01531 | 0.063452 | -0.00033333 | 0.076913 | -58.2779 | 62.1826 | -61.7386 | -61.5555 | 54.4464 | 24.2157 | 8.2947 | 7.6447 | 62.1552 | -61.7752 | -0.30212 | 0.013733 | 3.1586 | -0.11902 | -7.7225 | -0.33875 | -0.013733 | 3.4607 | 69.7311 | 69.0811 | 115.8829 | 123.6191 | 3.1586 | 123.5916 | 85.6522 | -0.33875 | 123.6191 | 3.1586 | 85.6522 | 115.8829 | 123.5916 | -123.9075 | -123.9441
4464.7188 | 123.7701 | -61.4227 | 62.1231 | 0.1284 | 0.016878 | 0.018968 | 0.014669 | 0.061316 | 0.00030767 | 0.077981 | -58.3374 | 62.1643 | -61.7523 | -61.6425 | 54.4464 | 24.2432 | 8.1757 | 7.5531 | 62.1323 | -61.7477 | -0.32959 | 0.041199 | 3.0853 | -0.21973 | -7.6767 | -0.32501 | 0.009155 | 3.4149 | 69.5984 | 68.9758 | 115.8691 | 123.587 | 3.0853 | 123.555 | 85.6659 | -0.32501 | 123.587 | 3.0853 | 85.6659 | 115.8691 | 123.555 | -123.8754 | -123.8709
4465.7188 | 123.7198 | -61.4319 | 62.1506 | 0.029221 | 0.016878 | 0.013413 | 0.015951 | 0.065375 | -0.00097413 | 0.080758 | -58.3099 | 62.2009 | -61.7294 | -61.647 | 54.4693 | 24.2065 | 8.226 | 7.5256 | 62.178 | -61.7706 | -0.29755 | 0.050354 | 3.1219 | -0.21515 | -7.6813 | -0.33874 | 0.027466 | 3.4195 | 69.6579 | 68.9575 | 115.9012 | 123.6328 | 3.1219 | 123.6099 | 85.6384 | -0.33874 | 123.6328 | 3.1219 | 85.6384 | 115.9012 | 123.6099 | -123.88 | -123.9212
4466.7188 | 123.7289 | -61.4456 | 62.1506 | 0.059738 | 0.018587 | 0.017899 | 0.016165 | 0.063666 | 9.4068e-05 | 0.080331 | -58.2916 | 62.1964 | -61.7294 | -61.6379 | 54.4739 | 24.2889 | 8.194 | 7.5485 | 62.1826 | -61.7523 | -0.28381 | 0.045776 | 3.154 | -0.19226 | -7.6767 | -0.3067 | 0.032043 | 3.4378 | 69.6396 | 68.9941 | 115.9195 | 123.642 | 3.154 | 123.6282 | 85.7346 | -0.3067 | 123.642 | 3.154 | 85.7346 | 115.9195 | 123.6282 | -123.88 | -123.9029
4467.7344 | 123.8434 | -61.3861 | 62.1185 | -0.16914 | 0.01346 | 0.015122 | 0.0063382 | 0.06153 | 9.4068e-05 | 0.079263 | -58.3054 | 62.0819 | -61.7294 | -61.528 | 54.6158 | 24.3759 | 8.107 | 7.7042 | 62.1552 | -61.6653 | -0.34332 | -0.036621 | 3.0807 | -0.14191 | -7.5027 | -0.27924 | 0.036621 | 3.4241 | 69.4931 | 69.0903 | 116.0019 | 123.468 | 3.0807 | 123.5413 | 85.762 | -0.27924 | 123.468 | 3.0807 | 85.762 | 116.0019 | 123.5413 | -123.848 | -123.7839
4468.7188 | 123.7198 | -61.441 | 62.1643 | -0.0012969 | 0.017519 | 0.017472 | 0.016592 | 0.063239 | 0.00030767 | 0.080972 | -58.255 | 62.1872 | -61.734 | -61.6196 | 54.4693 | 24.2065 | 8.1482 | 7.5302 | 62.1643 | -61.7523 | -0.29297 | 0.022888 | 3.186 | -0.17853 | -7.695 | -0.31128 | 0 | 3.479 | 69.5892 | 68.9713 | 115.9103 | 123.6282 | 3.186 | 123.6053 | 85.6476 | -0.31128 | 123.6282 | 3.186 | 85.6476 | 115.9103 | 123.6053 | -123.8983 | -123.9166
4469.7188 | 123.8022 | -61.4182 | 62.1185 | 0.067368 | 0.015169 | 0.011704 | 0.010824 | 0.064093 | -0.0018285 | 0.081399 | -58.3237 | 62.1002 | -61.7157 | -61.6196 | 54.5288 | 24.2752 | 8.0063 | 7.5851 | 62.146 | -61.7111 | -0.29755 | -0.01831 | 3.0945 | -0.20142 | -7.5897 | -0.29297 | 0.027466 | 3.392 | 69.4244 | 69.0033 | 115.947 | 123.5184 | 3.0945 | 123.5641 | 85.6934 | -0.29297 | 123.5184 | 3.0945 | 85.6934 | 115.947 | 123.5641 | -123.8342 | -123.8297
4470.7188 | 123.793 | -61.4136 | 62.1506 | -0.17677 | 0.016665 | 0.015763 | 0.019156 | 0.060889 | -0.00076053 | 0.078195 | -58.2825 | 62.1689 | -61.7294 | -61.5784 | 54.5563 | 24.3027 | 8.1802 | 7.6035 | 62.1597 | -61.7523 | -0.31586 | 0.01831 | 3.1311 | -0.1648 | -7.5943 | -0.33875 | 0.009155 | 3.447 | 69.5938 | 69.017 | 115.9698 | 123.5825 | 3.1311 | 123.5733 | 85.7162 | -0.33875 | 123.5825 | 3.1311 | 85.7162 | 115.9698 | 123.5733 | -123.88 | -123.9029
4471.7188 | 123.7427 | -61.4227 | 62.146 | -0.15388 | 0.01581 | 0.01854 | 0.016378 | 0.061957 | 0.00094847 | 0.079476 | -58.2825 | 62.1918 | -61.7432 | -61.6013 | 54.5013 | 24.2523 | 8.139 | 7.5531 | 62.1643 | -61.7523 | -0.32044 | 0.045776 | 3.1403 | -0.17853 | -7.6447 | -0.32959 | 0.018311 | 3.4607 | 69.5618 | 68.9758 | 115.9241 | 123.6145 | 3.1403 | 123.587 | 85.675 | -0.32959 | 123.6145 | 3.1403 | 85.675 | 115.9241 | 123.587 | -123.8892 | -123.8983
4472.7188 | 123.8525 | -61.3907 | 62.1277 | -0.10811 | 0.014742 | 0.014054 | 0.005911 | 0.064307 | 0.0011621 | 0.080331 | -58.3008 | 62.1368 | -61.7065 | -61.5555 | 54.6433 | 24.3576 | 8.0521 | 7.663 | 62.1368 | -61.7294 | -0.31586 | 0.009155 | 3.0899 | -0.16479 | -7.4844 | -0.33874 | 0.009155 | 3.4058 | 69.4427 | 69.0537 | 116.0339 | 123.5275 | 3.0899 | 123.5275 | 85.7483 | -0.33874 | 123.5275 | 3.0899 | 85.7483 | 116.0339 | 123.5275 | -123.8342 | -123.8571
4473.7188 | 123.7244 | -61.4365 | 62.1552 | -0.0089264 | 0.016665 | 0.014268 | 0.014883 | 0.061316 | 0.00030767 | 0.081185 | -58.3466 | 62.2055 | -61.7661 | -61.6196 | 54.4785 | 24.2294 | 8.1711 | 7.5348 | 62.1506 | -61.7752 | -0.32959 | 0.050354 | 3.0899 | -0.18311 | -7.6767 | -0.33875 | -0.004577 | 3.4195 | 69.6075 | 68.9713 | 115.9149 | 123.642 | 3.0899 | 123.587 | 85.6659 | -0.33875 | 123.642 | 3.0899 | 85.6659 | 115.9149 | 123.587 | -123.9212 | -123.9304
4474.7188 | 123.8205 | -61.409 | 62.0911 | 0.097885 | 0.016238 | 0.0132 | 0.014669 | 0.063239 | -0.00033333 | 0.07969 | -58.3511 | 62.114 | -61.7477 | -61.5738 | 54.5654 | 24.3118 | 8.0795 | 7.6401 | 62.1002 | -61.734 | -0.33875 | 0.022889 | 3.0579 | -0.16479 | -7.5256 | -0.32501 | 0.009156 | 3.3966 | 69.4885 | 69.0491 | 115.9744 | 123.523 | 3.0579 | 123.5092 | 85.7208 | -0.32501 | 123.523 | 3.0579 | 85.7208 | 115.9744 | 123.5092 | -123.8388 | -123.8251
4475.7188 | 123.7564 | -61.4182 | 62.1597 | -0.016556 | 0.017519 | 0.012559 | 0.01531 | 0.06388 | -0.00011953 | 0.080117 | -58.2916 | 62.1918 | -61.7203 | -61.6104 | 54.5334 | 24.2523 | 8.2031 | 7.5806 | 62.1552 | -61.7752 | -0.30212 | 0.032043 | 3.1265 | -0.19226 | -7.6263 | -0.35706 | -0.004578 | 3.4286 | 69.6213 | 68.9987 | 115.9515 | 123.6099 | 3.1265 | 123.5733 | 85.6705 | -0.35706 | 123.6099 | 3.1265 | 85.6705 | 115.9515 | 123.5733 | -123.88 | -123.9349
4476.7188 | 123.7564 | -61.4182 | 62.1368 | -0.039444 | 0.017733 | 0.018113 | 0.016806 | 0.062812 | -0.0018285 | 0.078195 | -58.287 | 62.2101 | -61.734 | -61.5738 | 54.5105 | 24.2752 | 8.2031 | 7.5943 | 62.1918 | -61.7386 | -0.31586 | 0.073242 | 3.1311 | -0.15564 | -7.6263 | -0.32043 | 0.054931 | 3.447 | 69.6213 | 69.0125 | 115.9287 | 123.6282 | 3.1311 | 123.6099 | 85.6934 | -0.32043 | 123.6282 | 3.1311 | 85.6934 | 115.9287 | 123.6099 | -123.8708 | -123.8754
4477.7188 | 123.7656 | -61.4136 | 62.1277 | -0.016556 | 0.016665 | 0.015122 | 0.015951 | 0.06388 | -0.0026831 | 0.079263 | -58.2642 | 62.2284 | -61.7294 | -61.5738 | 54.4968 | 24.234 | 8.2443 | 7.6218 | 62.2055 | -61.7386 | -0.31586 | 0.10071 | 3.1494 | -0.16022 | -7.6309 | -0.32501 | 0.077819 | 3.4653 | 69.6579 | 69.0353 | 115.9103 | 123.642 | 3.1494 | 123.6191 | 85.6476 | -0.32501 | 123.642 | 3.1494 | 85.6476 | 115.9103 | 123.6191 | -123.8571 | -123.8663
4478.7188 | 123.7473 | -61.409 | 62.1872 | -0.062332 | 0.014956 | 0.020463 | 0.014242 | 0.061743 | 0.00094847 | 0.078835 | -58.4702 | 62.1826 | -61.7661 | -61.5921 | 54.4968 | 24.2386 | 8.2535 | 7.6126 | 62.1597 | -61.7569 | -0.35706 | -0.004578 | 2.9388 | -0.1831 | -7.6904 | -0.3479 | -0.027466 | 3.2959 | 69.6625 | 69.0216 | 115.9058 | 123.5916 | 2.9388 | 123.5687 | 85.6476 | -0.3479 | 123.5916 | 2.9388 | 85.6476 | 115.9058 | 123.5687 | -123.9532 | -123.9441
4479.7344 | 123.8205 | -61.3907 | 62.1185 | 0.18944 | 0.01346 | 0.014909 | 0.0054836 | 0.062598 | 9.4068e-05 | 0.08204 | -58.3191 | 62.0956 | -61.7615 | -61.6058 | 54.5013 | 24.321 | 8.1207 | 7.6447 | 62.1323 | -61.702 | -0.37079 | -0.022888 | 3.0716 | -0.21515 | -7.6172 | -0.31128 | 0.013733 | 3.4424 | 69.5114 | 69.0353 | 115.892 | 123.4863 | 3.0716 | 123.5229 | 85.7117 | -0.31128 | 123.4863 | 3.0716 | 85.7117 | 115.892 | 123.5229 | -123.88 | -123.8205
4480.7188 | 123.7518 | -61.4273 | 62.146 | -0.054703 | 0.016451 | 0.013627 | 0.014669 | 0.063666 | 0.0018031 | 0.080972 | -58.2779 | 62.2055 | -61.7249 | -61.6104 | 54.4922 | 24.2661 | 8.2306 | 7.5897 | 62.1506 | -61.7752 | -0.29755 | 0.059509 | 3.1494 | -0.18311 | -7.6538 | -0.3479 | 0.004578 | 3.447 | 69.6579 | 69.017 | 115.9195 | 123.6328 | 3.1494 | 123.5779 | 85.6934 | -0.3479 | 123.6328 | 3.1494 | 85.6934 | 115.9195 | 123.5779 | -123.8708 | -123.9212
4481.7188 | 123.7198 | -61.4365 | 62.1597 | 0.04448 | 0.017519 | 0.012345 | 0.016806 | 0.06388 | 0.0011621 | 0.077767 | -58.3282 | 62.1918 | -61.7523 | -61.6516 | 54.4556 | 24.1928 | 8.2855 | 7.5531 | 62.1689 | -61.7569 | -0.31586 | 0.032043 | 3.1082 | -0.21515 | -7.7042 | -0.32044 | 0.009155 | 3.4241 | 69.722 | 68.9896 | 115.892 | 123.6282 | 3.1082 | 123.6053 | 85.6293 | -0.32044 | 123.6282 | 3.1082 | 85.6293 | 115.892 | 123.6053 | -123.912 | -123.9166
4482.7188 | 123.7747 | -61.4273 | 62.1552 | 0.79216 | 0.016878 | 0.013413 | 0.016165 | 0.065375 | -0.0024695 | 0.07969 | -58.1589 | 62.1964 | -61.7203 | -61.5967 | 54.4968 | 24.2935 | 8.2626 | 7.6401 | 62.1918 | -61.7523 | -0.29297 | 0.041199 | 3.2684 | -0.16937 | -7.6584 | -0.32501 | 0.036621 | 3.5614 | 69.6899 | 69.0674 | 115.9241 | 123.6237 | 3.2684 | 123.6191 | 85.7208 | -0.32501 | 123.6237 | 3.2684 | 85.7208 | 115.9241 | 123.6191 | -123.8754 | -123.9075
4483.7188 | 123.7656 | -61.3953 | 62.1826 | -0.2607 | 0.014956 | 0.014695 | 0.014029 | 0.063666 | 0.00073487 | 0.079263 | -58.3054 | 62.2101 | -61.7203 | -61.5784 | 54.5151 | 24.2752 | 8.3313 | 7.6492 | 62.1597 | -61.7477 | -0.32501 | 0.027466 | 3.0899 | -0.18311 | -7.6675 | -0.35248 | -0.022888 | 3.4149 | 69.7266 | 69.0445 | 115.9103 | 123.6053 | 3.0899 | 123.555 | 85.6705 | -0.35248 | 123.6053 | 3.0899 | 85.6705 | 115.9103 | 123.555 | -123.9029 | -123.9304
4484.7344 | 123.8068 | -61.3998 | 62.1002 | 0.13603 | 0.015169 | 0.0099954 | 0.0091152 | 0.060675 | -0.00054693 | 0.081399 | -58.3237 | 62.1002 | -61.734 | -61.6058 | 54.5151 | 24.3759 | 8.139 | 7.6767 | 62.1368 | -61.7203 | -0.33417 | 0 | 3.0762 | -0.20599 | -7.5851 | -0.32043 | 0.036621 | 3.4103 | 69.5389 | 69.0765 | 115.9149 | 123.5001 | 3.0762 | 123.5367 | 85.7758 | -0.32043 | 123.5001 | 3.0762 | 85.7758 | 115.9149 | 123.5367 | -123.8342 | -123.8205
4485.7188 | 123.7518 | -61.4182 | 62.1552 | -0.22255 | 0.016878 | 0.012559 | 0.014883 | 0.06153 | -0.00054693 | 0.07969 | -58.2733 | 62.2009 | -61.7523 | -61.6013 | 54.483 | 24.3027 | 8.2855 | 7.6309 | 62.1506 | -61.7661 | -0.33417 | 0.045777 | 3.1448 | -0.1831 | -7.6721 | -0.3479 | -0.004577 | 3.479 | 69.7037 | 69.0491 | 115.9012 | 123.6191 | 3.1448 | 123.5687 | 85.7208 | -0.3479 | 123.6191 | 3.1448 | 85.7208 | 115.9012 | 123.5687 | -123.9075 | -123.9212
4486.7188 | 123.7839 | -61.4319 | 62.178 | -0.016556 | 0.022005 | 0.01555 | 0.014883 | 0.062171 | -0.00033333 | 0.079263 | -58.3603 | 62.1735 | -61.7477 | -61.5784 | 54.4876 | 24.321 | 8.3496 | 7.6767 | 62.1643 | -61.7706 | -0.31586 | -0.004578 | 3.0716 | -0.14648 | -7.6904 | -0.33874 | -0.013733 | 3.3875 | 69.7815 | 69.1086 | 115.9195 | 123.6053 | 3.0716 | 123.5962 | 85.7529 | -0.33874 | 123.6053 | 3.0716 | 85.7529 | 115.9195 | 123.5962 | -123.9258 | -123.9487
4487.7188 | 123.7656 | -61.441 | 62.1597 | -0.12337 | 0.016024 | 0.017899 | 0.012533 | 0.064093 | 0.0041529 | 0.076699 | -58.2779 | 62.1964 | -61.7249 | -61.6379 | 54.6295 | 24.2661 | 8.1024 | 7.5851 | 62.2009 | -61.734 | -0.28381 | 0.036621 | 3.1631 | -0.19684 | -7.5302 | -0.29297 | 0.041199 | 3.447 | 69.5435 | 69.0262 | 116.0706 | 123.6374 | 3.1631 | 123.642 | 85.7071 | -0.29297 | 123.6374 | 3.1631 | 85.7071 | 116.0706 | 123.642 | -123.8846 | -123.8937
4488.7188 | 123.8159 | -61.4273 | 62.1552 | -0.077591 | 0.017947 | 0.012559 | 0.014456 | 0.064521 | -0.00076053 | 0.079263 | -58.2916 | 62.1918 | -61.7203 | -61.5829 | 54.483 | 24.353 | 7.9834 | 7.5119 | 62.1872 | -61.7477 | -0.29297 | 0.036621 | 3.1357 | -0.15564 | -7.6721 | -0.32044 | 0.032044 | 3.4286 | 69.4107 | 68.9392 | 115.9103 | 123.6191 | 3.1357 | 123.6145 | 85.7803 | -0.32044 | 123.6191 | 3.1357 | 85.7803 | 115.9103 | 123.6145 | -123.8754 | -123.9029
4489.7188 | 123.7381 | -61.4594 | 62.1002 | 0.13603 | 0.018801 | 0.011918 | 0.014242 | 0.062598 | -0.0028967 | 0.081826 | -58.3649 | 62.1964 | -61.7477 | -61.6608 | 54.483 | 24.2981 | 7.8598 | 7.4432 | 62.1826 | -61.7386 | -0.28839 | 0.09613 | 3.0945 | -0.20142 | -7.6172 | -0.27923 | 0.082397 | 3.3829 | 69.3192 | 68.9026 | 115.9424 | 123.6557 | 3.0945 | 123.642 | 85.7574 | -0.27923 | 123.6557 | 3.0945 | 85.7574 | 115.9424 | 123.642 | -123.848 | -123.8388
4490.7188 | 123.7747 | -61.4227 | 62.1735 | -0.13863 | 0.016878 | 0.015763 | 0.013815 | 0.062812 | 0.00094847 | 0.079263 | -58.3282 | 62.2101 | -61.7294 | -61.5921 | 54.5563 | 24.3484 | 7.8232 | 7.4615 | 62.1918 | -61.7477 | -0.3067 | 0.036621 | 3.0945 | -0.16937 | -7.6172 | -0.32501 | 0.01831 | 3.4012 | 69.2459 | 68.8843 | 115.979 | 123.6328 | 3.0945 | 123.6145 | 85.7712 | -0.32501 | 123.6328 | 3.0945 | 85.7712 | 115.979 | 123.6145 | -123.9029 | -123.9212
4491.7188 | 123.7701 | -61.4456 | 62.178 | -0.17677 | 0.01816 | 0.0132 | 0.012533 | 0.062812 | -0.0033239 | 0.078622 | -58.2916 | 62.2238 | -61.7203 | -61.5921 | 54.5471 | 24.3576 | 7.6401 | 7.489 | 62.2055 | -61.7249 | -0.27466 | 0.045776 | 3.154 | -0.14648 | -7.6309 | -0.27924 | 0.027465 | 3.4286 | 69.0857 | 68.9346 | 115.9927 | 123.6694 | 3.154 | 123.6511 | 85.8032 | -0.27924 | 123.6694 | 3.154 | 85.8032 | 115.9927 | 123.6511 | -123.8983 | -123.9029
4492.7188 | 123.7747 | -61.4136 | 62.1643 | -0.131 | 0.016238 | 0.017045 | 0.013601 | 0.064521 | -0.0014013 | 0.080331 | -58.2779 | 62.1552 | -61.7294 | -61.6104 | 54.4739 | 24.3622 | 7.4615 | 7.4203 | 62.2101 | -61.7386 | -0.31586 | -0.009156 | 3.1357 | -0.19684 | -7.6904 | -0.32501 | 0.045776 | 3.4515 | 68.8751 | 68.8339 | 115.8875 | 123.5687 | 3.1357 | 123.6237 | 85.7758 | -0.32501 | 123.5687 | 3.1357 | 85.7758 | 115.8875 | 123.6237 | -123.8937 | -123.9029
4493.7188 | 123.761 | -61.4319 | 62.1826 | -0.031814 | 0.015597 | 0.013841 | 0.014669 | 0.066016 | 0.00052127 | 0.079476 | -58.2825 | 62.2009 | -61.7294 | -61.5463 | 54.5288 | 24.3301 | 7.5577 | 7.3746 | 62.1597 | -61.7477 | -0.29755 | 0.018311 | 3.1494 | -0.11444 | -7.6538 | -0.31586 | -0.022888 | 3.447 | 68.9896 | 68.8065 | 115.9607 | 123.6328 | 3.1494 | 123.5916 | 85.762 | -0.31586 | 123.6328 | 3.1494 | 85.762 | 115.9607 | 123.5916 | -123.912 | -123.9304
4494.7188 | 123.7473 | -61.4227 | 62.1277 | 0.17418 | 0.016451 | 0.015122 | 0.010611 | 0.063025 | -0.00054693 | 0.079049 | -58.374 | 62.1735 | -61.7661 | -61.6745 | 54.4876 | 24.3439 | 7.7087 | 7.4295 | 62.1643 | -61.7661 | -0.34332 | 0.045776 | 3.0487 | -0.25177 | -7.6401 | -0.34332 | 0.036621 | 3.392 | 69.1315 | 68.8522 | 115.9103 | 123.5962 | 3.0487 | 123.587 | 85.7666 | -0.34332 | 123.5962 | 3.0487 | 85.7666 | 115.9103 | 123.587 | -123.8937 | -123.8937
4495.7188 | 123.6374 | -61.4273 | 62.1552 | -0.09285 | 0.016451 | 0.015977 | 0.01531 | 0.064521 | 9.4068e-05 | 0.080331 | -58.2962 | 62.2147 | -61.734 | -61.6058 | 54.5288 | 24.3851 | 7.8094 | 7.489 | 62.1872 | -61.7661 | -0.3067 | 0.05951 | 3.1311 | -0.17853 | -7.6263 | -0.33875 | 0.032044 | 3.4378 | 69.2368 | 68.9163 | 115.9561 | 123.642 | 3.1311 | 123.6145 | 85.8124 | -0.33875 | 123.642 | 3.1311 | 85.8124 | 115.9561 | 123.6145 | -123.8892 | -123.9212
4496.7188 | 123.7564 | -61.4182 | 62.1552 | -0.21492 | 0.019869 | 0.011277 | 0.011251 | 0.065161 | -0.00097413 | 0.078835 | -58.2962 | 62.2147 | -61.7294 | -61.5967 | 54.5425 | 24.4308 | 7.7454 | 7.4753 | 62.2238 | -61.7432 | -0.31128 | 0.05951 | 3.1219 | -0.17853 | -7.6126 | -0.32501 | 0.068665 | 3.4332 | 69.1635 | 68.8934 | 115.9607 | 123.6328 | 3.1219 | 123.642 | 85.849 | -0.32501 | 123.6328 | 3.1219 | 85.849 | 115.9607 | 123.642 | -123.8846 | -123.8983
4497.7188 | 123.7656 | -61.4365 | 62.1689 | -0.17677 | 0.016665 | 0.010209 | 0.0097562 | 0.062171 | 0.0018031 | 0.079049 | -58.3145 | 62.2192 | -61.7477 | -61.5875 | 54.5105 | 24.3896 | 7.8461 | 7.4478 | 62.2147 | -61.7386 | -0.31128 | 0.050354 | 3.1219 | -0.15106 | -7.6584 | -0.30212 | 0.045777 | 3.4332 | 69.2825 | 68.8843 | 115.947 | 123.6557 | 3.1219 | 123.6511 | 85.8261 | -0.30212 | 123.6557 | 3.1219 | 85.8261 | 115.947 | 123.6511 | -123.9166 | -123.9075
4498.7188 | 123.7656 | -61.4044 | 62.1643 | -0.16151 | 0.016024 | 0.014268 | 0.01232 | 0.063239 | -0.00076053 | 0.078622 | -58.3328 | 62.2192 | -61.7477 | -61.6196 | 54.4739 | 24.321 | 7.8964 | 7.4524 | 62.2284 | -61.7294 | -0.34332 | 0.054931 | 3.0716 | -0.21515 | -7.6904 | -0.32501 | 0.064087 | 3.4149 | 69.3008 | 68.8568 | 115.8783 | 123.6237 | 3.0716 | 123.6328 | 85.7254 | -0.32501 | 123.6237 | 3.0716 | 85.7254 | 115.8783 | 123.6328 | -123.912 | -123.8937
4499.7344 | 123.7885 | -61.4227 | 62.0728 | 0.18181 | 0.01581 | 0.013841 | 0.010183 | 0.06388 | 0.00052127 | 0.079263 | -58.2779 | 62.1231 | -61.7477 | -61.5875 | 54.5425 | 24.44 | 7.7499 | 7.5623 | 62.1323 | -61.6837 | -0.32501 | 0.050354 | 3.1448 | -0.1648 | -7.5302 | -0.26093 | 0.059509 | 3.4698 | 69.1727 | 68.985 | 115.9653 | 123.5458 | 3.1448 | 123.555 | 85.8627 | -0.26093 | 123.5458 | 3.1448 | 85.8627 | 115.9653 | 123.555 | -123.8205 | -123.7564
4500.7188 | 123.7656 | -61.4136 | 62.1368 | 0.94475 | 0.016024 | 0.016191 | 0.014669 | 0.062384 | -0.0014013 | 0.078622 | -58.1635 | 62.178 | -61.7477 | -61.5921 | 54.538 | 24.4263 | 7.9697 | 7.5577 | 62.1918 | -61.7386 | -0.33417 | 0.041199 | 3.2501 | -0.17853 | -7.5989 | -0.32501 | 0.054931 | 3.5843 | 69.3832 | 68.9713 | 115.9515 | 123.5916 | 3.2501 | 123.6053 | 85.8398 | -0.32501 | 123.5916 | 3.2501 | 85.8398 | 115.9515 | 123.6053 | -123.8846 | -123.8754
4501.7188 | 123.7701 | -61.4182 | 62.1552 | -0.047073 | 0.014742 | 0.016191 | 0.016165 | 0.065589 | 9.4068e-05 | 0.079904 | -58.461 | 62.1689 | -61.734 | -61.6013 | 54.5151 | 24.3668 | 7.9193 | 7.5394 | 62.2147 | -61.7523 | -0.31586 | 0.013733 | 2.9572 | -0.1831 | -7.6401 | -0.33417 | 0.05951 | 3.273 | 69.3375 | 68.9575 | 115.9332 | 123.587 | 2.9572 | 123.6328 | 85.7849 | -0.33417 | 123.587 | 2.9572 | 85.7849 | 115.9332 | 123.6328 | -123.8892 | -123.9075
4502.7188 | 123.7656 | -61.4136 | 62.1643 | -0.09285 | 0.016238 | 0.017686 | 0.014669 | 0.063239 | 0.00094847 | 0.079476 | -58.4793 | 62.1643 | -61.7569 | -61.5829 | 54.4647 | 24.3668 | 7.9468 | 7.5439 | 62.1826 | -61.7477 | -0.34332 | 0 | 2.9343 | -0.16937 | -7.6996 | -0.33417 | 0.01831 | 3.2776 | 69.3604 | 68.9575 | 115.8783 | 123.5779 | 2.9343 | 123.5962 | 85.7803 | -0.33417 | 123.5779 | 2.9343 | 85.7803 | 115.8783 | 123.5962 | -123.9212 | -123.912
4503.7188 | 123.7198 | -61.4136 | 62.1643 | -0.0089264 | 0.017947 | 0.017899 | 0.013388 | 0.064948 | -0.0016149 | 0.077981 | -58.2733 | 62.2009 | -61.734 | -61.6287 | 54.4693 | 24.3759 | 7.9514 | 7.5027 | 62.1735 | -61.7661 | -0.32044 | 0.036621 | 3.1403 | -0.21515 | -7.695 | -0.35248 | 0.009155 | 3.4607 | 69.3649 | 68.9163 | 115.8829 | 123.6145 | 3.1403 | 123.587 | 85.7895 | -0.35248 | 123.6145 | 3.1403 | 85.7895 | 115.8829 | 123.587 | -123.8983 | -123.9304
4504.7188 | 123.7656 | -61.3907 | 62.1552 | -0.17677 | 0.017519 | 0.014268 | 0.014669 | 0.064734 | 9.4068e-05 | 0.080117 | -58.255 | 62.2147 | -61.7386 | -61.5829 | 54.5242 | 24.4171 | 7.8506 | 7.5165 | 62.2192 | -61.7157 | -0.3479 | 0.05951 | 3.1357 | -0.19226 | -7.6309 | -0.32501 | 0.064087 | 3.4836 | 69.2413 | 68.9072 | 115.9149 | 123.6053 | 3.1357 | 123.6099 | 85.8078 | -0.32501 | 123.6053 | 3.1357 | 85.8078 | 115.9149 | 123.6099 | -123.8937 | -123.8708
4505.7188 | 123.7701 | -61.4273 | 62.1414 | -0.024185 | 0.016238 | 0.014054 | 0.014883 | 0.064734 | -0.0014013 | 0.080758 | -58.2962 | 62.2192 | -61.7432 | -61.6379 | 54.4373 | 24.4446 | 7.9514 | 7.4936 | 62.1735 | -61.7386 | -0.31586 | 0.07782 | 3.1311 | -0.21057 | -7.7042 | -0.31128 | 0.032044 | 3.447 | 69.3787 | 68.9209 | 115.8646 | 123.6465 | 3.1311 | 123.6008 | 85.8719 | -0.31128 | 123.6465 | 3.1311 | 85.8719 | 115.8646 | 123.6008 | -123.8846 | -123.88
4506.7188 | 123.7335 | -61.4273 | 62.1552 | -0.031814 | 0.017306 | 0.01555 | 0.014029 | 0.064521 | 0.00052127 | 0.078195 | -58.3054 | 62.1964 | -61.734 | -61.6379 | 54.5151 | 24.4308 | 7.933 | 7.4524 | 62.1918 | -61.7523 | -0.3067 | 0.041199 | 3.1219 | -0.21057 | -7.6401 | -0.32501 | 0.036621 | 3.4286 | 69.3604 | 68.8797 | 115.9424 | 123.6237 | 3.1219 | 123.6191 | 85.8582 | -0.32501 | 123.6237 | 3.1219 | 85.8582 | 115.9424 | 123.6191 | -123.8892 | -123.9075
4507.7188 | 123.7427 | -61.4227 | 62.1323 | 0.021591 | 0.015169 | 0.013841 | 0.015097 | 0.066016 | 9.4068e-05 | 0.081826 | -58.3099 | 62.2192 | -61.7523 | -61.6333 | 54.4647 | 24.4629 | 7.9056 | 7.4432 | 62.1872 | -61.7569 | -0.32959 | 0.086975 | 3.1128 | -0.21057 | -7.6675 | -0.33417 | 0.054932 | 3.4424 | 69.3283 | 68.866 | 115.8875 | 123.642 | 3.1128 | 123.6099 | 85.8856 | -0.33417 | 123.642 | 3.1128 | 85.8856 | 115.8875 | 123.6099 | -123.8846 | -123.8892
4508.7188 | 123.7518 | -61.4182 | 62.1506 | -0.0012969 | 0.017306 | 0.016831 | 0.01531 | 0.064521 | -0.00076053 | 0.078195 | -58.3008 | 62.2101 | -61.7249 | -61.647 | 54.5105 | 24.4812 | 7.9147 | 7.4295 | 62.2101 | -61.7477 | -0.3067 | 0.059509 | 3.1174 | -0.22888 | -7.6401 | -0.32959 | 0.059509 | 3.4241 | 69.3329 | 68.8477 | 115.9287 | 123.6282 | 3.1174 | 123.6282 | 85.8994 | -0.32959 | 123.6282 | 3.1174 | 85.8994 | 115.9287 | 123.6282 | -123.8754 | -123.8983
4509.7188 | 123.7885 | -61.409 | 62.1231 | -0.0012969 | 0.015597 | 0.016618 | 0.00527 | 0.061316 | -0.00054693 | 0.078195 | -58.3603 | 62.1048 | -61.7523 | -61.6196 | 54.5425 | 24.5087 | 7.782 | 7.4844 | 62.1735 | -61.7157 | -0.34332 | -0.018311 | 3.0487 | -0.21057 | -7.5806 | -0.3067 | 0.050354 | 3.392 | 69.191 | 68.8934 | 115.9515 | 123.5138 | 3.0487 | 123.5825 | 85.9177 | -0.3067 | 123.5138 | 3.0487 | 85.9177 | 115.9515 | 123.5825 | -123.8754 | -123.8388
4510.7188 | 123.7335 | -61.4136 | 62.1643 | -0.0089264 | 0.017733 | 0.013627 | 0.01531 | 0.06153 | 0.00073487 | 0.079476 | -58.2962 | 62.2055 | -61.7249 | -61.647 | 54.483 | 24.4492 | 7.8552 | 7.4295 | 62.1735 | -61.7432 | -0.31128 | 0.041198 | 3.1174 | -0.23346 | -7.6813 | -0.32959 | 0.009155 | 3.4286 | 69.2688 | 68.8431 | 115.8966 | 123.6191 | 3.1174 | 123.587 | 85.8627 | -0.32959 | 123.6191 | 3.1174 | 85.8627 | 115.8966 | 123.587 | -123.8892 | -123.9075
4511.7188 | 123.7244 | -61.4365 | 62.1643 | 0.021591 | 0.017733 | 0.016191 | 0.015738 | 0.064521 | -0.00054693 | 0.078408 | -58.2916 | 62.2147 | -61.7065 | -61.6425 | 54.4922 | 24.4308 | 7.8964 | 7.4432 | 62.2101 | -61.7752 | -0.27008 | 0.050354 | 3.1448 | -0.20599 | -7.6721 | -0.33875 | 0.045776 | 3.4149 | 69.3329 | 68.8797 | 115.9286 | 123.6511 | 3.1448 | 123.6465 | 85.8673 | -0.33875 | 123.6511 | 3.1448 | 85.8673 | 115.9286 | 123.6465 | -123.8709 | -123.9395
4512.7188 | 123.7198 | -61.441 | 62.146 | -0.024185 | 0.017092 | 0.014268 | 0.014456 | 0.066016 | 9.4068e-05 | 0.079476 | -58.3008 | 62.2192 | -61.734 | -61.6379 | 54.483 | 24.4171 | 7.8964 | 7.4432 | 62.1826 | -61.7477 | -0.29297 | 0.073242 | 3.1403 | -0.19684 | -7.663 | -0.3067 | 0.036621 | 3.4332 | 69.3375 | 68.8843 | 115.9241 | 123.6603 | 3.1403 | 123.6237 | 85.8582 | -0.3067 | 123.6603 | 3.1403 | 85.8582 | 115.9241 | 123.6237 | -123.88 | -123.8937
4513.7188 | 123.7061 | -61.4273 | 62.1643 | 0.074997 | 0.018374 | 0.011064 | 0.014669 | 0.063666 | -0.00033333 | 0.077767 | -58.3649 | 62.2009 | -61.7569 | -61.6928 | 54.451 | 24.3942 | 7.9559 | 7.4295 | 62.1826 | -61.7798 | -0.32959 | 0.036621 | 3.0624 | -0.2655 | -7.7133 | -0.35248 | 0.01831 | 3.392 | 69.3832 | 68.8568 | 115.8783 | 123.6282 | 3.0624 | 123.6099 | 85.8215 | -0.35248 | 123.6282 | 3.0624 | 85.8215 | 115.8783 | 123.6099 | -123.9212 | -123.9441
4514.7188 | 123.7335 | -61.4456 | 62.1414 | 3.7676 | 0.017519 | 0.013413 | 0.010397 | 0.064521 | 0.00052127 | 0.078835 | -58.2001 | 62.1643 | -61.7752 | -61.6608 | 54.5151 | 24.4217 | 7.9468 | 7.4524 | 62.1964 | -61.7889 | -0.32959 | 0.022889 | 3.2455 | -0.21515 | -7.6263 | -0.34332 | 0.054932 | 3.5751 | 69.3924 | 68.898 | 115.9607 | 123.6099 | 3.2455 | 123.642 | 85.8673 | -0.34332 | 123.6099 | 3.2455 | 85.8673 | 115.9607 | 123.642 | -123.9166 | -123.9304
4515.7188 | 123.7152 | -61.441 | 62.1368 | 0.090256 | 0.019228 | 0.017259 | 0.016378 | 0.066443 | 0.0011621 | 0.07969 | -58.3649 | 62.178 | -61.7569 | -61.6745 | 54.4281 | 24.3393 | 7.9239 | 7.4295 | 62.2009 | -61.7752 | -0.31586 | 0.041199 | 3.0762 | -0.23346 | -7.7087 | -0.33417 | 0.064087 | 3.392 | 69.3649 | 68.8705 | 115.8691 | 123.6191 | 3.0762 | 123.642 | 85.7803 | -0.33417 | 123.6191 | 3.0762 | 85.7803 | 115.8691 | 123.642 | -123.8937 | -123.912
4516.7188 | 123.6832 | -61.4502 | 62.1643 | 0.03685 | 0.018587 | 0.012773 | 0.013174 | 0.064521 | 0.0020167 | 0.07969 | -58.342 | 62.1918 | -61.7432 | -61.6653 | 54.3869 | 24.3164 | 7.8735 | 7.402 | 62.178 | -61.7661 | -0.29297 | 0.027465 | 3.1082 | -0.21515 | -7.7774 | -0.31586 | 0.013733 | 3.4012 | 69.3237 | 68.8522 | 115.8371 | 123.642 | 3.1082 | 123.6282 | 85.7666 | -0.31586 | 123.642 | 3.1082 | 85.7666 | 115.8371 | 123.6282 | -123.9075 | -123.9304
4517.7188 | 123.6923 | -61.4548 | 62.1506 | 0.04448 | 0.018801 | 0.012345 | 0.014669 | 0.067298 | -0.0020421 | 0.079049 | -58.3557 | 62.2147 | -61.7432 | -61.6516 | 54.4647 | 24.3622 | 7.9422 | 7.4387 | 62.2147 | -61.7661 | -0.28839 | 0.064087 | 3.0991 | -0.19684 | -7.6859 | -0.31128 | 0.064087 | 3.3875 | 69.397 | 68.8934 | 115.9195 | 123.6694 | 3.0991 | 123.6694 | 85.817 | -0.31128 | 123.6694 | 3.0991 | 85.817 | 115.9195 | 123.6694 | -123.8937 | -123.9166
4518.7188 | 123.761 | -61.4182 | 62.146 | -0.09285 | 0.016451 | 0.016831 | 0.013815 | 0.066016 | -0.00054693 | 0.079049 | -58.2916 | 62.1918 | -61.7294 | -61.6104 | 54.4968 | 24.3988 | 7.933 | 7.5165 | 62.1918 | -61.7523 | -0.31128 | 0.045776 | 3.1265 | -0.19226 | -7.6492 | -0.33417 | 0.045776 | 3.4378 | 69.3512 | 68.9346 | 115.9149 | 123.6099 | 3.1265 | 123.6099 | 85.817 | -0.33417 | 123.6099 | 3.1265 | 85.817 | 115.9149 | 123.6099 | -123.8754 | -123.8983
4519.7344 | 123.7747 | -61.3953 | 62.1368 | 0.067368 | 0.013033 | 0.017259 | 0.00527 | 0.062598 | 0.00052127 | 0.081826 | -58.2642 | 62.0636 | -61.734 | -61.6196 | 54.4876 | 24.3942 | 7.901 | 7.5668 | 62.1323 | -61.6928 | -0.33875 | -0.073242 | 3.1311 | -0.2243 | -7.6492 | -0.29755 | -0.004578 | 3.4698 | 69.2963 | 68.9621 | 115.8829 | 123.4589 | 3.1311 | 123.5275 | 85.7895 | -0.29755 | 123.4589 | 3.1311 | 85.7895 | 115.8829 | 123.5275 | -123.8708 | -123.8297
4520.7188 | 123.7244 | -61.4548 | 62.1368 | 0.15892 | 0.017519 | 0.0132 | 0.014456 | 0.065589 | 0.0011621 | 0.07969 | -58.2962 | 62.1872 | -61.7615 | -61.6882 | 54.3961 | 24.3347 | 7.933 | 7.4249 | 62.1689 | -61.8027 | -0.3067 | 0.050354 | 3.1586 | -0.23346 | -7.7408 | -0.3479 | 0.032043 | 3.4653 | 69.3878 | 68.8797 | 115.8508 | 123.642 | 3.1586 | 123.6237 | 85.7895 | -0.3479 | 123.642 | 3.1586 | 85.7895 | 115.8508 | 123.6237 | -123.8983 | -123.9395
4521.7188 | 123.6832 | -61.4456 | 62.1368 | 0.10551 | 0.016878 | 0.012986 | 0.014242 | 0.063666 | -0.00033333 | 0.078835 | -58.3237 | 62.1643 | -61.7432 | -61.6928 | 54.3823 | 24.3347 | 8.0063 | 7.4707 | 62.1872 | -61.7844 | -0.29755 | 0.027466 | 3.1219 | -0.24719 | -7.7545 | -0.33874 | 0.050354 | 3.4195 | 69.4519 | 68.9163 | 115.8279 | 123.6099 | 3.1219 | 123.6328 | 85.7803 | -0.33874 | 123.6099 | 3.1219 | 85.7803 | 115.8279 | 123.6328 | -123.88 | -123.9212
4522.7188 | 123.7198 | -61.4594 | 62.1506 | 0.04448 | 0.017947 | 0.012559 | 0.017233 | 0.064948 | -0.0020421 | 0.080544 | -58.3054 | 62.1964 | -61.734 | -61.6745 | 54.4098 | 24.3118 | 7.9926 | 7.4661 | 62.1918 | -61.7889 | -0.27466 | 0.045776 | 3.154 | -0.21515 | -7.7408 | -0.32959 | 0.041198 | 3.4286 | 69.4519 | 68.9255 | 115.8691 | 123.6557 | 3.154 | 123.6511 | 85.7712 | -0.32959 | 123.6557 | 3.154 | 85.7712 | 115.8691 | 123.6511 | -123.8846 | -123.9395
4523.7188 | 123.6969 | -61.4182 | 62.146 | 0.13603 | 0.01581 | 0.014909 | 0.013388 | 0.062384 | 0.0082117 | 0.078622 | -58.3511 | 62.1689 | -61.7752 | -61.8118 | 54.7165 | 24.527 | 7.8094 | 7.5256 | 62.2055 | -61.7615 | -0.35706 | 0.022888 | 3.067 | -0.39368 | -7.4295 | -0.34332 | 0.059509 | 3.4241 | 69.2276 | 68.9438 | 116.1346 | 123.587 | 3.067 | 123.6237 | 85.9451 | -0.34332 | 123.587 | 3.067 | 85.9451 | 116.1346 | 123.6237 | -123.9212 | -123.9075
4524.7188 | 123.6969 | -61.4365 | 62.146 | -0.0012969 | 0.018801 | 0.015122 | 0.014029 | 0.063025 | -0.0014013 | 0.079904 | -58.2779 | 62.1918 | -61.7706 | -61.6333 | 54.4693 | 24.3118 | 7.933 | 7.457 | 62.1872 | -61.7752 | -0.33417 | 0.045776 | 3.1586 | -0.19684 | -7.6767 | -0.33875 | 0.041199 | 3.4927 | 69.3695 | 68.8934 | 115.9058 | 123.6282 | 3.1586 | 123.6237 | 85.7483 | -0.33875 | 123.6282 | 3.1586 | 85.7483 | 115.9058 | 123.6237 | -123.9166 | -123.9212
4525.7188 | 123.7289 | -61.4319 | 62.1414 | 0.04448 | 0.018801 | 0.017686 | 0.016378 | 0.065375 | 0.00052127 | 0.079904 | -58.2367 | 62.1735 | -61.7752 | -61.5921 | 54.5471 | 24.4125 | 7.8827 | 7.5256 | 62.2147 | -61.7615 | -0.34332 | 0.032044 | 3.1952 | -0.16022 | -7.5943 | -0.32959 | 0.073243 | 3.5385 | 69.3146 | 68.9575 | 115.979 | 123.6053 | 3.1952 | 123.6465 | 85.8444 | -0.32959 | 123.6053 | 3.1952 | 85.8444 | 115.979 | 123.6465 | -123.9166 | -123.9029
4526.7188 | 123.7427 | -61.4319 | 62.1414 | 0.03685 | 0.017947 | 0.011704 | 0.015097 | 0.065589 | 0.00052127 | 0.081399 | -58.2825 | 62.2009 | -61.7523 | -61.6333 | 54.5197 | 24.3256 | 7.8964 | 7.4982 | 62.1918 | -61.7752 | -0.32043 | 0.05951 | 3.1494 | -0.20142 | -7.6218 | -0.34332 | 0.050354 | 3.4698 | 69.3283 | 68.9301 | 115.9515 | 123.6328 | 3.1494 | 123.6237 | 85.7574 | -0.34332 | 123.6328 | 3.1494 | 85.7574 | 115.9515 | 123.6237 | -123.8937 | -123.9166
4527.7188 | 123.6832 | -61.4548 | 62.1368 | 0.074997 | 0.019228 | 0.01085 | 0.017019 | 0.066016 | -0.00054693 | 0.079476 | -58.3282 | 62.2055 | -61.7661 | -61.6974 | 54.4876 | 24.3622 | 7.9697 | 7.4158 | 62.1872 | -61.7889 | -0.31128 | 0.068664 | 3.1265 | -0.24261 | -7.6492 | -0.33417 | 0.050354 | 3.4378 | 69.4244 | 68.8705 | 115.9424 | 123.6603 | 3.1265 | 123.642 | 85.817 | -0.33417 | 123.6603 | 3.1265 | 85.817 | 115.9424 | 123.642 | -123.9029 | -123.9258
4528.7188 | 123.7198 | -61.4639 | 62.1368 | 0.052109 | 0.018587 | 0.012132 | 0.013388 | 0.065589 | -0.0031103 | 0.079476 | -58.3099 | 62.2147 | -61.7752 | -61.6791 | 54.4922 | 24.3484 | 7.9514 | 7.4249 | 62.2009 | -61.7752 | -0.31128 | 0.07782 | 3.154 | -0.21515 | -7.6447 | -0.31128 | 0.064087 | 3.4653 | 69.4153 | 68.8889 | 115.9561 | 123.6786 | 3.154 | 123.6649 | 85.8124 | -0.31128 | 123.6786 | 3.154 | 85.8124 | 115.9561 | 123.6649 | -123.912 | -123.912
4529.7188 | 123.848 | -61.4182 | 62.1048 | -1.2449 | 0.012179 | 0.01555 | 0.0089016 | 0.06153 | 0.0011621 | 0.082253 | -58.3237 | 62.1048 | -61.734 | -61.5967 | 54.5563 | 24.4629 | 7.8186 | 7.5897 | 62.1597 | -61.7111 | -0.31586 | 0 | 3.0945 | -0.17853 | -7.5485 | -0.29297 | 0.054932 | 3.4103 | 69.2368 | 69.0079 | 115.9744 | 123.5229 | 3.0945 | 123.5779 | 85.881 | -0.29297 | 123.5229 | 3.0945 | 85.881 | 115.9744 | 123.5779 | -123.8388 | -123.8159
4530.7188 | 123.6877 | -61.441 | 62.1597 | 0.082626 | 0.016878 | 0.014909 | 0.016165 | 0.063666 | -0.0018285 | 0.077981 | -58.3008 | 62.1918 | -61.7477 | -61.647 | 54.483 | 24.3668 | 8.0109 | 7.4615 | 62.1918 | -61.7798 | -0.3067 | 0.032043 | 3.1403 | -0.20599 | -7.6767 | -0.33874 | 0.032043 | 3.447 | 69.4519 | 68.9026 | 115.9241 | 123.6328 | 3.1403 | 123.6328 | 85.8078 | -0.33874 | 123.6328 | 3.1403 | 85.8078 | 115.9241 | 123.6328 | -123.9075 | -123.9395
4531.7188 | 123.7701 | -61.4319 | 62.1414 | 0.11314 | 0.017306 | 0.014482 | 0.013601 | 0.065375 | -0.00033333 | 0.081399 | -58.3878 | 62.2147 | -61.7661 | -61.6699 | 54.4601 | 24.3256 | 7.6721 | 7.1594 | 62.1185 | -61.8301 | -0.33417 | 0.073243 | 3.0441 | -0.23804 | -7.6813 | -0.39825 | -0.022888 | 3.3783 | 69.104 | 68.5913 | 115.892 | 123.6465 | 3.0441 | 123.5504 | 85.7574 | -0.39825 | 123.6465 | 3.0441 | 85.7574 | 115.892 | 123.5504 | -123.9075 | -123.9716
4532.7188 | 123.7564 | -61.4273 | 62.146 | 0.029221 | 0.016665 | 0.017045 | 0.015524 | 0.061957 | -0.0026831 | 0.07969 | -58.3008 | 62.2055 | -61.7111 | -61.6104 | 54.5059 | 24.4034 | 7.9926 | 7.5302 | 62.146 | -61.7752 | -0.28381 | 0.059509 | 3.1265 | -0.18311 | -7.6401 | -0.3479 | 0 | 3.4103 | 69.4199 | 68.9575 | 115.9332 | 123.6328 | 3.1265 | 123.5733 | 85.8307 | -0.3479 | 123.6328 | 3.1265 | 85.8307 | 115.9332 | 123.5733 | -123.8571 | -123.9212
4533.7188 | 123.6969 | -61.4502 | 62.1231 | 0.13603 | 0.016878 | 0.017686 | 0.01296 | 0.064307 | 0.0011621 | 0.079049 | -58.3969 | 62.1826 | -61.7569 | -61.6974 | 54.4189 | 24.3073 | 7.9285 | 7.4341 | 62.1918 | -61.7935 | -0.3067 | 0.059509 | 3.0533 | -0.24719 | -7.7042 | -0.34332 | 0.068664 | 3.36 | 69.3787 | 68.8843 | 115.8691 | 123.6328 | 3.0533 | 123.642 | 85.7574 | -0.34332 | 123.6328 | 3.0533 | 85.7574 | 115.8691 | 123.642 | -123.88 | -123.9166
4534.7188 | 123.8159 | -61.4273 | 62.0911 | 0.18181 | 0.016024 | 0.011918 | 0.010397 | 0.064948 | -0.0033239 | 0.07969 | -58.3145 | 62.1002 | -61.7249 | -61.5738 | 54.6066 | 24.5041 | 7.782 | 7.576 | 62.1231 | -61.7386 | -0.29755 | 0.009156 | 3.1128 | -0.14648 | -7.4844 | -0.31128 | 0.032044 | 3.4103 | 69.2093 | 69.0033 | 116.0339 | 123.5275 | 3.1128 | 123.5504 | 85.9314 | -0.31128 | 123.5275 | 3.1128 | 85.9314 | 116.0339 | 123.5504 | -123.8159 | -123.8297
4535.7188 | 123.7015 | -61.4594 | 62.1552 | 0.067368 | 0.017306 | 0.013413 | 0.01531 | 0.062171 | 0.00052127 | 0.07969 | -58.3969 | 62.2101 | -61.7615 | -61.702 | 54.451 | 24.3347 | 7.9697 | 7.4249 | 62.1918 | -61.7798 | -0.30212 | 0.054932 | 3.0624 | -0.24261 | -7.7042 | -0.32043 | 0.036621 | 3.3646 | 69.429 | 68.8843 | 115.9103 | 123.6694 | 3.0624 | 123.6511 | 85.7941 | -0.32043 | 123.6694 | 3.0624 | 85.7941 | 115.9103 | 123.6511 | -123.9166 | -123.9349
4536.7188 | 123.7198 | -61.4594 | 62.146 | 0.013962 | 0.016665 | 0.017899 | 0.014029 | 0.062384 | 0.00094847 | 0.079904 | -58.3694 | 62.2147 | -61.7706 | -61.6699 | 54.4785 | 24.321 | 7.9742 | 7.4295 | 62.2009 | -61.7569 | -0.31128 | 0.068665 | 3.0899 | -0.21057 | -7.6675 | -0.29755 | 0.054932 | 3.4012 | 69.4336 | 68.8889 | 115.9378 | 123.674 | 3.0899 | 123.6603 | 85.7803 | -0.29755 | 123.674 | 3.0899 | 85.7803 | 115.9378 | 123.6603 | -123.9166 | -123.9029
4537.7188 | 123.7152 | -61.4639 | 62.1597 | 0.067368 | 0.017947 | 0.015763 | 0.014883 | 0.06388 | 0.0011621 | 0.079904 | -58.3878 | 62.2009 | -61.7477 | -61.6608 | 54.4922 | 24.3393 | 7.9971 | 7.4524 | 62.1964 | -61.7706 | -0.28381 | 0.041199 | 3.0762 | -0.19684 | -7.6675 | -0.3067 | 0.036621 | 3.36 | 69.4611 | 68.9163 | 115.9561 | 123.6649 | 3.0762 | 123.6603 | 85.8032 | -0.3067 | 123.6649 | 3.0762 | 85.8032 | 115.9561 | 123.6603 | -123.9075 | -123.9304
4538.7188 | 123.6969 | -61.4502 | 62.1597 | 0.0063326 | 0.017092 | 0.015122 | 0.013815 | 0.065161 | -0.00076053 | 0.081185 | -58.3694 | 62.1918 | -61.7569 | -61.6699 | 54.5059 | 24.3347 | 8.0017 | 7.457 | 62.2055 | -61.7615 | -0.3067 | 0.032043 | 3.0807 | -0.21973 | -7.6538 | -0.31128 | 0.045776 | 3.3875 | 69.4519 | 68.9072 | 115.9561 | 123.642 | 3.0807 | 123.6557 | 85.7849 | -0.31128 | 123.642 | 3.0807 | 85.7849 | 115.9561 | 123.6557 | -123.9166 | -123.9212
4539.7188 | 123.7198 | -61.4731 | 62.1506 | 0.029221 | 0.018587 | 0.01085 | 0.015524 | 0.064948 | -0.00097413 | 0.07969 | -58.3649 | 62.1964 | -61.7615 | -61.6608 | 54.538 | 24.3347 | 7.9834 | 7.4432 | 62.1872 | -61.7706 | -0.28839 | 0.045776 | 3.1082 | -0.18768 | -7.6126 | -0.29755 | 0.036621 | 3.3966 | 69.4565 | 68.9163 | 116.011 | 123.6694 | 3.1082 | 123.6603 | 85.8078 | -0.29755 | 123.6694 | 3.1082 | 85.8078 | 116.011 | 123.6603 | -123.912 | -123.9212
4540.7188 | 123.6969 | -61.4365 | 62.1368 | 0.04448 | 0.016238 | 0.016404 | 0.012106 | 0.065375 | -0.0014013 | 0.080972 | -58.3649 | 62.2147 | -61.734 | -61.6562 | 54.4601 | 23.6755 | 8.0246 | 7.4707 | 62.2055 | -61.7477 | -0.29755 | 0.07782 | 3.0716 | -0.21973 | -7.6767 | -0.31128 | 0.068664 | 3.3691 | 69.4611 | 68.9072 | 115.8966 | 123.6511 | 3.0716 | 123.642 | 85.112 | -0.31128 | 123.6511 | 3.0716 | 85.112 | 115.8966 | 123.642 | -123.8708 | -123.8846
4541.7188 | 123.7473 | -61.4456 | 62.1368 | 0.11314 | 0.016238 | 0.012559 | 0.0099698 | 0.064521 | 9.4068e-05 | 0.08204 | -58.3878 | 62.1826 | -61.7523 | -61.647 | 54.4922 | 23.4741 | 7.9605 | 7.4982 | 62.1735 | -61.7477 | -0.3067 | 0.045776 | 3.0579 | -0.20142 | -7.6447 | -0.30212 | 0.036621 | 3.3646 | 69.4061 | 68.9438 | 115.9378 | 123.6282 | 3.0579 | 123.6191 | 84.9197 | -0.30212 | 123.6282 | 3.0579 | 84.9197 | 115.9378 | 123.6191 | -123.8892 | -123.8846
4542.7188 | 123.7335 | -61.4273 | 62.1826 | 0.12077 | 0.014742 | 0.012345 | 0.012533 | 0.064948 | -0.0020421 | 0.080544 | -58.4015 | 62.2055 | -61.7569 | -61.6745 | 54.4693 | 23.3276 | 7.4844 | 7.2235 | 62.114 | -61.8073 | -0.32959 | 0.022888 | 3.0258 | -0.24719 | -7.7133 | -0.37994 | -0.068664 | 3.3554 | 68.9117 | 68.6508 | 115.8966 | 123.6328 | 3.0258 | 123.5413 | 84.7549 | -0.37994 | 123.6328 | 3.0258 | 84.7549 | 115.8966 | 123.5413 | -123.9395 | -123.9899
4543.7188 | 123.6511 | -61.4731 | 62.0636 | 0.12077 | 0.017733 | 0.016404 | 0.013815 | 0.063239 | 0.0015893 | 0.079263 | -58.4061 | 62.178 | -61.7889 | -61.6974 | 54.4968 | 23.7442 | 8.02 | 7.457 | 62.1918 | -61.7798 | -0.31586 | 0.11444 | 3.067 | -0.2243 | -7.5668 | -0.3067 | 0.12817 | 3.3829 | 69.4931 | 68.9301 | 115.9698 | 123.6511 | 3.067 | 123.6649 | 85.2173 | -0.3067 | 123.6511 | 3.067 | 85.2173 | 115.9698 | 123.6649 | -123.8525 | -123.8434
4544.7188 | 123.8159 | -61.4273 | 62.1323 | 0.15129 | 0.019228 | 0.015122 | 0.012106 | 0.065589 | 9.4068e-05 | 0.07969 | -58.3832 | 62.1552 | -61.7569 | -61.6379 | 54.5746 | 24.6323 | 7.869 | 7.5165 | 62.1506 | -61.7706 | -0.32959 | 0.022888 | 3.0441 | -0.21057 | -7.5577 | -0.34332 | 0.018311 | 3.3737 | 69.2963 | 68.9438 | 116.0019 | 123.5825 | 3.0441 | 123.5779 | 86.0596 | -0.34332 | 123.5825 | 3.0441 | 86.0596 | 116.0019 | 123.5779 | -123.8892 | -123.9029
4545.7188 | 123.7335 | -61.4502 | 62.1368 | 0.013962 | 0.017947 | 0.012345 | 0.014242 | 0.064734 | -0.00097413 | 0.080117 | -58.4335 | 62.1964 | -61.7432 | -61.6837 | 54.5197 | 24.5407 | 7.9834 | 7.4799 | 62.1735 | -61.7981 | -0.29297 | 0.059509 | 3.0167 | -0.23346 | -7.6172 | -0.3479 | 0.036621 | 3.3096 | 69.4336 | 68.9301 | 115.9698 | 123.6465 | 3.0167 | 123.6237 | 85.9909 | -0.3479 | 123.6465 | 3.0167 | 85.9909 | 115.9698 | 123.6237 | -123.88 | -123.9349
4546.7188 | 123.7381 | -61.4365 | 62.1277 | -0.047073 | 0.016878 | 0.014909 | 0.014883 | 0.063239 | 0.00073487 | 0.080331 | -58.3191 | 62.2101 | -61.7249 | -61.6379 | 54.538 | 24.4217 | 8.0292 | 7.5073 | 62.1964 | -61.7523 | -0.28839 | 0.082397 | 3.1174 | -0.20142 | -7.5897 | -0.31586 | 0.068664 | 3.4058 | 69.4656 | 68.9438 | 115.9744 | 123.6465 | 3.1174 | 123.6328 | 85.8582 | -0.31586 | 123.6465 | 3.1174 | 85.8582 | 115.9744 | 123.6328 | -123.8525 | -123.88
4547.7188 | 123.7244 | -61.4594 | 62.178 | 0.03685 | 0.019228 | 0.015122 | 0.014669 | 0.064093 | -0.00011953 | 0.078622 | -58.3511 | 62.1735 | -61.7569 | -61.6562 | 54.5334 | 24.4904 | 7.9788 | 7.4295 | 62.1689 | -61.7798 | -0.29755 | -0.004578 | 3.1082 | -0.19684 | -7.6447 | -0.32043 | -0.009156 | 3.4058 | 69.4382 | 68.8889 | 115.9927 | 123.6328 | 3.1082 | 123.6282 | 85.9497 | -0.32043 | 123.6328 | 3.1082 | 85.9497 | 115.9927 | 123.6282 | -123.9349 | -123.9578
4548.7344 | 123.8113 | -61.3907 | 62.0865 | 0.17418 | 0.01581 | 0.017686 | 0.0067654 | 0.062598 | 0.0011621 | 0.080117 | -58.3557 | 62.0773 | -61.7294 | -61.6058 | 54.6478 | 24.44 | 7.8049 | 7.5806 | 62.1323 | -61.702 | -0.33874 | -0.009155 | 3.035 | -0.21515 | -7.4387 | -0.31128 | 0.045776 | 3.3737 | 69.1956 | 68.9713 | 116.0385 | 123.468 | 3.035 | 123.5229 | 85.8307 | -0.31128 | 123.468 | 3.035 | 85.8307 | 116.0385 | 123.5229 | -123.8159 | -123.7885
4549.7344 | 123.8022 | -61.4182 | 62.1185 | 0.097885 | 0.016024 | 0.013627 | 0.0065518 | 0.061743 | -0.00011953 | 0.079476 | -58.3786 | 62.0956 | -61.7386 | -61.6196 | 54.5563 | 24.3942 | 7.8873 | 7.5806 | 62.1185 | -61.7203 | -0.32043 | -0.022888 | 3.0396 | -0.20142 | -7.5623 | -0.30212 | 0 | 3.36 | 69.3054 | 68.9987 | 115.9744 | 123.5138 | 3.0396 | 123.5367 | 85.8124 | -0.30212 | 123.5138 | 3.0396 | 85.8124 | 115.9744 | 123.5367 | -123.8571 | -123.8388
4550.7188 | 123.7198 | -61.441 | 62.1689 | 0.059738 | 0.016238 | 0.013841 | 0.017019 | 0.061957 | -0.00033333 | 0.078408 | -58.374 | 62.1872 | -61.7477 | -61.6791 | 54.538 | 24.3073 | 8.0246 | 7.4936 | 62.1689 | -61.7889 | -0.3067 | 0.018311 | 3.067 | -0.23804 | -7.6309 | -0.3479 | 0 | 3.3737 | 69.4656 | 68.9346 | 115.979 | 123.6282 | 3.067 | 123.6099 | 85.7483 | -0.3479 | 123.6282 | 3.067 | 85.7483 | 115.979 | 123.6099 | -123.9166 | -123.9578
4551.7188 | 123.7381 | -61.4136 | 62.178 | 0.052109 | 0.017733 | 0.01555 | 0.015097 | 0.062812 | -0.00097413 | 0.080972 | -58.3282 | 62.2009 | -61.7111 | -61.647 | 54.5563 | 23.6023 | 8.02 | 7.5348 | 62.1826 | -61.7661 | -0.29755 | 0.022888 | 3.0853 | -0.23346 | -7.6218 | -0.35248 | 0.004577 | 3.3829 | 69.4336 | 68.9484 | 115.9698 | 123.6145 | 3.0853 | 123.5962 | 85.0159 | -0.35248 | 123.6145 | 3.0853 | 85.0159 | 115.9698 | 123.5962 | -123.8892 | -123.9441
4552.7188 | 123.7289 | -61.4319 | 62.1552 | 0.03685 | 0.017947 | 0.015122 | 0.016806 | 0.065161 | -0.0028967 | 0.079263 | -58.3008 | 62.1918 | -61.734 | -61.6379 | 54.5609 | 24.0601 | 8.0521 | 7.5256 | 62.1918 | -61.7569 | -0.30212 | 0.036621 | 3.1311 | -0.20599 | -7.5943 | -0.32501 | 0.036621 | 3.4332 | 69.4839 | 68.9575 | 115.9927 | 123.6237 | 3.1311 | 123.6237 | 85.4919 | -0.32501 | 123.6237 | 3.1311 | 85.4919 | 115.9927 | 123.6237 | -123.8892 | -123.912
4553.7344 | 123.8205 | -61.3907 | 62.1048 | 0.15129 | 0.015383 | 0.01085 | 0.006979 | 0.065161 | 0.00073487 | 0.080758 | -58.3557 | 62.0865 | -61.7432 | -61.5921 | 54.5975 | 23.4192 | 7.8735 | 7.6447 | 62.1506 | -61.7065 | -0.35248 | -0.01831 | 3.035 | -0.20142 | -7.5073 | -0.31586 | 0.045777 | 3.3875 | 69.2642 | 69.0353 | 115.9882 | 123.4772 | 3.035 | 123.5413 | 84.8099 | -0.31586 | 123.4772 | 3.035 | 84.8099 | 115.9882 | 123.5413 | -123.848 | -123.8113
4554.7188 | 123.8342 | -61.3998 | 62.1094 | 0.18944 | 0.016238 | 0.01555 | 0.012747 | 0.060034 | -0.0016149 | 0.07969 | -58.374 | 62.1414 | -61.734 | -61.615 | 54.5151 | 23.085 | 7.8827 | 7.5623 | 62.1414 | -61.7615 | -0.33417 | 0.032043 | 3.0258 | -0.21515 | -7.5943 | -0.36163 | 0.032043 | 3.36 | 69.2825 | 68.9621 | 115.9149 | 123.5413 | 3.0258 | 123.5413 | 84.4849 | -0.36163 | 123.5413 | 3.0258 | 84.4849 | 115.9149 | 123.5413 | -123.8434 | -123.8708
4555.7188 | 123.761 | -61.4227 | 62.1552 | -0.024185 | 0.01581 | 0.017045 | 0.014883 | 0.062171 | 0.0015893 | 0.078195 | -58.3145 | 62.2009 | -61.7203 | -61.6013 | 54.5609 | 24.0234 | 7.9788 | 7.5531 | 62.1918 | -61.7523 | -0.29755 | 0.045777 | 3.1082 | -0.17853 | -7.5943 | -0.32959 | 0.036621 | 3.4058 | 69.4016 | 68.9758 | 115.9836 | 123.6237 | 3.1082 | 123.6145 | 85.4462 | -0.32959 | 123.6237 | 3.1082 | 85.4462 | 115.9836 | 123.6145 | -123.8754 | -123.9075
4556.7188 | 123.761 | -61.3998 | 62.1689 | -0.23018 | 0.018587 | 0.017899 | 0.014669 | 0.063666 | -0.00097413 | 0.078195 | -58.3008 | 62.2192 | -61.7203 | -61.5784 | 54.5197 | 23.1125 | 7.9788 | 7.5897 | 62.2238 | -61.7386 | -0.32043 | 0.050354 | 3.0991 | -0.17853 | -7.6492 | -0.33874 | 0.054932 | 3.4195 | 69.3787 | 68.9896 | 115.9195 | 123.6191 | 3.0991 | 123.6237 | 84.5123 | -0.33874 | 123.6191 | 3.0991 | 84.5123 | 115.9195 | 123.6237 | -123.8892 | -123.9075
4557.7188 | 123.7564 | -61.3907 | 62.146 | -0.062332 | 0.01581 | 0.011277 | 0.014456 | 0.064093 | -0.0020421 | 0.078408 | -58.3328 | 62.1643 | -61.7432 | -61.6058 | 54.5197 | 23.085 | 8.4366 | 7.7087 | 62.1964 | -61.7523 | -0.35248 | 0.018311 | 3.0579 | -0.21515 | -7.6263 | -0.36163 | 0.050354 | 3.4103 | 69.8273 | 69.0994 | 115.9103 | 123.555 | 3.0579 | 123.587 | 84.4757 | -0.36163 | 123.555 | 3.0579 | 84.4757 | 115.9103 | 123.587 | -123.8892 | -123.8983
4558.7188 | 123.8251 | -61.3907 | 62.0956 | 0.067368 | 0.01346 | 0.01555 | 0.0093288 | 0.064948 | -0.00011953 | 0.080117 | -58.3191 | 62.1277 | -61.6928 | -61.5601 | 54.6066 | 23.1079 | 7.7362 | 7.6492 | 62.1368 | -61.7157 | -0.30212 | 0.032044 | 3.0716 | -0.16937 | -7.489 | -0.32501 | 0.041199 | 3.3737 | 69.1269 | 69.0399 | 115.9973 | 123.5184 | 3.0716 | 123.5275 | 84.4986 | -0.32501 | 123.5184 | 3.0716 | 84.4986 | 115.9973 | 123.5275 | -123.7885 | -123.8113
4559.7188 | 123.6969 | -61.4456 | 62.1735 | 0.03685 | 0.015597 | 0.011918 | 0.013601 | 0.063452 | 0.00073487 | 0.079049 | -58.3511 | 62.2055 | -61.7432 | -61.6333 | 54.5151 | 23.0804 | 7.7957 | 7.4707 | 62.178 | -61.7661 | -0.29755 | 0.032043 | 3.0945 | -0.18768 | -7.6584 | -0.32043 | 0.004578 | 3.392 | 69.2413 | 68.9163 | 115.9607 | 123.6511 | 3.0945 | 123.6237 | 84.5261 | -0.32043 | 123.6511 | 3.0945 | 84.5261 | 115.9607 | 123.6237 | -123.9166 | -123.9395
4560.7188 | 123.7152 | -61.4319 | 62.1872 | -0.23018 | 0.014315 | 0.012773 | 0.0056972 | 0.060248 | -0.00011953 | 0.080544 | -58.374 | 62.1964 | -61.7432 | -61.7111 | 54.6021 | 23.1171 | 7.9422 | 7.608 | 62.2238 | -61.7111 | -0.31128 | 0.009155 | 3.0579 | -0.27924 | -7.5851 | -0.27924 | 0.036621 | 3.3691 | 69.3741 | 69.0399 | 116.0339 | 123.6282 | 3.0579 | 123.6557 | 84.549 | -0.27924 | 123.6282 | 3.0579 | 84.549 | 116.0339 | 123.6557 | -123.9304 | -123.8983
4561.7188 | 123.7976 | -61.4227 | 62.1735 | -0.2607 | 0.018374 | 0.012986 | 0.011679 | 0.063025 | 0.00052127 | 0.078622 | -58.3237 | 62.233 | -61.7157 | -61.5829 | 54.6066 | 23.14 | 7.9788 | 7.6355 | 62.2238 | -61.7065 | -0.29297 | 0.059509 | 3.0991 | -0.16022 | -7.5668 | -0.28381 | 0.050354 | 3.392 | 69.4016 | 69.0582 | 116.0294 | 123.6557 | 3.0991 | 123.6465 | 84.5627 | -0.28381 | 123.6557 | 3.0991 | 84.5627 | 116.0294 | 123.6465 | -123.8892 | -123.88
4562.7188 | 123.7381 | -61.4136 | 62.1826 | -0.22255 | 0.017092 | 0.0095682 | 0.012747 | 0.064093 | -0.00033333 | 0.079904 | -58.3694 | 62.2055 | -61.734 | -61.6287 | 54.5929 | 23.2086 | 7.9834 | 7.5943 | 62.2192 | -61.734 | -0.32044 | 0.022888 | 3.0441 | -0.21515 | -7.5897 | -0.32044 | 0.036621 | 3.3646 | 69.397 | 69.0079 | 116.0065 | 123.6191 | 3.0441 | 123.6328 | 84.6222 | -0.32044 | 123.6191 | 3.0441 | 84.6222 | 116.0065 | 123.6328 | -123.9166 | -123.9166
4563.7188 | 123.6877 | -61.4182 | 62.1964 | -0.34462 | 0.016451 | 0.0087138 | 0.011038 | 0.062171 | -0.0016149 | 0.080331 | -58.4106 | 62.1918 | -61.734 | -61.6196 | 54.5883 | 23.2498 | 8.0154 | 7.5943 | 62.2192 | -61.7157 | -0.31586 | -0.004578 | 3.0075 | -0.20142 | -7.608 | -0.29755 | 0.022888 | 3.3234 | 69.4336 | 69.0125 | 116.0065 | 123.6099 | 3.0075 | 123.6374 | 84.668 | -0.29755 | 123.6099 | 3.0075 | 84.668 | 116.0065 | 123.6374 | -123.9304 | -123.912
4564.7188 | 123.7656 | -61.4136 | 62.146 | -0.131 | 0.015383 | 0.011918 | 0.014029 | 0.063666 | -0.00076053 | 0.079049 | -58.2962 | 62.1918 | -61.702 | -61.5463 | 54.57 | 23.2407 | 7.8735 | 7.6172 | 62.1918 | -61.7294 | -0.28839 | 0.045776 | 3.1174 | -0.13275 | -7.576 | -0.31586 | 0.045776 | 3.4058 | 69.2871 | 69.0308 | 115.9836 | 123.6053 | 3.1174 | 123.6053 | 84.6542 | -0.31586 | 123.6053 | 3.1174 | 84.6542 | 115.9836 | 123.6053 | -123.848 | -123.8754
4565.7188 | 123.7335 | -61.409 | 62.1826 | -1.8934 | 0.015597 | 0.0097818 | 0.01296 | 0.061316 | 0.00052127 | 0.078622 | -58.4885 | 62.2055 | -61.7386 | -61.647 | 54.5105 | 23.1354 | 7.9056 | 7.5394 | 62.2513 | -61.7065 | -0.32959 | 0.022888 | 2.9205 | -0.23804 | -7.6721 | -0.29755 | 0.068665 | 3.2501 | 69.3146 | 68.9484 | 115.9195 | 123.6145 | 2.9205 | 123.6603 | 84.5444 | -0.29755 | 123.6145 | 2.9205 | 84.5444 | 115.9195 | 123.6603 | -123.9212 | -123.8892
4566.7188 | 123.7564 | -61.3815 | 62.1826 | -0.29121 | 0.01346 | 0.014054 | 0.0080472 | 0.06153 | 0.00052127 | 0.080331 | -58.342 | 62.1323 | -61.7157 | -61.5601 | 54.6524 | 23.6893 | 7.7362 | 7.6218 | 62.1964 | -61.6653 | -0.33417 | -0.050354 | 3.0396 | -0.17853 | -7.5302 | -0.28381 | 0.013733 | 3.3737 | 69.1177 | 69.0033 | 116.0339 | 123.5138 | 3.0396 | 123.5779 | 85.0708 | -0.28381 | 123.5138 | 3.0396 | 85.0708 | 116.0339 | 123.5779 | -123.8983 | -123.848
4567.7188 | 123.9487 | -61.3174 | 62.2192 | -0.16151 | 0.011751 | 0.007432 | 0.005911 | 0.058966 | -0.00054693 | 0.076699 | -58.3008 | 62.1002 | -61.7157 | -61.5097 | 54.6158 | 23.7213 | 7.6538 | 7.6675 | 62.1368 | -61.6882 | -0.39825 | -0.11902 | 3.0167 | -0.19226 | -7.6035 | -0.37079 | -0.082397 | 3.4149 | 68.9713 | 68.985 | 115.9332 | 123.4177 | 3.0167 | 123.4543 | 85.0388 | -0.37079 | 123.4177 | 3.0167 | 85.0388 | 115.9332 | 123.4543 | -123.9349 | -123.9075
4568.7188 | 123.8342 | -61.3815 | 62.1643 | -0.19203 | 0.013033 | 0.010636 | 0.012533 | 0.057685 | 0.0020167 | 0.080331 | -58.2275 | 62.1414 | -61.6516 | -61.5967 | 54.6936 | 23.7259 | 7.5897 | 7.6675 | 62.1323 | -61.702 | -0.27008 | -0.022889 | 3.154 | -0.21515 | -7.4707 | -0.32043 | -0.032044 | 3.4241 | 68.9713 | 69.0491 | 116.0751 | 123.5229 | 3.154 | 123.5138 | 85.1074 | -0.32043 | 123.5229 | 3.154 | 85.1074 | 116.0751 | 123.5138 | -123.8159 | -123.8663
4569.7188 | 123.8342 | -61.3632 | 62.1506 | -0.024185 | 0.013033 | 0.012132 | 0.011465 | 0.061957 | -0.0035375 | 0.080117 | -58.2642 | 62.0956 | -61.702 | -61.5051 | 54.6295 | 23.7579 | 7.5668 | 7.6218 | 62.1506 | -61.6562 | -0.33875 | -0.054932 | 3.0991 | -0.14191 | -7.5211 | -0.29297 | 0 | 3.4378 | 68.9301 | 68.985 | 115.9927 | 123.4589 | 3.0991 | 123.5138 | 85.1212 | -0.29297 | 123.4589 | 3.0991 | 85.1212 | 115.9927 | 123.5138 | -123.8525 | -123.8068
4570.7188 | 123.8709 | -61.3907 | 62.1323 | -0.16151 | 0.012392 | 0.0095682 | 0.010611 | 0.057898 | -0.0033239 | 0.076699 | -58.2733 | 62.0865 | -61.6837 | -61.5097 | 54.483 | 24.0829 | 7.8781 | 7.3151 | 62.1872 | -61.6333 | -0.29297 | -0.045776 | 3.1174 | -0.11902 | -7.6492 | -0.24262 | 0.054932 | 3.4103 | 69.2688 | 68.7057 | 115.8737 | 123.4772 | 3.1174 | 123.5779 | 85.4736 | -0.24262 | 123.4772 | 3.1174 | 85.4736 | 115.8737 | 123.5779 | -123.8159 | -123.7656
4571.7188 | 123.8663 | -61.377 | 62.1506 | -0.12337 | 0.011751 | 0.006791 | 0.010397 | 0.055548 | -0.00011953 | 0.079049 | -58.3191 | 62.0865 | -61.7203 | -61.528 | 54.6524 | 24.1425 | 7.5897 | 7.6584 | 62.146 | -61.6608 | -0.34332 | -0.064087 | 3.0579 | -0.15106 | -7.4982 | -0.28381 | -0.004578 | 3.4012 | 68.9667 | 69.0353 | 116.0294 | 123.4634 | 3.0579 | 123.5229 | 85.5194 | -0.28381 | 123.4634 | 3.0579 | 85.5194 | 116.0294 | 123.5229 | -123.8708 | -123.8113
4572.7188 | 123.8251 | -61.409 | 62.1277 | -0.031814 | 0.014742 | 0.0089274 | 0.011251 | 0.058325 | 0.00094847 | 0.079476 | -58.3466 | 62.0773 | -61.7249 | -61.5463 | 54.6249 | 23.8861 | 7.695 | 7.6401 | 62.1368 | -61.6791 | -0.31586 | -0.050354 | 3.0624 | -0.13733 | -7.5027 | -0.27008 | 0.009155 | 3.3783 | 69.104 | 69.0491 | 116.0339 | 123.4863 | 3.0624 | 123.5458 | 85.2951 | -0.27008 | 123.4863 | 3.0624 | 85.2951 | 116.0339 | 123.5458 | -123.8525 | -123.8068
4573.7188 | 123.8571 | -61.3724 | 62.1368 | -0.077591 | 0.01346 | 0.011277 | 0.0082608 | 0.058325 | -0.0024695 | 0.07969 | -58.3557 | 62.059 | -61.6837 | -61.528 | 54.6341 | 23.9136 | 7.6767 | 7.663 | 62.0956 | -61.6837 | -0.31128 | -0.07782 | 3.0167 | -0.15564 | -7.5027 | -0.31128 | -0.041199 | 3.3279 | 69.0491 | 69.0353 | 116.0065 | 123.4314 | 3.0167 | 123.468 | 85.2859 | -0.31128 | 123.4314 | 3.0167 | 85.2859 | 116.0065 | 123.468 | -123.8205 | -123.8205
4574.7344 | 123.7152 | -61.441 | 62.1689 | -0.12337 | 0.015169 | 0.014054 | 0.014669 | 0.058539 | -0.0016149 | 0.078622 | -58.3191 | 62.1689 | -61.6791 | -61.5875 | 54.5425 | 23.9594 | 7.8369 | 7.576 | 62.2192 | -61.7111 | -0.23804 | 0 | 3.1219 | -0.14648 | -7.6263 | -0.27008 | 0.050354 | 3.36 | 69.278 | 69.017 | 115.9836 | 123.6099 | 3.1219 | 123.6603 | 85.4004 | -0.27008 | 123.6099 | 3.1219 | 85.4004 | 115.9836 | 123.6603 | -123.848 | -123.88
4575.7188 | 123.8022 | -61.4182 | 62.1643 | -0.40565 | 0.013674 | 0.01085 | 0.0095424 | 0.058325 | 0.00030767 | 0.078408 | -58.4244 | 62.0636 | -61.7157 | -61.6013 | 54.5883 | 24.1837 | 7.9147 | 7.6767 | 62.1414 | -61.6882 | -0.29755 | -0.10071 | 2.9938 | -0.1831 | -7.576 | -0.27008 | -0.022889 | 3.2913 | 69.3329 | 69.0948 | 116.0065 | 123.4818 | 2.9938 | 123.5596 | 85.6018 | -0.27008 | 123.4818 | 2.9938 | 85.6018 | 116.0065 | 123.5596 | -123.88 | -123.8525
4576.7188 | 123.8113 | -61.3861 | 62.1643 | -0.016556 | 0.01282 | 0.0087138 | 0.010611 | 0.057685 | 0.0013757 | 0.07734 | -58.3832 | 62.0636 | -61.734 | -61.5875 | 54.5837 | 24.115 | 8.2718 | 7.7774 | 62.1277 | -61.7203 | -0.3479 | -0.10071 | 3.0029 | -0.20142 | -7.5806 | -0.33417 | -0.036621 | 3.3508 | 69.6579 | 69.1635 | 115.9698 | 123.4497 | 3.0029 | 123.5138 | 85.5011 | -0.33417 | 123.4497 | 3.0029 | 85.5011 | 115.9698 | 123.5138 | -123.8983 | -123.8846
4577.7188 | 123.8022 | -61.4182 | 62.1277 | 0.15129 | 0.015383 | 0.011277 | 0.010611 | 0.058753 | -0.0022559 | 0.077767 | -58.3832 | 62.0682 | -61.7477 | -61.6013 | 54.5792 | 24.0875 | 8.2672 | 7.7866 | 62.1048 | -61.7157 | -0.32959 | -0.05951 | 3.035 | -0.1831 | -7.5485 | -0.29755 | -0.022889 | 3.3646 | 69.6854 | 69.2047 | 115.9973 | 123.4863 | 3.035 | 123.5229 | 85.5057 | -0.29755 | 123.4863 | 3.035 | 85.5057 | 115.9973 | 123.5229 | -123.8754 | -123.8434
4578.7188 | 123.8068 | -61.4182 | 62.1185 | 0.097885 | 0.01346 | 0.013627 | 0.012533 | 0.060034 | 0.0018031 | 0.079904 | -58.3374 | 62.0682 | -61.7294 | -61.5784 | 54.5471 | 24.0692 | 8.2535 | 7.814 | 62.0865 | -61.6974 | -0.31128 | -0.050354 | 3.0808 | -0.16022 | -7.5714 | -0.27924 | -0.032043 | 3.392 | 69.6716 | 69.2322 | 115.9653 | 123.4863 | 3.0808 | 123.5046 | 85.4874 | -0.27924 | 123.4863 | 3.0808 | 85.4874 | 115.9653 | 123.5046 | -123.848 | -123.8159
4579.7188 | 123.7564 | -61.4044 | 62.1918 | -0.27596 | 0.015597 | 0.013627 | 0.013601 | 0.059394 | 9.4068e-05 | 0.079263 | -58.3786 | 62.0911 | -61.7294 | -61.5692 | 54.5837 | 24.1653 | 8.4824 | 7.8003 | 62.1735 | -61.7432 | -0.32501 | -0.10071 | 3.0258 | -0.1648 | -7.608 | -0.33875 | -0.01831 | 3.3508 | 69.8868 | 69.2047 | 115.9882 | 123.4955 | 3.0258 | 123.5779 | 85.5698 | -0.33875 | 123.4955 | 3.0258 | 85.5698 | 115.9882 | 123.5779 | -123.9212 | -123.9349
4580.7188 | 123.8251 | -61.3953 | 62.1277 | 0.18944 | 0.016665 | 0.011277 | 0.015738 | 0.061316 | -0.0016149 | 0.079049 | -58.3282 | 62.1048 | -61.7249 | -61.5463 | 54.5609 | 24.1562 | 7.4799 | 7.5668 | 62.1048 | -61.7065 | -0.32959 | -0.022889 | 3.067 | -0.15106 | -7.5668 | -0.31128 | -0.022889 | 3.3966 | 68.8751 | 68.9621 | 115.9561 | 123.5001 | 3.067 | 123.5001 | 85.5515 | -0.31128 | 123.5001 | 3.067 | 85.5515 | 115.9561 | 123.5001 | -123.8525 | -123.8342
4581.7188 | 123.793 | -61.4273 | 62.114 | 0.24284 | 0.016451 | 0.014268 | 0.01531 | 0.057898 | 0.00052127 | 0.078195 | -58.374 | 62.1368 | -61.7294 | -61.6013 | 54.57 | 24.115 | 7.5851 | 7.5439 | 62.1323 | -61.734 | -0.30212 | 0.022888 | 3.0533 | -0.17395 | -7.5439 | -0.3067 | 0.01831 | 3.3554 | 69.0125 | 68.9713 | 115.9973 | 123.5641 | 3.0533 | 123.5596 | 85.5423 | -0.3067 | 123.5641 | 3.0533 | 85.5423 | 115.9973 | 123.5596 | -123.8434 | -123.848
4582.7188 | 123.8297 | -61.3815 | 62.0773 | 0.19707 | 0.015169 | 0.012986 | 0.010183 | 0.061743 | -0.00033333 | 0.07734 | -58.2733 | 62.0819 | -61.7661 | -61.4777 | 54.6066 | 24.0463 | 7.576 | 7.6401 | 62.1002 | -61.6974 | -0.38452 | 0.004577 | 3.1082 | -0.09613 | -7.4707 | -0.31586 | 0.022888 | 3.4927 | 68.9575 | 69.0216 | 115.9882 | 123.4634 | 3.1082 | 123.4818 | 85.4279 | -0.31586 | 123.4634 | 3.1082 | 85.4279 | 115.9882 | 123.4818 | -123.8434 | -123.7747
4583.7188 | 123.8297 | -61.3953 | 62.0911 | 0.2047 | 0.017306 | 0.010423 | 0.015738 | 0.061316 | 0.0011621 | 0.080758 | -58.3054 | 62.0911 | -61.7065 | -61.528 | 54.6204 | 24.1516 | 7.5027 | 7.6401 | 62.0956 | -61.7065 | -0.31128 | 0 | 3.0899 | -0.13275 | -7.4707 | -0.31128 | 0.004578 | 3.4012 | 68.898 | 69.0353 | 116.0156 | 123.4863 | 3.0899 | 123.4909 | 85.5469 | -0.31128 | 123.4863 | 3.0899 | 85.5469 | 116.0156 | 123.4909 | -123.7976 | -123.7976
4584.7188 | 123.8297 | -61.409 | 62.1048 | 0.24284 | 0.015383 | 0.0132 | 0.015738 | 0.063025 | -0.00054693 | 0.080331 | -58.3328 | 62.1597 | -61.7294 | -61.5692 | 54.6112 | 24.1379 | 7.5027 | 7.5577 | 62.1048 | -61.7249 | -0.32043 | 0.054932 | 3.0762 | -0.16022 | -7.4936 | -0.31586 | 0 | 3.3966 | 68.9117 | 68.9667 | 116.0202 | 123.5687 | 3.0762 | 123.5138 | 85.5469 | -0.31586 | 123.5687 | 3.0762 | 85.5469 | 116.0202 | 123.5138 | -123.8342 | -123.8297
4585.7188 | 123.7701 | -61.409 | 62.1048 | 0.25047 | 0.016665 | 0.012773 | 0.014456 | 0.060034 | -0.00054693 | 0.078835 | -58.3786 | 62.1689 | -61.7157 | -61.6013 | 54.5837 | 24.1104 | 7.5897 | 7.5073 | 62.1094 | -61.7203 | -0.3067 | 0.064087 | 3.0304 | -0.19226 | -7.5211 | -0.31128 | 0.004578 | 3.3371 | 68.9987 | 68.9163 | 115.9927 | 123.5779 | 3.0304 | 123.5184 | 85.5194 | -0.31128 | 123.5779 | 3.0304 | 85.5194 | 115.9927 | 123.5184 | -123.8205 | -123.8251
4586.7188 | 123.7518 | -61.4594 | 62.1323 | 0.11314 | 0.018587 | 0.014482 | 0.017019 | 0.062598 | -0.00097413 | 0.077981 | -58.3832 | 62.1826 | -61.7523 | -61.6196 | 54.5242 | 24.0738 | 7.6767 | 7.4936 | 62.1597 | -61.7432 | -0.29297 | 0.050354 | 3.0762 | -0.16022 | -7.608 | -0.28381 | 0.027466 | 3.3691 | 69.136 | 68.9529 | 115.9836 | 123.642 | 3.0762 | 123.6191 | 85.5331 | -0.28381 | 123.642 | 3.0762 | 85.5331 | 115.9836 | 123.6191 | -123.8846 | -123.8754
4587.7188 | 123.7152 | -61.4365 | 62.1506 | -0.25307 | 0.017519 | 0.0132 | 0.016165 | 0.063452 | -0.0014013 | 0.078622 | -58.429 | 62.1826 | -61.7477 | -61.6699 | 54.5013 | 24.0967 | 7.7179 | 7.4341 | 62.1368 | -61.7615 | -0.31128 | 0.032043 | 3.0075 | -0.23346 | -7.6492 | -0.32501 | -0.013733 | 3.3188 | 69.1544 | 68.8705 | 115.9378 | 123.6191 | 3.0075 | 123.5733 | 85.5331 | -0.32501 | 123.6191 | 3.0075 | 85.5331 | 115.9378 | 123.5733 | -123.8983 | -123.912
4588.7188 | 123.8388 | -61.4731 | 62.1506 | 0.14366 | 0.016451 | 0.015977 | 0.016806 | 0.064521 | 9.4068e-05 | 0.079263 | -58.3878 | 62.1735 | -61.7477 | -61.6425 | 54.5059 | 24.0784 | 7.7316 | 7.0862 | 62.1323 | -61.7889 | -0.27466 | 0.022888 | 3.0853 | -0.16937 | -7.6447 | -0.31586 | -0.018311 | 3.36 | 69.2047 | 68.5593 | 115.979 | 123.6465 | 3.0853 | 123.6053 | 85.5515 | -0.31586 | 123.6465 | 3.0853 | 85.5515 | 115.979 | 123.6053 | -123.8983 | -123.9395
4589.7344 | 123.8525 | -61.4044 | 62.146 | 0.074997 | 0.015383 | 0.011277 | 0.0065518 | 0.061103 | -0.00076053 | 0.078835 | -58.3878 | 62.059 | -61.7157 | -61.6196 | 54.6066 | 24.2844 | 7.7866 | 7.6263 | 62.1185 | -61.6745 | -0.31128 | -0.086975 | 3.0167 | -0.21515 | -7.5394 | -0.27008 | -0.027466 | 3.3279 | 69.191 | 69.0308 | 116.011 | 123.4634 | 3.0167 | 123.5229 | 85.6888 | -0.27008 | 123.4634 | 3.0167 | 85.6888 | 116.011 | 123.5229 | -123.8617 | -123.8205
4590.7188 | 123.7152 | -61.4182 | 62.146 | 0.074997 | 0.018801 | 0.014695 | 0.017019 | 0.061743 | 0.00030767 | 0.079904 | -58.3923 | 62.178 | -61.7523 | -61.647 | 54.483 | 24.2798 | 7.3654 | 7.3196 | 62.0819 | -61.7981 | -0.33417 | 0.032044 | 3.0258 | -0.22888 | -7.663 | -0.37994 | -0.064087 | 3.36 | 68.7836 | 68.7378 | 115.9012 | 123.5962 | 3.0258 | 123.5001 | 85.6979 | -0.37994 | 123.5962 | 3.0258 | 85.6979 | 115.9012 | 123.5001 | -123.8983 | -123.9441
4591.7188 | 123.7152 | -61.4685 | 62.1506 | 0.04448 | 0.016024 | 0.017045 | 0.013815 | 0.062812 | -0.0011877 | 0.078408 | -58.3832 | 62.2009 | -61.7386 | -61.6837 | 54.5151 | 24.0784 | 8.2031 | 7.6126 | 62.1552 | -61.7569 | -0.27008 | 0.050354 | 3.0853 | -0.21515 | -7.6355 | -0.28839 | 0.004577 | 3.3554 | 69.6716 | 69.0811 | 115.9836 | 123.6694 | 3.0853 | 123.6237 | 85.5469 | -0.28839 | 123.6694 | 3.0853 | 85.5469 | 115.9836 | 123.6237 | -123.8892 | -123.9075
4592.7188 | 123.7106 | -61.4273 | 62.1368 | 0.013962 | 0.017092 | 0.013627 | 0.016592 | 0.064948 | -0.00054693 | 0.080331 | -58.374 | 62.1964 | -61.7432 | -61.6425 | 54.5151 | 24.1974 | 8.0109 | 7.5897 | 62.1597 | -61.7569 | -0.31586 | 0.059509 | 3.0533 | -0.21515 | -7.6218 | -0.32959 | 0.022888 | 3.3691 | 69.4382 | 69.017 | 115.9424 | 123.6237 | 3.0533 | 123.587 | 85.6247 | -0.32959 | 123.6237 | 3.0533 | 85.6247 | 115.9424 | 123.587 | -123.88 | -123.8937
4593.7188 | 123.7061 | -61.4502 | 62.1414 | 0.16655 | 0.019442 | 0.012345 | 0.014669 | 0.064093 | 0.0011621 | 0.080972 | -58.374 | 62.2238 | -61.7477 | -61.6562 | 54.4785 | 24.1333 | 8.02 | 7.5394 | 62.1735 | -61.7615 | -0.29755 | 0.082398 | 3.0762 | -0.20599 | -7.663 | -0.31128 | 0.032044 | 3.3737 | 69.4702 | 68.9896 | 115.9287 | 123.674 | 3.0762 | 123.6237 | 85.5835 | -0.31128 | 123.674 | 3.0762 | 85.5835 | 115.9287 | 123.6237 | -123.8892 | -123.9029
4594.7188 | 123.7793 | -61.3953 | 62.1048 | 0.21996 | 0.013674 | 0.011064 | 0.0074062 | 0.061316 | -0.00033333 | 0.080758 | -58.3786 | 62.0956 | -61.7157 | -61.6379 | 54.5242 | 24.2661 | 7.9239 | 7.7087 | 62.1368 | -61.702 | -0.32043 | -0.009155 | 3.0167 | -0.24261 | -7.5806 | -0.3067 | 0.032044 | 3.3371 | 69.3192 | 69.104 | 115.9195 | 123.4909 | 3.0167 | 123.5321 | 85.6613 | -0.3067 | 123.4909 | 3.0167 | 85.6613 | 115.9195 | 123.5321 | -123.8205 | -123.8068
4595.7188 | 123.7473 | -61.441 | 62.1643 | 0.56328 | 0.017092 | 0.016618 | 0.016378 | 0.061743 | -0.00011953 | 0.078835 | -58.2779 | 62.2147 | -61.7477 | -61.5784 | 54.5654 | 24.2569 | 7.9971 | 7.7042 | 62.1231 | -61.7386 | -0.3067 | 0.050354 | 3.1631 | -0.13733 | -7.5989 | -0.29755 | -0.041199 | 3.4698 | 69.4382 | 69.1452 | 116.0065 | 123.6557 | 3.1631 | 123.5641 | 85.6979 | -0.29755 | 123.6557 | 3.1631 | 85.6979 | 116.0065 | 123.5641 | -123.912 | -123.9029
4596.7188 | 123.7427 | -61.409 | 62.1414 | -0.016556 | 0.016878 | 0.012132 | 0.014883 | 0.063025 | -0.00054693 | 0.077554 | -58.3328 | 62.1964 | -61.7203 | -61.6104 | 54.5242 | 24.1379 | 8.0292 | 7.6355 | 62.1826 | -61.7523 | -0.31128 | 0.054932 | 3.0762 | -0.20142 | -7.6172 | -0.34332 | 0.041199 | 3.3875 | 69.4382 | 69.0445 | 115.9332 | 123.6053 | 3.0762 | 123.5916 | 85.5469 | -0.34332 | 123.6053 | 3.0762 | 85.5469 | 115.9332 | 123.5916 | -123.8617 | -123.8937
4597.7188 | 123.7198 | -61.441 | 62.1643 | -0.039444 | 0.016665 | 0.017899 | 0.016592 | 0.064093 | -0.0020421 | 0.078408 | -58.3878 | 62.2147 | -61.7569 | -61.6425 | 54.5242 | 24.1379 | 8.0292 | 7.5989 | 62.1597 | -61.7523 | -0.31586 | 0.050354 | 3.0533 | -0.20142 | -7.6401 | -0.31128 | -0.004578 | 3.3691 | 69.4702 | 69.0399 | 115.9653 | 123.6557 | 3.0533 | 123.6008 | 85.5789 | -0.31128 | 123.6557 | 3.0533 | 85.5789 | 115.9653 | 123.6008 | -123.9212 | -123.9166
4598.7188 | 123.7427 | -61.4456 | 62.146 | 0.013962 | 0.018801 | 0.013413 | 0.016378 | 0.065161 | -0.0020421 | 0.080331 | -58.3603 | 62.1643 | -61.7569 | -61.6287 | 54.4968 | 24.0784 | 7.9926 | 7.6126 | 62.2009 | -61.7661 | -0.31128 | 0.018311 | 3.0853 | -0.1831 | -7.6492 | -0.32043 | 0.054932 | 3.3966 | 69.4382 | 69.0582 | 115.9424 | 123.6099 | 3.0853 | 123.6465 | 85.524 | -0.32043 | 123.6099 | 3.0853 | 85.524 | 115.9424 | 123.6465 | -123.9029 | -123.912
4599.7188 | 123.6923 | -61.4273 | 62.1552 | 0.18181 | 0.017947 | 0.015763 | 0.0089016 | 0.064307 | 0.0022303 | 0.079476 | -58.3282 | 62.1964 | -61.7615 | -61.5967 | 54.5334 | 24.0509 | 8.0017 | 7.608 | 62.2009 | -61.7661 | -0.33417 | 0.041199 | 3.0991 | -0.16937 | -7.6218 | -0.33875 | 0.045777 | 3.4332 | 69.429 | 69.0353 | 115.9607 | 123.6237 | 3.0991 | 123.6282 | 85.4782 | -0.33875 | 123.6237 | 3.0991 | 85.4782 | 115.9607 | 123.6282 | -123.9166 | -123.9212
4600.7188 | 123.7564 | -61.4365 | 62.1185 | -0.077591 | 0.017733 | 0.014268 | 0.014242 | 0.065589 | -0.00054693 | 0.078622 | -58.3099 | 62.2101 | -61.7157 | -61.6058 | 54.57 | 24.5544 | 7.9514 | 7.6035 | 62.1552 | -61.7386 | -0.27924 | 0.091553 | 3.1265 | -0.16937 | -7.5485 | -0.30212 | 0.036621 | 3.4058 | 69.3878 | 69.0399 | 116.0065 | 123.6465 | 3.1265 | 123.5916 | 85.9909 | -0.30212 | 123.6465 | 3.1265 | 85.9909 | 116.0065 | 123.5916 | -123.8342 | -123.8571
4601.7188 | 123.7152 | -61.4273 | 62.1735 | -0.13863 | 0.017306 | 0.011277 | 0.012106 | 0.064734 | -0.00076053 | 0.076699 | -58.3878 | 62.2147 | -61.7065 | -61.6379 | 54.5746 | 24.3073 | 8.0338 | 7.6401 | 62.1872 | -61.7386 | -0.27924 | 0.041199 | 3.0396 | -0.21057 | -7.5989 | -0.31128 | 0.013733 | 3.3188 | 69.4611 | 69.0674 | 116.0019 | 123.642 | 3.0396 | 123.6145 | 85.7346 | -0.31128 | 123.642 | 3.0396 | 85.7346 | 116.0019 | 123.6145 | -123.88 | -123.912
4602.7188 | 123.7427 | -61.4319 | 62.178 | -0.1844 | 0.016665 | 0.01555 | 0.01296 | 0.063452 | -0.0011877 | 0.078835 | -58.3511 | 62.2284 | -61.7249 | -61.5738 | 54.5883 | 24.4308 | 8.1024 | 7.7042 | 62.1826 | -61.7111 | -0.29297 | 0.050354 | 3.0808 | -0.14191 | -7.5897 | -0.27924 | 0.004577 | 3.3737 | 69.5343 | 69.136 | 116.0202 | 123.6603 | 3.0808 | 123.6145 | 85.8627 | -0.27924 | 123.6603 | 3.0808 | 85.8627 | 116.0202 | 123.6145 | -123.9029 | -123.8892
4603.7188 | 123.7564 | -61.4182 | 62.146 | -0.131 | 0.014101 | 0.012132 | 0.013601 | 0.064307 | -0.00011953 | 0.077126 | -58.3191 | 62.2009 | -61.7432 | -61.6058 | 54.5792 | 24.3942 | 7.933 | 7.6447 | 62.1964 | -61.7386 | -0.32501 | 0.054932 | 3.0991 | -0.18768 | -7.5668 | -0.32043 | 0.050354 | 3.4241 | 69.3512 | 69.0628 | 115.9973 | 123.6191 | 3.0991 | 123.6145 | 85.8124 | -0.32043 | 123.6191 | 3.0991 | 85.8124 | 115.9973 | 123.6145 | -123.8892 | -123.8846
4604.7344 | 123.8159 | -61.4273 | 62.1185 | 0.25047 | 0.01816 | 0.013627 | 0.010824 | 0.064948 | -0.00011953 | 0.079263 | -58.3786 | 62.146 | -61.7569 | -61.6287 | 54.5837 | 24.5087 | 7.8598 | 7.6126 | 62.1552 | -61.734 | -0.32959 | 0.027466 | 3.0487 | -0.20142 | -7.5348 | -0.3067 | 0.036621 | 3.3783 | 69.2871 | 69.0399 | 116.011 | 123.5733 | 3.0487 | 123.5825 | 85.936 | -0.3067 | 123.5733 | 3.0487 | 85.936 | 116.011 | 123.5825 | -123.8754 | -123.8525
4605.7188 | 123.7656 | -61.4365 | 62.1597 | -0.09285 | 0.015383 | 0.012559 | 0.014242 | 0.064307 | -0.0014013 | 0.082253 | -58.3191 | 62.2055 | -61.7157 | -61.7798 | 54.4189 | 24.5224 | 7.8735 | 7.6172 | 62.1643 | -61.7615 | -0.27924 | 0.045776 | 3.1174 | -0.34332 | -7.7408 | -0.32501 | 0.004578 | 3.3966 | 69.31 | 69.0536 | 115.8554 | 123.642 | 3.1174 | 123.6008 | 85.9589 | -0.32501 | 123.642 | 3.1174 | 85.9589 | 115.8554 | 123.6008 | -123.8754 | -123.9212
4606.7188 | 123.793 | -61.3815 | 62.1689 | -0.28358 | 0.014315 | 0.011491 | 0.011679 | 0.063666 | -0.00011953 | 0.080117 | -58.3328 | 62.2055 | -61.734 | -61.6058 | 54.5242 | 24.4583 | 8.0292 | 7.6721 | 62.2055 | -61.7249 | -0.35248 | 0.036621 | 3.0487 | -0.2243 | -7.6447 | -0.34332 | 0.036621 | 3.4012 | 69.4107 | 69.0537 | 115.9058 | 123.587 | 3.0487 | 123.587 | 85.8398 | -0.34332 | 123.587 | 3.0487 | 85.8398 | 115.9058 | 123.587 | -123.9029 | -123.8937
4607.7188 | 123.7564 | -61.4273 | 62.1689 | -0.23018 | 0.013247 | 0.014482 | 0.013815 | 0.062812 | -0.00076053 | 0.077981 | -58.3832 | 62.1918 | -61.7111 | -61.6104 | 54.5059 | 24.3576 | 8.02 | 7.6492 | 62.2055 | -61.7065 | -0.28381 | 0.022888 | 3.0441 | -0.18311 | -7.663 | -0.27924 | 0.036621 | 3.3279 | 69.4473 | 69.0765 | 115.9332 | 123.6191 | 3.0441 | 123.6328 | 85.7849 | -0.27924 | 123.6191 | 3.0441 | 85.7849 | 115.9332 | 123.6328 | -123.88 | -123.8754
4608.7188 | 123.7427 | -61.4365 | 62.146 | -0.20729 | 0.013888 | 0.012132 | 0.013174 | 0.062598 | -0.00033333 | 0.079049 | -58.374 | 62.2101 | -61.7203 | -61.615 | 54.6021 | 24.4949 | 7.9651 | 7.6218 | 62.2147 | -61.734 | -0.28381 | 0.064087 | 3.0624 | -0.17853 | -7.5439 | -0.29755 | 0.068665 | 3.3463 | 69.4016 | 69.0582 | 116.0385 | 123.6465 | 3.0624 | 123.6511 | 85.9314 | -0.29755 | 123.6465 | 3.0624 | 85.9314 | 116.0385 | 123.6511 | -123.8663 | -123.88
4609.7188 | 123.7152 | -61.4502 | 62.1552 | 0.021591 | 0.016451 | 0.016404 | 0.017233 | 0.063666 | -0.00011953 | 0.080117 | -58.3832 | 62.1826 | -61.7386 | -61.6882 | 54.4418 | 24.4354 | 7.9788 | 7.5531 | 62.1872 | -61.7569 | -0.28839 | 0.027466 | 3.067 | -0.23804 | -7.7133 | -0.3067 | 0.032044 | 3.3554 | 69.429 | 69.0033 | 115.892 | 123.6328 | 3.067 | 123.6374 | 85.8856 | -0.3067 | 123.6328 | 3.067 | 85.8856 | 115.892 | 123.6374 | -123.8937 | -123.912
4610.7188 | 123.7381 | -61.4273 | 62.1872 | -0.16151 | 0.017092 | 0.016618 | 0.011679 | 0.064093 | 0.0018031 | 0.078835 | -58.3649 | 62.1964 | -61.7203 | -61.5921 | 54.538 | 24.4492 | 7.9971 | 7.6309 | 62.2009 | -61.7203 | -0.29297 | 0.009155 | 3.0624 | -0.16479 | -7.6492 | -0.29297 | 0.013733 | 3.3554 | 69.4244 | 69.0582 | 115.9653 | 123.6237 | 3.0624 | 123.6282 | 85.8765 | -0.29297 | 123.6237 | 3.0624 | 85.8765 | 115.9653 | 123.6282 | -123.9075 | -123.9075
4611.7188 | 123.7564 | -61.4365 | 62.1689 | -0.20729 | 0.017092 | 0.011064 | 0.011465 | 0.065161 | -0.00011953 | 0.075417 | -58.3557 | 62.1964 | -61.7477 | -61.6196 | 54.5517 | 24.4949 | 7.9651 | 7.6218 | 62.233 | -61.7386 | -0.31128 | 0.027466 | 3.0807 | -0.18311 | -7.6172 | -0.30212 | 0.064087 | 3.392 | 69.4016 | 69.0582 | 115.9882 | 123.6328 | 3.0807 | 123.6694 | 85.9314 | -0.30212 | 123.6328 | 3.0807 | 85.9314 | 115.9882 | 123.6694 | -123.9166 | -123.9075
4612.7188 | 123.7564 | -61.4227 | 62.1689 | -0.19966 | 0.016665 | 0.0087138 | 0.011251 | 0.064093 | 0.0013757 | 0.079263 | -58.374 | 62.1918 | -61.7477 | -61.6333 | 54.5425 | 24.4904 | 7.9926 | 7.5989 | 62.2375 | -61.7386 | -0.32501 | 0.022888 | 3.0487 | -0.21057 | -7.6263 | -0.31586 | 0.068665 | 3.3737 | 69.4153 | 69.0216 | 115.9653 | 123.6145 | 3.0487 | 123.6603 | 85.9131 | -0.31586 | 123.6145 | 3.0487 | 85.9131 | 115.9653 | 123.6603 | -123.9166 | -123.9075
4613.7188 | 123.7473 | -61.4319 | 62.1506 | -0.16914 | 0.017519 | 0.016404 | 0.011679 | 0.063452 | -0.00033333 | 0.078195 | -58.3282 | 62.178 | -61.7249 | -61.5921 | 54.5425 | 24.4995 | 7.9834 | 7.6309 | 62.2147 | -61.734 | -0.29297 | 0.027466 | 3.1036 | -0.16022 | -7.608 | -0.30212 | 0.064087 | 3.3966 | 69.4153 | 69.0628 | 115.9744 | 123.6099 | 3.1036 | 123.6465 | 85.9314 | -0.30212 | 123.6099 | 3.1036 | 85.9314 | 115.9744 | 123.6465 | -123.8754 | -123.8846
4614.7188 | 123.7518 | -61.4319 | 62.1552 | -0.4438 | 0.016024 | 0.014054 | 0.0082608 | 0.063239 | -0.00033333 | 0.078622 | -58.4244 | 62.1964 | -61.7523 | -61.6379 | 54.5197 | 24.44 | 8.0154 | 7.5989 | 62.1918 | -61.734 | -0.32043 | 0.041199 | 3.0075 | -0.20599 | -7.6355 | -0.30212 | 0.036621 | 3.3279 | 69.4473 | 69.0308 | 115.9515 | 123.6282 | 3.0075 | 123.6237 | 85.8719 | -0.30212 | 123.6282 | 3.0075 | 85.8719 | 115.9515 | 123.6237 | -123.9075 | -123.8892
4615.7188 | 123.7061 | -61.4319 | 62.1918 | -0.38277 | 0.017092 | 0.012559 | 0.011251 | 0.061316 | -0.00097413 | 0.079904 | -58.5388 | 62.1872 | -61.7386 | -61.647 | 54.4876 | 24.4125 | 7.9514 | 7.576 | 62.2238 | -61.7249 | -0.3067 | -0.004577 | 2.8931 | -0.21515 | -7.7042 | -0.29297 | 0.032044 | 3.1998 | 69.3832 | 69.0079 | 115.9195 | 123.6191 | 2.8931 | 123.6557 | 85.8444 | -0.29297 | 123.6191 | 2.8931 | 85.8444 | 115.9195 | 123.6557 | -123.9304 | -123.9166
4616.7188 | 123.7061 | -61.4548 | 62.1826 | -0.22255 | 0.016024 | 0.010423 | 0.0093288 | 0.060248 | 0.0026575 | 0.077981 | -58.3694 | 62.1826 | -61.7386 | -61.7294 | 54.4968 | 24.4629 | 7.869 | 7.5897 | 62.1964 | -61.7386 | -0.28381 | 0 | 3.0853 | -0.27466 | -7.6859 | -0.28381 | 0.013733 | 3.3691 | 69.3237 | 69.0445 | 115.9515 | 123.6374 | 3.0853 | 123.6511 | 85.9177 | -0.28381 | 123.6374 | 3.0853 | 85.9177 | 115.9515 | 123.6511 | -123.9212 | -123.9212
4617.7188 | 123.7427 | -61.4319 | 62.2101 | -0.19966 | 0.014315 | 0.017259 | 0.013174 | 0.062598 | -0.00033333 | 0.080117 | -58.3694 | 62.2055 | -61.7386 | -61.6241 | 54.4785 | 24.3851 | 7.9468 | 7.5943 | 62.2101 | -61.7294 | -0.3067 | -0.004578 | 3.0624 | -0.19226 | -7.7316 | -0.29755 | 0 | 3.3691 | 69.3787 | 69.0262 | 115.9103 | 123.6374 | 3.0624 | 123.642 | 85.817 | -0.29755 | 123.6374 | 3.0624 | 85.817 | 115.9103 | 123.642 | -123.9487 | -123.9395
4618.7188 | 123.7106 | -61.4136 | 62.1872 | -0.27596 | 0.016665 | 0.013627 | 0.012747 | 0.061743 | -0.0022559 | 0.079049 | -58.3786 | 62.1872 | -61.7111 | -61.6241 | 54.4876 | 24.4263 | 7.8552 | 7.5668 | 62.2009 | -61.7249 | -0.29755 | 0 | 3.035 | -0.21057 | -7.6996 | -0.31128 | 0.013733 | 3.3325 | 69.2688 | 68.9804 | 115.9012 | 123.6008 | 3.035 | 123.6145 | 85.8398 | -0.31128 | 123.6008 | 3.035 | 85.8398 | 115.9012 | 123.6145 | -123.8983 | -123.912
4619.7188 | 123.7061 | -61.4365 | 62.1918 | -0.047073 | 0.014956 | 0.011491 | 0.01531 | 0.060675 | 0.00094847 | 0.078622 | -58.3786 | 62.1918 | -61.7294 | -61.6287 | 54.451 | 24.408 | 7.7545 | 7.4982 | 62.2055 | -61.7569 | -0.29297 | 0 | 3.0579 | -0.19226 | -7.7408 | -0.32044 | 0.013733 | 3.3508 | 69.191 | 68.9346 | 115.8875 | 123.6282 | 3.0579 | 123.642 | 85.8444 | -0.32044 | 123.6282 | 3.0579 | 85.8444 | 115.8875 | 123.642 | -123.9212 | -123.9487
4620.7188 | 123.7335 | -61.4273 | 62.1918 | -0.21492 | 0.014315 | 0.0097818 | 0.0089016 | 0.062812 | -0.00097413 | 0.079476 | -58.1726 | 62.1918 | -61.7249 | -61.6013 | 54.4556 | 24.3668 | 7.8461 | 7.5211 | 62.2192 | -61.7065 | -0.29755 | 0 | 3.2547 | -0.17395 | -7.7362 | -0.27924 | 0.027466 | 3.5522 | 69.2734 | 68.9484 | 115.8829 | 123.6191 | 3.2547 | 123.6465 | 85.7941 | -0.27924 | 123.6191 | 3.2547 | 85.7941 | 115.8829 | 123.6465 | -123.9166 | -123.8983
4621.7188 | 123.7564 | -61.4044 | 62.1918 | -0.20729 | 0.016024 | 0.012132 | 0.011892 | 0.062812 | 0.00052127 | 0.077981 | -58.3603 | 62.2101 | -61.7523 | -61.6196 | 54.4418 | 24.3759 | 7.7957 | 7.5531 | 62.2055 | -61.7294 | -0.3479 | 0.018311 | 3.0441 | -0.21515 | -7.7499 | -0.32501 | 0.013733 | 3.392 | 69.2001 | 68.9575 | 115.8463 | 123.6145 | 3.0441 | 123.6099 | 85.7803 | -0.32501 | 123.6145 | 3.0441 | 85.7803 | 115.8463 | 123.6099 | -123.9441 | -123.9212
4622.7188 | 123.7473 | -61.3907 | 62.1506 | -0.30647 | 0.013888 | 0.010423 | 0.0078336 | 0.061957 | -0.0014013 | 0.078408 | -58.3328 | 62.1277 | -61.7203 | -61.5921 | 54.5059 | 24.4446 | 7.7866 | 7.6218 | 62.2055 | -61.6974 | -0.32959 | -0.022888 | 3.0579 | -0.20142 | -7.6447 | -0.3067 | 0.054931 | 3.3875 | 69.1772 | 69.0125 | 115.8966 | 123.5184 | 3.0579 | 123.5962 | 85.8353 | -0.3067 | 123.5184 | 3.0579 | 85.8353 | 115.8966 | 123.5962 | -123.8708 | -123.848
4623.7188 | 123.7061 | -61.441 | 62.1918 | -0.3141 | 0.01581 | 0.011277 | 0.011251 | 0.05918 | 0.00030767 | 0.079263 | -58.374 | 62.1689 | -61.7203 | -61.615 | 54.4785 | 24.4766 | 7.8873 | 7.5806 | 62.2284 | -61.7432 | -0.27924 | -0.022888 | 3.067 | -0.17395 | -7.7133 | -0.30212 | 0.036622 | 3.3463 | 69.3283 | 69.0216 | 115.9195 | 123.6099 | 3.067 | 123.6694 | 85.9177 | -0.30212 | 123.6099 | 3.067 | 85.9177 | 115.9195 | 123.6694 | -123.912 | -123.9349
4624.7344 | 123.7015 | -61.4227 | 62.1597 | 0.052109 | 0.01581 | 0.013627 | 0.017019 | 0.062812 | 0.00030767 | 0.079049 | -58.3832 | 62.1597 | -61.7432 | -61.6562 | 54.4556 | 24.4766 | 7.8827 | 7.5302 | 62.1872 | -61.7615 | -0.32044 | 0 | 3.0395 | -0.23346 | -7.7042 | -0.33875 | 0.027466 | 3.36 | 69.3054 | 68.9529 | 115.8783 | 123.5825 | 3.0395 | 123.6099 | 85.8994 | -0.33875 | 123.5825 | 3.0395 | 85.8994 | 115.8783 | 123.6099 | -123.9029 | -123.9212
4625.7188 | 123.7198 | -61.409 | 62.178 | -0.30647 | 0.015383 | 0.0089274 | 0.0099698 | 0.062384 | 0.00073487 | 0.076913 | -58.4106 | 62.178 | -61.7523 | -61.6745 | 54.538 | 24.3988 | 8.02 | 7.6172 | 62.2192 | -61.7294 | -0.34332 | 0 | 2.9984 | -0.2655 | -7.6401 | -0.32043 | 0.041198 | 3.3417 | 69.429 | 69.0262 | 115.947 | 123.587 | 2.9984 | 123.6282 | 85.8078 | -0.32043 | 123.587 | 2.9984 | 85.8078 | 115.947 | 123.6282 | -123.9304 | -123.9075
4626.7188 | 123.7061 | -61.377 | 62.2101 | -0.26833 | 0.015169 | 0.012132 | 0.008688 | 0.06153 | -0.00076053 | 0.079049 | -58.3969 | 62.1872 | -61.7432 | -61.6241 | 54.4785 | 24.3668 | 8.0566 | 7.5943 | 62.1872 | -61.7203 | -0.36621 | -0.022888 | 2.98 | -0.24719 | -7.7316 | -0.34332 | -0.022888 | 3.3463 | 69.4336 | 68.9713 | 115.8554 | 123.5641 | 2.98 | 123.5641 | 85.7437 | -0.34332 | 123.5641 | 2.98 | 85.7437 | 115.8554 | 123.5641 | -123.9532 | -123.9304
4627.7188 | 123.7518 | -61.4273 | 62.1918 | -0.21492 | 0.014529 | 0.010636 | 0.012106 | 0.061103 | -0.00097413 | 0.079904 | -58.3923 | 62.1826 | -61.7386 | -61.6241 | 54.4556 | 24.4125 | 8.075 | 7.6035 | 62.2147 | -61.6974 | -0.31128 | -0.009155 | 3.035 | -0.19684 | -7.7362 | -0.27008 | 0.022889 | 3.3463 | 69.5023 | 69.0308 | 115.8829 | 123.6099 | 3.035 | 123.642 | 85.8398 | -0.27008 | 123.6099 | 3.035 | 85.8398 | 115.8829 | 123.642 | -123.9304 | -123.8892
4628.7188 | 123.7244 | -61.4227 | 62.1826 | -0.23018 | 0.014315 | 0.0078592 | 0.0095424 | 0.062171 | -0.00076053 | 0.077554 | -58.3878 | 62.1735 | -61.7157 | -61.6196 | 54.4464 | 24.3439 | 8.0521 | 7.6218 | 62.2238 | -61.7065 | -0.29297 | -0.009155 | 3.035 | -0.19684 | -7.7362 | -0.28381 | 0.041199 | 3.3279 | 69.4748 | 69.0445 | 115.8691 | 123.5962 | 3.035 | 123.6465 | 85.7666 | -0.28381 | 123.5962 | 3.035 | 85.7666 | 115.8691 | 123.6465 | -123.8983 | -123.8892
4629.7344 | 123.7793 | -61.4273 | 62.1231 | 0.21996 | 0.016024 | 0.013627 | 0.015738 | 0.063025 | -0.00076053 | 0.080117 | -58.3694 | 62.1277 | -61.7615 | -61.6196 | 54.4785 | 24.3942 | 7.8369 | 7.2464 | 62.1231 | -61.734 | -0.33417 | 0.004578 | 3.0579 | -0.19226 | -7.6447 | -0.3067 | 0 | 3.392 | 69.2642 | 68.6737 | 115.9058 | 123.555 | 3.0579 | 123.5504 | 85.8215 | -0.3067 | 123.555 | 3.0579 | 85.8215 | 115.9058 | 123.5504 | -123.8846 | -123.8571
4630.7188 | 123.7747 | -61.3907 | 62.1689 | -0.23781 | 0.014529 | 0.012132 | 0.010183 | 0.061316 | -0.0016149 | 0.075631 | -58.3328 | 62.146 | -61.7065 | -61.5601 | 54.5609 | 24.4812 | 8.0017 | 7.283 | 62.1597 | -61.7065 | -0.31586 | -0.022888 | 3.0579 | -0.16937 | -7.608 | -0.31586 | -0.009155 | 3.3737 | 69.3924 | 68.6737 | 115.9515 | 123.5367 | 3.0579 | 123.5504 | 85.8719 | -0.31586 | 123.5367 | 3.0579 | 85.8719 | 115.9515 | 123.5504 | -123.8754 | -123.8754
4631.7188 | 123.7106 | -61.3953 | 62.1964 | -0.2607 | 0.013033 | 0.0087138 | 0.0097562 | 0.058539 | 9.4068e-05 | 0.081826 | -58.3832 | 62.1414 | -61.702 | -61.615 | 54.5105 | 24.4354 | 8.1161 | 7.251 | 62.1872 | -61.7065 | -0.3067 | -0.054932 | 3.0121 | -0.21973 | -7.6859 | -0.31128 | -0.009155 | 3.3188 | 69.5114 | 68.6462 | 115.9058 | 123.5367 | 3.0121 | 123.5825 | 85.8307 | -0.31128 | 123.5367 | 3.0121 | 85.8307 | 115.9058 | 123.5825 | -123.8983 | -123.9029
4632.7188 | 123.7335 | -61.4227 | 62.1918 | -0.23018 | 0.014742 | 0.0132 | 0.0093288 | 0.060462 | -0.0020421 | 0.080544 | -58.3466 | 62.1277 | -61.702 | -61.5875 | 54.483 | 24.5453 | 8.0841 | 7.6538 | 62.1735 | -61.6974 | -0.27924 | -0.064086 | 3.0762 | -0.1648 | -7.7087 | -0.27466 | -0.01831 | 3.3554 | 69.5068 | 69.0765 | 115.9058 | 123.5504 | 3.0762 | 123.5962 | 85.968 | -0.27466 | 123.5504 | 3.0762 | 85.968 | 115.9058 | 123.5962 | -123.8937 | -123.8892
4633.7188 | 123.7564 | -61.3678 | 62.1826 | -0.2607 | 0.013888 | 0.0076456 | 0.011038 | 0.060248 | -0.0026831 | 0.080331 | -58.3511 | 62.1185 | -61.7203 | -61.5509 | 54.5288 | 24.5316 | 8.1207 | 7.695 | 62.1643 | -61.6928 | -0.35248 | -0.064087 | 3.0167 | -0.1831 | -7.6538 | -0.32501 | -0.01831 | 3.3691 | 69.4885 | 69.0628 | 115.8966 | 123.4863 | 3.0167 | 123.5321 | 85.8994 | -0.32501 | 123.4863 | 3.0167 | 85.8994 | 115.8966 | 123.5321 | -123.9029 | -123.8754
4634.7344 | 123.8434 | -61.4182 | 62.0911 | 0.15129 | 0.013888 | 0.0099954 | 0.011251 | 0.060889 | -0.00076053 | 0.080544 | -58.3466 | 62.0636 | -61.7294 | -61.5601 | 54.5242 | 24.5178 | 7.9193 | 7.6813 | 62.0865 | -61.7203 | -0.31128 | -0.027465 | 3.0716 | -0.14191 | -7.5668 | -0.30212 | -0.004577 | 3.3829 | 69.3375 | 69.0994 | 115.9424 | 123.4818 | 3.0716 | 123.5046 | 85.936 | -0.30212 | 123.4818 | 3.0716 | 85.936 | 115.9424 | 123.5046 | -123.8205 | -123.8113
4635.7188 | 123.8525 | -61.3861 | 62.1414 | -0.19203 | 0.013033 | 0.010636 | 0.010611 | 0.059607 | -0.00076053 | 0.079476 | -58.3282 | 62.1048 | -61.7157 | -61.5143 | 54.5746 | 24.527 | 7.9193 | 7.3105 | 62.1506 | -61.6882 | -0.32959 | -0.036621 | 3.0579 | -0.12817 | -7.5668 | -0.30212 | 0.009156 | 3.3875 | 69.3054 | 68.6966 | 115.9607 | 123.4909 | 3.0579 | 123.5367 | 85.9131 | -0.30212 | 123.4909 | 3.0579 | 85.9131 | 115.9607 | 123.5367 | -123.8571 | -123.8297
4636.7188 | 123.8617 | -61.3861 | 62.1414 | -0.077591 | 0.012392 | 0.0089274 | 0.0091152 | 0.057898 | -0.00097413 | 0.078195 | -58.3145 | 62.0773 | -61.7111 | -61.4914 | 54.6158 | 24.6094 | 7.8506 | 7.5714 | 62.1368 | -61.6608 | -0.32501 | -0.064086 | 3.0716 | -0.10529 | -7.5256 | -0.27466 | -0.004577 | 3.3966 | 69.2368 | 68.9575 | 116.0019 | 123.4634 | 3.0716 | 123.5229 | 85.9955 | -0.27466 | 123.4634 | 3.0716 | 85.9955 | 116.0019 | 123.5229 | -123.8525 | -123.8022
4637.7188 | 123.8388 | -61.377 | 62.1368 | -0.23018 | 0.011965 | 0.0087138 | 0.0093288 | 0.061957 | 0.00030767 | 0.077767 | -58.3008 | 62.1002 | -61.6837 | -61.4731 | 54.5517 | 24.5407 | 7.9193 | 7.5485 | 62.1185 | -61.6928 | -0.3067 | -0.036621 | 3.0762 | -0.09613 | -7.5851 | -0.31586 | -0.018311 | 3.3829 | 69.2963 | 68.9255 | 115.9287 | 123.4772 | 3.0762 | 123.4955 | 85.9177 | -0.31586 | 123.4772 | 3.0762 | 85.9177 | 115.9287 | 123.4955 | -123.8205 | -123.8297
4638.7188 | 123.8113 | -61.3953 | 62.1506 | -0.26833 | 0.016451 | 0.011704 | 0.012747 | 0.058112 | -0.00033333 | 0.076486 | -58.3145 | 62.0956 | -61.6837 | -61.5097 | 54.5975 | 24.6414 | 7.9651 | 7.663 | 62.1094 | -61.702 | -0.28839 | -0.054932 | 3.0807 | -0.11444 | -7.5531 | -0.3067 | -0.041199 | 3.3691 | 69.3604 | 69.0582 | 115.9927 | 123.4909 | 3.0807 | 123.5046 | 86.0367 | -0.3067 | 123.4909 | 3.0807 | 86.0367 | 115.9927 | 123.5046 | -123.8342 | -123.8525
4639.7188 | 123.793 | -61.409 | 62.1094 | 0.11314 | 0.01346 | 0.0097818 | 0.014669 | 0.058112 | 0.0013757 | 0.078195 | -58.3237 | 62.0728 | -61.7432 | -61.5738 | 54.5654 | 24.7604 | 7.8964 | 7.5668 | 62.0911 | -61.7661 | -0.33417 | -0.036621 | 3.0853 | -0.16479 | -7.5439 | -0.35706 | -0.018311 | 3.4195 | 69.3054 | 68.9758 | 115.9744 | 123.4818 | 3.0853 | 123.5001 | 86.1694 | -0.35706 | 123.4818 | 3.0853 | 86.1694 | 115.9744 | 123.5001 | -123.8525 | -123.8754
4640.7188 | 123.8525 | -61.3724 | 62.1231 | -3.259 | 0.010897 | 0.014482 | 0.012106 | 0.05918 | -0.00054693 | 0.077767 | -58.1726 | 62.146 | -61.6837 | -61.5051 | 54.5517 | 24.646 | 7.9834 | 7.6447 | 62.1002 | -61.6653 | -0.31128 | 0.022888 | 3.1998 | -0.13275 | -7.5714 | -0.29297 | -0.022888 | 3.511 | 69.3558 | 69.017 | 115.9241 | 123.5184 | 3.1998 | 123.4726 | 86.0184 | -0.29297 | 123.5184 | 3.1998 | 86.0184 | 115.9241 | 123.4726 | -123.8068 | -123.7885
4641.7188 | 123.8754 | -61.3815 | 62.114 | -0.19966 | 0.01346 | 0.0095682 | 0.011251 | 0.058112 | -0.00011953 | 0.078408 | -58.2916 | 62.0865 | -61.702 | -61.4914 | 54.5883 | 24.8291 | 8.2031 | 7.3105 | 62.1872 | -61.6608 | -0.32043 | -0.027466 | 3.0899 | -0.10986 | -7.5256 | -0.27924 | 0.073242 | 3.4103 | 69.5847 | 68.692 | 115.9698 | 123.468 | 3.0899 | 123.5687 | 86.2106 | -0.27924 | 123.468 | 3.0899 | 86.2106 | 115.9698 | 123.5687 | -123.8159 | -123.7747
4642.7188 | 123.8388 | -61.3586 | 62.1597 | -0.10048 | 0.012606 | 0.012773 | 0.0099698 | 0.05683 | -0.0011877 | 0.078835 | -58.3054 | 62.0819 | -61.6837 | -61.4868 | 54.5563 | 24.6048 | 7.7683 | 7.5027 | 62.1231 | -61.6699 | -0.32501 | -0.07782 | 3.0533 | -0.12817 | -7.6035 | -0.31128 | -0.036621 | 3.3783 | 69.1269 | 68.8614 | 115.9149 | 123.4406 | 3.0533 | 123.4818 | 85.9634 | -0.31128 | 123.4406 | 3.0533 | 85.9634 | 115.9149 | 123.4818 | -123.8434 | -123.8297
4643.7188 | 123.8754 | -61.3632 | 62.1597 | -0.13863 | 0.012179 | 0.006791 | 0.010824 | 0.055548 | -0.00033333 | 0.077554 | -58.3099 | 62.0682 | -61.7294 | -61.5005 | 54.5837 | 24.614 | 7.7911 | 7.4295 | 62.114 | -61.6425 | -0.36621 | -0.091553 | 3.0533 | -0.13733 | -7.576 | -0.27924 | -0.045776 | 3.4195 | 69.1544 | 68.7927 | 115.947 | 123.4314 | 3.0533 | 123.4772 | 85.9772 | -0.27924 | 123.4314 | 3.0533 | 85.9772 | 115.947 | 123.4772 | -123.8892 | -123.8022
4644.7188 | 123.8251 | -61.3815 | 62.1414 | -0.10811 | 0.014529 | 0.013627 | 0.0095424 | 0.056189 | -0.00054693 | 0.080117 | -58.3282 | 62.0544 | -61.6974 | -61.5143 | 54.5929 | 24.6094 | 7.7454 | 7.3608 | 62.114 | -61.6653 | -0.31586 | -0.086975 | 3.0533 | -0.13275 | -7.5485 | -0.28381 | -0.027465 | 3.3691 | 69.1269 | 68.7424 | 115.9744 | 123.436 | 3.0533 | 123.4955 | 85.9909 | -0.28381 | 123.436 | 3.0533 | 85.9909 | 115.9744 | 123.4955 | -123.8388 | -123.8068
4645.7188 | 123.8525 | -61.3724 | 62.1185 | -0.15388 | 0.016238 | 0.012986 | 0.01296 | 0.058966 | -0.0020421 | 0.079049 | -58.2733 | 62.0956 | -61.6928 | -61.4868 | 54.6112 | 24.5911 | 8.313 | 7.6492 | 62.1964 | -61.6287 | -0.32044 | -0.022888 | 3.0991 | -0.11444 | -7.5073 | -0.25635 | 0.07782 | 3.4195 | 69.6854 | 69.0216 | 115.9836 | 123.468 | 3.0991 | 123.5687 | 85.9634 | -0.25635 | 123.468 | 3.0991 | 85.9634 | 115.9836 | 123.5687 | -123.8113 | -123.7473
4646.7188 | 123.8571 | -61.3724 | 62.1597 | -0.09285 | 0.013888 | 0.012773 | 0.010397 | 0.058753 | -0.0024695 | 0.079049 | -58.3008 | 62.059 | -61.6928 | -61.4639 | 54.6478 | 24.614 | 7.7683 | 7.3929 | 62.1231 | -61.6699 | -0.32044 | -0.10071 | 3.0716 | -0.091553 | -7.5119 | -0.29755 | -0.036621 | 3.392 | 69.1406 | 68.7653 | 116.0202 | 123.4314 | 3.0716 | 123.4955 | 85.9863 | -0.29755 | 123.4314 | 3.0716 | 85.9863 | 116.0202 | 123.4955 | -123.8525 | -123.8297
4647.7188 | 123.8709 | -61.3724 | 62.1597 | -0.14626 | 0.014956 | 0.006791 | 0.011038 | 0.057471 | -0.00033333 | 0.079049 | -58.2962 | 62.0911 | -61.6974 | -61.4731 | 54.6661 | 24.6552 | 7.7408 | 7.4615 | 62.114 | -61.6608 | -0.32501 | -0.068665 | 3.0762 | -0.10071 | -7.4936 | -0.28839 | -0.045776 | 3.4012 | 69.1132 | 68.8339 | 116.0385 | 123.4634 | 3.0762 | 123.4863 | 86.0275 | -0.28839 | 123.4634 | 3.0762 | 86.0275 | 116.0385 | 123.4863 | -123.8571 | -123.8205
4648.7188 | 123.8663 | -61.3541 | 62.1552 | -0.16151 | 0.011751 | 0.010636 | 0.0084744 | 0.057257 | 0.0024439 | 0.077126 | -58.3099 | 62.0911 | -61.6974 | -61.4731 | 54.5975 | 24.6094 | 7.7179 | 7.4982 | 62.114 | -61.647 | -0.34332 | -0.064087 | 3.0441 | -0.11902 | -7.5577 | -0.29297 | -0.041198 | 3.3875 | 69.072 | 68.8522 | 115.9515 | 123.4451 | 3.0441 | 123.468 | 85.9634 | -0.29297 | 123.4451 | 3.0441 | 85.9634 | 115.9515 | 123.468 | -123.8525 | -123.8022
4649.7188 | 123.8342 | -61.3678 | 62.1368 | -0.13863 | 0.014315 | 0.011491 | 0.008688 | 0.05918 | 0.0018031 | 0.078835 | -58.342 | 62.0636 | -61.6974 | -61.4822 | 54.6478 | 24.6185 | 7.782 | 7.5623 | 62.1094 | -61.6516 | -0.32959 | -0.073242 | 3.0258 | -0.11444 | -7.489 | -0.28381 | -0.027466 | 3.3554 | 69.1498 | 68.9301 | 116.0156 | 123.4314 | 3.0258 | 123.4772 | 85.9863 | -0.28381 | 123.4314 | 3.0258 | 85.9863 | 116.0156 | 123.4772 | -123.8342 | -123.7885
4650.7188 | 123.8297 | -61.3953 | 62.1094 | -0.10811 | 0.013033 | 0.011918 | 0.0097562 | 0.05918 | -0.0011877 | 0.07734 | -58.3099 | 62.0499 | -61.7111 | -61.5005 | 54.6066 | 24.6277 | 7.8049 | 7.5806 | 62.1231 | -61.6516 | -0.31586 | -0.059509 | 3.0853 | -0.10529 | -7.5027 | -0.25635 | 0.013733 | 3.4012 | 69.2001 | 68.9758 | 116.0019 | 123.4451 | 3.0853 | 123.5184 | 86.0229 | -0.25635 | 123.4451 | 3.0853 | 86.0229 | 116.0019 | 123.5184 | -123.8205 | -123.761
4651.7188 | 123.8754 | -61.377 | 62.146 | -0.10811 | 0.014315 | 0.0087138 | 0.0093288 | 0.058539 | -0.00076053 | 0.079049 | -58.3191 | 62.0682 | -61.7065 | -61.4914 | 54.6524 | 24.6414 | 7.8461 | 7.5577 | 62.0956 | -61.6608 | -0.32959 | -0.07782 | 3.0579 | -0.11444 | -7.4936 | -0.28381 | -0.050354 | 3.3875 | 69.223 | 68.9346 | 116.0294 | 123.4451 | 3.0579 | 123.4726 | 86.0184 | -0.28381 | 123.4451 | 3.0579 | 86.0184 | 116.0294 | 123.4726 | -123.8525 | -123.8068
4652.7188 | 123.8571 | -61.3953 | 62.1552 | -0.1844 | 0.01346 | 0.013413 | 0.015738 | 0.058325 | -0.0018285 | 0.079904 | -58.4473 | 62.0911 | -61.7111 | -61.5463 | 54.4785 | 24.5773 | 7.8598 | 7.5302 | 62.1277 | -61.6791 | -0.31586 | -0.064087 | 2.948 | -0.15106 | -7.6767 | -0.28381 | -0.027465 | 3.2639 | 69.2551 | 68.9255 | 115.8737 | 123.4863 | 2.948 | 123.5229 | 85.9726 | -0.28381 | 123.4863 | 2.948 | 85.9726 | 115.8737 | 123.5229 | -123.8663 | -123.8342
4653.7188 | 123.8205 | -61.3632 | 62.1414 | -0.1844 | 0.012392 | 0.0085 | 0.0061246 | 0.060248 | -0.00076053 | 0.076486 | -58.2962 | 62.0911 | -61.7157 | -61.5097 | 54.7485 | 24.7192 | 7.8323 | 7.6309 | 62.0865 | -61.6699 | -0.35248 | -0.050354 | 3.067 | -0.14648 | -7.3929 | -0.3067 | -0.054931 | 3.4195 | 69.1956 | 68.9941 | 116.1118 | 123.4543 | 3.067 | 123.4497 | 86.0825 | -0.3067 | 123.4543 | 3.067 | 86.0825 | 116.1118 | 123.4497 | -123.8571 | -123.8113
4654.7188 | 123.7701 | -61.4227 | 62.178 | -0.19966 | 0.016024 | 0.01085 | 0.017019 | 0.059394 | 0.00073487 | 0.077126 | -58.3649 | 62.1918 | -61.7249 | -61.5738 | 54.5197 | 24.6597 | 8.0612 | 7.4387 | 62.1552 | -61.7065 | -0.30213 | 0.013732 | 3.0579 | -0.15106 | -7.6584 | -0.28381 | -0.022889 | 3.36 | 69.4839 | 68.8614 | 115.9424 | 123.6145 | 3.0579 | 123.5779 | 86.0825 | -0.28381 | 123.6145 | 3.0579 | 86.0825 | 115.9424 | 123.5779 | -123.9029 | -123.8846
4655.7188 | 123.8617 | -61.3907 | 62.1414 | -0.16914 | 0.01346 | 0.0095682 | 0.008688 | 0.058966 | -0.0022559 | 0.077126 | -58.2916 | 62.0819 | -61.7111 | -61.2946 | 54.3777 | 24.5087 | 7.9285 | 7.3608 | 62.1002 | -61.6425 | -0.32043 | -0.059509 | 3.0991 | 0.09613 | -7.7637 | -0.25177 | -0.041198 | 3.4195 | 69.3192 | 68.7515 | 115.7684 | 123.4726 | 3.0991 | 123.4909 | 85.8994 | -0.25177 | 123.4726 | 3.0991 | 85.8994 | 115.7684 | 123.4909 | -123.8525 | -123.7839
4656.7188 | 123.7335 | -61.3998 | 62.1826 | -0.24544 | 0.013674 | 0.011704 | 0.01296 | 0.058539 | -0.0020421 | 0.079263 | -58.3511 | 62.1323 | -61.6928 | -61.5784 | 54.5471 | 24.5361 | 7.9651 | 7.3151 | 62.1689 | -61.6837 | -0.29297 | -0.050354 | 3.0487 | -0.17853 | -7.6355 | -0.28381 | -0.013733 | 3.3417 | 69.3649 | 68.7149 | 115.947 | 123.5321 | 3.0487 | 123.5687 | 85.936 | -0.28381 | 123.5321 | 3.0487 | 85.936 | 115.947 | 123.5687 | -123.8754 | -123.8663
4657.7188 | 123.8754 | -61.3953 | 62.146 | -0.17677 | 0.012179 | 0.011064 | 0.0093288 | 0.058753 | -0.0016149 | 0.077554 | -58.287 | 62.0819 | -61.7157 | -61.5005 | 54.3365 | 24.8291 | 8.194 | 7.1686 | 62.146 | -61.6699 | -0.32043 | -0.064087 | 3.1082 | -0.10529 | -7.8094 | -0.27466 | 0 | 3.4287 | 69.5892 | 68.5638 | 115.7318 | 123.4772 | 3.1082 | 123.5413 | 86.2244 | -0.27466 | 123.4772 | 3.1082 | 86.2244 | 115.7318 | 123.5413 | -123.8617 | -123.8159
4658.7188 | 123.7244 | -61.3632 | 62.1185 | -0.1844 | 0.013033 | 0.010423 | 0.0099698 | 0.05918 | -0.0016149 | 0.078622 | -58.2962 | 62.0865 | -61.6837 | -61.4822 | 54.6341 | 24.6689 | 7.8918 | 7.8186 | 62.1689 | -61.615 | -0.32044 | -0.032043 | 3.067 | -0.11902 | -7.4844 | -0.25177 | 0.050354 | 3.3875 | 69.2551 | 69.1818 | 115.9973 | 123.4497 | 3.067 | 123.5321 | 86.0321 | -0.25177 | 123.4497 | 3.067 | 86.0321 | 115.9973 | 123.5321 | -123.8022 | -123.7335
4659.7344 | 123.7839 | -61.4182 | 62.178 | -0.016556 | 0.016878 | 0.011491 | 0.017019 | 0.061103 | 0.00073487 | 0.07734 | -58.4564 | 62.1826 | -61.7523 | -61.5463 | 54.5334 | 24.5819 | 7.9147 | 7.338 | 62.1506 | -61.7477 | -0.33417 | 0.004577 | 2.9617 | -0.12817 | -7.6447 | -0.32959 | -0.027466 | 3.2959 | 69.3329 | 68.7561 | 115.9515 | 123.6008 | 2.9617 | 123.5687 | 86.0001 | -0.32959 | 123.6008 | 2.9617 | 86.0001 | 115.9515 | 123.5687 | -123.9304 | -123.9258
4660.7188 | 123.8342 | -61.3907 | 62.1689 | -0.20729 | 0.012179 | 0.011277 | 0.010183 | 0.058539 | -0.00011953 | 0.07969 | -58.3191 | 62.1094 | -61.7111 | -61.5051 | 54.6204 | 24.6368 | 7.9651 | 7.5027 | 62.1231 | -61.6791 | -0.32043 | -0.059509 | 3.0716 | -0.11444 | -7.5485 | -0.28839 | -0.045776 | 3.392 | 69.3558 | 68.8934 | 116.011 | 123.5001 | 3.0716 | 123.5138 | 86.0275 | -0.28839 | 123.5001 | 3.0716 | 86.0275 | 116.011 | 123.5138 | -123.88 | -123.848
4661.7188 | 123.8388 | -61.3724 | 62.1735 | -0.42091 | 0.013247 | 0.0093546 | 0.0089016 | 0.059821 | -0.0016149 | 0.077981 | -58.3099 | 62.1002 | -61.7065 | -61.5189 | 54.6616 | 24.6323 | 7.933 | 7.4249 | 62.146 | -61.6745 | -0.33417 | -0.073242 | 3.0624 | -0.14648 | -7.5119 | -0.30213 | -0.027466 | 3.3966 | 69.3054 | 68.7973 | 116.0339 | 123.4726 | 3.0624 | 123.5184 | 86.0046 | -0.30213 | 123.4726 | 3.0624 | 86.0046 | 116.0339 | 123.5184 | -123.88 | -123.848
4662.7188 | 123.8525 | -61.3907 | 62.1506 | -0.58113 | 0.011965 | 0.011064 | 0.0099698 | 0.058753 | -0.0018285 | 0.07969 | -58.3557 | 62.0865 | -61.7157 | -61.5097 | 54.6661 | 24.6918 | 8.0154 | 7.6309 | 62.1094 | -61.6837 | -0.32501 | -0.064087 | 3.035 | -0.11902 | -7.4844 | -0.29297 | -0.041199 | 3.36 | 69.4061 | 69.0216 | 116.0568 | 123.4772 | 3.035 | 123.5001 | 86.0825 | -0.29297 | 123.4772 | 3.035 | 86.0825 | 116.0568 | 123.5001 | -123.8663 | -123.8342
4663.7188 | 123.8663 | -61.3678 | 62.1414 | -0.21492 | 0.013674 | 0.012986 | 0.0093288 | 0.057685 | 0.00094847 | 0.07969 | -58.3145 | 62.0682 | -61.6882 | -61.4914 | 54.6616 | 24.678 | 7.9193 | 7.7179 | 62.1094 | -61.647 | -0.32043 | -0.073242 | 3.0533 | -0.1236 | -7.4799 | -0.27924 | -0.032043 | 3.3737 | 69.2871 | 69.0857 | 116.0294 | 123.436 | 3.0533 | 123.4772 | 86.0458 | -0.27924 | 123.436 | 3.0533 | 86.0458 | 116.0294 | 123.4772 | -123.8297 | -123.7885
4664.7188 | 123.7885 | -61.377 | 62.1826 | -0.27596 | 0.014742 | 0.010209 | 0.012747 | 0.058325 | -0.0018285 | 0.07734 | -58.3145 | 62.1048 | -61.7111 | -61.5234 | 54.5929 | 24.646 | 8.0109 | 7.6355 | 62.1231 | -61.6791 | -0.33417 | -0.07782 | 3.0624 | -0.14648 | -7.5897 | -0.30212 | -0.059509 | 3.3966 | 69.3878 | 69.0125 | 115.9698 | 123.4818 | 3.0624 | 123.5001 | 86.0229 | -0.30212 | 123.4818 | 3.0624 | 86.0229 | 115.9698 | 123.5001 | -123.8937 | -123.8617
4665.7188 | 123.7885 | -61.3953 | 62.1552 | -0.21492 | 0.013247 | 0.012345 | 0.0097562 | 0.057898 | -0.00011953 | 0.078835 | -58.3054 | 62.1094 | -61.7157 | -61.5372 | 54.5883 | 24.6506 | 7.9559 | 7.5394 | 62.1231 | -61.6791 | -0.32043 | -0.045776 | 3.0899 | -0.14191 | -7.5668 | -0.28381 | -0.032043 | 3.4103 | 69.3512 | 68.9346 | 115.9836 | 123.5046 | 3.0899 | 123.5184 | 86.0458 | -0.28381 | 123.5046 | 3.0899 | 86.0458 | 115.9836 | 123.5184 | -123.8708 | -123.8342
4666.7188 | 123.8022 | -61.3632 | 62.1506 | -0.20729 | 0.011111 | 0.0089274 | 0.0097562 | 0.058325 | 0.00030767 | 0.079049 | -58.3099 | 62.1002 | -61.7111 | -61.5372 | 54.5746 | 24.5407 | 7.9971 | 7.7728 | 62.1094 | -61.6837 | -0.3479 | -0.050354 | 3.0533 | -0.17395 | -7.576 | -0.32044 | -0.041199 | 3.4012 | 69.3604 | 69.136 | 115.9378 | 123.4634 | 3.0533 | 123.4726 | 85.9039 | -0.32044 | 123.4634 | 3.0533 | 85.9039 | 115.9378 | 123.4726 | -123.8617 | -123.8342
4667.7188 | 123.8113 | -61.3678 | 62.1689 | -0.16914 | 0.0091879 | 0.013841 | 0.010824 | 0.058112 | -0.0016149 | 0.07969 | -58.3054 | 62.114 | -61.7294 | -61.5326 | 54.6066 | 24.614 | 7.9788 | 7.7911 | 62.1277 | -61.6699 | -0.36163 | -0.054931 | 3.0624 | -0.16479 | -7.5623 | -0.30212 | -0.041198 | 3.4241 | 69.3466 | 69.1589 | 115.9744 | 123.4818 | 3.0624 | 123.4955 | 85.9818 | -0.30212 | 123.4818 | 3.0624 | 85.9818 | 115.9744 | 123.4955 | -123.8983 | -123.8388
4668.7188 | 123.8113 | -61.3678 | 62.1506 | -0.19966 | 0.013888 | 0.011918 | 0.011465 | 0.059607 | 9.4068e-05 | 0.079049 | -58.3145 | 62.0773 | -61.7157 | -61.528 | 54.6066 | 24.6552 | 7.9788 | 7.7454 | 62.1323 | -61.6837 | -0.3479 | -0.073242 | 3.0533 | -0.16022 | -7.5439 | -0.31586 | -0.018311 | 3.4012 | 69.3466 | 69.1132 | 115.9744 | 123.4451 | 3.0533 | 123.5001 | 86.0229 | -0.31586 | 123.4451 | 3.0533 | 86.0229 | 115.9744 | 123.5001 | -123.8663 | -123.8342
4669.7344 | 123.7152 | -61.3998 | 62.1414 | 0.013962 | 0.016665 | 0.014695 | 0.017874 | 0.061103 | -0.00011953 | 0.078195 | -58.3282 | 62.1643 | -61.7294 | -61.6058 | 54.5197 | 24.5499 | 8.0154 | 7.4249 | 62.1323 | -61.7294 | -0.32959 | 0.022889 | 3.0716 | -0.20599 | -7.6218 | -0.32959 | -0.009155 | 3.4012 | 69.4153 | 68.8248 | 115.9195 | 123.5641 | 3.0716 | 123.5321 | 85.9497 | -0.32959 | 123.5641 | 3.0716 | 85.9497 | 115.9195 | 123.5321 | -123.8708 | -123.8708
4670.7188 | 123.8388 | -61.3815 | 62.1643 | -0.21492 | 0.013247 | 0.007432 | 0.010397 | 0.060675 | 0.00030767 | 0.078622 | -58.2916 | 62.0956 | -61.702 | -61.5189 | 54.6158 | 24.6918 | 7.8506 | 7.7454 | 62.1414 | -61.6608 | -0.32043 | -0.068665 | 3.0899 | -0.13733 | -7.5485 | -0.27924 | -0.022889 | 3.4103 | 69.2322 | 69.1269 | 115.9973 | 123.4772 | 3.0899 | 123.5229 | 86.0733 | -0.27924 | 123.4772 | 3.0899 | 86.0733 | 115.9973 | 123.5229 | -123.8663 | -123.8251
4671.7188 | 123.7793 | -61.4182 | 62.1597 | -0.24544 | 0.013888 | 0.0089274 | 0.010397 | 0.060034 | -0.0028967 | 0.07734 | -58.3282 | 62.1414 | -61.7294 | -61.5509 | 54.5837 | 24.6643 | 7.9514 | 7.6447 | 62.1506 | -61.6837 | -0.31128 | -0.018311 | 3.0899 | -0.13275 | -7.576 | -0.2655 | -0.009155 | 3.4012 | 69.3695 | 69.0628 | 116.0019 | 123.5596 | 3.0899 | 123.5687 | 86.0825 | -0.2655 | 123.5596 | 3.0899 | 86.0825 | 116.0019 | 123.5687 | -123.8892 | -123.8434
4672.7188 | 123.7656 | -61.3861 | 62.1872 | -0.23781 | 0.013888 | 0.0093546 | 0.013601 | 0.061103 | -0.0018285 | 0.077981 | -58.3191 | 62.1185 | -61.7111 | -61.5509 | 54.5792 | 24.5773 | 7.988 | 7.489 | 62.1506 | -61.6882 | -0.32501 | -0.068665 | 3.067 | -0.16479 | -7.608 | -0.30212 | -0.036621 | 3.392 | 69.3741 | 68.8751 | 115.9653 | 123.5046 | 3.067 | 123.5367 | 85.9634 | -0.30212 | 123.5046 | 3.067 | 85.9634 | 115.9653 | 123.5367 | -123.8983 | -123.8754
4673.7188 | 123.7793 | -61.4227 | 62.1643 | -0.25307 | 0.01282 | 0.0097818 | 0.0091152 | 0.057685 | -0.00033333 | 0.078408 | -58.3282 | 62.1094 | -61.7157 | -61.5646 | 54.5609 | 24.6506 | 7.9926 | 7.6813 | 62.1185 | -61.6562 | -0.29297 | -0.054932 | 3.0945 | -0.14191 | -7.6035 | -0.23346 | -0.045777 | 3.3875 | 69.4153 | 69.104 | 115.9836 | 123.5321 | 3.0945 | 123.5413 | 86.0733 | -0.23346 | 123.5321 | 3.0945 | 86.0733 | 115.9836 | 123.5413 | -123.88 | -123.8205
4674.7188 | 123.761 | -61.4365 | 62.1414 | 0.0063326 | 0.015383 | 0.012773 | 0.019156 | 0.059821 | -0.00011953 | 0.07969 | -58.3145 | 62.2101 | -61.7157 | -61.5738 | 54.5334 | 24.6002 | 7.9605 | 7.5897 | 62.1414 | -61.734 | -0.27924 | 0.068665 | 3.1219 | -0.13733 | -7.608 | -0.29755 | 0 | 3.4012 | 69.397 | 69.0262 | 115.9698 | 123.6465 | 3.1219 | 123.5779 | 86.0367 | -0.29755 | 123.6465 | 3.1219 | 86.0367 | 115.9698 | 123.5779 | -123.8571 | -123.8754
4675.7188 | 123.793 | -61.4136 | 62.1643 | -0.23018 | 0.013888 | 0.010209 | 0.011465 | 0.061957 | -0.00054693 | 0.078622 | -58.3191 | 62.1048 | -61.702 | -61.5417 | 54.5837 | 24.6918 | 8.0338 | 7.7728 | 62.1643 | -61.6653 | -0.28839 | -0.05951 | 3.0945 | -0.12817 | -7.5806 | -0.25177 | 0 | 3.3829 | 69.4473 | 69.1864 | 115.9973 | 123.5184 | 3.0945 | 123.5779 | 86.1053 | -0.25177 | 123.5184 | 3.0945 | 86.1053 | 115.9973 | 123.5779 | -123.8663 | -123.8297
4676.7188 | 123.7885 | -61.3907 | 62.1597 | -0.24544 | 0.01581 | 0.0076456 | 0.010183 | 0.060248 | -0.00033333 | 0.078622 | -58.3282 | 62.114 | -61.7065 | -61.5326 | 54.5837 | 24.6277 | 8.0338 | 7.6859 | 62.1323 | -61.6653 | -0.31586 | -0.045776 | 3.0624 | -0.14191 | -7.576 | -0.27466 | -0.027466 | 3.3783 | 69.4244 | 69.0765 | 115.9744 | 123.5046 | 3.0624 | 123.5229 | 86.0184 | -0.27466 | 123.5046 | 3.0624 | 86.0184 | 115.9744 | 123.5229 | -123.8663 | -123.8251
4677.7188 | 123.8113 | -61.3907 | 62.1735 | -0.1844 | 0.013247 | 0.0099954 | 0.012106 | 0.059394 | -0.00097413 | 0.079904 | -58.3282 | 62.1185 | -61.702 | -61.5463 | 54.6112 | 24.6552 | 8.0475 | 7.7728 | 62.114 | -61.6791 | -0.31128 | -0.054932 | 3.0624 | -0.15564 | -7.5623 | -0.28839 | -0.059509 | 3.3737 | 69.4382 | 69.1635 | 116.0019 | 123.5092 | 3.0624 | 123.5046 | 86.0458 | -0.28839 | 123.5092 | 3.0624 | 86.0458 | 116.0019 | 123.5046 | -123.8754 | -123.8525
4678.7188 | 123.7885 | -61.3907 | 62.1597 | -0.16151 | 0.014956 | 0.0095682 | 0.011679 | 0.058966 | -0.0016149 | 0.078195 | -58.3466 | 62.0865 | -61.7065 | -61.5326 | 54.6112 | 24.7238 | 8.0521 | 7.901 | 62.1231 | -61.6745 | -0.31586 | -0.073242 | 3.0441 | -0.14191 | -7.5485 | -0.28381 | -0.036621 | 3.36 | 69.4427 | 69.2917 | 116.0019 | 123.4772 | 3.0441 | 123.5138 | 86.1145 | -0.28381 | 123.4772 | 3.0441 | 86.1145 | 116.0019 | 123.5138 | -123.8663 | -123.8342
4679.7188 | 123.7152 | -61.4227 | 62.1735 | -0.30647 | 0.014101 | 0.010636 | 0.01531 | 0.057685 | -0.0018285 | 0.079904 | -58.3969 | 62.1735 | -61.7249 | -61.7798 | 54.4052 | 24.4629 | 8.1848 | 7.6035 | 62.1414 | -61.7386 | -0.30213 | 0 | 3.0258 | -0.35706 | -7.7683 | -0.31586 | -0.032044 | 3.3279 | 69.6075 | 69.0262 | 115.8279 | 123.5962 | 3.0258 | 123.5641 | 85.8856 | -0.31586 | 123.5962 | 3.0258 | 85.8856 | 115.8279 | 123.5641 | -123.8983 | -123.912
4680.7188 | 123.7473 | -61.4227 | 62.1918 | -0.23018 | 0.013674 | 0.007432 | 0.011892 | 0.058325 | -0.0026831 | 0.077981 | -58.3328 | 62.1323 | -61.7065 | -61.5784 | 54.57 | 24.5911 | 8.0338 | 7.6126 | 62.1506 | -61.6882 | -0.28381 | -0.059509 | 3.0899 | -0.15564 | -7.6218 | -0.2655 | -0.041198 | 3.3737 | 69.4565 | 69.0353 | 115.9927 | 123.555 | 3.0899 | 123.5733 | 86.0138 | -0.2655 | 123.555 | 3.0899 | 86.0138 | 115.9927 | 123.5733 | -123.8983 | -123.88
4681.7188 | 123.7289 | -61.3861 | 62.1735 | -0.2607 | 0.013674 | 0.009141 | 0.0099698 | 0.059821 | -0.0024695 | 0.078622 | -58.3374 | 62.1368 | -61.7111 | -61.5738 | 54.5517 | 24.6094 | 8.0566 | 7.7362 | 62.1552 | -61.6745 | -0.32501 | -0.036621 | 3.0487 | -0.18768 | -7.6218 | -0.28839 | -0.018311 | 3.3737 | 69.4427 | 69.1223 | 115.9378 | 123.5229 | 3.0487 | 123.5413 | 85.9955 | -0.28839 | 123.5229 | 3.0487 | 85.9955 | 115.9378 | 123.5413 | -123.8846 | -123.848
4682.7188 | 123.7839 | -61.4044 | 62.1689 | -0.29121 | 0.015169 | 0.011491 | 0.010397 | 0.059607 | -0.0014013 | 0.078408 | -58.3282 | 62.1185 | -61.7157 | -61.5555 | 54.5609 | 24.5132 | 8.0109 | 7.6721 | 62.1643 | -61.7111 | -0.31128 | -0.050354 | 3.0762 | -0.15106 | -7.608 | -0.3067 | -0.004577 | 3.3875 | 69.4153 | 69.0765 | 115.9653 | 123.5229 | 3.0762 | 123.5687 | 85.9177 | -0.3067 | 123.5229 | 3.0762 | 85.9177 | 115.9653 | 123.5687 | -123.8846 | -123.88
4683.7188 | 123.7839 | -61.409 | 62.1597 | -0.32173 | 0.013674 | 0.011277 | 0.01232 | 0.057685 | -0.0026831 | 0.075845 | -58.3328 | 62.1048 | -61.7111 | -61.5509 | 54.5746 | 24.5087 | 7.9742 | 7.6996 | 62.1597 | -61.6653 | -0.30212 | -0.054932 | 3.0762 | -0.14191 | -7.5851 | -0.25635 | 0 | 3.3783 | 69.3832 | 69.1086 | 115.9836 | 123.5138 | 3.0762 | 123.5687 | 85.9177 | -0.25635 | 123.5138 | 3.0762 | 85.9177 | 115.9836 | 123.5687 | -123.8708 | -123.8251
4684.7188 | 123.7701 | -61.3998 | 62.2009 | -0.2607 | 0.016878 | 0.013413 | 0.017019 | 0.061103 | -0.0016149 | 0.077554 | -58.3282 | 62.1872 | -61.7432 | -61.5555 | 54.5471 | 24.4217 | 7.8827 | 7.338 | 62.1735 | -61.7249 | -0.34332 | -0.013733 | 3.0716 | -0.15564 | -7.6538 | -0.32501 | -0.027466 | 3.4149 | 69.2825 | 68.7378 | 115.947 | 123.587 | 3.0716 | 123.5733 | 85.8215 | -0.32501 | 123.587 | 3.0716 | 85.8215 | 115.947 | 123.5733 | -123.9441 | -123.9258
4685.7188 | 123.7198 | -61.409 | 62.1826 | -0.35225 | 0.014742 | 0.0097818 | 0.012747 | 0.059607 | -0.0033239 | 0.076699 | -58.3466 | 62.1826 | -61.7523 | -61.615 | 54.5425 | 24.4995 | 7.9514 | 7.2784 | 62.178 | -61.7111 | -0.34332 | 0 | 3.0624 | -0.20599 | -7.6401 | -0.30212 | -0.004577 | 3.4058 | 69.3604 | 68.6874 | 115.9515 | 123.5916 | 3.0624 | 123.587 | 85.9085 | -0.30212 | 123.5916 | 3.0624 | 85.9085 | 115.9515 | 123.587 | -123.9349 | -123.8937
4686.7188 | 123.7289 | -61.4319 | 62.1964 | -0.23018 | 0.014529 | 0.014695 | 0.013815 | 0.060034 | -0.0024695 | 0.079049 | -58.3557 | 62.1368 | -61.7157 | -61.6013 | 54.4922 | 24.5087 | 7.9834 | 7.4478 | 62.1643 | -61.6882 | -0.28381 | -0.059509 | 3.0762 | -0.16937 | -7.7042 | -0.25635 | -0.032043 | 3.36 | 69.4153 | 68.8797 | 115.9241 | 123.5687 | 3.0762 | 123.5962 | 85.9406 | -0.25635 | 123.5687 | 3.0762 | 85.9406 | 115.9241 | 123.5962 | -123.912 | -123.8846
4687.7188 | 123.7381 | -61.4273 | 62.1826 | -0.26833 | 0.015597 | 0.011918 | 0.016592 | 0.061103 | -0.0014013 | 0.079476 | -58.493 | 62.1872 | -61.7157 | -61.6379 | 54.483 | 24.408 | 7.9971 | 7.3151 | 62.1552 | -61.7203 | -0.28839 | 0.004578 | 2.9343 | -0.21057 | -7.6996 | -0.29297 | -0.027466 | 3.2227 | 69.4244 | 68.7424 | 115.9103 | 123.6145 | 2.9343 | 123.5825 | 85.8353 | -0.29297 | 123.6145 | 2.9343 | 85.8353 | 115.9103 | 123.5825 | -123.8983 | -123.9029
4688.7188 | 123.761 | -61.4044 | 62.2055 | -0.25307 | 0.013033 | 0.0132 | 0.011892 | 0.058112 | -0.00097413 | 0.07734 | -58.3466 | 62.1414 | -61.7111 | -61.5784 | 54.5288 | 24.5132 | 8.0658 | 7.4432 | 62.1597 | -61.6745 | -0.3067 | -0.064087 | 3.0579 | -0.17395 | -7.6767 | -0.27008 | -0.045776 | 3.3646 | 69.4702 | 68.8477 | 115.9332 | 123.5458 | 3.0579 | 123.5641 | 85.9177 | -0.27008 | 123.5458 | 3.0579 | 85.9177 | 115.9332 | 123.5641 | -123.9166 | -123.88
4689.7188 | 123.7793 | -61.4273 | 62.1643 | -0.16151 | 0.015383 | 0.011491 | 0.017447 | 0.060248 | -0.0028967 | 0.080331 | -58.3328 | 62.2192 | -61.7294 | -61.5509 | 54.5654 | 24.5316 | 8.0338 | 7.402 | 62.1597 | -61.7157 | -0.30212 | 0.054931 | 3.0945 | -0.1236 | -7.5989 | -0.28839 | -0.004578 | 3.3966 | 69.4611 | 68.8293 | 115.9927 | 123.6465 | 3.0945 | 123.587 | 85.9589 | -0.28839 | 123.6465 | 3.0945 | 85.9589 | 115.9927 | 123.587 | -123.8937 | -123.88
4690.7188 | 123.7747 | -61.4136 | 62.1689 | -0.21492 | 0.013247 | 0.012773 | 0.0091152 | 0.060462 | -0.0022559 | 0.078195 | -58.3145 | 62.1231 | -61.7203 | -61.5646 | 54.6341 | 24.4629 | 8.0154 | 7.457 | 62.1826 | -61.6516 | -0.3067 | -0.045776 | 3.0991 | -0.15106 | -7.5348 | -0.23804 | 0.013733 | 3.4058 | 69.429 | 68.8705 | 116.0477 | 123.5367 | 3.0991 | 123.5962 | 85.8765 | -0.23804 | 123.5367 | 3.0991 | 85.8765 | 116.0477 | 123.5962 | -123.8892 | -123.8205
4691.7188 | 123.8159 | -61.3861 | 62.1231 | -0.1844 | 0.01346 | 0.0076456 | 0.0061246 | 0.060889 | -0.00054693 | 0.079904 | -58.3191 | 62.0911 | -61.6837 | -61.615 | 54.7348 | 24.5178 | 7.8415 | 7.5577 | 62.0956 | -61.6745 | -0.29755 | -0.032044 | 3.067 | -0.22888 | -7.3883 | -0.28839 | -0.027466 | 3.3646 | 69.2276 | 68.9438 | 116.1209 | 123.4772 | 3.067 | 123.4818 | 85.9039 | -0.28839 | 123.4772 | 3.067 | 85.9039 | 116.1209 | 123.4818 | -123.8068 | -123.7976
4692.7188 | 123.7244 | -61.4227 | 62.178 | -0.30647 | 0.012392 | 0.0095682 | 0.012106 | 0.057257 | -0.0035375 | 0.080972 | -58.3878 | 62.1643 | -61.734 | -61.6928 | 54.5425 | 24.3805 | 8.0978 | 7.4341 | 62.1643 | -61.7294 | -0.31128 | -0.013733 | 3.035 | -0.27008 | -7.6355 | -0.3067 | -0.013733 | 3.3463 | 69.5206 | 68.8568 | 115.9653 | 123.587 | 3.035 | 123.587 | 85.8032 | -0.3067 | 123.587 | 3.035 | 85.8032 | 115.9653 | 123.587 | -123.912 | -123.9075
4693.7188 | 123.7381 | -61.4044 | 62.1826 | -0.30647 | 0.015169 | 0.011491 | 0.014883 | 0.058325 | -0.00097413 | 0.079476 | -58.3328 | 62.1323 | -61.6928 | -61.5646 | 54.5517 | 24.2844 | 7.9742 | 7.4203 | 62.1552 | -61.6745 | -0.28839 | -0.050354 | 3.0716 | -0.16022 | -7.6309 | -0.27008 | -0.027466 | 3.36 | 69.3787 | 68.8248 | 115.9561 | 123.5367 | 3.0716 | 123.5596 | 85.6888 | -0.27008 | 123.5367 | 3.0716 | 85.6888 | 115.9561 | 123.5596 | -123.8754 | -123.8571
4694.7188 | 123.7564 | -61.4044 | 62.1872 | -0.2607 | 0.014529 | 0.01085 | 0.015951 | 0.059607 | -0.0022559 | 0.077981 | -58.3374 | 62.1964 | -61.7065 | -61.5601 | 54.5425 | 24.2615 | 7.9971 | 7.4799 | 62.1643 | -61.7294 | -0.30212 | 0.009155 | 3.067 | -0.15564 | -7.6447 | -0.32501 | -0.022888 | 3.3691 | 69.4016 | 68.8843 | 115.947 | 123.6008 | 3.067 | 123.5687 | 85.6659 | -0.32501 | 123.6008 | 3.067 | 85.6659 | 115.947 | 123.5687 | -123.8937 | -123.9166
4695.7188 | 123.7106 | -61.4502 | 62.1826 | -0.50484 | 0.014742 | 0.013841 | 0.012106 | 0.058966 | -0.0020421 | 0.078835 | -58.3694 | 62.1643 | -61.7203 | -61.6241 | 54.4418 | 24.0829 | 8.1802 | 7.5211 | 62.2101 | -61.7065 | -0.27008 | -0.01831 | 3.0807 | -0.17395 | -7.7408 | -0.25635 | 0.027466 | 3.3508 | 69.6304 | 68.9713 | 115.892 | 123.6145 | 3.0807 | 123.6603 | 85.5331 | -0.25635 | 123.6145 | 3.0807 | 85.5331 | 115.892 | 123.6603 | -123.9029 | -123.8892
4696.7188 | 123.793 | -61.3815 | 62.1643 | -0.17677 | 0.014956 | 0.01085 | 0.0082608 | 0.060034 | -0.0016149 | 0.078835 | -58.3054 | 62.1185 | -61.6699 | -61.5372 | 54.5792 | 24.2844 | 7.9102 | 7.6172 | 62.1506 | -61.6425 | -0.28839 | -0.045777 | 3.0762 | -0.15564 | -7.5851 | -0.26093 | -0.013733 | 3.3646 | 69.2917 | 68.9987 | 115.9607 | 123.5001 | 3.0762 | 123.5321 | 85.6659 | -0.26093 | 123.5001 | 3.0762 | 85.6659 | 115.9607 | 123.5321 | -123.8342 | -123.8068
4697.7188 | 123.793 | -61.3815 | 62.1552 | -0.14626 | 0.012392 | 0.0097818 | 0.011038 | 0.058325 | -0.0020421 | 0.077981 | -58.3145 | 62.1002 | -61.6837 | -61.5417 | 54.5654 | 24.3301 | 7.9239 | 7.5485 | 62.114 | -61.6562 | -0.30212 | -0.054931 | 3.067 | -0.16022 | -7.5897 | -0.27466 | -0.041198 | 3.3691 | 69.3054 | 68.9301 | 115.947 | 123.4818 | 3.067 | 123.4955 | 85.7117 | -0.27466 | 123.4818 | 3.067 | 85.7117 | 115.947 | 123.4955 | -123.8388 | -123.8113
4698.7188 | 123.8388 | -61.3724 | 62.146 | -0.14626 | 0.01346 | 0.01085 | 0.011892 | 0.060462 | -0.0016149 | 0.07969 | -58.2825 | 62.114 | -61.7294 | -61.5189 | 54.5746 | 24.4675 | 7.9697 | 7.5577 | 62.146 | -61.6699 | -0.35706 | -0.032043 | 3.0899 | -0.14648 | -7.5714 | -0.29755 | 0 | 3.447 | 69.342 | 68.9301 | 115.947 | 123.4863 | 3.0899 | 123.5184 | 85.8398 | -0.29755 | 123.4863 | 3.0899 | 85.8398 | 115.947 | 123.5184 | -123.8754 | -123.8159
4699.7188 | 123.793 | -61.409 | 62.1552 | -0.15388 | 0.017733 | 0.012986 | 0.017019 | 0.059821 | -0.00076053 | 0.075845 | -58.3191 | 62.2192 | -61.6974 | -61.5646 | 54.5013 | 24.2157 | 8.0292 | 7.5394 | 62.1414 | -61.7249 | -0.28839 | 0.064087 | 3.0899 | -0.15564 | -7.6538 | -0.31586 | -0.013733 | 3.3783 | 69.4382 | 68.9484 | 115.9103 | 123.6282 | 3.0899 | 123.5504 | 85.6247 | -0.31586 | 123.6282 | 3.0899 | 85.6247 | 115.9103 | 123.5504 | -123.8525 | -123.88
4700.7188 | 123.8159 | -61.3953 | 62.178 | -0.23018 | 0.01346 | 0.01085 | 0.0091152 | 0.060248 | -0.0031103 | 0.07734 | -58.3145 | 62.1002 | -61.7157 | -61.5509 | 54.5837 | 24.4583 | 7.9514 | 7.4661 | 62.1414 | -61.6699 | -0.32043 | -0.07782 | 3.0807 | -0.15564 | -7.5943 | -0.27466 | -0.036622 | 3.4012 | 69.3466 | 68.8614 | 115.979 | 123.4955 | 3.0807 | 123.5367 | 85.8536 | -0.27466 | 123.4955 | 3.0807 | 85.8536 | 115.979 | 123.5367 | -123.8937 | -123.848
4701.7188 | 123.7885 | -61.3724 | 62.1552 | -0.17677 | 0.011538 | 0.0099954 | 0.0091152 | 0.060462 | -0.0033239 | 0.077126 | -58.3145 | 62.1094 | -61.7157 | -61.5417 | 54.5242 | 24.3073 | 8.0475 | 7.5485 | 62.1597 | -61.6791 | -0.34332 | -0.045776 | 3.0579 | -0.16937 | -7.6309 | -0.3067 | 0.004578 | 3.4012 | 69.4199 | 68.9209 | 115.8966 | 123.4818 | 3.0579 | 123.5321 | 85.6796 | -0.3067 | 123.4818 | 3.0579 | 85.6796 | 115.8966 | 123.5321 | -123.8708 | -123.8342
4702.7188 | 123.8205 | -61.377 | 62.1506 | -0.19966 | 0.0098287 | 0.011064 | 0.010611 | 0.060034 | -0.0022559 | 0.076913 | -58.2962 | 62.1094 | -61.7157 | -61.5372 | 54.5425 | 24.3713 | 8.0475 | 7.7271 | 62.1323 | -61.7111 | -0.33875 | -0.041199 | 3.0807 | -0.16022 | -7.608 | -0.33417 | -0.018311 | 3.4195 | 69.4244 | 69.104 | 115.9195 | 123.4863 | 3.0807 | 123.5092 | 85.7483 | -0.33417 | 123.4863 | 3.0807 | 85.7483 | 115.9195 | 123.5092 | -123.8663 | -123.8617
4703.7188 | 123.7381 | -61.3907 | 62.1826 | -0.21492 | 0.014742 | 0.0099954 | 0.013601 | 0.058753 | -0.0016149 | 0.077767 | -58.3557 | 62.1506 | -61.734 | -61.5875 | 54.5197 | 24.3896 | 8.0292 | 7.4295 | 62.1918 | -61.7157 | -0.34332 | -0.032043 | 3.035 | -0.19684 | -7.663 | -0.32501 | 0.009155 | 3.3783 | 69.4199 | 68.8202 | 115.9103 | 123.5413 | 3.035 | 123.5825 | 85.7803 | -0.32501 | 123.5413 | 3.035 | 85.7803 | 115.9103 | 123.5825 | -123.9166 | -123.8983
4704.7188 | 123.7427 | -61.4044 | 62.1506 | -0.17677 | 0.014956 | 0.012559 | 0.016592 | 0.061743 | 0.00073487 | 0.080758 | -58.3054 | 62.1872 | -61.7065 | -61.5555 | 54.5059 | 24.2569 | 7.9376 | 7.37 | 62.1552 | -61.734 | -0.30212 | 0.036621 | 3.0991 | -0.15106 | -7.6447 | -0.32959 | 0.004577 | 3.4012 | 69.342 | 68.7744 | 115.9103 | 123.5916 | 3.0991 | 123.5596 | 85.6613 | -0.32959 | 123.5916 | 3.0991 | 85.6613 | 115.9103 | 123.5596 | -123.8571 | -123.8846
4705.7188 | 123.8663 | -61.3678 | 62.1506 | -0.11574 | 0.014101 | 0.009141 | 0.0093288 | 0.060248 | 9.4068e-05 | 0.080544 | -58.2962 | 62.1002 | -61.7111 | -61.4914 | 54.6204 | 24.3896 | 7.8232 | 7.4799 | 62.1552 | -61.6562 | -0.34332 | -0.050354 | 3.0716 | -0.1236 | -7.5302 | -0.28839 | 0.004577 | 3.4149 | 69.191 | 68.8477 | 115.9882 | 123.468 | 3.0716 | 123.5229 | 85.7574 | -0.28839 | 123.468 | 3.0716 | 85.7574 | 115.9882 | 123.5229 | -123.8617 | -123.8068
4706.7188 | 123.8297 | -61.3724 | 62.1918 | -0.15388 | 0.012392 | 0.010423 | 0.011892 | 0.058325 | -0.0014013 | 0.079476 | -58.3099 | 62.1002 | -61.7111 | -61.5372 | 54.6112 | 24.3713 | 7.8827 | 7.5073 | 62.1368 | -61.6837 | -0.33875 | -0.091552 | 3.0624 | -0.1648 | -7.5806 | -0.31128 | -0.054931 | 3.4012 | 69.2551 | 68.8797 | 115.9836 | 123.4726 | 3.0624 | 123.5092 | 85.7437 | -0.31128 | 123.4726 | 3.0624 | 85.7437 | 115.9836 | 123.5092 | -123.9029 | -123.8754
4707.7188 | 123.7793 | -61.3861 | 62.1872 | -0.26833 | 0.013247 | 0.013841 | 0.011038 | 0.058966 | -0.00097413 | 0.077981 | -58.3374 | 62.1185 | -61.6928 | -61.5555 | 54.5883 | 24.408 | 8.0063 | 7.4158 | 62.1506 | -61.7157 | -0.3067 | -0.068665 | 3.0487 | -0.16937 | -7.5989 | -0.32959 | -0.036621 | 3.3554 | 69.3924 | 68.8019 | 115.9744 | 123.5046 | 3.0487 | 123.5367 | 85.7941 | -0.32959 | 123.5046 | 3.0487 | 85.7941 | 115.9744 | 123.5367 | -123.88 | -123.9029
4708.7188 | 123.7564 | -61.3815 | 62.1918 | -0.25307 | 0.011751 | 0.010209 | 0.0095424 | 0.057685 | -0.0039649 | 0.080972 | -58.3099 | 62.1185 | -61.7157 | -61.5509 | 54.5334 | 24.4263 | 7.9697 | 7.3975 | 62.1506 | -61.6745 | -0.33417 | -0.073242 | 3.0716 | -0.16937 | -7.6584 | -0.29297 | -0.041198 | 3.4058 | 69.3512 | 68.779 | 115.9149 | 123.5001 | 3.0716 | 123.5321 | 85.8078 | -0.29297 | 123.5001 | 3.0716 | 85.8078 | 115.9149 | 123.5321 | -123.9075 | -123.8663
4709.7344 | 123.7289 | -61.4319 | 62.1597 | -0.08522 | 0.017519 | 0.013413 | 0.018301 | 0.06153 | -0.0018285 | 0.07734 | -58.3191 | 62.178 | -61.7203 | -61.5921 | 54.4601 | 24.408 | 7.933 | 7.3929 | 62.1506 | -61.7523 | -0.28839 | 0.018311 | 3.1128 | -0.16022 | -7.6996 | -0.32043 | -0.009155 | 3.4012 | 69.3649 | 68.8248 | 115.892 | 123.6099 | 3.1128 | 123.5825 | 85.8398 | -0.32043 | 123.6099 | 3.1128 | 85.8398 | 115.892 | 123.5825 | -123.88 | -123.912
4710.7344 | 123.7061 | -61.4273 | 62.1597 | 0.052109 | 0.017519 | 0.012559 | 0.017019 | 0.060889 | -0.00076053 | 0.077126 | -58.3649 | 62.1964 | -61.7477 | -61.6425 | 54.5013 | 24.3164 | 7.9422 | 7.2464 | 62.1735 | -61.7432 | -0.32044 | 0.036621 | 3.0624 | -0.21515 | -7.6584 | -0.31586 | 0.013733 | 3.3829 | 69.3695 | 68.6737 | 115.9287 | 123.6237 | 3.0624 | 123.6008 | 85.7437 | -0.31586 | 123.6237 | 3.0624 | 85.7437 | 115.9287 | 123.6008 | -123.9075 | -123.9029
4711.7188 | 123.7244 | -61.441 | 62.1918 | -0.3141 | 0.017306 | 0.011064 | 0.011038 | 0.060675 | -0.00011953 | 0.078622 | -58.3786 | 62.1414 | -61.702 | -61.6013 | 54.5609 | 24.3851 | 8.0246 | 7.338 | 62.1964 | -61.6928 | -0.26093 | -0.050354 | 3.0624 | -0.16022 | -7.6309 | -0.25177 | 0.004578 | 3.3234 | 69.4656 | 68.779 | 116.0019 | 123.5825 | 3.0624 | 123.6374 | 85.8261 | -0.25177 | 123.5825 | 3.0624 | 85.8261 | 116.0019 | 123.6374 | -123.8937 | -123.8846
4712.7188 | 123.7885 | -61.3678 | 62.1231 | -0.19966 | 0.014742 | 0.010209 | 0.0095424 | 0.05918 | -0.0024695 | 0.07969 | -58.2962 | 62.0865 | -61.7111 | -61.4502 | 55.0232 | 24.733 | 7.5256 | 7.4066 | 62.1506 | -61.6562 | -0.34332 | -0.036621 | 3.0716 | -0.082397 | -7.0999 | -0.28839 | 0.027466 | 3.4149 | 68.8934 | 68.7744 | 116.391 | 123.4543 | 3.0716 | 123.5184 | 86.1008 | -0.28839 | 123.4543 | 3.0716 | 86.1008 | 116.391 | 123.5184 | -123.8342 | -123.7793
4713.7188 | 123.8251 | -61.377 | 62.1597 | -0.17677 | 0.012606 | 0.0099954 | 0.011465 | 0.058966 | -0.00054693 | 0.077126 | -58.3099 | 62.1002 | -61.7249 | -61.528 | 54.5792 | 24.5087 | 7.9926 | 7.489 | 62.1323 | -61.7157 | -0.3479 | -0.059509 | 3.067 | -0.15106 | -7.5806 | -0.33875 | -0.027466 | 3.4149 | 69.3695 | 68.866 | 115.9561 | 123.4772 | 3.067 | 123.5092 | 85.8856 | -0.33875 | 123.4772 | 3.067 | 85.8856 | 115.9561 | 123.5092 | -123.8846 | -123.8754
4714.7188 | 123.7656 | -61.4273 | 62.1735 | -0.024185 | 0.013888 | 0.012345 | 0.017447 | 0.061316 | -0.00054693 | 0.078835 | -58.2504 | 62.1918 | -61.734 | -61.5784 | 54.4739 | 24.5544 | 8.1253 | 7.4982 | 62.1323 | -61.7249 | -0.3067 | 0.01831 | 3.1769 | -0.15106 | -7.6996 | -0.29755 | -0.041199 | 3.4836 | 69.5526 | 68.9255 | 115.9012 | 123.6191 | 3.1769 | 123.5596 | 85.9818 | -0.29755 | 123.6191 | 3.1769 | 85.9818 | 115.9012 | 123.5596 | -123.9075 | -123.8983
4715.7344 | 123.7198 | -61.4639 | 62.1368 | 0.15892 | 0.017092 | 0.013841 | 0.016378 | 0.062384 | 0.0018031 | 0.078835 | -58.6761 | 62.0911 | -61.8118 | -61.6425 | 54.364 | 24.3622 | 8.2123 | 7.489 | 62.1643 | -61.7523 | -0.3479 | -0.045777 | 2.7878 | -0.17853 | -7.7728 | -0.28839 | 0.027466 | 3.1357 | 69.6762 | 68.9529 | 115.8279 | 123.555 | 2.7878 | 123.6282 | 85.8261 | -0.28839 | 123.555 | 2.7878 | 85.8261 | 115.8279 | 123.6282 | -123.9487 | -123.8892
4716.7188 | 123.7701 | -61.409 | 62.1506 | -0.28358 | 0.013033 | 0.010423 | 0.0093288 | 0.058539 | -0.0020421 | 0.07969 | -58.3466 | 62.1231 | -61.7111 | -61.5463 | 54.5563 | 24.4583 | 8.1024 | 7.5394 | 62.1872 | -61.6974 | -0.30212 | -0.027466 | 3.0624 | -0.13733 | -7.5943 | -0.28839 | 0.036621 | 3.3646 | 69.5114 | 68.9484 | 115.9653 | 123.5321 | 3.0624 | 123.5962 | 85.8673 | -0.28839 | 123.5321 | 3.0624 | 85.8673 | 115.9653 | 123.5962 | -123.8617 | -123.848
4717.7188 | 123.8068 | -61.3907 | 62.1323 | -0.23781 | 0.01282 | 0.0097818 | 0.008688 | 0.058753 | -0.0018285 | 0.076486 | -58.3237 | 62.1094 | -61.7157 | -61.5509 | 54.6387 | 24.6368 | 7.9926 | 7.4615 | 62.1368 | -61.6837 | -0.32501 | -0.022888 | 3.067 | -0.16022 | -7.4936 | -0.29297 | 0.004578 | 3.392 | 69.3832 | 68.8522 | 116.0294 | 123.5001 | 3.067 | 123.5275 | 86.0275 | -0.29297 | 123.5001 | 3.067 | 86.0275 | 116.0294 | 123.5275 | -123.848 | -123.8159
4718.7188 | 123.8068 | -61.4044 | 62.1643 | -0.1844 | 0.011965 | 0.0132 | 0.011251 | 0.059607 | -0.0020421 | 0.079263 | -58.3145 | 62.0956 | -61.7111 | -61.5372 | 54.6341 | 24.646 | 8.0292 | 7.5485 | 62.1231 | -61.6837 | -0.3067 | -0.068665 | 3.0899 | -0.13275 | -7.5302 | -0.27924 | -0.041199 | 3.3966 | 69.4336 | 68.9529 | 116.0385 | 123.5001 | 3.0899 | 123.5275 | 86.0504 | -0.27924 | 123.5001 | 3.0899 | 86.0504 | 116.0385 | 123.5275 | -123.8754 | -123.848
4719.7188 | 123.7198 | -61.4044 | 62.2055 | -0.27596 | 0.014956 | 0.0080728 | 0.013388 | 0.05918 | -0.0028967 | 0.074563 | -58.3649 | 62.178 | -61.7432 | -61.3998 | 54.4739 | 24.353 | 8.1436 | 7.4936 | 62.178 | -61.7157 | -0.33875 | -0.027465 | 3.0396 | 0.004578 | -7.7316 | -0.31128 | -0.027465 | 3.3783 | 69.548 | 68.898 | 115.8783 | 123.5825 | 3.0396 | 123.5825 | 85.7574 | -0.31128 | 123.5825 | 3.0396 | 85.7574 | 115.8783 | 123.5825 | -123.9487 | -123.9212
4720.7188 | 123.8525 | -61.4273 | 62.114 | 0.2047 | 0.015597 | 0.014054 | 0.0095424 | 0.05918 | -0.0016149 | 0.080117 | -58.3282 | 62.0819 | -61.7386 | -61.5875 | 54.6524 | 24.614 | 7.8506 | 7.5485 | 62.1048 | -61.6974 | -0.31128 | -0.032044 | 3.0991 | -0.16022 | -7.4615 | -0.27008 | -0.009156 | 3.4103 | 69.278 | 68.9758 | 116.0797 | 123.5092 | 3.0991 | 123.5321 | 86.0413 | -0.27008 | 123.5092 | 3.0991 | 86.0413 | 116.0797 | 123.5321 | -123.8525 | -123.8113
4721.7188 | 123.7885 | -61.3998 | 62.1506 | -0.22255 | 0.016238 | 0.009141 | 0.010183 | 0.058966 | -0.00097413 | 0.076699 | -58.3282 | 62.1048 | -61.7111 | -61.5509 | 54.6204 | 24.5636 | 8.1253 | 7.663 | 62.1597 | -61.6882 | -0.31128 | -0.045777 | 3.0716 | -0.15106 | -7.5302 | -0.28839 | 0.009155 | 3.3829 | 69.5251 | 69.0628 | 116.0202 | 123.5046 | 3.0716 | 123.5596 | 85.9634 | -0.28839 | 123.5046 | 3.0716 | 85.9634 | 116.0202 | 123.5596 | -123.8617 | -123.8388
4722.7188 | 123.7976 | -61.3953 | 62.1506 | -0.19203 | 0.01282 | 0.014695 | 0.010824 | 0.059394 | 0.0015893 | 0.080331 | -58.3145 | 62.0773 | -61.7157 | -61.5417 | 54.6204 | 24.527 | 8.2397 | 7.7408 | 62.1506 | -61.6745 | -0.32043 | -0.073242 | 3.0807 | -0.14648 | -7.5302 | -0.27924 | 0 | 3.4012 | 69.635 | 69.136 | 116.0156 | 123.4726 | 3.0807 | 123.5458 | 85.9222 | -0.27924 | 123.4726 | 3.0807 | 85.9222 | 116.0156 | 123.5458 | -123.8663 | -123.8251
4723.7188 | 123.8113 | -61.3815 | 62.1597 | -0.17677 | 0.013247 | 0.0082864 | 0.012106 | 0.058753 | -0.0014013 | 0.078835 | -58.3054 | 62.0911 | -61.6974 | -61.528 | 54.6295 | 24.5682 | 8.1711 | 7.7362 | 62.1185 | -61.6699 | -0.31586 | -0.068665 | 3.0762 | -0.14648 | -7.5302 | -0.28839 | -0.041199 | 3.392 | 69.5526 | 69.1177 | 116.011 | 123.4726 | 3.0762 | 123.5001 | 85.9497 | -0.28839 | 123.4726 | 3.0762 | 85.9497 | 116.011 | 123.5001 | -123.8571 | -123.8297
4724.7188 | 123.7793 | -61.4227 | 62.1689 | -0.21492 | 0.016451 | 0.01085 | 0.020651 | 0.059607 | -0.0022559 | 0.078408 | -58.3054 | 62.2101 | -61.7157 | -61.5692 | 54.5197 | 24.4583 | 8.1528 | 7.5577 | 62.1552 | -61.7203 | -0.29297 | 0.041199 | 3.1174 | -0.14649 | -7.6492 | -0.29755 | -0.013733 | 3.4103 | 69.5755 | 68.9804 | 115.9424 | 123.6328 | 3.1174 | 123.5779 | 85.881 | -0.29755 | 123.6328 | 3.1174 | 85.881 | 115.9424 | 123.5779 | -123.8846 | -123.8892
4725.7188 | 123.8068 | -61.3907 | 62.1597 | -0.47432 | 0.010256 | 0.0132 | 0.0080472 | 0.059607 | -0.00054693 | 0.078835 | -58.3054 | 62.0773 | -61.7157 | -61.528 | 54.6158 | 24.4858 | 8.1665 | 7.7774 | 62.1368 | -61.6699 | -0.32501 | -0.082397 | 3.0853 | -0.13733 | -7.5439 | -0.27924 | -0.022888 | 3.4103 | 69.5572 | 69.1681 | 116.0065 | 123.468 | 3.0853 | 123.5275 | 85.8765 | -0.27924 | 123.468 | 3.0853 | 85.8765 | 116.0065 | 123.5275 | -123.8754 | -123.8297
4726.7188 | 123.8434 | -61.3907 | 62.1552 | -0.72609 | 0.014315 | 0.010636 | 0.0095424 | 0.058753 | -0.0026831 | 0.078622 | -58.3878 | 62.0636 | -61.7111 | -61.5326 | 54.6021 | 24.4812 | 8.1161 | 7.7774 | 62.1643 | -61.6516 | -0.32043 | -0.091552 | 3.0029 | -0.14191 | -7.5531 | -0.26093 | 0.009156 | 3.3234 | 69.5068 | 69.1681 | 115.9927 | 123.4543 | 3.0029 | 123.555 | 85.8719 | -0.26093 | 123.4543 | 3.0029 | 85.8719 | 115.9927 | 123.555 | -123.8663 | -123.8068
4727.7188 | 123.8297 | -61.3815 | 62.1368 | -0.19203 | 0.011751 | 0.011918 | 0.012747 | 0.05683 | -0.0018285 | 0.07969 | -58.4244 | 62.1185 | -61.6791 | -61.5921 | 54.5471 | 24.527 | 8.0887 | 7.8003 | 62.1048 | -61.6745 | -0.29755 | -0.018311 | 2.9572 | -0.21057 | -7.5897 | -0.29297 | -0.032044 | 3.2547 | 69.4702 | 69.1818 | 115.9287 | 123.5001 | 2.9572 | 123.4863 | 85.9085 | -0.29297 | 123.5001 | 2.9572 | 85.9085 | 115.9287 | 123.4863 | -123.8159 | -123.8113
4728.7188 | 123.7976 | -61.3907 | 62.146 | -0.17677 | 0.014742 | 0.0085 | 0.011892 | 0.058966 | -0.0016149 | 0.079049 | -58.3191 | 62.1094 | -61.7203 | -61.5189 | 54.6158 | 24.5911 | 8.1116 | 7.6859 | 62.1231 | -61.6745 | -0.32959 | -0.036621 | 3.0716 | -0.12817 | -7.5302 | -0.28381 | -0.022888 | 3.4012 | 69.5023 | 69.0765 | 116.0065 | 123.5001 | 3.0716 | 123.5138 | 85.9818 | -0.28381 | 123.5001 | 3.0716 | 85.9818 | 116.0065 | 123.5138 | -123.8663 | -123.8205
4729.7188 | 123.7518 | -61.4365 | 62.1872 | -0.21492 | 0.016451 | 0.0095682 | 0.015524 | 0.05918 | -0.0014013 | 0.078195 | -58.3649 | 62.1735 | -61.6974 | -61.5875 | 54.5197 | 24.3942 | 8.2352 | 7.5256 | 62.1689 | -61.7477 | -0.26093 | -0.013733 | 3.0716 | -0.15106 | -7.6675 | -0.31128 | -0.018311 | 3.3325 | 69.6716 | 68.9621 | 115.9561 | 123.6099 | 3.0716 | 123.6053 | 85.8307 | -0.31128 | 123.6099 | 3.0716 | 85.8307 | 115.9561 | 123.6053 | -123.8846 | -123.9349
4730.7188 | 123.8388 | -61.377 | 62.1552 | -0.5735 | 0.012606 | 0.011704 | 0.0095424 | 0.059821 | -0.0024695 | 0.080758 | -58.3374 | 62.0865 | -61.702 | -61.5143 | 54.6341 | 24.5819 | 7.9697 | 7.6767 | 62.1231 | -61.6837 | -0.32501 | -0.068664 | 3.0396 | -0.13733 | -7.5211 | -0.3067 | -0.032043 | 3.3646 | 69.3466 | 69.0537 | 116.011 | 123.4634 | 3.0396 | 123.5001 | 85.9589 | -0.3067 | 123.4634 | 3.0396 | 85.9589 | 116.011 | 123.5001 | -123.8571 | -123.8388
4731.7188 | 123.8342 | -61.3861 | 62.146 | -2.7021 | 0.013888 | 0.014695 | 0.011892 | 0.058753 | -0.0020421 | 0.078408 | -58.5983 | 62.1002 | -61.7157 | -61.5463 | 54.5654 | 24.6277 | 8.1116 | 7.8506 | 62.1414 | -61.6653 | -0.32959 | -0.045776 | 2.7878 | -0.16022 | -7.5806 | -0.27924 | -0.004578 | 3.1174 | 69.4977 | 69.2368 | 115.9515 | 123.4863 | 2.7878 | 123.5275 | 86.0138 | -0.27924 | 123.4863 | 2.7878 | 86.0138 | 115.9515 | 123.5275 | -123.8617 | -123.8113
4732.7188 | 123.8205 | -61.3815 | 62.1368 | -0.1844 | 0.011324 | 0.0076456 | 0.0080472 | 0.054694 | -0.0014013 | 0.080331 | -58.3099 | 62.0728 | -61.6928 | -61.8118 | 54.5654 | 24.646 | 7.9468 | 7.6859 | 62.1002 | -61.6791 | -0.31128 | -0.064087 | 3.0716 | -0.4303 | -7.5714 | -0.29755 | -0.036621 | 3.3829 | 69.3283 | 69.0674 | 115.947 | 123.4543 | 3.0716 | 123.4818 | 86.0275 | -0.29755 | 123.4543 | 3.0716 | 86.0275 | 115.947 | 123.4818 | -123.8297 | -123.8159
4733.7188 | 123.7335 | -61.3678 | 62.1277 | -0.14626 | 0.011324 | 0.0063638 | 0.011892 | 0.058539 | 0.00073487 | 0.080331 | -58.2916 | 62.0865 | -61.6974 | -61.4914 | 54.6661 | 24.7238 | 8.0887 | 8.0109 | 62.1231 | -61.6653 | -0.32959 | -0.041199 | 3.0762 | -0.1236 | -7.4615 | -0.29755 | -0.004578 | 3.4058 | 69.4565 | 69.3787 | 116.0339 | 123.4543 | 3.0762 | 123.4909 | 86.0916 | -0.29755 | 123.4543 | 3.0762 | 86.0916 | 116.0339 | 123.4909 | -123.8251 | -123.793
4734.7344 | 123.7701 | -61.4227 | 62.1689 | -0.21492 | 0.017092 | 0.011064 | 0.017447 | 0.060248 | -0.0024695 | 0.077981 | -58.3282 | 62.1918 | -61.7249 | -61.5555 | 54.5609 | 24.646 | 8.2855 | 7.7042 | 62.1552 | -61.7294 | -0.30213 | 0.022888 | 3.0945 | -0.13275 | -7.608 | -0.3067 | -0.013733 | 3.3966 | 69.7083 | 69.1269 | 115.9836 | 123.6145 | 3.0945 | 123.5779 | 86.0687 | -0.3067 | 123.6145 | 3.0945 | 86.0687 | 115.9836 | 123.5779 | -123.8937 | -123.8983
4735.7188 | 123.8434 | -61.377 | 62.1506 | -1.0236 | 0.014315 | 0.010209 | 0.011038 | 0.059607 | -0.0018285 | 0.077981 | -58.3786 | 62.059 | -61.734 | -61.5189 | 54.6524 | 24.733 | 8.2031 | 7.8278 | 62.1368 | -61.6562 | -0.35706 | -0.091553 | 2.9984 | -0.14191 | -7.4982 | -0.27924 | -0.013733 | 3.3554 | 69.5801 | 69.2047 | 116.0294 | 123.436 | 2.9984 | 123.5138 | 86.1099 | -0.27924 | 123.436 | 2.9984 | 86.1099 | 116.0294 | 123.5138 | -123.8846 | -123.8068
4736.7188 | 123.8342 | -61.3403 | 62.1368 | -0.23018 | 0.013033 | 0.011704 | 0.0091152 | 0.058966 | -0.0014013 | 0.079263 | -58.3054 | 62.1048 | -61.6882 | -61.5967 | 54.6753 | 24.6277 | 8.1573 | 7.7911 | 62.114 | -61.6653 | -0.3479 | -0.032044 | 3.035 | -0.25635 | -7.4615 | -0.32501 | -0.022888 | 3.3829 | 69.4977 | 69.1315 | 116.0156 | 123.4451 | 3.035 | 123.4543 | 85.968 | -0.32501 | 123.4451 | 3.035 | 85.968 | 116.0156 | 123.4543 | -123.8251 | -123.8022
4737.7188 | 123.8159 | -61.3953 | 62.114 | -0.1844 | 0.014101 | 0.0072184 | 0.0093288 | 0.060248 | -0.0035375 | 0.078195 | -58.2962 | 62.0773 | -61.7157 | -61.5967 | 54.8676 | 24.8154 | 7.8873 | 7.5623 | 62.114 | -61.6608 | -0.32043 | -0.036621 | 3.0991 | -0.20142 | -7.2464 | -0.2655 | 0 | 3.4195 | 69.2825 | 68.9575 | 116.2628 | 123.4726 | 3.0991 | 123.5092 | 86.2106 | -0.2655 | 123.4726 | 3.0991 | 86.2106 | 116.2628 | 123.5092 | -123.8297 | -123.7747
4738.7188 | 123.8983 | -61.3541 | 62.2147 | -0.13863 | 0.010683 | 0.012559 | 0.012533 | 0.059607 | -0.0035375 | 0.077554 | -58.3099 | 62.0728 | -61.7065 | -61.496 | 54.6707 | 24.5316 | 8.1848 | 7.9102 | 62.1368 | -61.6608 | -0.35248 | -0.14191 | 3.0441 | -0.14191 | -7.5439 | -0.3067 | -0.07782 | 3.3966 | 69.5389 | 69.2642 | 116.0248 | 123.4268 | 3.0441 | 123.4909 | 85.8856 | -0.3067 | 123.4268 | 3.0441 | 85.8856 | 116.0248 | 123.4909 | -123.9212 | -123.8754
4739.7188 | 123.8388 | -61.3998 | 62.1368 | -0.08522 | 0.012392 | 0.0085 | 0.0095424 | 0.057257 | 0.0015893 | 0.080972 | -58.3054 | 62.059 | -61.702 | -61.496 | 54.689 | 24.5132 | 8.2809 | 7.9605 | 62.1094 | -61.6791 | -0.30212 | -0.07782 | 3.0945 | -0.096131 | -7.4478 | -0.27924 | -0.027466 | 3.3966 | 69.6808 | 69.3604 | 116.0889 | 123.4589 | 3.0945 | 123.5092 | 85.9131 | -0.27924 | 123.4589 | 3.0945 | 85.9131 | 116.0889 | 123.5092 | -123.8388 | -123.8159
4740.7188 | 123.8754 | -61.3998 | 62.1323 | -0.1844 | 0.014101 | 0.0082864 | 0.0099698 | 0.057471 | -0.00011953 | 0.079263 | -58.3237 | 62.0499 | -61.6974 | -61.5097 | 54.6753 | 24.5865 | 8.3496 | 7.9834 | 62.1094 | -61.6974 | -0.29755 | -0.082397 | 3.0762 | -0.10986 | -7.457 | -0.29755 | -0.022888 | 3.3737 | 69.7494 | 69.3832 | 116.0751 | 123.4497 | 3.0762 | 123.5092 | 85.9863 | -0.29755 | 123.4497 | 3.0762 | 85.9863 | 116.0751 | 123.5092 | -123.8297 | -123.8297
4741.7188 | 123.8709 | -61.3815 | 62.1323 | -0.077591 | 0.012179 | 0.011277 | 0.0095424 | 0.057044 | 9.4068e-05 | 0.077767 | -58.3054 | 62.0773 | -61.7111 | -61.5097 | 54.6387 | 24.5132 | 8.226 | 7.8964 | 62.1277 | -61.647 | -0.32959 | -0.054931 | 3.0762 | -0.12817 | -7.4936 | -0.2655 | -0.004577 | 3.4058 | 69.6075 | 69.278 | 116.0202 | 123.4589 | 3.0762 | 123.5092 | 85.8948 | -0.2655 | 123.4589 | 3.0762 | 85.8948 | 116.0202 | 123.5092 | -123.8434 | -123.7793
4742.7188 | 123.8297 | -61.3953 | 62.114 | -0.16914 | 0.014101 | 0.010423 | 0.015097 | 0.061103 | -0.0031103 | 0.080117 | -58.3191 | 62.0773 | -61.7157 | -61.5417 | 54.5242 | 24.6185 | 8.2169 | 7.7866 | 62.1048 | -61.6562 | -0.32043 | -0.036621 | 3.0762 | -0.14648 | -7.5897 | -0.26093 | -0.009156 | 3.3966 | 69.6121 | 69.1818 | 115.9195 | 123.4726 | 3.0762 | 123.5001 | 86.0138 | -0.26093 | 123.4726 | 3.0762 | 86.0138 | 115.9195 | 123.5001 | -123.8297 | -123.7701
4743.7188 | 123.8663 | -61.4044 | 62.1323 | -0.22255 | 0.012606 | 0.0063638 | 0.01232 | 0.060034 | -0.0033239 | 0.078835 | -58.287 | 62.0636 | -61.7111 | -61.6241 | 54.3045 | 24.559 | 8.3176 | 7.7271 | 62.0773 | -61.6699 | -0.3067 | -0.068664 | 3.1174 | -0.21973 | -7.8278 | -0.2655 | -0.054931 | 3.4241 | 69.722 | 69.1315 | 115.7089 | 123.468 | 3.1174 | 123.4818 | 85.9634 | -0.2655 | 123.468 | 3.1174 | 85.9634 | 115.7089 | 123.4818 | -123.8434 | -123.8022
4744.7188 | 123.7015 | -61.4182 | 62.1872 | -0.19966 | 0.014742 | 0.009141 | 0.015097 | 0.056189 | -0.0018285 | 0.079049 | -58.287 | 62.1872 | -61.7203 | -61.6196 | 54.5654 | 24.5224 | 8.3954 | 7.608 | 62.1643 | -61.7294 | -0.30212 | 0 | 3.1311 | -0.20142 | -7.6218 | -0.31128 | -0.022888 | 3.4332 | 69.8135 | 69.0262 | 115.9836 | 123.6053 | 3.1311 | 123.5825 | 85.9406 | -0.31128 | 123.6053 | 3.1311 | 85.9406 | 115.9836 | 123.5825 | -123.9075 | -123.9166
4745.7188 | 123.8342 | -61.3953 | 62.1277 | -0.16151 | 0.01346 | 0.012559 | 0.0089016 | 0.05918 | -0.00076053 | 0.077554 | -58.3054 | 62.0865 | -61.7157 | -61.496 | 54.689 | 24.678 | 8.7662 | 8.0566 | 62.1643 | -61.6241 | -0.32043 | -0.041199 | 3.0899 | -0.10071 | -7.4387 | -0.22888 | 0.036621 | 3.4103 | 70.1614 | 69.4519 | 116.0843 | 123.4818 | 3.0899 | 123.5596 | 86.0733 | -0.22888 | 123.4818 | 3.0899 | 86.0733 | 116.0843 | 123.5596 | -123.8434 | -123.7518
4746.7188 | 123.8022 | -61.3998 | 62.146 | -0.16151 | 0.010897 | 0.0080728 | 0.011038 | 0.058539 | -0.0022559 | 0.080544 | -58.3099 | 62.0956 | -61.6882 | -61.5143 | 54.6936 | 24.6185 | 8.2901 | 7.9193 | 62.114 | -61.6791 | -0.28839 | -0.050354 | 3.0899 | -0.11444 | -7.4524 | -0.27924 | -0.032043 | 3.3783 | 69.6899 | 69.3192 | 116.0934 | 123.4955 | 3.0899 | 123.5138 | 86.0184 | -0.27924 | 123.4955 | 3.0899 | 86.0184 | 116.0934 | 123.5138 | -123.8342 | -123.8251
4747.7188 | 123.8251 | -61.3724 | 62.1735 | -0.19966 | 0.013247 | 0.0089274 | 0.0074062 | 0.057044 | -0.0014013 | 0.079263 | -58.3008 | 62.0865 | -61.7249 | -61.4822 | 54.6799 | 24.5911 | 8.2947 | 7.933 | 62.1185 | -61.6837 | -0.35248 | -0.086975 | 3.0716 | -0.10986 | -7.4936 | -0.31128 | -0.054932 | 3.4241 | 69.6671 | 69.3054 | 116.0522 | 123.4589 | 3.0716 | 123.4909 | 85.9634 | -0.31128 | 123.4589 | 3.0716 | 85.9634 | 116.0522 | 123.4909 | -123.8983 | -123.8571
4748.7188 | 123.8571 | -61.3953 | 62.146 | -0.1844 | 0.012606 | 0.010423 | 0.011251 | 0.059607 | -0.00097413 | 0.081613 | -58.3145 | 62.1094 | -61.7111 | -61.5143 | 54.6616 | 24.5178 | 8.2489 | 7.8186 | 62.0911 | -61.702 | -0.31586 | -0.036621 | 3.0807 | -0.11902 | -7.4844 | -0.3067 | -0.054932 | 3.3966 | 69.6442 | 69.2139 | 116.0568 | 123.5046 | 3.0807 | 123.4863 | 85.9131 | -0.3067 | 123.5046 | 3.0807 | 85.9131 | 116.0568 | 123.4863 | -123.8571 | -123.848
4749.7188 | 123.7518 | -61.3953 | 62.1643 | -0.21492 | 0.016238 | 0.014054 | 0.017233 | 0.060462 | -0.0016149 | 0.079476 | -58.3237 | 62.1872 | -61.7111 | -61.5372 | 54.5792 | 24.2889 | 8.2993 | 7.7316 | 62.1368 | -61.7294 | -0.31586 | 0.022888 | 3.0716 | -0.14191 | -7.5851 | -0.33417 | -0.027466 | 3.3875 | 69.6945 | 69.1269 | 115.9744 | 123.5825 | 3.0716 | 123.5321 | 85.6842 | -0.33417 | 123.5825 | 3.0716 | 85.6842 | 115.9744 | 123.5321 | -123.8754 | -123.8937
4750.7188 | 123.8297 | -61.3907 | 62.146 | -0.12337 | 0.013033 | 0.0095682 | 0.010824 | 0.059394 | -0.0014013 | 0.07969 | -58.3099 | 62.0911 | -61.7249 | -61.5143 | 54.6249 | 24.6231 | 8.226 | 7.7683 | 62.1231 | -61.647 | -0.33417 | -0.054932 | 3.0807 | -0.1236 | -7.5211 | -0.25635 | -0.022888 | 3.4149 | 69.6167 | 69.1589 | 116.0156 | 123.4818 | 3.0807 | 123.5138 | 86.0138 | -0.25635 | 123.4818 | 3.0807 | 86.0138 | 116.0156 | 123.5138 | -123.8708 | -123.793
4751.7188 | 123.8205 | -61.3815 | 62.1414 | -0.1844 | 0.010256 | 0.010209 | 0.011679 | 0.059607 | -0.0018285 | 0.07734 | -58.342 | 62.0956 | -61.6928 | -61.5143 | 54.6204 | 24.5087 | 8.2535 | 7.8552 | 62.0956 | -61.6653 | -0.31128 | -0.045776 | 3.0396 | -0.13275 | -7.5211 | -0.28381 | -0.045776 | 3.3508 | 69.635 | 69.2368 | 116.0019 | 123.4772 | 3.0396 | 123.4772 | 85.8902 | -0.28381 | 123.4772 | 3.0396 | 85.8902 | 116.0019 | 123.4772 | -123.8342 | -123.8068
4752.7188 | 123.8205 | -61.4044 | 62.1689 | -0.43617 | 0.013247 | 0.0080728 | 0.010397 | 0.058539 | -0.0016149 | 0.077554 | -58.3328 | 62.0865 | -61.7294 | -61.5189 | 54.6387 | 24.6048 | 8.2718 | 7.8644 | 62.1048 | -61.6745 | -0.32501 | -0.082397 | 3.0716 | -0.11444 | -7.5302 | -0.27008 | -0.064087 | 3.3966 | 69.6762 | 69.2688 | 116.0431 | 123.4909 | 3.0716 | 123.5092 | 86.0092 | -0.27008 | 123.4909 | 3.0716 | 86.0092 | 116.0431 | 123.5092 | -123.8983 | -123.8434
4753.7188 | 123.848 | -61.3861 | 62.1552 | -0.2607 | 0.012392 | 0.011491 | 0.0082608 | 0.058753 | -0.0033239 | 0.077981 | -58.3191 | 62.0911 | -61.7249 | -61.5051 | 54.6799 | 24.5819 | 8.3954 | 7.9468 | 62.0773 | -61.6608 | -0.33875 | -0.064087 | 3.067 | -0.11902 | -7.4753 | -0.27466 | -0.077819 | 3.4058 | 69.7815 | 69.3329 | 116.066 | 123.4772 | 3.067 | 123.4634 | 85.968 | -0.27466 | 123.4772 | 3.067 | 85.968 | 116.066 | 123.4634 | -123.88 | -123.8159
4754.7188 | 123.848 | -61.3815 | 62.1094 | -0.61928 | 0.012179 | 0.0089274 | 0.0095424 | 0.05918 | -0.00076053 | 0.078622 | -58.3282 | 62.0911 | -61.702 | -61.5097 | 54.7165 | 24.4949 | 8.3542 | 8.0612 | 62.114 | -61.6516 | -0.32043 | -0.018311 | 3.0533 | -0.12817 | -7.3929 | -0.27008 | 0.004578 | 3.3737 | 69.7357 | 69.4427 | 116.098 | 123.4726 | 3.0533 | 123.4955 | 85.8765 | -0.27008 | 123.4726 | 3.0533 | 85.8765 | 116.098 | 123.4955 | -123.8113 | -123.761
4755.7188 | 123.7701 | -61.3907 | 62.1735 | -0.2607 | 0.014101 | 0.011918 | 0.013388 | 0.058325 | -0.0016149 | 0.078835 | -58.3237 | 62.0911 | -61.7477 | -61.5509 | 54.6753 | 24.4995 | 8.3633 | 7.9971 | 62.1231 | -61.702 | -0.35706 | -0.082398 | 3.067 | -0.16022 | -7.4982 | -0.31128 | -0.050354 | 3.4241 | 69.754 | 69.3878 | 116.066 | 123.4818 | 3.067 | 123.5138 | 85.8902 | -0.31128 | 123.4818 | 3.067 | 85.8902 | 116.066 | 123.5138 | -123.9212 | -123.8754
4756.7188 | 123.8022 | -61.3953 | 62.1597 | -0.19203 | 0.010683 | 0.012773 | 0.011038 | 0.059821 | -0.0041785 | 0.081826 | -58.3145 | 62.114 | -61.702 | -61.5326 | 54.6433 | 24.3759 | 8.313 | 7.8644 | 62.1323 | -61.6882 | -0.3067 | -0.045776 | 3.0807 | -0.13733 | -7.5165 | -0.29297 | -0.027466 | 3.3875 | 69.7083 | 69.2596 | 116.0385 | 123.5092 | 3.0807 | 123.5275 | 85.7712 | -0.29297 | 123.5092 | 3.0807 | 85.7712 | 116.0385 | 123.5275 | -123.8617 | -123.848
4757.7188 | 123.7976 | -61.4136 | 62.1552 | -0.23018 | 0.015169 | 0.012559 | 0.010397 | 0.057685 | -0.0018285 | 0.077767 | -58.3282 | 62.0911 | -61.7065 | -61.5417 | 54.6478 | 24.472 | 8.3038 | 7.8964 | 62.1323 | -61.6791 | -0.29297 | -0.064087 | 3.0853 | -0.12817 | -7.5073 | -0.2655 | -0.022888 | 3.3783 | 69.7174 | 69.31 | 116.0614 | 123.5046 | 3.0853 | 123.5458 | 85.8856 | -0.2655 | 123.5046 | 3.0853 | 85.8856 | 116.0614 | 123.5458 | -123.8617 | -123.8342
4758.7188 | 123.761 | -61.377 | 62.1597 | -0.19203 | 0.013033 | 0.013413 | 0.010824 | 0.058966 | -0.0018285 | 0.078195 | -58.3237 | 62.114 | -61.6928 | -61.5234 | 54.6295 | 24.4446 | 8.226 | 7.9193 | 62.1552 | -61.6699 | -0.31586 | -0.045776 | 3.0533 | -0.14648 | -7.5302 | -0.29297 | -0.004578 | 3.3691 | 69.603 | 69.2963 | 116.0065 | 123.4909 | 3.0533 | 123.5321 | 85.8215 | -0.29297 | 123.4909 | 3.0533 | 85.8215 | 116.0065 | 123.5321 | -123.8525 | -123.8297
4759.7188 | 123.7427 | -61.4319 | 62.1689 | -0.11574 | 0.017306 | 0.012986 | 0.016592 | 0.058325 | -0.0020421 | 0.077767 | -58.3008 | 62.1643 | -61.7249 | -61.5601 | 54.5837 | 24.3713 | 8.3496 | 7.8827 | 62.1368 | -61.702 | -0.29297 | -0.004577 | 3.1311 | -0.12817 | -7.5851 | -0.27008 | -0.032043 | 3.4241 | 69.7815 | 69.3146 | 116.0156 | 123.5962 | 3.1311 | 123.5687 | 85.8032 | -0.27008 | 123.5962 | 3.1311 | 85.8032 | 116.0156 | 123.5687 | -123.8937 | -123.8708
4760.7188 | 123.9532 | -61.3495 | 62.146 | -0.15388 | 0.012392 | 0.010423 | 0.0067654 | 0.059607 | -0.0026831 | 0.079904 | -58.3099 | 62.0956 | -61.7203 | -61.4914 | 54.6936 | 24.4034 | 8.2809 | 7.9651 | 62.1185 | -61.6241 | -0.37079 | -0.050354 | 3.0396 | -0.14191 | -7.4524 | -0.27466 | -0.027466 | 3.4103 | 69.6304 | 69.3146 | 116.0431 | 123.4451 | 3.0396 | 123.468 | 85.7529 | -0.27466 | 123.4451 | 3.0396 | 85.7529 | 116.0431 | 123.468 | -123.8663 | -123.7701
4761.7188 | 123.7381 | -61.4136 | 62.1643 | -0.3141 | 0.014742 | 0.012345 | 0.012533 | 0.057898 | 0.0013757 | 0.079049 | -58.3603 | 62.1323 | -61.7249 | -61.5784 | 54.6844 | 24.5224 | 8.5281 | 7.933 | 62.1323 | -61.6928 | -0.31128 | -0.032044 | 3.0533 | -0.1648 | -7.4799 | -0.27924 | -0.032044 | 3.3646 | 69.9417 | 69.3466 | 116.098 | 123.5458 | 3.0533 | 123.5458 | 85.936 | -0.27924 | 123.5458 | 3.0533 | 85.936 | 116.098 | 123.5458 | -123.8892 | -123.8571
4762.7188 | 123.7518 | -61.4182 | 62.1552 | -0.2607 | 0.014101 | 0.011918 | 0.014456 | 0.059607 | -0.0020421 | 0.079904 | -58.4335 | 62.1231 | -61.702 | -61.5601 | 54.6753 | 24.5041 | 8.519 | 8.0017 | 62.1231 | -61.6882 | -0.28381 | -0.032043 | 2.9846 | -0.14191 | -7.4799 | -0.27008 | -0.032043 | 3.2684 | 69.9371 | 69.4199 | 116.0934 | 123.5413 | 2.9846 | 123.5413 | 85.9222 | -0.27008 | 123.5413 | 2.9846 | 85.9222 | 116.0934 | 123.5413 | -123.8571 | -123.8434
4763.7188 | 123.7701 | -61.3861 | 62.1597 | -0.26833 | 0.01346 | 0.0099954 | 0.01232 | 0.058539 | -0.00011953 | 0.078195 | -58.3237 | 62.0956 | -61.7065 | -61.5463 | 54.657 | 24.4949 | 8.5144 | 8.0063 | 62.1277 | -61.6928 | -0.32044 | -0.064087 | 3.0624 | -0.16022 | -7.5027 | -0.3067 | -0.032043 | 3.3829 | 69.9005 | 69.3924 | 116.0431 | 123.4818 | 3.0624 | 123.5138 | 85.881 | -0.3067 | 123.4818 | 3.0624 | 85.881 | 116.0431 | 123.5138 | -123.8663 | -123.8525
4764.7344 | 123.7564 | -61.441 | 62.1597 | -0.039444 | 0.016238 | 0.01555 | 0.018728 | 0.061743 | -0.0031103 | 0.078408 | -58.3054 | 62.1918 | -61.7249 | -61.5921 | 54.5975 | 24.4263 | 8.4274 | 7.9193 | 62.1552 | -61.734 | -0.28381 | 0.032043 | 3.1357 | -0.15106 | -7.5623 | -0.29297 | -0.004578 | 3.4195 | 69.8685 | 69.3604 | 116.0385 | 123.6328 | 3.1357 | 123.5962 | 85.8673 | -0.29297 | 123.6328 | 3.1357 | 85.8673 | 116.0385 | 123.5962 | -123.8846 | -123.8937
4765.7188 | 123.8205 | -61.4044 | 62.1506 | -0.19966 | 0.013247 | 0.013627 | 0.0082608 | 0.059821 | -0.0016149 | 0.079476 | -58.3191 | 62.0956 | -61.7203 | -61.5463 | 54.6844 | 24.6552 | 8.3954 | 8.0246 | 62.1414 | -61.6928 | -0.31586 | -0.054932 | 3.0853 | -0.14191 | -7.4661 | -0.28839 | -0.009156 | 3.4012 | 69.7998 | 69.429 | 116.0889 | 123.5001 | 3.0853 | 123.5458 | 86.0596 | -0.28839 | 123.5001 | 3.0853 | 86.0596 | 116.0889 | 123.5458 | -123.8708 | -123.8434
4766.7188 | 123.7976 | -61.377 | 62.1506 | -0.13863 | 0.012606 | 0.0059366 | 0.011251 | 0.05918 | -0.0026831 | 0.079476 | -58.3237 | 62.0819 | -61.7249 | -61.5189 | 54.7211 | 24.7971 | 8.3405 | 7.9468 | 62.1048 | -61.6516 | -0.3479 | -0.068665 | 3.0533 | -0.14191 | -7.4295 | -0.27466 | -0.045777 | 3.4012 | 69.7174 | 69.3237 | 116.098 | 123.4589 | 3.0533 | 123.4818 | 86.174 | -0.27466 | 123.4589 | 3.0533 | 86.174 | 116.098 | 123.4818 | -123.8754 | -123.8022
4767.7188 | 123.8022 | -61.4136 | 62.1506 | -0.23781 | 0.01346 | 0.011064 | 0.011038 | 0.059394 | -0.0014013 | 0.079049 | -58.3237 | 62.0956 | -61.6974 | -61.5234 | 54.6982 | 24.5636 | 8.3313 | 8.0063 | 62.1277 | -61.6699 | -0.28381 | -0.054932 | 3.0899 | -0.10986 | -7.4524 | -0.25635 | -0.022888 | 3.3737 | 69.7449 | 69.4199 | 116.1118 | 123.5092 | 3.0899 | 123.5413 | 85.9772 | -0.25635 | 123.5092 | 3.0899 | 85.9772 | 116.1118 | 123.5413 | -123.848 | -123.8205
4768.7188 | 123.8434 | -61.377 | 62.1597 | -0.10048 | 0.01282 | 0.013413 | 0.010824 | 0.05683 | -0.0020421 | 0.079476 | -58.3328 | 62.0773 | -61.7111 | -61.5463 | 54.6936 | 24.6231 | 8.3817 | 8.0017 | 62.114 | -61.6745 | -0.33417 | -0.082397 | 3.0441 | -0.16937 | -7.4661 | -0.29755 | -0.045776 | 3.3783 | 69.7586 | 69.3787 | 116.0706 | 123.4543 | 3.0441 | 123.4909 | 86.0001 | -0.29755 | 123.4543 | 3.0441 | 86.0001 | 116.0706 | 123.4909 | -123.8708 | -123.8342
4769.7188 | 123.674 | -61.4273 | 62.2147 | -0.23781 | 0.01581 | 0.011704 | 0.016165 | 0.059821 | -0.0011877 | 0.077126 | -58.4015 | 62.1552 | -61.7706 | -61.6104 | 54.5975 | 24.5407 | 8.4091 | 7.4936 | 62.146 | -61.6928 | -0.34332 | -0.05951 | 3.0258 | -0.18311 | -7.6172 | -0.2655 | -0.068665 | 3.3691 | 69.8364 | 68.9209 | 116.0248 | 123.5825 | 3.0258 | 123.5733 | 85.968 | -0.2655 | 123.5825 | 3.0258 | 85.968 | 116.0248 | 123.5733 | -123.9853 | -123.9075
4770.7188 | 123.7885 | -61.3861 | 62.1552 | -0.30647 | 0.01282 | 0.011704 | 0.010824 | 0.058966 | -0.0011877 | 0.07734 | -58.3191 | 62.114 | -61.7203 | -61.5463 | 54.6433 | 24.6185 | 8.2306 | 7.2647 | 62.1368 | -61.6745 | -0.33417 | -0.041198 | 3.067 | -0.16022 | -7.5119 | -0.28839 | -0.01831 | 3.4012 | 69.6167 | 68.6508 | 116.0294 | 123.5001 | 3.067 | 123.5229 | 86.0046 | -0.28839 | 123.5001 | 3.067 | 86.0046 | 116.0294 | 123.5229 | -123.8754 | -123.8297
4771.7188 | 123.793 | -61.4044 | 62.1735 | -0.24544 | 0.015169 | 0.0089274 | 0.011251 | 0.05918 | -0.0014013 | 0.076486 | -58.3191 | 62.1048 | -61.6837 | -61.5463 | 54.6799 | 24.6323 | 8.1757 | 7.3013 | 62.1368 | -61.6425 | -0.27924 | -0.068665 | 3.0853 | -0.14191 | -7.4936 | -0.23804 | -0.036621 | 3.3646 | 69.5801 | 68.7057 | 116.0843 | 123.5092 | 3.0853 | 123.5413 | 86.0367 | -0.23804 | 123.5092 | 3.0853 | 86.0367 | 116.0843 | 123.5413 | -123.8571 | -123.8159
4772.7188 | 123.7976 | -61.3907 | 62.1689 | -0.20729 | 0.011538 | 0.011064 | 0.011679 | 0.057685 | -0.0035375 | 0.077554 | -58.3237 | 62.0911 | -61.7249 | -61.5372 | 54.6707 | 24.6094 | 8.2809 | 7.4707 | 62.1185 | -61.6791 | -0.33417 | -0.07782 | 3.067 | -0.14648 | -7.4982 | -0.28839 | -0.050354 | 3.4012 | 69.6716 | 68.8614 | 116.0614 | 123.4818 | 3.067 | 123.5092 | 86.0001 | -0.28839 | 123.4818 | 3.067 | 86.0001 | 116.0614 | 123.5092 | -123.8937 | -123.848
4773.7188 | 123.8022 | -61.3998 | 62.1689 | -0.25307 | 0.013674 | 0.011277 | 0.011251 | 0.058539 | -0.0024695 | 0.078408 | -58.3237 | 62.1094 | -61.7249 | -61.5509 | 54.6844 | 24.5636 | 8.313 | 7.7683 | 62.1231 | -61.6699 | -0.32501 | -0.059509 | 3.0762 | -0.15106 | -7.4844 | -0.27008 | -0.045776 | 3.4012 | 69.7128 | 69.1681 | 116.0843 | 123.5092 | 3.0762 | 123.5229 | 85.9634 | -0.27008 | 123.5092 | 3.0762 | 85.9634 | 116.0843 | 123.5229 | -123.8937 | -123.8388
4774.7188 | 123.7564 | -61.4182 | 62.1826 | -0.16151 | 0.017733 | 0.012773 | 0.017874 | 0.061316 | -0.0016149 | 0.076058 | -58.3649 | 62.2101 | -61.7249 | -61.5738 | 54.6249 | 24.3805 | 8.4824 | 7.5348 | 62.1506 | -61.7065 | -0.3067 | 0.027466 | 3.0533 | -0.15564 | -7.5577 | -0.28839 | -0.032043 | 3.36 | 69.9005 | 68.9529 | 116.0431 | 123.6282 | 3.0533 | 123.5687 | 85.7986 | -0.28839 | 123.6282 | 3.0533 | 85.7986 | 116.0431 | 123.5687 | -123.9075 | -123.8892
4775.7188 | 123.8251 | -61.3998 | 62.1552 | -0.17677 | 0.01282 | 0.0093546 | 0.0095424 | 0.060034 | -0.0048193 | 0.077767 | -58.3191 | 62.1002 | -61.7294 | -61.5417 | 54.7119 | 24.472 | 8.3817 | 7.6126 | 62.114 | -61.6791 | -0.32959 | -0.054931 | 3.0807 | -0.14191 | -7.4432 | -0.27924 | -0.041198 | 3.4103 | 69.7815 | 69.0125 | 116.1118 | 123.5001 | 3.0807 | 123.5138 | 85.8719 | -0.27924 | 123.5001 | 3.0807 | 85.8719 | 116.1118 | 123.5138 | -123.8846 | -123.8342
4776.7188 | 123.7473 | -61.4273 | 62.1872 | -0.23018 | 0.014956 | 0.01085 | 0.013601 | 0.059607 | -0.0011877 | 0.078195 | -58.3466 | 62.114 | -61.7249 | -61.5967 | 54.6295 | 24.4858 | 8.3908 | 7.5073 | 62.1689 | -61.7065 | -0.29755 | -0.073242 | 3.0807 | -0.16937 | -7.5577 | -0.27924 | -0.018311 | 3.3783 | 69.8181 | 68.9346 | 116.0568 | 123.5413 | 3.0807 | 123.5962 | 85.9131 | -0.27924 | 123.5413 | 3.0807 | 85.9131 | 116.0568 | 123.5962 | -123.912 | -123.8937
4777.7188 | 123.7061 | -61.441 | 62.1735 | -0.23018 | 0.016238 | 0.0076456 | 0.010824 | 0.054694 | 0.00073487 | 0.077981 | -58.3923 | 62.146 | -61.7203 | -61.7249 | 54.6021 | 24.3027 | 8.3267 | 7.5119 | 62.1506 | -61.702 | -0.27924 | -0.027466 | 3.0487 | -0.28381 | -7.5714 | -0.26093 | -0.022888 | 3.3279 | 69.7678 | 68.9529 | 116.0431 | 123.587 | 3.0487 | 123.5916 | 85.7437 | -0.26093 | 123.587 | 3.0487 | 85.7437 | 116.0431 | 123.5916 | -123.8937 | -123.8754
4778.7188 | 123.7473 | -61.4136 | 62.1826 | -0.2607 | 0.014315 | 0.0082864 | 0.011679 | 0.059607 | -0.0011877 | 0.079049 | -58.3466 | 62.1277 | -61.7157 | -61.5738 | 54.6249 | 24.3484 | 8.3862 | 7.6126 | 62.1689 | -61.6791 | -0.30212 | -0.054931 | 3.067 | -0.16022 | -7.5577 | -0.2655 | -0.013733 | 3.3691 | 69.7998 | 69.0262 | 116.0385 | 123.5413 | 3.067 | 123.5825 | 85.762 | -0.2655 | 123.5413 | 3.067 | 85.762 | 116.0385 | 123.5825 | -123.8983 | -123.8617
4779.7344 | 123.7152 | -61.4456 | 62.1506 | 0.03685 | 0.014315 | 0.014482 | 0.020224 | 0.061316 | -0.0035375 | 0.080544 | -58.3603 | 62.1964 | -61.7249 | -61.6516 | 54.5609 | 24.2294 | 8.432 | 7.489 | 62.1506 | -61.7615 | -0.27924 | 0.045776 | 3.0853 | -0.20599 | -7.5897 | -0.31586 | 0 | 3.3646 | 69.8776 | 68.9346 | 116.0065 | 123.642 | 3.0853 | 123.5962 | 85.675 | -0.31586 | 123.642 | 3.0853 | 85.675 | 116.0065 | 123.5962 | -123.8754 | -123.912
4780.7188 | 123.7381 | -61.3953 | 62.1689 | -0.29121 | 0.014529 | 0.011277 | 0.01232 | 0.060462 | -0.0026831 | 0.076913 | -58.3466 | 62.1231 | -61.734 | -61.5738 | 54.6799 | 24.6368 | 8.4412 | 7.6538 | 62.178 | -61.6791 | -0.33875 | -0.045776 | 3.0487 | -0.17853 | -7.489 | -0.28381 | 0.009156 | 3.3875 | 69.8364 | 69.0491 | 116.0751 | 123.5184 | 3.0487 | 123.5733 | 86.0321 | -0.28381 | 123.5184 | 3.0487 | 86.0321 | 116.0751 | 123.5733 | -123.9029 | -123.848
4781.7188 | 123.8297 | -61.3907 | 62.1323 | -0.42854 | 0.014101 | 0.0072184 | 0.0093288 | 0.059394 | -0.0016149 | 0.07969 | -58.3511 | 62.0865 | -61.7294 | -61.5005 | 54.7394 | 24.4583 | 8.313 | 7.7362 | 62.1368 | -61.6882 | -0.33874 | -0.045776 | 3.0396 | -0.10986 | -7.3929 | -0.29755 | 0.004578 | 3.3783 | 69.7037 | 69.1269 | 116.1301 | 123.4772 | 3.0396 | 123.5275 | 85.849 | -0.29755 | 123.4772 | 3.0396 | 85.849 | 116.1301 | 123.5275 | -123.8617 | -123.8205
4782.7188 | 123.7793 | -61.409 | 62.1826 | -0.24544 | 0.014742 | 0.012986 | 0.011465 | 0.058539 | -0.0020421 | 0.080117 | -58.3237 | 62.114 | -61.7203 | -61.5509 | 54.6799 | 24.3439 | 8.4274 | 7.6767 | 62.1323 | -61.7065 | -0.31128 | -0.068664 | 3.0853 | -0.14191 | -7.5027 | -0.29755 | -0.050354 | 3.3966 | 69.8364 | 69.0857 | 116.0889 | 123.523 | 3.0853 | 123.5413 | 85.7529 | -0.29755 | 123.523 | 3.0853 | 85.7529 | 116.0889 | 123.5413 | -123.9029 | -123.8892
4783.7188 | 123.7152 | -61.4319 | 62.1689 | -0.45143 | 0.015169 | 0.011918 | 0.013601 | 0.058966 | -0.0016149 | 0.080758 | -58.3878 | 62.146 | -61.7249 | -61.6013 | 54.5654 | 24.2981 | 8.4412 | 7.4661 | 62.1643 | -61.702 | -0.29297 | -0.022888 | 3.0441 | -0.16937 | -7.6035 | -0.27008 | -0.004577 | 3.3371 | 69.873 | 68.898 | 115.9973 | 123.5779 | 3.0441 | 123.5962 | 85.73 | -0.27008 | 123.5779 | 3.0441 | 85.73 | 115.9973 | 123.5962 | -123.8937 | -123.8708
4784.7188 | 123.7381 | -61.4044 | 62.1552 | -0.10048 | 0.015383 | 0.014695 | 0.01766 | 0.06153 | -0.0011877 | 0.078622 | -58.2916 | 62.1735 | -61.7386 | -61.5829 | 54.5883 | 24.2935 | 8.3313 | 7.5165 | 62.1368 | -61.7386 | -0.33417 | 0.018311 | 3.1128 | -0.17853 | -7.5668 | -0.33417 | -0.01831 | 3.447 | 69.7357 | 68.9209 | 115.9927 | 123.5779 | 3.1128 | 123.5413 | 85.6979 | -0.33417 | 123.5779 | 3.1128 | 85.6979 | 115.9927 | 123.5413 | -123.8937 | -123.8937
4785.7188 | 123.7106 | -61.4273 | 62.1964 | 1.7992 | 0.016451 | 0.007432 | 0.014669 | 0.060248 | -0.0022559 | 0.078835 | -58.493 | 62.1368 | -61.7523 | -61.6104 | 54.6066 | 24.4171 | 8.4686 | 7.5623 | 62.178 | -61.702 | -0.32501 | -0.059509 | 2.9343 | -0.18311 | -7.5897 | -0.27466 | -0.01831 | 3.2593 | 69.8959 | 68.9896 | 116.0339 | 123.5641 | 2.9343 | 123.6053 | 85.8444 | -0.27466 | 123.5641 | 2.9343 | 85.8444 | 116.0339 | 123.6053 | -123.9487 | -123.8983
4786.7188 | 123.7381 | -61.4182 | 62.1826 | -0.26833 | 0.013033 | 0.006791 | 0.011679 | 0.06153 | -0.0016149 | 0.078622 | -58.3557 | 62.1231 | -61.7294 | -61.5967 | 54.57 | 24.2432 | 8.4686 | 7.6035 | 62.1597 | -61.702 | -0.31128 | -0.059509 | 3.0624 | -0.17853 | -7.6126 | -0.28381 | -0.022888 | 3.3737 | 69.8868 | 69.0216 | 115.9882 | 123.5413 | 3.0624 | 123.5779 | 85.6613 | -0.28381 | 123.5413 | 3.0624 | 85.6613 | 115.9882 | 123.5779 | -123.912 | -123.8846
4787.7188 | 123.7473 | -61.4182 | 62.178 | -0.23781 | 0.013888 | 0.0097818 | 0.011892 | 0.062384 | -0.0026831 | 0.077126 | -58.342 | 62.1231 | -61.7249 | -61.5875 | 54.5975 | 24.408 | 8.4778 | 7.7225 | 62.1826 | -61.6882 | -0.3067 | -0.054932 | 3.0762 | -0.16937 | -7.5806 | -0.27008 | 0.004577 | 3.3829 | 69.8959 | 69.1406 | 116.0156 | 123.5413 | 3.0762 | 123.6008 | 85.8261 | -0.27008 | 123.5413 | 3.0762 | 85.8261 | 116.0156 | 123.6008 | -123.9029 | -123.8663
4788.7188 | 123.8297 | -61.3998 | 62.146 | -0.23018 | 0.013888 | 0.010209 | 0.010824 | 0.060462 | -0.0024695 | 0.080758 | -58.3191 | 62.1094 | -61.6974 | -61.5189 | 54.6524 | 24.5773 | 8.2672 | 7.7271 | 62.1414 | -61.6608 | -0.29755 | -0.036621 | 3.0807 | -0.11902 | -7.4936 | -0.26093 | -0.004578 | 3.3783 | 69.6671 | 69.1269 | 116.0522 | 123.5092 | 3.0807 | 123.5413 | 85.9772 | -0.26093 | 123.5092 | 3.0807 | 85.9772 | 116.0522 | 123.5413 | -123.8434 | -123.8068
4789.7344 | 123.7335 | -61.4639 | 62.1552 | 0.013962 | 0.014529 | 0.012559 | 0.018515 | 0.061103 | -0.0020421 | 0.078835 | -58.3328 | 62.1826 | -61.7294 | -61.6287 | 54.5837 | 24.5041 | 8.2901 | 7.5027 | 62.1277 | -61.7249 | -0.2655 | 0.027466 | 3.1311 | -0.16479 | -7.5714 | -0.26093 | -0.027465 | 3.3966 | 69.754 | 68.9667 | 116.0477 | 123.6465 | 3.1311 | 123.5916 | 85.968 | -0.26093 | 123.6465 | 3.1311 | 85.968 | 116.0477 | 123.5916 | -123.8846 | -123.88
4790.7188 | 123.7335 | -61.4273 | 62.1643 | -0.21492 | 0.012606 | 0.013841 | 0.01531 | 0.060034 | -0.0026831 | 0.079049 | -58.3786 | 62.178 | -61.7477 | -61.615 | 54.6341 | 24.527 | 8.3405 | 7.2372 | 62.2055 | -61.702 | -0.32044 | 0.013733 | 3.0487 | -0.18768 | -7.5302 | -0.27466 | 0.041198 | 3.3691 | 69.7678 | 68.6646 | 116.0614 | 123.6053 | 3.0487 | 123.6328 | 85.9543 | -0.27466 | 123.6053 | 3.0487 | 85.9543 | 116.0614 | 123.6328 | -123.912 | -123.8663
4791.7344 | 123.8159 | -61.3907 | 62.0773 | 0.28099 | 0.014742 | 0.012345 | 0.014669 | 0.062384 | 0.00073487 | 0.078195 | -58.3099 | 62.114 | -61.7203 | -61.5692 | 54.6478 | 24.3713 | 8.0978 | 7.5027 | 62.1002 | -61.6974 | -0.32959 | 0.036621 | 3.0807 | -0.17853 | -7.4295 | -0.3067 | 0.022888 | 3.4103 | 69.4885 | 68.8934 | 116.0385 | 123.5046 | 3.0807 | 123.4909 | 85.762 | -0.3067 | 123.5046 | 3.0807 | 85.762 | 116.0385 | 123.4909 | -123.7976 | -123.7747
4792.7188 | 123.7198 | -61.4548 | 62.1643 | -0.27596 | 0.01581 | 0.0093546 | 0.01232 | 0.060462 | -0.0028967 | 0.07969 | -58.3878 | 62.1506 | -61.734 | -61.6287 | 54.6066 | 24.1837 | 8.7067 | 7.5897 | 62.1918 | -61.7157 | -0.27924 | -0.013733 | 3.067 | -0.17395 | -7.5577 | -0.26093 | 0.027465 | 3.3463 | 70.1614 | 69.0445 | 116.0614 | 123.6053 | 3.067 | 123.6465 | 85.6384 | -0.26093 | 123.6053 | 3.067 | 85.6384 | 116.0614 | 123.6465 | -123.8983 | -123.88
4793.7188 | 123.7518 | -61.4227 | 62.1597 | -0.1844 | 0.015597 | 0.0093546 | 0.016378 | 0.059394 | 0.00052127 | 0.075845 | -58.3694 | 62.1735 | -61.734 | -61.6287 | 54.6295 | 24.5041 | 8.4045 | 7.6309 | 62.1689 | -61.7111 | -0.31128 | 0.013733 | 3.0533 | -0.20599 | -7.5302 | -0.28839 | 0.009155 | 3.3646 | 69.8273 | 69.0536 | 116.0522 | 123.5962 | 3.0533 | 123.5916 | 85.9268 | -0.28839 | 123.5962 | 3.0533 | 85.9268 | 116.0522 | 123.5916 | -123.8937 | -123.8708
4794.7188 | 123.7335 | -61.4502 | 62.1506 | -0.039444 | 0.016238 | 0.011491 | 0.016806 | 0.063452 | -0.0031103 | 0.078408 | -58.3054 | 62.178 | -61.734 | -61.6241 | 54.5883 | 24.1974 | 8.3679 | 7.6859 | 62.1643 | -61.7294 | -0.28381 | 0.027466 | 3.1448 | -0.17395 | -7.5623 | -0.27924 | 0.013733 | 3.4286 | 69.8181 | 69.136 | 116.0385 | 123.6282 | 3.1448 | 123.6145 | 85.6476 | -0.27924 | 123.6282 | 3.1448 | 85.6476 | 116.0385 | 123.6145 | -123.8846 | -123.88
4795.7188 | 123.6603 | -61.4365 | 62.1597 | -0.27596 | 0.015383 | 0.011491 | 0.011679 | 0.05918 | -0.0026831 | 0.078622 | -58.3969 | 62.1872 | -61.7432 | -61.6196 | 54.6249 | 24.2249 | 8.5648 | 7.8049 | 62.2284 | -61.702 | -0.3067 | 0.027466 | 3.0395 | -0.18311 | -7.5348 | -0.2655 | 0.068665 | 3.3463 | 70.0012 | 69.2413 | 116.0614 | 123.6237 | 3.0395 | 123.6649 | 85.6613 | -0.2655 | 123.6237 | 3.0395 | 85.6613 | 116.0614 | 123.6649 | -123.9029 | -123.8617
4796.7344 | 123.6649 | -61.4594 | 62.1414 | 0.067368 | 0.016238 | 0.012559 | 0.016806 | 0.062812 | -0.0011877 | 0.079476 | -58.3923 | 62.2009 | -61.7386 | -61.647 | 54.5792 | 24.1928 | 8.3679 | 7.3837 | 62.1597 | -61.7706 | -0.27923 | 0.05951 | 3.067 | -0.18768 | -7.5623 | -0.31128 | 0.018311 | 3.3463 | 69.8273 | 68.8431 | 116.0385 | 123.6603 | 3.067 | 123.6191 | 85.6522 | -0.31128 | 123.6603 | 3.067 | 85.6522 | 116.0385 | 123.6191 | -123.88 | -123.912
4797.7188 | 123.7244 | -61.4273 | 62.1597 | -0.16914 | 0.016665 | 0.0093546 | 0.011892 | 0.060675 | -0.0020421 | 0.07734 | -58.3878 | 62.1964 | -61.7523 | -61.6196 | 54.657 | 24.3027 | 8.4961 | 7.7408 | 62.178 | -61.7477 | -0.32501 | 0.036621 | 3.0396 | -0.19226 | -7.5027 | -0.32044 | 0.018311 | 3.3646 | 69.9234 | 69.1681 | 116.0843 | 123.6237 | 3.0396 | 123.6053 | 85.73 | -0.32044 | 123.6237 | 3.0396 | 85.73 | 116.0843 | 123.6053 | -123.912 | -123.9075
4798.7188 | 123.7061 | -61.4365 | 62.1689 | -0.25307 | 0.013033 | 0.012345 | 0.012533 | 0.060462 | -0.0018285 | 0.07969 | -58.3786 | 62.1872 | -61.7523 | -61.6287 | 54.6158 | 24.1745 | 8.3817 | 7.7362 | 62.1643 | -61.7065 | -0.31586 | 0.018311 | 3.0579 | -0.19226 | -7.5531 | -0.27008 | -0.004577 | 3.3737 | 69.8181 | 69.1727 | 116.0522 | 123.6237 | 3.0579 | 123.6008 | 85.611 | -0.27008 | 123.6237 | 3.0579 | 85.611 | 116.0522 | 123.6008 | -123.9212 | -123.8754
4799.7188 | 123.6877 | -61.4182 | 62.1597 | 0.03685 | 0.015169 | 0.014482 | 0.012533 | 0.065589 | -0.0014013 | 0.079476 | -58.3694 | 62.1964 | -61.7432 | -61.6562 | 54.5746 | 24.1425 | 8.345 | 7.6401 | 62.1735 | -61.7615 | -0.32501 | 0.036621 | 3.0487 | -0.23804 | -7.5851 | -0.34332 | 0.013733 | 3.3737 | 69.7632 | 69.0582 | 115.9927 | 123.6145 | 3.0487 | 123.5916 | 85.5606 | -0.34332 | 123.6145 | 3.0487 | 85.5606 | 115.9927 | 123.5916 | -123.9029 | -123.9212
4800.7188 | 123.7244 | -61.441 | 62.1735 | -0.0089264 | 0.016451 | 0.013627 | 0.011251 | 0.06388 | 0.00094847 | 0.078195 | -58.3603 | 62.1918 | -61.7432 | -61.6241 | 54.6021 | 24.1241 | 8.4732 | 7.6996 | 62.178 | -61.7432 | -0.30212 | 0.01831 | 3.0807 | -0.18311 | -7.5714 | -0.30212 | 0.004578 | 3.3829 | 69.9142 | 69.1406 | 116.0431 | 123.6328 | 3.0807 | 123.6191 | 85.5652 | -0.30212 | 123.6328 | 3.0807 | 85.5652 | 116.0431 | 123.6191 | -123.9166 | -123.9166
4801.7344 | 123.7335 | -61.4456 | 62.114 | 0.11314 | 0.017092 | 0.011918 | 0.01232 | 0.064734 | 0.0015893 | 0.078835 | -58.4015 | 62.1735 | -61.7569 | -61.6699 | 54.57 | 24.1196 | 8.432 | 7.7911 | 62.1414 | -61.7569 | -0.31128 | 0.059509 | 3.0441 | -0.2243 | -7.5439 | -0.31128 | 0.027465 | 3.3554 | 69.8776 | 69.2368 | 116.0156 | 123.6191 | 3.0441 | 123.587 | 85.5652 | -0.31128 | 123.6191 | 3.0441 | 85.5652 | 116.0156 | 123.587 | -123.8709 | -123.8709
4802.7188 | 123.7152 | -61.4227 | 62.1597 | 1.6543 | 0.015169 | 0.0132 | 0.0099698 | 0.061743 | -0.0011877 | 0.078408 | -58.374 | 62.1689 | -61.7615 | -61.6241 | 54.6295 | 24.2569 | 8.6243 | 7.9422 | 62.2009 | -61.7477 | -0.33875 | 0.009155 | 3.0487 | -0.20142 | -7.5302 | -0.32501 | 0.041199 | 3.3875 | 70.047 | 69.3649 | 116.0522 | 123.5916 | 3.0487 | 123.6237 | 85.6796 | -0.32501 | 123.5916 | 3.0487 | 85.6796 | 116.0522 | 123.6237 | -123.9212 | -123.9075
4803.7188 | 123.7381 | -61.4227 | 62.1735 | -0.23781 | 0.012179 | 0.011918 | 0.011679 | 0.062598 | -0.00033333 | 0.078622 | -58.168 | 62.2192 | -61.7294 | -61.615 | 54.5609 | 24.0326 | 8.5648 | 7.8598 | 62.1964 | -61.7615 | -0.3067 | 0.045776 | 3.2547 | -0.19226 | -7.6126 | -0.33875 | 0.022888 | 3.5614 | 69.9875 | 69.2825 | 115.9836 | 123.642 | 3.2547 | 123.6191 | 85.4553 | -0.33875 | 123.642 | 3.2547 | 85.4553 | 115.9836 | 123.6191 | -123.9029 | -123.9349
4804.7188 | 123.7381 | -61.4456 | 62.1506 | 0.029221 | 0.014315 | 0.015763 | 0.016165 | 0.06388 | -0.0033239 | 0.07734 | -58.3191 | 62.2055 | -61.734 | -61.6287 | 54.538 | 24.0829 | 8.4137 | 7.7042 | 62.1414 | -61.7432 | -0.28839 | 0.054931 | 3.1265 | -0.1831 | -7.6126 | -0.29755 | -0.009156 | 3.4149 | 69.8593 | 69.1498 | 115.9836 | 123.6511 | 3.1265 | 123.587 | 85.5286 | -0.29755 | 123.6511 | 3.1265 | 85.5286 | 115.9836 | 123.587 | -123.8846 | -123.8937
4805.7188 | 123.7564 | -61.4273 | 62.178 | -0.20729 | 0.016238 | 0.011918 | 0.014669 | 0.06153 | -0.00076053 | 0.077767 | -58.3603 | 62.1964 | -61.7569 | -61.615 | 54.5517 | 24.202 | 8.4778 | 7.7545 | 62.1964 | -61.7386 | -0.32959 | 0.01831 | 3.067 | -0.18768 | -7.6263 | -0.31128 | 0.01831 | 3.3966 | 69.9051 | 69.1818 | 115.979 | 123.6237 | 3.067 | 123.6237 | 85.6293 | -0.31128 | 123.6237 | 3.067 | 85.6293 | 115.979 | 123.6237 | -123.9349 | -123.9166
4806.7188 | 123.8159 | -61.4044 | 62.1048 | 0.10551 | 0.013033 | 0.009141 | 0.0078336 | 0.061743 | -0.0039649 | 0.080331 | -58.3191 | 62.0956 | -61.702 | -61.5921 | 54.6158 | 24.202 | 8.2397 | 7.8186 | 62.1048 | -61.7157 | -0.29755 | -0.009155 | 3.0853 | -0.18768 | -7.489 | -0.31128 | 0 | 3.3829 | 69.6442 | 69.223 | 116.0202 | 123.5001 | 3.0853 | 123.5092 | 85.6064 | -0.31128 | 123.5001 | 3.0853 | 85.6064 | 116.0202 | 123.5092 | -123.8068 | -123.8205
4807.7188 | 123.7198 | -61.4365 | 62.1918 | 0.029221 | 0.015597 | 0.0089274 | 0.013815 | 0.059821 | -0.0016149 | 0.078408 | -58.3374 | 62.1826 | -61.7294 | -61.6196 | 54.5883 | 24.028 | 8.4457 | 7.6767 | 62.1964 | -61.7477 | -0.29297 | -0.009155 | 3.0991 | -0.18311 | -7.6035 | -0.31128 | 0.004578 | 3.392 | 69.8822 | 69.1132 | 116.0248 | 123.6191 | 3.0991 | 123.6328 | 85.4645 | -0.31128 | 123.6191 | 3.0991 | 85.4645 | 116.0248 | 123.6328 | -123.9212 | -123.9395
4808.7188 | 123.7289 | -61.4548 | 62.1735 | -0.73372 | 0.017947 | 0.016191 | 0.013601 | 0.06153 | -0.00054693 | 0.077981 | -58.3923 | 62.1826 | -61.7752 | -61.6196 | 54.5334 | 24.2386 | 8.4549 | 7.695 | 62.2009 | -61.7203 | -0.32043 | 0.009155 | 3.0624 | -0.16479 | -7.6401 | -0.2655 | 0.027466 | 3.3829 | 69.9097 | 69.1498 | 115.9882 | 123.6374 | 3.0624 | 123.6557 | 85.6934 | -0.2655 | 123.6374 | 3.0624 | 85.6934 | 115.9882 | 123.6557 | -123.9487 | -123.8937
4809.7344 | 123.8068 | -61.4227 | 62.1094 | 0.22758 | 0.016878 | 0.0097818 | 0.014669 | 0.062598 | -0.0020421 | 0.081399 | -58.3603 | 62.1414 | -61.7432 | -61.615 | 54.5746 | 24.2249 | 8.2581 | 7.6126 | 62.1277 | -61.7661 | -0.32044 | 0.032043 | 3.0624 | -0.19226 | -7.5348 | -0.34332 | 0.018311 | 3.3829 | 69.6808 | 69.0353 | 115.9973 | 123.5641 | 3.0624 | 123.5504 | 85.6476 | -0.34332 | 123.5641 | 3.0624 | 85.6476 | 115.9973 | 123.5504 | -123.8525 | -123.8754
4810.7188 | 123.7106 | -61.4365 | 62.1826 | -0.25307 | 0.016024 | 0.0132 | 0.011465 | 0.063025 | -0.0037511 | 0.075631 | -58.3649 | 62.2055 | -61.7249 | -61.409 | 54.5425 | 24.0372 | 8.4503 | 7.5073 | 62.1872 | -61.7661 | -0.28839 | 0.022888 | 3.0716 | 0.027465 | -7.6401 | -0.32959 | 0.004578 | 3.36 | 69.8868 | 68.9438 | 115.979 | 123.642 | 3.0716 | 123.6237 | 85.4736 | -0.32959 | 123.642 | 3.0716 | 85.4736 | 115.979 | 123.6237 | -123.9075 | -123.9487
4811.7188 | 123.7473 | -61.409 | 62.1826 | -0.1844 | 0.014956 | 0.014909 | 0.017019 | 0.05918 | -0.0018285 | 0.078835 | -58.3603 | 62.178 | -61.734 | -61.6058 | 54.5975 | 24.1333 | 8.4229 | 7.5302 | 62.2055 | -61.7157 | -0.32501 | -0.004577 | 3.0487 | -0.19684 | -7.5851 | -0.3067 | 0.022888 | 3.3737 | 69.8318 | 68.9392 | 116.0065 | 123.587 | 3.0487 | 123.6145 | 85.5423 | -0.3067 | 123.587 | 3.0487 | 85.5423 | 116.0065 | 123.6145 | -123.9166 | -123.8983
4812.7188 | 123.7152 | -61.4319 | 62.1552 | -0.1844 | 0.016665 | 0.009141 | 0.012106 | 0.062598 | -0.00011953 | 0.077554 | -58.3649 | 62.1918 | -61.7523 | -61.615 | 54.5746 | 24.1745 | 8.4915 | 7.6172 | 62.1964 | -61.7386 | -0.32043 | 0.036621 | 3.067 | -0.1831 | -7.5806 | -0.3067 | 0.041199 | 3.3875 | 69.9234 | 69.0491 | 116.0065 | 123.6237 | 3.067 | 123.6282 | 85.6064 | -0.3067 | 123.6237 | 3.067 | 85.6064 | 116.0065 | 123.6282 | -123.9075 | -123.8937
4813.7188 | 123.7244 | -61.4227 | 62.1689 | -0.48195 | 0.015597 | 0.012132 | 0.011038 | 0.060889 | -0.0028967 | 0.078195 | -58.3878 | 62.1918 | -61.7569 | -61.6287 | 54.5563 | 24.0646 | 8.4732 | 7.7408 | 62.1872 | -61.7294 | -0.33417 | 0.022888 | 3.035 | -0.20599 | -7.6126 | -0.3067 | 0.018311 | 3.3691 | 69.8959 | 69.1635 | 115.979 | 123.6145 | 3.035 | 123.6099 | 85.4874 | -0.3067 | 123.6145 | 3.035 | 85.4874 | 115.979 | 123.6099 | -123.9258 | -123.8983
4814.7188 | 123.7701 | -61.4273 | 62.1872 | -0.09285 | 0.016451 | 0.0132 | 0.015951 | 0.062171 | -0.00054693 | 0.077981 | -58.2916 | 62.2009 | -61.7386 | -61.5921 | 54.6158 | 24.321 | 8.3221 | 7.7179 | 62.1826 | -61.7203 | -0.31128 | 0.013733 | 3.1357 | -0.16479 | -7.5714 | -0.29297 | -0.004578 | 3.447 | 69.7495 | 69.1452 | 116.0431 | 123.6282 | 3.1357 | 123.6099 | 85.7483 | -0.29297 | 123.6282 | 3.1357 | 85.7483 | 116.0431 | 123.6099 | -123.9258 | -123.9075
4815.7188 | 123.7289 | -61.4456 | 62.1872 | -0.21492 | 0.013888 | 0.0078592 | 0.013388 | 0.061743 | -0.0024695 | 0.078835 | -58.3786 | 62.1735 | -61.734 | -61.6653 | 54.5471 | 24.2203 | 8.4229 | 7.7408 | 62.1872 | -61.7249 | -0.28839 | -0.013733 | 3.067 | -0.21973 | -7.6401 | -0.27924 | 0 | 3.3554 | 69.8685 | 69.1864 | 115.9927 | 123.6191 | 3.067 | 123.6328 | 85.6659 | -0.27924 | 123.6191 | 3.067 | 85.6659 | 115.9927 | 123.6328 | -123.9212 | -123.912
4816.7188 | 123.7152 | -61.4594 | 62.1964 | -0.19966 | 0.014956 | 0.015977 | 0.012106 | 0.060248 | -0.0016149 | 0.081399 | -58.3557 | 62.1918 | -61.7386 | -61.4136 | 54.7028 | 24.0097 | 8.3496 | 7.695 | 62.1918 | -61.7249 | -0.27923 | -0.004578 | 3.1036 | 0.045777 | -7.4936 | -0.2655 | -0.004578 | 3.3829 | 69.809 | 69.1544 | 116.1621 | 123.6511 | 3.1036 | 123.6511 | 85.4691 | -0.2655 | 123.6511 | 3.1036 | 85.4691 | 116.1621 | 123.6511 | -123.9349 | -123.9212
4817.7188 | 123.6786 | -61.4044 | 62.1414 | -0.23781 | 0.015383 | 0.011704 | 0.011465 | 0.060248 | -0.0018285 | 0.079476 | -58.374 | 62.178 | -61.7615 | -61.6196 | 54.6112 | 24.1882 | 8.4961 | 7.9651 | 62.2147 | -61.7249 | -0.35706 | 0.036622 | 3.0304 | -0.21515 | -7.5302 | -0.32044 | 0.073243 | 3.3875 | 69.9005 | 69.3695 | 116.0156 | 123.5825 | 3.0304 | 123.6191 | 85.5927 | -0.32044 | 123.5825 | 3.0304 | 85.5927 | 116.0156 | 123.6191 | -123.9029 | -123.8663
4818.7188 | 123.7518 | -61.4319 | 62.1872 | -0.30647 | 0.016024 | 0.0080728 | 0.01296 | 0.061103 | -0.0033239 | 0.079263 | -58.3786 | 62.1689 | -61.7706 | -61.6287 | 54.6021 | 24.2981 | 8.5144 | 7.7774 | 62.1735 | -61.7294 | -0.33874 | -0.018311 | 3.0533 | -0.19684 | -7.5851 | -0.29755 | -0.013733 | 3.392 | 69.9463 | 69.2093 | 116.0339 | 123.6008 | 3.0533 | 123.6053 | 85.73 | -0.29755 | 123.6008 | 3.0533 | 85.73 | 116.0339 | 123.6053 | -123.9578 | -123.9166
4819.7188 | 123.7061 | -61.4548 | 62.1643 | 0.013962 | 0.01816 | 0.015763 | 0.015097 | 0.062812 | -0.0022559 | 0.077981 | -58.3511 | 62.2055 | -61.7569 | -61.6608 | 54.5792 | 24.1974 | 8.3542 | 7.6767 | 62.1826 | -61.7752 | -0.30212 | 0.041198 | 3.1036 | -0.20599 | -7.5851 | -0.32043 | 0.01831 | 3.4058 | 69.809 | 69.1315 | 116.0339 | 123.6603 | 3.1036 | 123.6374 | 85.6522 | -0.32043 | 123.6603 | 3.1036 | 85.6522 | 116.0339 | 123.6374 | -123.9212 | -123.9395
4820.7188 | 123.7198 | -61.4365 | 62.1964 | 0.067368 | 0.014956 | 0.010209 | 0.0097562 | 0.064093 | -0.0020421 | 0.077767 | -58.3511 | 62.1826 | -61.7432 | -61.6379 | 54.5837 | 24.1745 | 8.3954 | 7.6721 | 62.2147 | -61.702 | -0.3067 | -0.013733 | 3.0853 | -0.20142 | -7.6126 | -0.2655 | 0.018311 | 3.392 | 69.8318 | 69.1086 | 116.0202 | 123.6191 | 3.0853 | 123.6511 | 85.611 | -0.2655 | 123.6191 | 3.0853 | 85.611 | 116.0202 | 123.6511 | -123.9395 | -123.8983
4821.7188 | 123.7427 | -61.441 | 62.1552 | -0.5201 | 0.015383 | 0.011277 | 0.010397 | 0.060675 | -0.00076053 | 0.078408 | -58.3786 | 62.178 | -61.7706 | -61.6379 | 54.5563 | 24.2294 | 8.5144 | 8.0063 | 62.178 | -61.7523 | -0.32959 | 0.022889 | 3.0624 | -0.19684 | -7.5989 | -0.31128 | 0.022889 | 3.392 | 69.9554 | 69.4473 | 115.9973 | 123.6191 | 3.0624 | 123.6191 | 85.6705 | -0.31128 | 123.6191 | 3.0624 | 85.6705 | 115.9973 | 123.6191 | -123.9258 | -123.9075
4822.7188 | 123.7289 | -61.4548 | 62.1414 | 0.1284 | 0.015169 | 0.019822 | 0.013174 | 0.061316 | -0.00076053 | 0.079476 | -58.3511 | 62.1872 | -61.7569 | -61.6241 | 54.6066 | 24.4125 | 8.4686 | 7.9559 | 62.1826 | -61.7294 | -0.30212 | 0.045777 | 3.1036 | -0.16937 | -7.5348 | -0.27466 | 0.041199 | 3.4058 | 69.9234 | 69.4107 | 116.0614 | 123.642 | 3.1036 | 123.6374 | 85.8673 | -0.27466 | 123.642 | 3.1036 | 85.8673 | 116.0614 | 123.6374 | -123.8983 | -123.8708
4823.7188 | 123.7701 | -61.4227 | 62.146 | -0.21492 | 0.015383 | 0.014909 | 0.012747 | 0.062171 | -0.0011877 | 0.077981 | -58.342 | 62.1918 | -61.7157 | -61.6104 | 54.6066 | 24.3027 | 8.551 | 7.8644 | 62.1826 | -61.7386 | -0.29297 | 0.045776 | 3.0807 | -0.18768 | -7.5394 | -0.31586 | 0.036621 | 3.3737 | 69.9738 | 69.2871 | 116.0294 | 123.6145 | 3.0807 | 123.6053 | 85.7254 | -0.31586 | 123.6145 | 3.0807 | 85.7254 | 116.0294 | 123.6053 | -123.8617 | -123.8846
4824.7344 | 123.7198 | -61.441 | 62.1277 | 0.13603 | 0.017306 | 0.011704 | 0.01296 | 0.065161 | -0.00076053 | 0.077767 | -58.3786 | 62.1872 | -61.7523 | -61.6699 | 54.5517 | 24.3759 | 8.3725 | 7.8323 | 62.1643 | -61.7661 | -0.31128 | 0.059509 | 3.0624 | -0.22888 | -7.576 | -0.32501 | 0.036621 | 3.3737 | 69.8135 | 69.2734 | 115.9927 | 123.6282 | 3.0624 | 123.6053 | 85.817 | -0.32501 | 123.6282 | 3.0624 | 85.817 | 115.9927 | 123.6053 | -123.88 | -123.8937
4825.7188 | 123.7518 | -61.4319 | 62.146 | -0.16914 | 0.014956 | 0.015977 | 0.01531 | 0.062598 | -0.0011877 | 0.078835 | -58.2779 | 62.178 | -61.7203 | -61.6013 | 54.6021 | 24.3896 | 8.4137 | 7.869 | 62.178 | -61.7294 | -0.28839 | 0.032044 | 3.154 | -0.16937 | -7.5439 | -0.29755 | 0.032044 | 3.4424 | 69.8456 | 69.3008 | 116.0339 | 123.6099 | 3.154 | 123.6099 | 85.8215 | -0.29755 | 123.6099 | 3.154 | 85.8215 | 116.0339 | 123.6099 | -123.8663 | -123.8754
4826.7188 | 123.761 | -61.441 | 62.1597 | -0.23018 | 0.019656 | 0.014695 | 0.013388 | 0.064521 | -0.0018285 | 0.079049 | -58.342 | 62.1689 | -61.7203 | -61.6058 | 54.6295 | 24.4446 | 8.3725 | 7.8873 | 62.2147 | -61.7249 | -0.27924 | 0.009155 | 3.0991 | -0.16479 | -7.5302 | -0.28381 | 0.054932 | 3.3783 | 69.8135 | 69.3283 | 116.0706 | 123.6099 | 3.0991 | 123.6557 | 85.8856 | -0.28381 | 123.6099 | 3.0991 | 85.8856 | 116.0706 | 123.6557 | -123.88 | -123.8846
4827.7188 | 123.7335 | -61.4273 | 62.1552 | -0.11574 | 0.016451 | 0.011918 | 0.013388 | 0.063452 | -0.00011953 | 0.078835 | -58.3237 | 62.1918 | -61.734 | -61.5967 | 54.6021 | 24.3439 | 8.4045 | 7.8552 | 62.2009 | -61.7477 | -0.3067 | 0.036621 | 3.1036 | -0.16937 | -7.5531 | -0.32044 | 0.045777 | 3.4103 | 69.8318 | 69.2825 | 116.0294 | 123.6191 | 3.1036 | 123.6282 | 85.7712 | -0.32044 | 123.6191 | 3.1036 | 85.7712 | 116.0294 | 123.6282 | -123.8892 | -123.9029
4828.7188 | 123.7564 | -61.4273 | 62.1689 | -0.15388 | 0.017306 | 0.011064 | 0.01296 | 0.062384 | -0.0018285 | 0.081399 | -58.342 | 62.178 | -61.7477 | -61.5967 | 54.5883 | 24.44 | 8.4641 | 7.7362 | 62.1918 | -61.7111 | -0.32044 | 0.009156 | 3.0853 | -0.16937 | -7.5806 | -0.28381 | 0.022888 | 3.4058 | 69.8914 | 69.1635 | 116.0156 | 123.6053 | 3.0853 | 123.6191 | 85.8673 | -0.28381 | 123.6053 | 3.0853 | 85.8673 | 116.0156 | 123.6191 | -123.9166 | -123.88
4829.7188 | 123.8434 | -61.4548 | 62.1323 | 0.082626 | 0.017092 | 0.015336 | 0.014456 | 0.064093 | -0.00011953 | 0.081185 | -58.3786 | 62.1643 | -61.7844 | -61.6699 | 54.5288 | 24.2844 | 8.3817 | 7.4203 | 62.1277 | -61.7889 | -0.32959 | 0.032044 | 3.0762 | -0.21515 | -7.6035 | -0.33417 | -0.004577 | 3.4058 | 69.8364 | 68.8751 | 115.9836 | 123.6191 | 3.0762 | 123.5825 | 85.7391 | -0.33417 | 123.6191 | 3.0762 | 85.7391 | 115.9836 | 123.5825 | -123.9166 | -123.9212
4830.7188 | 123.7656 | -61.4136 | 62.1597 | -0.17677 | 0.014956 | 0.010209 | 0.013174 | 0.064948 | -0.0016149 | 0.079263 | -58.3191 | 62.1964 | -61.7615 | -61.6058 | 54.5929 | 24.3942 | 8.4915 | 7.8918 | 62.1826 | -61.7523 | -0.3479 | 0.036621 | 3.0945 | -0.19226 | -7.5668 | -0.33875 | 0.022888 | 3.4424 | 69.9051 | 69.3054 | 116.0065 | 123.6099 | 3.0945 | 123.5962 | 85.8078 | -0.33875 | 123.6099 | 3.0945 | 85.8078 | 116.0065 | 123.5962 | -123.9212 | -123.912
4831.7188 | 123.7427 | -61.4227 | 62.1597 | -0.09285 | 0.015597 | 0.0082864 | 0.013388 | 0.064521 | -0.0031103 | 0.081185 | -58.2687 | 62.1872 | -61.7477 | -61.5829 | 54.6295 | 24.4446 | 8.3267 | 7.7087 | 62.178 | -61.7477 | -0.32501 | 0.027466 | 3.154 | -0.16022 | -7.5302 | -0.32501 | 0.018311 | 3.479 | 69.7494 | 69.1315 | 116.0522 | 123.6099 | 3.154 | 123.6008 | 85.8673 | -0.32501 | 123.6099 | 3.154 | 85.8673 | 116.0522 | 123.6008 | -123.9075 | -123.9075
4832.7188 | 123.7427 | -61.409 | 62.1414 | -0.16151 | 0.017092 | 0.015763 | 0.015097 | 0.063452 | 0.00030767 | 0.078408 | -58.2779 | 62.1872 | -61.7203 | -61.5921 | 54.6204 | 24.4354 | 8.3496 | 7.8186 | 62.1597 | -61.7477 | -0.31128 | 0.045777 | 3.1311 | -0.1831 | -7.5211 | -0.33875 | 0.018311 | 3.4424 | 69.7586 | 69.2276 | 116.0294 | 123.5962 | 3.1311 | 123.5687 | 85.8444 | -0.33875 | 123.5962 | 3.1311 | 85.8444 | 116.0294 | 123.5687 | -123.8617 | -123.8892
4833.7188 | 123.7885 | -61.4273 | 62.1323 | -0.1844 | 0.014101 | 0.014695 | 0.01531 | 0.063666 | -0.0031103 | 0.077554 | -58.2916 | 62.1872 | -61.7432 | -61.5921 | 54.57 | 24.4583 | 8.2764 | 7.7911 | 62.1689 | -61.7523 | -0.31586 | 0.054932 | 3.1357 | -0.16479 | -7.5623 | -0.32501 | 0.036621 | 3.4515 | 69.7037 | 69.2184 | 115.9973 | 123.6145 | 3.1357 | 123.5962 | 85.8856 | -0.32501 | 123.6145 | 3.1357 | 85.8856 | 115.9973 | 123.5962 | -123.8754 | -123.8846
4834.7344 | 123.7701 | -61.441 | 62.1414 | 0.25047 | 0.016451 | 0.015336 | 0.01232 | 0.062384 | -0.0014013 | 0.079263 | -58.3603 | 62.1231 | -61.7569 | -61.647 | 54.5242 | 24.4812 | 8.2535 | 7.7683 | 62.1597 | -61.734 | -0.31586 | -0.01831 | 3.0807 | -0.20599 | -7.6172 | -0.29297 | 0.018311 | 3.3966 | 69.6945 | 69.2093 | 115.9653 | 123.5641 | 3.0807 | 123.6008 | 85.9222 | -0.29297 | 123.5641 | 3.0807 | 85.9222 | 115.9653 | 123.6008 | -123.8983 | -123.8754
4835.7188 | 123.7656 | -61.4044 | 62.1414 | -0.08522 | 0.013674 | 0.01555 | 0.013388 | 0.064948 | -0.00011953 | 0.078622 | -58.287 | 62.1964 | -61.7432 | -61.5692 | 54.6021 | 24.4949 | 8.4045 | 7.8232 | 62.1918 | -61.734 | -0.33875 | 0.054932 | 3.1174 | -0.1648 | -7.5394 | -0.32959 | 0.050354 | 3.4561 | 69.809 | 69.2276 | 116.0065 | 123.6008 | 3.1174 | 123.5962 | 85.8994 | -0.32959 | 123.6008 | 3.1174 | 85.8994 | 116.0065 | 123.5962 | -123.8846 | -123.8754
4836.7188 | 123.7564 | -61.4227 | 62.178 | -0.22255 | 0.017733 | 0.0095682 | 0.010824 | 0.064734 | -0.0014013 | 0.079049 | -58.342 | 62.2009 | -61.7386 | -61.6241 | 54.5563 | 24.408 | 8.519 | 7.7408 | 62.2192 | -61.7386 | -0.31586 | 0.022888 | 3.0807 | -0.20142 | -7.6218 | -0.31586 | 0.041198 | 3.3966 | 69.9417 | 69.1635 | 115.979 | 123.6237 | 3.0807 | 123.642 | 85.8307 | -0.31586 | 123.6237 | 3.0807 | 85.8307 | 115.979 | 123.642 | -123.9166 | -123.9166
4837.7188 | 123.7564 | -61.4365 | 62.1735 | -0.22255 | 0.015597 | 0.013841 | 0.014242 | 0.063452 | -0.0031103 | 0.080331 | -58.2962 | 62.1918 | -61.7569 | -61.5875 | 54.6021 | 24.4492 | 8.4045 | 7.8415 | 62.1689 | -61.7477 | -0.32044 | 0.01831 | 3.1403 | -0.15106 | -7.5714 | -0.31128 | -0.004578 | 3.4607 | 69.841 | 69.278 | 116.0385 | 123.6282 | 3.1403 | 123.6053 | 85.8856 | -0.31128 | 123.6282 | 3.1403 | 85.8856 | 116.0385 | 123.6053 | -123.9304 | -123.9212
4838.7188 | 123.7518 | -61.4365 | 62.1414 | -0.047073 | 0.016024 | 0.01085 | 0.015524 | 0.063025 | -0.0018285 | 0.080544 | -58.2825 | 62.2101 | -61.7523 | -61.5875 | 54.57 | 24.4629 | 8.3771 | 7.5943 | 62.1552 | -61.7615 | -0.31586 | 0.068665 | 3.154 | -0.15106 | -7.5714 | -0.32501 | 0.013733 | 3.4698 | 69.8135 | 69.0308 | 116.0065 | 123.6465 | 3.154 | 123.5916 | 85.8994 | -0.32501 | 123.6465 | 3.154 | 85.8994 | 116.0065 | 123.5916 | -123.8937 | -123.9029
4839.7188 | 123.6694 | -61.4365 | 62.1689 | 0.14366 | 0.019656 | 0.017472 | 0.01296 | 0.065802 | 0.0018031 | 0.080117 | -58.3832 | 62.1964 | -61.7706 | -61.6928 | 54.744 | 24.2569 | 8.107 | 8.1848 | 62.114 | -61.7889 | -0.33417 | 0.027466 | 3.0533 | -0.25635 | -7.4249 | -0.35248 | -0.054931 | 3.3875 | 69.5435 | 69.6213 | 116.1804 | 123.6328 | 3.0533 | 123.5504 | 85.6934 | -0.35248 | 123.6328 | 3.0533 | 85.6934 | 116.1804 | 123.5504 | -123.9395 | -123.9578
4840.7188 | 123.7564 | -61.4365 | 62.1552 | -0.08522 | 0.016451 | 0.014695 | 0.01531 | 0.064521 | -0.00076053 | 0.079263 | -58.2962 | 62.1826 | -61.7249 | -61.5921 | 54.6066 | 24.5132 | 8.4229 | 7.869 | 62.1872 | -61.7386 | -0.28839 | 0.027466 | 3.1403 | -0.15564 | -7.5485 | -0.30212 | 0.032044 | 3.4286 | 69.8593 | 69.3054 | 116.0431 | 123.6191 | 3.1403 | 123.6237 | 85.9497 | -0.30212 | 123.6191 | 3.1403 | 85.9497 | 116.0431 | 123.6237 | -123.88 | -123.8937
4841.7188 | 123.7518 | -61.409 | 62.1506 | -0.16914 | 0.016238 | 0.015763 | 0.014029 | 0.064093 | -0.0026831 | 0.079263 | -58.3466 | 62.2101 | -61.7111 | -61.6013 | 54.57 | 24.44 | 8.519 | 8.0704 | 62.1872 | -61.7386 | -0.30212 | 0.059509 | 3.0624 | -0.19226 | -7.5806 | -0.32959 | 0.036621 | 3.3646 | 69.928 | 69.4794 | 115.979 | 123.6191 | 3.0624 | 123.5962 | 85.849 | -0.32959 | 123.6191 | 3.0624 | 85.849 | 115.979 | 123.5962 | -123.8617 | -123.8892
4842.7188 | 123.7564 | -61.3953 | 62.1506 | -0.23018 | 0.017306 | 0.012559 | 0.014456 | 0.063239 | -0.0024695 | 0.079476 | -58.3054 | 62.2009 | -61.7386 | -61.6013 | 54.5883 | 24.4446 | 8.5007 | 7.9605 | 62.1964 | -61.7203 | -0.34332 | 0.050354 | 3.0899 | -0.20599 | -7.5623 | -0.32501 | 0.045776 | 3.4332 | 69.8959 | 69.3558 | 115.9836 | 123.5962 | 3.0899 | 123.5916 | 85.8398 | -0.32501 | 123.5962 | 3.0899 | 85.8398 | 115.9836 | 123.5916 | -123.8892 | -123.8708
4843.7188 | 123.7289 | -61.4182 | 62.1735 | -0.1844 | 0.014315 | 0.011704 | 0.010397 | 0.062384 | 0.0015893 | 0.079049 | -58.3649 | 62.1918 | -61.7386 | -61.6241 | 54.5746 | 24.4125 | 8.6243 | 8.0154 | 62.2238 | -61.7523 | -0.32043 | 0.01831 | 3.0533 | -0.20599 | -7.5989 | -0.33417 | 0.050354 | 3.3737 | 70.0424 | 69.4336 | 115.9927 | 123.6099 | 3.0533 | 123.642 | 85.8307 | -0.33417 | 123.6099 | 3.0533 | 85.8307 | 115.9927 | 123.642 | -123.912 | -123.9258
4844.7188 | 123.6786 | -61.4456 | 62.1506 | -0.054703 | 0.016451 | 0.014695 | 0.012747 | 0.062384 | -0.0028967 | 0.079476 | -58.287 | 62.1918 | -61.7432 | -61.6058 | 54.6204 | 24.472 | 8.5419 | 7.9285 | 62.1643 | -61.7615 | -0.29755 | 0.041198 | 3.1586 | -0.16022 | -7.5302 | -0.31586 | 0.013733 | 3.4561 | 69.9875 | 69.3741 | 116.066 | 123.6374 | 3.1586 | 123.6099 | 85.9177 | -0.31586 | 123.6374 | 3.1586 | 85.9177 | 116.066 | 123.6099 | -123.8937 | -123.912
4845.7188 | 123.7747 | -61.4227 | 62.1506 | -0.0089264 | 0.014315 | 0.013627 | 0.014669 | 0.065589 | -0.00097413 | 0.080331 | -58.2916 | 62.178 | -61.7752 | -61.6013 | 54.6158 | 24.3622 | 8.606 | 7.9651 | 62.2101 | -61.7569 | -0.35248 | 0.027466 | 3.1311 | -0.17853 | -7.5348 | -0.33417 | 0.059509 | 3.4836 | 70.0287 | 69.3878 | 116.0385 | 123.6008 | 3.1311 | 123.6328 | 85.7849 | -0.33417 | 123.6008 | 3.1311 | 85.7849 | 116.0385 | 123.6328 | -123.9258 | -123.9075
4846.7188 | 123.7473 | -61.4273 | 62.1323 | -0.069961 | 0.017519 | 0.014482 | 0.013388 | 0.064093 | -0.0024695 | 0.080544 | -58.3145 | 62.1872 | -61.7477 | -61.6058 | 54.657 | 24.5041 | 8.5831 | 7.9193 | 62.1689 | -61.7523 | -0.32044 | 0.054932 | 3.1128 | -0.17853 | -7.4753 | -0.32501 | 0.036621 | 3.4332 | 70.0104 | 69.3466 | 116.0843 | 123.6145 | 3.1128 | 123.5962 | 85.9314 | -0.32501 | 123.6145 | 3.1128 | 85.9314 | 116.0843 | 123.5962 | -123.88 | -123.8846
4847.7188 | 123.7564 | -61.3953 | 62.1506 | -0.1844 | 0.013674 | 0.012132 | 0.012106 | 0.061743 | -0.0018285 | 0.078408 | -58.3099 | 62.1964 | -61.7432 | -61.6013 | 54.6524 | 24.4995 | 8.6151 | 7.9605 | 62.2101 | -61.7249 | -0.3479 | 0.045776 | 3.0853 | -0.20599 | -7.4982 | -0.32959 | 0.059509 | 3.4332 | 70.0104 | 69.3558 | 116.0477 | 123.5916 | 3.0853 | 123.6053 | 85.8948 | -0.32959 | 123.5916 | 3.0853 | 85.8948 | 116.0477 | 123.6053 | -123.8937 | -123.8754
4848.7188 | 123.7656 | -61.4227 | 62.1277 | -0.15388 | 0.017519 | 0.015122 | 0.011892 | 0.063666 | -0.0024695 | 0.079476 | -58.287 | 62.1872 | -61.7432 | -61.5875 | 54.6478 | 24.5224 | 8.6792 | 8.075 | 62.178 | -61.7569 | -0.32044 | 0.059509 | 3.1357 | -0.1648 | -7.4799 | -0.33417 | 0.050354 | 3.4561 | 70.1019 | 69.4977 | 116.0706 | 123.6099 | 3.1357 | 123.6008 | 85.9451 | -0.33417 | 123.6099 | 3.1357 | 85.9451 | 116.0706 | 123.6008 | -123.8708 | -123.8846
4849.7188 | 123.7381 | -61.4456 | 62.1277 | 0.1284 | 0.018801 | 0.017899 | 0.012747 | 0.065161 | -0.0011877 | 0.079049 | -58.4885 | 62.146 | -61.7981 | -61.6379 | 54.5197 | 24.3942 | 8.6426 | 7.8323 | 62.2055 | -61.7661 | -0.35248 | 0.01831 | 2.9572 | -0.19226 | -7.608 | -0.32043 | 0.077819 | 3.3096 | 70.0882 | 69.278 | 115.9653 | 123.5916 | 2.9572 | 123.6511 | 85.8398 | -0.32043 | 123.5916 | 2.9572 | 85.8398 | 115.9653 | 123.6511 | -123.9258 | -123.8937
4850.7188 | 123.7793 | -61.4227 | 62.146 | -0.19966 | 0.015597 | 0.013627 | 0.012747 | 0.06153 | -0.00076053 | 0.078408 | -58.3145 | 62.2192 | -61.7661 | -61.5967 | 54.5975 | 24.4583 | 8.6609 | 7.9651 | 62.2101 | -61.7523 | -0.34332 | 0.073242 | 3.1082 | -0.17395 | -7.5485 | -0.32959 | 0.064087 | 3.4515 | 70.0836 | 69.3878 | 116.0202 | 123.642 | 3.1082 | 123.6328 | 85.881 | -0.32959 | 123.642 | 3.1082 | 85.881 | 116.0202 | 123.6328 | -123.912 | -123.8983
4851.7188 | 123.7564 | -61.4502 | 62.1506 | -0.2607 | 0.016878 | 0.014482 | 0.010611 | 0.06623 | -0.0026831 | 0.078622 | -58.3328 | 62.2147 | -61.734 | -61.6104 | 54.6158 | 24.4263 | 8.7204 | 8.0338 | 62.2147 | -61.7294 | -0.28381 | 0.064087 | 3.1174 | -0.16022 | -7.5348 | -0.27924 | 0.064087 | 3.4012 | 70.1706 | 69.4839 | 116.066 | 123.6649 | 3.1174 | 123.6649 | 85.8765 | -0.27924 | 123.6649 | 3.1174 | 85.8765 | 116.066 | 123.6649 | -123.8846 | -123.88
4852.7188 | 123.7473 | -61.4685 | 62.1552 | -0.19203 | 0.017306 | 0.012986 | 0.013601 | 0.063666 | -0.00033333 | 0.078408 | -58.2733 | 62.1964 | -61.7569 | -61.6013 | 54.5517 | 24.4583 | 8.638 | 7.9742 | 62.178 | -61.7477 | -0.28839 | 0.041199 | 3.1952 | -0.13275 | -7.6035 | -0.27924 | 0.022889 | 3.4836 | 70.1065 | 69.4427 | 116.0202 | 123.6649 | 3.1952 | 123.6465 | 85.9268 | -0.27924 | 123.6649 | 3.1952 | 85.9268 | 116.0202 | 123.6465 | -123.912 | -123.9029
4853.7188 | 123.761 | -61.441 | 62.1414 | -0.21492 | 0.013247 | 0.015977 | 0.015738 | 0.063666 | -0.00097413 | 0.080331 | -58.3099 | 62.1826 | -61.7615 | -61.6013 | 54.5975 | 24.5087 | 8.6746 | 8.0978 | 62.1872 | -61.7432 | -0.32043 | 0.041199 | 3.1311 | -0.16022 | -7.5439 | -0.30212 | 0.045777 | 3.4515 | 70.1157 | 69.5389 | 116.0385 | 123.6237 | 3.1311 | 123.6282 | 85.9497 | -0.30212 | 123.6237 | 3.1311 | 85.9497 | 116.0385 | 123.6282 | -123.9029 | -123.8846
4854.7188 | 123.793 | -61.4456 | 62.1689 | -0.23781 | 0.016451 | 0.016191 | 0.01232 | 0.064948 | -0.00097413 | 0.078622 | -58.2733 | 62.1872 | -61.734 | -61.5967 | 54.5929 | 24.4949 | 8.6792 | 8.0246 | 62.1826 | -61.7569 | -0.28839 | 0.018311 | 3.1723 | -0.15106 | -7.576 | -0.31128 | 0.013733 | 3.4607 | 70.1248 | 69.4702 | 116.0385 | 123.6328 | 3.1723 | 123.6282 | 85.9406 | -0.31128 | 123.6328 | 3.1723 | 85.9406 | 116.0385 | 123.6282 | -123.9029 | -123.9258
4855.7188 | 123.7381 | -61.4273 | 62.1643 | -0.1844 | 0.019015 | 0.014054 | 0.013388 | 0.063452 | -0.00097413 | 0.079049 | -58.3191 | 62.2101 | -61.7615 | -61.5921 | 54.5929 | 24.4904 | 8.7067 | 8.0246 | 62.1872 | -61.7477 | -0.33417 | 0.045776 | 3.1082 | -0.16479 | -7.5714 | -0.32044 | 0.022888 | 3.4424 | 70.134 | 69.4519 | 116.0202 | 123.6374 | 3.1082 | 123.6145 | 85.9177 | -0.32044 | 123.6374 | 3.1082 | 85.9177 | 116.0202 | 123.6145 | -123.9258 | -123.912
4856.7188 | 123.7564 | -61.4502 | 62.1643 | -0.2607 | 0.015169 | 0.015763 | 0.013601 | 0.064521 | -0.0014013 | 0.080331 | -58.3145 | 62.1826 | -61.7569 | -61.6013 | 54.57 | 24.4308 | 8.6517 | 8.0246 | 62.1872 | -61.7294 | -0.3067 | 0.01831 | 3.1357 | -0.15106 | -7.5943 | -0.27924 | 0.022888 | 3.4424 | 70.1019 | 69.4748 | 116.0202 | 123.6328 | 3.1357 | 123.6374 | 85.881 | -0.27924 | 123.6328 | 3.1357 | 85.881 | 116.0202 | 123.6374 | -123.9212 | -123.8937
4857.7188 | 123.7427 | -61.4548 | 62.146 | -0.25307 | 0.014956 | 0.014268 | 0.01232 | 0.063025 | -0.0014013 | 0.080544 | -58.3145 | 62.1918 | -61.7386 | -61.6104 | 54.6112 | 24.4629 | 8.6655 | 7.9697 | 62.2101 | -61.7569 | -0.28381 | 0.045776 | 3.1403 | -0.15564 | -7.5348 | -0.30212 | 0.064087 | 3.4241 | 70.1202 | 69.4244 | 116.066 | 123.6465 | 3.1403 | 123.6649 | 85.9177 | -0.30212 | 123.6465 | 3.1403 | 85.9177 | 116.066 | 123.6649 | -123.8846 | -123.9029
4858.7188 | 123.7335 | -61.4273 | 62.1872 | -0.1844 | 0.017092 | 0.012986 | 0.011679 | 0.062598 | -0.00076053 | 0.07969 | -58.3237 | 62.2375 | -61.7432 | -61.6104 | 54.5563 | 24.4034 | 8.6792 | 8.02 | 62.2375 | -61.7249 | -0.31586 | 0.050354 | 3.1036 | -0.18311 | -7.6309 | -0.29755 | 0.050354 | 3.4195 | 70.1065 | 69.4473 | 115.9836 | 123.6649 | 3.1036 | 123.6649 | 85.8307 | -0.29755 | 123.6649 | 3.1036 | 85.8307 | 115.9836 | 123.6649 | -123.9304 | -123.912
4859.7188 | 123.6923 | -61.4594 | 62.1231 | 0.18944 | 0.01581 | 0.014695 | 0.012533 | 0.063666 | -0.00033333 | 0.079904 | -58.3374 | 62.178 | -61.7661 | -61.6928 | 54.4785 | 24.3622 | 8.6517 | 7.8964 | 62.2009 | -61.7523 | -0.3067 | 0.054932 | 3.1219 | -0.23346 | -7.6447 | -0.29297 | 0.07782 | 3.4287 | 70.1111 | 69.3558 | 115.9378 | 123.6374 | 3.1219 | 123.6603 | 85.8215 | -0.29297 | 123.6374 | 3.1219 | 85.8215 | 115.9378 | 123.6603 | -123.8892 | -123.8754
4860.7188 | 123.761 | -61.4456 | 62.1689 | -0.131 | 0.016024 | 0.0097818 | 0.014456 | 0.062598 | -0.0026831 | 0.078408 | -58.2733 | 62.2101 | -61.7523 | -61.6013 | 54.6112 | 24.3759 | 8.6838 | 8.0658 | 62.2147 | -61.7477 | -0.3067 | 0.041199 | 3.1723 | -0.15564 | -7.5577 | -0.30212 | 0.045777 | 3.479 | 70.1294 | 69.5114 | 116.0568 | 123.6557 | 3.1723 | 123.6603 | 85.8215 | -0.30212 | 123.6557 | 3.1723 | 85.8215 | 116.0568 | 123.6603 | -123.9212 | -123.9166
4861.7188 | 123.7656 | -61.4456 | 62.1368 | -0.16914 | 0.01816 | 0.013413 | 0.010611 | 0.061743 | 9.4068e-05 | 0.079263 | -58.3099 | 62.178 | -61.7615 | -61.5967 | 54.57 | 24.408 | 8.7112 | 8.0978 | 62.2009 | -61.7661 | -0.31586 | 0.041199 | 3.1357 | -0.15106 | -7.5668 | -0.32043 | 0.064087 | 3.4515 | 70.1569 | 69.5435 | 116.0156 | 123.6237 | 3.1357 | 123.6465 | 85.8536 | -0.32043 | 123.6237 | 3.1357 | 85.8536 | 116.0156 | 123.6465 | -123.8983 | -123.9029
4862.7188 | 123.7473 | -61.4273 | 62.1597 | -0.23781 | 0.011751 | 0.012773 | 0.012533 | 0.063025 | -0.0022559 | 0.076272 | -58.3282 | 62.1826 | -61.7569 | -61.615 | 54.5471 | 24.2706 | 8.7753 | 8.0887 | 62.2009 | -61.7065 | -0.32959 | 0.022888 | 3.0991 | -0.18768 | -7.6126 | -0.27924 | 0.041199 | 3.4287 | 70.2026 | 69.516 | 115.9744 | 123.6099 | 3.0991 | 123.6282 | 85.6979 | -0.27924 | 123.6099 | 3.0991 | 85.6979 | 115.9744 | 123.6282 | -123.9166 | -123.8663
4863.7188 | 123.7518 | -61.4685 | 62.1552 | -0.13863 | 0.017947 | 0.011918 | 0.012533 | 0.062171 | -0.0014013 | 0.078408 | -58.2825 | 62.2009 | -61.7752 | -61.5738 | 54.5609 | 24.2523 | 8.7158 | 8.1482 | 62.2009 | -61.7386 | -0.3067 | 0.045777 | 3.186 | -0.10529 | -7.5943 | -0.27008 | 0.045777 | 3.4927 | 70.1843 | 69.6167 | 116.0294 | 123.6694 | 3.186 | 123.6694 | 85.7208 | -0.27008 | 123.6694 | 3.186 | 85.7208 | 116.0294 | 123.6694 | -123.9304 | -123.8937
4864.7188 | 123.7106 | -61.4731 | 62.1552 | 0.029221 | 0.018801 | 0.011491 | 0.013601 | 0.063666 | -0.00054693 | 0.080117 | -58.3237 | 62.1918 | -61.7523 | -61.6653 | 54.4785 | 24.2661 | 8.7204 | 8.0475 | 62.1964 | -61.7615 | -0.27924 | 0.036621 | 3.1494 | -0.19226 | -7.6767 | -0.28839 | 0.041199 | 3.4286 | 70.1935 | 69.5206 | 115.9515 | 123.6649 | 3.1494 | 123.6694 | 85.7391 | -0.28839 | 123.6649 | 3.1494 | 85.7391 | 115.9515 | 123.6694 | -123.9075 | -123.9166
4865.7188 | 123.7198 | -61.4365 | 62.1552 | 1.227 | 0.017092 | 0.011277 | 0.0082608 | 0.062812 | -0.00097413 | 0.07969 | -58.3008 | 62.1643 | -61.7523 | -61.6287 | 54.57 | 24.4583 | 8.7296 | 8.075 | 62.2055 | -61.7569 | -0.31586 | 0.009156 | 3.1357 | -0.19226 | -7.5851 | -0.32044 | 0.050354 | 3.4515 | 70.166 | 69.5114 | 116.0065 | 123.6008 | 3.1357 | 123.642 | 85.8948 | -0.32044 | 123.6008 | 3.1357 | 85.8948 | 116.0065 | 123.642 | -123.9075 | -123.912
4866.7188 | 123.7473 | -61.441 | 62.1552 | -0.16914 | 0.017947 | 0.014909 | 0.012533 | 0.062598 | -0.0016149 | 0.078195 | -58.342 | 62.1826 | -61.7523 | -61.6196 | 54.5792 | 24.4308 | 8.6792 | 7.9468 | 62.2055 | -61.7477 | -0.31128 | 0.027466 | 3.0991 | -0.17853 | -7.576 | -0.3067 | 0.050354 | 3.4103 | 70.1202 | 69.3878 | 116.0202 | 123.6237 | 3.0991 | 123.6465 | 85.8719 | -0.3067 | 123.6237 | 3.0991 | 85.8719 | 116.0202 | 123.6465 | -123.9075 | -123.9029
4867.7188 | 123.7152 | -61.4182 | 62.178 | -0.20729 | 0.01581 | 0.012986 | 0.012106 | 0.061103 | -0.0014013 | 0.079263 | -58.3466 | 62.1826 | -61.7432 | -61.647 | 54.5425 | 24.3942 | 8.7112 | 7.9788 | 62.2055 | -61.7203 | -0.32501 | 0.004577 | 3.0716 | -0.22888 | -7.6355 | -0.30212 | 0.027465 | 3.3966 | 70.1294 | 69.397 | 115.9607 | 123.6008 | 3.0716 | 123.6237 | 85.8124 | -0.30212 | 123.6008 | 3.0716 | 85.8124 | 115.9607 | 123.6237 | -123.9212 | -123.8983
4868.7188 | 123.7152 | -61.4456 | 62.1826 | -0.33699 | 0.016238 | 0.015336 | 0.011679 | 0.061957 | -0.0028967 | 0.080117 | -58.5251 | 62.178 | -61.7615 | -61.6837 | 54.5334 | 24.5087 | 8.7296 | 8.0154 | 62.2055 | -61.734 | -0.31586 | -0.004577 | 2.9205 | -0.23804 | -7.6492 | -0.28839 | 0.022888 | 3.2364 | 70.1752 | 69.4611 | 115.979 | 123.6237 | 2.9205 | 123.6511 | 85.9543 | -0.28839 | 123.6237 | 2.9205 | 85.9543 | 115.979 | 123.6511 | -123.9441 | -123.9166
4869.7188 | 123.7244 | -61.4502 | 62.1094 | 0.19707 | 0.017306 | 0.012773 | 0.01296 | 0.063025 | 0.00030767 | 0.077126 | -58.3603 | 62.1689 | -61.7386 | -61.6699 | 54.5013 | 24.3622 | 8.6426 | 8.0154 | 62.1368 | -61.7477 | -0.28839 | 0.059509 | 3.0899 | -0.21973 | -7.608 | -0.29755 | 0.027466 | 3.3783 | 70.0928 | 69.4656 | 115.9515 | 123.6191 | 3.0899 | 123.587 | 85.8124 | -0.29755 | 123.6191 | 3.0899 | 85.8124 | 115.9515 | 123.587 | -123.848 | -123.8571
4870.7188 | 123.7198 | -61.4273 | 62.1689 | -0.24544 | 0.015597 | 0.0097818 | 0.0095424 | 0.060889 | -0.00011953 | 0.079904 | -58.3649 | 62.1506 | -61.7477 | -61.6425 | 54.5425 | 24.3942 | 8.7387 | 7.988 | 62.2101 | -61.7477 | -0.32044 | -0.01831 | 3.0624 | -0.21515 | -7.6263 | -0.32044 | 0.041199 | 3.3829 | 70.166 | 69.4153 | 115.9698 | 123.5779 | 3.0624 | 123.6374 | 85.8215 | -0.32044 | 123.5779 | 3.0624 | 85.8215 | 115.9698 | 123.6374 | -123.9166 | -123.9166
4871.7188 | 123.6877 | -61.4365 | 62.1643 | -0.21492 | 0.013247 | 0.011064 | 0.011038 | 0.060248 | -0.0011877 | 0.079049 | -58.3557 | 62.1552 | -61.734 | -61.6379 | 54.5609 | 24.3027 | 8.7204 | 8.0292 | 62.1872 | -61.734 | -0.29755 | -0.009156 | 3.0807 | -0.20142 | -7.6035 | -0.29755 | 0.022888 | 3.3783 | 70.1569 | 69.4656 | 115.9973 | 123.5916 | 3.0807 | 123.6237 | 85.7391 | -0.29755 | 123.5916 | 3.0807 | 85.7391 | 115.9973 | 123.6237 | -123.8983 | -123.8983
4872.7344 | 123.7198 | -61.4731 | 62.1231 | -2.9386 | 0.016238 | 0.017259 | 0.014669 | 0.06388 | -0.0014013 | 0.079263 | -58.429 | 62.1826 | -61.7523 | -61.6882 | 54.4876 | 24.2706 | 8.6517 | 7.988 | 62.1689 | -61.7615 | -0.27924 | 0.059509 | 3.0441 | -0.21515 | -7.6355 | -0.28839 | 0.045776 | 3.3234 | 70.1248 | 69.4611 | 115.9607 | 123.6557 | 3.0441 | 123.642 | 85.7437 | -0.28839 | 123.6557 | 3.0441 | 85.7437 | 115.9607 | 123.642 | -123.8754 | -123.8846
4873.7188 | 123.7015 | -61.4273 | 62.1506 | 0.013962 | 0.014529 | 0.010209 | 0.0097562 | 0.06153 | -0.00033333 | 0.076699 | -58.3466 | 62.1643 | -61.734 | -61.6333 | 54.5151 | 24.3576 | 8.7753 | 8.0978 | 62.1918 | -61.734 | -0.3067 | 0.013733 | 3.0807 | -0.20599 | -7.6355 | -0.3067 | 0.041198 | 3.3875 | 70.2026 | 69.5251 | 115.9424 | 123.5916 | 3.0807 | 123.6191 | 85.7849 | -0.3067 | 123.5916 | 3.0807 | 85.7849 | 115.9424 | 123.6191 | -123.8846 | -123.8846
4874.7188 | 123.7473 | -61.3953 | 62.1826 | -0.1844 | 0.014529 | 0.014054 | 0.011038 | 0.060462 | -0.0014013 | 0.077981 | -58.3511 | 62.1964 | -61.734 | -61.5967 | 54.538 | 24.3118 | 8.8028 | 8.1345 | 62.2009 | -61.7294 | -0.33875 | 0.013733 | 3.0441 | -0.20142 | -7.6447 | -0.33417 | 0.018311 | 3.3829 | 70.1981 | 69.5297 | 115.9332 | 123.5916 | 3.0441 | 123.5962 | 85.7071 | -0.33417 | 123.5916 | 3.0441 | 85.7071 | 115.9332 | 123.5962 | -123.9166 | -123.912
4875.7188 | 123.7244 | -61.441 | 62.1689 | -0.26833 | 0.01346 | 0.014695 | 0.0093288 | 0.059394 | -0.0016149 | 0.078622 | -58.2825 | 62.114 | -61.7157 | -61.5829 | 54.5975 | 24.3713 | 8.8028 | 8.2489 | 62.178 | -61.7157 | -0.27466 | -0.054931 | 3.1586 | -0.14191 | -7.5714 | -0.27466 | 0.009156 | 3.4332 | 70.2438 | 69.6899 | 116.0385 | 123.555 | 3.1586 | 123.6191 | 85.8124 | -0.27466 | 123.555 | 3.1586 | 85.8124 | 116.0385 | 123.6191 | -123.8846 | -123.8846
4876.7188 | 123.7701 | -61.3861 | 62.1689 | -0.2607 | 0.010256 | 0.012559 | 0.0091152 | 0.057898 | -0.0028967 | 0.078408 | -58.2504 | 62.1002 | -61.7249 | -61.5829 | 54.6341 | 24.353 | 8.7296 | 8.2489 | 62.1552 | -61.6928 | -0.33875 | -0.068664 | 3.1357 | -0.19684 | -7.5348 | -0.3067 | -0.013733 | 3.4744 | 70.1157 | 69.635 | 116.0202 | 123.4863 | 3.1357 | 123.5413 | 85.7391 | -0.3067 | 123.4863 | 3.1357 | 85.7391 | 116.0202 | 123.5413 | -123.8937 | -123.8617
4877.7344 | 123.6832 | -61.4639 | 62.1323 | 0.082626 | 0.016451 | 0.011704 | 0.018087 | 0.062384 | 0.00052127 | 0.078622 | -58.3191 | 62.1689 | -61.7569 | -61.6882 | 54.4922 | 24.2477 | 8.757 | 8.1528 | 62.1552 | -61.8073 | -0.29297 | 0.036621 | 3.1448 | -0.2243 | -7.6401 | -0.34332 | 0.022888 | 3.4378 | 70.2209 | 69.6167 | 115.9561 | 123.6328 | 3.1448 | 123.6191 | 85.7117 | -0.34332 | 123.6328 | 3.1448 | 85.7117 | 115.9561 | 123.6191 | -123.8892 | -123.9395
4878.7188 | 123.8159 | -61.3678 | 62.1552 | -0.32173 | 0.010256 | 0.0078592 | 0.0071926 | 0.061103 | -0.0014013 | 0.080758 | -58.255 | 62.0956 | -61.7203 | -61.5326 | 54.6295 | 24.4354 | 8.6426 | 8.2947 | 62.1506 | -61.6791 | -0.35248 | -0.059509 | 3.1128 | -0.16479 | -7.5256 | -0.31128 | -0.004577 | 3.4653 | 70.0104 | 69.6625 | 115.9973 | 123.4634 | 3.1128 | 123.5184 | 85.8032 | -0.31128 | 123.4634 | 3.1128 | 85.8032 | 115.9973 | 123.5184 | -123.8754 | -123.8342
4879.7344 | 123.6786 | -61.4365 | 62.1368 | -0.08522 | 0.015169 | 0.012559 | 0.015097 | 0.060034 | -0.0020421 | 0.079049 | -58.2413 | 62.1826 | -61.7294 | -61.5784 | 54.57 | 24.4308 | 8.7936 | 8.2535 | 62.1506 | -61.7615 | -0.29297 | 0.045776 | 3.1952 | -0.14191 | -7.5668 | -0.32501 | 0.013733 | 3.4882 | 70.2301 | 69.6899 | 116.0065 | 123.6191 | 3.1952 | 123.587 | 85.8673 | -0.32501 | 123.6191 | 3.1952 | 85.8673 | 116.0065 | 123.587 | -123.8663 | -123.8983
4880.7188 | 123.8388 | -61.3907 | 62.1552 | -0.23018 | 0.01282 | 0.010636 | 0.0089016 | 0.060889 | -0.0016149 | 0.079049 | -58.2733 | 62.0728 | -61.734 | -61.5509 | 54.6341 | 24.4263 | 8.7433 | 8.3771 | 62.1414 | -61.6699 | -0.34332 | -0.082397 | 3.1174 | -0.16022 | -7.5211 | -0.27924 | -0.013733 | 3.4607 | 70.134 | 69.7678 | 116.0248 | 123.4634 | 3.1174 | 123.5321 | 85.817 | -0.27924 | 123.4634 | 3.1174 | 85.817 | 116.0248 | 123.5321 | -123.8892 | -123.8251
4881.7188 | 123.7885 | -61.3724 | 62.1323 | -0.09285 | 0.013247 | 0.0093546 | 0.0091152 | 0.059607 | -0.0033239 | 0.080331 | -58.2733 | 62.1002 | -61.7111 | -61.5326 | 54.6295 | 24.5041 | 8.7158 | 8.3313 | 62.1048 | -61.6882 | -0.33875 | -0.032043 | 3.0991 | -0.16022 | -7.5027 | -0.31586 | -0.027466 | 3.4378 | 70.0882 | 69.7037 | 116.0019 | 123.4726 | 3.0991 | 123.4772 | 85.8765 | -0.31586 | 123.4726 | 3.0991 | 85.8765 | 116.0019 | 123.4772 | -123.8434 | -123.8205
4882.7344 | 123.7061 | -61.4548 | 62.1552 | 0.074997 | 0.014529 | 0.011491 | 0.017019 | 0.061957 | -0.00054693 | 0.079904 | -58.342 | 62.1414 | -61.7706 | -61.6653 | 54.5013 | 24.4034 | 8.7982 | 8.2031 | 62.1323 | -61.7523 | -0.31586 | -0.013733 | 3.1128 | -0.21057 | -7.6538 | -0.29755 | -0.022888 | 3.4286 | 70.253 | 69.6579 | 115.9561 | 123.5962 | 3.1128 | 123.587 | 85.8582 | -0.29755 | 123.5962 | 3.1128 | 85.8582 | 115.9561 | 123.587 | -123.9258 | -123.9075
4883.7188 | 123.848 | -61.377 | 62.1002 | -0.19203 | 0.011965 | 0.01085 | 0.0014248 | 0.060889 | 0.0013757 | 0.079049 | -58.2596 | 62.0636 | -61.6974 | -61.5967 | 54.7623 | 24.6506 | 8.6105 | 8.3725 | 62.1323 | -61.6974 | -0.32043 | -0.036621 | 3.1174 | -0.21973 | -7.338 | -0.32043 | 0.032043 | 3.4378 | 69.9875 | 69.7495 | 116.1392 | 123.4406 | 3.1174 | 123.5092 | 86.0275 | -0.32043 | 123.4406 | 3.1174 | 86.0275 | 116.1392 | 123.5092 | -123.7976 | -123.7976
4884.7188 | 123.7518 | -61.441 | 62.1506 | -0.21492 | 0.019228 | 0.011704 | 0.014242 | 0.059821 | -0.0014013 | 0.079476 | -58.3237 | 62.1506 | -61.702 | -61.6196 | 54.5471 | 24.4537 | 8.8989 | 8.2123 | 62.1689 | -61.734 | -0.26093 | 0 | 3.1174 | -0.17853 | -7.6035 | -0.29297 | 0.01831 | 3.3783 | 70.34 | 69.6533 | 115.9882 | 123.5916 | 3.1174 | 123.6099 | 85.8948 | -0.29297 | 123.5916 | 3.1174 | 85.8948 | 115.9882 | 123.6099 | -123.8525 | -123.8846
4885.7188 | 123.8617 | -61.3861 | 62.1002 | -0.12337 | 0.013888 | 0.0089274 | 0.0074062 | 0.061316 | -0.00097413 | 0.077554 | -58.2596 | 62.0728 | -61.702 | -61.5143 | 54.6707 | 24.5636 | 8.6929 | 8.3771 | 62.1185 | -61.6608 | -0.31586 | -0.027466 | 3.1265 | -0.12817 | -7.4295 | -0.27466 | 0.01831 | 3.4424 | 70.079 | 69.7632 | 116.0568 | 123.4589 | 3.1265 | 123.5046 | 85.9497 | -0.27466 | 123.4589 | 3.1265 | 85.9497 | 116.0568 | 123.5046 | -123.8022 | -123.761
4886.7188 | 123.8525 | -61.3907 | 62.114 | -0.16151 | 0.012392 | 0.007432 | 0.010611 | 0.057471 | -0.00033333 | 0.077554 | -58.2687 | 62.059 | -61.7111 | -61.5326 | 54.6524 | 24.5911 | 8.7204 | 8.3633 | 62.1002 | -61.6699 | -0.32043 | -0.054932 | 3.1219 | -0.14191 | -7.4615 | -0.27924 | -0.013733 | 3.4424 | 70.1111 | 69.754 | 116.0431 | 123.4497 | 3.1219 | 123.4909 | 85.9818 | -0.27924 | 123.4497 | 3.1219 | 85.9818 | 116.0431 | 123.4909 | -123.8251 | -123.7839
4887.7188 | 123.8159 | -61.4044 | 62.1185 | -0.16914 | 0.012392 | 0.0085 | 0.0091152 | 0.060462 | -0.00011953 | 0.077767 | -58.255 | 62.0865 | -61.7157 | -61.4868 | 54.6341 | 24.5361 | 8.7204 | 8.3359 | 62.1048 | -61.6745 | -0.31128 | -0.032043 | 3.1494 | -0.082397 | -7.4844 | -0.27008 | -0.013733 | 3.4607 | 70.1248 | 69.7403 | 116.0385 | 123.4909 | 3.1494 | 123.5092 | 85.9406 | -0.27008 | 123.4909 | 3.1494 | 85.9406 | 116.0385 | 123.5092 | -123.8342 | -123.793
4888.7188 | 123.9075 | -61.3861 | 62.0911 | -0.20729 | 0.013674 | 0.0082864 | 0.011038 | 0.057685 | -0.0026831 | 0.078195 | -58.2367 | 62.0407 | -61.7203 | -61.5189 | 54.5288 | 24.8108 | 9.0225 | 7.988 | 62.178 | -61.6653 | -0.33417 | -0.050354 | 3.1494 | -0.13275 | -7.5623 | -0.27924 | 0.086976 | 3.4836 | 70.4086 | 69.3741 | 115.9149 | 123.4268 | 3.1494 | 123.5641 | 86.1969 | -0.27924 | 123.4268 | 3.1494 | 86.1969 | 115.9149 | 123.5641 | -123.8113 | -123.7564
4889.7188 | 123.7381 | -61.4365 | 62.1689 | -0.21492 | 0.014101 | 0.011704 | 0.017019 | 0.060889 | -0.0039649 | 0.077767 | -58.2962 | 62.1689 | -61.7432 | -61.6058 | 54.5334 | 24.3851 | 8.8257 | 8.1299 | 62.1735 | -61.7294 | -0.3067 | 0 | 3.1403 | -0.16937 | -7.6355 | -0.29297 | 0.004578 | 3.447 | 70.2621 | 69.5663 | 115.9698 | 123.6053 | 3.1403 | 123.6099 | 85.8215 | -0.29297 | 123.6053 | 3.1403 | 85.8215 | 115.9698 | 123.6099 | -123.912 | -123.8983
4890.7188 | 123.8754 | -61.377 | 62.1414 | -0.12337 | 0.011751 | 0.0099954 | 0.0093288 | 0.05918 | -0.00097413 | 0.080972 | -58.2642 | 62.0728 | -61.7111 | -61.5005 | 54.6295 | 24.5682 | 8.6517 | 8.3359 | 62.1185 | -61.6653 | -0.33417 | -0.068664 | 3.1128 | -0.1236 | -7.5119 | -0.28839 | -0.022888 | 3.447 | 70.0287 | 69.7128 | 116.0065 | 123.4497 | 3.1128 | 123.4955 | 85.9451 | -0.28839 | 123.4497 | 3.1128 | 85.9451 | 116.0065 | 123.4955 | -123.8525 | -123.8068
4891.7188 | 123.8663 | -61.377 | 62.1094 | -0.13863 | 0.01346 | 0.012559 | 0.01232 | 0.059394 | -0.00033333 | 0.079263 | -58.2687 | 62.059 | -61.7203 | -61.5189 | 54.6478 | 24.646 | 8.6517 | 8.3038 | 62.0911 | -61.6745 | -0.34332 | -0.050354 | 3.1082 | -0.14191 | -7.4615 | -0.29755 | -0.018311 | 3.4515 | 70.0287 | 69.6808 | 116.0248 | 123.436 | 3.1082 | 123.468 | 86.0229 | -0.29755 | 123.436 | 3.1082 | 86.0229 | 116.0248 | 123.468 | -123.8297 | -123.7839
4892.7188 | 123.8251 | -61.377 | 62.1094 | -0.16151 | 0.014315 | 0.0061502 | 0.0082608 | 0.057898 | -0.0011877 | 0.079263 | -58.2733 | 62.0728 | -61.7203 | -61.5326 | 54.5975 | 24.5728 | 8.638 | 8.3221 | 62.0956 | -61.6791 | -0.34332 | -0.036621 | 3.1036 | -0.15564 | -7.5119 | -0.30212 | -0.013733 | 3.447 | 70.015 | 69.6991 | 115.9744 | 123.4497 | 3.1036 | 123.4726 | 85.9497 | -0.30212 | 123.4497 | 3.1036 | 85.9497 | 115.9744 | 123.4726 | -123.8297 | -123.7885
4893.7188 | 123.8525 | -61.3815 | 62.1368 | -0.12337 | 0.011751 | 0.011064 | 0.0095424 | 0.058753 | -0.0018285 | 0.076272 | -58.2687 | 62.0636 | -61.7294 | -61.5143 | 54.6249 | 24.5316 | 8.606 | 8.2901 | 62.1231 | -61.6791 | -0.3479 | -0.073242 | 3.1128 | -0.13275 | -7.5119 | -0.29755 | -0.013733 | 3.4607 | 69.9875 | 69.6716 | 116.0065 | 123.4451 | 3.1128 | 123.5046 | 85.9131 | -0.29755 | 123.4451 | 3.1128 | 85.9131 | 116.0065 | 123.5046 | -123.8663 | -123.8159
4894.7344 | 123.7335 | -61.4365 | 62.1597 | -0.19203 | 0.015169 | 0.0048684 | 0.017019 | 0.057685 | 0.00030767 | 0.075845 | -58.287 | 62.1918 | -61.7249 | -61.5967 | 54.5654 | 24.5178 | 8.7753 | 8.1665 | 62.146 | -61.7432 | -0.28839 | 0.032043 | 3.1494 | -0.16022 | -7.5943 | -0.3067 | -0.013733 | 3.4378 | 70.2118 | 69.603 | 116.0019 | 123.6282 | 3.1494 | 123.5825 | 85.9543 | -0.3067 | 123.6282 | 3.1494 | 85.9543 | 116.0019 | 123.5825 | -123.8846 | -123.9029
4895.7188 | 123.8251 | -61.3907 | 62.146 | -0.1844 | 0.013674 | 0.0097818 | 0.0091152 | 0.058539 | -0.00054693 | 0.077981 | -58.2733 | 62.0636 | -61.734 | -61.5005 | 54.6799 | 24.5682 | 8.6472 | 8.345 | 62.1231 | -61.6562 | -0.34332 | -0.082397 | 3.1174 | -0.10986 | -7.4661 | -0.2655 | -0.022888 | 3.4607 | 70.0378 | 69.7357 | 116.0706 | 123.4543 | 3.1174 | 123.5138 | 85.9589 | -0.2655 | 123.4543 | 3.1174 | 85.9589 | 116.0706 | 123.5138 | -123.88 | -123.8022
4896.7188 | 123.8709 | -61.3953 | 62.1231 | -0.15388 | 0.012606 | 0.01085 | 0.010611 | 0.060034 | -0.0011877 | 0.077554 | -58.2596 | 62.0682 | -61.7203 | -61.496 | 54.657 | 24.6368 | 8.606 | 8.2626 | 62.1094 | -61.6516 | -0.32501 | -0.054932 | 3.1357 | -0.10071 | -7.4661 | -0.25635 | -0.013733 | 3.4607 | 70.0012 | 69.6579 | 116.0522 | 123.4634 | 3.1357 | 123.5046 | 86.0321 | -0.25635 | 123.4634 | 3.1357 | 86.0321 | 116.0522 | 123.5046 | -123.8434 | -123.7747
4897.7188 | 123.8663 | -61.4044 | 62.114 | -0.08522 | 0.012392 | 0.0099954 | 0.0065518 | 0.059394 | -0.0022559 | 0.07969 | -58.2733 | 62.059 | -61.7386 | -61.5189 | 54.6387 | 24.6231 | 8.638 | 8.2764 | 62.0865 | -61.6653 | -0.33417 | -0.054932 | 3.1311 | -0.11444 | -7.4753 | -0.26093 | -0.027466 | 3.4653 | 70.0424 | 69.6808 | 116.0431 | 123.4634 | 3.1311 | 123.4909 | 86.0275 | -0.26093 | 123.4634 | 3.1311 | 86.0275 | 116.0431 | 123.4909 | -123.8525 | -123.7793
4898.7188 | 123.8068 | -61.3861 | 62.1368 | -0.077591 | 0.013247 | 0.0095682 | 0.0091152 | 0.057898 | -0.00097413 | 0.078622 | -58.3237 | 62.0499 | -61.7386 | -61.5326 | 54.6021 | 24.6277 | 8.6746 | 8.2809 | 62.1185 | -61.6699 | -0.35248 | -0.086975 | 3.0624 | -0.14648 | -7.5348 | -0.28381 | -0.018311 | 3.4149 | 70.0607 | 69.6671 | 115.9882 | 123.436 | 3.0624 | 123.5046 | 86.0138 | -0.28381 | 123.436 | 3.0624 | 86.0138 | 115.9882 | 123.5046 | -123.8754 | -123.8068
4899.7188 | 123.8434 | -61.4182 | 62.1414 | -0.08522 | 0.011751 | 0.0097818 | 0.010183 | 0.057044 | -0.0016149 | 0.077767 | -58.2825 | 62.0407 | -61.7386 | -61.5417 | 54.6524 | 24.614 | 8.6792 | 8.3313 | 62.0728 | -61.6882 | -0.32043 | -0.10071 | 3.1357 | -0.1236 | -7.489 | -0.27008 | -0.068664 | 3.4561 | 70.0974 | 69.7495 | 116.0706 | 123.4589 | 3.1357 | 123.4909 | 86.0321 | -0.27008 | 123.4589 | 3.1357 | 86.0321 | 116.0706 | 123.4909 | -123.88 | -123.8297
4900.7188 | 123.8022 | -61.3907 | 62.1368 | -0.077591 | 0.011751 | 0.0082864 | 0.0091152 | 0.058325 | -0.00011953 | 0.078195 | -58.3191 | 62.0544 | -61.7249 | -61.5417 | 54.6433 | 24.7055 | 8.6838 | 8.313 | 62.0911 | -61.6974 | -0.33417 | -0.082398 | 3.0716 | -0.15106 | -7.4936 | -0.3067 | -0.045777 | 3.4058 | 70.0745 | 69.7037 | 116.0339 | 123.4451 | 3.0716 | 123.4818 | 86.0962 | -0.3067 | 123.4451 | 3.0716 | 86.0962 | 116.0339 | 123.4818 | -123.8617 | -123.8342
4901.7188 | 123.8342 | -61.3861 | 62.1368 | -0.08522 | 0.013247 | 0.0087138 | 0.008688 | 0.057257 | 9.4068e-05 | 0.077554 | -58.2504 | 62.0636 | -61.7615 | -61.5097 | 54.6387 | 24.6506 | 8.6746 | 8.3725 | 62.0911 | -61.6928 | -0.37537 | -0.073242 | 3.1357 | -0.1236 | -7.4982 | -0.3067 | -0.045777 | 3.511 | 70.0607 | 69.7586 | 116.0248 | 123.4497 | 3.1357 | 123.4772 | 86.0367 | -0.3067 | 123.4497 | 3.1357 | 86.0367 | 116.0248 | 123.4772 | -123.8983 | -123.8297
4902.7188 | 123.8571 | -61.4044 | 62.146 | -0.10811 | 0.013247 | 0.010423 | 0.008688 | 0.058539 | 0.0024439 | 0.076699 | -58.2687 | 62.059 | -61.7569 | -61.5372 | 54.657 | 24.6826 | 8.6838 | 8.3725 | 62.0819 | -61.6791 | -0.35248 | -0.086975 | 3.1357 | -0.13275 | -7.489 | -0.27466 | -0.064087 | 3.4882 | 70.0882 | 69.7769 | 116.0614 | 123.4634 | 3.1357 | 123.4863 | 86.087 | -0.27466 | 123.4634 | 3.1357 | 86.087 | 116.0614 | 123.4863 | -123.9029 | -123.8251
4903.7188 | 123.8388 | -61.3815 | 62.1231 | -0.077591 | 0.013033 | 0.011918 | 0.0071926 | 0.058753 | -0.00033333 | 0.081399 | -58.2458 | 62.0499 | -61.734 | -61.528 | 54.657 | 24.6552 | 8.67 | 8.3817 | 62.0911 | -61.6974 | -0.35248 | -0.073242 | 3.1357 | -0.14648 | -7.4661 | -0.31586 | -0.032044 | 3.4882 | 70.0516 | 69.7632 | 116.0385 | 123.4314 | 3.1357 | 123.4726 | 86.0367 | -0.31586 | 123.4314 | 3.1357 | 86.0367 | 116.0385 | 123.4726 | -123.8571 | -123.8205
4904.7188 | 123.6603 | -61.4365 | 62.1964 | -0.22255 | 0.016665 | 0.0070048 | 0.013815 | 0.058325 | -0.0024695 | 0.076272 | -58.287 | 62.114 | -61.7477 | -61.615 | 54.5746 | 24.6002 | 8.8669 | 8.2764 | 62.1414 | -61.7157 | -0.31128 | -0.082397 | 3.1494 | -0.17853 | -7.6218 | -0.27924 | -0.054932 | 3.4607 | 70.3033 | 69.7128 | 116.011 | 123.5504 | 3.1494 | 123.5779 | 86.0367 | -0.27924 | 123.5504 | 3.1494 | 86.0367 | 116.011 | 123.5779 | -123.9441 | -123.912
4905.7188 | 123.8617 | -61.3953 | 62.1094 | -0.29884 | 0.013033 | 0.01085 | 0.0074062 | 0.059394 | -0.0022559 | 0.07969 | -58.2779 | 62.0499 | -61.7523 | -61.5097 | 54.6844 | 24.6918 | 8.67 | 8.4045 | 62.1094 | -61.6653 | -0.35706 | -0.059509 | 3.1174 | -0.11444 | -7.4249 | -0.27008 | 0 | 3.4744 | 70.0653 | 69.7998 | 116.0797 | 123.4451 | 3.1174 | 123.5046 | 86.087 | -0.27008 | 123.4451 | 3.1174 | 86.087 | 116.0797 | 123.5046 | -123.8617 | -123.7747
4906.7188 | 123.8022 | -61.409 | 62.1231 | -0.016556 | 0.011538 | 0.014268 | 0.0089016 | 0.057044 | -0.00033333 | 0.076486 | -58.2916 | 62.0865 | -61.734 | -61.5692 | 54.5883 | 24.5956 | 8.6746 | 8.345 | 62.0956 | -61.6928 | -0.32501 | -0.036621 | 3.1174 | -0.16022 | -7.5348 | -0.28381 | -0.027466 | 3.4424 | 70.0836 | 69.754 | 115.9973 | 123.4955 | 3.1174 | 123.5046 | 86.0046 | -0.28381 | 123.4955 | 3.1174 | 86.0046 | 115.9973 | 123.5046 | -123.8571 | -123.8159
4907.7188 | 123.8205 | -61.409 | 62.1185 | 0.23521 | 0.014315 | 0.015122 | 0.0084744 | 0.058112 | -0.0011877 | 0.078835 | -58.4702 | 62.059 | -61.7294 | -61.5784 | 54.5654 | 24.7696 | 8.7204 | 8.3588 | 62.1094 | -61.7157 | -0.32043 | -0.059509 | 2.9388 | -0.16937 | -7.5531 | -0.3067 | -0.009155 | 3.2593 | 70.1294 | 69.7678 | 115.9744 | 123.468 | 2.9388 | 123.5184 | 86.1786 | -0.3067 | 123.468 | 2.9388 | 86.1786 | 115.9744 | 123.5184 | -123.848 | -123.8342
4908.7188 | 123.8113 | -61.3907 | 62.1185 | -0.09285 | 0.011538 | 0.009141 | 0.010397 | 0.058325 | -0.0014013 | 0.079263 | -58.3008 | 62.0407 | -61.734 | -61.5326 | 54.6616 | 24.6643 | 8.638 | 8.3725 | 62.0773 | -61.6745 | -0.34332 | -0.07782 | 3.0899 | -0.14191 | -7.457 | -0.28381 | -0.041198 | 3.4332 | 70.0287 | 69.7632 | 116.0522 | 123.4314 | 3.0899 | 123.468 | 86.055 | -0.28381 | 123.4314 | 3.0899 | 86.055 | 116.0522 | 123.468 | -123.8525 | -123.793
4909.7188 | 123.7244 | -61.4182 | 62.178 | -0.22255 | 0.014742 | 0.011918 | 0.01296 | 0.058966 | -0.0026831 | 0.078835 | -58.1268 | 62.1414 | -61.7294 | -61.5829 | 54.5517 | 24.5819 | 8.8074 | 8.2901 | 62.1506 | -61.7249 | -0.31128 | -0.036622 | 3.2913 | -0.16479 | -7.6263 | -0.3067 | -0.027466 | 3.6026 | 70.2255 | 69.7083 | 115.9698 | 123.5596 | 3.2913 | 123.5687 | 86.0001 | -0.3067 | 123.5596 | 3.2913 | 86.0001 | 115.9698 | 123.5687 | -123.9075 | -123.9029
4910.7188 | 123.8388 | -61.3998 | 62.1231 | 0.074997 | 0.01282 | 0.0089274 | 0.0093288 | 0.057044 | 0.00030767 | 0.079049 | -58.2413 | 62.0499 | -61.7523 | -61.5784 | 54.6021 | 24.5911 | 8.6151 | 8.3405 | 62.0911 | -61.6837 | -0.35248 | -0.073242 | 3.1586 | -0.17853 | -7.5211 | -0.28381 | -0.032044 | 3.511 | 70.015 | 69.7403 | 116.0019 | 123.4497 | 3.1586 | 123.4909 | 85.9909 | -0.28381 | 123.4497 | 3.1586 | 85.9909 | 116.0019 | 123.4909 | -123.8754 | -123.8068
4911.7188 | 123.8022 | -61.4273 | 62.114 | -1.8171 | 0.013888 | 0.010636 | 0.0078336 | 0.057685 | -0.0011877 | 0.079904 | -58.4518 | 62.0682 | -61.7386 | -61.5921 | 54.5837 | 24.6506 | 8.6426 | 8.345 | 62.0865 | -61.702 | -0.31128 | -0.045777 | 2.9755 | -0.16479 | -7.5302 | -0.27466 | -0.027466 | 3.2867 | 70.0699 | 69.7723 | 116.011 | 123.4955 | 2.9755 | 123.5138 | 86.0779 | -0.27466 | 123.4955 | 2.9755 | 86.0779 | 116.011 | 123.5138 | -123.8525 | -123.8159
4912.7188 | 123.761 | -61.4273 | 62.1231 | 0.090256 | 0.014956 | 0.011064 | 0.0097562 | 0.057471 | -0.00011953 | 0.077981 | -58.2184 | 62.0773 | -61.7432 | -61.5829 | 54.5929 | 24.7742 | 8.6472 | 8.2169 | 62.0956 | -61.6882 | -0.31586 | -0.045776 | 3.2089 | -0.15564 | -7.5302 | -0.26093 | -0.027466 | 3.5248 | 70.0745 | 69.6442 | 116.0202 | 123.5046 | 3.2089 | 123.5229 | 86.2015 | -0.26093 | 123.5046 | 3.2089 | 86.2015 | 116.0202 | 123.5229 | -123.8663 | -123.8113
4913.7188 | 123.7885 | -61.409 | 62.1094 | 0.15129 | 0.013888 | 0.006791 | 0.010824 | 0.059607 | 0.00052127 | 0.078622 | -58.2092 | 62.0636 | -61.7523 | -61.5875 | 54.5563 | 24.5132 | 8.7021 | 8.3679 | 62.0819 | -61.6791 | -0.34332 | -0.045776 | 3.1998 | -0.17853 | -7.5531 | -0.27008 | -0.027466 | 3.5431 | 70.1111 | 69.7769 | 115.9653 | 123.4726 | 3.1998 | 123.4909 | 85.9222 | -0.27008 | 123.4726 | 3.1998 | 85.9222 | 115.9653 | 123.4909 | -123.8617 | -123.7885
4914.7344 | 123.761 | -61.4182 | 62.1506 | -0.26833 | 0.013033 | 0.011064 | 0.011038 | 0.055762 | -0.00054693 | 0.079476 | -58.255 | 62.1231 | -61.7157 | -61.5463 | 54.5975 | 24.5773 | 8.7708 | 8.3954 | 62.1094 | -61.6974 | -0.29755 | -0.027466 | 3.1631 | -0.12817 | -7.5531 | -0.27924 | -0.041199 | 3.4607 | 70.1889 | 69.8135 | 116.0156 | 123.5413 | 3.1631 | 123.5275 | 85.9955 | -0.27924 | 123.5413 | 3.1631 | 85.9955 | 116.0156 | 123.5275 | -123.8663 | -123.848
4915.7188 | 123.7747 | -61.409 | 62.1277 | -0.0012969 | 0.013888 | 0.0093546 | 0.0093288 | 0.060248 | -0.0020421 | 0.077554 | -58.3237 | 62.0499 | -61.734 | -61.4365 | 54.6204 | 24.4492 | 8.7021 | 8.2901 | 62.0819 | -61.6837 | -0.32501 | -0.07782 | 3.0853 | -0.027465 | -7.5073 | -0.27466 | -0.045777 | 3.4103 | 70.1111 | 69.6991 | 116.0294 | 123.4589 | 3.0853 | 123.4909 | 85.8582 | -0.27466 | 123.4589 | 3.0853 | 85.8582 | 116.0294 | 123.4909 | -123.8617 | -123.8113
4916.7188 | 123.7976 | -61.4273 | 62.1094 | 0.082626 | 0.014956 | 0.0087138 | 0.0089016 | 0.057898 | -0.0016149 | 0.07734 | -58.3282 | 62.0682 | -61.734 | -61.5967 | 54.5975 | 24.7192 | 8.6838 | 8.3588 | 62.0865 | -61.6837 | -0.3067 | -0.041199 | 3.0991 | -0.16937 | -7.5119 | -0.25635 | -0.022888 | 3.4058 | 70.1111 | 69.7861 | 116.0248 | 123.4955 | 3.0991 | 123.5138 | 86.1465 | -0.25635 | 123.4955 | 3.0991 | 86.1465 | 116.0248 | 123.5138 | -123.8434 | -123.793
4917.7188 | 123.7564 | -61.4273 | 62.1094 | 0.097885 | 0.014956 | 0.0085 | 0.0091152 | 0.058539 | -0.0020421 | 0.077554 | -58.3008 | 62.059 | -61.7569 | -61.6058 | 54.5517 | 24.5911 | 8.7112 | 8.4 | 62.0865 | -61.7157 | -0.32959 | -0.050354 | 3.1265 | -0.17853 | -7.5577 | -0.28839 | -0.022888 | 3.4561 | 70.1385 | 69.8273 | 115.979 | 123.4863 | 3.1265 | 123.5138 | 86.0184 | -0.28839 | 123.4863 | 3.1265 | 86.0184 | 115.979 | 123.5138 | -123.8663 | -123.8251
4918.7188 | 123.8022 | -61.441 | 62.1094 | 0.15129 | 0.01581 | 0.010209 | 0.010183 | 0.056617 | 9.4068e-05 | 0.078622 | -58.3145 | 62.0499 | -61.7523 | -61.6013 | 54.57 | 24.6002 | 8.6746 | 8.3908 | 62.0773 | -61.7065 | -0.31128 | -0.059509 | 3.1265 | -0.16022 | -7.5394 | -0.2655 | -0.032043 | 3.4378 | 70.1157 | 69.8318 | 116.011 | 123.4909 | 3.1265 | 123.5184 | 86.0413 | -0.2655 | 123.4909 | 3.1265 | 86.0413 | 116.011 | 123.5184 | -123.8617 | -123.8159
4919.7188 | 123.8937 | -61.409 | 62.114 | 0.067368 | 0.016024 | 0.009141 | 0.011679 | 0.059394 | 0.00073487 | 0.077981 | -58.3145 | 62.0453 | -61.7294 | -61.5875 | 54.57 | 24.5178 | 8.6517 | 8.3954 | 62.0819 | -61.7203 | -0.32043 | -0.068665 | 3.0945 | -0.17853 | -7.5439 | -0.31128 | -0.032044 | 3.4149 | 70.0607 | 69.8044 | 115.979 | 123.4543 | 3.0945 | 123.4909 | 85.9268 | -0.31128 | 123.4543 | 3.0945 | 85.9268 | 115.979 | 123.4909 | -123.8434 | -123.8342
4920.7188 | 123.7839 | -61.3998 | 62.0865 | 0.1284 | 0.016665 | 0.0132 | 0.010824 | 0.056617 | -0.0011877 | 0.077981 | -58.2825 | 62.0316 | -61.7294 | -61.5875 | 54.6112 | 24.5956 | 8.6105 | 8.4183 | 62.0316 | -61.7203 | -0.32959 | -0.054932 | 3.1174 | -0.18768 | -7.4753 | -0.32043 | -0.054932 | 3.447 | 70.0104 | 69.8181 | 116.011 | 123.4314 | 3.1174 | 123.4314 | 85.9955 | -0.32043 | 123.4314 | 3.1174 | 85.9955 | 116.011 | 123.4314 | -123.8159 | -123.8068
4921.7188 | 123.793 | -61.3998 | 62.0819 | 0.10551 | 0.014742 | 0.014268 | 0.011038 | 0.057471 | -0.00033333 | 0.077126 | -58.2642 | 62.0544 | -61.7523 | -61.5555 | 54.6249 | 24.5407 | 8.638 | 8.432 | 62.0773 | -61.7157 | -0.35248 | -0.027466 | 3.1357 | -0.15564 | -7.457 | -0.31586 | -0.004577 | 3.4882 | 70.0378 | 69.8318 | 116.0248 | 123.4543 | 3.1357 | 123.4772 | 85.9406 | -0.31586 | 123.4543 | 3.1357 | 85.9406 | 116.0248 | 123.4772 | -123.8342 | -123.7976
4922.7188 | 123.761 | -61.3953 | 62.0911 | 0.097885 | 0.013247 | 0.012773 | 0.0091152 | 0.059607 | -0.0018285 | 0.079263 | -58.2047 | 62.0453 | -61.7477 | -61.5875 | 54.5883 | 24.527 | 8.7158 | 8.3633 | 62.0773 | -61.7157 | -0.35248 | -0.045776 | 3.1906 | -0.19226 | -7.5027 | -0.32043 | -0.013732 | 3.5431 | 70.1111 | 69.7586 | 115.9836 | 123.4406 | 3.1906 | 123.4726 | 85.9222 | -0.32043 | 123.4406 | 3.1906 | 85.9222 | 115.9836 | 123.4726 | -123.8388 | -123.8068
4923.7188 | 123.7885 | -61.4227 | 62.1094 | 0.13603 | 0.017733 | 0.014054 | 0.010824 | 0.059821 | -0.0035375 | 0.081185 | -58.1726 | 62.0453 | -61.734 | -61.5829 | 54.5883 | 24.5499 | 8.6609 | 8.313 | 62.0499 | -61.7203 | -0.31128 | -0.064087 | 3.2501 | -0.16022 | -7.5211 | -0.29755 | -0.059509 | 3.5614 | 70.0836 | 69.7357 | 116.011 | 123.468 | 3.2501 | 123.4726 | 85.9726 | -0.29755 | 123.468 | 3.2501 | 85.9726 | 116.011 | 123.4726 | -123.8434 | -123.8297
4924.7188 | 123.7976 | -61.4227 | 62.1048 | -0.031814 | 0.01282 | 0.010423 | 0.0093288 | 0.057257 | -0.00076053 | 0.079904 | -58.2138 | 62.0956 | -61.7249 | -61.5555 | 54.6204 | 24.5956 | 8.7296 | 8.3313 | 62.0865 | -61.6608 | -0.30213 | -0.009155 | 3.2089 | -0.13275 | -7.4844 | -0.23804 | -0.01831 | 3.511 | 70.1523 | 69.754 | 116.0431 | 123.5184 | 3.2089 | 123.5092 | 86.0184 | -0.23804 | 123.5184 | 3.2089 | 86.0184 | 116.0431 | 123.5092 | -123.8297 | -123.7656
4925.7188 | 123.8205 | -61.4182 | 62.1002 | 0.12077 | 0.013033 | 0.011064 | 0.013601 | 0.057685 | -0.0020421 | 0.079904 | -58.1589 | 62.0636 | -61.7523 | -61.5601 | 54.6021 | 24.6597 | 8.6472 | 8.3359 | 62.0636 | -61.7111 | -0.33417 | -0.036621 | 3.2593 | -0.14191 | -7.4982 | -0.29297 | -0.036621 | 3.5934 | 70.0653 | 69.754 | 116.0202 | 123.4818 | 3.2593 | 123.4818 | 86.0779 | -0.29297 | 123.4818 | 3.2593 | 86.0779 | 116.0202 | 123.4818 | -123.8525 | -123.8113
4926.7188 | 123.8251 | -61.441 | 62.0956 | 0.21233 | 0.016451 | 0.013627 | 0.01531 | 0.061743 | 0.00094847 | 0.077981 | -58.168 | 62.059 | -61.7569 | -61.5463 | 54.5929 | 24.6368 | 8.638 | 8.3496 | 62.0544 | -61.7249 | -0.31586 | -0.036621 | 3.273 | -0.10529 | -7.5027 | -0.28381 | -0.041199 | 3.5889 | 70.079 | 69.7906 | 116.0339 | 123.5001 | 3.273 | 123.4955 | 86.0779 | -0.28381 | 123.5001 | 3.273 | 86.0779 | 116.0339 | 123.4955 | -123.8525 | -123.8205
4927.7188 | 123.8525 | -61.3953 | 62.0865 | 0.22758 | 0.014742 | 0.0082864 | 0.017233 | 0.065161 | 0.0015893 | 0.078195 | -58.168 | 62.0499 | -61.734 | -61.4273 | 54.7028 | 24.6094 | 8.6655 | 8.3542 | 62.0682 | -61.7111 | -0.33875 | -0.036621 | 3.2272 | -0.032043 | -7.3837 | -0.31586 | -0.018311 | 3.566 | 70.0607 | 69.7495 | 116.098 | 123.4451 | 3.2272 | 123.4634 | 86.0046 | -0.31586 | 123.4451 | 3.2272 | 86.0046 | 116.098 | 123.4634 | -123.8205 | -123.7976
4928.7188 | 123.8113 | -61.3953 | 62.0956 | 0.15892 | 0.017519 | 0.010636 | 0.011892 | 0.060462 | -0.00097413 | 0.079476 | -58.1818 | 62.0499 | -61.7386 | -61.5738 | 54.5837 | 24.6368 | 8.6334 | 8.3496 | 62.0544 | -61.734 | -0.34332 | -0.045776 | 3.2135 | -0.17853 | -7.5119 | -0.33875 | -0.041199 | 3.5568 | 70.0287 | 69.7449 | 115.979 | 123.4451 | 3.2135 | 123.4497 | 86.0321 | -0.33875 | 123.4451 | 3.2135 | 86.0321 | 115.979 | 123.4497 | -123.8342 | -123.8297
4929.7188 | 123.8251 | -61.3861 | 62.1048 | -0.077591 | 0.013888 | 0.011918 | 0.0089016 | 0.060462 | -0.0014013 | 0.078408 | -58.2825 | 62.0728 | -61.7386 | -61.5143 | 54.5975 | 24.6872 | 8.67 | 8.4137 | 62.0865 | -61.6837 | -0.35248 | -0.032043 | 3.1036 | -0.12817 | -7.5073 | -0.29755 | -0.01831 | 3.4561 | 70.0562 | 69.7998 | 115.9836 | 123.4589 | 3.1036 | 123.4726 | 86.0733 | -0.29755 | 123.4589 | 3.1036 | 86.0733 | 115.9836 | 123.4726 | -123.8434 | -123.7885
4930.7188 | 123.8297 | -61.3815 | 62.0773 | 0.2047 | 0.019656 | 0.012773 | 0.013388 | 0.05918 | -0.00011953 | 0.078622 | -58.4656 | 62.0361 | -61.7615 | -61.5784 | 54.6295 | 24.7055 | 8.606 | 8.3359 | 62.027 | -61.7249 | -0.37994 | -0.041199 | 2.916 | -0.19684 | -7.4478 | -0.34332 | -0.050354 | 3.2959 | 69.9875 | 69.7174 | 116.011 | 123.4177 | 2.916 | 123.4085 | 86.087 | -0.34332 | 123.4177 | 2.916 | 86.087 | 116.011 | 123.4085 | -123.8388 | -123.8022
4931.7188 | 123.88 | -61.3998 | 62.0956 | 0.15129 | 0.017092 | 0.016831 | 0.01531 | 0.060034 | -0.0016149 | 0.078835 | -58.2596 | 62.0865 | -61.7157 | -61.5967 | 54.3457 | 24.5316 | 8.8028 | 8.3084 | 62.0728 | -61.7065 | -0.31586 | -0.009155 | 3.1403 | -0.19684 | -7.7499 | -0.3067 | -0.022888 | 3.4561 | 70.2026 | 69.7083 | 115.7455 | 123.4863 | 3.1403 | 123.4726 | 85.9314 | -0.3067 | 123.4863 | 3.1403 | 85.9314 | 115.7455 | 123.4726 | -123.8113 | -123.8022
4932.7188 | 123.8068 | -61.4044 | 62.0499 | 0.15129 | 0.016024 | 0.012132 | 0.015097 | 0.059821 | -0.0028967 | 0.078835 | -58.2504 | 62.0865 | -61.7386 | -61.5601 | 54.5792 | 24.7192 | 8.6014 | 8.2901 | 62.0316 | -61.7203 | -0.33417 | 0.036621 | 3.154 | -0.15564 | -7.4707 | -0.31586 | -0.018311 | 3.4882 | 70.0058 | 69.6945 | 115.9836 | 123.4909 | 3.154 | 123.436 | 86.1237 | -0.31586 | 123.4909 | 3.154 | 86.1237 | 115.9836 | 123.436 | -123.7885 | -123.7701
4933.7188 | 123.8159 | -61.3953 | 62.0819 | 0.074997 | 0.015169 | 0.0132 | 0.010397 | 0.058539 | -0.00076053 | 0.078835 | -58.2779 | 62.0865 | -61.7798 | -61.5692 | 54.6112 | 24.7192 | 8.6151 | 8.3084 | 62.0728 | -61.7294 | -0.38452 | 0.004578 | 3.1174 | -0.17395 | -7.4707 | -0.33417 | -0.009155 | 3.5019 | 70.0104 | 69.7037 | 116.0065 | 123.4818 | 3.1174 | 123.468 | 86.1145 | -0.33417 | 123.4818 | 3.1174 | 86.1145 | 116.0065 | 123.468 | -123.8617 | -123.8113
4934.7188 | 123.793 | -61.4227 | 62.1048 | -0.0089264 | 0.014529 | 0.0063638 | 0.0093288 | 0.058539 | -0.00033333 | 0.079263 | -58.3328 | 62.0682 | -61.7798 | -61.5829 | 54.57 | 24.6506 | 8.6792 | 8.2901 | 62.0773 | -61.6974 | -0.35706 | -0.036621 | 3.0899 | -0.16022 | -7.5348 | -0.27466 | -0.027465 | 3.447 | 70.1019 | 69.7128 | 115.9927 | 123.4909 | 3.0899 | 123.5001 | 86.0733 | -0.27466 | 123.4909 | 3.0899 | 86.0733 | 115.9927 | 123.5001 | -123.8846 | -123.8022
4935.7188 | 123.8068 | -61.4136 | 62.0956 | 2.0205 | 0.01581 | 0.013627 | 0.013601 | 0.058112 | -0.00054693 | 0.07734 | -58.2596 | 62.0499 | -61.7569 | -61.5738 | 54.6249 | 24.7192 | 8.5693 | 8.2809 | 62.0728 | -61.7157 | -0.34332 | -0.045776 | 3.154 | -0.16022 | -7.4707 | -0.30212 | -0.022888 | 3.4973 | 69.9829 | 69.6945 | 116.0385 | 123.4634 | 3.154 | 123.4863 | 86.1328 | -0.30212 | 123.4634 | 3.154 | 86.1328 | 116.0385 | 123.4863 | -123.8525 | -123.8113
4936.7188 | 123.8342 | -61.4044 | 62.0728 | 0.19707 | 0.016451 | 0.014482 | 0.017233 | 0.061316 | -0.0020421 | 0.075845 | -58.2321 | 62.0819 | -61.7432 | -61.4822 | 54.5151 | 24.7009 | 8.6243 | 8.2993 | 62.0499 | -61.7111 | -0.33875 | 0.009155 | 3.1723 | -0.07782 | -7.5577 | -0.3067 | -0.022888 | 3.511 | 70.0287 | 69.7037 | 115.9195 | 123.4863 | 3.1723 | 123.4543 | 86.1053 | -0.3067 | 123.4863 | 3.1723 | 86.1053 | 115.9195 | 123.4543 | -123.8159 | -123.7839
4937.7188 | 123.8525 | -61.3907 | 62.0819 | 0.2047 | 0.015597 | 0.01555 | 0.016165 | 0.060248 | -0.00054693 | 0.076699 | -58.2321 | 62.0956 | -61.7203 | -61.5601 | 54.57 | 24.5453 | 8.6243 | 8.5556 | 62.0316 | -61.702 | -0.32959 | 0.013733 | 3.1586 | -0.16937 | -7.5119 | -0.31128 | -0.050354 | 3.4882 | 70.015 | 69.9463 | 115.9607 | 123.4863 | 3.1586 | 123.4222 | 85.936 | -0.31128 | 123.4863 | 3.1586 | 85.936 | 115.9607 | 123.4222 | -123.8022 | -123.7839
4938.7188 | 123.7885 | -61.409 | 62.0682 | 0.12077 | 0.014742 | 0.007432 | 0.015738 | 0.060248 | -0.00011953 | 0.07969 | -58.2413 | 62.0956 | -61.7249 | -61.5692 | 54.6341 | 24.7147 | 8.5785 | 8.3359 | 62.0544 | -61.7157 | -0.31586 | 0.027466 | 3.1677 | -0.16022 | -7.4341 | -0.3067 | -0.013733 | 3.4836 | 69.9875 | 69.7449 | 116.0431 | 123.5046 | 3.1677 | 123.4634 | 86.1237 | -0.3067 | 123.5046 | 3.1677 | 86.1237 | 116.0431 | 123.4634 | -123.793 | -123.7839
4939.7344 | 123.8068 | -61.377 | 62.1094 | -0.25307 | 0.013247 | 0.0059366 | 0.0061246 | 0.061957 | -0.0011877 | 0.078195 | -58.223 | 62.0682 | -61.7249 | -61.4822 | 54.6799 | 24.7467 | 8.67 | 8.4229 | 62.0728 | -61.6974 | -0.3479 | -0.041199 | 3.154 | -0.10529 | -7.4295 | -0.32043 | -0.036621 | 3.5019 | 70.047 | 69.7998 | 116.0568 | 123.4451 | 3.154 | 123.4497 | 86.1237 | -0.32043 | 123.4451 | 3.154 | 86.1237 | 116.0568 | 123.4497 | -123.8342 | -123.8068
4940.7188 | 123.8388 | -61.4182 | 62.0865 | 0.10551 | 0.016878 | 0.011277 | 0.015097 | 0.061743 | -0.00097413 | 0.079049 | -58.2642 | 62.059 | -61.7386 | -61.5692 | 54.5975 | 24.7421 | 8.5648 | 8.313 | 62.0636 | -61.7111 | -0.32043 | -0.027466 | 3.154 | -0.15106 | -7.489 | -0.29297 | -0.022888 | 3.4744 | 69.9829 | 69.7311 | 116.0156 | 123.4772 | 3.154 | 123.4818 | 86.1603 | -0.29297 | 123.4772 | 3.154 | 86.1603 | 116.0156 | 123.4818 | -123.8251 | -123.7976
4941.7188 | 123.8113 | -61.409 | 62.1048 | 0.097885 | 0.01581 | 0.011064 | 0.015524 | 0.060034 | -0.0014013 | 0.07969 | -58.2733 | 62.0636 | -61.7477 | -61.5692 | 54.6112 | 24.6963 | 8.6197 | 8.3267 | 62.0682 | -61.6974 | -0.33875 | -0.041198 | 3.1357 | -0.16022 | -7.4936 | -0.28839 | -0.036621 | 3.4744 | 70.0287 | 69.7357 | 116.0202 | 123.4726 | 3.1357 | 123.4772 | 86.1053 | -0.28839 | 123.4726 | 3.1357 | 86.1053 | 116.0202 | 123.4772 | -123.8525 | -123.8022
4942.7188 | 123.8342 | -61.4136 | 62.0682 | 0.090256 | 0.015383 | 0.013627 | 0.012106 | 0.060248 | -0.0011877 | 0.078622 | -58.3466 | 62.0316 | -61.7432 | -61.6013 | 54.6158 | 24.7696 | 8.5556 | 8.2993 | 62.0728 | -61.7065 | -0.32959 | -0.036621 | 3.067 | -0.18768 | -7.4524 | -0.29297 | 0.004578 | 3.3966 | 69.9692 | 69.7128 | 116.0294 | 123.4451 | 3.067 | 123.4863 | 86.1832 | -0.29297 | 123.4451 | 3.067 | 86.1832 | 116.0294 | 123.4863 | -123.8113 | -123.7747
4943.7188 | 123.8205 | -61.4227 | 62.0819 | 0.18181 | 0.015597 | 0.018968 | 0.010824 | 0.058753 | -0.0035375 | 0.077767 | -58.2321 | 62.059 | -61.734 | -61.5921 | 54.6066 | 24.8245 | 8.5831 | 8.3542 | 62.0773 | -61.7203 | -0.31128 | -0.022888 | 3.1906 | -0.16937 | -7.4753 | -0.29755 | -0.004577 | 3.5019 | 70.0058 | 69.7769 | 116.0294 | 123.4818 | 3.1906 | 123.5001 | 86.2473 | -0.29755 | 123.4818 | 3.1906 | 86.2473 | 116.0294 | 123.5001 | -123.8159 | -123.8022
4944.7188 | 123.8297 | -61.4136 | 62.059 | 0.21996 | 0.014315 | 0.011277 | 0.014029 | 0.060889 | -0.00097413 | 0.080544 | -58.2275 | 62.0728 | -61.7615 | -61.7752 | 54.5013 | 24.939 | 8.6288 | 8.2947 | 62.0682 | -61.7065 | -0.3479 | 0.013733 | 3.186 | -0.36163 | -7.5577 | -0.29297 | 0.009155 | 3.5339 | 70.0424 | 69.7083 | 115.9149 | 123.4863 | 3.186 | 123.4818 | 86.3525 | -0.29297 | 123.4863 | 3.186 | 86.3525 | 115.9149 | 123.4818 | -123.8205 | -123.7656
4945.7188 | 123.9212 | -61.4319 | 62.0636 | 0.18944 | 0.017947 | 0.017045 | 0.014883 | 0.060675 | -0.0016149 | 0.077767 | -58.223 | 62.0911 | -61.7569 | -61.5463 | 54.5471 | 24.6689 | 8.5098 | 8.0795 | 62.0407 | -61.7523 | -0.32501 | 0.027465 | 3.2089 | -0.11444 | -7.5165 | -0.32043 | -0.022889 | 3.5339 | 69.9417 | 69.5114 | 115.979 | 123.5229 | 3.2089 | 123.4726 | 86.1008 | -0.32043 | 123.5229 | 3.2089 | 86.1008 | 115.979 | 123.4726 | -123.8205 | -123.8159
4946.7188 | 123.8434 | -61.4044 | 62.0956 | 0.15892 | 0.014101 | 0.015122 | 0.014242 | 0.061316 | -0.0014013 | 0.080117 | -58.2321 | 62.0956 | -61.7294 | -61.5601 | 54.5517 | 24.6963 | 8.5922 | 8.2993 | 62.0453 | -61.734 | -0.32501 | 0 | 3.1723 | -0.15564 | -7.5439 | -0.32959 | -0.050354 | 3.4973 | 69.9966 | 69.7037 | 115.9561 | 123.5001 | 3.1723 | 123.4497 | 86.1008 | -0.32959 | 123.5001 | 3.1723 | 86.1008 | 115.9561 | 123.4497 | -123.8251 | -123.8297
4947.7188 | 123.8068 | -61.3953 | 62.0819 | 0.23521 | 0.014742 | 0.0097818 | 0.017233 | 0.062384 | -0.0018285 | 0.078835 | -58.2367 | 62.0636 | -61.7569 | -61.5784 | 54.5242 | 24.7147 | 8.606 | 8.3313 | 62.0544 | -61.7432 | -0.36163 | -0.01831 | 3.1586 | -0.18311 | -7.5577 | -0.3479 | -0.027466 | 3.5202 | 70.0012 | 69.7266 | 115.9195 | 123.4589 | 3.1586 | 123.4497 | 86.1099 | -0.3479 | 123.4589 | 3.1586 | 86.1099 | 115.9195 | 123.4497 | -123.8388 | -123.8251
4948.7344 | 123.7885 | -61.3907 | 62.1094 | -0.17677 | 0.013247 | 0.0082864 | 0.0093288 | 0.05918 | -0.00033333 | 0.079476 | -58.2092 | 62.0819 | -61.7294 | -61.5189 | 54.5975 | 24.8291 | 9.2148 | 8.7021 | 62.1826 | -61.647 | -0.33874 | -0.027466 | 3.1815 | -0.12817 | -7.5119 | -0.25635 | 0.073242 | 3.5202 | 70.6055 | 70.0928 | 115.9882 | 123.4726 | 3.1815 | 123.5733 | 86.2198 | -0.25635 | 123.4726 | 3.1815 | 86.2198 | 115.9882 | 123.5733 | -123.8388 | -123.7564
4949.7344 | 123.9441 | -61.3632 | 62.1872 | -0.1844 | 0.012179 | 0.013627 | 0.0095424 | 0.058753 | -0.0016149 | 0.078622 | -58.2138 | 62.0728 | -61.7203 | -61.5051 | 54.6158 | 24.7513 | 8.7433 | 8.3954 | 62.0956 | -61.702 | -0.35706 | -0.11444 | 3.1494 | -0.14191 | -7.5714 | -0.33875 | -0.091553 | 3.5065 | 70.1065 | 69.7586 | 115.979 | 123.436 | 3.1494 | 123.4589 | 86.1145 | -0.33875 | 123.436 | 3.1494 | 86.1145 | 115.979 | 123.4589 | -123.9075 | -123.8892
4950.7188 | 123.8297 | -61.3953 | 62.1094 | 0.61668 | 0.015169 | 0.011064 | 0.011679 | 0.060462 | -0.00097413 | 0.079263 | -58.0948 | 62.059 | -61.7203 | -61.5326 | 54.2725 | 24.5544 | 8.6655 | 8.3405 | 62.0224 | -61.7203 | -0.32501 | -0.050354 | 3.3005 | -0.13733 | -7.8369 | -0.32501 | -0.086975 | 3.6255 | 70.0607 | 69.7357 | 115.6677 | 123.4543 | 3.3005 | 123.4177 | 85.9497 | -0.32501 | 123.4543 | 3.3005 | 85.9497 | 115.6677 | 123.4177 | -123.8297 | -123.8297
4951.7188 | 123.848 | -61.3998 | 62.0865 | 0.17418 | 0.017947 | 0.015336 | 0.016592 | 0.060034 | -0.00033333 | 0.078195 | -58.3786 | 62.0407 | -61.7569 | -61.5921 | 54.3137 | 24.678 | 8.6563 | 8.3221 | 62.0636 | -61.7203 | -0.35706 | -0.045777 | 3.0212 | -0.19226 | -7.7728 | -0.32043 | -0.022888 | 3.3783 | 70.0562 | 69.722 | 115.7135 | 123.4406 | 3.0212 | 123.4634 | 86.0779 | -0.32043 | 123.4406 | 3.0212 | 86.0779 | 115.7135 | 123.4634 | -123.8434 | -123.8068
4952.7188 | 123.8205 | -61.4319 | 62.0819 | 0.18181 | 0.014742 | 0.01085 | 0.013388 | 0.060034 | -0.00076053 | 0.079049 | -58.429 | 62.0499 | -61.7477 | -61.5829 | 54.4418 | 24.7192 | 8.5968 | 8.3221 | 62.0819 | -61.7294 | -0.31586 | -0.032043 | 3.0029 | -0.15106 | -7.6401 | -0.29755 | 0 | 3.3188 | 70.0287 | 69.754 | 115.8737 | 123.4818 | 3.0029 | 123.5138 | 86.1511 | -0.29755 | 123.4818 | 3.0029 | 86.1511 | 115.8737 | 123.5138 | -123.8297 | -123.8113
4953.7344 | 123.7656 | -61.3998 | 62.1552 | -0.25307 | 0.014529 | 0.0076456 | 0.011679 | 0.057257 | -0.0016149 | 0.078408 | -58.2367 | 62.1231 | -61.7157 | -61.5738 | 54.3045 | 24.6506 | 8.8257 | 8.3267 | 62.146 | -61.7294 | -0.31586 | -0.032043 | 3.1631 | -0.17395 | -7.8506 | -0.32959 | -0.009155 | 3.479 | 70.2255 | 69.7266 | 115.7043 | 123.5229 | 3.1631 | 123.5458 | 86.0504 | -0.32959 | 123.5229 | 3.1631 | 86.0504 | 115.7043 | 123.5458 | -123.8708 | -123.8846
4954.7188 | 123.8068 | -61.4044 | 62.146 | -0.2607 | 0.014315 | 0.014268 | 0.01296 | 0.057257 | -0.0024695 | 0.078408 | -58.2321 | 62.1094 | -61.734 | -61.5463 | 54.332 | 24.6597 | 8.8165 | 8.4045 | 62.1002 | -61.6882 | -0.32959 | -0.036621 | 3.1723 | -0.14191 | -7.814 | -0.28381 | -0.045776 | 3.5019 | 70.2209 | 69.809 | 115.7364 | 123.5138 | 3.1723 | 123.5046 | 86.0641 | -0.28381 | 123.5138 | 3.1723 | 86.0641 | 115.7364 | 123.5046 | -123.88 | -123.8342
4955.7188 | 123.8205 | -61.3907 | 62.1094 | 0.18181 | 0.015169 | 0.013413 | 0.012747 | 0.059821 | -0.0024695 | 0.078622 | -58.2138 | 62.0316 | -61.7386 | -61.5326 | 54.3777 | 24.6185 | 8.6243 | 8.4091 | 62.0682 | -61.7249 | -0.3479 | -0.07782 | 3.1769 | -0.14191 | -7.7316 | -0.33417 | -0.041199 | 3.5248 | 70.015 | 69.7998 | 115.7684 | 123.4222 | 3.1769 | 123.4589 | 86.0092 | -0.33417 | 123.4222 | 3.1769 | 86.0092 | 115.7684 | 123.4589 | -123.848 | -123.8342
4956.7188 | 123.8022 | -61.4227 | 62.0773 | 0.090256 | 0.015169 | 0.014268 | 0.011038 | 0.059607 | 9.4068e-05 | 0.080544 | -58.2138 | 62.0728 | -61.7477 | -61.5875 | 54.3365 | 24.5911 | 8.638 | 8.3633 | 62.1002 | -61.7111 | -0.32501 | -0.004578 | 3.2089 | -0.1648 | -7.7408 | -0.28839 | 0.022888 | 3.5339 | 70.0607 | 69.7861 | 115.7593 | 123.4955 | 3.2089 | 123.5229 | 86.0138 | -0.28839 | 123.4955 | 3.2089 | 86.0138 | 115.7593 | 123.5229 | -123.8251 | -123.7885
4957.7188 | 123.7747 | -61.4273 | 62.0682 | 0.1284 | 0.015383 | 0.009141 | 0.015097 | 0.058966 | -0.00011953 | 0.077981 | -58.2413 | 62.0544 | -61.7477 | -61.5646 | 54.3823 | 24.6414 | 8.6334 | 8.3542 | 62.0499 | -61.7203 | -0.32044 | -0.013733 | 3.186 | -0.13733 | -7.6859 | -0.29297 | -0.01831 | 3.5065 | 70.0607 | 69.7815 | 115.8096 | 123.4818 | 3.186 | 123.4772 | 86.0687 | -0.29297 | 123.4818 | 3.186 | 86.0687 | 115.8096 | 123.4772 | -123.8159 | -123.7885
4958.7344 | 123.8251 | -61.3861 | 62.1185 | 0.38017 | 0.01282 | 0.0082864 | 0.0082608 | 0.058325 | -0.0033239 | 0.077554 | -58.1909 | 62.0865 | -61.7249 | -61.5189 | 54.4144 | 24.6963 | 8.7524 | 8.4732 | 62.1002 | -61.6745 | -0.33875 | -0.032043 | 3.1952 | -0.13275 | -7.7042 | -0.28839 | -0.01831 | 3.5339 | 70.1385 | 69.8593 | 115.8005 | 123.4726 | 3.1952 | 123.4863 | 86.0825 | -0.28839 | 123.4726 | 3.1952 | 86.0825 | 115.8005 | 123.4863 | -123.8434 | -123.793
4959.7188 | 123.8068 | -61.3953 | 62.1002 | 0.15129 | 0.013888 | 0.015336 | 0.014242 | 0.05918 | -0.00097413 | 0.081613 | -58.2596 | 62.0682 | -61.7432 | -61.5646 | 54.4052 | 24.733 | 8.6884 | 8.4045 | 62.059 | -61.7065 | -0.3479 | -0.032044 | 3.1357 | -0.16937 | -7.695 | -0.31128 | -0.041199 | 3.4836 | 70.0836 | 69.7998 | 115.8005 | 123.4634 | 3.1357 | 123.4543 | 86.1282 | -0.31128 | 123.4634 | 3.1357 | 86.1282 | 115.8005 | 123.4543 | -123.8434 | -123.8068
4960.7188 | 123.8022 | -61.3998 | 62.0819 | 0.11314 | 0.014529 | 0.0089274 | 0.015097 | 0.05918 | -0.00033333 | 0.080117 | -58.2596 | 62.0544 | -61.7661 | -61.5692 | 54.3549 | 24.6735 | 8.67 | 8.3862 | 62.0682 | -61.7249 | -0.36621 | -0.027466 | 3.1403 | -0.16937 | -7.7271 | -0.32501 | -0.013733 | 3.5065 | 70.0699 | 69.7861 | 115.7547 | 123.4543 | 3.1403 | 123.468 | 86.0733 | -0.32501 | 123.4543 | 3.1403 | 86.0733 | 115.7547 | 123.468 | -123.848 | -123.8068
4961.7188 | 123.8022 | -61.3953 | 62.0773 | 0.074997 | 0.01282 | 0.014268 | 0.014669 | 0.060034 | -0.0048193 | 0.077767 | -58.255 | 62.0407 | -61.7477 | -61.5646 | 54.3503 | 24.7147 | 8.6746 | 8.4412 | 62.0865 | -61.7294 | -0.35248 | -0.036622 | 3.1403 | -0.16937 | -7.7271 | -0.33417 | 0.009155 | 3.4927 | 70.0699 | 69.8364 | 115.7455 | 123.436 | 3.1403 | 123.4818 | 86.1099 | -0.33417 | 123.436 | 3.1403 | 86.1099 | 115.7455 | 123.4818 | -123.8251 | -123.8068
4962.7188 | 123.8342 | -61.4136 | 62.0682 | 0.13603 | 0.015597 | 0.011704 | 0.013174 | 0.060248 | -0.0046057 | 0.079904 | -58.2275 | 62.0728 | -61.734 | -61.5509 | 54.3732 | 24.6643 | 8.7067 | 8.4091 | 62.0636 | -61.7249 | -0.32044 | 0.004578 | 3.186 | -0.13733 | -7.695 | -0.31128 | -0.004577 | 3.5065 | 70.1202 | 69.8227 | 115.7867 | 123.4863 | 3.186 | 123.4772 | 86.0779 | -0.31128 | 123.4863 | 3.186 | 86.0779 | 115.7867 | 123.4772 | -123.8022 | -123.793
4963.7344 | 123.8113 | -61.4044 | 62.1231 | -0.16914 | 0.013033 | 0.0099954 | 0.010824 | 0.057471 | -0.0024695 | 0.078408 | -58.2275 | 62.0728 | -61.734 | -61.5372 | 54.3686 | 24.7055 | 8.8394 | 8.4869 | 62.114 | -61.6974 | -0.32959 | -0.050354 | 3.1769 | -0.13275 | -7.7545 | -0.29297 | -0.009155 | 3.5065 | 70.2438 | 69.8914 | 115.773 | 123.4772 | 3.1769 | 123.5184 | 86.1099 | -0.29297 | 123.4772 | 3.1769 | 86.1099 | 115.773 | 123.5184 | -123.8571 | -123.8205
4964.7188 | 123.8342 | -61.3861 | 62.1277 | -0.17677 | 0.01282 | 0.010423 | 0.0097562 | 0.058539 | -0.0016149 | 0.078835 | -58.2138 | 62.0682 | -61.7157 | -61.4914 | 54.4052 | 24.7009 | 8.8303 | 8.5281 | 62.0865 | -61.6928 | -0.32959 | -0.05951 | 3.1723 | -0.10529 | -7.7225 | -0.3067 | -0.041199 | 3.5019 | 70.2164 | 69.9142 | 115.7913 | 123.4543 | 3.1723 | 123.4726 | 86.087 | -0.3067 | 123.4543 | 3.1723 | 86.087 | 115.7913 | 123.4726 | -123.8434 | -123.8205
4965.7188 | 123.7885 | -61.4227 | 62.0865 | 0.13603 | 0.016024 | 0.011491 | 0.012747 | 0.058325 | 9.4068e-05 | 0.078835 | -58.2321 | 62.0316 | -61.7203 | -61.5646 | 54.3503 | 24.7009 | 8.7433 | 8.4274 | 62.0361 | -61.7111 | -0.29755 | -0.054932 | 3.1906 | -0.14191 | -7.7362 | -0.28839 | -0.050354 | 3.4882 | 70.166 | 69.8502 | 115.773 | 123.4543 | 3.1906 | 123.4589 | 86.1237 | -0.28839 | 123.4543 | 3.1906 | 86.1237 | 115.773 | 123.4589 | -123.8068 | -123.7976
4966.7188 | 123.7793 | -61.4182 | 62.0956 | 0.16655 | 0.01346 | 0.014054 | 0.011465 | 0.060248 | -0.0014013 | 0.079263 | -58.2413 | 62.0544 | -61.7294 | -61.5784 | 54.3091 | 24.6689 | 8.7433 | 8.4183 | 62.0636 | -61.7111 | -0.31128 | -0.041199 | 3.1769 | -0.16022 | -7.7866 | -0.29297 | -0.032043 | 3.4882 | 70.1614 | 69.8364 | 115.7272 | 123.4726 | 3.1769 | 123.4818 | 86.087 | -0.29297 | 123.4726 | 3.1769 | 86.087 | 115.7272 | 123.4818 | -123.8251 | -123.8068
4967.7188 | 123.793 | -61.4182 | 62.1094 | 0.082626 | 0.014315 | 0.011277 | 0.010183 | 0.058753 | -0.00054693 | 0.080544 | -58.2825 | 62.0499 | -61.7432 | -61.5921 | 54.3274 | 24.7513 | 8.7662 | 8.345 | 62.0773 | -61.7157 | -0.32501 | -0.059509 | 3.1357 | -0.17395 | -7.782 | -0.29755 | -0.032043 | 3.4607 | 70.1843 | 69.7632 | 115.7455 | 123.468 | 3.1357 | 123.4955 | 86.1694 | -0.29755 | 123.468 | 3.1357 | 86.1694 | 115.7455 | 123.4955 | -123.8525 | -123.8251
4968.7188 | 123.8297 | -61.4136 | 62.0682 | 0.31914 | 0.012392 | 0.010636 | 0.014242 | 0.059394 | -0.0016149 | 0.07969 | -58.2367 | 62.0636 | -61.7477 | -61.5463 | 54.3686 | 24.8383 | 8.6517 | 8.4091 | 62.0682 | -61.6928 | -0.33417 | -0.004577 | 3.1769 | -0.13275 | -7.6996 | -0.27924 | 0 | 3.511 | 70.0653 | 69.8227 | 115.7822 | 123.4772 | 3.1769 | 123.4818 | 86.2518 | -0.27924 | 123.4772 | 3.1769 | 86.2518 | 115.7822 | 123.4818 | -123.8159 | -123.761
4969.7188 | 123.8251 | -61.4044 | 62.114 | -0.077591 | 0.014529 | 0.010209 | 0.0093288 | 0.058112 | 0.0015893 | 0.079904 | -58.2413 | 62.059 | -61.702 | -61.528 | 54.3777 | 24.8108 | 8.7158 | 8.4641 | 62.0728 | -61.702 | -0.29755 | -0.054932 | 3.1631 | -0.1236 | -7.7362 | -0.29755 | -0.041199 | 3.4607 | 70.1202 | 69.8685 | 115.7822 | 123.4634 | 3.1631 | 123.4772 | 86.2152 | -0.29755 | 123.4634 | 3.1631 | 86.2152 | 115.7822 | 123.4772 | -123.8159 | -123.8159
4970.7188 | 123.7976 | -61.4273 | 62.0911 | 0.18944 | 0.01581 | 0.012345 | 0.013388 | 0.058753 | -0.0024695 | 0.077981 | -58.255 | 62.0499 | -61.7432 | -61.5875 | 54.3045 | 24.7513 | 8.6792 | 8.3908 | 62.0636 | -61.7386 | -0.31586 | -0.041198 | 3.1723 | -0.16022 | -7.7866 | -0.31128 | -0.027465 | 3.4882 | 70.1065 | 69.8181 | 115.7318 | 123.4772 | 3.1723 | 123.4909 | 86.1786 | -0.31128 | 123.4772 | 3.1723 | 86.1786 | 115.7318 | 123.4909 | -123.8342 | -123.8297
4971.7188 | 123.7976 | -61.4182 | 62.1002 | 0.1284 | 0.014101 | 0.011491 | 0.012747 | 0.057685 | -0.0011877 | 0.078408 | -58.2321 | 62.0682 | -61.7386 | -61.5829 | 54.3228 | 24.8062 | 8.6792 | 8.4091 | 62.059 | -61.7294 | -0.32043 | -0.032044 | 3.186 | -0.16479 | -7.7774 | -0.31128 | -0.041199 | 3.5065 | 70.0974 | 69.8273 | 115.741 | 123.4863 | 3.186 | 123.4772 | 86.2244 | -0.31128 | 123.4863 | 3.186 | 86.2244 | 115.741 | 123.4772 | -123.8388 | -123.8297
4972.7188 | 123.7747 | -61.409 | 62.114 | 0.03685 | 0.013033 | 0.0080728 | 0.0067654 | 0.056403 | -0.0011877 | 0.079263 | -58.2687 | 62.0361 | -61.7661 | -61.5555 | 54.4006 | 24.7971 | 8.7936 | 8.4 | 62.0682 | -61.6745 | -0.35706 | -0.07782 | 3.1403 | -0.14648 | -7.7133 | -0.2655 | -0.045777 | 3.4973 | 70.2026 | 69.809 | 115.8096 | 123.4451 | 3.1403 | 123.4772 | 86.2061 | -0.2655 | 123.4451 | 3.1403 | 86.2061 | 115.8096 | 123.4772 | -123.88 | -123.7885
4973.7188 | 123.8205 | -61.3815 | 62.0819 | 0.28862 | 0.015597 | 0.014054 | 0.013174 | 0.059821 | -0.00076053 | 0.077767 | -58.2138 | 62.0453 | -61.7477 | -61.5692 | 54.364 | 24.8795 | 8.6517 | 8.3038 | 62.0728 | -61.7157 | -0.36621 | -0.036621 | 3.1677 | -0.18768 | -7.7179 | -0.33417 | -0.009155 | 3.5339 | 70.0333 | 69.6854 | 115.7455 | 123.4268 | 3.1677 | 123.4543 | 86.261 | -0.33417 | 123.4268 | 3.1677 | 86.261 | 115.7455 | 123.4543 | -123.8297 | -123.7976
4974.7188 | 123.7793 | -61.4319 | 62.0956 | 0.13603 | 0.015383 | 0.010209 | 0.013388 | 0.060034 | -0.0020421 | 0.080758 | -58.2596 | 62.0499 | -61.7477 | -61.5829 | 54.3594 | 24.8428 | 8.67 | 8.2993 | 62.0544 | -61.7111 | -0.31586 | -0.045776 | 3.1723 | -0.15106 | -7.7362 | -0.27924 | -0.041199 | 3.4882 | 70.1019 | 69.7311 | 115.7913 | 123.4818 | 3.1723 | 123.4863 | 86.2747 | -0.27924 | 123.4818 | 3.1723 | 86.2747 | 115.7913 | 123.4863 | -123.8434 | -123.8068
4975.7188 | 123.8159 | -61.3998 | 62.059 | 0.21233 | 0.013888 | 0.012986 | 0.010611 | 0.058966 | -0.00054693 | 0.078408 | -58.1085 | 62.059 | -61.7523 | -61.5005 | 54.4327 | 24.8474 | 8.67 | 8.3817 | 62.0636 | -61.7157 | -0.35248 | 0 | 3.2913 | -0.10071 | -7.6263 | -0.31586 | 0.004578 | 3.6438 | 70.0699 | 69.7815 | 115.8325 | 123.4589 | 3.2913 | 123.4634 | 86.2473 | -0.31586 | 123.4589 | 3.2913 | 86.2473 | 115.8325 | 123.4634 | -123.8113 | -123.7747
4976.7188 | 123.8388 | -61.3998 | 62.0956 | 0.14366 | 0.014315 | 0.012559 | 0.014669 | 0.058539 | -0.0016149 | 0.079049 | -58.2092 | 62.0728 | -61.7386 | -61.5555 | 54.3777 | 24.7009 | 8.7753 | 8.5327 | 62.0636 | -61.7157 | -0.33874 | -0.022888 | 3.1906 | -0.15564 | -7.7179 | -0.31586 | -0.032043 | 3.5294 | 70.1752 | 69.9326 | 115.7776 | 123.4726 | 3.1906 | 123.4634 | 86.1008 | -0.31586 | 123.4726 | 3.1906 | 86.1008 | 115.7776 | 123.4634 | -123.8342 | -123.8113
4977.7188 | 123.8159 | -61.4136 | 62.1231 | -0.031814 | 0.013888 | 0.0080728 | 0.0091152 | 0.058325 | -0.0014013 | 0.080331 | -58.287 | 62.0682 | -61.7432 | -61.5738 | 54.4144 | 24.8016 | 8.7204 | 8.3496 | 62.1002 | -61.7111 | -0.32959 | -0.054932 | 3.1265 | -0.16022 | -7.7087 | -0.29755 | -0.022888 | 3.4561 | 70.134 | 69.7632 | 115.8279 | 123.4818 | 3.1265 | 123.5138 | 86.2152 | -0.29755 | 123.4818 | 3.1265 | 86.2152 | 115.8279 | 123.5138 | -123.8663 | -123.8342
4978.7188 | 123.8342 | -61.3953 | 62.0865 | -0.047073 | 0.01581 | 0.011704 | 0.010611 | 0.060889 | -0.0018285 | 0.080117 | -58.2321 | 62.0682 | -61.7294 | -61.5601 | 54.3915 | 24.7787 | 8.6517 | 8.3405 | 62.0544 | -61.7111 | -0.33417 | -0.018311 | 3.1631 | -0.1648 | -7.695 | -0.31586 | -0.032044 | 3.4973 | 70.047 | 69.7357 | 115.7867 | 123.4634 | 3.1631 | 123.4497 | 86.174 | -0.31586 | 123.4634 | 3.1631 | 86.174 | 115.7867 | 123.4497 | -123.8159 | -123.7976
4979.7188 | 123.8342 | -61.377 | 62.1094 | -0.09285 | 0.014529 | 0.0063638 | 0.0065518 | 0.058753 | -0.0026831 | 0.080117 | -58.2504 | 62.0636 | -61.7294 | -61.5509 | 54.4556 | 24.8062 | 8.6884 | 8.3725 | 62.0728 | -61.6791 | -0.35248 | -0.045776 | 3.1265 | -0.17395 | -7.6538 | -0.30212 | -0.036621 | 3.479 | 70.0653 | 69.7495 | 115.8325 | 123.4406 | 3.1265 | 123.4497 | 86.1832 | -0.30212 | 123.4406 | 3.1265 | 86.1832 | 115.8325 | 123.4497 | -123.8388 | -123.7885
4980.7188 | 123.8113 | -61.409 | 62.0956 | 0.2047 | 0.014956 | 0.013841 | 0.014029 | 0.059394 | -0.00097413 | 0.079904 | -58.1268 | 62.0819 | -61.7432 | -61.5097 | 54.4464 | 24.7467 | 8.638 | 8.3954 | 62.0636 | -61.7157 | -0.33417 | -0.013733 | 3.2822 | -0.10071 | -7.6492 | -0.3067 | -0.032043 | 3.6163 | 70.047 | 69.8044 | 115.8554 | 123.4909 | 3.2822 | 123.4726 | 86.1557 | -0.3067 | 123.4909 | 3.2822 | 86.1557 | 115.8554 | 123.4726 | -123.8388 | -123.8113
4981.7188 | 123.8113 | -61.3907 | 62.0956 | 0.14366 | 0.01282 | 0.0085 | 0.012747 | 0.058753 | -0.00033333 | 0.076486 | -58.2367 | 62.0499 | -61.7294 | -61.5738 | 54.3915 | 24.6826 | 8.6655 | 8.3496 | 62.0636 | -61.7065 | -0.33874 | -0.045776 | 3.154 | -0.18311 | -7.7042 | -0.31586 | -0.032043 | 3.4927 | 70.0562 | 69.7403 | 115.7822 | 123.4406 | 3.154 | 123.4543 | 86.0733 | -0.31586 | 123.4406 | 3.154 | 86.0733 | 115.7822 | 123.4543 | -123.8251 | -123.8022
4982.7188 | 123.8251 | -61.3953 | 62.1231 | -0.16914 | 0.013888 | 0.0097818 | 0.0097562 | 0.058753 | -0.0037511 | 0.078408 | -58.2367 | 62.0682 | -61.734 | -61.5189 | 54.4235 | 24.7192 | 8.7708 | 8.4549 | 62.0956 | -61.6745 | -0.33875 | -0.054932 | 3.1586 | -0.1236 | -7.6996 | -0.27924 | -0.027466 | 3.4973 | 70.166 | 69.8502 | 115.8188 | 123.4634 | 3.1586 | 123.4909 | 86.1145 | -0.27924 | 123.4634 | 3.1586 | 86.1145 | 115.8188 | 123.4909 | -123.8571 | -123.7976
4983.7188 | 123.8205 | -61.4319 | 62.1048 | 0.23521 | 0.015383 | 0.013413 | 0.014883 | 0.059394 | -0.00054693 | 0.078622 | -58.223 | 62.0956 | -61.7432 | -61.5646 | 54.4235 | 24.7513 | 8.6472 | 8.3679 | 62.0682 | -61.7249 | -0.31128 | -0.009155 | 3.2089 | -0.13275 | -7.6813 | -0.29297 | -0.036621 | 3.5202 | 70.079 | 69.7998 | 115.8554 | 123.5275 | 3.2089 | 123.5001 | 86.1832 | -0.29297 | 123.5275 | 3.2089 | 86.1832 | 115.8554 | 123.5001 | -123.848 | -123.8297
4984.7188 | 123.8434 | -61.3998 | 62.1002 | -0.031814 | 0.014101 | 0.011918 | 0.0084744 | 0.057898 | -0.0018285 | 0.078622 | -58.2642 | 62.0728 | -61.7386 | -61.5555 | 54.483 | 24.7925 | 8.7158 | 8.4457 | 62.0956 | -61.6837 | -0.33874 | -0.027466 | 3.1357 | -0.15564 | -7.6172 | -0.28381 | -0.004578 | 3.4744 | 70.1157 | 69.8456 | 115.8829 | 123.4726 | 3.1357 | 123.4955 | 86.1923 | -0.28381 | 123.4726 | 3.1357 | 86.1923 | 115.8829 | 123.4955 | -123.8388 | -123.7839
4985.7188 | 123.7976 | -61.3907 | 62.0911 | 0.2047 | 0.01581 | 0.0063638 | 0.014242 | 0.059821 | -0.00076053 | 0.077767 | -58.2321 | 62.0819 | -61.734 | -61.5646 | 54.4006 | 24.4629 | 8.6334 | 8.3771 | 62.0544 | -61.7157 | -0.34332 | -0.009155 | 3.1586 | -0.17395 | -7.6904 | -0.32501 | -0.036621 | 3.5019 | 70.0241 | 69.7678 | 115.7913 | 123.4726 | 3.1586 | 123.4451 | 85.8536 | -0.32501 | 123.4726 | 3.1586 | 85.8536 | 115.7913 | 123.4451 | -123.8251 | -123.8068
4986.7188 | 123.8434 | -61.3998 | 62.1277 | 0.92949 | 0.015597 | 0.0132 | 0.013174 | 0.060248 | -0.0022559 | 0.078835 | -58.2047 | 62.059 | -61.7157 | -61.528 | 54.4052 | 24.408 | 8.606 | 8.4229 | 62.0682 | -61.7294 | -0.31586 | -0.068665 | 3.1952 | -0.12817 | -7.7225 | -0.32959 | -0.05951 | 3.511 | 70.0058 | 69.8227 | 115.8051 | 123.4589 | 3.1952 | 123.468 | 85.8078 | -0.32959 | 123.4589 | 3.1952 | 85.8078 | 115.8051 | 123.468 | -123.8434 | -123.8571
4987.7344 | 123.7976 | -61.3953 | 62.1231 | -0.25307 | 0.014315 | 0.0082864 | 0.010397 | 0.057685 | 9.4068e-05 | 0.077767 | -58.2596 | 62.0911 | -61.7294 | -61.528 | 54.4373 | 24.5041 | 8.7708 | 8.4869 | 62.114 | -61.6562 | -0.33417 | -0.032044 | 3.1357 | -0.13275 | -7.6859 | -0.26093 | -0.009155 | 3.4698 | 70.166 | 69.8822 | 115.8325 | 123.4863 | 3.1357 | 123.5092 | 85.8994 | -0.26093 | 123.4863 | 3.1357 | 85.8994 | 115.8325 | 123.5092 | -123.8525 | -123.7793
4988.7188 | 123.8388 | -61.409 | 62.0819 | 0.15892 | 0.017092 | 0.013627 | 0.017447 | 0.061957 | -0.0028967 | 0.07969 | -58.255 | 62.0636 | -61.7432 | -61.4868 | 54.3457 | 24.4537 | 8.6746 | 8.4229 | 62.0819 | -61.7157 | -0.33417 | -0.01831 | 3.154 | -0.077819 | -7.7362 | -0.3067 | 0 | 3.4882 | 70.0836 | 69.8318 | 115.7547 | 123.4726 | 3.154 | 123.4909 | 85.8627 | -0.3067 | 123.4726 | 3.154 | 85.8627 | 115.7547 | 123.4909 | -123.8251 | -123.7976
4989.7344 | 123.7518 | -61.4044 | 62.1597 | -0.2607 | 0.013674 | 0.01555 | 0.013388 | 0.059394 | -0.00076053 | 0.078195 | -58.2687 | 62.0911 | -61.7249 | -61.5692 | 54.4418 | 24.4492 | 8.8943 | 8.4778 | 62.146 | -61.734 | -0.32044 | -0.068665 | 3.1357 | -0.1648 | -7.7179 | -0.32959 | -0.013733 | 3.4561 | 70.2988 | 69.8822 | 115.8463 | 123.4955 | 3.1357 | 123.5504 | 85.8536 | -0.32959 | 123.4955 | 3.1357 | 85.8536 | 115.8463 | 123.5504 | -123.8846 | -123.8937
4990.7188 | 123.8342 | -61.4044 | 62.114 | 0.19707 | 0.014315 | 0.017686 | 0.014883 | 0.060675 | -0.0022559 | 0.079263 | -58.255 | 62.0499 | -61.7294 | -61.5143 | 54.3182 | 24.2752 | 8.8623 | 8.5785 | 62.0819 | -61.7203 | -0.32501 | -0.064087 | 3.1494 | -0.10986 | -7.7957 | -0.31586 | -0.032044 | 3.4744 | 70.2667 | 69.9829 | 115.7227 | 123.4543 | 3.1494 | 123.4863 | 85.6796 | -0.31586 | 123.4543 | 3.1494 | 85.6796 | 115.7227 | 123.4863 | -123.8434 | -123.8342
4991.7188 | 123.8113 | -61.3998 | 62.0956 | 0.13603 | 0.017306 | 0.012345 | 0.013174 | 0.061103 | -0.00054693 | 0.079049 | -58.2458 | 62.0819 | -61.7157 | -61.5646 | 54.3961 | 24.4446 | 8.6884 | 8.4686 | 62.059 | -61.7157 | -0.31586 | -0.013733 | 3.154 | -0.16479 | -7.6996 | -0.31586 | -0.036621 | 3.4698 | 70.0882 | 69.8685 | 115.7959 | 123.4818 | 3.154 | 123.4589 | 85.8444 | -0.31586 | 123.4818 | 3.154 | 85.8444 | 115.7959 | 123.4589 | -123.8113 | -123.8113
4992.7344 | 123.7427 | -61.4319 | 62.114 | 0.013962 | 0.014742 | 0.013413 | 0.016806 | 0.061743 | -0.0018285 | 0.079904 | -58.2687 | 62.1643 | -61.7569 | -61.5784 | 54.3823 | 24.4995 | 8.8303 | 8.4229 | 62.114 | -61.7523 | -0.32501 | 0.050354 | 3.1631 | -0.14648 | -7.7316 | -0.32043 | 0 | 3.4882 | 70.2621 | 69.8547 | 115.8142 | 123.5962 | 3.1631 | 123.5458 | 85.9314 | -0.32043 | 123.5962 | 3.1631 | 85.9314 | 115.8142 | 123.5458 | -123.8709 | -123.8663
4993.7188 | 123.8388 | -61.4182 | 62.0544 | 0.15129 | 0.014315 | 0.013627 | 0.014456 | 0.061316 | -0.0014013 | 0.079904 | -58.2962 | 62.059 | -61.7477 | -61.5555 | 54.4098 | 24.5361 | 8.67 | 8.4869 | 62.0819 | -61.6791 | -0.32959 | 0.004578 | 3.1219 | -0.13733 | -7.6447 | -0.26093 | 0.027466 | 3.4515 | 70.0882 | 69.9051 | 115.8279 | 123.4772 | 3.1219 | 123.5001 | 85.9543 | -0.26093 | 123.4772 | 3.1219 | 85.9543 | 115.8279 | 123.5001 | -123.8022 | -123.7335
4994.7188 | 123.8617 | -61.3907 | 62.1048 | -0.069961 | 0.012392 | 0.0072184 | 0.0084744 | 0.057257 | -0.0022559 | 0.081826 | -58.2642 | 62.0728 | -61.7203 | -61.5509 | 54.4418 | 24.6048 | 8.7341 | 8.5602 | 62.114 | -61.6837 | -0.32959 | -0.032043 | 3.1265 | -0.16022 | -7.663 | -0.29297 | 0.009156 | 3.4561 | 70.1248 | 69.9509 | 115.8325 | 123.4634 | 3.1265 | 123.5046 | 85.9955 | -0.29297 | 123.4634 | 3.1265 | 85.9955 | 115.8325 | 123.5046 | -123.8251 | -123.7885
4995.7188 | 123.793 | -61.4273 | 62.1094 | 0.17418 | 0.013674 | 0.0132 | 0.011038 | 0.060034 | -0.0014013 | 0.080544 | -58.287 | 62.0499 | -61.7615 | -61.5967 | 54.3915 | 24.5178 | 8.6792 | 8.4686 | 62.0636 | -61.7203 | -0.33417 | -0.059509 | 3.1403 | -0.16937 | -7.7179 | -0.29297 | -0.045776 | 3.4744 | 70.1065 | 69.8959 | 115.8188 | 123.4772 | 3.1403 | 123.4909 | 85.9451 | -0.29297 | 123.4772 | 3.1403 | 85.9451 | 115.8188 | 123.4909 | -123.8708 | -123.8297
4996.7188 | 123.8159 | -61.4273 | 62.0911 | 0.19707 | 0.016238 | 0.0080728 | 0.011251 | 0.057898 | -0.0014013 | 0.079263 | -58.287 | 62.059 | -61.7523 | -61.6013 | 54.3869 | 24.5682 | 8.7112 | 8.4503 | 62.059 | -61.6974 | -0.32501 | -0.032043 | 3.1403 | -0.17395 | -7.7042 | -0.27008 | -0.032043 | 3.4653 | 70.1385 | 69.8776 | 115.8142 | 123.4863 | 3.1403 | 123.4863 | 85.9955 | -0.27008 | 123.4863 | 3.1403 | 85.9955 | 115.8142 | 123.4863 | -123.8434 | -123.7885
4997.7344 | 123.8342 | -61.4182 | 62.0911 | 0.24284 | 0.017092 | 0.01555 | 0.012533 | 0.05918 | -0.0014013 | 0.079904 | -58.2642 | 62.0636 | -61.7249 | -61.5601 | 54.4144 | 24.5636 | 8.7067 | 8.5007 | 62.059 | -61.7157 | -0.3067 | -0.027465 | 3.154 | -0.14191 | -7.6767 | -0.29755 | -0.032043 | 3.4607 | 70.1248 | 69.9188 | 115.8325 | 123.4818 | 3.154 | 123.4772 | 85.9818 | -0.29755 | 123.4818 | 3.154 | 85.9818 | 115.8325 | 123.4772 | -123.8159 | -123.8068
4998.7188 | 123.8159 | -61.4136 | 62.1048 | 0.15129 | 0.017306 | 0.014054 | 0.01232 | 0.058112 | -0.00076053 | 0.080972 | -58.2916 | 62.0499 | -61.7294 | -61.5829 | 54.3137 | 24.527 | 8.6609 | 8.4641 | 62.0499 | -61.7294 | -0.31586 | -0.054931 | 3.1219 | -0.16937 | -7.7911 | -0.31586 | -0.054931 | 3.4378 | 70.0745 | 69.8776 | 115.7272 | 123.4634 | 3.1219 | 123.4634 | 85.9406 | -0.31586 | 123.4634 | 3.1219 | 85.9406 | 115.7272 | 123.4634 | -123.8342 | -123.8342
4999.7344 | 123.674 | -61.409 | 62.2192 | -0.27596 | 0.013674 | 0.012559 | 0.016378 | 0.058539 | -0.00033333 | 0.077554 | -58.3099 | 62.1597 | -61.734 | -61.6104 | 54.332 | 24.3851 | 8.9539 | 8.3725 | 62.1231 | -61.7294 | -0.32501 | -0.059509 | 3.0991 | -0.20142 | -7.8873 | -0.32043 | -0.09613 | 3.4241 | 70.3629 | 69.7815 | 115.741 | 123.5687 | 3.0991 | 123.5321 | 85.7941 | -0.32043 | 123.5687 | 3.0991 | 85.7941 | 115.741 | 123.5321 | -123.9532 | -123.9487
5000.7188 | 123.8113 | -61.4227 | 62.1094 | 0.029221 | 0.01346 | 0.0085 | 0.0097562 | 0.057898 | -0.0014013 | 0.077981 | -58.1955 | 62.114 | -61.734 | -61.5784 | 54.3594 | 24.5041 | 8.7524 | 8.4137 | 62.0865 | -61.702 | -0.31128 | 0.004578 | 3.2272 | -0.15564 | -7.7499 | -0.27924 | -0.022888 | 3.5385 | 70.1752 | 69.8364 | 115.7822 | 123.5367 | 3.2272 | 123.5092 | 85.9268 | -0.27924 | 123.5367 | 3.2272 | 85.9268 | 115.7822 | 123.5092 | -123.8434 | -123.8113
5001.7188 | 123.8068 | -61.3907 | 62.1277 | -0.016556 | 0.012392 | 0.009141 | 0.010611 | 0.057257 | -0.0018285 | 0.079049 | -58.3282 | 62.0636 | -61.7157 | -61.5646 | 54.4006 | 24.5087 | 8.7158 | 8.4457 | 62.0544 | -61.6608 | -0.32501 | -0.064087 | 3.0624 | -0.17395 | -7.7271 | -0.27008 | -0.073243 | 3.3875 | 70.1065 | 69.8364 | 115.7913 | 123.4543 | 3.0624 | 123.4451 | 85.8994 | -0.27008 | 123.4543 | 3.0624 | 85.8994 | 115.7913 | 123.4451 | -123.8434 | -123.7885
5002.7344 | 123.8297 | -61.3998 | 62.1277 | -0.039444 | 0.013674 | 0.0087138 | 0.0080472 | 0.058966 | -0.00076053 | 0.080117 | -58.3099 | 62.0819 | -61.7157 | -61.5417 | 54.3915 | 24.5316 | 8.7296 | 8.4778 | 62.0728 | -61.6882 | -0.31586 | -0.045777 | 3.0899 | -0.14191 | -7.7362 | -0.28839 | -0.054932 | 3.4058 | 70.1294 | 69.8776 | 115.7913 | 123.4818 | 3.0899 | 123.4726 | 85.9314 | -0.28839 | 123.4818 | 3.0899 | 85.9314 | 115.7913 | 123.4726 | -123.8434 | -123.8159
5003.7188 | 123.793 | -61.4319 | 62.1323 | 0.13603 | 0.01282 | 0.0099954 | 0.010183 | 0.058753 | -0.0014013 | 0.077126 | -58.3237 | 62.0361 | -61.7249 | -61.6058 | 54.3182 | 24.5224 | 8.7433 | 8.4183 | 62.0544 | -61.6882 | -0.29297 | -0.09613 | 3.1082 | -0.17395 | -7.814 | -0.25635 | -0.07782 | 3.4012 | 70.1752 | 69.8502 | 115.7501 | 123.468 | 3.1082 | 123.4863 | 85.9543 | -0.25635 | 123.468 | 3.1082 | 85.9543 | 115.7501 | 123.4863 | -123.8571 | -123.8205
5004.7344 | 123.8342 | -61.3724 | 62.1368 | -0.21492 | 0.015597 | 0.011491 | 0.011251 | 0.057685 | -0.0056737 | 0.075204 | -58.2413 | 62.0911 | -61.702 | -61.2625 | 54.4006 | 24.3118 | 8.8028 | 8.5098 | 62.0911 | -61.6974 | -0.32959 | -0.045777 | 3.1311 | 0.10986 | -7.7362 | -0.32501 | -0.045777 | 3.4607 | 70.1752 | 69.8822 | 115.773 | 123.4634 | 3.1311 | 123.4634 | 85.6842 | -0.32501 | 123.4634 | 3.1311 | 85.6842 | 115.773 | 123.4634 | -123.8388 | -123.8342
5005.7188 | 123.8251 | -61.4182 | 62.1231 | -0.062332 | 0.013888 | 0.0099954 | 0.010183 | 0.058753 | 0.0026575 | 0.081185 | -58.3099 | 62.0682 | -61.7432 | -61.5784 | 54.3732 | 24.5453 | 8.7204 | 8.4457 | 62.0544 | -61.7157 | -0.32501 | -0.054932 | 3.1082 | -0.16022 | -7.7499 | -0.29755 | -0.068665 | 3.4332 | 70.1385 | 69.8639 | 115.7913 | 123.4863 | 3.1082 | 123.4726 | 85.9634 | -0.29755 | 123.4863 | 3.1082 | 85.9634 | 115.7913 | 123.4726 | -123.8663 | -123.8388
5006.7188 | 123.8022 | -61.409 | 62.1002 | 0.18944 | 0.014101 | 0.011277 | 0.012106 | 0.057898 | 0.00030767 | 0.079904 | -58.2916 | 62.0316 | -61.7569 | -61.5738 | 54.3823 | 24.5224 | 8.6609 | 8.4229 | 62.0636 | -61.7111 | -0.3479 | -0.068665 | 3.1174 | -0.16479 | -7.7179 | -0.30212 | -0.036621 | 3.4653 | 70.0699 | 69.8318 | 115.7913 | 123.4406 | 3.1174 | 123.4726 | 85.9314 | -0.30212 | 123.4406 | 3.1174 | 85.9314 | 115.7913 | 123.4726 | -123.8571 | -123.8113
5007.7344 | 123.793 | -61.4182 | 62.0773 | -0.031814 | 0.012606 | 0.010423 | 0.0063382 | 0.058112 | 0.00094847 | 0.078195 | -58.3328 | 62.0682 | -61.7294 | -61.5875 | 54.3732 | 24.5224 | 8.7982 | 8.6655 | 62.1185 | -61.6882 | -0.31128 | -0.009156 | 3.0853 | -0.16937 | -7.7042 | -0.27008 | 0.041198 | 3.3966 | 70.2164 | 70.0836 | 115.7913 | 123.4863 | 3.0853 | 123.5367 | 85.9406 | -0.27008 | 123.4863 | 3.0853 | 85.9406 | 115.7913 | 123.5367 | -123.8068 | -123.7656
5008.7188 | 123.8388 | -61.3953 | 62.1002 | -0.054703 | 0.014742 | 0.0099954 | 0.0080472 | 0.057471 | -0.00054693 | 0.076272 | -58.2916 | 62.0499 | -61.734 | -61.5417 | 54.3915 | 24.559 | 8.7799 | 8.5327 | 62.0773 | -61.6837 | -0.33875 | -0.050354 | 3.1036 | -0.14648 | -7.7087 | -0.28839 | -0.022888 | 3.4424 | 70.1752 | 69.928 | 115.7867 | 123.4451 | 3.1036 | 123.4726 | 85.9543 | -0.28839 | 123.4451 | 3.1036 | 85.9543 | 115.7867 | 123.4726 | -123.8342 | -123.7839
5009.7344 | 123.7518 | -61.4319 | 62.1185 | -0.22255 | 0.014315 | 0.015336 | 0.016165 | 0.058753 | 0.0018031 | 0.076913 | -58.255 | 62.1643 | -61.7386 | -61.5555 | 54.3182 | 24.527 | 8.8943 | 8.4595 | 62.1597 | -61.7477 | -0.3067 | 0.045777 | 3.1769 | -0.1236 | -7.8003 | -0.31586 | 0.041199 | 3.4836 | 70.3262 | 69.8914 | 115.7501 | 123.5962 | 3.1769 | 123.5916 | 85.9589 | -0.31586 | 123.5962 | 3.1769 | 85.9589 | 115.7501 | 123.5916 | -123.8571 | -123.8663
5010.7188 | 123.8342 | -61.4044 | 62.1231 | -0.08522 | 0.011751 | 0.0078592 | 0.0095424 | 0.059607 | 0.00052127 | 0.079904 | -58.2962 | 62.0819 | -61.7294 | -61.5463 | 54.3594 | 24.5132 | 8.7067 | 8.5052 | 62.1048 | -61.6699 | -0.32501 | -0.041199 | 3.1082 | -0.14191 | -7.7637 | -0.2655 | -0.018311 | 3.4332 | 70.1111 | 69.9097 | 115.7639 | 123.4863 | 3.1082 | 123.5092 | 85.9177 | -0.2655 | 123.4863 | 3.1082 | 85.9177 | 115.7639 | 123.5092 | -123.8525 | -123.793
5011.7188 | 123.7793 | -61.4136 | 62.114 | 0.1284 | 0.014101 | 0.015336 | 0.010824 | 0.058753 | -0.00033333 | 0.079049 | -58.3099 | 62.0499 | -61.7477 | -61.5967 | 54.3549 | 24.527 | 8.7296 | 8.4549 | 62.059 | -61.702 | -0.33417 | -0.064087 | 3.1036 | -0.18311 | -7.7591 | -0.28839 | -0.054932 | 3.4378 | 70.1431 | 69.8685 | 115.7684 | 123.4634 | 3.1036 | 123.4726 | 85.9406 | -0.28839 | 123.4634 | 3.1036 | 85.9406 | 115.7684 | 123.4726 | -123.8617 | -123.8159
5012.7344 | 123.8251 | -61.3998 | 62.1002 | 0.18944 | 0.01816 | 0.014909 | 0.014883 | 0.05918 | -0.0018285 | 0.078195 | -58.461 | 62.0224 | -61.7706 | -61.5784 | 54.3732 | 24.5911 | 8.6609 | 8.4686 | 62.0544 | -61.7203 | -0.37079 | -0.07782 | 2.9388 | -0.17853 | -7.7271 | -0.32043 | -0.045777 | 3.3096 | 70.0607 | 69.8685 | 115.773 | 123.4222 | 2.9388 | 123.4543 | 85.9909 | -0.32043 | 123.4222 | 2.9388 | 85.9909 | 115.773 | 123.4543 | -123.8708 | -123.8205
5013.7188 | 123.8113 | -61.3953 | 62.1002 | 0.04448 | 0.01282 | 0.011918 | 0.010611 | 0.058112 | -0.00076053 | 0.078195 | -58.3237 | 62.0499 | -61.7249 | -61.5555 | 54.4052 | 24.6002 | 8.7845 | 8.5327 | 62.1185 | -61.6974 | -0.32959 | -0.050354 | 3.0716 | -0.16022 | -7.695 | -0.30212 | 0.01831 | 3.4012 | 70.1797 | 69.928 | 115.8005 | 123.4451 | 3.0716 | 123.5138 | 85.9955 | -0.30212 | 123.4451 | 3.0716 | 85.9955 | 115.8005 | 123.5138 | -123.8251 | -123.7976
5014.7188 | 123.8022 | -61.377 | 62.1094 | -0.14626 | 0.013674 | 0.011918 | 0.0076198 | 0.057898 | 9.4068e-05 | 0.080972 | -58.255 | 62.0773 | -61.7111 | -61.7065 | 54.4785 | 24.7421 | 8.6609 | 8.5922 | 62.0636 | -61.6882 | -0.33417 | -0.032043 | 3.1219 | -0.32959 | -7.6309 | -0.31128 | -0.045776 | 3.4561 | 70.0378 | 69.9692 | 115.8554 | 123.4543 | 3.1219 | 123.4406 | 86.1191 | -0.31128 | 123.4543 | 3.1219 | 86.1191 | 115.8554 | 123.4406 | -123.8205 | -123.7976
5015.7188 | 123.7976 | -61.3861 | 62.1048 | -0.16151 | 0.010897 | 0.011277 | 0.008688 | 0.058539 | -0.00011953 | 0.076913 | -58.2184 | 62.0407 | -61.6928 | -61.322 | 54.808 | 24.8611 | 8.4274 | 8.5236 | 62.0819 | -61.6928 | -0.3067 | -0.064087 | 3.1677 | 0.064087 | -7.2968 | -0.3067 | -0.022888 | 3.4744 | 69.8135 | 69.9097 | 116.1942 | 123.4268 | 3.1677 | 123.468 | 86.2473 | -0.3067 | 123.4268 | 3.1677 | 86.2473 | 116.1942 | 123.468 | -123.7976 | -123.7976
5016.7188 | 123.7793 | -61.3907 | 62.1368 | -0.19966 | 0.011965 | 0.0132 | 0.0089016 | 0.05918 | -0.00097413 | 0.078195 | -58.2184 | 62.0682 | -61.7157 | -61.5005 | 54.4647 | 24.6231 | 8.9676 | 8.8852 | 62.1552 | -61.6379 | -0.32501 | -0.068665 | 3.1723 | -0.10986 | -7.6721 | -0.24719 | 0.01831 | 3.4973 | 70.3583 | 70.2759 | 115.8554 | 123.4589 | 3.1723 | 123.5458 | 86.0138 | -0.24719 | 123.4589 | 3.1723 | 86.0138 | 115.8554 | 123.5458 | -123.8525 | -123.7747
5017.7344 | 123.8113 | -61.4044 | 62.1048 | -0.0089264 | 0.010683 | 0.0085 | 0.010611 | 0.057044 | -0.00076053 | 0.077126 | -58.3054 | 62.0819 | -61.7386 | -61.5829 | 54.4235 | 24.5865 | 8.7753 | 8.4595 | 62.1002 | -61.6928 | -0.33417 | -0.022888 | 3.0991 | -0.17853 | -7.6813 | -0.28839 | -0.004577 | 3.4332 | 70.1797 | 69.8639 | 115.8279 | 123.4863 | 3.0991 | 123.5046 | 85.9909 | -0.28839 | 123.4863 | 3.0991 | 85.9909 | 115.8279 | 123.5046 | -123.8434 | -123.7976
5018.7344 | 123.8022 | -61.4365 | 62.0544 | 0.1284 | 0.01581 | 0.012773 | 0.016806 | 0.058753 | -0.00097413 | 0.07734 | -58.2321 | 62.0865 | -61.734 | -61.5509 | 54.4235 | 24.6735 | 8.6929 | 8.4595 | 62.0636 | -61.702 | -0.29755 | 0.032044 | 3.2043 | -0.11444 | -7.6309 | -0.2655 | 0.009156 | 3.5019 | 70.1294 | 69.8959 | 115.86 | 123.5229 | 3.2043 | 123.5001 | 86.1099 | -0.2655 | 123.5229 | 3.2043 | 86.1099 | 115.86 | 123.5001 | -123.7885 | -123.7564
5019.7188 | 123.8754 | -61.3907 | 62.1185 | -0.12337 | 0.014101 | 0.0082864 | 0.008688 | 0.057471 | -0.0011877 | 0.07734 | -58.2779 | 62.0682 | -61.7157 | -61.496 | 54.4739 | 25.0351 | 8.757 | 8.5602 | 62.0865 | -61.6653 | -0.32501 | -0.050354 | 3.1128 | -0.10529 | -7.6447 | -0.27466 | -0.032043 | 3.4378 | 70.1477 | 69.9509 | 115.8646 | 123.4589 | 3.1128 | 123.4772 | 86.4258 | -0.27466 | 123.4589 | 3.1128 | 86.4258 | 115.8646 | 123.4772 | -123.8342 | -123.7839
5020.7188 | 123.793 | -61.3953 | 62.1094 | 0.15892 | 0.013888 | 0.011918 | 0.011251 | 0.057471 | -0.0016149 | 0.077981 | -58.3603 | 62.0407 | -61.7569 | -61.5921 | 54.3869 | 24.8474 | 8.7708 | 8.4412 | 62.0819 | -61.7249 | -0.36163 | -0.068665 | 3.035 | -0.19684 | -7.7225 | -0.32959 | -0.027466 | 3.3966 | 70.166 | 69.8364 | 115.7822 | 123.436 | 3.035 | 123.4772 | 86.2427 | -0.32959 | 123.436 | 3.035 | 86.2427 | 115.7822 | 123.4772 | -123.8663 | -123.8342
5021.7188 | 123.793 | -61.409 | 62.1002 | -0.016556 | 0.017306 | 0.010209 | 0.008688 | 0.057685 | -0.0024695 | 0.078835 | -58.3237 | 62.059 | -61.7569 | -61.5509 | 54.4373 | 24.9985 | 8.8486 | 8.5419 | 62.0911 | -61.6928 | -0.3479 | -0.041199 | 3.0853 | -0.14191 | -7.663 | -0.28381 | -0.009156 | 3.4332 | 70.2576 | 69.9509 | 115.8463 | 123.468 | 3.0853 | 123.5001 | 86.4075 | -0.28381 | 123.468 | 3.0853 | 86.4075 | 115.8463 | 123.5001 | -123.8571 | -123.793
5022.7188 | 123.8251 | -61.4273 | 62.1094 | 0.029221 | 0.014956 | 0.0070048 | 0.0095424 | 0.058112 | 0.00030767 | 0.075631 | -58.374 | 62.0636 | -61.7523 | -61.4456 | 54.5334 | 24.9619 | 8.8028 | 8.5281 | 62.0773 | -61.6882 | -0.32501 | -0.045776 | 3.0533 | -0.018311 | -7.576 | -0.26093 | -0.032043 | 3.3783 | 70.2301 | 69.9554 | 115.9607 | 123.4909 | 3.0533 | 123.5046 | 86.3892 | -0.26093 | 123.4909 | 3.0533 | 86.3892 | 115.9607 | 123.5046 | -123.8617 | -123.7976
5023.7188 | 123.8342 | -61.3907 | 62.1094 | -0.0012969 | 0.01282 | 0.010209 | 0.010183 | 0.057898 | -0.0018285 | 0.07734 | -58.342 | 62.0544 | -61.7386 | -61.5921 | 54.3182 | 24.9619 | 9.0225 | 8.638 | 62.1002 | -61.6974 | -0.3479 | -0.054932 | 3.0487 | -0.20142 | -7.7911 | -0.3067 | -0.009155 | 3.3966 | 70.4132 | 70.0287 | 115.7089 | 123.4451 | 3.0487 | 123.4909 | 86.3525 | -0.3067 | 123.4451 | 3.0487 | 86.3525 | 115.7089 | 123.4909 | -123.848 | -123.8068
5024.7188 | 123.7656 | -61.4136 | 62.0865 | 0.18944 | 0.013888 | 0.010423 | 0.010183 | 0.059607 | 0.00030767 | 0.080544 | -58.3374 | 62.0178 | -61.7432 | -61.5829 | 54.3228 | 24.9619 | 8.7753 | 8.5144 | 62.0865 | -61.7203 | -0.32959 | -0.068665 | 3.0762 | -0.16937 | -7.7637 | -0.3067 | 0 | 3.4058 | 70.1889 | 69.928 | 115.7364 | 123.4314 | 3.0762 | 123.5001 | 86.3754 | -0.3067 | 123.4314 | 3.0762 | 86.3754 | 115.7364 | 123.5001 | -123.8297 | -123.8068
5025.7188 | 123.8068 | -61.3815 | 62.1094 | 0.052109 | 0.013888 | 0.0080728 | 0.0089016 | 0.057685 | -0.00033333 | 0.079263 | -58.3511 | 62.0544 | -61.7477 | -61.5921 | 54.3365 | 24.9893 | 8.8486 | 8.5464 | 62.0819 | -61.6882 | -0.36621 | -0.054932 | 3.0304 | -0.21057 | -7.7728 | -0.3067 | -0.027466 | 3.3966 | 70.2301 | 69.928 | 115.7181 | 123.436 | 3.0304 | 123.4634 | 86.3709 | -0.3067 | 123.436 | 3.0304 | 86.3709 | 115.7181 | 123.4634 | -123.8571 | -123.7976
5026.7188 | 123.7976 | -61.3403 | 62.1048 | -0.13863 | 0.014101 | 0.0082864 | 0.0093288 | 0.058753 | -0.00054693 | 0.079476 | -58.2642 | 62.0407 | -61.6928 | -61.4868 | 54.4464 | 25.09 | 8.7799 | 8.6151 | 62.0819 | -61.6699 | -0.35248 | -0.064087 | 3.0762 | -0.14648 | -7.6584 | -0.32959 | -0.022888 | 3.4287 | 70.1202 | 69.9554 | 115.7867 | 123.381 | 3.0762 | 123.4222 | 86.4304 | -0.32959 | 123.381 | 3.0762 | 86.4304 | 115.7867 | 123.4222 | -123.7976 | -123.7747
5027.7188 | 123.8068 | -61.4227 | 62.1323 | 0.15892 | 0.014529 | 0.009141 | 0.0089016 | 0.057685 | -0.00076053 | 0.076913 | -58.3511 | 62.0636 | -61.7432 | -61.5692 | 54.4052 | 24.9664 | 8.8394 | 8.5602 | 62.0911 | -61.6928 | -0.32044 | -0.068664 | 3.0716 | -0.14649 | -7.7271 | -0.27008 | -0.041199 | 3.392 | 70.2621 | 69.9829 | 115.8279 | 123.4863 | 3.0716 | 123.5138 | 86.3892 | -0.27008 | 123.4863 | 3.0716 | 86.3892 | 115.8279 | 123.5138 | -123.8754 | -123.8251
5028.7344 | 123.7061 | -61.4273 | 62.1414 | -0.17677 | 0.01581 | 0.014482 | 0.015951 | 0.059394 | -0.00054693 | 0.079263 | -58.3191 | 62.1552 | -61.7111 | -61.6058 | 54.3274 | 24.8428 | 8.9767 | 8.5007 | 62.1231 | -61.7523 | -0.28381 | 0.013733 | 3.1082 | -0.17853 | -7.814 | -0.32501 | -0.01831 | 3.392 | 70.4041 | 69.928 | 115.7547 | 123.5825 | 3.1082 | 123.5504 | 86.2701 | -0.32501 | 123.5825 | 3.1082 | 86.2701 | 115.7547 | 123.5504 | -123.8525 | -123.8937
5029.7188 | 123.8251 | -61.409 | 62.1368 | -0.039444 | 0.013247 | 0.0087138 | 0.0091152 | 0.058753 | -0.0020421 | 0.077981 | -58.3008 | 62.0728 | -61.7294 | -61.5601 | 54.4006 | 24.9573 | 8.8303 | 8.5693 | 62.0865 | -61.6608 | -0.32043 | -0.064087 | 3.1082 | -0.15106 | -7.7362 | -0.25177 | -0.050354 | 3.4286 | 70.2393 | 69.9783 | 115.8096 | 123.4818 | 3.1082 | 123.4955 | 86.3663 | -0.25177 | 123.4818 | 3.1082 | 86.3663 | 115.8096 | 123.4955 | -123.8663 | -123.7976
5030.7188 | 123.8388 | -61.3815 | 62.1231 | -1.2296 | 0.013247 | 0.014695 | 0.011038 | 0.057898 | -0.0011877 | 0.079263 | -58.3511 | 62.0728 | -61.7111 | -61.5051 | 54.4189 | 24.7513 | 8.7341 | 8.519 | 62.0911 | -61.6608 | -0.32959 | -0.050354 | 3.0304 | -0.1236 | -7.7042 | -0.27924 | -0.032044 | 3.36 | 70.1157 | 69.9005 | 115.8005 | 123.4543 | 3.0304 | 123.4726 | 86.1328 | -0.27924 | 123.4543 | 3.0304 | 86.1328 | 115.8005 | 123.4726 | -123.8342 | -123.7839
5031.7188 | 123.8663 | -61.377 | 62.1231 | -0.10811 | 0.015383 | 0.010209 | 0.010183 | 0.05448 | -0.00054693 | 0.07969 | -58.287 | 62.0819 | -61.7294 | -61.4914 | 54.4464 | 24.7421 | 8.6838 | 8.4824 | 62.0728 | -61.6608 | -0.35248 | -0.041199 | 3.0899 | -0.11444 | -7.6767 | -0.28381 | -0.050354 | 3.4424 | 70.0607 | 69.8593 | 115.8234 | 123.4589 | 3.0899 | 123.4497 | 86.1191 | -0.28381 | 123.4589 | 3.0899 | 86.1191 | 115.8234 | 123.4497 | -123.8525 | -123.7839
5032.7188 | 123.7976 | -61.3998 | 62.1368 | 0.0063326 | 0.012179 | 0.006791 | 0.0097562 | 0.057471 | -0.00054693 | 0.077126 | -58.342 | 62.0682 | -61.7432 | -61.5646 | 54.3869 | 24.7284 | 8.7479 | 8.4778 | 62.0956 | -61.6791 | -0.34332 | -0.068665 | 3.0579 | -0.16479 | -7.7499 | -0.27924 | -0.041199 | 3.4012 | 70.1477 | 69.8776 | 115.7867 | 123.468 | 3.0579 | 123.4955 | 86.1282 | -0.27924 | 123.468 | 3.0579 | 86.1282 | 115.7867 | 123.4955 | -123.88 | -123.8159
5033.7188 | 123.8342 | -61.3998 | 62.1231 | -0.19966 | 0.012392 | 0.012132 | 0.0097562 | 0.057044 | -0.00033333 | 0.073281 | -58.2367 | 62.0682 | -61.7294 | -61.2213 | 54.6982 | 24.6048 | 8.5876 | 8.6517 | 62.0819 | -61.6699 | -0.32959 | -0.054932 | 3.1631 | 0.17853 | -7.4249 | -0.27008 | -0.041199 | 3.4927 | 69.9875 | 70.0516 | 116.098 | 123.468 | 3.1631 | 123.4818 | 86.0046 | -0.27008 | 123.468 | 3.1631 | 86.0046 | 116.098 | 123.4818 | -123.8525 | -123.793
5034.7344 | 123.7701 | -61.4319 | 62.1735 | -0.19966 | 0.015383 | 0.012986 | 0.018087 | 0.061316 | 0.0013757 | 0.077126 | -58.2733 | 62.1735 | -61.734 | -61.5509 | 54.3137 | 24.7192 | 8.8486 | 8.4732 | 62.1231 | -61.7249 | -0.30212 | 0 | 3.1586 | -0.11902 | -7.8598 | -0.29297 | -0.050354 | 3.4607 | 70.2805 | 69.9051 | 115.7455 | 123.6053 | 3.1586 | 123.555 | 86.1511 | -0.29297 | 123.6053 | 3.1586 | 86.1511 | 115.7455 | 123.555 | -123.9075 | -123.8983
5035.7188 | 123.7793 | -61.3907 | 62.1094 | -0.054703 | 0.01346 | 0.012345 | 0.0078336 | 0.061316 | -0.00076053 | 0.079263 | -58.3649 | 62.0636 | -61.7294 | -61.5829 | 54.3365 | 24.7147 | 8.812 | 8.5373 | 62.1002 | -61.6928 | -0.33874 | -0.045776 | 3.0258 | -0.19226 | -7.7728 | -0.30212 | -0.009155 | 3.3646 | 70.2026 | 69.928 | 115.7272 | 123.4543 | 3.0258 | 123.4909 | 86.1053 | -0.30212 | 123.4543 | 3.0258 | 86.1053 | 115.7272 | 123.4909 | -123.8388 | -123.8022
5036.7188 | 123.793 | -61.409 | 62.114 | -0.0012969 | 0.011324 | 0.0050822 | 0.005911 | 0.057471 | -0.00011953 | 0.077981 | -58.3466 | 62.0453 | -61.7523 | -61.5921 | 54.3869 | 24.7284 | 8.8348 | 8.5098 | 62.0682 | -61.7111 | -0.34332 | -0.068665 | 3.0624 | -0.1831 | -7.7271 | -0.30212 | -0.045777 | 3.4058 | 70.2438 | 69.9188 | 115.7959 | 123.4543 | 3.0624 | 123.4772 | 86.1374 | -0.30212 | 123.4543 | 3.0624 | 86.1374 | 115.7959 | 123.4772 | -123.8663 | -123.8251
5037.7344 | 123.7473 | -61.4182 | 62.1506 | -0.047073 | 0.016451 | 0.011491 | 0.020437 | 0.059821 | 0.0037257 | 0.079476 | -58.2596 | 62.1735 | -61.7294 | -61.6562 | 54.483 | 24.7055 | 8.8577 | 8.5144 | 62.1277 | -61.7477 | -0.31128 | 0.022888 | 3.1586 | -0.23804 | -7.6675 | -0.32959 | -0.022888 | 3.4698 | 70.2759 | 69.9326 | 115.9012 | 123.5916 | 3.1586 | 123.5458 | 86.1237 | -0.32959 | 123.5916 | 3.1586 | 86.1237 | 115.9012 | 123.5458 | -123.88 | -123.8983
5038.7188 | 123.848 | -61.3724 | 62.1094 | -0.10048 | 0.014315 | 0.015336 | 0.0082608 | 0.059607 | -0.0018285 | 0.078408 | -58.2962 | 62.0544 | -61.7569 | -61.5005 | 54.4693 | 24.8245 | 8.7616 | 8.6014 | 62.0865 | -61.6608 | -0.38452 | -0.054932 | 3.0762 | -0.12817 | -7.6401 | -0.28839 | -0.022888 | 3.4607 | 70.134 | 69.9738 | 115.8417 | 123.4268 | 3.0762 | 123.4589 | 86.1969 | -0.28839 | 123.4268 | 3.0762 | 86.1969 | 115.8417 | 123.4589 | -123.8663 | -123.7701
5039.7344 | 123.7061 | -61.441 | 62.1597 | -0.29884 | 0.015169 | 0.011704 | 0.016592 | 0.058325 | -0.0026831 | 0.077554 | -58.3282 | 62.178 | -61.7523 | -61.615 | 54.3045 | 24.5728 | 8.9401 | 8.4503 | 62.1231 | -61.734 | -0.31128 | 0.018311 | 3.1128 | -0.17395 | -7.8552 | -0.29297 | -0.036621 | 3.4241 | 70.3812 | 69.8914 | 115.7455 | 123.6191 | 3.1128 | 123.5641 | 86.0138 | -0.29297 | 123.6191 | 3.1128 | 86.0138 | 115.7455 | 123.5641 | -123.912 | -123.8937
5040.7344 | 123.7381 | -61.4319 | 62.1552 | -0.30647 | 0.015597 | 0.014054 | 0.014883 | 0.060034 | -0.0016149 | 0.078408 | -58.3282 | 62.1735 | -61.7569 | -61.6287 | 54.3686 | 24.5911 | 8.9035 | 8.4641 | 62.146 | -61.702 | -0.32501 | 0.018311 | 3.1036 | -0.19684 | -7.7866 | -0.27008 | -0.009155 | 3.4287 | 70.3354 | 69.8959 | 115.8005 | 123.6053 | 3.1036 | 123.5779 | 86.0229 | -0.27008 | 123.6053 | 3.1036 | 86.0229 | 115.8005 | 123.5779 | -123.912 | -123.8571
5041.7188 | 123.8022 | -61.409 | 62.114 | -0.047073 | 0.012179 | 0.0095682 | 0.010183 | 0.058539 | -0.0011877 | 0.078622 | -58.3328 | 62.0682 | -61.7386 | -61.5601 | 54.4281 | 24.559 | 8.7662 | 8.5556 | 62.0911 | -61.7065 | -0.32959 | -0.045777 | 3.0762 | -0.15106 | -7.6859 | -0.29755 | -0.022889 | 3.4058 | 70.1752 | 69.9646 | 115.8371 | 123.4772 | 3.0762 | 123.5001 | 85.968 | -0.29755 | 123.4772 | 3.0762 | 85.968 | 115.8371 | 123.5001 | -123.8525 | -123.8205
5042.7188 | 123.8388 | -61.3953 | 62.1277 | -2.7479 | 0.01346 | 0.0080728 | 0.01232 | 0.059821 | -0.0011877 | 0.077554 | -58.1863 | 62.1185 | -61.6974 | -61.5143 | 54.4739 | 24.7375 | 8.8165 | 8.6014 | 62.0682 | -61.6516 | -0.30212 | -0.009156 | 3.2089 | -0.11902 | -7.6538 | -0.25635 | -0.05951 | 3.511 | 70.2118 | 69.9966 | 115.8691 | 123.5138 | 3.2089 | 123.4634 | 86.1328 | -0.25635 | 123.5138 | 3.2089 | 86.1328 | 115.8691 | 123.4634 | -123.8251 | -123.7793
5043.7344 | 123.7015 | -61.4548 | 62.1506 | -0.64217 | 0.014101 | 0.009141 | 0.014242 | 0.059607 | -0.0024695 | 0.077981 | -58.4015 | 62.1826 | -61.7569 | -61.6058 | 54.4144 | 24.6323 | 8.9722 | 8.4549 | 62.146 | -61.7203 | -0.30212 | 0.032043 | 3.0533 | -0.15106 | -7.7362 | -0.2655 | -0.004578 | 3.3554 | 70.4269 | 69.9097 | 115.8691 | 123.6374 | 3.0533 | 123.6008 | 86.087 | -0.2655 | 123.6374 | 3.0533 | 86.087 | 115.8691 | 123.6008 | -123.9075 | -123.8708
5044.7344 | 123.7015 | -61.4365 | 62.146 | -0.0089264 | 0.018587 | 0.012345 | 0.019583 | 0.061103 | -0.0018285 | 0.078835 | -58.342 | 62.1735 | -61.734 | -61.647 | 54.4006 | 24.646 | 8.8806 | 8.4137 | 62.114 | -61.7386 | -0.29755 | 0.027466 | 3.0945 | -0.21057 | -7.7454 | -0.30212 | -0.032043 | 3.392 | 70.3171 | 69.8502 | 115.8371 | 123.6099 | 3.0945 | 123.5504 | 86.0825 | -0.30212 | 123.6099 | 3.0945 | 86.0825 | 115.8371 | 123.5504 | -123.88 | -123.8846
5045.7188 | 123.8709 | -61.3998 | 62.0956 | -0.039444 | 0.013674 | 0.010423 | 0.0065518 | 0.060889 | -0.0014013 | 0.079476 | -58.3054 | 62.0773 | -61.7249 | -61.5463 | 54.5105 | 24.5499 | 8.7845 | 8.6197 | 62.0819 | -61.6882 | -0.32501 | -0.01831 | 3.0945 | -0.14648 | -7.5851 | -0.28839 | -0.013733 | 3.4195 | 70.1843 | 70.0195 | 115.9103 | 123.4772 | 3.0945 | 123.4818 | 85.9497 | -0.28839 | 123.4772 | 3.0945 | 85.9497 | 115.9103 | 123.4818 | -123.8205 | -123.7839
5046.7344 | 123.7061 | -61.4365 | 62.1643 | -0.12337 | 0.015169 | 0.011491 | 0.015738 | 0.056403 | -0.00054693 | 0.078622 | -58.4885 | 62.1552 | -61.7615 | -61.6333 | 54.4373 | 24.4492 | 8.9218 | 8.4641 | 62.1414 | -61.7706 | -0.32501 | -0.009156 | 2.948 | -0.19684 | -7.7271 | -0.33417 | -0.022889 | 3.273 | 70.3583 | 69.9005 | 115.8737 | 123.5916 | 2.948 | 123.5779 | 85.8856 | -0.33417 | 123.5916 | 2.948 | 85.8856 | 115.8737 | 123.5779 | -123.9258 | -123.9349
5047.7188 | 123.8159 | -61.4136 | 62.114 | -0.016556 | 0.014529 | 0.01085 | 0.0080472 | 0.05918 | -0.00033333 | 0.079904 | -58.3511 | 62.0773 | -61.7569 | -61.6013 | 54.4647 | 24.5316 | 8.7341 | 8.5602 | 62.1185 | -61.6791 | -0.34332 | -0.036621 | 3.0624 | -0.18768 | -7.6492 | -0.2655 | 0.004577 | 3.4058 | 70.1477 | 69.9738 | 115.8783 | 123.4909 | 3.0624 | 123.5321 | 85.9451 | -0.2655 | 123.4909 | 3.0624 | 85.9451 | 115.8783 | 123.5321 | -123.8709 | -123.793
5048.7188 | 123.7701 | -61.3907 | 62.1094 | -0.1844 | 0.01282 | 0.012345 | 0.0097562 | 0.058112 | -0.00054693 | 0.080331 | -58.2596 | 62.0407 | -61.7065 | -61.5097 | 54.8859 | 24.8749 | 8.3908 | 8.5464 | 62.0865 | -61.6699 | -0.31586 | -0.068665 | 3.1311 | -0.11902 | -7.2235 | -0.27924 | -0.022888 | 3.447 | 69.7815 | 69.9371 | 116.2766 | 123.4314 | 3.1311 | 123.4772 | 86.2656 | -0.27924 | 123.4314 | 3.1311 | 86.2656 | 116.2766 | 123.4772 | -123.8159 | -123.7793
5049.7344 | 123.7244 | -61.4273 | 62.1277 | 0.03685 | 0.017306 | 0.012773 | 0.020224 | 0.061957 | -0.00097413 | 0.078835 | -58.3008 | 62.1918 | -61.7386 | -61.6287 | 54.3777 | 24.4995 | 8.9172 | 8.5007 | 62.0956 | -61.7615 | -0.31128 | 0.064086 | 3.1265 | -0.20142 | -7.7499 | -0.33417 | -0.032044 | 3.4378 | 70.3445 | 69.928 | 115.8051 | 123.6191 | 3.1265 | 123.5229 | 85.9268 | -0.33417 | 123.6191 | 3.1265 | 85.9268 | 115.8051 | 123.5229 | -123.8663 | -123.8892
5050.7188 | 123.8159 | -61.4227 | 62.0773 | 0.029221 | 0.013888 | 0.01085 | 0.0097562 | 0.060889 | -0.00011953 | 0.079476 | -58.3694 | 62.0682 | -61.7477 | -61.5829 | 54.4373 | 24.4858 | 8.8303 | 8.5785 | 62.0819 | -61.7111 | -0.32501 | -0.009156 | 3.0533 | -0.16022 | -7.6401 | -0.28839 | 0.004577 | 3.3783 | 70.253 | 70.0012 | 115.86 | 123.4909 | 3.0533 | 123.5046 | 85.9085 | -0.28839 | 123.4909 | 3.0533 | 85.9085 | 115.86 | 123.5046 | -123.8251 | -123.7885
5051.7188 | 123.8068 | -61.3861 | 62.1231 | -0.2607 | 0.013247 | 0.0070048 | 0.010611 | 0.057044 | -0.0035375 | 0.079476 | -58.2779 | 62.0636 | -61.7249 | -61.5189 | 54.4785 | 24.6277 | 8.8486 | 8.638 | 62.0819 | -61.6882 | -0.33875 | -0.059509 | 3.1082 | -0.13275 | -7.6447 | -0.30212 | -0.041199 | 3.447 | 70.2347 | 70.0241 | 115.8646 | 123.4497 | 3.1082 | 123.468 | 86.0138 | -0.30212 | 123.4497 | 3.1082 | 86.0138 | 115.8646 | 123.468 | -123.848 | -123.8113
5052.7344 | 123.7289 | -61.409 | 62.1689 | -0.19203 | 0.015597 | 0.0089274 | 0.01766 | 0.057898 | -0.0011877 | 0.078622 | -58.342 | 62.1689 | -61.7661 | -61.6241 | 54.4052 | 24.5132 | 9.0134 | 8.5464 | 62.1552 | -61.7432 | -0.35706 | 0 | 3.067 | -0.21515 | -7.7637 | -0.33417 | -0.013733 | 3.4241 | 70.4224 | 69.9554 | 115.8142 | 123.5779 | 3.067 | 123.5641 | 85.9222 | -0.33417 | 123.5779 | 3.067 | 85.9222 | 115.8142 | 123.5641 | -123.9349 | -123.912
5053.7188 | 123.8068 | -61.3678 | 62.146 | -0.16914 | 0.011751 | 0.010423 | 0.011038 | 0.058966 | -0.0043921 | 0.078622 | -58.2825 | 62.0773 | -61.734 | -61.5097 | 54.5242 | 24.6368 | 8.8074 | 8.5831 | 62.1002 | -61.6516 | -0.36621 | -0.068664 | 3.0853 | -0.14191 | -7.6218 | -0.28381 | -0.045776 | 3.4515 | 70.1752 | 69.9509 | 115.892 | 123.4451 | 3.0853 | 123.468 | 86.0046 | -0.28381 | 123.4451 | 3.0853 | 86.0046 | 115.892 | 123.468 | -123.88 | -123.7976
5054.7188 | 123.7244 | -61.4365 | 62.1643 | -0.27596 | 0.012392 | 0.0078592 | 0.015097 | 0.058966 | -0.0039649 | 0.080117 | -58.3649 | 62.146 | -61.7752 | -61.6196 | 54.3777 | 24.5087 | 8.9813 | 8.5144 | 62.1597 | -61.7157 | -0.33875 | -0.018311 | 3.0716 | -0.18311 | -7.7866 | -0.27924 | -0.004578 | 3.4103 | 70.4178 | 69.9509 | 115.8142 | 123.5825 | 3.0716 | 123.5962 | 85.9451 | -0.27924 | 123.5825 | 3.0716 | 85.9451 | 115.8142 | 123.5962 | -123.9395 | -123.88
5055.7344 | 123.7152 | -61.4273 | 62.1094 | -0.15388 | 0.017306 | 0.013413 | 0.017874 | 0.064948 | -0.0011877 | 0.077767 | -58.2916 | 62.1689 | -61.7386 | -61.5646 | 54.4189 | 24.5316 | 8.8394 | 8.5007 | 62.1506 | -61.7477 | -0.31128 | 0.059509 | 3.1357 | -0.13733 | -7.6904 | -0.32044 | 0.041199 | 3.447 | 70.2667 | 69.928 | 115.8463 | 123.5962 | 3.1357 | 123.5779 | 85.9589 | -0.32044 | 123.5962 | 3.1357 | 85.9589 | 115.8463 | 123.5779 | -123.848 | -123.8571
5056.7188 | 123.8297 | -61.4136 | 62.1185 | -0.12337 | 0.01346 | 0.0085 | 0.0071926 | 0.059821 | 9.4068e-05 | 0.077981 | -58.2916 | 62.0544 | -61.7386 | -61.5326 | 54.4739 | 24.5819 | 8.7204 | 8.5922 | 62.0911 | -61.6699 | -0.32501 | -0.064087 | 3.1219 | -0.11902 | -7.6447 | -0.25635 | -0.027466 | 3.447 | 70.134 | 70.0058 | 115.8875 | 123.468 | 3.1219 | 123.5046 | 85.9955 | -0.25635 | 123.468 | 3.1219 | 85.9955 | 115.8875 | 123.5046 | -123.8571 | -123.7885
5057.7188 | 123.8022 | -61.3724 | 62.1185 | -0.20729 | 0.01282 | 0.0078592 | 0.0061246 | 0.059394 | -0.0011877 | 0.077554 | -58.2825 | 62.0956 | -61.7157 | -61.5372 | 54.5425 | 24.884 | 8.8348 | 8.7204 | 62.0728 | -61.6928 | -0.34332 | -0.022888 | 3.0899 | -0.1648 | -7.576 | -0.32044 | -0.045776 | 3.4332 | 70.2072 | 70.0928 | 115.9149 | 123.468 | 3.0899 | 123.4451 | 86.2564 | -0.32044 | 123.468 | 3.0899 | 86.2564 | 115.9149 | 123.4451 | -123.8342 | -123.8113
5058.7188 | 123.7106 | -61.4365 | 62.1689 | -0.27596 | 0.013247 | 0.0087138 | 0.014883 | 0.058539 | -0.0020421 | 0.076272 | -58.3466 | 62.114 | -61.7294 | -61.6013 | 54.3777 | 24.8474 | 8.9767 | 8.5327 | 62.1323 | -61.7157 | -0.29297 | -0.054931 | 3.0899 | -0.16479 | -7.7911 | -0.27924 | -0.036621 | 3.3829 | 70.4132 | 69.9692 | 115.8142 | 123.5504 | 3.0899 | 123.5687 | 86.2839 | -0.27924 | 123.5504 | 3.0899 | 86.2839 | 115.8142 | 123.5687 | -123.8983 | -123.8846
5059.7188 | 123.8434 | -61.3815 | 62.1185 | -0.039444 | 0.01282 | 0.011064 | 0.0076198 | 0.057044 | -0.0018285 | 0.080544 | -58.342 | 62.059 | -61.7249 | -61.5417 | 54.4693 | 24.9756 | 8.7387 | 8.6014 | 62.0819 | -61.6928 | -0.34332 | -0.059509 | 3.0396 | -0.16022 | -7.6492 | -0.31128 | -0.036621 | 3.3829 | 70.1202 | 69.9829 | 115.8508 | 123.4406 | 3.0396 | 123.4634 | 86.3571 | -0.31128 | 123.4406 | 3.0396 | 86.3571 | 115.8508 | 123.4634 | -123.8434 | -123.8113
5060.7188 | 123.7152 | -61.3861 | 62.1277 | -0.19966 | 0.010683 | 0.011491 | 0.011679 | 0.058112 | -0.0020421 | 0.078195 | -58.2687 | 62.0819 | -61.6928 | -61.5372 | 54.5105 | 25.1312 | 8.7387 | 8.9676 | 62.178 | -61.6699 | -0.3067 | -0.045777 | 3.1174 | -0.15106 | -7.6172 | -0.28381 | 0.050354 | 3.4241 | 70.1248 | 70.3537 | 115.8966 | 123.468 | 3.1174 | 123.5641 | 86.5173 | -0.28381 | 123.468 | 3.1174 | 86.5173 | 115.8966 | 123.5641 | -123.8205 | -123.7976
5061.7344 | 123.7198 | -61.441 | 62.1506 | -0.039444 | 0.017519 | 0.012132 | 0.018301 | 0.059821 | -0.0026831 | 0.077767 | -58.3878 | 62.1597 | -61.7615 | -61.615 | 54.3549 | 24.6552 | 8.8348 | 8.3633 | 62.1277 | -61.7706 | -0.32043 | 0.009155 | 3.0533 | -0.17395 | -7.7957 | -0.32959 | -0.022888 | 3.3737 | 70.2759 | 69.8044 | 115.7959 | 123.6008 | 3.0533 | 123.5687 | 86.0962 | -0.32959 | 123.6008 | 3.0533 | 86.0962 | 115.7959 | 123.5687 | -123.912 | -123.9212
5062.7188 | 123.8571 | -61.3861 | 62.1185 | -0.10811 | 0.011538 | 0.0085 | 0.0078336 | 0.059607 | -0.0016149 | 0.080331 | -58.2504 | 62.0636 | -61.7294 | -61.5051 | 54.4876 | 24.678 | 8.7616 | 8.5739 | 62.0911 | -61.6608 | -0.34332 | -0.054931 | 3.1357 | -0.11902 | -7.6309 | -0.27466 | -0.027466 | 3.479 | 70.1477 | 69.96 | 115.8737 | 123.4497 | 3.1357 | 123.4772 | 86.0641 | -0.27466 | 123.4497 | 3.1357 | 86.0641 | 115.8737 | 123.4772 | -123.848 | -123.7793
5063.7188 | 123.8342 | -61.409 | 62.1002 | -0.11574 | 0.012392 | 0.0065774 | 0.0099698 | 0.056617 | -0.0035375 | 0.079263 | -58.3191 | 62.059 | -61.7294 | -61.5509 | 54.483 | 24.7925 | 8.7204 | 8.4869 | 62.0773 | -61.6974 | -0.32043 | -0.041199 | 3.0899 | -0.14191 | -7.6172 | -0.28839 | -0.022888 | 3.4103 | 70.1294 | 69.8959 | 115.892 | 123.468 | 3.0899 | 123.4863 | 86.2015 | -0.28839 | 123.468 | 3.0899 | 86.2015 | 115.892 | 123.4863 | -123.8297 | -123.7976
5064.7344 | 123.761 | -61.4319 | 62.1323 | -0.016556 | 0.017733 | 0.010423 | 0.020224 | 0.059607 | -0.0011877 | 0.076699 | -58.2687 | 62.1643 | -61.6974 | -61.5738 | 54.4876 | 24.7696 | 8.8165 | 8.4 | 62.1277 | -61.7569 | -0.2655 | 0.032044 | 3.1631 | -0.14191 | -7.6447 | -0.32501 | -0.004577 | 3.4286 | 70.2484 | 69.8318 | 115.9195 | 123.5962 | 3.1631 | 123.5596 | 86.2015 | -0.32501 | 123.5962 | 3.1631 | 86.2015 | 115.9195 | 123.5596 | -123.8297 | -123.8892
5065.7188 | 123.8342 | -61.4182 | 62.1094 | -0.10048 | 0.014315 | 0.014268 | 0.0067654 | 0.057685 | 0.0022303 | 0.078408 | -58.3145 | 62.0728 | -61.7294 | -61.528 | 54.5517 | 24.733 | 8.7524 | 8.5419 | 62.0819 | -61.7111 | -0.31128 | -0.036621 | 3.1036 | -0.10986 | -7.5577 | -0.29297 | -0.027466 | 3.4149 | 70.1706 | 69.96 | 115.9698 | 123.4909 | 3.1036 | 123.5001 | 86.1511 | -0.29297 | 123.4909 | 3.1036 | 86.1511 | 115.9698 | 123.5001 | -123.8388 | -123.8205
5066.7188 | 123.8525 | -61.3861 | 62.0956 | -0.19966 | 0.013674 | 0.006791 | 0.011892 | 0.055121 | -0.0011877 | 0.077981 | -58.255 | 62.0682 | -61.7157 | -61.5234 | 54.5471 | 25.0259 | 9.0317 | 8.2123 | 62.114 | -61.6653 | -0.32959 | -0.027466 | 3.1311 | -0.13733 | -7.5485 | -0.27924 | 0.018311 | 3.4607 | 70.4178 | 69.5984 | 115.9332 | 123.4543 | 3.1311 | 123.5001 | 86.412 | -0.27924 | 123.4543 | 3.1311 | 86.412 | 115.9332 | 123.5001 | -123.8113 | -123.761
5067.7344 | 123.7198 | -61.4182 | 62.1368 | -0.20729 | 0.014529 | 0.014054 | 0.01766 | 0.057898 | 0.0011621 | 0.076913 | -58.3282 | 62.2055 | -61.7432 | -61.6013 | 54.4098 | 24.8108 | 8.963 | 8.4366 | 62.114 | -61.7523 | -0.32501 | 0.068664 | 3.0899 | -0.1831 | -7.7271 | -0.33417 | -0.022888 | 3.4149 | 70.3812 | 69.8547 | 115.8279 | 123.6237 | 3.0899 | 123.5321 | 86.2289 | -0.33417 | 123.6237 | 3.0899 | 86.2289 | 115.8279 | 123.5321 | -123.88 | -123.8892
5068.7188 | 123.8617 | -61.3815 | 62.1277 | -0.21492 | 0.013888 | 0.011064 | 0.0095424 | 0.057685 | -0.0011877 | 0.076486 | -58.2733 | 62.059 | -61.7432 | -61.5051 | 54.5197 | 24.5407 | 8.7158 | 8.5922 | 62.114 | -61.6699 | -0.36163 | -0.068665 | 3.1082 | -0.1236 | -7.608 | -0.28839 | -0.013733 | 3.4698 | 70.0974 | 69.9738 | 115.9012 | 123.4406 | 3.1082 | 123.4955 | 85.9222 | -0.28839 | 123.4406 | 3.1082 | 85.9222 | 115.9012 | 123.4955 | -123.8708 | -123.7976
5069.7344 | 123.7564 | -61.4273 | 62.146 | -0.16151 | 0.016238 | 0.0089274 | 0.01531 | 0.05918 | -0.0043921 | 0.078835 | -58.2825 | 62.1597 | -61.7386 | -61.5692 | 54.4464 | 24.7055 | 8.8623 | 8.4366 | 62.1414 | -61.7249 | -0.31128 | 0.013733 | 3.1448 | -0.14191 | -7.6996 | -0.29755 | -0.004578 | 3.4561 | 70.2896 | 69.8639 | 115.8737 | 123.587 | 3.1448 | 123.5687 | 86.1328 | -0.29755 | 123.587 | 3.1448 | 86.1328 | 115.8737 | 123.5687 | -123.8846 | -123.8708
5070.7188 | 123.793 | -61.4227 | 62.1185 | -0.047073 | 0.01581 | 0.0095682 | 0.0080472 | 0.05918 | -0.0018285 | 0.080544 | -58.3511 | 62.0682 | -61.7569 | -61.5784 | 54.4968 | 24.7284 | 8.757 | 8.5098 | 62.0911 | -61.6928 | -0.33417 | -0.050354 | 3.0716 | -0.15564 | -7.6218 | -0.27008 | -0.027466 | 3.4058 | 70.1797 | 69.9326 | 115.9195 | 123.4909 | 3.0716 | 123.5138 | 86.1511 | -0.27008 | 123.4909 | 3.0716 | 86.1511 | 115.9195 | 123.5138 | -123.8754 | -123.8113
5071.7188 | 123.7747 | -61.4273 | 62.114 | 0.03685 | 0.014529 | 0.0089274 | 0.0089016 | 0.05683 | -0.0011877 | 0.080544 | -58.3603 | 62.0636 | -61.7569 | -61.5738 | 54.4968 | 24.6597 | 8.8074 | 8.4915 | 62.1048 | -61.7203 | -0.32959 | -0.050354 | 3.067 | -0.14648 | -7.6172 | -0.29297 | -0.009156 | 3.3966 | 70.2347 | 69.9188 | 115.9241 | 123.4909 | 3.067 | 123.5321 | 86.087 | -0.29297 | 123.4909 | 3.067 | 86.087 | 115.9241 | 123.5321 | -123.8709 | -123.8342
5072.7344 | 123.7152 | -61.4273 | 62.1277 | -0.062332 | 0.016878 | 0.012345 | 0.018728 | 0.060248 | -0.0037511 | 0.077981 | -58.2916 | 62.178 | -61.7111 | -61.5829 | 54.451 | 24.6368 | 8.8806 | 8.4412 | 62.1231 | -61.7432 | -0.28381 | 0.050354 | 3.1357 | -0.15564 | -7.6767 | -0.31586 | -0.004578 | 3.4195 | 70.3079 | 69.8685 | 115.8783 | 123.6053 | 3.1357 | 123.5504 | 86.0641 | -0.31586 | 123.6053 | 3.1357 | 86.0641 | 115.8783 | 123.5504 | -123.8388 | -123.8708
5073.7344 | 123.7885 | -61.4136 | 62.1094 | 0.097885 | 0.011965 | 0.011064 | 0.010824 | 0.060462 | -0.0014013 | 0.078408 | -58.3466 | 62.0682 | -61.7477 | -61.6196 | 54.4693 | 24.6963 | 8.7799 | 8.4824 | 62.1094 | -61.6974 | -0.33417 | -0.041199 | 3.067 | -0.20599 | -7.6401 | -0.28381 | 0 | 3.4012 | 70.1935 | 69.8959 | 115.8829 | 123.4818 | 3.067 | 123.5229 | 86.1099 | -0.28381 | 123.4818 | 3.067 | 86.1099 | 115.8829 | 123.5229 | -123.8571 | -123.8068
5074.7344 | 123.7244 | -61.4319 | 62.1506 | -1.0694 | 0.016024 | 0.013413 | 0.017233 | 0.060675 | -0.0011877 | 0.077126 | -58.287 | 62.1597 | -61.7432 | -61.5875 | 54.4373 | 24.4034 | 8.8989 | 8.4869 | 62.1368 | -61.7477 | -0.31128 | 0.009155 | 3.1448 | -0.15564 | -7.7133 | -0.31586 | -0.013733 | 3.4561 | 70.3308 | 69.9188 | 115.8691 | 123.5916 | 3.1448 | 123.5687 | 85.8353 | -0.31586 | 123.5916 | 3.1448 | 85.8353 | 115.8691 | 123.5687 | -123.8937 | -123.8983
5075.7188 | 123.7839 | -61.409 | 62.1002 | -0.43617 | 0.013674 | 0.012345 | 0.010611 | 0.060462 | -0.0020421 | 0.080117 | -58.3832 | 62.0361 | -61.7798 | -61.6013 | 54.451 | 24.6277 | 8.812 | 8.5236 | 62.0865 | -61.6928 | -0.37079 | -0.064087 | 3.0258 | -0.19226 | -7.6492 | -0.28381 | -0.013733 | 3.3966 | 70.2209 | 69.9326 | 115.86 | 123.4451 | 3.0258 | 123.4955 | 86.0367 | -0.28381 | 123.4451 | 3.0258 | 86.0367 | 115.86 | 123.4955 | -123.88 | -123.793
5076.7188 | 123.7747 | -61.409 | 62.114 | 0.013962 | 0.014956 | 0.014482 | 0.005911 | 0.060675 | 0.00052127 | 0.079263 | -58.3374 | 62.0453 | -61.7569 | -61.5829 | 54.4418 | 24.5819 | 8.812 | 8.5144 | 62.1002 | -61.7203 | -0.3479 | -0.068665 | 3.0716 | -0.17395 | -7.6721 | -0.31128 | -0.013733 | 3.4195 | 70.2209 | 69.9234 | 115.8508 | 123.4543 | 3.0716 | 123.5092 | 85.9909 | -0.31128 | 123.4543 | 3.0716 | 85.9909 | 115.8508 | 123.5092 | -123.8709 | -123.8342
5077.7188 | 123.7289 | -61.4365 | 62.1689 | -0.1844 | 0.015597 | 0.0132 | 0.014456 | 0.060034 | -0.0031103 | 0.078408 | -58.3237 | 62.1506 | -61.734 | -61.615 | 54.451 | 24.646 | 8.9676 | 8.4824 | 62.1231 | -61.7432 | -0.29755 | -0.01831 | 3.1128 | -0.17853 | -7.7179 | -0.3067 | -0.045776 | 3.4103 | 70.4041 | 69.9188 | 115.8875 | 123.587 | 3.1128 | 123.5596 | 86.0825 | -0.3067 | 123.587 | 3.1128 | 86.0825 | 115.8875 | 123.5596 | -123.9029 | -123.912
5078.7344 | 123.7289 | -61.4182 | 62.1552 | -0.84816 | 0.017519 | 0.01085 | 0.018515 | 0.061103 | 0.0015893 | 0.077767 | -58.2687 | 62.178 | -61.7432 | -61.5829 | 54.4235 | 24.6094 | 8.8303 | 8.3954 | 62.1643 | -61.7294 | -0.32501 | 0.022889 | 3.1494 | -0.16479 | -7.7316 | -0.31128 | 0.009156 | 3.4744 | 70.2484 | 69.8135 | 115.8417 | 123.5962 | 3.1494 | 123.5825 | 86.0275 | -0.31128 | 123.5962 | 3.1494 | 86.0275 | 115.8417 | 123.5825 | -123.8983 | -123.8846
5079.7188 | 123.8022 | -61.4136 | 62.1002 | -0.26833 | 0.01282 | 0.0089274 | 0.0067654 | 0.061743 | -0.0031103 | 0.07969 | -58.3603 | 62.059 | -61.7477 | -61.5967 | 54.4693 | 24.6185 | 8.7753 | 8.4503 | 62.114 | -61.6882 | -0.33417 | -0.041199 | 3.0533 | -0.18311 | -7.6309 | -0.27466 | 0.013733 | 3.3875 | 70.1889 | 69.8639 | 115.8829 | 123.4726 | 3.0533 | 123.5275 | 86.0321 | -0.27466 | 123.4726 | 3.0533 | 86.0321 | 115.8829 | 123.5275 | -123.848 | -123.7885
5080.7188 | 123.7976 | -61.4182 | 62.1094 | 0.15892 | 0.01346 | 0.01085 | 0.0084744 | 0.058325 | -0.0011877 | 0.080758 | -58.3511 | 62.059 | -61.7706 | -61.6058 | 54.4647 | 24.6597 | 8.7891 | 8.4686 | 62.0911 | -61.7111 | -0.35248 | -0.050354 | 3.067 | -0.18768 | -7.6447 | -0.29297 | -0.018311 | 3.4195 | 70.2072 | 69.8868 | 115.8829 | 123.4772 | 3.067 | 123.5092 | 86.0779 | -0.29297 | 123.4772 | 3.067 | 86.0779 | 115.8829 | 123.5092 | -123.88 | -123.8205
5081.7188 | 123.8159 | -61.4136 | 62.1185 | -0.0089264 | 0.014956 | 0.0082864 | 0.0074062 | 0.058112 | -0.0011877 | 0.079263 | -58.3282 | 62.0636 | -61.7432 | -61.5509 | 54.483 | 24.7696 | 8.8028 | 8.519 | 62.0911 | -61.702 | -0.32959 | -0.054931 | 3.0853 | -0.13733 | -7.6355 | -0.28839 | -0.027466 | 3.4149 | 70.2164 | 69.9326 | 115.8966 | 123.4772 | 3.0853 | 123.5046 | 86.1832 | -0.28839 | 123.4772 | 3.0853 | 86.1832 | 115.8966 | 123.5046 | -123.8617 | -123.8205
5082.7188 | 123.8159 | -61.409 | 62.1323 | -0.23018 | 0.012179 | 0.0095682 | 0.015951 | 0.055762 | -0.00097413 | 0.079049 | -58.4381 | 62.1002 | -61.6699 | -61.5692 | 54.4144 | 24.8154 | 8.7296 | 8.519 | 62.0819 | -61.6928 | -0.26093 | -0.032043 | 2.9709 | -0.16022 | -7.7179 | -0.28381 | -0.050354 | 3.2318 | 70.1385 | 69.928 | 115.8234 | 123.5092 | 2.9709 | 123.4909 | 86.2244 | -0.28381 | 123.5092 | 2.9709 | 86.2244 | 115.8234 | 123.4909 | -123.8022 | -123.8251
5083.7188 | 123.8892 | -61.3998 | 62.1368 | 0.090256 | 0.014742 | 0.0080728 | 0.0082608 | 0.057257 | -0.00011953 | 0.077981 | -58.342 | 62.0682 | -61.7203 | -61.5829 | 54.451 | 24.646 | 8.7799 | 8.4549 | 62.0682 | -61.7065 | -0.32043 | -0.068665 | 3.0579 | -0.18311 | -7.6859 | -0.3067 | -0.068665 | 3.3783 | 70.1797 | 69.8547 | 115.8508 | 123.468 | 3.0579 | 123.468 | 86.0458 | -0.3067 | 123.468 | 3.0579 | 86.0458 | 115.8508 | 123.468 | -123.8571 | -123.8434
5084.7188 | 123.8617 | -61.3632 | 62.1094 | -0.16914 | 0.01282 | 0.0080728 | 0.0097562 | 0.058112 | -0.0024695 | 0.075845 | -58.2596 | 62.0636 | -61.7294 | -61.5097 | 54.5242 | 24.6963 | 8.7296 | 8.5602 | 62.0911 | -61.6745 | -0.36621 | -0.045776 | 3.1036 | -0.14648 | -7.5851 | -0.31128 | -0.018311 | 3.4698 | 70.0928 | 69.9234 | 115.8875 | 123.4268 | 3.1036 | 123.4543 | 86.0596 | -0.31128 | 123.4268 | 3.1036 | 86.0596 | 115.8875 | 123.4543 | -123.8388 | -123.7839
5085.7188 | 123.8022 | -61.3724 | 62.1185 | -0.09285 | 0.014101 | 0.0070048 | 0.0084744 | 0.057685 | 0.00094847 | 0.077554 | -58.3008 | 62.0773 | -61.7249 | -61.5463 | 54.4785 | 24.6735 | 8.7616 | 8.5281 | 62.1094 | -61.6837 | -0.35248 | -0.041198 | 3.0716 | -0.17395 | -7.6401 | -0.31128 | -0.009155 | 3.4241 | 70.134 | 69.9005 | 115.8508 | 123.4497 | 3.0716 | 123.4818 | 86.0458 | -0.31128 | 123.4497 | 3.0716 | 86.0458 | 115.8508 | 123.4818 | -123.8434 | -123.8022
5086.7188 | 123.8113 | -61.3998 | 62.0911 | 0.0063326 | 0.010897 | 0.012345 | 0.0076198 | 0.05448 | 9.4068e-05 | 0.078195 | -58.3191 | 62.0544 | -61.7203 | -61.5601 | 54.4739 | 24.7238 | 8.7616 | 8.519 | 62.0728 | -61.6928 | -0.32043 | -0.036621 | 3.0807 | -0.16022 | -7.6172 | -0.29297 | -0.01831 | 3.4012 | 70.1614 | 69.9188 | 115.8737 | 123.4543 | 3.0807 | 123.4726 | 86.1237 | -0.29297 | 123.4543 | 3.0807 | 86.1237 | 115.8737 | 123.4726 | -123.8113 | -123.7839
5087.7188 | 123.8113 | -61.3724 | 62.1231 | -0.10811 | 0.014101 | 0.010209 | 0.0089016 | 0.058539 | -0.00011953 | 0.079904 | -58.2825 | 62.0499 | -61.702 | -61.5234 | 54.5059 | 24.7009 | 8.7158 | 8.5693 | 62.0911 | -61.6699 | -0.32959 | -0.073242 | 3.0899 | -0.15106 | -7.6172 | -0.29755 | -0.032044 | 3.4195 | 70.0882 | 69.9417 | 115.8783 | 123.4222 | 3.0899 | 123.4634 | 86.0733 | -0.29755 | 123.4222 | 3.0899 | 86.0733 | 115.8783 | 123.4634 | -123.8251 | -123.793
5088.7188 | 123.7885 | -61.3907 | 62.1231 | -0.016556 | 0.01282 | 0.010423 | 0.0067654 | 0.05683 | 0.0020167 | 0.078622 | -58.3282 | 62.0544 | -61.7203 | -61.5509 | 54.4922 | 24.8337 | 8.7524 | 8.4961 | 62.0956 | -61.6974 | -0.32959 | -0.068665 | 3.0624 | -0.16022 | -7.6309 | -0.3067 | -0.027466 | 3.392 | 70.1431 | 69.8868 | 115.8829 | 123.4451 | 3.0624 | 123.4863 | 86.2244 | -0.3067 | 123.4451 | 3.0624 | 86.2244 | 115.8829 | 123.4863 | -123.8434 | -123.8205
5089.7344 | 123.7152 | -61.4044 | 62.178 | -0.29121 | 0.012606 | 0.010209 | 0.01296 | 0.055762 | 9.4068e-05 | 0.076913 | -58.3054 | 62.114 | -61.7386 | -61.5875 | 54.4556 | 24.733 | 8.9676 | 8.4915 | 62.1323 | -61.7386 | -0.33417 | -0.064087 | 3.0991 | -0.18311 | -7.7225 | -0.33417 | -0.045777 | 3.4332 | 70.372 | 69.8959 | 115.86 | 123.5184 | 3.0991 | 123.5367 | 86.1374 | -0.33417 | 123.5184 | 3.0991 | 86.1374 | 115.86 | 123.5367 | -123.9166 | -123.9166
5090.7188 | 123.8159 | -61.3953 | 62.1185 | -0.069961 | 0.014529 | 0.0061502 | 0.0089016 | 0.056403 | -0.0016149 | 0.077767 | -58.2825 | 62.0728 | -61.7432 | -61.5463 | 54.5334 | 24.7879 | 8.7662 | 8.5556 | 62.0819 | -61.6837 | -0.3479 | -0.045776 | 3.1128 | -0.15106 | -7.5851 | -0.28839 | -0.036621 | 3.4607 | 70.1614 | 69.9509 | 115.9287 | 123.468 | 3.1128 | 123.4772 | 86.1832 | -0.28839 | 123.468 | 3.1128 | 86.1832 | 115.9287 | 123.4772 | -123.8617 | -123.8022
5091.7188 | 123.793 | -61.3861 | 62.1231 | 0.074997 | 0.015169 | 0.006791 | 0.010824 | 0.055976 | -0.0018285 | 0.078408 | -58.3511 | 62.0728 | -61.7523 | -61.5784 | 54.4052 | 24.678 | 8.7616 | 8.5007 | 62.0728 | -61.7157 | -0.36621 | -0.050354 | 3.035 | -0.19226 | -7.7179 | -0.32959 | -0.050354 | 3.4012 | 70.1477 | 69.8868 | 115.7913 | 123.4589 | 3.035 | 123.4589 | 86.0641 | -0.32959 | 123.4589 | 3.035 | 86.0641 | 115.7913 | 123.4589 | -123.8754 | -123.8388
5092.7188 | 123.7244 | -61.4227 | 62.178 | -0.20729 | 0.014742 | 0.014268 | 0.013601 | 0.057257 | -0.00097413 | 0.078408 | -58.3466 | 62.1597 | -61.7523 | -61.615 | 54.3411 | 24.614 | 8.9127 | 8.4412 | 62.146 | -61.7065 | -0.32959 | -0.018311 | 3.0762 | -0.19226 | -7.8369 | -0.28381 | -0.032044 | 3.4058 | 70.3354 | 69.8639 | 115.7639 | 123.5825 | 3.0762 | 123.5687 | 86.0367 | -0.28381 | 123.5825 | 3.0762 | 86.0367 | 115.7639 | 123.5687 | -123.9304 | -123.8846
5093.7188 | 123.7885 | -61.409 | 62.1231 | -0.024185 | 0.015597 | 0.011064 | 0.0089016 | 0.058753 | -0.0024695 | 0.078835 | -58.223 | 62.0819 | -61.7157 | -61.5875 | 54.3869 | 24.6185 | 8.7616 | 8.4961 | 62.0865 | -61.6837 | -0.3067 | -0.041199 | 3.186 | -0.17853 | -7.7362 | -0.27466 | -0.036621 | 3.4927 | 70.1706 | 69.9051 | 115.7959 | 123.4909 | 3.186 | 123.4955 | 86.0275 | -0.27466 | 123.4909 | 3.186 | 86.0275 | 115.7959 | 123.4955 | -123.8388 | -123.8068
5094.7188 | 123.8754 | -61.3815 | 62.1231 | -0.131 | 0.011538 | 0.011277 | 0.0080472 | 0.057257 | 9.4068e-05 | 0.07969 | -58.3054 | 62.0682 | -61.7294 | -61.5005 | 54.451 | 24.6735 | 8.7524 | 8.606 | 62.0956 | -61.6745 | -0.3479 | -0.054932 | 3.0762 | -0.11902 | -7.6721 | -0.29297 | -0.027466 | 3.4241 | 70.134 | 69.9875 | 115.8325 | 123.4497 | 3.0762 | 123.4772 | 86.055 | -0.29297 | 123.4497 | 3.0762 | 86.055 | 115.8325 | 123.4772 | -123.8525 | -123.7976
5095.7188 | 123.8113 | -61.4044 | 62.1231 | -0.0012969 | 0.014101 | 0.014482 | 0.0091152 | 0.059394 | -0.0011877 | 0.077554 | -58.3511 | 62.0499 | -61.7477 | -61.5646 | 54.4144 | 24.7238 | 8.7708 | 8.5144 | 62.0956 | -61.6882 | -0.34332 | -0.073242 | 3.0533 | -0.16022 | -7.7087 | -0.28381 | -0.027466 | 3.3966 | 70.1752 | 69.9188 | 115.8188 | 123.4543 | 3.0533 | 123.5001 | 86.1282 | -0.28381 | 123.4543 | 3.0533 | 86.1282 | 115.8188 | 123.5001 | -123.8709 | -123.8113
5096.7188 | 123.7885 | -61.441 | 62.1231 | 0.013962 | 0.01346 | 0.01085 | 0.0099698 | 0.057044 | -0.0020421 | 0.07734 | -58.3511 | 62.0361 | -61.7569 | -61.5784 | 54.3869 | 24.559 | 8.7891 | 8.4961 | 62.0865 | -61.7203 | -0.31586 | -0.086975 | 3.0899 | -0.13733 | -7.7362 | -0.27924 | -0.036621 | 3.4058 | 70.2301 | 69.9371 | 115.8279 | 123.4772 | 3.0899 | 123.5275 | 86.0001 | -0.27924 | 123.4772 | 3.0899 | 86.0001 | 115.8279 | 123.5275 | -123.88 | -123.8434
5097.7188 | 123.8205 | -61.3861 | 62.1277 | -0.12337 | 0.012606 | 0.01085 | 0.0084744 | 0.05683 | -0.00011953 | 0.075417 | -58.3145 | 62.0636 | -61.7065 | -61.528 | 54.4601 | 24.5773 | 8.7524 | 8.5922 | 62.0819 | -61.6974 | -0.32044 | -0.064087 | 3.0716 | -0.14191 | -7.6675 | -0.31128 | -0.045777 | 3.392 | 70.1385 | 69.9783 | 115.8463 | 123.4497 | 3.0716 | 123.468 | 85.9634 | -0.31128 | 123.4497 | 3.0716 | 85.9634 | 115.8463 | 123.468 | -123.8342 | -123.8251
5098.7188 | 123.8251 | -61.3815 | 62.1277 | -0.12337 | 0.012392 | 0.011064 | 0.0080472 | 0.056403 | -0.00033333 | 0.078195 | -58.2642 | 62.0636 | -61.7111 | -61.4822 | 54.4693 | 24.7009 | 8.7021 | 8.6151 | 62.0544 | -61.6791 | -0.32959 | -0.064087 | 3.1174 | -0.10071 | -7.6584 | -0.29755 | -0.073243 | 3.447 | 70.0836 | 69.9966 | 115.8508 | 123.4451 | 3.1174 | 123.436 | 86.0825 | -0.29755 | 123.4451 | 3.1174 | 86.0825 | 115.8508 | 123.436 | -123.8388 | -123.8068
5099.7188 | 123.7289 | -61.4227 | 62.178 | 1.6085 | 0.014956 | 0.0046548 | 0.012533 | 0.057044 | -0.0014013 | 0.077981 | -58.3328 | 62.1414 | -61.7569 | -61.5875 | 54.3915 | 24.6185 | 8.9218 | 8.4595 | 62.1414 | -61.7111 | -0.33417 | -0.036622 | 3.0899 | -0.1648 | -7.7866 | -0.28839 | -0.036622 | 3.4241 | 70.3445 | 69.8822 | 115.8142 | 123.5641 | 3.0899 | 123.5641 | 86.0413 | -0.28839 | 123.5641 | 3.0899 | 86.0413 | 115.8142 | 123.5641 | -123.9349 | -123.8892
5100.7188 | 123.7839 | -61.3907 | 62.114 | 0.12077 | 0.014742 | 0.012986 | 0.011679 | 0.058539 | -0.00054693 | 0.079904 | -58.3511 | 62.0361 | -61.7523 | -61.6013 | 54.4052 | 24.5407 | 8.7296 | 8.4274 | 62.0773 | -61.6745 | -0.36163 | -0.07782 | 3.0396 | -0.21057 | -7.7087 | -0.28381 | -0.036621 | 3.4012 | 70.1202 | 69.8181 | 115.7959 | 123.4268 | 3.0396 | 123.468 | 85.9314 | -0.28381 | 123.4268 | 3.0396 | 85.9314 | 115.7959 | 123.468 | -123.8663 | -123.7885
5101.7188 | 123.761 | -61.3907 | 62.0865 | 0.18181 | 0.016024 | 0.011064 | 0.010611 | 0.058753 | -0.00033333 | 0.079049 | -58.3328 | 62.059 | -61.7706 | -61.6013 | 54.4693 | 24.614 | 8.6975 | 8.3588 | 62.059 | -61.7386 | -0.37994 | -0.027466 | 3.0579 | -0.21057 | -7.6172 | -0.3479 | -0.027466 | 3.4378 | 70.0882 | 69.7495 | 115.86 | 123.4497 | 3.0579 | 123.4497 | 86.0046 | -0.3479 | 123.4497 | 3.0579 | 86.0046 | 115.86 | 123.4497 | -123.8571 | -123.8251
5102.7344 | 123.6603 | -61.4273 | 62.1689 | -0.23018 | 0.016024 | 0.0093546 | 0.013174 | 0.058539 | 9.4068e-05 | 0.075845 | -58.3649 | 62.1597 | -61.7432 | -61.5601 | 54.6661 | 24.6002 | 8.7158 | 8.345 | 62.146 | -61.7523 | -0.31586 | -0.009155 | 3.0624 | -0.13275 | -7.5027 | -0.32501 | -0.022888 | 3.3783 | 70.1431 | 69.7723 | 116.0934 | 123.587 | 3.0624 | 123.5733 | 86.0275 | -0.32501 | 123.587 | 3.0624 | 86.0275 | 116.0934 | 123.5733 | -123.912 | -123.9212
5103.7188 | 123.793 | -61.409 | 62.0911 | 0.074997 | 0.01282 | 0.014054 | 0.010824 | 0.060248 | -0.00054693 | 0.078835 | -58.342 | 62.0316 | -61.7752 | -61.6058 | 54.451 | 24.7147 | 8.7158 | 8.4229 | 62.0865 | -61.6974 | -0.36621 | -0.059509 | 3.067 | -0.19684 | -7.6401 | -0.28839 | -0.004577 | 3.4332 | 70.1248 | 69.8318 | 115.86 | 123.4406 | 3.067 | 123.4955 | 86.1237 | -0.28839 | 123.4406 | 3.067 | 86.1237 | 115.86 | 123.4955 | -123.8663 | -123.7885
5104.7188 | 123.8251 | -61.4044 | 62.1048 | -0.0089264 | 0.014315 | 0.010209 | 0.01232 | 0.058112 | 0.0011621 | 0.078408 | -58.3649 | 62.059 | -61.7249 | -61.5646 | 54.4693 | 24.8291 | 8.7616 | 8.4503 | 62.0728 | -61.6974 | -0.32044 | -0.045776 | 3.0396 | -0.16022 | -7.6355 | -0.29297 | -0.032043 | 3.36 | 70.166 | 69.8547 | 115.8737 | 123.4634 | 3.0396 | 123.4772 | 86.2335 | -0.29297 | 123.4634 | 3.0396 | 86.2335 | 115.8737 | 123.4772 | -123.8297 | -123.8022
5105.7188 | 123.8022 | -61.4273 | 62.1002 | 0.03685 | 0.014529 | 0.010636 | 0.0093288 | 0.058112 | -0.0024695 | 0.080117 | -58.3466 | 62.059 | -61.7432 | -61.5829 | 54.3961 | 24.6689 | 8.7708 | 8.432 | 62.0728 | -61.6882 | -0.31586 | -0.041199 | 3.0807 | -0.15564 | -7.7042 | -0.26093 | -0.027466 | 3.3966 | 70.1981 | 69.8593 | 115.8234 | 123.4863 | 3.0807 | 123.5001 | 86.0962 | -0.26093 | 123.4863 | 3.0807 | 86.0962 | 115.8234 | 123.5001 | -123.8434 | -123.7885
5106.7188 | 123.7976 | -61.4044 | 62.114 | 0.73113 | 0.013247 | 0.0076456 | 0.008688 | 0.058539 | -0.0011877 | 0.078408 | -58.3328 | 62.0728 | -61.734 | -61.6013 | 54.4418 | 24.6597 | 8.7982 | 8.4641 | 62.059 | -61.6928 | -0.32959 | -0.041199 | 3.0716 | -0.19684 | -7.6721 | -0.28839 | -0.054932 | 3.4012 | 70.2026 | 69.8685 | 115.8463 | 123.4772 | 3.0716 | 123.4634 | 86.0641 | -0.28839 | 123.4772 | 3.0716 | 86.0641 | 115.8463 | 123.4634 | -123.848 | -123.8068
5107.7188 | 123.8617 | -61.377 | 62.0819 | -0.062332 | 0.012392 | 0.005723 | 0.0078336 | 0.057898 | 0.00030767 | 0.07969 | -58.2962 | 62.0636 | -61.7111 | -61.5097 | 54.4052 | 24.7925 | 8.7387 | 8.5327 | 62.0499 | -61.6928 | -0.33417 | -0.01831 | 3.0807 | -0.13275 | -7.6767 | -0.31586 | -0.032043 | 3.4149 | 70.1157 | 69.9097 | 115.7822 | 123.4406 | 3.0807 | 123.4268 | 86.1694 | -0.31586 | 123.4406 | 3.0807 | 86.1694 | 115.7822 | 123.4268 | -123.793 | -123.7747
5108.7188 | 123.7701 | -61.4227 | 62.1002 | 0.2047 | 0.016665 | 0.011277 | 0.008688 | 0.059394 | -0.00054693 | 0.07969 | -58.3191 | 62.0407 | -61.7477 | -61.5692 | 54.3594 | 24.8016 | 8.638 | 8.3954 | 62.0361 | -61.6882 | -0.32501 | -0.05951 | 3.1036 | -0.14649 | -7.7408 | -0.2655 | -0.064087 | 3.4287 | 70.0607 | 69.8181 | 115.7822 | 123.4634 | 3.1036 | 123.4589 | 86.2244 | -0.2655 | 123.4634 | 3.1036 | 86.2244 | 115.7822 | 123.4589 | -123.848 | -123.7885
5109.7188 | 123.7793 | -61.4044 | 62.1231 | -0.63454 | 0.01282 | 0.0082864 | 0.0091152 | 0.05683 | -0.00097413 | 0.078835 | -58.3557 | 62.0819 | -61.7157 | -61.5738 | 54.3915 | 24.7238 | 8.7204 | 8.4549 | 62.0682 | -61.6974 | -0.31128 | -0.041199 | 3.0487 | -0.16937 | -7.7316 | -0.29297 | -0.054932 | 3.36 | 70.1248 | 69.8593 | 115.7959 | 123.4863 | 3.0487 | 123.4726 | 86.1282 | -0.29297 | 123.4863 | 3.0487 | 86.1282 | 115.7959 | 123.4726 | -123.8388 | -123.8205
5110.7188 | 123.8205 | -61.3953 | 62.0956 | 0.0063326 | 0.014101 | 0.013841 | 0.0082608 | 0.057257 | -0.00054693 | 0.078622 | -58.3557 | 62.0544 | -61.7386 | -61.5784 | 54.3961 | 24.9161 | 8.9081 | 8.6472 | 62.1002 | -61.6745 | -0.34332 | -0.041199 | 3.0396 | -0.18311 | -7.6996 | -0.27924 | 0.004578 | 3.3829 | 70.3033 | 70.0424 | 115.7913 | 123.4497 | 3.0396 | 123.4955 | 86.3113 | -0.27924 | 123.4497 | 3.0396 | 86.3113 | 115.7913 | 123.4955 | -123.8342 | -123.7701
5111.7188 | 123.8251 | -61.4182 | 62.0499 | 1.5246 | 0.015383 | 0.012986 | 0.011892 | 0.058112 | -0.0020421 | 0.07969 | -58.2642 | 62.0544 | -61.7432 | -61.5372 | 54.4189 | 24.7238 | 8.6426 | 8.5007 | 62.0544 | -61.7065 | -0.32501 | 0.004577 | 3.154 | -0.11902 | -7.6309 | -0.28839 | 0.004577 | 3.479 | 70.0607 | 69.9188 | 115.8371 | 123.4726 | 3.154 | 123.4726 | 86.142 | -0.28839 | 123.4726 | 3.154 | 86.142 | 115.8371 | 123.4726 | -123.793 | -123.7564
5112.7188 | 123.793 | -61.4182 | 62.1185 | -0.1844 | 0.013888 | 0.010423 | 0.0097562 | 0.059394 | -0.00054693 | 0.079049 | -58.287 | 62.0682 | -61.7477 | -61.5051 | 54.4327 | 24.9527 | 8.8303 | 8.5739 | 62.0911 | -61.6928 | -0.32959 | -0.050354 | 3.1311 | -0.086975 | -7.6859 | -0.27466 | -0.027466 | 3.4607 | 70.2484 | 69.9921 | 115.8508 | 123.4863 | 3.1311 | 123.5092 | 86.3709 | -0.27466 | 123.4863 | 3.1311 | 86.3709 | 115.8508 | 123.5092 | -123.8663 | -123.8113
5113.7188 | 123.8251 | -61.4182 | 62.0636 | 0.34203 | 0.013888 | 0.010636 | 0.013388 | 0.059607 | -0.00033333 | 0.078622 | -58.2687 | 62.0728 | -61.7523 | -61.5555 | 54.4373 | 24.9435 | 8.7112 | 8.519 | 62.0682 | -61.6882 | -0.33417 | 0.009155 | 3.1494 | -0.13733 | -7.6263 | -0.27008 | 0.004577 | 3.4836 | 70.1294 | 69.9371 | 115.8554 | 123.4909 | 3.1494 | 123.4863 | 86.3617 | -0.27008 | 123.4909 | 3.1494 | 86.3617 | 115.8554 | 123.4863 | -123.8159 | -123.7518
5114.7188 | 123.8022 | -61.3998 | 62.1048 | 0.55565 | 0.012392 | 0.010636 | 0.0095424 | 0.058966 | -0.0011877 | 0.077554 | -58.3237 | 62.0819 | -61.7432 | -61.5967 | 54.4006 | 24.8474 | 8.7891 | 8.4778 | 62.0682 | -61.702 | -0.34332 | -0.022888 | 3.0762 | -0.19684 | -7.7042 | -0.30212 | -0.036621 | 3.4195 | 70.1889 | 69.8776 | 115.8005 | 123.4818 | 3.0762 | 123.468 | 86.2473 | -0.30212 | 123.4818 | 3.0762 | 86.2473 | 115.8005 | 123.468 | -123.848 | -123.8068
5115.7188 | 123.8297 | -61.4136 | 62.0911 | 0.16655 | 0.017306 | 0.013413 | 0.012747 | 0.05918 | -0.0014013 | 0.078622 | -58.2687 | 62.0728 | -61.7432 | -61.5692 | 54.4235 | 24.8703 | 8.6929 | 8.4732 | 62.0316 | -61.734 | -0.32959 | -0.01831 | 3.1448 | -0.15564 | -7.6675 | -0.32044 | -0.059509 | 3.4744 | 70.1065 | 69.8868 | 115.8371 | 123.4863 | 3.1448 | 123.4451 | 86.2839 | -0.32044 | 123.4863 | 3.1448 | 86.2839 | 115.8371 | 123.4451 | -123.8342 | -123.8251
5116.7188 | 123.8205 | -61.4044 | 62.0956 | 0.21996 | 0.01581 | 0.015122 | 0.015524 | 0.057685 | -0.00011953 | 0.077767 | -58.3054 | 62.0773 | -61.7386 | -61.5555 | 54.4235 | 24.9207 | 8.7204 | 8.4915 | 62.0636 | -61.7432 | -0.33417 | -0.01831 | 3.0991 | -0.15106 | -7.6721 | -0.33875 | -0.032043 | 3.4332 | 70.1248 | 69.8959 | 115.8279 | 123.4818 | 3.0991 | 123.468 | 86.3251 | -0.33875 | 123.4818 | 3.0991 | 86.3251 | 115.8279 | 123.468 | -123.8342 | -123.8388
5117.7344 | 123.8068 | -61.4227 | 62.1002 | -0.024185 | 0.012179 | 0.010423 | 0.010183 | 0.061103 | -0.0041785 | 0.079049 | -58.3511 | 62.0499 | -61.7661 | -61.5555 | 54.4556 | 24.9619 | 8.7982 | 8.5281 | 62.1002 | -61.7157 | -0.34332 | -0.050354 | 3.0716 | -0.13275 | -7.6447 | -0.29297 | 0 | 3.4149 | 70.2209 | 69.9509 | 115.8783 | 123.4726 | 3.0716 | 123.5229 | 86.3846 | -0.29297 | 123.4726 | 3.0716 | 86.3846 | 115.8783 | 123.5229 | -123.8663 | -123.8159
5118.7188 | 123.7793 | -61.4273 | 62.0865 | 0.16655 | 0.014956 | 0.013841 | 0.011251 | 0.059394 | -0.0016149 | 0.079049 | -58.2962 | 62.0682 | -61.7386 | -61.5921 | 54.4327 | 24.9344 | 8.7799 | 8.519 | 62.0682 | -61.734 | -0.31128 | -0.018311 | 3.1311 | -0.16479 | -7.6538 | -0.3067 | -0.018311 | 3.4424 | 70.2072 | 69.9463 | 115.86 | 123.4955 | 3.1311 | 123.4955 | 86.3617 | -0.3067 | 123.4955 | 3.1311 | 86.3617 | 115.86 | 123.4955 | -123.8251 | -123.8205
5119.7188 | 123.8068 | -61.4044 | 62.0911 | 0.097885 | 0.01346 | 0.014054 | 0.0097562 | 0.058325 | -0.0018285 | 0.079049 | -58.3374 | 62.0361 | -61.7569 | -61.6241 | 54.4601 | 24.9207 | 8.812 | 8.519 | 62.0819 | -61.7203 | -0.35248 | -0.054931 | 3.067 | -0.21973 | -7.6309 | -0.31586 | -0.009155 | 3.4195 | 70.2164 | 69.9234 | 115.8646 | 123.4406 | 3.067 | 123.4863 | 86.3251 | -0.31586 | 123.4406 | 3.067 | 86.3251 | 115.8646 | 123.4863 | -123.848 | -123.8113
5120.7344 | 123.793 | -61.409 | 62.1048 | -0.19203 | 0.011965 | 0.011277 | 0.0091152 | 0.060462 | -0.0024695 | 0.077981 | -58.2779 | 62.0682 | -61.6928 | -61.4914 | 54.5837 | 24.9252 | 8.8989 | 8.6517 | 62.0636 | -61.6516 | -0.28381 | -0.036621 | 3.1311 | -0.082397 | -7.5211 | -0.24261 | -0.041198 | 3.4149 | 70.3079 | 70.0607 | 115.9927 | 123.4772 | 3.1311 | 123.4726 | 86.3342 | -0.24261 | 123.4772 | 3.1311 | 86.3342 | 115.9927 | 123.4726 | -123.7976 | -123.7564
5121.7188 | 123.7656 | -61.4502 | 62.0911 | 0.18181 | 0.018374 | 0.015122 | 0.016378 | 0.058966 | 0.00030767 | 0.078835 | -58.342 | 62.1185 | -61.7523 | -61.6241 | 54.3594 | 24.971 | 8.8074 | 8.4229 | 62.0956 | -61.7706 | -0.30212 | 0.027466 | 3.1082 | -0.17395 | -7.7316 | -0.32043 | 0.004578 | 3.4103 | 70.2576 | 69.873 | 115.8096 | 123.5687 | 3.1082 | 123.5458 | 86.4212 | -0.32043 | 123.5687 | 3.1082 | 86.4212 | 115.8096 | 123.5458 | -123.8434 | -123.8617
5122.7344 | 123.7885 | -61.4182 | 62.1094 | 0.11314 | 0.015383 | 0.0095682 | 0.0084744 | 0.060248 | -0.00011953 | 0.078408 | -58.3237 | 62.0407 | -61.7661 | -61.6013 | 54.4189 | 24.9573 | 8.757 | 8.5098 | 62.0636 | -61.7111 | -0.3479 | -0.068665 | 3.0945 | -0.1831 | -7.6904 | -0.29297 | -0.045776 | 3.4424 | 70.1752 | 69.928 | 115.8371 | 123.4589 | 3.0945 | 123.4818 | 86.3754 | -0.29297 | 123.4589 | 3.0945 | 86.3754 | 115.8371 | 123.4818 | -123.8754 | -123.8205
5123.7188 | 123.7061 | -61.4731 | 62.114 | -1.1152 | 0.017306 | 0.01555 | 0.018728 | 0.060034 | -0.00011953 | 0.078835 | -58.429 | 62.1826 | -61.7477 | -61.6745 | 54.3228 | 24.8199 | 8.8486 | 8.3496 | 62.1002 | -61.7661 | -0.27466 | 0.068664 | 3.0441 | -0.20142 | -7.7911 | -0.29297 | -0.013733 | 3.3188 | 70.3217 | 69.8227 | 115.7959 | 123.6557 | 3.0441 | 123.5733 | 86.293 | -0.29297 | 123.6557 | 3.0441 | 86.293 | 115.7959 | 123.5733 | -123.8617 | -123.88
5124.7188 | 123.7289 | -61.4502 | 62.1002 | 0.15892 | 0.015383 | 0.013627 | 0.015738 | 0.062384 | 9.4068e-05 | 0.07734 | -58.3511 | 62.1506 | -61.7752 | -61.6562 | 54.332 | 24.7513 | 8.8577 | 8.4137 | 62.1094 | -61.7477 | -0.32501 | 0.050354 | 3.0991 | -0.20599 | -7.7683 | -0.29755 | 0.009155 | 3.4241 | 70.3079 | 69.8639 | 115.7822 | 123.6008 | 3.0991 | 123.5596 | 86.2015 | -0.29755 | 123.6008 | 3.0991 | 86.2015 | 115.7822 | 123.5596 | -123.8754 | -123.848
5125.7344 | 123.8113 | -61.3815 | 62.1185 | 0.37254 | 0.014529 | 0.0082864 | 0.008688 | 0.062171 | -0.0031103 | 0.078408 | -58.2138 | 62.0819 | -61.7157 | -61.5097 | 54.5105 | 24.9435 | 8.8211 | 8.606 | 62.1185 | -61.6928 | -0.33417 | -0.036621 | 3.1677 | -0.12817 | -7.608 | -0.31128 | 0 | 3.5019 | 70.2026 | 69.9875 | 115.892 | 123.4634 | 3.1677 | 123.5001 | 86.3251 | -0.31128 | 123.4634 | 3.1677 | 86.3251 | 115.892 | 123.5001 | -123.8342 | -123.8113
5126.7188 | 123.7656 | -61.4456 | 62.0682 | 0.16655 | 0.015597 | 0.014054 | 0.01531 | 0.062598 | -0.0041785 | 0.079476 | -58.3466 | 62.146 | -61.7615 | -61.6104 | 54.3777 | 24.6918 | 8.7845 | 8.4274 | 62.0819 | -61.734 | -0.31586 | 0.07782 | 3.0991 | -0.16479 | -7.6904 | -0.28839 | 0.013733 | 3.4149 | 70.2301 | 69.873 | 115.8234 | 123.5916 | 3.0991 | 123.5275 | 86.1374 | -0.28839 | 123.5916 | 3.0991 | 86.1374 | 115.8234 | 123.5275 | -123.8297 | -123.8022
5127.7344 | 123.7976 | -61.3907 | 62.0956 | 0.052109 | 0.015169 | 0.0097818 | 0.0089016 | 0.060675 | -0.0011877 | 0.078408 | -58.3923 | 62.0636 | -61.7432 | -61.5875 | 54.4601 | 24.8474 | 8.7936 | 8.5464 | 62.0819 | -61.7386 | -0.35248 | -0.032043 | 2.9984 | -0.19684 | -7.6355 | -0.3479 | -0.013733 | 3.3508 | 70.1843 | 69.9371 | 115.8508 | 123.4543 | 2.9984 | 123.4726 | 86.2381 | -0.3479 | 123.4543 | 2.9984 | 86.2381 | 115.8508 | 123.4726 | -123.8388 | -123.8342
5128.7188 | 123.6969 | -61.4594 | 62.1368 | 0.067368 | 0.016451 | 0.017045 | 0.019796 | 0.060462 | -0.0026831 | 0.079263 | -58.3099 | 62.1689 | -61.7386 | -61.6287 | 54.3732 | 24.8199 | 8.8669 | 8.4183 | 62.1414 | -61.7844 | -0.27923 | 0.032043 | 3.1494 | -0.16937 | -7.7637 | -0.32501 | 0.004577 | 3.4286 | 70.3262 | 69.8776 | 115.8325 | 123.6282 | 3.1494 | 123.6008 | 86.2793 | -0.32501 | 123.6282 | 3.1494 | 86.2793 | 115.8325 | 123.6008 | -123.8754 | -123.9212
5129.7188 | 123.7427 | -61.4685 | 62.1368 | -0.047073 | 0.017092 | 0.013841 | 0.015524 | 0.061957 | -0.0022559 | 0.07734 | -58.3832 | 62.1597 | -61.7615 | -61.647 | 54.3961 | 24.8474 | 8.812 | 8.3679 | 62.1048 | -61.7432 | -0.29297 | 0.022888 | 3.0853 | -0.17853 | -7.7408 | -0.27466 | -0.032044 | 3.3783 | 70.2805 | 69.8364 | 115.8646 | 123.6282 | 3.0853 | 123.5733 | 86.3159 | -0.27466 | 123.6282 | 3.0853 | 86.3159 | 115.8646 | 123.5733 | -123.8983 | -123.88
5130.7344 | 123.848 | -61.377 | 62.1185 | -0.131 | 0.013674 | 0.0070048 | 0.0071926 | 0.059607 | -0.0014013 | 0.077981 | -58.3099 | 62.0682 | -61.7294 | -61.5555 | 54.5334 | 25.0076 | 8.7204 | 8.5327 | 62.0911 | -61.6699 | -0.35248 | -0.050354 | 3.067 | -0.17853 | -7.5851 | -0.29297 | -0.027466 | 3.4195 | 70.0974 | 69.9097 | 115.9103 | 123.4451 | 3.067 | 123.468 | 86.3846 | -0.29297 | 123.4451 | 3.067 | 86.3846 | 115.9103 | 123.468 | -123.848 | -123.7885
5131.7188 | 123.7061 | -61.4456 | 62.1506 | 0.059738 | 0.016238 | 0.013841 | 0.02001 | 0.061103 | -0.00033333 | 0.078835 | -58.3466 | 62.1918 | -61.7615 | -61.6516 | 54.2999 | 24.7421 | 8.844 | 8.3405 | 62.1277 | -61.7889 | -0.31586 | 0.041198 | 3.0991 | -0.20599 | -7.8506 | -0.34332 | -0.022888 | 3.4149 | 70.2896 | 69.7861 | 115.7455 | 123.6374 | 3.0991 | 123.5733 | 86.1877 | -0.34332 | 123.6374 | 3.0991 | 86.1877 | 115.7455 | 123.5733 | -123.912 | -123.9395
5132.7188 | 123.7976 | -61.4136 | 62.0865 | 0.067368 | 0.014742 | 0.01085 | 0.0074062 | 0.059821 | -0.0011877 | 0.079476 | -58.3694 | 62.059 | -61.7294 | -61.6196 | 54.6524 | 24.9069 | 8.6426 | 8.519 | 62.0865 | -61.6974 | -0.31586 | -0.027466 | 3.0441 | -0.20599 | -7.4341 | -0.28381 | 0 | 3.36 | 70.0562 | 69.9326 | 116.066 | 123.4726 | 3.0441 | 123.5001 | 86.3205 | -0.28381 | 123.4726 | 3.0441 | 86.3205 | 116.066 | 123.5001 | -123.8159 | -123.7839
5133.7188 | 123.6923 | -61.4594 | 62.1048 | 0.11314 | 0.017519 | 0.011704 | 0.018087 | 0.063452 | -0.00097413 | 0.07969 | -58.3603 | 62.1689 | -61.7523 | -61.6837 | 54.2999 | 24.4629 | 8.8669 | 8.3817 | 62.1323 | -61.7935 | -0.29297 | 0.064087 | 3.0991 | -0.2243 | -7.8049 | -0.33417 | 0.027466 | 3.392 | 70.3262 | 69.841 | 115.7593 | 123.6282 | 3.0991 | 123.5916 | 85.9222 | -0.33417 | 123.6282 | 3.0991 | 85.9222 | 115.7593 | 123.5916 | -123.8571 | -123.8983
5134.7188 | 123.7701 | -61.4502 | 62.0911 | 0.21233 | 0.013674 | 0.012345 | 0.014029 | 0.063239 | -0.0028967 | 0.078408 | -58.3649 | 62.1414 | -61.7615 | -61.6333 | 54.364 | 24.7925 | 8.8257 | 8.4732 | 62.0911 | -61.7523 | -0.31128 | 0.050354 | 3.0853 | -0.18311 | -7.7271 | -0.30212 | 0 | 3.3966 | 70.2759 | 69.9234 | 115.8142 | 123.5916 | 3.0853 | 123.5413 | 86.2427 | -0.30212 | 123.5916 | 3.0853 | 86.2427 | 115.8142 | 123.5413 | -123.8525 | -123.8434
5135.7188 | 123.6465 | -61.4182 | 62.146 | -0.25307 | 0.01581 | 0.012345 | 0.011892 | 0.062598 | -0.0024695 | 0.077554 | -58.3649 | 62.1689 | -61.7706 | -61.6104 | 54.3777 | 24.8016 | 8.963 | 8.5419 | 62.1643 | -61.7569 | -0.35248 | 0.022888 | 3.0533 | -0.19226 | -7.7682 | -0.33875 | 0.018311 | 3.4058 | 70.3812 | 69.96 | 115.7959 | 123.587 | 3.0533 | 123.5825 | 86.2198 | -0.33875 | 123.587 | 3.0533 | 86.2198 | 115.7959 | 123.5825 | -123.9166 | -123.9029
5136.7188 | 123.7244 | -61.4594 | 62.1368 | 0.13603 | 0.016878 | 0.013841 | 0.015524 | 0.058325 | 9.4068e-05 | 0.077767 | -58.3786 | 62.1735 | -61.7752 | -61.6837 | 54.3732 | 24.7055 | 8.8852 | 8.4503 | 62.1552 | -61.7661 | -0.31586 | 0.036621 | 3.0807 | -0.2243 | -7.7637 | -0.3067 | 0.01831 | 3.3966 | 70.3445 | 69.9097 | 115.8325 | 123.6328 | 3.0807 | 123.6145 | 86.1649 | -0.3067 | 123.6328 | 3.0807 | 86.1649 | 115.8325 | 123.6145 | -123.912 | -123.9029
5137.7188 | 123.7976 | -61.4227 | 62.0728 | 0.17418 | 0.01282 | 0.012559 | 0.012106 | 0.062384 | -0.0016149 | 0.08204 | -58.4564 | 62.0682 | -61.7706 | -61.5875 | 54.4281 | 24.939 | 8.7158 | 8.519 | 62.0911 | -61.7249 | -0.3479 | -0.004578 | 2.9663 | -0.1648 | -7.6447 | -0.30213 | 0.01831 | 3.3142 | 70.1385 | 69.9417 | 115.8508 | 123.4909 | 2.9663 | 123.5138 | 86.3617 | -0.30213 | 123.4909 | 2.9663 | 86.3617 | 115.8508 | 123.5138 | -123.8434 | -123.7976
5138.7188 | 123.7976 | -61.4182 | 62.0865 | 0.22758 | 0.016451 | 0.011491 | 0.014669 | 0.062598 | 9.4068e-05 | 0.077981 | -58.3328 | 62.1231 | -61.7523 | -61.5875 | 54.4189 | 24.7971 | 8.6975 | 8.5144 | 62.0728 | -61.7386 | -0.33417 | 0.036621 | 3.0853 | -0.16937 | -7.6675 | -0.32043 | -0.013733 | 3.4195 | 70.1157 | 69.9326 | 115.8371 | 123.5413 | 3.0853 | 123.4909 | 86.2152 | -0.32043 | 123.5413 | 3.0853 | 86.2152 | 115.8371 | 123.4909 | -123.8388 | -123.8251
5139.7188 | 123.8159 | -61.441 | 62.0773 | 0.2047 | 0.017733 | 0.012345 | 0.015524 | 0.061743 | -0.0018285 | 0.080544 | -58.3328 | 62.114 | -61.7477 | -61.615 | 54.4052 | 24.8016 | 8.7158 | 8.4091 | 62.0911 | -61.7386 | -0.3067 | 0.036621 | 3.1082 | -0.17395 | -7.6721 | -0.29755 | 0.013732 | 3.4149 | 70.1569 | 69.8502 | 115.8463 | 123.555 | 3.1082 | 123.5321 | 86.2427 | -0.29755 | 123.555 | 3.1082 | 86.2427 | 115.8463 | 123.5321 | -123.8251 | -123.8159
5140.7188 | 123.7152 | -61.4594 | 62.1323 | -0.0012969 | 0.015169 | 0.017472 | 0.015524 | 0.061743 | -0.0014013 | 0.080117 | -58.3191 | 62.1964 | -61.7569 | -61.647 | 54.3549 | 24.6872 | 8.9081 | 8.3633 | 62.146 | -61.7889 | -0.29755 | 0.064087 | 3.1403 | -0.18768 | -7.7774 | -0.32959 | 0.013733 | 3.4378 | 70.3674 | 69.8227 | 115.8142 | 123.6557 | 3.1403 | 123.6053 | 86.1465 | -0.32959 | 123.6557 | 3.1403 | 86.1465 | 115.8142 | 123.6053 | -123.8892 | -123.9212
5141.7188 | 123.6832 | -61.4273 | 62.1231 | 0.067368 | 0.017733 | 0.014482 | 0.017233 | 0.060462 | 0.00030767 | 0.077554 | -58.3328 | 62.1918 | -61.7477 | -61.647 | 54.3411 | 24.5819 | 8.9264 | 8.3862 | 62.146 | -61.7889 | -0.32044 | 0.068664 | 3.0945 | -0.21973 | -7.782 | -0.36163 | 0.022888 | 3.4149 | 70.3537 | 69.8135 | 115.7684 | 123.6191 | 3.0945 | 123.5733 | 86.0092 | -0.36163 | 123.6191 | 3.0945 | 86.0092 | 115.7684 | 123.5733 | -123.8709 | -123.912
5142.7344 | 123.8022 | -61.3998 | 62.0956 | 0.1284 | 0.016024 | 0.014054 | 0.0097562 | 0.060675 | -0.00076053 | 0.078622 | -58.342 | 62.0636 | -61.7477 | -61.5829 | 54.4052 | 24.6735 | 8.725 | 8.4549 | 62.0728 | -61.734 | -0.3479 | -0.032043 | 3.0579 | -0.18311 | -7.6904 | -0.33417 | -0.022888 | 3.4058 | 70.1248 | 69.8547 | 115.8051 | 123.4634 | 3.0579 | 123.4726 | 86.0733 | -0.33417 | 123.4634 | 3.0579 | 86.0733 | 115.8051 | 123.4726 | -123.8434 | -123.8297
5143.7188 | 123.7747 | -61.441 | 62.1002 | 0.28099 | 0.015597 | 0.015336 | 0.014669 | 0.062171 | -0.00054693 | 0.079476 | -58.3466 | 62.114 | -61.7661 | -61.6333 | 54.364 | 24.6231 | 8.7753 | 8.3817 | 62.0911 | -61.7752 | -0.32501 | 0.013733 | 3.0945 | -0.19226 | -7.7362 | -0.33417 | -0.009156 | 3.4195 | 70.2164 | 69.8227 | 115.8051 | 123.555 | 3.0945 | 123.5321 | 86.0641 | -0.33417 | 123.555 | 3.0945 | 86.0641 | 115.8051 | 123.5321 | -123.8663 | -123.8754
5144.7188 | 123.8892 | -61.4319 | 62.027 | 0.19707 | 0.014529 | 0.013841 | 0.010183 | 0.062171 | -0.00076053 | 0.079263 | -58.2779 | 62.1048 | -61.7294 | -61.5875 | 54.4235 | 24.7421 | 8.7479 | 8.4549 | 62.0773 | -61.7432 | -0.29755 | 0.077819 | 3.154 | -0.15564 | -7.6035 | -0.31128 | 0.050354 | 3.4515 | 70.1797 | 69.8868 | 115.8554 | 123.5367 | 3.154 | 123.5092 | 86.174 | -0.31128 | 123.5367 | 3.154 | 86.174 | 115.8554 | 123.5092 | -123.7564 | -123.7701
5145.7188 | 123.7015 | -61.4639 | 62.1277 | 0.04448 | 0.017306 | 0.013841 | 0.01531 | 0.060889 | -0.00033333 | 0.078835 | -58.3603 | 62.1643 | -61.7706 | -61.6791 | 54.3091 | 24.6368 | 8.9584 | 8.3267 | 62.1368 | -61.7752 | -0.3067 | 0.036621 | 3.1036 | -0.21515 | -7.8186 | -0.31128 | 0.009155 | 3.4103 | 70.4224 | 69.7906 | 115.773 | 123.6282 | 3.1036 | 123.6008 | 86.1008 | -0.31128 | 123.6282 | 3.1036 | 86.1008 | 115.773 | 123.6008 | -123.8983 | -123.9029
5146.7188 | 123.7381 | -61.441 | 62.1094 | 0.36491 | 0.01816 | 0.0097818 | 0.015524 | 0.063025 | -0.00097413 | 0.081613 | -58.3282 | 62.1964 | -61.7752 | -61.6882 | 54.3823 | 24.733 | 8.844 | 8.3267 | 62.1231 | -61.7844 | -0.33417 | 0.086975 | 3.1128 | -0.24719 | -7.7271 | -0.34332 | 0.013733 | 3.447 | 70.285 | 69.7678 | 115.8234 | 123.6374 | 3.1128 | 123.5641 | 86.174 | -0.34332 | 123.6374 | 3.1128 | 86.174 | 115.8234 | 123.5641 | -123.8846 | -123.8937
5147.7344 | 123.8022 | -61.4044 | 62.114 | 0.029221 | 0.014529 | 0.005723 | 0.006979 | 0.059821 | 9.4068e-05 | 0.079904 | -58.3557 | 62.059 | -61.734 | -61.6241 | 54.4235 | 24.7238 | 9.0637 | 8.4961 | 62.1414 | -61.6745 | -0.32959 | -0.054932 | 3.0487 | -0.21973 | -7.6904 | -0.27008 | 0.027465 | 3.3783 | 70.4681 | 69.9005 | 115.8279 | 123.4634 | 3.0487 | 123.5458 | 86.1282 | -0.27008 | 123.4634 | 3.0487 | 86.1282 | 115.8279 | 123.5458 | -123.848 | -123.7885
5148.7188 | 123.6877 | -61.4777 | 62.1323 | 0.11314 | 0.016024 | 0.016404 | 0.016378 | 0.062171 | -0.00097413 | 0.076913 | -58.3603 | 62.1826 | -61.7432 | -61.702 | 54.3549 | 24.6735 | 8.8989 | 8.313 | 62.1414 | -61.7661 | -0.2655 | 0.050354 | 3.1174 | -0.2243 | -7.7774 | -0.28839 | 0.009155 | 3.3829 | 70.3766 | 69.7906 | 115.8325 | 123.6603 | 3.1174 | 123.6191 | 86.1511 | -0.28839 | 123.6603 | 3.1174 | 86.1511 | 115.8325 | 123.6191 | -123.8754 | -123.8983
5149.7188 | 123.7518 | -61.4319 | 62.1048 | 0.18944 | 0.016878 | 0.0097818 | 0.014029 | 0.062598 | -0.0028967 | 0.080331 | -58.3694 | 62.1323 | -61.7981 | -61.6379 | 54.3961 | 24.7742 | 8.8074 | 8.3817 | 62.114 | -61.7661 | -0.36621 | 0.027466 | 3.0624 | -0.20599 | -7.7087 | -0.33417 | 0.009156 | 3.4286 | 70.2393 | 69.8135 | 115.8279 | 123.5641 | 3.0624 | 123.5458 | 86.2061 | -0.33417 | 123.5641 | 3.0624 | 86.2061 | 115.8279 | 123.5458 | -123.9029 | -123.8708
5150.7188 | 123.761 | -61.4502 | 62.1048 | 0.21996 | 0.017947 | 0.012345 | 0.014883 | 0.06153 | -0.0016149 | 0.079904 | -58.3511 | 62.1414 | -61.7844 | -61.6287 | 54.3777 | 24.6689 | 8.8348 | 8.4183 | 62.1506 | -61.7706 | -0.33417 | 0.036621 | 3.0991 | -0.17853 | -7.727 | -0.32043 | 0.045777 | 3.4332 | 70.285 | 69.8685 | 115.8279 | 123.5916 | 3.0991 | 123.6008 | 86.1191 | -0.32043 | 123.5916 | 3.0991 | 86.1191 | 115.8279 | 123.6008 | -123.8892 | -123.8754
5151.7188 | 123.7976 | -61.4227 | 62.0636 | 0.2581 | 0.014315 | 0.013413 | 0.010611 | 0.060462 | -0.0011877 | 0.078835 | -58.3099 | 62.0865 | -61.7294 | -61.5784 | 54.4235 | 24.9161 | 8.7112 | 8.5144 | 62.059 | -61.7386 | -0.3067 | 0.022888 | 3.1128 | -0.15564 | -7.6401 | -0.31586 | -0.004578 | 3.4195 | 70.134 | 69.9371 | 115.8463 | 123.5092 | 3.1128 | 123.4818 | 86.3388 | -0.31586 | 123.5092 | 3.1128 | 86.3388 | 115.8463 | 123.4818 | -123.793 | -123.8022
5152.7344 | 123.8617 | -61.3815 | 62.1048 | -0.11574 | 0.013247 | 0.0093546 | 0.0078336 | 0.058753 | 9.4068e-05 | 0.078835 | -58.287 | 62.0819 | -61.7386 | -61.5601 | 54.5059 | 24.971 | 8.7708 | 8.5876 | 62.0956 | -61.7249 | -0.35705 | -0.022888 | 3.0945 | -0.17853 | -7.5989 | -0.34332 | -0.009155 | 3.4515 | 70.1523 | 69.9692 | 115.8875 | 123.4634 | 3.0945 | 123.4772 | 86.3525 | -0.34332 | 123.4634 | 3.0945 | 86.3525 | 115.8875 | 123.4772 | -123.8434 | -123.8297
5153.7188 | 123.6969 | -61.4594 | 62.1094 | 0.38017 | 0.017092 | 0.015763 | 0.016592 | 0.060034 | 0.00030767 | 0.079263 | -58.3557 | 62.1735 | -61.7889 | -61.6882 | 54.3411 | 24.8016 | 8.8715 | 8.4045 | 62.1048 | -61.7981 | -0.32959 | 0.064087 | 3.1036 | -0.22888 | -7.7683 | -0.33875 | -0.004578 | 3.4332 | 70.3308 | 69.8639 | 115.8005 | 123.6328 | 3.1036 | 123.5641 | 86.261 | -0.33875 | 123.6328 | 3.1036 | 86.261 | 115.8005 | 123.5641 | -123.8983 | -123.9075
5154.7188 | 123.8159 | -61.4273 | 62.0773 | 0.28099 | 0.013888 | 0.01085 | 0.01296 | 0.061103 | -0.00097413 | 0.079049 | -58.3145 | 62.0682 | -61.7432 | -61.5784 | 54.4373 | 24.939 | 8.6884 | 8.5052 | 62.0819 | -61.7111 | -0.31586 | -0.009156 | 3.1128 | -0.15106 | -7.6401 | -0.28381 | 0.004577 | 3.4286 | 70.1157 | 69.9326 | 115.8646 | 123.4955 | 3.1128 | 123.5092 | 86.3663 | -0.28381 | 123.4955 | 3.1128 | 86.3663 | 115.8646 | 123.5092 | -123.8205 | -123.7885
5155.7188 | 123.7656 | -61.4639 | 62.0911 | 0.16655 | 0.017092 | 0.012345 | 0.016592 | 0.060889 | -0.0037511 | 0.078408 | -58.3557 | 62.1231 | -61.7935 | -61.6425 | 54.4052 | 24.8703 | 8.8074 | 8.4274 | 62.0911 | -61.7844 | -0.32959 | 0.032044 | 3.1082 | -0.17853 | -7.6859 | -0.32043 | 0 | 3.4378 | 70.2713 | 69.8914 | 115.8691 | 123.587 | 3.1082 | 123.555 | 86.3342 | -0.32043 | 123.587 | 3.1082 | 86.3342 | 115.8691 | 123.555 | -123.8846 | -123.8754
5156.7188 | 123.6923 | -61.4502 | 62.1094 | 1.0973 | 0.013033 | 0.0097818 | 0.015951 | 0.062171 | -0.0016149 | 0.075845 | -58.1268 | 62.1368 | -61.7615 | -61.6241 | 54.3686 | 24.9527 | 8.8806 | 8.3633 | 62.1185 | -61.7935 | -0.31128 | 0.027466 | 3.3234 | -0.17395 | -7.7408 | -0.34332 | 0.009155 | 3.6346 | 70.3308 | 69.8135 | 115.8188 | 123.587 | 3.3234 | 123.5687 | 86.4029 | -0.34332 | 123.587 | 3.3234 | 86.4029 | 115.8188 | 123.5687 | -123.8708 | -123.9029
5157.7188 | 123.8205 | -61.4182 | 62.0911 | 0.15129 | 0.014101 | 0.012132 | 0.0095424 | 0.059394 | -0.0020421 | 0.078622 | -58.3237 | 62.0453 | -61.7798 | -61.6058 | 54.4601 | 24.9939 | 8.6746 | 8.4503 | 62.0956 | -61.7294 | -0.36163 | -0.045776 | 3.0945 | -0.18768 | -7.6309 | -0.31128 | 0.004578 | 3.4561 | 70.0928 | 69.8685 | 115.8783 | 123.4634 | 3.0945 | 123.5138 | 86.412 | -0.31128 | 123.4634 | 3.0945 | 86.412 | 115.8783 | 123.5138 | -123.8708 | -123.8205
5158.7188 | 123.8297 | -61.4136 | 62.0773 | 0.18181 | 0.016878 | 0.016831 | 0.013388 | 0.061316 | -0.00097413 | 0.076486 | -58.3099 | 62.1002 | -61.7615 | -61.5738 | 54.4373 | 24.9573 | 8.6884 | 8.4915 | 62.0911 | -61.7569 | -0.3479 | 0.022888 | 3.1036 | -0.16022 | -7.6401 | -0.34332 | 0.013732 | 3.4515 | 70.1019 | 69.9051 | 115.8508 | 123.5138 | 3.1036 | 123.5046 | 86.3708 | -0.34332 | 123.5138 | 3.1036 | 86.3708 | 115.8508 | 123.5046 | -123.8388 | -123.8342
5159.7188 | 123.7885 | -61.4227 | 62.0819 | 0.082626 | 0.014529 | 0.011277 | 0.0093288 | 0.060034 | -0.00097413 | 0.080972 | -58.374 | 62.0361 | -61.7523 | -61.615 | 54.4647 | 24.852 | 8.812 | 8.5052 | 62.1002 | -61.7523 | -0.32959 | -0.045776 | 3.0487 | -0.19226 | -7.6172 | -0.32959 | 0.018311 | 3.3783 | 70.2347 | 69.928 | 115.8875 | 123.4589 | 3.0487 | 123.5229 | 86.2747 | -0.32959 | 123.4589 | 3.0487 | 86.2747 | 115.8875 | 123.5229 | -123.8342 | -123.8342
5160.7188 | 123.7244 | -61.4594 | 62.0865 | 0.21996 | 0.018587 | 0.0132 | 0.01766 | 0.061103 | -0.0035375 | 0.079476 | -58.3694 | 62.1506 | -61.7844 | -61.6653 | 54.3823 | 24.7925 | 8.876 | 8.4274 | 62.1277 | -61.7752 | -0.32501 | 0.064087 | 3.0899 | -0.20599 | -7.7042 | -0.31586 | 0.041199 | 3.4149 | 70.3354 | 69.8868 | 115.8417 | 123.6099 | 3.0899 | 123.587 | 86.2518 | -0.31586 | 123.6099 | 3.0899 | 86.2518 | 115.8417 | 123.587 | -123.8708 | -123.8617
5161.7188 | 123.793 | -61.4319 | 62.0773 | 0.22758 | 0.017733 | 0.017472 | 0.014669 | 0.061103 | -0.00054693 | 0.078408 | -58.3374 | 62.1002 | -61.7798 | -61.6013 | 54.3961 | 24.8154 | 8.812 | 8.519 | 62.1048 | -61.7477 | -0.3479 | 0.022888 | 3.0945 | -0.16937 | -7.6813 | -0.31586 | 0.027465 | 3.4424 | 70.2438 | 69.9509 | 115.8279 | 123.5321 | 3.0945 | 123.5367 | 86.2473 | -0.31586 | 123.5321 | 3.0945 | 86.2473 | 115.8279 | 123.5367 | -123.8571 | -123.8251
5162.7188 | 123.7289 | -61.4639 | 62.114 | 0.47173 | 0.016665 | 0.0085 | 0.015951 | 0.062171 | -0.00097413 | 0.079049 | -58.342 | 62.1552 | -61.7523 | -61.6653 | 54.3182 | 24.7513 | 8.9401 | 8.4732 | 62.1231 | -61.7798 | -0.28839 | 0.041198 | 3.1219 | -0.20142 | -7.7957 | -0.31586 | 0.009155 | 3.4103 | 70.4041 | 69.9371 | 115.7822 | 123.6191 | 3.1219 | 123.587 | 86.2152 | -0.31586 | 123.6191 | 3.1219 | 86.2152 | 115.7822 | 123.587 | -123.8663 | -123.8937
5163.7188 | 123.7335 | -61.4227 | 62.1048 | 0.19707 | 0.017092 | 0.014054 | 0.01531 | 0.062812 | -0.00076053 | 0.078408 | -58.3603 | 62.1277 | -61.7752 | -61.6425 | 54.4006 | 24.8703 | 8.8531 | 8.519 | 62.1277 | -61.7386 | -0.35248 | 0.022889 | 3.0624 | -0.21973 | -7.7042 | -0.31586 | 0.022889 | 3.4149 | 70.2759 | 69.9417 | 115.8234 | 123.5504 | 3.0624 | 123.5504 | 86.293 | -0.31586 | 123.5504 | 3.0624 | 86.293 | 115.8234 | 123.5504 | -123.88 | -123.8434
5164.7188 | 123.793 | -61.4182 | 62.0773 | 0.15892 | 0.013247 | 0.010636 | 0.010824 | 0.059821 | -0.00076053 | 0.076913 | -58.3328 | 62.059 | -61.7661 | -61.615 | 54.4235 | 24.9069 | 8.7799 | 8.5693 | 62.0636 | -61.7432 | -0.3479 | -0.018311 | 3.0853 | -0.19684 | -7.6538 | -0.32501 | -0.013733 | 3.4332 | 70.1981 | 69.9875 | 115.8417 | 123.4772 | 3.0853 | 123.4818 | 86.3251 | -0.32501 | 123.4772 | 3.0853 | 86.3251 | 115.8417 | 123.4818 | -123.8434 | -123.8205
5165.7188 | 123.7198 | -61.4456 | 62.0956 | 0.097885 | 0.016878 | 0.011064 | 0.017233 | 0.061103 | -0.00054693 | 0.078195 | -58.3557 | 62.1323 | -61.7798 | -61.6745 | 54.3823 | 24.8611 | 8.9401 | 8.5052 | 62.114 | -61.8027 | -0.33417 | 0.036621 | 3.0899 | -0.22888 | -7.7133 | -0.35705 | 0.018311 | 3.4241 | 70.3857 | 69.9509 | 115.8279 | 123.5779 | 3.0899 | 123.5596 | 86.3068 | -0.35705 | 123.5779 | 3.0899 | 86.3068 | 115.8279 | 123.5596 | -123.8754 | -123.8983
5166.7188 | 123.8068 | -61.441 | 62.0956 | 0.21996 | 0.01816 | 0.013627 | 0.016165 | 0.063025 | -0.00076053 | 0.079476 | -58.3328 | 62.1323 | -61.7706 | -61.5967 | 54.4189 | 24.9252 | 8.8257 | 8.5785 | 62.0819 | -61.7569 | -0.32959 | 0.036621 | 3.1082 | -0.15564 | -7.6767 | -0.31586 | -0.013733 | 3.4378 | 70.2667 | 70.0195 | 115.86 | 123.5733 | 3.1082 | 123.5229 | 86.3663 | -0.31586 | 123.5733 | 3.1082 | 86.3663 | 115.86 | 123.5229 | -123.8663 | -123.8525
5167.7188 | 123.9075 | -61.4365 | 62.059 | 0.16655 | 0.016665 | 0.014054 | 0.011251 | 0.06153 | -0.00097413 | 0.081399 | -58.3008 | 62.0865 | -61.7523 | -61.5829 | 54.5105 | 24.8749 | 8.7158 | 8.313 | 62.0728 | -61.7706 | -0.31586 | 0.027466 | 3.1357 | -0.14648 | -7.5485 | -0.33417 | 0.013733 | 3.4515 | 70.1523 | 69.7494 | 115.947 | 123.5229 | 3.1357 | 123.5092 | 86.3113 | -0.33417 | 123.5229 | 3.1357 | 86.3113 | 115.947 | 123.5092 | -123.8113 | -123.8297
5168.7188 | 123.8297 | -61.4227 | 62.0911 | 0.15129 | 0.015597 | 0.009141 | 0.010183 | 0.062598 | -0.0011877 | 0.078835 | -58.2962 | 62.0499 | -61.7661 | -61.5875 | 54.5105 | 24.8795 | 8.7616 | 8.5098 | 62.0911 | -61.7477 | -0.34332 | -0.041198 | 3.1265 | -0.1648 | -7.5806 | -0.32501 | 0 | 3.4698 | 70.1843 | 69.9326 | 115.9332 | 123.4726 | 3.1265 | 123.5138 | 86.3022 | -0.32501 | 123.4726 | 3.1265 | 86.3022 | 115.9332 | 123.5138 | -123.8571 | -123.8388
5169.7188 | 123.8251 | -61.3998 | 62.1094 | -0.10811 | 0.014315 | 0.011277 | 0.008688 | 0.059607 | -0.00097413 | 0.077981 | -58.3145 | 62.1002 | -61.7111 | -61.5646 | 54.5517 | 24.8886 | 8.8211 | 8.5602 | 62.0911 | -61.7157 | -0.31128 | -0.009155 | 3.0853 | -0.16479 | -7.5577 | -0.31586 | -0.018311 | 3.3966 | 70.2209 | 69.96 | 115.9515 | 123.5001 | 3.0853 | 123.4909 | 86.2885 | -0.31586 | 123.5001 | 3.0853 | 86.2885 | 115.9515 | 123.4909 | -123.8205 | -123.8251
5170.7188 | 123.7015 | -61.4731 | 62.1323 | 0.15129 | 0.016665 | 0.012345 | 0.019156 | 0.062598 | -0.0020421 | 0.079049 | -58.6121 | 62.1323 | -61.8118 | -61.6608 | 54.3869 | 24.6414 | 8.9355 | 8.3679 | 62.1414 | -61.7798 | -0.33875 | 0 | 2.861 | -0.18768 | -7.7454 | -0.3067 | 0.009155 | 3.1998 | 70.4086 | 69.841 | 115.86 | 123.6053 | 2.861 | 123.6145 | 86.1145 | -0.3067 | 123.6053 | 2.861 | 86.1145 | 115.86 | 123.6145 | -123.9441 | -123.912
5171.7188 | 123.8251 | -61.4182 | 62.0819 | 0.21233 | 0.016024 | 0.014054 | 0.015097 | 0.06153 | 0.00030767 | 0.079263 | -58.3099 | 62.0956 | -61.7477 | -61.5738 | 54.5563 | 24.7513 | 8.7387 | 8.4961 | 62.1185 | -61.7386 | -0.32959 | 0.013733 | 3.1082 | -0.15564 | -7.5256 | -0.32043 | 0.036621 | 3.4378 | 70.1569 | 69.9142 | 115.9744 | 123.5138 | 3.1082 | 123.5367 | 86.1694 | -0.32043 | 123.5138 | 3.1082 | 86.1694 | 115.9744 | 123.5367 | -123.8297 | -123.8205
5172.7344 | 123.8159 | -61.409 | 62.1094 | -0.039444 | 0.014742 | 0.010636 | 0.008688 | 0.058112 | -0.0016149 | 0.079049 | -58.3237 | 62.0728 | -61.734 | -61.5509 | 54.5517 | 24.8108 | 8.7845 | 8.5785 | 62.1048 | -61.7111 | -0.32501 | -0.036621 | 3.0853 | -0.14191 | -7.5577 | -0.30212 | -0.004578 | 3.4103 | 70.1935 | 69.9875 | 115.9607 | 123.4818 | 3.0853 | 123.5138 | 86.2198 | -0.30212 | 123.4818 | 3.0853 | 86.2198 | 115.9607 | 123.5138 | -123.8434 | -123.8205
5173.7188 | 123.7793 | -61.441 | 62.1002 | 0.18944 | 0.017733 | 0.014909 | 0.018301 | 0.060462 | -0.00097413 | 0.078408 | -58.3466 | 62.1231 | -61.734 | -61.6104 | 54.4693 | 24.6689 | 8.8165 | 8.5327 | 62.0728 | -61.7615 | -0.29297 | 0.022888 | 3.0945 | -0.16937 | -7.6309 | -0.32043 | -0.027466 | 3.3875 | 70.2576 | 69.9738 | 115.9103 | 123.5641 | 3.0945 | 123.5138 | 86.1099 | -0.32043 | 123.5641 | 3.0945 | 86.1099 | 115.9103 | 123.5138 | -123.8342 | -123.8617
5174.7188 | 123.8709 | -61.377 | 62.146 | -0.13863 | 0.013033 | 0.011277 | 0.010824 | 0.05918 | -0.0011877 | 0.079263 | -58.2779 | 62.059 | -61.7432 | -61.5051 | 54.6341 | 24.7421 | 8.8669 | 8.67 | 62.0956 | -61.702 | -0.36621 | -0.086975 | 3.0991 | -0.12817 | -7.5119 | -0.32501 | -0.050354 | 3.4653 | 70.2438 | 70.047 | 116.011 | 123.436 | 3.0991 | 123.4726 | 86.1191 | -0.32501 | 123.436 | 3.0991 | 86.1191 | 116.011 | 123.4726 | -123.8892 | -123.848
5175.7188 | 123.8022 | -61.4136 | 62.1002 | 0.090256 | 0.016878 | 0.012132 | 0.016165 | 0.059821 | -0.0037511 | 0.077981 | -58.3237 | 62.0819 | -61.7569 | -61.5738 | 54.5288 | 24.6094 | 8.7662 | 8.5922 | 62.0636 | -61.7477 | -0.34332 | -0.018311 | 3.0899 | -0.16022 | -7.5714 | -0.33417 | -0.036621 | 3.4332 | 70.1797 | 70.0058 | 115.9424 | 123.4955 | 3.0899 | 123.4772 | 86.0229 | -0.33417 | 123.4955 | 3.0899 | 86.0229 | 115.9424 | 123.4772 | -123.8571 | -123.848
5176.7188 | 123.8022 | -61.409 | 62.0682 | 0.2047 | 0.016878 | 0.0099954 | 0.016165 | 0.061957 | -0.0018285 | 0.079049 | -58.3282 | 62.1048 | -61.7477 | -61.5738 | 54.5197 | 24.6506 | 8.7433 | 8.5785 | 62.0819 | -61.7386 | -0.33875 | 0.036621 | 3.0808 | -0.16479 | -7.5485 | -0.32959 | 0.013733 | 3.4195 | 70.1523 | 69.9875 | 115.9287 | 123.5138 | 3.0808 | 123.4909 | 86.0596 | -0.32959 | 123.5138 | 3.0808 | 86.0596 | 115.9287 | 123.4909 | -123.8159 | -123.8068
5177.7188 | 123.793 | -61.3998 | 62.1002 | 0.15129 | 0.014315 | 0.012773 | 0.0089016 | 0.061103 | -0.0022559 | 0.078408 | -58.3145 | 62.0544 | -61.7569 | -61.5829 | 54.538 | 24.7925 | 8.7616 | 8.5831 | 62.0819 | -61.7477 | -0.35706 | -0.045777 | 3.0853 | -0.18311 | -7.5623 | -0.3479 | -0.018311 | 3.4424 | 70.1614 | 69.9829 | 115.9378 | 123.4543 | 3.0853 | 123.4818 | 86.1923 | -0.3479 | 123.4543 | 3.0853 | 86.1923 | 115.9378 | 123.4818 | -123.8571 | -123.848
5178.7188 | 123.761 | -61.4502 | 62.114 | 0.21233 | 0.017306 | 0.013413 | 0.018087 | 0.059821 | 0.00052127 | 0.079476 | -58.3694 | 62.1689 | -61.7569 | -61.6379 | 54.4098 | 24.6552 | 8.9127 | 8.4869 | 62.1277 | -61.7661 | -0.3067 | 0.054931 | 3.0807 | -0.18768 | -7.7042 | -0.31586 | 0.013733 | 3.3875 | 70.3629 | 69.9371 | 115.86 | 123.6191 | 3.0807 | 123.5779 | 86.1053 | -0.31586 | 123.6191 | 3.0807 | 86.1053 | 115.86 | 123.5779 | -123.8709 | -123.88
5179.7188 | 123.7793 | -61.4182 | 62.0865 | 0.15892 | 0.015383 | 0.0093546 | 0.010611 | 0.058325 | -0.0011877 | 0.076486 | -58.3511 | 62.0544 | -61.7569 | -61.6241 | 54.4739 | 24.8016 | 8.8394 | 8.5281 | 62.0728 | -61.7386 | -0.33875 | -0.032044 | 3.067 | -0.20599 | -7.6126 | -0.32043 | -0.013733 | 3.4058 | 70.2576 | 69.9463 | 115.892 | 123.4726 | 3.067 | 123.4909 | 86.2198 | -0.32043 | 123.4726 | 3.067 | 86.2198 | 115.892 | 123.4909 | -123.8434 | -123.8251
5180.7188 | 123.6923 | -61.4822 | 62.1323 | -0.54298 | 0.015169 | 0.014268 | 0.015951 | 0.060248 | -0.0024695 | 0.080117 | -58.2733 | 62.1689 | -61.7798 | -61.6425 | 54.4006 | 24.7101 | 8.9218 | 8.4412 | 62.1231 | -61.7981 | -0.29755 | 0.036621 | 3.2089 | -0.16022 | -7.7316 | -0.31586 | -0.009155 | 3.5065 | 70.4041 | 69.9234 | 115.8829 | 123.6511 | 3.2089 | 123.6053 | 86.1923 | -0.31586 | 123.6511 | 3.2089 | 86.1923 | 115.8829 | 123.6053 | -123.912 | -123.9304
5181.7188 | 123.6969 | -61.4639 | 62.114 | 0.2047 | 0.02051 | 0.012773 | 0.014883 | 0.063025 | -0.0018285 | 0.079049 | -58.493 | 62.1323 | -61.7844 | -61.6104 | 54.3732 | 24.5865 | 9.0225 | 8.4595 | 62.1506 | -61.7935 | -0.32043 | 0.01831 | 2.9709 | -0.14648 | -7.7408 | -0.32959 | 0.036621 | 3.2913 | 70.4865 | 69.9234 | 115.8371 | 123.5962 | 2.9709 | 123.6145 | 86.0504 | -0.32959 | 123.5962 | 2.9709 | 86.0504 | 115.8371 | 123.6145 | -123.8983 | -123.9075
5182.7188 | 123.8159 | -61.4182 | 62.0682 | 0.45647 | 0.014956 | 0.014054 | 0.011465 | 0.062171 | -0.0014013 | 0.078835 | -58.1772 | 62.0728 | -61.734 | -61.5509 | 54.5105 | 24.7055 | 8.812 | 8.6334 | 62.0865 | -61.7111 | -0.31586 | 0.004578 | 3.241 | -0.13275 | -7.5577 | -0.29297 | 0.018311 | 3.5568 | 70.2301 | 70.0516 | 115.9287 | 123.4909 | 3.241 | 123.5046 | 86.1237 | -0.29297 | 123.4909 | 3.241 | 86.1237 | 115.9287 | 123.5046 | -123.8022 | -123.7793
5183.7188 | 123.7518 | -61.4502 | 62.1002 | 0.12077 | 0.016238 | 0.010423 | 0.016378 | 0.06153 | -0.0014013 | 0.078408 | -58.3786 | 62.1643 | -61.7935 | -61.6425 | 54.364 | 24.5682 | 8.9035 | 8.5236 | 62.114 | -61.7844 | -0.34332 | 0.064087 | 3.0716 | -0.19226 | -7.7362 | -0.33417 | 0.013733 | 3.4149 | 70.3537 | 69.9738 | 115.8142 | 123.6145 | 3.0716 | 123.5641 | 86.0184 | -0.33417 | 123.6145 | 3.0716 | 86.0184 | 115.8142 | 123.5641 | -123.8937 | -123.8846
5184.7188 | 123.8663 | -61.3861 | 62.0911 | -0.131 | 0.01346 | 0.011064 | 0.010611 | 0.060675 | -0.00097413 | 0.079476 | -58.3054 | 62.0956 | -61.7249 | -61.5097 | 54.5334 | 24.7009 | 8.8348 | 8.6472 | 62.1185 | -61.7157 | -0.33875 | 0.004578 | 3.0807 | -0.1236 | -7.5577 | -0.32959 | 0.027466 | 3.4195 | 70.2209 | 70.0333 | 115.9195 | 123.4818 | 3.0807 | 123.5046 | 86.087 | -0.32959 | 123.4818 | 3.0807 | 86.087 | 115.9195 | 123.5046 | -123.8159 | -123.8068
5185.7188 | 123.8205 | -61.4227 | 62.0865 | 0.18181 | 0.017519 | 0.011064 | 0.016806 | 0.060034 | -0.00097413 | 0.078195 | -58.3282 | 62.1094 | -61.7661 | -61.5921 | 54.4556 | 24.6323 | 8.7479 | 8.5052 | 62.0636 | -61.7432 | -0.34332 | 0.022888 | 3.0945 | -0.16937 | -7.6309 | -0.32044 | -0.022888 | 3.4378 | 70.1706 | 69.928 | 115.8783 | 123.5321 | 3.0945 | 123.4863 | 86.055 | -0.32044 | 123.5321 | 3.0945 | 86.055 | 115.8783 | 123.4863 | -123.8525 | -123.8297
5186.7188 | 123.7152 | -61.4456 | 62.0728 | 0.15892 | 0.014529 | 0.011064 | 0.017019 | 0.061743 | -0.0018285 | 0.077126 | -58.3603 | 62.1643 | -61.7798 | -61.6562 | 54.4144 | 24.4995 | 8.9172 | 8.4778 | 62.1094 | -61.7615 | -0.33417 | 0.091553 | 3.0853 | -0.21057 | -7.6584 | -0.31586 | 0.036621 | 3.4195 | 70.3629 | 69.9234 | 115.86 | 123.6099 | 3.0853 | 123.555 | 85.9451 | -0.31586 | 123.6099 | 3.0853 | 85.9451 | 115.86 | 123.555 | -123.8525 | -123.8342
5187.7344 | 123.7839 | -61.4365 | 62.0956 | 0.052109 | 0.011324 | 0.010209 | 0.011251 | 0.061957 | -0.0020421 | 0.080117 | -58.2138 | 62.0865 | -61.702 | -61.6196 | 54.483 | 24.6872 | 8.8577 | 8.6014 | 62.1048 | -61.7065 | -0.2655 | -0.009155 | 3.2227 | -0.18311 | -7.6126 | -0.27008 | 0.009155 | 3.4882 | 70.2942 | 70.0378 | 115.9195 | 123.5229 | 3.2227 | 123.5413 | 86.1237 | -0.27008 | 123.5229 | 3.2227 | 86.1237 | 115.9195 | 123.5413 | -123.7976 | -123.8022
5188.7188 | 123.7381 | -61.4731 | 62.1048 | 0.18181 | 0.017733 | 0.013627 | 0.014029 | 0.05918 | -0.0020421 | 0.077767 | -58.3786 | 62.1552 | -61.7798 | -61.6608 | 54.4281 | 24.5911 | 8.876 | 8.4412 | 62.0956 | -61.7935 | -0.3067 | 0.050354 | 3.0945 | -0.18768 | -7.6767 | -0.32043 | -0.009155 | 3.4012 | 70.3491 | 69.9142 | 115.9012 | 123.6282 | 3.0945 | 123.5687 | 86.0641 | -0.32043 | 123.6282 | 3.0945 | 86.0641 | 115.9012 | 123.5687 | -123.8846 | -123.8983
5189.7188 | 123.8159 | -61.3953 | 62.0911 | -0.077591 | 0.01346 | 0.012559 | 0.0095424 | 0.058966 | -0.00097413 | 0.078195 | -58.3237 | 62.1094 | -61.7203 | -61.5463 | 54.5425 | 24.6597 | 8.757 | 8.5831 | 62.1094 | -61.7111 | -0.32501 | 0.018311 | 3.0716 | -0.15106 | -7.5485 | -0.31586 | 0.018311 | 3.3966 | 70.1523 | 69.9783 | 115.9378 | 123.5046 | 3.0716 | 123.5046 | 86.055 | -0.31586 | 123.5046 | 3.0716 | 86.055 | 115.9378 | 123.5046 | -123.8113 | -123.8022
5190.7188 | 123.7289 | -61.4685 | 62.1231 | 0.14366 | 0.016451 | 0.0097818 | 0.01766 | 0.058753 | -0.0031103 | 0.078622 | -58.3878 | 62.146 | -61.7615 | -61.6608 | 54.4281 | 24.5865 | 8.8989 | 8.4137 | 62.1185 | -61.7889 | -0.29297 | 0.022888 | 3.0807 | -0.19226 | -7.695 | -0.32043 | -0.004578 | 3.3737 | 70.3674 | 69.8822 | 115.8966 | 123.6145 | 3.0807 | 123.587 | 86.055 | -0.32043 | 123.6145 | 3.0807 | 86.055 | 115.8966 | 123.587 | -123.8846 | -123.912
5191.7188 | 123.8159 | -61.441 | 62.1048 | 0.17418 | 0.017306 | 0.013841 | 0.014456 | 0.063025 | -0.0022559 | 0.079904 | -58.3466 | 62.1323 | -61.7706 | -61.5967 | 54.4327 | 24.7009 | 8.7799 | 8.4869 | 62.0956 | -61.7432 | -0.32959 | 0.027466 | 3.0945 | -0.15564 | -7.6721 | -0.30212 | -0.009155 | 3.4241 | 70.2209 | 69.928 | 115.8737 | 123.5733 | 3.0945 | 123.5367 | 86.142 | -0.30212 | 123.5733 | 3.0945 | 86.142 | 115.8737 | 123.5367 | -123.8754 | -123.848
5192.7188 | 123.7701 | -61.4319 | 62.0865 | 0.16655 | 0.016024 | 0.016831 | 0.008688 | 0.059607 | -0.00097413 | 0.078622 | -58.3511 | 62.0682 | -61.7477 | -61.6013 | 54.4647 | 24.8062 | 8.7936 | 8.5098 | 62.0865 | -61.7432 | -0.31586 | -0.018311 | 3.0808 | -0.16937 | -7.6218 | -0.31128 | 0 | 3.3966 | 70.2255 | 69.9417 | 115.8966 | 123.5001 | 3.0808 | 123.5184 | 86.2381 | -0.31128 | 123.5001 | 3.0808 | 86.2381 | 115.8966 | 123.5184 | -123.8342 | -123.8297
5193.7188 | 123.7839 | -61.4136 | 62.0453 | 0.21996 | 0.01581 | 0.011491 | 0.016592 | 0.060462 | -0.0031103 | 0.079263 | -58.2779 | 62.0911 | -61.7249 | -61.5784 | 54.4785 | 24.733 | 8.7433 | 8.5602 | 62.0728 | -61.7523 | -0.31128 | 0.045776 | 3.1357 | -0.1648 | -7.5668 | -0.33875 | 0.027466 | 3.447 | 70.1569 | 69.9738 | 115.892 | 123.5046 | 3.1357 | 123.4863 | 86.1465 | -0.33875 | 123.5046 | 3.1357 | 86.1465 | 115.892 | 123.4863 | -123.7701 | -123.7976
5194.7188 | 123.7793 | -61.3861 | 62.1323 | -0.22255 | 0.016238 | 0.013627 | 0.011465 | 0.060248 | -0.00054693 | 0.077126 | -58.2916 | 62.1231 | -61.7065 | -61.5326 | 54.5288 | 24.8108 | 8.8715 | 8.6426 | 62.1048 | -61.7294 | -0.32044 | -0.009155 | 3.0945 | -0.14648 | -7.6035 | -0.34332 | -0.027466 | 3.4149 | 70.2576 | 70.0287 | 115.9149 | 123.5092 | 3.0945 | 123.4909 | 86.1969 | -0.34332 | 123.5092 | 3.0945 | 86.1969 | 115.9149 | 123.4909 | -123.8388 | -123.8617
5195.7188 | 123.8251 | -61.409 | 62.0956 | 0.30388 | 0.01346 | 0.012986 | 0.01531 | 0.060675 | -0.0011877 | 0.07969 | -58.3145 | 62.0728 | -61.7477 | -61.5738 | 54.5242 | 24.9207 | 8.7936 | 8.6197 | 62.0728 | -61.734 | -0.33875 | -0.022888 | 3.0945 | -0.16479 | -7.5714 | -0.32501 | -0.022888 | 3.4332 | 70.2026 | 70.0287 | 115.9332 | 123.4818 | 3.0945 | 123.4818 | 86.3297 | -0.32501 | 123.4818 | 3.0945 | 86.3297 | 115.9332 | 123.4818 | -123.8434 | -123.8297
5196.7344 | 123.7747 | -61.4365 | 62.1048 | -0.1844 | 0.012179 | 0.0095682 | 0.0099698 | 0.057898 | -0.0046057 | 0.077554 | -58.2687 | 62.0773 | -61.7477 | -61.4456 | 54.9408 | 25.0854 | 8.5648 | 8.7067 | 62.0865 | -61.7111 | -0.31128 | -0.027465 | 3.1677 | -0.009156 | -7.164 | -0.27466 | -0.01831 | 3.479 | 70.0012 | 70.1431 | 116.3773 | 123.5138 | 3.1677 | 123.5229 | 86.5219 | -0.27466 | 123.5138 | 3.1677 | 86.5219 | 116.3773 | 123.5229 | -123.8525 | -123.8159
5197.7188 | 123.793 | -61.4044 | 62.1277 | 0.067368 | 0.013247 | 0.0085 | 0.010824 | 0.058325 | -0.00076053 | 0.078622 | -58.3557 | 62.0499 | -61.734 | -61.6104 | 54.4556 | 24.7009 | 8.8943 | 8.5648 | 62.0728 | -61.7157 | -0.32959 | -0.07782 | 3.0487 | -0.20599 | -7.6721 | -0.31128 | -0.054932 | 3.3783 | 70.2988 | 69.9692 | 115.86 | 123.4543 | 3.0487 | 123.4772 | 86.1053 | -0.31128 | 123.4543 | 3.0487 | 86.1053 | 115.86 | 123.4772 | -123.8617 | -123.8434
5198.7344 | 123.848 | -61.377 | 62.1643 | -0.131 | 0.011111 | 0.012559 | 0.01232 | 0.057257 | 0.00030767 | 0.078622 | -58.2687 | 62.0636 | -61.7157 | -61.5051 | 54.5746 | 24.8291 | 8.8898 | 8.6563 | 62.0865 | -61.6882 | -0.33875 | -0.10071 | 3.1082 | -0.12817 | -7.5897 | -0.31128 | -0.07782 | 3.447 | 70.2667 | 70.0333 | 115.9515 | 123.4406 | 3.1082 | 123.4634 | 86.2061 | -0.31128 | 123.4406 | 3.1082 | 86.2061 | 115.9515 | 123.4634 | -123.88 | -123.8525
5199.7188 | 123.793 | -61.4136 | 62.1185 | 0.10551 | 0.014956 | 0.01085 | 0.012747 | 0.058753 | -0.00011953 | 0.079476 | -58.342 | 62.059 | -61.7432 | -61.6013 | 54.4785 | 24.7787 | 8.8989 | 8.5693 | 62.0911 | -61.7432 | -0.32959 | -0.059509 | 3.0716 | -0.18768 | -7.6401 | -0.32959 | -0.027466 | 3.4012 | 70.3125 | 69.9829 | 115.892 | 123.4726 | 3.0716 | 123.5046 | 86.1923 | -0.32959 | 123.4726 | 3.0716 | 86.1923 | 115.892 | 123.5046 | -123.8617 | -123.8617
5200.7188 | 123.7976 | -61.4273 | 62.059 | 0.1284 | 0.015169 | 0.012132 | 0.014669 | 0.058753 | -0.0022559 | 0.079263 | -58.3054 | 62.0773 | -61.7477 | -61.5646 | 54.4785 | 24.8108 | 8.8486 | 8.6105 | 62.0499 | -61.734 | -0.32044 | 0.018311 | 3.1219 | -0.13733 | -7.5806 | -0.3067 | -0.009155 | 3.4424 | 70.2759 | 70.0378 | 115.9058 | 123.5046 | 3.1219 | 123.4772 | 86.2381 | -0.3067 | 123.5046 | 3.1219 | 86.2381 | 115.9058 | 123.4772 | -123.8068 | -123.793
5201.7344 | 123.7106 | -61.4227 | 62.1414 | -0.19203 | 0.014101 | 0.0087138 | 0.016165 | 0.058539 | -0.0028967 | 0.076699 | -58.3694 | 62.1506 | -61.7661 | -61.6104 | 54.4235 | 24.7421 | 9.1507 | 8.6197 | 62.1506 | -61.734 | -0.34332 | 0.009156 | 3.0533 | -0.18768 | -7.7179 | -0.31128 | 0.009156 | 3.3966 | 70.5734 | 70.0424 | 115.8463 | 123.5733 | 3.0533 | 123.5733 | 86.1649 | -0.31128 | 123.5733 | 3.0533 | 86.1649 | 115.8463 | 123.5733 | -123.9075 | -123.8754
5202.7344 | 123.7518 | -61.3953 | 62.1231 | -0.2607 | 0.012392 | 0.0097818 | 0.011251 | 0.059394 | -0.0022559 | 0.076486 | -58.3008 | 62.1048 | -61.7203 | -61.5372 | 54.5242 | 24.8749 | 9.0271 | 8.7112 | 62.1414 | -61.6974 | -0.32501 | -0.018311 | 3.0945 | -0.14191 | -7.5989 | -0.30212 | 0.01831 | 3.4195 | 70.4224 | 70.1065 | 115.9195 | 123.5001 | 3.0945 | 123.5367 | 86.2701 | -0.30212 | 123.5001 | 3.0945 | 86.2701 | 115.9195 | 123.5367 | -123.8434 | -123.8205
5203.7188 | 123.8754 | -61.4502 | 62.0865 | 0.15129 | 0.016878 | 0.0095682 | 0.014883 | 0.060675 | 9.4068e-05 | 0.078835 | -58.3054 | 62.0682 | -61.7523 | -61.5646 | 54.5334 | 24.8062 | 8.7708 | 8.6243 | 62.059 | -61.7432 | -0.30212 | -0.018311 | 3.1448 | -0.11444 | -7.5531 | -0.29297 | -0.027466 | 3.447 | 70.2209 | 70.0745 | 115.9836 | 123.5184 | 3.1448 | 123.5092 | 86.2564 | -0.29297 | 123.5184 | 3.1448 | 86.2564 | 115.9836 | 123.5092 | -123.8388 | -123.8297
5204.7188 | 123.7701 | -61.4227 | 62.0911 | 0.03685 | 0.015169 | 0.009141 | 0.010611 | 0.057685 | -0.00011953 | 0.078195 | -58.3511 | 62.1002 | -61.7477 | -61.5921 | 54.4464 | 25.0351 | 8.8531 | 8.5281 | 62.1048 | -61.7203 | -0.32501 | 0.009156 | 3.0716 | -0.16937 | -7.6447 | -0.29755 | 0.013733 | 3.3966 | 70.2759 | 69.9509 | 115.8691 | 123.5229 | 3.0716 | 123.5275 | 86.4578 | -0.29755 | 123.5229 | 3.0716 | 86.4578 | 115.8691 | 123.5275 | -123.8388 | -123.8113
5205.7188 | 123.8113 | -61.4182 | 62.0956 | 0.16655 | 0.017947 | 0.014482 | 0.015524 | 0.059607 | -0.00054693 | 0.077554 | -58.2962 | 62.0682 | -61.7615 | -61.5646 | 54.57 | 24.8337 | 8.8165 | 8.5327 | 62.0636 | -61.7615 | -0.34332 | -0.027466 | 3.1219 | -0.14648 | -7.5256 | -0.34332 | -0.032043 | 3.4653 | 70.2347 | 69.9509 | 115.9882 | 123.4863 | 3.1219 | 123.4818 | 86.2518 | -0.34332 | 123.4863 | 3.1219 | 86.2518 | 115.9882 | 123.4818 | -123.8571 | -123.8571
5206.7344 | 123.8342 | -61.3953 | 62.1094 | -0.12337 | 0.01346 | 0.0099954 | 0.0080472 | 0.057471 | -0.00097413 | 0.080331 | -58.3282 | 62.0361 | -61.7432 | -61.5326 | 54.5975 | 24.8337 | 8.8852 | 8.6472 | 62.0956 | -61.6882 | -0.3479 | -0.073242 | 3.067 | -0.13733 | -7.5119 | -0.29297 | -0.013733 | 3.4149 | 70.2805 | 70.0424 | 115.9927 | 123.4314 | 3.067 | 123.4909 | 86.2289 | -0.29297 | 123.4314 | 3.067 | 86.2289 | 115.9927 | 123.4909 | -123.8525 | -123.7976
5207.7188 | 123.7747 | -61.4182 | 62.1094 | -0.0089264 | 0.014956 | 0.0085 | 0.0091152 | 0.056617 | 0.00030767 | 0.07969 | -58.3786 | 62.0682 | -61.7523 | -61.5784 | 54.5837 | 24.7421 | 8.9401 | 8.5968 | 62.0636 | -61.7065 | -0.33417 | -0.041199 | 3.0396 | -0.16022 | -7.5256 | -0.28839 | -0.045776 | 3.3737 | 70.3583 | 70.015 | 116.0019 | 123.4863 | 3.0396 | 123.4818 | 86.1603 | -0.28839 | 123.4863 | 3.0396 | 86.1603 | 116.0019 | 123.4818 | -123.8617 | -123.8159
5208.7188 | 123.7701 | -61.4182 | 62.0865 | 0.13603 | 0.011751 | 0.010423 | 0.012106 | 0.059607 | -0.00011953 | 0.078408 | -58.3328 | 62.0728 | -61.7065 | -61.5784 | 54.538 | 24.765 | 8.8943 | 8.6151 | 62.0453 | -61.7523 | -0.28839 | -0.013733 | 3.0853 | -0.16022 | -7.5485 | -0.33417 | -0.041199 | 3.3737 | 70.3125 | 70.0333 | 115.9561 | 123.4909 | 3.0853 | 123.4634 | 86.1832 | -0.33417 | 123.4909 | 3.0853 | 86.1832 | 115.9561 | 123.4634 | -123.793 | -123.8388
5209.7188 | 123.8342 | -61.3998 | 62.0819 | 0.17418 | 0.014742 | 0.014268 | 0.014242 | 0.062171 | -0.0035375 | 0.077126 | -58.2916 | 62.0453 | -61.7798 | -61.528 | 54.5151 | 24.6963 | 8.9539 | 8.6792 | 62.059 | -61.734 | -0.37994 | -0.036621 | 3.1082 | -0.12817 | -7.5668 | -0.33417 | -0.022888 | 3.4882 | 70.3537 | 70.079 | 115.9149 | 123.4451 | 3.1082 | 123.4589 | 86.0962 | -0.33417 | 123.4451 | 3.1082 | 86.0962 | 115.9149 | 123.4589 | -123.8617 | -123.8159
5210.7188 | 123.8251 | -61.409 | 62.0636 | 0.22758 | 0.015597 | 0.015977 | 0.015097 | 0.061103 | -0.0018285 | 0.079049 | -58.3328 | 62.0911 | -61.7798 | -61.5692 | 54.538 | 24.852 | 8.8852 | 8.6655 | 62.059 | -61.7386 | -0.37079 | 0.027465 | 3.0762 | -0.16022 | -7.5256 | -0.32959 | -0.004578 | 3.447 | 70.2942 | 70.0745 | 115.947 | 123.5001 | 3.0762 | 123.468 | 86.261 | -0.32959 | 123.5001 | 3.0762 | 86.261 | 115.947 | 123.468 | -123.8434 | -123.8022
5211.7344 | 123.7106 | -61.4273 | 62.1597 | -0.26833 | 0.016024 | 0.0095682 | 0.010183 | 0.060248 | -0.0014013 | 0.079476 | -58.3786 | 62.1552 | -61.7477 | -61.6196 | 54.5242 | 24.9115 | 9.1873 | 8.6426 | 62.1597 | -61.7386 | -0.32044 | -0.004578 | 3.0487 | -0.19226 | -7.6355 | -0.31128 | 0 | 3.3691 | 70.6146 | 70.0699 | 115.9515 | 123.5825 | 3.0487 | 123.587 | 86.3388 | -0.31128 | 123.5825 | 3.0487 | 86.3388 | 115.9515 | 123.587 | -123.9075 | -123.8983
5212.7188 | 123.7976 | -61.4182 | 62.1094 | 0.03685 | 0.011751 | 0.010423 | 0.01232 | 0.06153 | -0.0026831 | 0.07734 | -58.3832 | 62.0544 | -61.734 | -61.6013 | 54.5059 | 24.8428 | 9.0271 | 8.6838 | 62.0819 | -61.702 | -0.31586 | -0.054932 | 3.035 | -0.1831 | -7.6035 | -0.28381 | -0.027466 | 3.3508 | 70.4453 | 70.1019 | 115.9241 | 123.4726 | 3.035 | 123.5001 | 86.261 | -0.28381 | 123.4726 | 3.035 | 86.261 | 115.9241 | 123.5001 | -123.8434 | -123.8113
5213.7188 | 123.7473 | -61.4548 | 62.0499 | 0.16655 | 0.01581 | 0.0132 | 0.014883 | 0.060675 | -0.0026831 | 0.078835 | -58.3008 | 62.1002 | -61.7477 | -61.5646 | 54.5517 | 24.8383 | 8.9218 | 8.7067 | 62.0544 | -61.7523 | -0.29297 | 0.050354 | 3.154 | -0.10986 | -7.4982 | -0.29755 | 0.004577 | 3.447 | 70.3766 | 70.1614 | 116.0065 | 123.555 | 3.154 | 123.5092 | 86.293 | -0.29755 | 123.555 | 3.154 | 86.293 | 116.0065 | 123.5092 | -123.7976 | -123.8022
5214.7188 | 123.8892 | -61.4273 | 62.0544 | 0.15129 | 0.016878 | 0.014054 | 0.014242 | 0.060034 | -0.00011953 | 0.078195 | -58.3054 | 62.0865 | -61.7569 | -61.5555 | 54.57 | 25.1038 | 8.8898 | 8.6609 | 62.0544 | -61.7386 | -0.32959 | 0.032044 | 3.1219 | -0.12817 | -7.4844 | -0.31128 | 0 | 3.4515 | 70.3171 | 70.0882 | 115.9973 | 123.5138 | 3.1219 | 123.4818 | 86.5311 | -0.31128 | 123.5138 | 3.1219 | 86.5311 | 115.9973 | 123.4818 | -123.8113 | -123.793
5215.7188 | 123.8297 | -61.4044 | 62.0682 | 0.17418 | 0.017947 | 0.016191 | 0.015524 | 0.06153 | 0.0011621 | 0.07734 | -58.3145 | 62.0636 | -61.7203 | -61.5646 | 54.57 | 24.9069 | 8.8303 | 8.5373 | 62.0407 | -61.7432 | -0.31586 | -0.004577 | 3.0899 | -0.16022 | -7.4982 | -0.33875 | -0.027466 | 3.4058 | 70.2347 | 69.9417 | 115.9744 | 123.468 | 3.0899 | 123.4451 | 86.3113 | -0.33875 | 123.468 | 3.0899 | 86.3113 | 115.9744 | 123.4451 | -123.7885 | -123.8113
5216.7188 | 123.8251 | -61.4227 | 62.0728 | 0.41832 | 0.014956 | 0.012132 | 0.016378 | 0.060675 | -0.0016149 | 0.080544 | -58.3191 | 62.0911 | -61.7569 | -61.5601 | 54.5609 | 24.8474 | 8.8257 | 8.5831 | 62.0773 | -61.7294 | -0.33417 | 0.01831 | 3.1036 | -0.13733 | -7.5119 | -0.3067 | 0.004578 | 3.4378 | 70.2484 | 70.0058 | 115.9836 | 123.5138 | 3.1036 | 123.5001 | 86.2701 | -0.3067 | 123.5138 | 3.1036 | 86.2701 | 115.9836 | 123.5001 | -123.8297 | -123.8022
5217.7344 | 123.7152 | -61.3495 | 62.1048 | -0.13863 | 0.013888 | 0.0095682 | 0.0091152 | 0.060675 | -0.0018285 | 0.080544 | -58.3008 | 62.0682 | -61.7386 | -61.5051 | 54.5883 | 24.9069 | 8.9539 | 8.8715 | 62.1094 | -61.6562 | -0.3891 | -0.036621 | 3.0487 | -0.15564 | -7.5165 | -0.3067 | 0.004578 | 3.4378 | 70.3033 | 70.2209 | 115.9378 | 123.4177 | 3.0487 | 123.4589 | 86.2564 | -0.3067 | 123.4177 | 3.0487 | 86.2564 | 115.9378 | 123.4589 | -123.8434 | -123.761
5218.7188 | 123.8068 | -61.409 | 62.0865 | 0.21233 | 0.015597 | 0.010423 | 0.016806 | 0.061103 | -0.0041785 | 0.079904 | -58.342 | 62.0865 | -61.7661 | -61.5692 | 54.5929 | 24.9207 | 8.9035 | 8.6151 | 62.059 | -61.7203 | -0.35706 | 0 | 3.067 | -0.16022 | -7.4936 | -0.31128 | -0.027466 | 3.4241 | 70.3125 | 70.0241 | 116.0019 | 123.4955 | 3.067 | 123.468 | 86.3297 | -0.31128 | 123.4955 | 3.067 | 86.3297 | 116.0019 | 123.468 | -123.8525 | -123.8068
5219.7188 | 123.8068 | -61.4319 | 62.1185 | 0.090256 | 0.015169 | 0.011491 | 0.011465 | 0.058753 | -0.0033239 | 0.076699 | -58.3832 | 62.0636 | -61.734 | -61.6104 | 54.5654 | 25.0031 | 8.9172 | 8.6105 | 62.0728 | -61.7111 | -0.30212 | -0.054931 | 3.0487 | -0.17853 | -7.5531 | -0.27924 | -0.045776 | 3.3508 | 70.3491 | 70.0424 | 115.9973 | 123.4955 | 3.0487 | 123.5046 | 86.4349 | -0.27924 | 123.4955 | 3.0487 | 86.4349 | 115.9973 | 123.5046 | -123.8525 | -123.8297
5220.7188 | 123.88 | -61.4365 | 62.0773 | 0.17418 | 0.015597 | 0.011918 | 0.015951 | 0.060462 | -0.0022559 | 0.078622 | -58.3191 | 62.0865 | -61.7569 | -61.5784 | 54.5609 | 24.9756 | 8.844 | 8.4457 | 62.0361 | -61.7523 | -0.32044 | 0.009155 | 3.1174 | -0.14191 | -7.5165 | -0.31586 | -0.041199 | 3.4378 | 70.2805 | 69.8822 | 115.9973 | 123.5229 | 3.1174 | 123.4726 | 86.412 | -0.31586 | 123.5229 | 3.1174 | 86.412 | 115.9973 | 123.4726 | -123.8342 | -123.8297
5221.7188 | 123.8388 | -61.4273 | 62.0773 | 0.26573 | 0.015597 | 0.012559 | 0.012106 | 0.060248 | -0.00076053 | 0.07734 | -58.3328 | 62.0773 | -61.7386 | -61.5784 | 54.5746 | 25.0671 | 8.8531 | 8.6334 | 62.0636 | -61.7203 | -0.31128 | 0 | 3.0945 | -0.15106 | -7.5027 | -0.29297 | -0.013733 | 3.4058 | 70.2805 | 70.0607 | 116.0019 | 123.5046 | 3.0945 | 123.4909 | 86.4944 | -0.29297 | 123.5046 | 3.0945 | 86.4944 | 116.0019 | 123.4909 | -123.8159 | -123.7976
5222.7188 | 123.8159 | -61.3998 | 62.1094 | -0.3904 | 0.013674 | 0.010209 | 0.011465 | 0.057685 | -0.0037511 | 0.075631 | -58.3557 | 62.059 | -61.7386 | -61.5234 | 54.5929 | 24.9298 | 8.9722 | 8.6655 | 62.0773 | -61.6882 | -0.33874 | -0.050354 | 3.0441 | -0.1236 | -7.5165 | -0.28839 | -0.032043 | 3.3829 | 70.372 | 70.0653 | 115.9927 | 123.4589 | 3.0441 | 123.4772 | 86.3297 | -0.28839 | 123.4589 | 3.0441 | 86.3297 | 115.9927 | 123.4772 | -123.848 | -123.7976
5223.7188 | 123.793 | -61.4227 | 62.1094 | 0.1284 | 0.01346 | 0.0085 | 0.0097562 | 0.057898 | 0.0020167 | 0.078195 | -58.374 | 62.0773 | -61.7569 | -61.6196 | 54.5471 | 24.678 | 8.9447 | 8.5876 | 62.0682 | -61.734 | -0.33417 | -0.032043 | 3.0487 | -0.19684 | -7.5623 | -0.31128 | -0.041199 | 3.3829 | 70.3674 | 70.0104 | 115.9698 | 123.5001 | 3.0487 | 123.4909 | 86.1008 | -0.31128 | 123.5001 | 3.0487 | 86.1008 | 115.9698 | 123.4909 | -123.8663 | -123.8434
5224.7188 | 123.7885 | -61.4044 | 62.1277 | 0.11314 | 0.015597 | 0.010209 | 0.011892 | 0.058539 | -0.0018285 | 0.080758 | -58.3694 | 62.0911 | -61.734 | -61.6104 | 54.5197 | 24.7147 | 8.9401 | 8.606 | 62.0544 | -61.7432 | -0.32959 | -0.036622 | 3.035 | -0.20599 | -7.608 | -0.33875 | -0.073243 | 3.3646 | 70.3445 | 70.0104 | 115.9241 | 123.4955 | 3.035 | 123.4589 | 86.1191 | -0.33875 | 123.4955 | 3.035 | 86.1191 | 115.9241 | 123.4589 | -123.8617 | -123.8708
5225.7188 | 123.7839 | -61.4319 | 62.0773 | 0.21233 | 0.017519 | 0.011704 | 0.01766 | 0.05918 | -0.00097413 | 0.078195 | -58.374 | 62.114 | -61.821 | -61.6287 | 54.5105 | 24.7421 | 8.9172 | 8.5419 | 62.0773 | -61.7477 | -0.3891 | 0.036621 | 3.0579 | -0.19684 | -7.5668 | -0.31586 | 0 | 3.447 | 70.3491 | 69.9738 | 115.9424 | 123.5458 | 3.0579 | 123.5092 | 86.174 | -0.31586 | 123.5458 | 3.0579 | 86.174 | 115.9424 | 123.5092 | -123.8983 | -123.8251
5226.7188 | 123.8068 | -61.4136 | 62.0682 | 0.2047 | 0.017733 | 0.016618 | 0.016592 | 0.062384 | -0.0011877 | 0.077554 | -58.2962 | 62.0956 | -61.7798 | -61.5738 | 54.5746 | 24.8016 | 8.8577 | 8.6563 | 62.0407 | -61.7203 | -0.36621 | 0.027466 | 3.1174 | -0.16022 | -7.4936 | -0.3067 | -0.027466 | 3.4836 | 70.2713 | 70.0699 | 115.9882 | 123.5092 | 3.1174 | 123.4543 | 86.2152 | -0.3067 | 123.5092 | 3.1174 | 86.2152 | 115.9882 | 123.4543 | -123.848 | -123.7885
5227.7344 | 123.8022 | -61.3861 | 62.1048 | -0.09285 | 0.011324 | 0.0078592 | 0.008688 | 0.059821 | 9.4068e-05 | 0.077981 | -58.3511 | 62.059 | -61.7523 | -61.5646 | 54.5883 | 24.8611 | 8.9447 | 8.6975 | 62.0728 | -61.7111 | -0.36621 | -0.045776 | 3.035 | -0.17853 | -7.5165 | -0.32501 | -0.032043 | 3.4012 | 70.3308 | 70.0836 | 115.9744 | 123.4451 | 3.035 | 123.4589 | 86.2473 | -0.32501 | 123.4451 | 3.035 | 86.2473 | 115.9744 | 123.4589 | -123.8571 | -123.8159
5228.7188 | 123.8022 | -61.4273 | 62.1048 | 0.18944 | 0.016451 | 0.011491 | 0.017019 | 0.05918 | -0.0028967 | 0.078622 | -58.3511 | 62.1323 | -61.7523 | -61.6104 | 54.5242 | 24.8291 | 8.8898 | 8.6197 | 62.0682 | -61.7661 | -0.32501 | 0.027466 | 3.0762 | -0.18311 | -7.5806 | -0.33875 | -0.036621 | 3.4012 | 70.3171 | 70.047 | 115.9515 | 123.5596 | 3.0762 | 123.4955 | 86.2564 | -0.33875 | 123.5596 | 3.0762 | 86.2564 | 115.9515 | 123.4955 | -123.8571 | -123.8708
5229.7188 | 123.7656 | -61.4548 | 62.0911 | 0.21996 | 0.017947 | 0.012773 | 0.016165 | 0.061957 | -0.00011953 | 0.078195 | -58.3832 | 62.1414 | -61.7935 | -61.6241 | 54.5151 | 24.8245 | 8.9493 | 8.5785 | 62.1094 | -61.7706 | -0.33874 | 0.050354 | 3.0716 | -0.16937 | -7.576 | -0.31586 | 0.018311 | 3.4103 | 70.4041 | 70.0333 | 115.9698 | 123.5962 | 3.0716 | 123.5641 | 86.2793 | -0.31586 | 123.5962 | 3.0716 | 86.2793 | 115.9698 | 123.5641 | -123.8846 | -123.8617
5230.7188 | 123.8022 | -61.4182 | 62.0544 | 0.30388 | 0.01346 | 0.01085 | 0.012533 | 0.062598 | -0.0033239 | 0.07969 | -58.3328 | 62.1094 | -61.7523 | -61.5738 | 54.5746 | 24.8886 | 8.8531 | 8.6426 | 62.0728 | -61.734 | -0.33417 | 0.054932 | 3.0853 | -0.15564 | -7.4799 | -0.31586 | 0.018311 | 3.4195 | 70.2713 | 70.0607 | 115.9927 | 123.5275 | 3.0853 | 123.4909 | 86.3068 | -0.31586 | 123.5275 | 3.0853 | 86.3068 | 115.9927 | 123.4909 | -123.8068 | -123.7885
5231.7188 | 123.7473 | -61.4594 | 62.0956 | 0.1284 | 0.016238 | 0.0095682 | 0.01531 | 0.060889 | -0.00011953 | 0.076913 | -58.3969 | 62.1414 | -61.7661 | -61.6562 | 54.5059 | 24.8428 | 8.9905 | 8.551 | 62.0728 | -61.7706 | -0.3067 | 0.045776 | 3.0624 | -0.19684 | -7.5897 | -0.31128 | -0.022888 | 3.3691 | 70.4498 | 70.0104 | 115.9653 | 123.6008 | 3.0624 | 123.5321 | 86.3022 | -0.31128 | 123.6008 | 3.0624 | 86.3022 | 115.9653 | 123.5321 | -123.8617 | -123.8663
5232.7188 | 123.7839 | -61.409 | 62.0911 | 0.16655 | 0.01346 | 0.009141 | 0.0074062 | 0.059607 | 0.00094847 | 0.077981 | -58.3832 | 62.0453 | -61.7432 | -61.6333 | 54.5517 | 24.8795 | 8.9493 | 8.6334 | 62.0819 | -61.7111 | -0.33417 | -0.045776 | 3.0258 | -0.2243 | -7.5394 | -0.30212 | -0.009155 | 3.36 | 70.3583 | 70.0424 | 115.9607 | 123.4543 | 3.0258 | 123.4909 | 86.2885 | -0.30212 | 123.4543 | 3.0258 | 86.2885 | 115.9607 | 123.4909 | -123.8342 | -123.8022
5233.7188 | 123.7656 | -61.4456 | 62.1048 | 0.16655 | 0.018587 | 0.014482 | 0.017447 | 0.061316 | 9.4068e-05 | 0.080331 | -58.3786 | 62.1368 | -61.7615 | -61.6196 | 54.5059 | 24.8886 | 8.9584 | 8.5739 | 62.0773 | -61.7752 | -0.31586 | 0.032044 | 3.067 | -0.17395 | -7.5989 | -0.32959 | -0.027465 | 3.3829 | 70.4041 | 70.0195 | 115.9515 | 123.5825 | 3.067 | 123.523 | 86.3342 | -0.32959 | 123.5825 | 3.067 | 86.3342 | 115.9515 | 123.523 | -123.8663 | -123.88
5234.7188 | 123.7427 | -61.4456 | 62.1002 | 0.17418 | 0.017092 | 0.011064 | 0.016165 | 0.06388 | -0.00033333 | 0.078408 | -58.3832 | 62.1277 | -61.7752 | -61.6379 | 54.483 | 24.8611 | 8.9905 | 8.5648 | 62.0956 | -61.7432 | -0.32959 | 0.027466 | 3.0624 | -0.19226 | -7.6172 | -0.29755 | -0.004578 | 3.392 | 70.4361 | 70.0104 | 115.9287 | 123.5733 | 3.0624 | 123.5413 | 86.3068 | -0.29755 | 123.5733 | 3.0624 | 86.3068 | 115.9287 | 123.5413 | -123.8754 | -123.8434
5235.7188 | 123.7473 | -61.4822 | 62.0865 | 0.082626 | 0.016665 | 0.010209 | 0.016592 | 0.060034 | -0.00033333 | 0.077981 | -58.3878 | 62.1414 | -61.7752 | -61.6562 | 54.4876 | 24.8932 | 9.0546 | 8.5831 | 62.0956 | -61.7844 | -0.29297 | 0.054931 | 3.0945 | -0.17395 | -7.5989 | -0.30212 | 0.009155 | 3.3875 | 70.5368 | 70.0653 | 115.9698 | 123.6237 | 3.0945 | 123.5779 | 86.3754 | -0.30212 | 123.6237 | 3.0945 | 86.3754 | 115.9698 | 123.5779 | -123.8617 | -123.8708
5236.7188 | 123.7061 | -61.441 | 62.0911 | -0.031814 | 0.017092 | 0.015336 | 0.01531 | 0.06153 | -0.00011953 | 0.07734 | -58.4198 | 62.1597 | -61.7752 | -61.6608 | 54.5288 | 24.9481 | 9.0866 | 8.5556 | 62.1185 | -61.7844 | -0.33417 | 0.068665 | 3.0212 | -0.21973 | -7.5623 | -0.34332 | 0.027466 | 3.3554 | 70.5276 | 69.9966 | 115.9698 | 123.6008 | 3.0212 | 123.5596 | 86.3892 | -0.34332 | 123.6008 | 3.0212 | 86.3892 | 115.9698 | 123.5596 | -123.8663 | -123.8754
5237.7344 | 123.761 | -61.409 | 62.0773 | -0.016556 | 0.014742 | 0.014054 | 0.0063382 | 0.060462 | -0.0039649 | 0.079476 | -58.3832 | 62.0773 | -61.7523 | -61.6104 | 54.5975 | 25.0259 | 8.9722 | 8.7021 | 62.0956 | -61.7249 | -0.34332 | 0 | 3.0258 | -0.20142 | -7.4799 | -0.31586 | 0.01831 | 3.3691 | 70.3812 | 70.1111 | 116.0065 | 123.4863 | 3.0258 | 123.5046 | 86.4349 | -0.31586 | 123.4863 | 3.0258 | 86.4349 | 116.0065 | 123.5046 | -123.8297 | -123.8022
5238.7188 | 123.6786 | -61.4502 | 62.114 | 0.16655 | 0.014742 | 0.012986 | 0.019583 | 0.064521 | 0.00094847 | 0.077554 | -58.3832 | 62.1597 | -61.7706 | -61.6058 | 54.8538 | 25.0031 | 9.0088 | 8.67 | 62.146 | -61.7889 | -0.32043 | 0.045776 | 3.067 | -0.15564 | -7.2601 | -0.33874 | 0.032043 | 3.3875 | 70.459 | 70.1202 | 116.304 | 123.6099 | 3.067 | 123.5962 | 86.4532 | -0.33874 | 123.6099 | 3.067 | 86.4532 | 116.304 | 123.5962 | -123.8846 | -123.9029
5239.7188 | 123.6053 | -61.4777 | 62.0316 | 0.090256 | 0.015169 | 0.0095682 | 0.015951 | 0.061316 | -0.0018285 | 0.078408 | -58.4381 | 62.178 | -61.7615 | -61.6516 | 54.5059 | 24.8154 | 9.0317 | 8.4824 | 62.1368 | -61.7935 | -0.28381 | 0.14649 | 3.0396 | -0.17395 | -7.5256 | -0.31586 | 0.10529 | 3.3234 | 70.5093 | 69.96 | 115.9836 | 123.6557 | 3.0396 | 123.6145 | 86.293 | -0.31586 | 123.6557 | 3.0396 | 86.293 | 115.9836 | 123.6145 | -123.793 | -123.8251
5240.7188 | 123.7244 | -61.4639 | 62.0956 | 0.41069 | 0.016878 | 0.012986 | 0.014456 | 0.062384 | -0.00097413 | 0.080331 | -58.3511 | 62.1689 | -61.7752 | -61.6699 | 54.5242 | 25.0168 | 9.0134 | 8.5007 | 62.1368 | -61.7706 | -0.31128 | 0.073242 | 3.1128 | -0.20599 | -7.5714 | -0.3067 | 0.041199 | 3.4241 | 70.4773 | 69.9646 | 115.9882 | 123.6328 | 3.1128 | 123.6008 | 86.4807 | -0.3067 | 123.6328 | 3.1128 | 86.4807 | 115.9882 | 123.6008 | -123.8708 | -123.8663
5241.7188 | 123.7106 | -61.4639 | 62.1002 | 1.5398 | 0.014742 | 0.0089274 | 0.015738 | 0.063025 | -0.00097413 | 0.078622 | -58.1131 | 62.1277 | -61.7706 | -61.6379 | 54.5563 | 24.8474 | 9.0134 | 8.519 | 62.1597 | -61.7844 | -0.3067 | 0.027466 | 3.3508 | -0.17395 | -7.5439 | -0.32043 | 0.059509 | 3.6575 | 70.4773 | 69.9829 | 116.0202 | 123.5916 | 3.3508 | 123.6237 | 86.3113 | -0.32043 | 123.5916 | 3.3508 | 86.3113 | 116.0202 | 123.6237 | -123.8708 | -123.8846
5242.7188 | 123.7885 | -61.4044 | 62.059 | 0.1284 | 0.015169 | 0.0132 | 0.011892 | 0.062384 | -0.00011953 | 0.079904 | -58.3008 | 62.0544 | -61.7752 | -61.6058 | 54.6295 | 24.9985 | 8.8165 | 8.606 | 62.0728 | -61.7432 | -0.37079 | -0.004578 | 3.1036 | -0.20142 | -7.4295 | -0.33875 | 0.013733 | 3.4744 | 70.2209 | 70.0104 | 116.0339 | 123.4589 | 3.1036 | 123.4772 | 86.4029 | -0.33875 | 123.4589 | 3.1036 | 86.4029 | 116.0339 | 123.4772 | -123.8342 | -123.8022
5243.7188 | 123.6374 | -61.4685 | 62.027 | 0.10551 | 0.017733 | 0.013413 | 0.017233 | 0.060675 | -0.0031103 | 0.079049 | -58.3786 | 62.1826 | -61.7615 | -61.6699 | 54.5242 | 24.9481 | 8.9767 | 8.4824 | 62.1185 | -61.821 | -0.29297 | 0.15564 | 3.0899 | -0.20142 | -7.5027 | -0.35248 | 0.091552 | 3.3829 | 70.4453 | 69.9509 | 115.9927 | 123.6511 | 3.0899 | 123.587 | 86.4166 | -0.35248 | 123.6511 | 3.0899 | 86.4166 | 115.9927 | 123.587 | -123.7885 | -123.848
5244.7188 | 123.7564 | -61.4685 | 62.0865 | -0.062332 | 0.016238 | 0.012559 | 0.016165 | 0.060675 | -0.00097413 | 0.078408 | -58.3603 | 62.1597 | -61.7935 | -61.6791 | 54.5334 | 24.8199 | 8.9447 | 8.519 | 62.114 | -61.7935 | -0.32501 | 0.073242 | 3.1082 | -0.21057 | -7.5531 | -0.32501 | 0.027466 | 3.4332 | 70.4132 | 69.9875 | 116.0019 | 123.6282 | 3.1082 | 123.5825 | 86.2885 | -0.32501 | 123.6282 | 3.1082 | 86.2885 | 116.0019 | 123.5825 | -123.88 | -123.88
5245.7188 | 123.6832 | -61.4639 | 62.114 | 0.052109 | 0.017947 | 0.012132 | 0.014883 | 0.062384 | -0.00011953 | 0.079049 | -58.3603 | 62.1689 | -61.7432 | -61.6837 | 54.5334 | 24.8795 | 8.9905 | 8.4732 | 62.1231 | -61.8118 | -0.27924 | 0.054931 | 3.1036 | -0.21973 | -7.5806 | -0.3479 | 0.009155 | 3.3829 | 70.4544 | 69.9371 | 115.9973 | 123.6328 | 3.1036 | 123.587 | 86.3434 | -0.3479 | 123.6328 | 3.1036 | 86.3434 | 115.9973 | 123.587 | -123.8571 | -123.9258
5246.7188 | 123.6832 | -61.441 | 62.1185 | 0.04448 | 0.01816 | 0.014695 | 0.015951 | 0.064307 | -0.0018285 | 0.078408 | -58.3328 | 62.1735 | -61.7798 | -61.6608 | 54.5471 | 24.8795 | 8.9722 | 8.4778 | 62.1552 | -61.7661 | -0.33874 | 0.054932 | 3.1082 | -0.21973 | -7.5714 | -0.32501 | 0.036621 | 3.447 | 70.4132 | 69.9188 | 115.9882 | 123.6145 | 3.1082 | 123.5962 | 86.3205 | -0.32501 | 123.6145 | 3.1082 | 86.3205 | 115.9882 | 123.5962 | -123.8983 | -123.8846
5247.7188 | 123.8159 | -61.4182 | 62.0636 | 0.17418 | 0.013674 | 0.014482 | 0.011892 | 0.063025 | -0.0016149 | 0.079049 | -58.3054 | 62.0636 | -61.7661 | -61.6013 | 54.6021 | 25.0534 | 8.7753 | 8.5922 | 62.0819 | -61.734 | -0.3479 | 0 | 3.1128 | -0.1831 | -7.4615 | -0.31586 | 0.01831 | 3.4607 | 70.1935 | 70.0104 | 116.0202 | 123.4818 | 3.1128 | 123.5001 | 86.4716 | -0.31586 | 123.4818 | 3.1128 | 86.4716 | 116.0202 | 123.5001 | -123.8297 | -123.7976
5248.7188 | 123.6832 | -61.4548 | 62.114 | 0.12077 | 0.016238 | 0.014695 | 0.015738 | 0.061316 | -0.00033333 | 0.080117 | -58.3786 | 62.1735 | -61.7798 | -61.702 | 54.4876 | 24.8795 | 8.8943 | 8.4732 | 62.1185 | -61.8027 | -0.32501 | 0.059509 | 3.0762 | -0.24719 | -7.6263 | -0.3479 | 0.004577 | 3.4012 | 70.3491 | 69.928 | 115.9424 | 123.6282 | 3.0762 | 123.5733 | 86.3342 | -0.3479 | 123.6282 | 3.0762 | 86.3342 | 115.9424 | 123.5733 | -123.8937 | -123.9166
5249.7188 | 123.6877 | -61.4594 | 62.1094 | 0.0063326 | 0.017947 | 0.016404 | 0.013388 | 0.062598 | -0.0020421 | 0.078408 | -58.3603 | 62.1735 | -61.7661 | -61.6928 | 54.4739 | 24.9802 | 8.9676 | 8.4732 | 62.1323 | -61.7706 | -0.3067 | 0.064087 | 3.0991 | -0.23346 | -7.6355 | -0.31128 | 0.022888 | 3.4058 | 70.4269 | 69.9326 | 115.9332 | 123.6328 | 3.0991 | 123.5916 | 86.4395 | -0.31128 | 123.6328 | 3.0991 | 86.4395 | 115.9332 | 123.5916 | -123.8754 | -123.88
5250.7188 | 123.6832 | -61.4594 | 62.114 | 0.052109 | 0.018374 | 0.0097818 | 0.016165 | 0.064521 | -0.00076053 | 0.079476 | -58.342 | 62.1735 | -61.7889 | -61.6974 | 54.4785 | 24.8886 | 8.963 | 8.4732 | 62.146 | -61.7889 | -0.32959 | 0.059509 | 3.1174 | -0.23804 | -7.6355 | -0.32959 | 0.032043 | 3.447 | 70.4224 | 69.9326 | 115.9378 | 123.6328 | 3.1174 | 123.6053 | 86.348 | -0.32959 | 123.6328 | 3.1174 | 86.348 | 115.9378 | 123.6053 | -123.9029 | -123.9029
5251.7188 | 123.7015 | -61.4868 | 62.1414 | 0.14366 | 0.017092 | 0.013841 | 0.017019 | 0.062812 | -0.0033239 | 0.077767 | -58.3832 | 62.1597 | -61.7935 | -61.6608 | 54.4327 | 25.0031 | 8.9951 | 8.4412 | 62.1414 | -61.7844 | -0.3067 | 0.018311 | 3.1036 | -0.17395 | -7.7087 | -0.29755 | 0 | 3.4103 | 70.4819 | 69.928 | 115.9195 | 123.6465 | 3.1036 | 123.6282 | 86.4899 | -0.29755 | 123.6465 | 3.1036 | 86.4899 | 115.9195 | 123.6282 | -123.9349 | -123.9258
5252.7188 | 123.793 | -61.409 | 62.059 | 0.22758 | 0.018374 | 0.012345 | 0.012106 | 0.06388 | -0.00033333 | 0.078195 | -58.342 | 62.0956 | -61.7844 | -61.6104 | 54.5837 | 24.9298 | 8.8257 | 8.638 | 62.0911 | -61.7477 | -0.37537 | 0.036621 | 3.067 | -0.20142 | -7.4753 | -0.33875 | 0.032043 | 3.4424 | 70.2347 | 70.047 | 115.9927 | 123.5046 | 3.067 | 123.5001 | 86.3388 | -0.33875 | 123.5046 | 3.067 | 86.3388 | 115.9927 | 123.5001 | -123.8434 | -123.8068
5253.7188 | 123.7061 | -61.441 | 62.1185 | -0.016556 | 0.017733 | 0.015336 | 0.015951 | 0.064521 | -0.00033333 | 0.078195 | -58.3374 | 62.1826 | -61.7661 | -61.647 | 54.5013 | 24.9069 | 9.0179 | 8.5739 | 62.146 | -61.8073 | -0.32501 | 0.064087 | 3.1036 | -0.20599 | -7.6172 | -0.36621 | 0.027466 | 3.4287 | 70.459 | 70.015 | 115.9424 | 123.6237 | 3.1036 | 123.587 | 86.348 | -0.36621 | 123.6237 | 3.1036 | 86.348 | 115.9424 | 123.587 | -123.8846 | -123.9258
5254.7188 | 123.6832 | -61.4502 | 62.1185 | 0.052109 | 0.01581 | 0.017045 | 0.015738 | 0.063025 | -0.0028967 | 0.079263 | -58.3694 | 62.1964 | -61.7706 | -61.7065 | 54.5105 | 24.8383 | 9.0271 | 8.4869 | 62.1368 | -61.7889 | -0.32043 | 0.07782 | 3.0807 | -0.25635 | -7.608 | -0.33874 | 0.018311 | 3.4012 | 70.4773 | 69.9371 | 115.9607 | 123.6465 | 3.0807 | 123.587 | 86.2885 | -0.33874 | 123.6465 | 3.0807 | 86.2885 | 115.9607 | 123.587 | -123.8892 | -123.9075
5255.7188 | 123.7106 | -61.4502 | 62.1277 | 0.052109 | 0.016665 | 0.012345 | 0.015951 | 0.06388 | -0.00033333 | 0.079476 | -58.3694 | 62.1735 | -61.7889 | -61.6837 | 54.4647 | 24.8383 | 9.0179 | 8.4549 | 62.1414 | -61.8027 | -0.33874 | 0.045776 | 3.0807 | -0.23346 | -7.663 | -0.35248 | 0.013732 | 3.4195 | 70.4681 | 69.9051 | 115.9149 | 123.6237 | 3.0807 | 123.5916 | 86.2885 | -0.35248 | 123.6237 | 3.0807 | 86.2885 | 115.9149 | 123.5916 | -123.9166 | -123.9304
5256.7188 | 123.7061 | -61.4548 | 62.1277 | -0.0089264 | 0.015169 | 0.014054 | 0.01296 | 0.062598 | -0.0014013 | 0.081399 | -58.3466 | 62.1826 | -61.7798 | -61.6653 | 54.5242 | 24.8657 | 9.0271 | 8.4961 | 62.1643 | -61.7889 | -0.32501 | 0.054931 | 3.1082 | -0.21057 | -7.6035 | -0.33417 | 0.036621 | 3.4332 | 70.4819 | 69.9509 | 115.979 | 123.6374 | 3.1082 | 123.6191 | 86.3205 | -0.33417 | 123.6374 | 3.1082 | 86.3205 | 115.979 | 123.6191 | -123.9075 | -123.9166
5257.7188 | 123.7061 | -61.4456 | 62.1231 | -0.0012969 | 0.015383 | 0.017472 | 0.016378 | 0.063666 | -0.0026831 | 0.07969 | -58.3282 | 62.1735 | -61.7706 | -61.6608 | 54.5288 | 24.939 | 8.9905 | 8.4778 | 62.1552 | -61.7981 | -0.32501 | 0.050354 | 3.1174 | -0.21515 | -7.5943 | -0.35248 | 0.032043 | 3.4424 | 70.4361 | 69.9234 | 115.9744 | 123.6191 | 3.1174 | 123.6008 | 86.3846 | -0.35248 | 123.6191 | 3.1174 | 86.3846 | 115.9744 | 123.6008 | -123.8937 | -123.9212
5258.7344 | 123.7564 | -61.4319 | 62.0819 | 0.18181 | 0.014529 | 0.013627 | 0.0078336 | 0.063666 | -0.0024695 | 0.079904 | -58.3466 | 62.0544 | -61.7661 | -61.6287 | 54.5609 | 25.0992 | 8.844 | 8.5556 | 62.1231 | -61.7157 | -0.33417 | -0.027466 | 3.0853 | -0.19684 | -7.5211 | -0.28381 | 0.041199 | 3.4195 | 70.2759 | 69.9875 | 115.9927 | 123.4863 | 3.0853 | 123.555 | 86.5311 | -0.28381 | 123.4863 | 3.0853 | 86.5311 | 115.9927 | 123.555 | -123.848 | -123.7976
5259.7188 | 123.7335 | -61.4365 | 62.1231 | -0.062332 | 0.015597 | 0.014909 | 0.015951 | 0.062598 | -0.0011877 | 0.078195 | -58.2962 | 62.1735 | -61.7661 | -61.647 | 54.538 | 25.0351 | 9.0134 | 8.5693 | 62.1323 | -61.7935 | -0.32959 | 0.050354 | 3.1403 | -0.21057 | -7.5851 | -0.35706 | 0.009155 | 3.4698 | 70.4498 | 70.0058 | 115.9744 | 123.6099 | 3.1403 | 123.5687 | 86.4716 | -0.35706 | 123.6099 | 3.1403 | 86.4716 | 115.9744 | 123.5687 | -123.8892 | -123.9166
5260.7188 | 123.7473 | -61.441 | 62.1002 | -0.1844 | 0.016878 | 0.012132 | 0.015738 | 0.064307 | -0.0026831 | 0.077981 | -58.2825 | 62.1643 | -61.7523 | -61.6241 | 54.5654 | 25.1633 | 9.0363 | 8.6151 | 62.1368 | -61.7844 | -0.31128 | 0.064087 | 3.1586 | -0.18311 | -7.5348 | -0.34332 | 0.036621 | 3.4698 | 70.4773 | 70.0562 | 116.0065 | 123.6053 | 3.1586 | 123.5779 | 86.6043 | -0.34332 | 123.6053 | 3.1586 | 86.6043 | 116.0065 | 123.5779 | -123.8525 | -123.8846
5261.7188 | 123.6969 | -61.4594 | 62.1094 | -0.024185 | 0.01816 | 0.010423 | 0.012747 | 0.063452 | -0.0020421 | 0.078408 | -58.3145 | 62.1735 | -61.7569 | -61.6516 | 54.5242 | 24.9985 | 9.0637 | 8.6105 | 62.146 | -61.7661 | -0.29755 | 0.064087 | 3.1448 | -0.19226 | -7.5851 | -0.3067 | 0.036621 | 3.4424 | 70.5231 | 70.0699 | 115.9836 | 123.6328 | 3.1448 | 123.6053 | 86.4578 | -0.3067 | 123.6328 | 3.1448 | 86.4578 | 115.9836 | 123.6053 | -123.8663 | -123.8754
5262.7188 | 123.8159 | -61.4227 | 62.0682 | 0.2047 | 0.014742 | 0.0080728 | 0.011038 | 0.065589 | -0.0011877 | 0.078408 | -58.3145 | 62.114 | -61.7889 | -61.6058 | 54.5654 | 25.177 | 8.8898 | 8.6426 | 62.0911 | -61.7569 | -0.36621 | 0.045777 | 3.1082 | -0.18311 | -7.5027 | -0.33417 | 0.022888 | 3.4744 | 70.3125 | 70.0653 | 115.9882 | 123.5367 | 3.1082 | 123.5138 | 86.5997 | -0.33417 | 123.5367 | 3.1082 | 86.5997 | 115.9882 | 123.5138 | -123.8571 | -123.8251
5263.7188 | 123.7518 | -61.4273 | 62.1277 | -0.054703 | 0.01816 | 0.014054 | 0.013388 | 0.062812 | 0.00094847 | 0.077126 | -58.2916 | 62.1826 | -61.7798 | -61.615 | 54.5746 | 25.1633 | 9.0134 | 8.6014 | 62.146 | -61.7844 | -0.35248 | 0.054931 | 3.1357 | -0.18768 | -7.5531 | -0.35706 | 0.01831 | 3.4882 | 70.4407 | 70.0287 | 116.0019 | 123.6099 | 3.1357 | 123.5733 | 86.5906 | -0.35706 | 123.6099 | 3.1357 | 86.5906 | 116.0019 | 123.5733 | -123.9075 | -123.912
5264.7188 | 123.7289 | -61.4365 | 62.1002 | 0.30388 | 0.016878 | 0.011064 | 0.013388 | 0.063239 | -0.0011877 | 0.079263 | -58.2596 | 62.1826 | -61.7569 | -61.615 | 54.5609 | 25.0488 | 8.9676 | 8.6105 | 62.1597 | -61.7798 | -0.32044 | 0.082397 | 3.1769 | -0.17853 | -7.5394 | -0.34332 | 0.059509 | 3.4973 | 70.4041 | 70.047 | 115.9973 | 123.6191 | 3.1769 | 123.5962 | 86.4853 | -0.34332 | 123.6191 | 3.1769 | 86.4853 | 115.9973 | 123.5962 | -123.8571 | -123.88
5265.7188 | 123.7015 | -61.4731 | 62.1185 | 0.067368 | 0.016024 | 0.015977 | 0.014669 | 0.063452 | -0.0018285 | 0.078835 | -58.3649 | 62.1872 | -61.7935 | -61.6974 | 54.4876 | 24.9573 | 9.0042 | 8.5281 | 62.1414 | -61.7798 | -0.32043 | 0.068665 | 3.1082 | -0.2243 | -7.6309 | -0.3067 | 0.022888 | 3.4286 | 70.4773 | 70.0012 | 115.9607 | 123.6603 | 3.1082 | 123.6145 | 86.4304 | -0.3067 | 123.6603 | 3.1082 | 86.4304 | 115.9607 | 123.6145 | -123.912 | -123.8983
5266.7188 | 123.7106 | -61.4319 | 62.1094 | -0.031814 | 0.01816 | 0.015977 | 0.013815 | 0.064948 | -0.0016149 | 0.079476 | -58.2962 | 62.178 | -61.7661 | -61.6425 | 54.5792 | 25.1541 | 9.0591 | 8.6151 | 62.1368 | -61.7844 | -0.33417 | 0.068665 | 3.1357 | -0.21057 | -7.5302 | -0.35248 | 0.027466 | 3.4698 | 70.491 | 70.047 | 116.011 | 123.6099 | 3.1357 | 123.5687 | 86.586 | -0.35248 | 123.6099 | 3.1357 | 86.586 | 116.011 | 123.5687 | -123.8754 | -123.8937
5267.7188 | 123.5916 | -61.4639 | 62.0499 | 0.11314 | 0.017306 | 0.012986 | 0.014669 | 0.063239 | -0.0026831 | 0.079476 | -58.4015 | 62.1689 | -61.7889 | -61.7203 | 54.4968 | 25.1175 | 9.0591 | 8.551 | 62.1597 | -61.7844 | -0.32501 | 0.11902 | 3.0624 | -0.25635 | -7.5531 | -0.32043 | 0.10986 | 3.3875 | 70.5231 | 70.015 | 115.9607 | 123.6328 | 3.0624 | 123.6237 | 86.5814 | -0.32043 | 123.6328 | 3.0624 | 86.5814 | 115.9607 | 123.6237 | -123.8388 | -123.8342
5268.7188 | 123.761 | -61.441 | 62.1231 | -1.0084 | 0.016238 | 0.012986 | 0.015097 | 0.063452 | -0.0024695 | 0.077126 | -58.3145 | 62.1643 | -61.7706 | -61.6287 | 54.5288 | 25.1038 | 9.0408 | 8.6288 | 62.146 | -61.7844 | -0.32959 | 0.041199 | 3.1265 | -0.18768 | -7.5943 | -0.34332 | 0.022888 | 3.4561 | 70.4819 | 70.0699 | 115.9698 | 123.6053 | 3.1265 | 123.587 | 86.5448 | -0.34332 | 123.6053 | 3.1265 | 86.5448 | 115.9698 | 123.587 | -123.8937 | -123.9075
5269.7188 | 123.7289 | -61.4456 | 62.114 | -0.062332 | 0.017947 | 0.017045 | 0.013601 | 0.066016 | -0.0020421 | 0.079476 | -58.287 | 62.1689 | -61.7523 | -61.5921 | 54.4922 | 25.0763 | 9.0546 | 8.6288 | 62.1735 | -61.7752 | -0.3067 | 0.054931 | 3.1586 | -0.14648 | -7.6218 | -0.32959 | 0.059509 | 3.4653 | 70.5002 | 70.0745 | 115.9378 | 123.6145 | 3.1586 | 123.6191 | 86.5219 | -0.32959 | 123.6145 | 3.1586 | 86.5219 | 115.9378 | 123.6191 | -123.8663 | -123.8892
5270.7188 | 123.7335 | -61.4365 | 62.1277 | -0.062332 | 0.016238 | 0.012773 | 0.013174 | 0.063025 | -0.0018285 | 0.080544 | -58.3008 | 62.1643 | -61.7615 | -61.6241 | 54.538 | 25.058 | 9.0363 | 8.3588 | 62.1552 | -61.7935 | -0.32501 | 0.036621 | 3.1357 | -0.18768 | -7.5897 | -0.35706 | 0.027465 | 3.4607 | 70.4727 | 69.7952 | 115.9744 | 123.6008 | 3.1357 | 123.5916 | 86.4944 | -0.35706 | 123.6008 | 3.1357 | 86.4944 | 115.9744 | 123.5916 | -123.8892 | -123.9212
5271.7188 | 123.7793 | -61.4456 | 62.114 | -0.16151 | 0.017519 | 0.014268 | 0.014883 | 0.063025 | -0.0016149 | 0.07734 | -58.3008 | 62.1918 | -61.7661 | -61.6196 | 54.4968 | 25.0534 | 9.0271 | 8.6472 | 62.178 | -61.7752 | -0.32043 | 0.077819 | 3.1448 | -0.17395 | -7.6172 | -0.32959 | 0.064087 | 3.4653 | 70.4727 | 70.0928 | 115.9424 | 123.6374 | 3.1448 | 123.6237 | 86.499 | -0.32959 | 123.6374 | 3.1448 | 86.499 | 115.9424 | 123.6237 | -123.88 | -123.8892
5272.7188 | 123.8251 | -61.4136 | 62.0682 | 0.31151 | 0.014101 | 0.009141 | 0.0091152 | 0.06388 | -0.00033333 | 0.07734 | -58.2733 | 62.0956 | -61.734 | -61.6058 | 54.5563 | 25.0443 | 8.8806 | 8.6563 | 62.1002 | -61.734 | -0.32044 | 0.027466 | 3.1403 | -0.19226 | -7.5119 | -0.32044 | 0.032044 | 3.4607 | 70.2942 | 70.0699 | 115.9698 | 123.5092 | 3.1403 | 123.5138 | 86.4578 | -0.32044 | 123.5092 | 3.1403 | 86.4578 | 115.9698 | 123.5138 | -123.8022 | -123.8022
5273.7188 | 123.7244 | -61.4365 | 62.1597 | -0.15388 | 0.014956 | 0.012773 | 0.01531 | 0.061103 | 0.0018031 | 0.077554 | -58.287 | 62.2147 | -61.7661 | -61.6104 | 54.5471 | 25.058 | 9.0683 | 8.6197 | 62.1689 | -61.7798 | -0.32959 | 0.054932 | 3.1494 | -0.17395 | -7.6126 | -0.34332 | 0.009155 | 3.479 | 70.5048 | 70.0562 | 115.9836 | 123.6511 | 3.1494 | 123.6053 | 86.4944 | -0.34332 | 123.6511 | 3.1494 | 86.4944 | 115.9836 | 123.6053 | -123.9258 | -123.9395
5274.7188 | 123.7335 | -61.4273 | 62.1323 | -0.11574 | 0.016451 | 0.010636 | 0.012106 | 0.063452 | -0.0014013 | 0.078622 | -58.2779 | 62.1918 | -61.7523 | -61.615 | 54.5563 | 25.0351 | 9.1324 | 8.67 | 62.178 | -61.7706 | -0.32501 | 0.059509 | 3.1494 | -0.18768 | -7.576 | -0.34332 | 0.045777 | 3.4744 | 70.5597 | 70.0974 | 115.9836 | 123.6191 | 3.1494 | 123.6053 | 86.4624 | -0.34332 | 123.6191 | 3.1494 | 86.4624 | 115.9836 | 123.6053 | -123.8846 | -123.9029
5275.7188 | 123.7289 | -61.4594 | 62.0865 | -0.062332 | 0.015597 | 0.012345 | 0.015097 | 0.063239 | -0.00054693 | 0.078835 | -58.3008 | 62.1826 | -61.7798 | -61.5875 | 54.5197 | 25.0992 | 9.1095 | 8.6517 | 62.1689 | -61.7706 | -0.32043 | 0.09613 | 3.1586 | -0.12817 | -7.5668 | -0.31128 | 0.082397 | 3.479 | 70.5688 | 70.1111 | 115.979 | 123.642 | 3.1586 | 123.6282 | 86.5585 | -0.31128 | 123.642 | 3.1586 | 86.5585 | 115.979 | 123.6282 | -123.8663 | -123.8571
5276.7188 | 123.7335 | -61.4273 | 62.1277 | -0.09285 | 0.017947 | 0.0132 | 0.016592 | 0.06388 | -0.0022559 | 0.076913 | -58.2962 | 62.1689 | -61.7615 | -61.6104 | 54.5288 | 25.1038 | 9.1278 | 8.6884 | 62.178 | -61.7432 | -0.33417 | 0.041198 | 3.1311 | -0.18311 | -7.5989 | -0.31586 | 0.050354 | 3.4653 | 70.5551 | 70.1157 | 115.9561 | 123.5962 | 3.1311 | 123.6053 | 86.5311 | -0.31586 | 123.5962 | 3.1311 | 86.5311 | 115.9561 | 123.6053 | -123.8892 | -123.8708
5277.7188 | 123.6923 | -61.4502 | 62.0865 | -0.25307 | 0.017733 | 0.010636 | 0.014029 | 0.063239 | 0.00094847 | 0.080117 | -58.3878 | 62.1872 | -61.7752 | -61.6974 | 54.4601 | 25.0992 | 9.1461 | 8.606 | 62.146 | -61.8027 | -0.32501 | 0.10071 | 3.0624 | -0.24719 | -7.6263 | -0.35248 | 0.059509 | 3.3875 | 70.5963 | 70.0562 | 115.9103 | 123.6374 | 3.0624 | 123.5962 | 86.5494 | -0.35248 | 123.6374 | 3.0624 | 86.5494 | 115.9103 | 123.5962 | -123.8617 | -123.8892
5278.7188 | 123.7564 | -61.4319 | 62.1094 | -0.22255 | 0.014742 | 0.012773 | 0.013388 | 0.064093 | 0.0013757 | 0.076913 | -58.2916 | 62.1826 | -61.7432 | -61.6058 | 54.57 | 25.1907 | 9.1415 | 8.6838 | 62.1552 | -61.7523 | -0.31128 | 0.073242 | 3.1403 | -0.17395 | -7.5394 | -0.32043 | 0.045776 | 3.4515 | 70.5734 | 70.1157 | 116.0019 | 123.6145 | 3.1403 | 123.587 | 86.6226 | -0.32043 | 123.6145 | 3.1403 | 86.6226 | 116.0019 | 123.587 | -123.8525 | -123.8617
5279.7188 | 123.7015 | -61.4227 | 62.1323 | -0.047073 | 0.016451 | 0.012986 | 0.015524 | 0.061957 | -0.00054693 | 0.077981 | -58.3008 | 62.178 | -61.7706 | -61.6425 | 54.538 | 25.0259 | 9.1782 | 8.6472 | 62.178 | -61.7798 | -0.3479 | 0.045777 | 3.1219 | -0.21973 | -7.5943 | -0.35706 | 0.045777 | 3.4698 | 70.6009 | 70.0699 | 115.9607 | 123.6008 | 3.1219 | 123.6008 | 86.4487 | -0.35706 | 123.6008 | 3.1219 | 86.4487 | 115.9607 | 123.6008 | -123.9029 | -123.912
5280.7188 | 123.7473 | -61.4594 | 62.1231 | -0.15388 | 0.017519 | 0.012132 | 0.013388 | 0.063025 | 9.4068e-05 | 0.077554 | -58.2962 | 62.1689 | -61.7615 | -61.615 | 54.5563 | 25.0488 | 9.2056 | 8.7158 | 62.1872 | -61.7752 | -0.30212 | 0.045776 | 3.1631 | -0.15564 | -7.5668 | -0.31586 | 0.064087 | 3.4653 | 70.665 | 70.1752 | 116.0156 | 123.6282 | 3.1631 | 123.6465 | 86.5082 | -0.31586 | 123.6282 | 3.1631 | 86.5082 | 116.0156 | 123.6465 | -123.8846 | -123.8983
5281.7188 | 123.7564 | -61.4365 | 62.1506 | -0.031814 | 0.015597 | 0.014695 | 0.01296 | 0.062171 | -0.0011877 | 0.078835 | -58.3008 | 62.1597 | -61.7569 | -61.6196 | 54.538 | 25.0671 | 9.1278 | 8.6655 | 62.1552 | -61.7798 | -0.32044 | 0.009155 | 3.1357 | -0.18311 | -7.6126 | -0.34332 | 0.004577 | 3.4561 | 70.5643 | 70.1019 | 115.9744 | 123.5962 | 3.1357 | 123.5916 | 86.5036 | -0.34332 | 123.5962 | 3.1357 | 86.5036 | 115.9744 | 123.5916 | -123.9075 | -123.9304
5282.7344 | 123.8159 | -61.409 | 62.0956 | -0.062332 | 0.011965 | 0.01085 | 0.004202 | 0.061743 | 0.00030767 | 0.078622 | -58.342 | 62.0636 | -61.7935 | -61.5875 | 54.5929 | 25.0809 | 9.0225 | 8.7524 | 62.1231 | -61.6974 | -0.38452 | -0.032043 | 3.067 | -0.17853 | -7.5027 | -0.28839 | 0.027466 | 3.4515 | 70.4315 | 70.1614 | 116.0019 | 123.4726 | 3.067 | 123.5321 | 86.4899 | -0.28839 | 123.4726 | 3.067 | 86.4899 | 116.0019 | 123.5321 | -123.8892 | -123.793
5283.7188 | 123.7289 | -61.441 | 62.1368 | -0.16914 | 0.015169 | 0.012345 | 0.016378 | 0.061743 | -0.00054693 | 0.078408 | -58.2642 | 62.1826 | -61.7203 | -61.615 | 54.4922 | 25.0031 | 9.05 | 8.6838 | 62.178 | -61.7889 | -0.27924 | 0.045776 | 3.1769 | -0.17395 | -7.6447 | -0.3479 | 0.041199 | 3.4561 | 70.491 | 70.1248 | 115.9332 | 123.6237 | 3.1769 | 123.6191 | 86.4441 | -0.3479 | 123.6237 | 3.1769 | 86.4441 | 115.9332 | 123.6191 | -123.8571 | -123.9258
5284.7188 | 123.7473 | -61.4365 | 62.1094 | -0.09285 | 0.018801 | 0.01085 | 0.015097 | 0.064093 | -0.0022559 | 0.079904 | -58.2733 | 62.1643 | -61.7249 | -61.5921 | 54.5563 | 25.1221 | 9.1187 | 8.7021 | 62.1597 | -61.7661 | -0.28839 | 0.054932 | 3.1631 | -0.15564 | -7.5531 | -0.32959 | 0.050354 | 3.4515 | 70.5551 | 70.1385 | 115.9927 | 123.6008 | 3.1631 | 123.5962 | 86.5585 | -0.32959 | 123.6008 | 3.1631 | 86.5585 | 115.9927 | 123.5962 | -123.8342 | -123.8754
5285.7188 | 123.7427 | -61.4319 | 62.1368 | -0.12337 | 0.016024 | 0.013413 | 0.014456 | 0.062812 | 0.00052127 | 0.076272 | -58.2825 | 62.1643 | -61.7615 | -61.615 | 54.5883 | 25.1312 | 9.1049 | 8.6838 | 62.1735 | -61.7477 | -0.32959 | 0.027466 | 3.1494 | -0.1831 | -7.5485 | -0.31586 | 0.036621 | 3.479 | 70.5368 | 70.1157 | 116.0202 | 123.5962 | 3.1494 | 123.6053 | 86.5631 | -0.31586 | 123.5962 | 3.1494 | 86.5631 | 116.0202 | 123.6053 | -123.8983 | -123.8846
5286.7188 | 123.7427 | -61.441 | 62.1277 | -0.16914 | 0.016451 | 0.013841 | 0.013174 | 0.060462 | -0.0016149 | 0.07969 | -58.2733 | 62.146 | -61.7569 | -61.6241 | 54.5563 | 25.0351 | 8.9951 | 8.4366 | 62.146 | -61.7889 | -0.31586 | 0.01831 | 3.1677 | -0.18311 | -7.5714 | -0.3479 | 0.01831 | 3.4836 | 70.4361 | 69.8776 | 115.9973 | 123.587 | 3.1677 | 123.587 | 86.4761 | -0.3479 | 123.587 | 3.1677 | 86.4761 | 115.9973 | 123.587 | -123.8846 | -123.9166
5287.7344 | 123.8068 | -61.409 | 62.1094 | -0.024185 | 0.013674 | 0.010209 | 0.0033474 | 0.061103 | -0.00097413 | 0.081185 | -58.3237 | 62.0682 | -61.7661 | -61.5921 | 54.5975 | 25.1038 | 9.0271 | 8.7753 | 62.1277 | -61.702 | -0.35706 | -0.041199 | 3.0853 | -0.1831 | -7.5119 | -0.29297 | 0.018311 | 3.4424 | 70.4361 | 70.1843 | 116.0065 | 123.4772 | 3.0853 | 123.5367 | 86.5128 | -0.29297 | 123.4772 | 3.0853 | 86.5128 | 116.0065 | 123.5367 | -123.8754 | -123.8113
5288.7188 | 123.7564 | -61.4548 | 62.1368 | -0.14626 | 0.016451 | 0.011064 | 0.014883 | 0.059821 | -0.0011877 | 0.077554 | -58.287 | 62.1872 | -61.7432 | -61.6013 | 54.5563 | 25.0946 | 9.1461 | 8.7067 | 62.1368 | -61.7752 | -0.28839 | 0.050354 | 3.1677 | -0.14648 | -7.5806 | -0.32043 | 0 | 3.4561 | 70.6009 | 70.1614 | 116.011 | 123.642 | 3.1677 | 123.5916 | 86.5494 | -0.32043 | 123.642 | 3.1677 | 86.5494 | 116.011 | 123.5916 | -123.88 | -123.912
5289.7188 | 123.7289 | -61.4273 | 62.1231 | -0.069961 | 0.016451 | 0.0132 | 0.014242 | 0.064307 | 0.00030767 | 0.078835 | -58.2596 | 62.1735 | -61.7477 | -61.6104 | 54.5471 | 25.1175 | 9.0866 | 8.6746 | 62.1735 | -61.7477 | -0.32044 | 0.050354 | 3.1677 | -0.18311 | -7.576 | -0.32044 | 0.050354 | 3.4882 | 70.5139 | 70.1019 | 115.9744 | 123.6008 | 3.1677 | 123.6008 | 86.5448 | -0.32044 | 123.6008 | 3.1677 | 86.5448 | 115.9744 | 123.6008 | -123.8709 | -123.8709
5290.7188 | 123.7335 | -61.4365 | 62.1368 | -0.09285 | 0.015169 | 0.011918 | 0.012106 | 0.063025 | -0.0031103 | 0.075845 | -58.287 | 62.1872 | -61.7569 | -61.5784 | 54.5288 | 25.1358 | 9.0866 | 8.6838 | 62.178 | -61.7844 | -0.32044 | 0.050354 | 3.1494 | -0.14191 | -7.608 | -0.3479 | 0.041199 | 3.4698 | 70.5231 | 70.1202 | 115.9653 | 123.6237 | 3.1494 | 123.6145 | 86.5723 | -0.3479 | 123.6237 | 3.1494 | 86.5723 | 115.9653 | 123.6145 | -123.8937 | -123.9212
5291.7188 | 123.761 | -61.4456 | 62.1185 | -0.19966 | 0.014742 | 0.011064 | 0.013388 | 0.064307 | -0.0018285 | 0.078622 | -58.2962 | 62.178 | -61.7661 | -61.5738 | 54.5792 | 25.1404 | 9.082 | 8.6929 | 62.1964 | -61.7615 | -0.32043 | 0.05951 | 3.1494 | -0.12817 | -7.5394 | -0.31586 | 0.07782 | 3.4698 | 70.5276 | 70.1386 | 116.0248 | 123.6237 | 3.1494 | 123.642 | 86.586 | -0.31586 | 123.6237 | 3.1494 | 86.586 | 116.0248 | 123.642 | -123.8846 | -123.88
5292.7344 | 123.8342 | -61.3953 | 62.0865 | -0.15388 | 0.011965 | 0.0065774 | 0.005911 | 0.060248 | 9.4068e-05 | 0.077981 | -58.3099 | 62.0453 | -61.7615 | -61.5692 | 54.6433 | 25.2411 | 8.9584 | 8.7067 | 62.1414 | -61.6928 | -0.36621 | -0.041199 | 3.0853 | -0.17395 | -7.4432 | -0.29755 | 0.054931 | 3.4515 | 70.3537 | 70.1019 | 116.0385 | 123.4406 | 3.0853 | 123.5367 | 86.6364 | -0.29755 | 123.4406 | 3.0853 | 86.6364 | 116.0385 | 123.5367 | -123.848 | -123.7793
5293.7188 | 123.7564 | -61.4548 | 62.1323 | -0.14626 | 0.014529 | 0.015122 | 0.01766 | 0.060248 | -0.0014013 | 0.077981 | -58.2916 | 62.178 | -61.7386 | -61.6013 | 54.5471 | 24.7467 | 9.082 | 8.606 | 62.1414 | -61.7844 | -0.28381 | 0.045777 | 3.1631 | -0.14648 | -7.5851 | -0.32959 | 0.009155 | 3.447 | 70.5368 | 70.0607 | 116.0019 | 123.6328 | 3.1631 | 123.5962 | 86.2015 | -0.32959 | 123.6328 | 3.1631 | 86.2015 | 116.0019 | 123.5962 | -123.8708 | -123.9166
5294.7188 | 123.7198 | -61.4365 | 62.1552 | -0.16914 | 0.016238 | 0.0095682 | 0.014669 | 0.06153 | 0.00030767 | 0.077126 | -58.3008 | 62.1826 | -61.7386 | -61.5875 | 54.5425 | 24.3668 | 9.1095 | 8.6563 | 62.178 | -61.7477 | -0.30212 | 0.027466 | 3.1357 | -0.15106 | -7.6126 | -0.31128 | 0.022889 | 3.4378 | 70.546 | 70.0928 | 115.979 | 123.6191 | 3.1357 | 123.6145 | 85.8032 | -0.31128 | 123.6191 | 3.1357 | 85.8032 | 115.979 | 123.6145 | -123.8937 | -123.9029
5295.7188 | 123.7473 | -61.4044 | 62.1368 | -0.20729 | 0.014956 | 0.015122 | 0.018087 | 0.061103 | -0.00076053 | 0.079049 | -58.255 | 62.1872 | -61.7569 | -61.5967 | 54.5242 | 24.4034 | 9.0454 | 8.6609 | 62.1872 | -61.7569 | -0.35248 | 0.050354 | 3.1494 | -0.19226 | -7.6126 | -0.35248 | 0.050354 | 3.5019 | 70.4498 | 70.0653 | 115.9287 | 123.5916 | 3.1494 | 123.5916 | 85.8078 | -0.35248 | 123.5916 | 3.1494 | 85.8078 | 115.9287 | 123.5916 | -123.8937 | -123.8937
5296.7188 | 123.7473 | -61.441 | 62.1277 | -0.20729 | 0.016238 | 0.0082864 | 0.013601 | 0.063666 | 0.00030767 | 0.078408 | -58.2825 | 62.1826 | -61.734 | -61.5875 | 54.5883 | 24.5728 | 9.1095 | 8.7112 | 62.1826 | -61.7432 | -0.29297 | 0.054931 | 3.1586 | -0.14648 | -7.5394 | -0.30212 | 0.054931 | 3.4515 | 70.5505 | 70.1523 | 116.0294 | 123.6237 | 3.1586 | 123.6237 | 86.0138 | -0.30212 | 123.6237 | 3.1586 | 86.0138 | 116.0294 | 123.6237 | -123.8617 | -123.8708
5297.7344 | 123.793 | -61.409 | 62.0773 | -0.0012969 | 0.014101 | 0.012986 | 0.0091152 | 0.063239 | -0.0035375 | 0.077767 | -58.2733 | 62.0682 | -61.7615 | -61.5967 | 54.5792 | 24.6414 | 8.9264 | 8.7479 | 62.114 | -61.7294 | -0.35248 | -0.009156 | 3.1357 | -0.18768 | -7.4982 | -0.32043 | 0.036621 | 3.4882 | 70.3354 | 70.1569 | 115.9882 | 123.4772 | 3.1357 | 123.523 | 86.0504 | -0.32043 | 123.4772 | 3.1357 | 86.0504 | 115.9882 | 123.523 | -123.8388 | -123.8068
5298.7188 | 123.7518 | -61.4319 | 62.1277 | -0.1844 | 0.014956 | 0.012559 | 0.014029 | 0.06153 | -0.00033333 | 0.078408 | -58.3099 | 62.1872 | -61.734 | -61.6013 | 54.5609 | 24.4858 | 9.1278 | 8.6975 | 62.1826 | -61.7706 | -0.30212 | 0.059509 | 3.1219 | -0.16937 | -7.5668 | -0.33874 | 0.054931 | 3.4241 | 70.5597 | 70.1294 | 115.9927 | 123.6191 | 3.1219 | 123.6145 | 85.9177 | -0.33874 | 123.6191 | 3.1219 | 85.9177 | 115.9927 | 123.6145 | -123.8617 | -123.8983
5299.7188 | 123.7564 | -61.4548 | 62.1506 | -0.131 | 0.014101 | 0.012986 | 0.011679 | 0.062384 | -0.0035375 | 0.079049 | -58.3145 | 62.2055 | -61.7706 | -61.6058 | 54.5471 | 24.4034 | 9.1736 | 8.7112 | 62.1735 | -61.7523 | -0.31586 | 0.054931 | 3.1403 | -0.15106 | -7.6035 | -0.29755 | 0.022888 | 3.4561 | 70.6284 | 70.166 | 116.0019 | 123.6603 | 3.1403 | 123.6282 | 85.8582 | -0.29755 | 123.6603 | 3.1403 | 85.8582 | 116.0019 | 123.6282 | -123.9212 | -123.9029
5300.7188 | 123.7152 | -61.4319 | 62.1506 | -0.15388 | 0.016238 | 0.0099954 | 0.011251 | 0.060675 | -0.00011953 | 0.076913 | -58.3328 | 62.178 | -61.7798 | -61.6287 | 54.538 | 24.4537 | 9.1553 | 8.67 | 62.1826 | -61.734 | -0.3479 | 0.027466 | 3.0991 | -0.19684 | -7.6126 | -0.30212 | 0.032043 | 3.447 | 70.5872 | 70.1019 | 115.9698 | 123.6099 | 3.0991 | 123.6145 | 85.8856 | -0.30212 | 123.6099 | 3.0991 | 85.8856 | 115.9698 | 123.6145 | -123.9304 | -123.8846
5301.7188 | 123.7152 | -61.4273 | 62.1414 | -0.22255 | 0.01581 | 0.017045 | 0.011465 | 0.061103 | -0.0018285 | 0.076272 | -58.3191 | 62.1735 | -61.7706 | -61.6241 | 54.5151 | 24.5087 | 9.1736 | 8.6792 | 62.1872 | -61.7661 | -0.34332 | 0.032044 | 3.1082 | -0.19684 | -7.6263 | -0.33875 | 0.045777 | 3.4515 | 70.6009 | 70.1065 | 115.9424 | 123.6008 | 3.1082 | 123.6145 | 85.936 | -0.33875 | 123.6008 | 3.1082 | 85.936 | 115.9424 | 123.6145 | -123.912 | -123.9075
5302.7188 | 123.7106 | -61.4548 | 62.1323 | -0.031814 | 0.017733 | 0.013413 | 0.016165 | 0.062812 | -0.00097413 | 0.078835 | -58.2916 | 62.1597 | -61.7523 | -61.615 | 54.5334 | 24.7467 | 9.1049 | 8.67 | 62.1506 | -61.7661 | -0.29755 | 0.027466 | 3.1631 | -0.16022 | -7.5989 | -0.31128 | 0.018311 | 3.4607 | 70.5597 | 70.1248 | 115.9882 | 123.6145 | 3.1631 | 123.6053 | 86.2015 | -0.31128 | 123.6145 | 3.1631 | 86.2015 | 115.9882 | 123.6053 | -123.8846 | -123.8983
5303.7188 | 123.7747 | -61.441 | 62.1689 | -0.29121 | 0.017092 | 0.014054 | 0.01296 | 0.060462 | -0.00033333 | 0.079476 | -58.3328 | 62.1872 | -61.7432 | -61.5921 | 54.5654 | 24.6689 | 9.1736 | 8.7067 | 62.1414 | -61.7569 | -0.30212 | 0.018311 | 3.1082 | -0.15106 | -7.6035 | -0.31586 | -0.027466 | 3.4103 | 70.6146 | 70.1477 | 116.0065 | 123.6282 | 3.1082 | 123.5825 | 86.1099 | -0.31586 | 123.6282 | 3.1082 | 86.1099 | 116.0065 | 123.5825 | -123.912 | -123.9258
5304.7188 | 123.7061 | -61.4502 | 62.1735 | -0.17677 | 0.016878 | 0.0085 | 0.011892 | 0.061316 | -0.0028967 | 0.079049 | -58.3328 | 62.1689 | -61.7615 | -61.6425 | 54.538 | 24.6185 | 9.2148 | 8.6929 | 62.1735 | -61.7432 | -0.31128 | -0.004578 | 3.1174 | -0.19226 | -7.6355 | -0.29297 | 0 | 3.4286 | 70.665 | 70.1431 | 115.9882 | 123.6191 | 3.1174 | 123.6237 | 86.0687 | -0.29297 | 123.6191 | 3.1174 | 86.0687 | 115.9882 | 123.6237 | -123.9349 | -123.9166
5305.7188 | 123.7244 | -61.4502 | 62.1506 | -0.23781 | 0.016878 | 0.0099954 | 0.012533 | 0.061957 | -0.00054693 | 0.077554 | -58.3374 | 62.1552 | -61.7706 | -61.6425 | 54.5654 | 24.7055 | 9.2194 | 8.6838 | 62.2147 | -61.7386 | -0.32043 | 0.004577 | 3.1128 | -0.19226 | -7.5851 | -0.28839 | 0.064087 | 3.4332 | 70.6696 | 70.134 | 116.0156 | 123.6053 | 3.1128 | 123.6649 | 86.1557 | -0.28839 | 123.6053 | 3.1128 | 86.1557 | 116.0156 | 123.6649 | -123.9212 | -123.8892
5306.7188 | 123.7335 | -61.4548 | 62.1323 | -0.24544 | 0.015383 | 0.0099954 | 0.015097 | 0.060675 | -0.0020421 | 0.079263 | -58.2916 | 62.1689 | -61.7615 | -61.5921 | 54.5654 | 24.7238 | 9.1782 | 8.6929 | 62.178 | -61.7432 | -0.3067 | 0.036621 | 3.1631 | -0.13733 | -7.5668 | -0.28839 | 0.045777 | 3.4698 | 70.6329 | 70.1477 | 116.0202 | 123.6237 | 3.1631 | 123.6328 | 86.1786 | -0.28839 | 123.6237 | 3.1631 | 86.1786 | 116.0202 | 123.6328 | -123.8937 | -123.8754
5307.7188 | 123.6832 | -61.4502 | 62.1323 | 0.029221 | 0.018801 | 0.011704 | 0.015738 | 0.062598 | -0.00097413 | 0.080117 | -58.3008 | 62.1689 | -61.7752 | -61.6608 | 54.5334 | 24.7833 | 9.1782 | 8.5739 | 62.146 | -61.7706 | -0.32501 | 0.036621 | 3.1494 | -0.21057 | -7.5989 | -0.32043 | 0.013733 | 3.4744 | 70.6284 | 70.0241 | 115.9836 | 123.6191 | 3.1494 | 123.5962 | 86.2335 | -0.32043 | 123.6191 | 3.1494 | 86.2335 | 115.9836 | 123.5962 | -123.9075 | -123.9029
5308.7188 | 123.7106 | -61.4365 | 62.1643 | -0.25307 | 0.015597 | 0.0087138 | 0.0097562 | 0.05918 | 0.00073487 | 0.078195 | -58.374 | 62.1826 | -61.7569 | -61.7157 | 54.6021 | 24.8154 | 9.1187 | 8.6472 | 62.1643 | -61.7798 | -0.32044 | 0.01831 | 3.0624 | -0.27924 | -7.5623 | -0.34332 | 0 | 3.3829 | 70.5551 | 70.0836 | 116.0385 | 123.6191 | 3.0624 | 123.6008 | 86.2518 | -0.34332 | 123.6191 | 3.0624 | 86.2518 | 116.0385 | 123.6008 | -123.9212 | -123.9441
5309.7188 | 123.7152 | -61.4548 | 62.146 | -0.24544 | 0.014315 | 0.013413 | 0.010824 | 0.062598 | -0.0024695 | 0.079263 | -58.3374 | 62.1414 | -61.7477 | -61.6287 | 54.5654 | 24.9252 | 9.1965 | 8.6334 | 62.1735 | -61.7523 | -0.29297 | -0.004578 | 3.1174 | -0.17395 | -7.5806 | -0.29755 | 0.027466 | 3.4103 | 70.6512 | 70.0882 | 116.0202 | 123.5962 | 3.1174 | 123.6282 | 86.38 | -0.29755 | 123.5962 | 3.1174 | 86.38 | 116.0202 | 123.6282 | -123.8937 | -123.8983
5310.7188 | 123.6832 | -61.4319 | 62.1368 | -0.069961 | 0.013674 | 0.013627 | 0.011892 | 0.062171 | -0.00033333 | 0.077981 | -58.3282 | 62.1597 | -61.7569 | -61.647 | 54.5334 | 24.9207 | 9.2194 | 8.6334 | 62.1872 | -61.7661 | -0.32501 | 0.022888 | 3.1036 | -0.21515 | -7.6035 | -0.33417 | 0.050354 | 3.4287 | 70.6512 | 70.0653 | 115.9653 | 123.5916 | 3.1036 | 123.6191 | 86.3525 | -0.33417 | 123.5916 | 3.1036 | 86.3525 | 115.9653 | 123.6191 | -123.8937 | -123.9029
5311.7188 | 123.7106 | -61.4456 | 62.1506 | -0.3904 | 0.015597 | 0.011064 | 0.012533 | 0.059394 | -0.0014013 | 0.076913 | -58.4747 | 62.1597 | -61.7981 | -61.6745 | 54.5792 | 24.9023 | 9.2148 | 8.6288 | 62.2009 | -61.7477 | -0.35248 | 0.009155 | 2.9709 | -0.22888 | -7.5714 | -0.30212 | 0.050354 | 3.3234 | 70.6604 | 70.0745 | 116.0248 | 123.6053 | 2.9709 | 123.6465 | 86.348 | -0.30212 | 123.6053 | 2.9709 | 86.348 | 116.0248 | 123.6465 | -123.9487 | -123.8983
5312.7188 | 123.7244 | -61.4731 | 62.1048 | 0.14366 | 0.015597 | 0.0076456 | 0.015097 | 0.062812 | -0.00076053 | 0.077554 | -58.3649 | 62.1368 | -61.7661 | -61.6699 | 54.5609 | 24.9985 | 9.082 | 8.5968 | 62.1185 | -61.7844 | -0.29297 | 0.032044 | 3.1082 | -0.19684 | -7.5439 | -0.31128 | 0.013733 | 3.4012 | 70.5551 | 70.0699 | 116.0339 | 123.6099 | 3.1082 | 123.5916 | 86.4716 | -0.31128 | 123.6099 | 3.1082 | 86.4716 | 116.0339 | 123.5916 | -123.8708 | -123.8892
5313.7188 | 123.7152 | -61.4456 | 62.1506 | -0.21492 | 0.014742 | 0.010209 | 0.014456 | 0.060248 | -0.0026831 | 0.07734 | -58.3511 | 62.1643 | -61.7477 | -61.6379 | 54.5746 | 24.9893 | 9.256 | 8.67 | 62.178 | -61.7889 | -0.30212 | 0.013733 | 3.0945 | -0.19226 | -7.576 | -0.34332 | 0.027466 | 3.3966 | 70.7016 | 70.1157 | 116.0202 | 123.6099 | 3.0945 | 123.6237 | 86.4349 | -0.34332 | 123.6099 | 3.0945 | 86.4349 | 116.0202 | 123.6237 | -123.8983 | -123.9395
5314.7188 | 123.7152 | -61.4319 | 62.1414 | -0.29884 | 0.016878 | 0.0132 | 0.0097562 | 0.061316 | -0.0022559 | 0.076699 | -58.3511 | 62.1506 | -61.7661 | -61.6608 | 54.5792 | 25.0534 | 9.2514 | 8.6517 | 62.1689 | -61.7523 | -0.33417 | 0.009156 | 3.0808 | -0.22888 | -7.5623 | -0.32043 | 0.027466 | 3.4149 | 70.6833 | 70.0836 | 116.011 | 123.5825 | 3.0808 | 123.6008 | 86.4853 | -0.32043 | 123.5825 | 3.0808 | 86.4853 | 116.011 | 123.6008 | -123.9075 | -123.8937
5315.7188 | 123.7244 | -61.4548 | 62.1552 | -0.27596 | 0.015597 | 0.016191 | 0.010824 | 0.060462 | -0.0011877 | 0.079263 | -58.342 | 62.1414 | -61.7386 | -61.6333 | 54.57 | 24.9664 | 9.256 | 8.7021 | 62.1689 | -61.7294 | -0.28381 | -0.013733 | 3.1128 | -0.17853 | -7.5851 | -0.27466 | 0.013733 | 3.3966 | 70.7108 | 70.1569 | 116.0248 | 123.5962 | 3.1128 | 123.6237 | 86.4212 | -0.27466 | 123.5962 | 3.1128 | 86.4212 | 116.0248 | 123.6237 | -123.8937 | -123.8846
5316.7188 | 123.7061 | -61.4136 | 62.1552 | -0.25307 | 0.014742 | 0.0082864 | 0.012106 | 0.064734 | -0.00054693 | 0.077981 | -58.3649 | 62.1506 | -61.7935 | -61.6196 | 54.5471 | 24.7925 | 9.2743 | 8.6197 | 62.146 | -61.7386 | -0.37994 | -0.004577 | 3.0487 | -0.20599 | -7.608 | -0.32501 | -0.009155 | 3.4286 | 70.6879 | 70.0333 | 115.9607 | 123.5641 | 3.0487 | 123.5596 | 86.2061 | -0.32501 | 123.5641 | 3.0487 | 86.2061 | 115.9607 | 123.5596 | -123.9487 | -123.8937
5317.7188 | 123.7198 | -61.4182 | 62.1506 | -0.1844 | 0.015597 | 0.011704 | 0.010611 | 0.060889 | -0.0024695 | 0.07734 | -58.3511 | 62.1552 | -61.7752 | -61.6379 | 54.5105 | 24.8474 | 9.5489 | 8.6929 | 62.2147 | -61.7065 | -0.35706 | 0.004577 | 3.067 | -0.21973 | -7.6401 | -0.28839 | 0.064087 | 3.4241 | 70.9671 | 70.1111 | 115.9287 | 123.5733 | 3.067 | 123.6328 | 86.2656 | -0.28839 | 123.5733 | 3.067 | 86.2656 | 115.9287 | 123.6328 | -123.9258 | -123.8571
5318.7344 | 123.6832 | -61.4502 | 62.1094 | 0.16655 | 0.016024 | 0.0132 | 0.011251 | 0.058539 | -0.00011953 | 0.079263 | -58.3786 | 62.1414 | -61.7844 | -61.6791 | 54.5883 | 24.9481 | 9.0912 | 8.6014 | 62.1323 | -61.7844 | -0.33417 | 0.032043 | 3.0716 | -0.22888 | -7.5211 | -0.33417 | 0.022888 | 3.4058 | 70.5414 | 70.0516 | 116.0385 | 123.5916 | 3.0716 | 123.5825 | 86.3983 | -0.33417 | 123.5916 | 3.0716 | 86.3983 | 116.0385 | 123.5825 | -123.8937 | -123.8937
5319.7188 | 123.7244 | -61.4365 | 62.1323 | -0.29884 | 0.016665 | 0.011918 | 0.011679 | 0.057257 | -0.0018285 | 0.079263 | -58.3557 | 62.146 | -61.7661 | -61.6333 | 54.5151 | 24.971 | 9.256 | 8.6288 | 62.1506 | -61.7477 | -0.32959 | 0.013733 | 3.0807 | -0.19684 | -7.6172 | -0.31128 | 0.018311 | 3.4103 | 70.6924 | 70.0653 | 115.9515 | 123.5825 | 3.0807 | 123.587 | 86.4075 | -0.31128 | 123.5825 | 3.0807 | 86.4075 | 115.9515 | 123.587 | -123.8983 | -123.88
5320.7188 | 123.6969 | -61.4273 | 62.1552 | 1.5932 | 0.014742 | 0.010423 | 0.010824 | 0.060675 | 0.00094847 | 0.078622 | -58.3145 | 62.1552 | -61.7706 | -61.6241 | 54.538 | 24.9435 | 9.2697 | 8.6609 | 62.1872 | -61.7294 | -0.34332 | 0 | 3.1128 | -0.19684 | -7.6172 | -0.30212 | 0.032044 | 3.4561 | 70.697 | 70.0882 | 115.9653 | 123.5825 | 3.1128 | 123.6145 | 86.3708 | -0.30212 | 123.5825 | 3.1128 | 86.3708 | 115.9653 | 123.6145 | -123.9258 | -123.8846
5321.7188 | 123.7198 | -61.4136 | 62.146 | -0.26833 | 0.014101 | 0.01085 | 0.0089016 | 0.059821 | -0.00054693 | 0.079049 | -58.3054 | 62.1185 | -61.734 | -61.6104 | 54.4876 | 24.8566 | 9.3018 | 8.6609 | 62.1964 | -61.7294 | -0.32044 | -0.027466 | 3.1082 | -0.19684 | -7.6584 | -0.31586 | 0.050354 | 3.4286 | 70.7153 | 70.0745 | 115.9012 | 123.5321 | 3.1082 | 123.6099 | 86.2701 | -0.31586 | 123.5321 | 3.1082 | 86.2701 | 115.9012 | 123.6099 | -123.88 | -123.8754
5322.7344 | 123.7198 | -61.4456 | 62.1368 | -0.031814 | 0.016878 | 0.0089274 | 0.018301 | 0.061316 | -0.0052465 | 0.076486 | -58.3008 | 62.1597 | -61.7523 | -61.6379 | 54.4281 | 24.7421 | 9.2422 | 8.6563 | 62.1368 | -61.7615 | -0.3067 | 0.022888 | 3.1448 | -0.19226 | -7.7087 | -0.31586 | 0 | 3.4515 | 70.6879 | 70.1019 | 115.8737 | 123.6053 | 3.1448 | 123.5825 | 86.1877 | -0.31586 | 123.6053 | 3.1448 | 86.1877 | 115.8737 | 123.5825 | -123.8892 | -123.8983
5323.7188 | 123.6191 | -61.3998 | 62.1597 | -0.19203 | 0.014315 | 0.0078592 | 0.011251 | 0.063666 | -0.0020421 | 0.077767 | -58.3649 | 62.1231 | -61.7523 | -61.647 | 54.4968 | 24.8886 | 9.3384 | 8.7524 | 62.1872 | -61.7249 | -0.35248 | -0.036621 | 3.035 | -0.24719 | -7.663 | -0.32501 | 0.027466 | 3.3875 | 70.7382 | 70.1523 | 115.8966 | 123.5229 | 3.035 | 123.587 | 86.2885 | -0.32501 | 123.5229 | 3.035 | 86.2885 | 115.8966 | 123.587 | -123.912 | -123.8846
5324.7188 | 123.7106 | -61.4227 | 62.1735 | -0.25307 | 0.012606 | 0.0087138 | 0.011251 | 0.060248 | -0.00011953 | 0.078622 | -58.374 | 62.1323 | -61.7432 | -61.647 | 54.4922 | 24.8795 | 9.3384 | 8.6884 | 62.1735 | -61.7386 | -0.32044 | -0.041199 | 3.0487 | -0.22431 | -7.6813 | -0.31586 | 0 | 3.3691 | 70.7611 | 70.1111 | 115.9149 | 123.555 | 3.0487 | 123.5962 | 86.3022 | -0.31586 | 123.555 | 3.0487 | 86.3022 | 115.9149 | 123.5962 | -123.9166 | -123.912
5325.7188 | 123.7198 | -61.441 | 62.1597 | -0.3141 | 0.013674 | 0.010636 | 0.011679 | 0.060462 | -0.0026831 | 0.079049 | -58.3603 | 62.1231 | -61.7661 | -61.6287 | 54.4876 | 24.8657 | 9.2972 | 8.7021 | 62.1597 | -61.734 | -0.32501 | -0.036621 | 3.0807 | -0.18768 | -7.6721 | -0.29297 | 0 | 3.4058 | 70.7382 | 70.1431 | 115.9287 | 123.5641 | 3.0807 | 123.6008 | 86.3068 | -0.29297 | 123.5641 | 3.0807 | 86.3068 | 115.9287 | 123.6008 | -123.9258 | -123.8937
5326.7188 | 123.6923 | -61.4456 | 62.178 | -0.12337 | 0.014315 | 0.0072184 | 0.010824 | 0.061103 | -0.0026831 | 0.078195 | -58.3237 | 62.1323 | -61.7661 | -61.6333 | 54.4968 | 24.8383 | 9.2422 | 8.6838 | 62.1872 | -61.7386 | -0.32043 | -0.045777 | 3.1219 | -0.18768 | -7.6813 | -0.29297 | 0.009155 | 3.4424 | 70.6879 | 70.1294 | 115.9424 | 123.5779 | 3.1219 | 123.6328 | 86.2839 | -0.29297 | 123.5779 | 3.1219 | 86.2839 | 115.9424 | 123.6328 | -123.9441 | -123.9166
5327.7188 | 123.7061 | -61.4594 | 62.1094 | -0.66505 | 0.015383 | 0.015122 | 0.019369 | 0.062384 | -0.00033333 | 0.080972 | -58.3694 | 62.146 | -61.7523 | -61.6562 | 54.5105 | 24.8428 | 9.1507 | 8.6151 | 62.1277 | -61.7844 | -0.29297 | 0.036621 | 3.0899 | -0.19684 | -7.5989 | -0.32501 | 0.018311 | 3.3829 | 70.61 | 70.0745 | 115.9698 | 123.6053 | 3.0899 | 123.587 | 86.3022 | -0.32501 | 123.6053 | 3.0899 | 86.3022 | 115.9698 | 123.587 | -123.8617 | -123.8937
5328.7188 | 123.7015 | -61.4319 | 62.1277 | -0.26833 | 0.013674 | 0.0085 | 0.012747 | 0.060462 | -0.00097413 | 0.076486 | -58.3099 | 62.146 | -61.7477 | -61.615 | 54.5883 | 24.852 | 9.169 | 8.6929 | 62.1643 | -61.7203 | -0.31586 | 0.01831 | 3.1219 | -0.1831 | -7.5394 | -0.28839 | 0.036621 | 3.4378 | 70.6009 | 70.1248 | 116.0202 | 123.5779 | 3.1219 | 123.5962 | 86.2839 | -0.28839 | 123.5779 | 3.1219 | 86.2839 | 116.0202 | 123.5962 | -123.8754 | -123.848
5329.7188 | 123.7061 | -61.4456 | 62.1506 | -0.19203 | 0.014529 | 0.01085 | 0.011251 | 0.058966 | -0.0016149 | 0.079263 | -58.3145 | 62.1185 | -61.7203 | -61.5829 | 54.6066 | 24.9847 | 9.1782 | 8.7296 | 62.146 | -61.7386 | -0.27466 | -0.032044 | 3.1311 | -0.13733 | -7.5439 | -0.29297 | -0.004578 | 3.4058 | 70.6238 | 70.1752 | 116.0522 | 123.5641 | 3.1311 | 123.5916 | 86.4304 | -0.29297 | 123.5641 | 3.1311 | 86.4304 | 116.0522 | 123.5916 | -123.8708 | -123.8892
5330.7188 | 123.7152 | -61.4456 | 62.1414 | -0.2607 | 0.017092 | 0.0089274 | 0.013388 | 0.061316 | -0.0028967 | 0.079476 | -58.3557 | 62.1506 | -61.7569 | -61.647 | 54.5563 | 24.8062 | 9.5444 | 8.6243 | 62.2284 | -61.7294 | -0.31128 | 0.009156 | 3.0899 | -0.20142 | -7.5851 | -0.28381 | 0.086976 | 3.4012 | 70.99 | 70.0699 | 116.0019 | 123.5962 | 3.0899 | 123.674 | 86.2518 | -0.28381 | 123.5962 | 3.0899 | 86.2518 | 116.0019 | 123.674 | -123.8983 | -123.8708
5331.7188 | 123.7015 | -61.4182 | 62.1918 | -0.3141 | 0.017306 | 0.011704 | 0.012533 | 0.059607 | -0.0020421 | 0.078195 | -58.3603 | 62.1552 | -61.7706 | -61.615 | 54.5334 | 24.939 | 9.2056 | 8.638 | 62.146 | -61.7432 | -0.35248 | -0.036621 | 3.0579 | -0.19684 | -7.6584 | -0.32501 | -0.045776 | 3.4103 | 70.6238 | 70.0562 | 115.9515 | 123.5733 | 3.0579 | 123.5641 | 86.3571 | -0.32501 | 123.5733 | 3.0579 | 86.3571 | 115.9515 | 123.5641 | -123.9624 | -123.9349
5332.7344 | 123.6923 | -61.4548 | 62.146 | 0.052109 | 0.015169 | 0.011704 | 0.020224 | 0.061957 | -0.0020421 | 0.079049 | -58.3374 | 62.1735 | -61.7386 | -61.6516 | 54.5242 | 24.9527 | 9.1324 | 8.5556 | 62.1368 | -61.7935 | -0.28381 | 0.027466 | 3.1174 | -0.19684 | -7.6218 | -0.33874 | -0.009155 | 3.4012 | 70.5872 | 70.0104 | 115.979 | 123.6282 | 3.1174 | 123.5916 | 86.4075 | -0.33874 | 123.6282 | 3.1174 | 86.4075 | 115.979 | 123.5916 | -123.8846 | -123.9395
5333.7188 | 123.7061 | -61.4548 | 62.1552 | -0.27596 | 0.016024 | 0.013627 | 0.012533 | 0.061743 | -0.0026831 | 0.077126 | -58.3878 | 62.1552 | -61.7569 | -61.6287 | 54.5334 | 24.9298 | 9.2011 | 8.6655 | 62.2009 | -61.7523 | -0.30212 | 0 | 3.067 | -0.17395 | -7.6218 | -0.29755 | 0.045777 | 3.3691 | 70.6558 | 70.1202 | 115.9882 | 123.6099 | 3.067 | 123.6557 | 86.3846 | -0.29755 | 123.6099 | 3.067 | 86.3846 | 115.9882 | 123.6557 | -123.912 | -123.9075
5334.7188 | 123.7061 | -61.4365 | 62.114 | -0.76424 | 0.015383 | 0.007432 | 0.012533 | 0.058753 | -0.0028967 | 0.080117 | -58.4061 | 62.1552 | -61.7523 | -61.6287 | 54.4922 | 24.8978 | 9.1782 | 8.6334 | 62.1872 | -61.7294 | -0.31586 | 0.041198 | 3.0304 | -0.19226 | -7.6218 | -0.29297 | 0.073242 | 3.3463 | 70.6146 | 70.0699 | 115.9286 | 123.5916 | 3.0304 | 123.6237 | 86.3342 | -0.29297 | 123.5916 | 3.0304 | 86.3342 | 115.9286 | 123.6237 | -123.8663 | -123.8434
5335.7188 | 123.6923 | -61.4136 | 62.1506 | -0.29884 | 0.013888 | 0.010209 | 0.0097562 | 0.059821 | -0.00097413 | 0.079049 | -58.342 | 62.1506 | -61.7523 | -61.615 | 54.4968 | 24.8978 | 9.2468 | 8.7296 | 62.1826 | -61.7157 | -0.33875 | 0 | 3.0716 | -0.20142 | -7.6538 | -0.30212 | 0.032043 | 3.4103 | 70.6604 | 70.1431 | 115.9103 | 123.5641 | 3.0716 | 123.5962 | 86.3113 | -0.30212 | 123.5641 | 3.0716 | 86.3113 | 115.9103 | 123.5962 | -123.9029 | -123.8663
5336.7188 | 123.7198 | -61.4365 | 62.1277 | -0.24544 | 0.013674 | 0.012132 | 0.01232 | 0.059394 | -0.0018285 | 0.078835 | -58.3237 | 62.1277 | -61.7523 | -61.6104 | 54.4968 | 24.8795 | 9.2697 | 8.7616 | 62.1643 | -61.7477 | -0.31586 | 0 | 3.1128 | -0.17395 | -7.6309 | -0.31128 | 0.036621 | 3.4286 | 70.7062 | 70.1981 | 115.9332 | 123.5641 | 3.1128 | 123.6008 | 86.3159 | -0.31128 | 123.5641 | 3.1128 | 86.3159 | 115.9332 | 123.6008 | -123.88 | -123.8754
5337.7188 | 123.7473 | -61.4319 | 62.146 | -0.054703 | 0.016665 | 0.014909 | 0.016806 | 0.06153 | -0.0011877 | 0.076058 | -58.223 | 62.1414 | -61.7477 | -61.5921 | 54.5517 | 25.0534 | 9.2011 | 8.7479 | 62.146 | -61.7386 | -0.31586 | -0.004578 | 3.2089 | -0.16022 | -7.5943 | -0.3067 | 0 | 3.5248 | 70.6329 | 70.1797 | 115.9836 | 123.5733 | 3.2089 | 123.5779 | 86.4853 | -0.3067 | 123.5733 | 3.2089 | 86.4853 | 115.9836 | 123.5779 | -123.8937 | -123.8846
5338.7188 | 123.7885 | -61.409 | 62.1597 | -0.26833 | 0.01346 | 0.009141 | 0.011038 | 0.060248 | -0.00076053 | 0.076913 | -58.3649 | 62.1094 | -61.7661 | -61.6425 | 54.4647 | 24.9527 | 9.3384 | 8.7662 | 62.1872 | -61.7523 | -0.35706 | -0.050354 | 3.0441 | -0.23346 | -7.695 | -0.34332 | 0.027466 | 3.4012 | 70.7474 | 70.1752 | 115.8737 | 123.5184 | 3.0441 | 123.5962 | 86.3617 | -0.34332 | 123.5184 | 3.0441 | 86.3617 | 115.8737 | 123.5962 | -123.9258 | -123.912
5339.7188 | 123.7015 | -61.4548 | 62.1597 | -0.20729 | 0.01346 | 0.0082864 | 0.010611 | 0.060675 | -0.0018285 | 0.079476 | -58.3466 | 62.1323 | -61.7615 | -61.6379 | 54.5242 | 24.9985 | 9.3246 | 8.7204 | 62.1552 | -61.734 | -0.3067 | -0.027466 | 3.1082 | -0.1831 | -7.6355 | -0.27924 | -0.004578 | 3.4149 | 70.7794 | 70.1752 | 115.979 | 123.587 | 3.1082 | 123.6099 | 86.4532 | -0.27924 | 123.587 | 3.1082 | 86.4532 | 115.979 | 123.6099 | -123.9212 | -123.8937
5340.7188 | 123.7335 | -61.4456 | 62.1552 | -0.51247 | 0.014742 | 0.006791 | 0.012533 | 0.060248 | -0.0016149 | 0.079476 | -58.3603 | 62.1368 | -61.7432 | -61.647 | 54.483 | 24.9435 | 9.3201 | 8.725 | 62.1506 | -61.7386 | -0.29755 | -0.01831 | 3.0853 | -0.20142 | -7.6721 | -0.29297 | -0.004577 | 3.3829 | 70.7657 | 70.1706 | 115.9287 | 123.5825 | 3.0853 | 123.5962 | 86.3892 | -0.29297 | 123.5825 | 3.0853 | 86.3892 | 115.9287 | 123.5962 | -123.8983 | -123.8937
5341.7188 | 123.7152 | -61.4456 | 62.1506 | 1.6085 | 0.016451 | 0.011704 | 0.011679 | 0.060034 | -0.00054693 | 0.076486 | -58.3282 | 62.146 | -61.7706 | -61.615 | 54.5105 | 24.971 | 9.3155 | 8.7067 | 62.1689 | -61.7477 | -0.32501 | -0.004578 | 3.1174 | -0.16937 | -7.6401 | -0.30212 | 0.01831 | 3.4424 | 70.7611 | 70.1523 | 115.9561 | 123.5916 | 3.1174 | 123.6145 | 86.4166 | -0.30212 | 123.5916 | 3.1174 | 86.4166 | 115.9561 | 123.6145 | -123.9212 | -123.8983
5342.7344 | 123.6877 | -61.4822 | 62.114 | 0.14366 | 0.016665 | 0.014909 | 0.017233 | 0.062171 | -0.0022559 | 0.075845 | -58.3511 | 62.1597 | -61.7844 | -61.6882 | 54.4189 | 24.8108 | 9.288 | 8.6105 | 62.146 | -61.7706 | -0.30212 | 0.045776 | 3.1311 | -0.20599 | -7.695 | -0.28839 | 0.032043 | 3.4332 | 70.7703 | 70.0928 | 115.9012 | 123.642 | 3.1311 | 123.6282 | 86.293 | -0.28839 | 123.642 | 3.1311 | 86.293 | 115.9012 | 123.6282 | -123.8983 | -123.8846
5343.7188 | 123.6969 | -61.4273 | 62.1323 | -0.22255 | 0.014529 | 0.0082864 | 0.010611 | 0.060034 | -0.0033239 | 0.078622 | -58.3008 | 62.1185 | -61.7661 | -61.5967 | 54.5242 | 25.0168 | 9.3109 | 8.7341 | 62.1735 | -61.7249 | -0.33875 | -0.013733 | 3.1265 | -0.16937 | -7.608 | -0.29755 | 0.041199 | 3.4653 | 70.7382 | 70.1614 | 115.9515 | 123.5458 | 3.1265 | 123.6008 | 86.4441 | -0.29755 | 123.5458 | 3.1265 | 86.4441 | 115.9515 | 123.6008 | -123.8983 | -123.8571
5344.7188 | 123.7701 | -61.4136 | 62.1552 | -0.20729 | 0.012392 | 0.011704 | 0.011465 | 0.058966 | 0.00073487 | 0.078195 | -58.3557 | 62.146 | -61.7569 | -61.6379 | 54.5059 | 24.9939 | 9.3613 | 8.7433 | 62.1689 | -61.7706 | -0.34332 | -0.009155 | 3.0579 | -0.2243 | -7.6492 | -0.35706 | 0.013733 | 3.4012 | 70.7748 | 70.1569 | 115.9195 | 123.5596 | 3.0579 | 123.5825 | 86.4075 | -0.35706 | 123.5596 | 3.0579 | 86.4075 | 115.9195 | 123.5825 | -123.912 | -123.9258
5345.7188 | 123.7061 | -61.4319 | 62.146 | -0.22255 | 0.015383 | 0.011491 | 0.014883 | 0.060675 | -0.0011877 | 0.078408 | -58.3649 | 62.1323 | -61.7569 | -61.6562 | 54.5334 | 25.0717 | 9.3704 | 8.757 | 62.1689 | -61.7294 | -0.32501 | -0.013733 | 3.067 | -0.2243 | -7.6126 | -0.29755 | 0.022888 | 3.392 | 70.8023 | 70.1889 | 115.9653 | 123.5641 | 3.067 | 123.6008 | 86.5036 | -0.29755 | 123.5641 | 3.067 | 86.5036 | 115.9653 | 123.6008 | -123.9029 | -123.8754
5346.7188 | 123.6877 | -61.4365 | 62.1597 | -0.27596 | 0.013674 | 0.0099954 | 0.011679 | 0.05918 | -0.0031103 | 0.079476 | -58.3603 | 62.1277 | -61.7798 | -61.6516 | 54.5334 | 25.09 | 9.3155 | 8.7067 | 62.1552 | -61.7111 | -0.34332 | -0.032043 | 3.0762 | -0.21515 | -7.6263 | -0.27466 | -0.004578 | 3.4195 | 70.752 | 70.1431 | 115.9698 | 123.5641 | 3.0762 | 123.5916 | 86.5265 | -0.27466 | 123.5641 | 3.0762 | 86.5265 | 115.9698 | 123.5916 | -123.9395 | -123.8708
5347.7188 | 123.7015 | -61.4594 | 62.1185 | 1.5093 | 0.017733 | 0.011918 | 0.017019 | 0.063452 | -0.00076053 | 0.077126 | -58.2687 | 62.1552 | -61.7523 | -61.6791 | 54.4739 | 24.9893 | 9.1965 | 8.6105 | 62.1323 | -61.7615 | -0.29297 | 0.036621 | 3.1906 | -0.21973 | -7.6447 | -0.30212 | 0.013733 | 3.4836 | 70.6558 | 70.0699 | 115.9332 | 123.6145 | 3.1906 | 123.5916 | 86.4487 | -0.30212 | 123.6145 | 3.1906 | 86.4487 | 115.9332 | 123.5916 | -123.8708 | -123.88
5348.7188 | 123.6877 | -61.4365 | 62.146 | -0.27596 | 0.01581 | 0.01085 | 0.01232 | 0.060462 | -0.0014013 | 0.075631 | -58.3603 | 62.1506 | -61.7569 | -61.6516 | 54.5288 | 24.8886 | 9.2789 | 8.6975 | 62.178 | -61.7615 | -0.32044 | 0.004578 | 3.0762 | -0.21515 | -7.6172 | -0.32501 | 0.032044 | 3.3966 | 70.7153 | 70.134 | 115.9653 | 123.587 | 3.0762 | 123.6145 | 86.3251 | -0.32501 | 123.587 | 3.0762 | 86.3251 | 115.9653 | 123.6145 | -123.9029 | -123.9075
5349.7188 | 123.7152 | -61.4273 | 62.1414 | -0.2607 | 0.01282 | 0.011064 | 0.0089016 | 0.05918 | -0.0041785 | 0.079263 | -58.3145 | 62.1323 | -61.7203 | -61.6058 | 54.5517 | 24.9573 | 9.2422 | 8.7479 | 62.1506 | -61.7157 | -0.29297 | -0.009155 | 3.1128 | -0.17853 | -7.5897 | -0.28839 | 0.009156 | 3.4058 | 70.6696 | 70.1752 | 115.979 | 123.5596 | 3.1128 | 123.5779 | 86.3846 | -0.28839 | 123.5596 | 3.1128 | 86.3846 | 115.979 | 123.5779 | -123.8617 | -123.8571
5350.7188 | 123.7473 | -61.4136 | 62.1506 | -0.25307 | 0.014315 | 0.0089274 | 0.010397 | 0.060462 | -0.00011953 | 0.078195 | -58.287 | 62.1002 | -61.7249 | -61.5875 | 54.5792 | 24.939 | 9.1873 | 8.7662 | 62.1643 | -61.7157 | -0.31128 | -0.050354 | 3.1265 | -0.17395 | -7.5714 | -0.30212 | 0.013733 | 3.4378 | 70.6009 | 70.1797 | 115.9927 | 123.5138 | 3.1265 | 123.5779 | 86.3525 | -0.30212 | 123.5138 | 3.1265 | 86.3525 | 115.9927 | 123.5779 | -123.8754 | -123.8663
5351.7188 | 123.6786 | -61.4502 | 62.1552 | -0.19966 | 0.013674 | 0.0089274 | 0.011892 | 0.057898 | -0.0011877 | 0.078195 | -58.3511 | 62.1185 | -61.7523 | -61.6379 | 54.5151 | 24.8199 | 9.2789 | 8.7479 | 62.1689 | -61.7386 | -0.30212 | -0.036621 | 3.0991 | -0.18768 | -7.6401 | -0.28839 | 0.013733 | 3.4012 | 70.7291 | 70.1981 | 115.9653 | 123.5687 | 3.0991 | 123.6191 | 86.2701 | -0.28839 | 123.5687 | 3.0991 | 86.2701 | 115.9653 | 123.6191 | -123.9075 | -123.8937
5352.7344 | 123.6832 | -61.4319 | 62.1277 | 0.013962 | 0.014956 | 0.013413 | 0.01531 | 0.061103 | -0.00011953 | 0.077126 | -58.3328 | 62.1323 | -61.7661 | -61.6608 | 54.4739 | 24.8016 | 9.1736 | 8.6792 | 62.1368 | -61.7752 | -0.33417 | 0.004577 | 3.0991 | -0.22888 | -7.6538 | -0.34332 | 0.009155 | 3.4332 | 70.6055 | 70.1111 | 115.9058 | 123.5641 | 3.0991 | 123.5687 | 86.2335 | -0.34332 | 123.5641 | 3.0991 | 86.2335 | 115.9058 | 123.5687 | -123.8937 | -123.9029
5353.7188 | 123.7198 | -61.4365 | 62.1506 | -0.24544 | 0.013674 | 0.011491 | 0.010824 | 0.060034 | -0.0011877 | 0.077126 | -58.3191 | 62.1231 | -61.7523 | -61.615 | 54.5425 | 24.9481 | 9.2697 | 8.7387 | 62.1735 | -61.734 | -0.31586 | -0.027466 | 3.1174 | -0.17853 | -7.608 | -0.29755 | 0.022888 | 3.4332 | 70.7062 | 70.1752 | 115.979 | 123.5596 | 3.1174 | 123.6099 | 86.3846 | -0.29755 | 123.5596 | 3.1174 | 86.3846 | 115.979 | 123.6099 | -123.9029 | -123.8846
5354.7188 | 123.7061 | -61.4136 | 62.1323 | -0.30647 | 0.013674 | 0.0080728 | 0.011679 | 0.061103 | -0.0035375 | 0.078195 | -58.3145 | 62.0911 | -61.7477 | -61.6104 | 54.5425 | 24.9893 | 9.169 | 8.7753 | 62.1643 | -61.7111 | -0.33417 | -0.041199 | 3.0991 | -0.19684 | -7.5897 | -0.29755 | 0.032044 | 3.4332 | 70.5826 | 70.1889 | 115.9561 | 123.5046 | 3.0991 | 123.5779 | 86.4029 | -0.29755 | 123.5046 | 3.0991 | 86.4029 | 115.9561 | 123.5779 | -123.88 | -123.8434
5355.7188 | 123.7106 | -61.4456 | 62.146 | -0.26833 | 0.013888 | 0.0046548 | 0.013174 | 0.057685 | -0.0028967 | 0.075845 | -58.3649 | 62.1323 | -61.7615 | -61.6379 | 54.5059 | 24.9847 | 9.2422 | 8.7479 | 62.1597 | -61.7111 | -0.31586 | -0.013733 | 3.0808 | -0.19226 | -7.6401 | -0.2655 | 0.013733 | 3.3966 | 70.6879 | 70.1935 | 115.9515 | 123.5779 | 3.0808 | 123.6053 | 86.4304 | -0.2655 | 123.5779 | 3.0808 | 86.4304 | 115.9515 | 123.6053 | -123.9075 | -123.8571
5356.7188 | 123.7976 | -61.4136 | 62.1368 | -0.23018 | 0.014956 | 0.012132 | 0.0097562 | 0.060889 | -0.0035375 | 0.076699 | -58.3054 | 62.0956 | -61.7386 | -61.5646 | 54.5883 | 25.058 | 9.1599 | 8.844 | 62.1368 | -61.702 | -0.32501 | -0.041199 | 3.1082 | -0.15106 | -7.5485 | -0.28839 | 0 | 3.4332 | 70.5734 | 70.2576 | 116.0019 | 123.5092 | 3.1082 | 123.5504 | 86.4716 | -0.28839 | 123.5092 | 3.1082 | 86.4716 | 116.0019 | 123.5504 | -123.8754 | -123.8388
5357.7188 | 123.7244 | -61.441 | 62.1323 | -0.10048 | 0.017519 | 0.013841 | 0.01766 | 0.061316 | -0.00076053 | 0.07969 | -58.255 | 62.178 | -61.7477 | -61.5967 | 54.5151 | 24.971 | 9.1553 | 8.7662 | 62.1368 | -61.7615 | -0.3067 | 0.045777 | 3.186 | -0.15564 | -7.6172 | -0.32043 | 0.004578 | 3.4927 | 70.5963 | 70.2072 | 115.9561 | 123.6191 | 3.186 | 123.5779 | 86.412 | -0.32043 | 123.6191 | 3.186 | 86.412 | 115.9561 | 123.5779 | -123.88 | -123.8937
5358.7188 | 123.7564 | -61.4319 | 62.146 | -0.23018 | 0.013888 | 0.014482 | 0.0095424 | 0.058966 | -0.0020421 | 0.077126 | -58.3237 | 62.1231 | -61.7432 | -61.6058 | 54.538 | 24.9893 | 9.1919 | 8.7067 | 62.1368 | -61.7157 | -0.31128 | -0.022888 | 3.1082 | -0.17395 | -7.608 | -0.28381 | -0.009155 | 3.4195 | 70.6238 | 70.1385 | 115.9698 | 123.555 | 3.1082 | 123.5687 | 86.4212 | -0.28381 | 123.555 | 3.1082 | 86.4212 | 115.9698 | 123.5687 | -123.8892 | -123.8617
5359.7188 | 123.7335 | -61.4456 | 62.1277 | -0.23018 | 0.011538 | 0.011277 | 0.010824 | 0.060034 | 9.4068e-05 | 0.078622 | -58.3145 | 62.1002 | -61.7386 | -61.5967 | 54.5517 | 24.9802 | 9.1095 | 8.7158 | 62.1506 | -61.6974 | -0.29297 | -0.027466 | 3.1311 | -0.15106 | -7.576 | -0.25177 | 0.022888 | 3.4241 | 70.5551 | 70.1614 | 115.9973 | 123.5458 | 3.1311 | 123.5962 | 86.4258 | -0.25177 | 123.5458 | 3.1311 | 86.4258 | 115.9973 | 123.5962 | -123.8663 | -123.8251
5360.7188 | 123.761 | -61.4044 | 62.1368 | -0.26833 | 0.014742 | 0.0085 | 0.013388 | 0.059821 | -0.0018285 | 0.07734 | -58.2916 | 62.0728 | -61.7432 | -61.5646 | 54.5883 | 25.09 | 9.1003 | 8.7753 | 62.1414 | -61.7065 | -0.33875 | -0.064087 | 3.1128 | -0.16022 | -7.5485 | -0.30212 | 0.004577 | 3.4515 | 70.5048 | 70.1797 | 115.9927 | 123.4772 | 3.1128 | 123.5458 | 86.4944 | -0.30212 | 123.4772 | 3.1128 | 86.4944 | 115.9927 | 123.5458 | -123.88 | -123.8434
5361.7188 | 123.7473 | -61.441 | 62.1735 | -0.21492 | 0.01346 | 0.011491 | 0.01232 | 0.060248 | -0.0033239 | 0.077126 | -58.3557 | 62.114 | -61.7523 | -61.6196 | 54.5013 | 25.1404 | 9.1736 | 8.6975 | 62.146 | -61.7386 | -0.31128 | -0.059509 | 3.0853 | -0.17853 | -7.6721 | -0.29755 | -0.027466 | 3.3966 | 70.6146 | 70.1385 | 115.9424 | 123.555 | 3.0853 | 123.587 | 86.5814 | -0.29755 | 123.555 | 3.0853 | 86.5814 | 115.9424 | 123.587 | -123.9258 | -123.912
5362.7344 | 123.7152 | -61.4502 | 62.146 | 0.04448 | 0.019015 | 0.016404 | 0.018301 | 0.060462 | 0.00030767 | 0.079263 | -58.3145 | 62.1552 | -61.7706 | -61.6287 | 54.4968 | 24.9664 | 9.1232 | 8.6288 | 62.1277 | -61.7798 | -0.32043 | 0.009155 | 3.1357 | -0.17853 | -7.6492 | -0.32959 | -0.01831 | 3.4561 | 70.5734 | 70.079 | 115.947 | 123.6053 | 3.1357 | 123.5779 | 86.4166 | -0.32959 | 123.6053 | 3.1357 | 86.4166 | 115.947 | 123.5779 | -123.9166 | -123.9258
5363.7188 | 123.7885 | -61.3998 | 62.114 | -0.131 | 0.012606 | 0.010209 | 0.0091152 | 0.060248 | -0.0031103 | 0.075845 | -58.2779 | 62.0636 | -61.7249 | -61.5509 | 54.5883 | 25.1678 | 9.05 | 8.7616 | 62.1094 | -61.6745 | -0.32501 | -0.050354 | 3.1219 | -0.15106 | -7.5256 | -0.27466 | -0.004578 | 3.447 | 70.4498 | 70.1614 | 115.9882 | 123.4634 | 3.1219 | 123.5092 | 86.5677 | -0.27466 | 123.4634 | 3.1219 | 86.5677 | 115.9882 | 123.5092 | -123.8388 | -123.7885
5364.7188 | 123.8297 | -61.4227 | 62.1231 | -0.42091 | 0.013888 | 0.012773 | 0.010824 | 0.056617 | -0.0022559 | 0.076699 | -58.2825 | 62.0819 | -61.7249 | -61.5189 | 54.6112 | 25.1633 | 9.0546 | 8.7753 | 62.0865 | -61.6928 | -0.30213 | -0.041199 | 3.1403 | -0.096131 | -7.5119 | -0.27008 | -0.036621 | 3.4424 | 70.4773 | 70.1981 | 116.0339 | 123.5046 | 3.1403 | 123.5092 | 86.586 | -0.27008 | 123.5046 | 3.1403 | 86.586 | 116.0339 | 123.5092 | -123.848 | -123.8159
5365.7188 | 123.7564 | -61.4136 | 62.1323 | -0.23781 | 0.012606 | 0.0132 | 0.010824 | 0.058753 | -0.0018285 | 0.076913 | -58.3054 | 62.0819 | -61.7111 | -61.5646 | 54.5654 | 25.1678 | 9.0912 | 8.7158 | 62.1368 | -61.7203 | -0.29755 | -0.050354 | 3.1082 | -0.15106 | -7.5668 | -0.3067 | 0.004578 | 3.4058 | 70.5048 | 70.1294 | 115.979 | 123.4955 | 3.1082 | 123.5504 | 86.5814 | -0.3067 | 123.4955 | 3.1082 | 86.5814 | 115.979 | 123.5504 | -123.8434 | -123.8525
5366.7188 | 123.8022 | -61.3953 | 62.1231 | -0.15388 | 0.01282 | 0.010209 | 0.011465 | 0.059821 | -0.0037511 | 0.078835 | -58.287 | 62.0773 | -61.7294 | -61.5601 | 54.6204 | 25.2457 | 9.0866 | 8.7891 | 62.1368 | -61.6974 | -0.33417 | -0.045776 | 3.1082 | -0.1648 | -7.5027 | -0.30212 | 0.013733 | 3.4424 | 70.4819 | 70.1843 | 116.0156 | 123.4726 | 3.1082 | 123.5321 | 86.6409 | -0.30212 | 123.4726 | 3.1082 | 86.6409 | 116.0156 | 123.5321 | -123.8525 | -123.8205
5367.7188 | 123.7427 | -61.4319 | 62.1414 | -0.22255 | 0.01282 | 0.0097818 | 0.013388 | 0.060034 | -0.0018285 | 0.078835 | -58.3191 | 62.114 | -61.7249 | -61.615 | 54.5563 | 25.0992 | 9.1644 | 8.7158 | 62.146 | -61.7157 | -0.29297 | -0.027465 | 3.1128 | -0.1831 | -7.5851 | -0.28381 | 0.004578 | 3.4058 | 70.5963 | 70.1477 | 115.9882 | 123.5458 | 3.1128 | 123.5779 | 86.5311 | -0.28381 | 123.5458 | 3.1128 | 86.5311 | 115.9882 | 123.5779 | -123.8663 | -123.8571
5368.7344 | 123.6877 | -61.4777 | 62.1277 | 0.14366 | 0.017306 | 0.02089 | 0.017233 | 0.059607 | -0.0011877 | 0.079476 | -58.6121 | 62.0865 | -61.7889 | -61.6882 | 54.4876 | 25.09 | 9.1187 | 8.5922 | 62.1414 | -61.7523 | -0.31128 | -0.041199 | 2.8656 | -0.21057 | -7.6401 | -0.27466 | 0.013732 | 3.1769 | 70.5963 | 70.0699 | 115.9653 | 123.5641 | 2.8656 | 123.6191 | 86.5677 | -0.27466 | 123.5641 | 2.8656 | 86.5677 | 115.9653 | 123.6191 | -123.9166 | -123.88
5369.7188 | 123.761 | -61.409 | 62.1368 | -0.23018 | 0.011965 | 0.01085 | 0.011038 | 0.059607 | -0.0014013 | 0.07734 | -58.2962 | 62.0956 | -61.734 | -61.5601 | 54.5837 | 25.1495 | 9.137 | 8.7753 | 62.1231 | -61.7065 | -0.32501 | -0.041199 | 3.1128 | -0.15106 | -7.5531 | -0.29755 | -0.013733 | 3.4378 | 70.546 | 70.1843 | 115.9927 | 123.5046 | 3.1128 | 123.5321 | 86.5585 | -0.29755 | 123.5046 | 3.1128 | 86.5585 | 115.9927 | 123.5321 | -123.8708 | -123.8434
5370.7188 | 123.8434 | -61.409 | 62.1368 | -0.14626 | 0.011751 | 0.0099954 | 0.014456 | 0.062171 | -0.0039649 | 0.07734 | -58.3008 | 62.059 | -61.7523 | -61.5509 | 54.4693 | 25.2136 | 9.1278 | 8.7753 | 62.0819 | -61.6974 | -0.34332 | -0.07782 | 3.1082 | -0.14191 | -7.6675 | -0.28839 | -0.054932 | 3.4515 | 70.5368 | 70.1843 | 115.8783 | 123.468 | 3.1082 | 123.4909 | 86.6226 | -0.28839 | 123.468 | 3.1082 | 86.6226 | 115.8783 | 123.4909 | -123.8892 | -123.8342
5371.7188 | 123.7747 | -61.4044 | 62.146 | -0.131 | 0.014101 | 0.010423 | 0.013388 | 0.057257 | -0.0026831 | 0.075845 | -58.2962 | 62.0865 | -61.7386 | -61.5463 | 54.6158 | 25.2731 | 9.1278 | 8.8165 | 62.1048 | -61.7065 | -0.33417 | -0.059509 | 3.1082 | -0.14191 | -7.5302 | -0.30212 | -0.041199 | 3.4424 | 70.5322 | 70.2209 | 116.0202 | 123.4909 | 3.1082 | 123.5092 | 86.6776 | -0.30212 | 123.4909 | 3.1082 | 86.6776 | 116.0202 | 123.5092 | -123.8846 | -123.8525
5372.7188 | 123.7198 | -61.4456 | 62.1643 | -0.28358 | 0.015169 | 0.0093546 | 0.013388 | 0.057471 | -0.0016149 | 0.078195 | -58.3237 | 62.1002 | -61.7569 | -61.5921 | 54.5334 | 25.0854 | 9.1827 | 8.725 | 62.1323 | -61.702 | -0.31128 | -0.064087 | 3.1219 | -0.14648 | -7.6309 | -0.25635 | -0.032044 | 3.4332 | 70.6284 | 70.1706 | 115.979 | 123.5458 | 3.1219 | 123.5779 | 86.5311 | -0.25635 | 123.5458 | 3.1219 | 86.5311 | 115.979 | 123.5779 | -123.9212 | -123.8663
5373.7344 | 123.7198 | -61.4273 | 62.1185 | -0.077591 | 0.01581 | 0.011704 | 0.020651 | 0.060889 | -0.0014013 | 0.076272 | -58.3099 | 62.146 | -61.7432 | -61.6196 | 54.4693 | 25.0488 | 9.1232 | 8.6655 | 62.0956 | -61.7752 | -0.31586 | 0.027466 | 3.1174 | -0.19226 | -7.6492 | -0.3479 | -0.022888 | 3.4332 | 70.5505 | 70.0928 | 115.8966 | 123.5733 | 3.1174 | 123.5229 | 86.4761 | -0.3479 | 123.5733 | 3.1174 | 86.4761 | 115.8966 | 123.5229 | -123.8617 | -123.8937
5374.7188 | 123.8159 | -61.3998 | 62.1323 | 0.38017 | 0.016238 | 0.0132 | 0.0089016 | 0.059607 | -0.0022559 | 0.077126 | -58.2779 | 62.0499 | -61.7615 | -61.528 | 54.5288 | 25.177 | 9.0454 | 8.7982 | 62.1414 | -61.6837 | -0.36163 | -0.082397 | 3.1219 | -0.12817 | -7.6035 | -0.28381 | 0.009155 | 3.4836 | 70.4453 | 70.1981 | 115.9287 | 123.4497 | 3.1219 | 123.5413 | 86.5768 | -0.28381 | 123.4497 | 3.1219 | 86.5768 | 115.9287 | 123.5413 | -123.8937 | -123.8159
5375.7188 | 123.7885 | -61.3815 | 62.1368 | -0.24544 | 0.012392 | 0.0097818 | 0.0093288 | 0.057685 | -0.0031103 | 0.077981 | -58.287 | 62.059 | -61.7386 | -61.5509 | 54.5471 | 25.2502 | 9.1003 | 8.7662 | 62.146 | -61.6745 | -0.35705 | -0.07782 | 3.0945 | -0.16937 | -7.5897 | -0.29297 | 0.009155 | 3.4515 | 70.4819 | 70.1477 | 115.9287 | 123.4406 | 3.0945 | 123.5275 | 86.6318 | -0.29297 | 123.4406 | 3.0945 | 86.6318 | 115.9287 | 123.5275 | -123.8754 | -123.8113
5376.7188 | 123.7976 | -61.4044 | 62.1323 | -0.19966 | 0.012392 | 0.0065774 | 0.010611 | 0.057898 | -0.0026831 | 0.078835 | -58.2962 | 62.0819 | -61.7294 | -61.5463 | 54.4876 | 25.1953 | 9.082 | 8.7479 | 62.1094 | -61.7065 | -0.32501 | -0.050354 | 3.1082 | -0.14191 | -7.6447 | -0.30212 | -0.022888 | 3.4332 | 70.4864 | 70.1523 | 115.892 | 123.4863 | 3.1082 | 123.5138 | 86.5997 | -0.30212 | 123.4863 | 3.1082 | 86.5997 | 115.892 | 123.5138 | -123.8617 | -123.8388
5377.7188 | 123.7564 | -61.4273 | 62.1597 | -0.21492 | 0.016024 | 0.017045 | 0.016592 | 0.059394 | -0.00054693 | 0.078195 | -58.3282 | 62.1597 | -61.7661 | -61.6058 | 54.4556 | 25.1495 | 9.1782 | 8.6563 | 62.1506 | -61.7477 | -0.33875 | 0 | 3.0991 | -0.17853 | -7.7042 | -0.32044 | -0.009155 | 3.4378 | 70.6055 | 70.0836 | 115.8829 | 123.587 | 3.0991 | 123.5779 | 86.5768 | -0.32044 | 123.587 | 3.0991 | 86.5768 | 115.8829 | 123.5779 | -123.9258 | -123.9075
5378.7344 | 123.7564 | -61.441 | 62.0361 | 0.2047 | 0.01346 | 0.014695 | 0.014883 | 0.060675 | -0.0035375 | 0.080331 | -58.2962 | 62.0361 | -61.7752 | -61.5738 | 54.4785 | 25.3006 | 8.9493 | 8.6884 | 62.0819 | -61.7065 | -0.33417 | 0 | 3.1448 | -0.13275 | -7.5577 | -0.2655 | 0.045776 | 3.479 | 70.3903 | 70.1294 | 115.9195 | 123.4772 | 3.1448 | 123.5229 | 86.7416 | -0.2655 | 123.4772 | 3.1448 | 86.7416 | 115.9195 | 123.5229 | -123.8113 | -123.7427
5379.7188 | 123.8205 | -61.3907 | 62.1094 | -0.24544 | 0.014956 | 0.011064 | 0.0093288 | 0.060462 | -0.0018285 | 0.075204 | -58.2733 | 62.0544 | -61.7065 | -61.5463 | 54.538 | 25.2686 | 9.0042 | 8.7387 | 62.1002 | -61.7157 | -0.31586 | -0.054932 | 3.1174 | -0.15564 | -7.5714 | -0.32501 | -0.009155 | 3.4332 | 70.3949 | 70.1294 | 115.9287 | 123.4451 | 3.1174 | 123.4909 | 86.6592 | -0.32501 | 123.4451 | 3.1174 | 86.6592 | 115.9287 | 123.4909 | -123.8159 | -123.8251
5380.7188 | 123.8113 | -61.4227 | 62.1002 | -0.24544 | 0.013888 | 0.015122 | 0.0099698 | 0.058325 | 9.4068e-05 | 0.077767 | -58.2962 | 62.0544 | -61.7432 | -61.5509 | 54.5197 | 25.264 | 9.0317 | 8.7524 | 62.1048 | -61.6928 | -0.32044 | -0.045777 | 3.1265 | -0.12817 | -7.5806 | -0.27008 | 0.004577 | 3.447 | 70.4544 | 70.1752 | 115.9424 | 123.4772 | 3.1265 | 123.5275 | 86.6867 | -0.27008 | 123.4772 | 3.1265 | 86.6867 | 115.9424 | 123.5275 | -123.8434 | -123.793
5381.7188 | 123.8022 | -61.4044 | 62.0956 | -0.61928 | 0.01346 | 0.0063638 | 0.01296 | 0.058325 | -0.0026831 | 0.077554 | -58.3099 | 62.0499 | -61.734 | -61.5234 | 54.5151 | 25.2411 | 9.0317 | 8.7387 | 62.0956 | -61.702 | -0.32959 | -0.045776 | 3.0945 | -0.11902 | -7.5806 | -0.29755 | 0 | 3.4241 | 70.4361 | 70.1431 | 115.9195 | 123.4543 | 3.0945 | 123.5001 | 86.6455 | -0.29755 | 123.4543 | 3.0945 | 86.6455 | 115.9195 | 123.5001 | -123.8297 | -123.7976
5382.7344 | 123.7381 | -61.4365 | 62.1368 | -0.077591 | 0.014529 | 0.012773 | 0.018728 | 0.05918 | -0.0018285 | 0.077981 | -58.2825 | 62.1552 | -61.7386 | -61.6104 | 54.4006 | 25.1175 | 9.169 | 8.6243 | 62.1231 | -61.7661 | -0.30212 | 0.01831 | 3.154 | -0.17395 | -7.7362 | -0.32959 | -0.013733 | 3.4561 | 70.6055 | 70.0607 | 115.8371 | 123.5916 | 3.154 | 123.5596 | 86.554 | -0.32959 | 123.5916 | 3.154 | 86.554 | 115.8371 | 123.5596 | -123.8754 | -123.9029
5383.7344 | 123.8251 | -61.4639 | 62.1323 | 0.13603 | 0.016024 | 0.011277 | 0.01531 | 0.061316 | -0.0035375 | 0.076913 | -58.3923 | 62.1094 | -61.7935 | -61.6745 | 54.3411 | 25.0214 | 9.137 | 8.1848 | 62.1094 | -61.7615 | -0.32959 | -0.022888 | 3.0716 | -0.21057 | -7.7911 | -0.29755 | -0.022888 | 3.4012 | 70.6009 | 69.6487 | 115.8051 | 123.5733 | 3.0716 | 123.5733 | 86.4853 | -0.29755 | 123.5733 | 3.0716 | 86.4853 | 115.8051 | 123.5733 | -123.9258 | -123.8937
5384.7188 | 123.8297 | -61.3861 | 62.0865 | -0.23781 | 0.011965 | 0.013413 | 0.0082608 | 0.053412 | -0.0043921 | 0.080331 | -58.2825 | 62.0773 | -61.734 | -61.7523 | 54.2084 | 25.2228 | 8.9951 | 8.6288 | 62.0911 | -61.6928 | -0.3479 | -0.009155 | 3.1036 | -0.36621 | -7.8781 | -0.3067 | 0.004577 | 3.4515 | 70.3812 | 70.015 | 115.5945 | 123.4634 | 3.1036 | 123.4772 | 86.6089 | -0.3067 | 123.4634 | 3.1036 | 86.6089 | 115.5945 | 123.4772 | -123.8205 | -123.7793
5385.7188 | 123.7976 | -61.409 | 62.1094 | -0.23018 | 0.013674 | 0.0087138 | 0.0091152 | 0.058753 | -0.0031103 | 0.079476 | -58.287 | 62.1002 | -61.7111 | -61.5601 | 54.4876 | 25.2823 | 9.0637 | 8.7524 | 62.1277 | -61.6974 | -0.30212 | -0.009155 | 3.1219 | -0.15106 | -7.6218 | -0.28839 | 0.018311 | 3.4241 | 70.4727 | 70.1614 | 115.8966 | 123.5092 | 3.1219 | 123.5367 | 86.6913 | -0.28839 | 123.5092 | 3.1219 | 86.6913 | 115.8966 | 123.5367 | -123.8205 | -123.8068
5386.7188 | 123.7885 | -61.3907 | 62.1231 | -0.21492 | 0.013247 | 0.0072184 | 0.010611 | 0.057471 | -0.0022559 | 0.078622 | -58.2779 | 62.0544 | -61.7249 | -61.5463 | 54.4922 | 25.1907 | 9.0637 | 8.7616 | 62.1231 | -61.6837 | -0.33417 | -0.068665 | 3.1128 | -0.15564 | -7.6309 | -0.29297 | 0 | 3.447 | 70.4544 | 70.1523 | 115.8829 | 123.4451 | 3.1128 | 123.5138 | 86.5814 | -0.29297 | 123.4451 | 3.1128 | 86.5814 | 115.8829 | 123.5138 | -123.848 | -123.8068
5387.7344 | 123.7656 | -61.4227 | 62.1231 | -0.13863 | 0.014742 | 0.013413 | 0.020865 | 0.059394 | -0.0026831 | 0.076699 | -58.3054 | 62.1689 | -61.7432 | -61.5875 | 54.4144 | 25.1587 | 9.1003 | 8.6472 | 62.1185 | -61.7432 | -0.32044 | 0.045776 | 3.1174 | -0.1648 | -7.7087 | -0.32044 | -0.004578 | 3.4378 | 70.5231 | 70.0699 | 115.8371 | 123.5916 | 3.1174 | 123.5413 | 86.5814 | -0.32044 | 123.5916 | 3.1174 | 86.5814 | 115.8371 | 123.5413 | -123.8663 | -123.8663
5388.7188 | 123.8251 | -61.3907 | 62.1094 | -0.55061 | 0.01282 | 0.01085 | 0.012533 | 0.060675 | -0.0039649 | 0.078622 | -58.3054 | 62.0453 | -61.7432 | -61.5417 | 54.5563 | 25.2365 | 9.0546 | 8.7479 | 62.0911 | -61.6699 | -0.35248 | -0.064087 | 3.0853 | -0.15106 | -7.5531 | -0.27924 | -0.018311 | 3.4378 | 70.4453 | 70.1386 | 115.947 | 123.436 | 3.0853 | 123.4818 | 86.6272 | -0.27924 | 123.436 | 3.0853 | 86.6272 | 115.947 | 123.4818 | -123.8525 | -123.7793
5389.7188 | 123.7885 | -61.409 | 62.1185 | -0.23781 | 0.016024 | 0.013627 | 0.014029 | 0.058966 | -0.0016149 | 0.076913 | -58.287 | 62.0773 | -61.7432 | -61.5601 | 54.5151 | 25.2594 | 9.1278 | 8.6884 | 62.1323 | -61.702 | -0.33417 | -0.041198 | 3.1219 | -0.15106 | -7.6035 | -0.29297 | 0.013733 | 3.4561 | 70.5368 | 70.0974 | 115.9241 | 123.4863 | 3.1219 | 123.5413 | 86.6684 | -0.29297 | 123.4863 | 3.1219 | 86.6684 | 115.9241 | 123.5413 | -123.8617 | -123.8205
5390.7188 | 123.8159 | -61.4044 | 62.0956 | -0.17677 | 0.014101 | 0.0050822 | 0.011892 | 0.058966 | -0.0014013 | 0.078835 | -58.1863 | 62.1002 | -61.6974 | -61.5829 | 54.5609 | 25.2777 | 8.9539 | 8.757 | 62.114 | -61.6837 | -0.29297 | 0.004578 | 3.2181 | -0.17853 | -7.5348 | -0.27924 | 0.018311 | 3.511 | 70.3583 | 70.1614 | 115.9653 | 123.5046 | 3.2181 | 123.5184 | 86.6821 | -0.27924 | 123.5046 | 3.2181 | 86.6821 | 115.9653 | 123.5184 | -123.793 | -123.7793
5391.7188 | 123.8342 | -61.3953 | 62.1002 | -0.22255 | 0.011538 | 0.010636 | 0.010397 | 0.06153 | -0.0088781 | 0.076699 | -58.2504 | 62.0819 | -61.7203 | -61.2579 | 54.4739 | 24.9847 | 9.1232 | 8.7616 | 62.1048 | -61.6837 | -0.32501 | -0.018311 | 3.1448 | 0.13733 | -7.6263 | -0.28839 | 0.004577 | 3.4698 | 70.5185 | 70.1569 | 115.8691 | 123.4772 | 3.1448 | 123.5001 | 86.38 | -0.28839 | 123.4772 | 3.1448 | 86.38 | 115.8691 | 123.5001 | -123.8205 | -123.7839
5392.7188 | 123.7289 | -61.4456 | 62.1597 | -0.23018 | 0.016451 | 0.013413 | 0.015738 | 0.05918 | -0.0020421 | 0.07734 | -58.3008 | 62.1735 | -61.7752 | -61.6058 | 54.4601 | 25.1495 | 9.2331 | 8.6746 | 62.1231 | -61.7523 | -0.32959 | 0.013733 | 3.1448 | -0.16022 | -7.6996 | -0.3067 | -0.036621 | 3.4744 | 70.6787 | 70.1202 | 115.9058 | 123.6191 | 3.1448 | 123.5687 | 86.5952 | -0.3067 | 123.6191 | 3.1448 | 86.5952 | 115.9058 | 123.5687 | -123.9349 | -123.912
5393.7188 | 123.8022 | -61.3998 | 62.1277 | -0.29884 | 0.011751 | 0.0063638 | 0.0084744 | 0.058966 | -0.00033333 | 0.076913 | -58.2733 | 62.0682 | -61.7477 | -61.5417 | 54.538 | 25.3052 | 9.0958 | 8.812 | 62.0911 | -61.6699 | -0.3479 | -0.05951 | 3.1265 | -0.14191 | -7.5897 | -0.27008 | -0.036622 | 3.4744 | 70.4956 | 70.2118 | 115.9378 | 123.468 | 3.1265 | 123.4909 | 86.705 | -0.27008 | 123.468 | 3.1265 | 86.705 | 115.9378 | 123.4909 | -123.8754 | -123.7976
5394.7188 | 123.8068 | -61.4182 | 62.1048 | 0.54802 | 0.01346 | 0.0093546 | 0.0097562 | 0.058966 | -0.0022559 | 0.076486 | -58.2779 | 62.0224 | -61.734 | -61.5463 | 54.5563 | 25.2228 | 9.1415 | 8.844 | 62.1094 | -61.6745 | -0.31586 | -0.082397 | 3.1403 | -0.12817 | -7.5485 | -0.25635 | 0.004578 | 3.4561 | 70.5597 | 70.2621 | 115.9744 | 123.4406 | 3.1403 | 123.5275 | 86.6409 | -0.25635 | 123.4406 | 3.1403 | 86.6409 | 115.9744 | 123.5275 | -123.8388 | -123.7793
5395.7188 | 123.8205 | -61.3861 | 62.1185 | -0.23018 | 0.014101 | 0.012345 | 0.011465 | 0.060034 | -0.0016149 | 0.076913 | -58.1223 | 62.0911 | -61.7065 | -61.5784 | 54.5929 | 25.264 | 9.0775 | 8.8165 | 62.1185 | -61.6745 | -0.32044 | -0.027466 | 3.2639 | -0.19226 | -7.5256 | -0.28839 | 0 | 3.5843 | 70.4636 | 70.2026 | 115.979 | 123.4772 | 3.2639 | 123.5046 | 86.6501 | -0.28839 | 123.4772 | 3.2639 | 86.6501 | 115.979 | 123.5046 | -123.8251 | -123.793
5396.7188 | 123.7839 | -61.3907 | 62.114 | -0.12337 | 0.011751 | 0.007432 | 0.011251 | 0.058112 | -0.0026831 | 0.079904 | -58.2916 | 62.0728 | -61.7249 | -61.5372 | 54.5242 | 25.3372 | 9.2331 | 8.8531 | 62.0911 | -61.6928 | -0.33417 | -0.041199 | 3.0991 | -0.14648 | -7.5897 | -0.30212 | -0.022889 | 3.4332 | 70.6238 | 70.2438 | 115.9149 | 123.4634 | 3.0991 | 123.4818 | 86.7279 | -0.30212 | 123.4634 | 3.0991 | 86.7279 | 115.9149 | 123.4818 | -123.8388 | -123.8068
5397.7188 | 123.7473 | -61.4502 | 62.1368 | -0.23018 | 0.01581 | 0.0089274 | 0.017233 | 0.058325 | -0.0028967 | 0.07734 | -58.3328 | 62.1552 | -61.7569 | -61.6058 | 54.4647 | 25.1678 | 9.256 | 8.7021 | 62.1368 | -61.7432 | -0.3067 | 0.01831 | 3.1174 | -0.15564 | -7.6721 | -0.29297 | 0 | 3.4241 | 70.7062 | 70.1523 | 115.9149 | 123.6053 | 3.1174 | 123.587 | 86.618 | -0.29297 | 123.6053 | 3.1174 | 86.618 | 115.9149 | 123.587 | -123.8937 | -123.88
5398.7188 | 123.8388 | -61.3998 | 62.1002 | -0.08522 | 0.011751 | 0.0072184 | 0.0095424 | 0.059394 | -0.0043921 | 0.076913 | -58.2779 | 62.0224 | -61.7477 | -61.496 | 54.5746 | 25.2594 | 9.1049 | 8.844 | 62.1094 | -61.6653 | -0.3479 | -0.07782 | 3.1219 | -0.096131 | -7.5256 | -0.2655 | 0.009155 | 3.4698 | 70.5048 | 70.2438 | 115.9744 | 123.4222 | 3.1219 | 123.5092 | 86.6592 | -0.2655 | 123.4222 | 3.1219 | 86.6592 | 115.9744 | 123.5092 | -123.848 | -123.7656
5399.7188 | 123.8068 | -61.4044 | 62.1048 | -0.42091 | 0.015169 | 0.013413 | 0.011251 | 0.060034 | -0.0048193 | 0.079049 | -58.5342 | 62.0636 | -61.7294 | -61.5784 | 54.5563 | 25.3647 | 9.1232 | 8.8303 | 62.1323 | -61.6745 | -0.32501 | -0.041198 | 2.8702 | -0.17395 | -7.5485 | -0.27008 | 0.027466 | 3.1952 | 70.5276 | 70.2347 | 115.9607 | 123.468 | 2.8702 | 123.5367 | 86.7691 | -0.27008 | 123.468 | 2.8702 | 86.7691 | 115.9607 | 123.5367 | -123.8342 | -123.7793
5400.7188 | 123.8709 | -61.3815 | 62.1094 | 0.067368 | 0.011751 | 0.0087138 | 0.012106 | 0.058539 | -0.0058875 | 0.077126 | -58.2275 | 62.0636 | -61.7432 | -61.5234 | 54.5837 | 25.383 | 9.1003 | 8.8898 | 62.0773 | -61.6974 | -0.36163 | -0.045776 | 3.154 | -0.14191 | -7.5256 | -0.31586 | -0.032043 | 3.5156 | 70.4819 | 70.2713 | 115.9653 | 123.4451 | 3.154 | 123.4589 | 86.7645 | -0.31586 | 123.4451 | 3.154 | 86.7645 | 115.9653 | 123.4589 | -123.8525 | -123.8068
5401.7188 | 123.8434 | -61.3861 | 62.114 | -0.17677 | 0.01346 | 0.010209 | 0.011038 | 0.058539 | -0.0026831 | 0.076486 | -58.2733 | 62.0407 | -61.7157 | -61.5143 | 54.6021 | 25.4334 | 9.1187 | 8.8943 | 62.0773 | -61.6653 | -0.32959 | -0.073243 | 3.1128 | -0.12817 | -7.5119 | -0.27924 | -0.036621 | 3.4424 | 70.5048 | 70.2805 | 115.9882 | 123.4268 | 3.1128 | 123.4634 | 86.8195 | -0.27924 | 123.4268 | 3.1128 | 86.8195 | 115.9882 | 123.4634 | -123.8297 | -123.7793
5402.7344 | 123.7473 | -61.4456 | 62.1277 | -0.054703 | 0.016878 | 0.0132 | 0.017447 | 0.060248 | -0.0022559 | 0.076913 | -58.2779 | 62.1597 | -61.7477 | -61.5875 | 54.4922 | 25.3281 | 9.1553 | 8.7021 | 62.1002 | -61.7661 | -0.30212 | 0.032043 | 3.1677 | -0.14191 | -7.6355 | -0.32043 | -0.027466 | 3.4698 | 70.6009 | 70.1477 | 115.9378 | 123.6053 | 3.1677 | 123.5458 | 86.7737 | -0.32043 | 123.6053 | 3.1677 | 86.7737 | 115.9378 | 123.5458 | -123.8754 | -123.8937
5403.7188 | 123.8159 | -61.4044 | 62.1231 | -0.28358 | 0.011538 | 0.0080728 | 0.0084744 | 0.058112 | -0.0011877 | 0.079049 | -58.2779 | 62.0636 | -61.7569 | -61.5189 | 54.5975 | 25.3693 | 9.1141 | 8.8257 | 62.1048 | -61.6699 | -0.35248 | -0.059509 | 3.1265 | -0.11444 | -7.5256 | -0.2655 | -0.018311 | 3.479 | 70.5185 | 70.2301 | 116.0019 | 123.468 | 3.1265 | 123.5092 | 86.7737 | -0.2655 | 123.468 | 3.1265 | 86.7737 | 116.0019 | 123.5092 | -123.88 | -123.793
5404.7188 | 123.8205 | -61.3998 | 62.1048 | -0.131 | 0.013247 | 0.0038004 | 0.0097562 | 0.058539 | 0.00030767 | 0.078408 | -58.2825 | 62.0636 | -61.7386 | -61.5372 | 54.5929 | 25.3693 | 9.0958 | 8.8715 | 62.0956 | -61.6837 | -0.33874 | -0.041198 | 3.1174 | -0.13733 | -7.5119 | -0.28381 | -0.009155 | 3.4561 | 70.4956 | 70.2713 | 115.9927 | 123.4634 | 3.1174 | 123.4955 | 86.7691 | -0.28381 | 123.4634 | 3.1174 | 86.7691 | 115.9927 | 123.4955 | -123.8434 | -123.7885
5405.7188 | 123.8205 | -61.4136 | 62.0773 | -0.11574 | 0.010897 | 0.013841 | 0.011251 | 0.057471 | -0.00011953 | 0.078835 | -58.287 | 62.0224 | -61.7569 | -61.5417 | 54.5517 | 25.2731 | 9.0912 | 8.8623 | 62.1002 | -61.6837 | -0.34332 | -0.054932 | 3.1265 | -0.12817 | -7.5256 | -0.27008 | 0.022888 | 3.4698 | 70.5048 | 70.2759 | 115.9653 | 123.436 | 3.1265 | 123.5138 | 86.6867 | -0.27008 | 123.436 | 3.1265 | 86.6867 | 115.9653 | 123.5138 | -123.8342 | -123.761
5406.7188 | 123.8388 | -61.3998 | 62.1185 | -0.14626 | 0.01282 | 0.0078592 | 0.0084744 | 0.059821 | -0.0020421 | 0.080544 | -58.2504 | 62.0544 | -61.7477 | -61.5784 | 54.5563 | 25.351 | 9.1003 | 8.8715 | 62.059 | -61.6837 | -0.3479 | -0.064087 | 3.1494 | -0.17853 | -7.5623 | -0.28381 | -0.059509 | 3.4973 | 70.5002 | 70.2713 | 115.9561 | 123.4543 | 3.1494 | 123.4589 | 86.7508 | -0.28381 | 123.4543 | 3.1494 | 86.7508 | 115.9561 | 123.4589 | -123.8663 | -123.8022
5407.7188 | 123.8251 | -61.3907 | 62.1185 | -0.19203 | 0.012392 | 0.0076456 | 0.012747 | 0.057471 | -0.0016149 | 0.07734 | -58.2733 | 62.0499 | -61.7294 | -61.5509 | 54.4601 | 25.2869 | 9.2331 | 8.8989 | 62.0819 | -61.7065 | -0.33874 | -0.068664 | 3.1174 | -0.16022 | -7.6584 | -0.31586 | -0.036621 | 3.4561 | 70.6238 | 70.2896 | 115.8508 | 123.4406 | 3.1174 | 123.4726 | 86.6776 | -0.31586 | 123.4406 | 3.1174 | 86.6776 | 115.8508 | 123.4726 | -123.848 | -123.8251
5408.7188 | 123.8159 | -61.4182 | 62.1231 | -0.10048 | 0.012392 | 0.0097818 | 0.010183 | 0.057471 | -0.0016149 | 0.079263 | -58.2687 | 62.0407 | -61.7386 | -61.5097 | 54.5654 | 25.3922 | 9.1324 | 8.9035 | 62.0865 | -61.6745 | -0.32043 | -0.082398 | 3.1494 | -0.091553 | -7.5577 | -0.25635 | -0.036621 | 3.4698 | 70.5505 | 70.3217 | 115.9836 | 123.4589 | 3.1494 | 123.5046 | 86.8103 | -0.25635 | 123.4589 | 3.1494 | 86.8103 | 115.9836 | 123.5046 | -123.8617 | -123.7976
5409.7188 | 123.8342 | -61.3907 | 62.1094 | 0.83794 | 0.014742 | 0.0063638 | 0.0080472 | 0.057898 | 0.00030767 | 0.079049 | -58.429 | 62.0178 | -61.7477 | -61.5509 | 54.6112 | 25.3372 | 9.1049 | 8.8669 | 62.0636 | -61.6791 | -0.35706 | -0.091553 | 2.9617 | -0.16022 | -7.4982 | -0.28839 | -0.045776 | 3.3188 | 70.4956 | 70.2576 | 116.0019 | 123.4085 | 2.9617 | 123.4543 | 86.7279 | -0.28839 | 123.4085 | 2.9617 | 86.7279 | 116.0019 | 123.4543 | -123.8571 | -123.7885
5410.7188 | 123.8159 | -61.3861 | 62.1368 | -0.25307 | 0.014315 | 0.010209 | 0.011038 | 0.056403 | -0.00076053 | 0.077767 | -58.2596 | 62.0544 | -61.7294 | -61.5189 | 54.5929 | 25.3372 | 9.1553 | 8.876 | 62.0911 | -61.6974 | -0.34332 | -0.082398 | 3.1265 | -0.13275 | -7.5439 | -0.31128 | -0.045777 | 3.4698 | 70.5414 | 70.2621 | 115.979 | 123.4406 | 3.1265 | 123.4772 | 86.7233 | -0.31128 | 123.4406 | 3.1265 | 86.7233 | 115.979 | 123.4772 | -123.8663 | -123.8342
5411.7188 | 123.7015 | -61.4273 | 62.1506 | -0.29884 | 0.016024 | 0.0082864 | 0.013601 | 0.058966 | -0.0022559 | 0.078195 | -58.3237 | 62.1368 | -61.7844 | -61.5967 | 54.4647 | 25.1999 | 9.3018 | 8.7524 | 62.1597 | -61.7203 | -0.35706 | -0.013733 | 3.1036 | -0.16937 | -7.6859 | -0.29297 | 0.009155 | 3.4607 | 70.7291 | 70.1797 | 115.892 | 123.5641 | 3.1036 | 123.587 | 86.6272 | -0.29297 | 123.5641 | 3.1036 | 86.6272 | 115.892 | 123.587 | -123.9349 | -123.8708
5412.7188 | 123.7335 | -61.4273 | 62.1414 | -0.25307 | 0.011965 | 0.0078592 | 0.012747 | 0.058753 | -0.00033333 | 0.076486 | -58.2916 | 62.1368 | -61.7432 | -61.5784 | 54.4968 | 25.1633 | 9.2377 | 8.7753 | 62.1414 | -61.7157 | -0.31586 | -0.004577 | 3.1357 | -0.15106 | -7.6447 | -0.28839 | 0 | 3.4515 | 70.665 | 70.2026 | 115.9241 | 123.5641 | 3.1357 | 123.5687 | 86.5906 | -0.28839 | 123.5641 | 3.1357 | 86.5906 | 115.9241 | 123.5687 | -123.8846 | -123.8571
5413.7188 | 123.8434 | -61.3861 | 62.1048 | -0.19203 | 0.013247 | 0.0097818 | 0.008688 | 0.058112 | -0.0020421 | 0.079049 | -58.2642 | 62.0407 | -61.7386 | -61.5051 | 54.5563 | 25.2274 | 9.0454 | 8.8806 | 62.1094 | -61.6608 | -0.35248 | -0.064087 | 3.1219 | -0.11902 | -7.5485 | -0.27466 | 0.004578 | 3.4744 | 70.4315 | 70.2667 | 115.9424 | 123.4268 | 3.1219 | 123.4955 | 86.6135 | -0.27466 | 123.4268 | 3.1219 | 86.6135 | 115.9424 | 123.4955 | -123.8434 | -123.7656
5414.7188 | 123.8205 | -61.3724 | 62.114 | -0.1844 | 0.014315 | 0.010209 | 0.010397 | 0.057471 | -0.00054693 | 0.079476 | -58.2916 | 62.0499 | -61.7249 | -61.5143 | 54.5425 | 25.296 | 9.0454 | 8.8531 | 62.0819 | -61.6562 | -0.35248 | -0.064087 | 3.0807 | -0.14191 | -7.5714 | -0.28381 | -0.032044 | 3.4332 | 70.4178 | 70.2255 | 115.9149 | 123.4222 | 3.0807 | 123.4543 | 86.6684 | -0.28381 | 123.4222 | 3.0807 | 86.6684 | 115.9149 | 123.4543 | -123.8388 | -123.7701
5415.7188 | 123.848 | -61.3998 | 62.1231 | -0.09285 | 0.015169 | 0.0089274 | 0.010183 | 0.057685 | -0.0011877 | 0.077554 | -58.2779 | 62.0453 | -61.734 | -61.5372 | 54.5151 | 25.2548 | 9.0591 | 8.8394 | 62.0682 | -61.6653 | -0.33417 | -0.07782 | 3.1219 | -0.13733 | -7.608 | -0.2655 | -0.054932 | 3.4561 | 70.459 | 70.2393 | 115.9149 | 123.4451 | 3.1219 | 123.468 | 86.6547 | -0.2655 | 123.4451 | 3.1219 | 86.6547 | 115.9149 | 123.468 | -123.8571 | -123.7885
5416.7188 | 123.8205 | -61.3907 | 62.1002 | -0.077591 | 0.014101 | 0.0065774 | 0.010824 | 0.057898 | -0.00011953 | 0.077767 | -58.3374 | 62.0499 | -61.7249 | -61.528 | 54.5334 | 25.3418 | 9.0317 | 8.8028 | 62.0911 | -61.6791 | -0.33417 | -0.050354 | 3.0533 | -0.13733 | -7.5668 | -0.28839 | -0.009156 | 3.3875 | 70.4224 | 70.1935 | 115.9241 | 123.4406 | 3.0533 | 123.4818 | 86.7325 | -0.28839 | 123.4406 | 3.0533 | 86.7325 | 115.9241 | 123.4818 | -123.8251 | -123.7793
5417.7188 | 123.7518 | -61.4227 | 62.0956 | -0.17677 | 0.011538 | 0.013627 | 0.011038 | 0.058753 | -0.0018285 | 0.078195 | -58.2596 | 62.0773 | -61.7157 | -61.4548 | 54.8264 | 25.4654 | 8.8028 | 8.7753 | 62.1002 | -61.6882 | -0.29297 | -0.01831 | 3.1631 | -0.032044 | -7.2693 | -0.2655 | 0.004578 | 3.4561 | 70.2255 | 70.1981 | 116.2491 | 123.5001 | 3.1631 | 123.5229 | 86.8881 | -0.2655 | 123.5001 | 3.1631 | 86.8881 | 116.2491 | 123.5229 | -123.8113 | -123.7839
5418.7188 | 123.8251 | -61.3998 | 62.1185 | -0.12337 | 0.014742 | 0.0076456 | 0.0080472 | 0.05918 | 0.00094847 | 0.080544 | -58.3099 | 62.0499 | -61.7249 | -61.5509 | 54.4968 | 25.2594 | 9.0317 | 8.7341 | 62.0773 | -61.6791 | -0.32501 | -0.068664 | 3.0899 | -0.15106 | -7.6218 | -0.27924 | -0.041198 | 3.4149 | 70.4315 | 70.134 | 115.8966 | 123.4497 | 3.0899 | 123.4772 | 86.6592 | -0.27924 | 123.4497 | 3.0899 | 86.6592 | 115.8966 | 123.4772 | -123.8434 | -123.7976
5419.7188 | 123.7885 | -61.409 | 62.114 | -0.031814 | 0.014529 | 0.0070048 | 0.0095424 | 0.059607 | -0.0035375 | 0.077554 | -58.287 | 62.0865 | -61.7249 | -61.5646 | 54.5013 | 25.1999 | 8.963 | 8.6792 | 62.059 | -61.6791 | -0.31586 | -0.027466 | 3.1219 | -0.15564 | -7.6126 | -0.27008 | -0.054932 | 3.4378 | 70.372 | 70.0882 | 115.9103 | 123.4955 | 3.1219 | 123.468 | 86.6089 | -0.27008 | 123.4955 | 3.1219 | 86.6089 | 115.9103 | 123.468 | -123.8388 | -123.793
5420.7188 | 123.8297 | -61.3815 | 62.1002 | -0.09285 | 0.013247 | 0.011704 | 0.010824 | 0.05918 | -0.0011877 | 0.080117 | -58.2825 | 62.059 | -61.734 | -61.528 | 54.5059 | 25.1358 | 8.9722 | 8.7067 | 62.0636 | -61.702 | -0.35248 | -0.041199 | 3.0991 | -0.14648 | -7.5943 | -0.32043 | -0.036621 | 3.4515 | 70.3537 | 70.0882 | 115.8875 | 123.4406 | 3.0991 | 123.4451 | 86.5173 | -0.32043 | 123.4406 | 3.0991 | 86.5173 | 115.8875 | 123.4451 | -123.8342 | -123.8022
5421.7188 | 123.7976 | -61.3998 | 62.1231 | -0.08522 | 0.014315 | 0.0095682 | 0.006979 | 0.055548 | 9.4068e-05 | 0.077767 | -58.287 | 62.0453 | -61.734 | -61.5234 | 54.5151 | 25.0626 | 8.931 | 8.6746 | 62.0728 | -61.6882 | -0.33417 | -0.07782 | 3.1128 | -0.1236 | -7.608 | -0.28839 | -0.050354 | 3.447 | 70.3308 | 70.0745 | 115.9149 | 123.4451 | 3.1128 | 123.4726 | 86.4624 | -0.28839 | 123.4451 | 3.1128 | 86.4624 | 115.9149 | 123.4726 | -123.8571 | -123.8113
5422.7344 | 123.6877 | -61.409 | 62.1643 | -0.23018 | 0.014742 | 0.010423 | 0.014669 | 0.058112 | -0.00054693 | 0.079049 | -58.3099 | 62.146 | -61.734 | -61.5967 | 54.3915 | 25.0717 | 9.2697 | 8.725 | 62.1643 | -61.702 | -0.32501 | -0.018311 | 3.0991 | -0.18768 | -7.7728 | -0.29297 | 0 | 3.4241 | 70.6787 | 70.134 | 115.8005 | 123.555 | 3.0991 | 123.5733 | 86.4807 | -0.29297 | 123.555 | 3.0991 | 86.4807 | 115.8005 | 123.5733 | -123.8983 | -123.8663
5423.7188 | 123.8159 | -61.3953 | 62.1002 | -0.016556 | 0.01346 | 0.007432 | 0.0095424 | 0.059607 | -0.0026831 | 0.077981 | -58.3282 | 62.0544 | -61.7386 | -61.5692 | 54.451 | 24.9985 | 8.8531 | 8.5831 | 62.0911 | -61.7065 | -0.34332 | -0.045777 | 3.067 | -0.17395 | -7.6492 | -0.31128 | -0.009156 | 3.4103 | 70.2484 | 69.9783 | 115.8463 | 123.4497 | 3.067 | 123.4863 | 86.3937 | -0.31128 | 123.4497 | 3.067 | 86.3937 | 115.8463 | 123.4863 | -123.8388 | -123.8068
5424.7188 | 123.8068 | -61.3861 | 62.114 | -0.10811 | 0.010042 | 0.0080728 | 0.010183 | 0.056617 | -0.00054693 | 0.080117 | -58.2687 | 62.0728 | -61.7386 | -61.5189 | 54.4601 | 25.177 | 8.7845 | 8.551 | 62.0728 | -61.6791 | -0.35248 | -0.041199 | 3.1174 | -0.13275 | -7.6538 | -0.29297 | -0.041199 | 3.4698 | 70.1706 | 69.9371 | 115.8463 | 123.4589 | 3.1174 | 123.4589 | 86.5631 | -0.29297 | 123.4589 | 3.1174 | 86.5631 | 115.8463 | 123.4589 | -123.8525 | -123.793
5425.7188 | 123.7564 | -61.409 | 62.114 | 0.021591 | 0.014742 | 0.0063638 | 0.0097562 | 0.057257 | -0.00054693 | 0.07499 | -58.2916 | 62.0499 | -61.7615 | -61.5646 | 54.4098 | 25.0305 | 8.7708 | 8.4641 | 62.0819 | -61.6928 | -0.35248 | -0.064087 | 3.1174 | -0.15564 | -7.7042 | -0.28381 | -0.032044 | 3.4698 | 70.1797 | 69.873 | 115.8188 | 123.4589 | 3.1174 | 123.4909 | 86.4395 | -0.28381 | 123.4589 | 3.1174 | 86.4395 | 115.8188 | 123.4909 | -123.8754 | -123.8068
5426.7188 | 123.7793 | -61.4365 | 62.0956 | 0.067368 | 0.013247 | 0.011704 | 0.0076198 | 0.056189 | 0.00073487 | 0.079476 | -58.3145 | 62.0636 | -61.7477 | -61.5692 | 54.3777 | 24.9664 | 8.7708 | 8.4549 | 62.0773 | -61.6745 | -0.31128 | -0.032043 | 3.1219 | -0.13275 | -7.7179 | -0.23804 | -0.01831 | 3.4332 | 70.2072 | 69.8914 | 115.8142 | 123.5001 | 3.1219 | 123.5138 | 86.4029 | -0.23804 | 123.5001 | 3.1219 | 86.4029 | 115.8142 | 123.5138 | -123.8434 | -123.7701
5427.7188 | 123.7427 | -61.4044 | 62.1597 | -0.29884 | 0.011538 | 0.0078592 | 0.013174 | 0.056403 | -0.00011953 | 0.07734 | -58.2642 | 62.114 | -61.7294 | -61.5738 | 54.3503 | 24.8566 | 8.9172 | 8.4183 | 62.1185 | -61.7157 | -0.32501 | -0.045776 | 3.1403 | -0.16937 | -7.8094 | -0.31128 | -0.041199 | 3.4653 | 70.3217 | 69.8227 | 115.7547 | 123.5184 | 3.1403 | 123.5229 | 86.261 | -0.31128 | 123.5184 | 3.1403 | 86.261 | 115.7547 | 123.5229 | -123.8892 | -123.8754
5428.7188 | 123.7701 | -61.3998 | 62.1002 | -0.0089264 | 0.013247 | 0.009141 | 0.010611 | 0.058112 | -0.0018285 | 0.077126 | -58.2687 | 62.0544 | -61.7203 | -61.5646 | 54.4006 | 25.177 | 8.6105 | 8.4 | 62.1094 | -61.6608 | -0.32043 | -0.045777 | 3.1311 | -0.16479 | -7.6996 | -0.26093 | 0.009155 | 3.4515 | 70.0104 | 69.7998 | 115.8005 | 123.4543 | 3.1311 | 123.5092 | 86.5768 | -0.26093 | 123.4543 | 3.1311 | 86.5768 | 115.8005 | 123.5092 | -123.8205 | -123.761
5429.7188 | 123.7747 | -61.409 | 62.0773 | 0.059738 | 0.013674 | 0.0059366 | 0.0099698 | 0.05918 | -0.00033333 | 0.079476 | -58.2825 | 62.059 | -61.734 | -61.5875 | 54.3411 | 25.0076 | 8.6563 | 8.3313 | 62.0453 | -61.6699 | -0.32501 | -0.018311 | 3.1265 | -0.17853 | -7.7362 | -0.26093 | -0.032044 | 3.4515 | 70.0653 | 69.7403 | 115.7501 | 123.468 | 3.1265 | 123.4543 | 86.4166 | -0.26093 | 123.468 | 3.1265 | 86.4166 | 115.7501 | 123.4543 | -123.8113 | -123.7473
5430.7188 | 123.8068 | -61.4044 | 62.1048 | 0.12077 | 0.014315 | 0.011704 | 0.0071926 | 0.057898 | 0.00094847 | 0.079904 | -58.2687 | 62.0773 | -61.7569 | -61.5601 | 54.3411 | 24.8566 | 8.67 | 8.3771 | 62.0911 | -61.702 | -0.35248 | -0.027465 | 3.1357 | -0.15564 | -7.7637 | -0.29755 | -0.013733 | 3.4882 | 70.0745 | 69.7815 | 115.7455 | 123.4818 | 3.1357 | 123.4955 | 86.261 | -0.29755 | 123.4818 | 3.1357 | 86.261 | 115.7455 | 123.4955 | -123.8617 | -123.8068
5431.7188 | 123.7793 | -61.3998 | 62.1094 | -0.054703 | 0.011538 | 0.010423 | 0.011465 | 0.055121 | 0.00052127 | 0.079049 | -58.3282 | 62.0865 | -61.7249 | -61.5646 | 54.332 | 24.9115 | 8.6197 | 8.2993 | 62.0911 | -61.7065 | -0.32501 | -0.022888 | 3.0716 | -0.16479 | -7.7774 | -0.3067 | -0.018311 | 3.3966 | 70.0195 | 69.6991 | 115.7318 | 123.4863 | 3.0716 | 123.4909 | 86.3113 | -0.3067 | 123.4863 | 3.0716 | 86.3113 | 115.7318 | 123.4909 | -123.8342 | -123.8159
5432.7344 | 123.7152 | -61.409 | 62.1735 | -0.97786 | 0.014742 | 0.0097818 | 0.015951 | 0.054694 | 0.00052127 | 0.075417 | -58.3054 | 62.1826 | -61.734 | -61.5875 | 54.2862 | 24.8383 | 8.7845 | 8.2443 | 62.1277 | -61.6974 | -0.32501 | 0.009155 | 3.1036 | -0.17853 | -7.8873 | -0.28839 | -0.045776 | 3.4286 | 70.1935 | 69.6533 | 115.6952 | 123.5916 | 3.1036 | 123.5367 | 86.2473 | -0.28839 | 123.5916 | 3.1036 | 86.2473 | 115.6952 | 123.5367 | -123.9075 | -123.8708
5433.7188 | 123.7701 | -61.3998 | 62.1048 | 0.18181 | 0.013888 | 0.01085 | 0.0093288 | 0.057685 | -0.0018285 | 0.078622 | -58.2642 | 62.0544 | -61.7386 | -61.5921 | 54.3228 | 24.8657 | 8.6151 | 8.2764 | 62.0773 | -61.6745 | -0.33874 | -0.050354 | 3.1357 | -0.19226 | -7.782 | -0.27466 | -0.027465 | 3.4744 | 70.015 | 69.6762 | 115.7227 | 123.4543 | 3.1357 | 123.4772 | 86.2656 | -0.27466 | 123.4543 | 3.1357 | 86.2656 | 115.7227 | 123.4772 | -123.8434 | -123.7793
5434.7188 | 123.7976 | -61.4182 | 62.114 | 0.0063326 | 0.013247 | 0.0095682 | 0.0093288 | 0.057898 | -0.0014013 | 0.077767 | -58.2779 | 62.0636 | -61.7386 | -61.5967 | 54.2953 | 24.8199 | 8.6105 | 8.2809 | 62.0865 | -61.6928 | -0.32043 | -0.050354 | 3.1403 | -0.17853 | -7.8186 | -0.27466 | -0.027466 | 3.4607 | 70.0287 | 69.6991 | 115.7135 | 123.4818 | 3.1403 | 123.5046 | 86.2381 | -0.27466 | 123.4818 | 3.1403 | 86.2381 | 115.7135 | 123.5046 | -123.8525 | -123.8068
5435.7188 | 123.7701 | -61.3998 | 62.114 | 0.14366 | 0.01346 | 0.011918 | 0.010397 | 0.060248 | -0.0018285 | 0.078195 | -58.255 | 62.0911 | -61.7386 | -61.5875 | 54.2725 | 24.7604 | 8.5693 | 8.2306 | 62.0407 | -61.702 | -0.33874 | -0.022889 | 3.1448 | -0.18768 | -7.8415 | -0.30212 | -0.073243 | 3.4836 | 69.9692 | 69.6304 | 115.6723 | 123.4909 | 3.1448 | 123.4406 | 86.1603 | -0.30212 | 123.4909 | 3.1448 | 86.1603 | 115.6723 | 123.4406 | -123.8525 | -123.8159
5436.7188 | 123.7656 | -61.4044 | 62.1002 | 0.15892 | 0.014315 | 0.015336 | 0.010611 | 0.057044 | 0.00073487 | 0.079263 | -58.2458 | 62.0544 | -61.7386 | -61.5921 | 54.2816 | 24.8474 | 8.5236 | 8.2352 | 62.0499 | -61.6974 | -0.33417 | -0.045777 | 3.1586 | -0.18768 | -7.8186 | -0.29297 | -0.050354 | 3.4927 | 69.928 | 69.6396 | 115.686 | 123.4589 | 3.1586 | 123.4543 | 86.2518 | -0.29297 | 123.4589 | 3.1586 | 86.2518 | 115.686 | 123.4543 | -123.8388 | -123.7976
5437.7188 | 123.9349 | -61.3541 | 62.1506 | -0.1844 | 0.013033 | 0.0089274 | 0.0065518 | 0.060675 | -0.00033333 | 0.077767 | -58.1726 | 62.0911 | -61.7111 | -61.496 | 54.3228 | 24.7971 | 8.5098 | 8.2764 | 62.0865 | -61.6791 | -0.35706 | -0.05951 | 3.1815 | -0.14191 | -7.8278 | -0.32501 | -0.064087 | 3.5385 | 69.8639 | 69.6304 | 115.6769 | 123.4451 | 3.1815 | 123.4406 | 86.1511 | -0.32501 | 123.4451 | 3.1815 | 86.1511 | 115.6769 | 123.4406 | -123.8617 | -123.8297
5438.7344 | 123.6877 | -61.4182 | 62.1597 | -0.19203 | 0.014742 | 0.0099954 | 0.014883 | 0.057898 | 9.4068e-05 | 0.076486 | -58.255 | 62.1414 | -61.7386 | -61.5692 | 54.2313 | 24.678 | 8.6792 | 8.1253 | 62.146 | -61.6974 | -0.32043 | -0.018311 | 3.1631 | -0.15106 | -7.9285 | -0.27924 | -0.013733 | 3.4836 | 70.0974 | 69.5435 | 115.6494 | 123.5596 | 3.1631 | 123.5641 | 86.0962 | -0.27924 | 123.5596 | 3.1631 | 86.0962 | 115.6494 | 123.5641 | -123.8983 | -123.8571
5439.7188 | 123.7885 | -61.3953 | 62.1002 | 0.17418 | 0.016451 | 0.011704 | 0.011465 | 0.060462 | -0.00097413 | 0.078622 | -58.1909 | 62.0453 | -61.7294 | -61.5417 | 54.277 | 24.7787 | 8.3725 | 8.1619 | 62.0819 | -61.6745 | -0.33417 | -0.054932 | 3.2043 | -0.14648 | -7.8232 | -0.27924 | -0.018311 | 3.5385 | 69.7678 | 69.5572 | 115.6723 | 123.4406 | 3.2043 | 123.4772 | 86.174 | -0.27924 | 123.4406 | 3.2043 | 86.174 | 115.6723 | 123.4772 | -123.8297 | -123.7747
5440.7188 | 123.8113 | -61.409 | 62.1094 | -0.2607 | 0.013888 | 0.0072184 | 0.013601 | 0.059394 | -0.0028967 | 0.078835 | -58.2138 | 62.0773 | -61.7111 | -61.5463 | 54.2633 | 24.7787 | 8.3633 | 8.1711 | 62.0499 | -61.6882 | -0.30212 | -0.032043 | 3.1952 | -0.13733 | -7.8461 | -0.27923 | -0.059509 | 3.4973 | 69.7723 | 69.5801 | 115.6723 | 123.4863 | 3.1952 | 123.4589 | 86.1877 | -0.27923 | 123.4863 | 3.1952 | 86.1877 | 115.6723 | 123.4589 | -123.8205 | -123.7976
5441.7188 | 123.7656 | -61.3861 | 62.1094 | 0.097885 | 0.015597 | 0.009141 | 0.011892 | 0.05918 | -0.0026831 | 0.078622 | -58.2092 | 62.0544 | -61.7249 | -61.5417 | 54.2221 | 24.9023 | 8.3313 | 8.1116 | 62.0728 | -61.702 | -0.33875 | -0.054932 | 3.1769 | -0.15564 | -7.8873 | -0.31586 | -0.036621 | 3.5156 | 69.7174 | 69.4977 | 115.6082 | 123.4406 | 3.1769 | 123.4589 | 86.2885 | -0.31586 | 123.4406 | 3.1769 | 86.2885 | 115.6082 | 123.4589 | -123.8342 | -123.8113
5442.7344 | 123.7244 | -61.3815 | 62.1414 | -0.22255 | 0.014742 | 0.010423 | 0.012533 | 0.057898 | -0.0031103 | 0.077767 | -58.1726 | 62.1185 | -61.7157 | -61.5189 | 54.1855 | 24.7833 | 8.4778 | 8.1116 | 62.1094 | -61.6745 | -0.33417 | -0.022888 | 3.2089 | -0.13733 | -7.9559 | -0.29297 | -0.032043 | 3.5431 | 69.8593 | 69.4931 | 115.567 | 123.5001 | 3.2089 | 123.4909 | 86.1649 | -0.29297 | 123.5001 | 3.2089 | 86.1649 | 115.567 | 123.4909 | -123.8571 | -123.8159
5443.7188 | 123.8068 | -61.4044 | 62.1048 | 0.13603 | 0.015383 | 0.0132 | 0.013388 | 0.058753 | -0.00011953 | 0.078622 | -58.1772 | 62.0682 | -61.6974 | -61.5417 | 54.1809 | 24.8291 | 8.3038 | 8.0841 | 62.0544 | -61.702 | -0.29297 | -0.036621 | 3.2272 | -0.13733 | -7.9239 | -0.29755 | -0.050354 | 3.5202 | 69.7083 | 69.4885 | 115.5853 | 123.4726 | 3.2272 | 123.4589 | 86.2335 | -0.29755 | 123.4726 | 3.2272 | 86.2335 | 115.5853 | 123.4589 | -123.8022 | -123.8068
5444.7188 | 123.761 | -61.4182 | 62.1002 | 0.15129 | 0.013247 | 0.0093546 | 0.012747 | 0.060462 | -0.00097413 | 0.077767 | -58.2092 | 62.0544 | -61.734 | -61.5601 | 54.1397 | 24.7833 | 8.3176 | 8.0338 | 62.0865 | -61.6974 | -0.31586 | -0.045777 | 3.2089 | -0.14191 | -7.9605 | -0.27924 | -0.013733 | 3.5248 | 69.7357 | 69.4519 | 115.5579 | 123.4726 | 3.2089 | 123.5046 | 86.2015 | -0.27924 | 123.4726 | 3.2089 | 86.2015 | 115.5579 | 123.5046 | -123.8342 | -123.7976
5445.7188 | 123.7656 | -61.4182 | 62.1094 | 0.1284 | 0.015597 | 0.0093546 | 0.013174 | 0.058539 | -0.00054693 | 0.077554 | -58.1772 | 62.0636 | -61.7432 | -61.5601 | 54.1718 | 24.8108 | 8.3359 | 8.0704 | 62.0773 | -61.7111 | -0.32501 | -0.045776 | 3.241 | -0.14191 | -7.9376 | -0.29297 | -0.032043 | 3.566 | 69.754 | 69.4885 | 115.5899 | 123.4818 | 3.241 | 123.4955 | 86.2289 | -0.29297 | 123.4818 | 3.241 | 86.2289 | 115.5899 | 123.4955 | -123.8525 | -123.8205
5446.7188 | 123.8571 | -61.3998 | 62.0819 | 0.16655 | 0.016024 | 0.014909 | 0.015524 | 0.060675 | -0.00097413 | 0.078835 | -58.1589 | 62.0682 | -61.7432 | -61.5509 | 53.8742 | 24.6368 | 8.4915 | 8.0933 | 62.0636 | -61.7065 | -0.34332 | -0.013733 | 3.241 | -0.15106 | -8.2077 | -0.3067 | -0.01831 | 3.5843 | 69.8914 | 69.4931 | 115.274 | 123.468 | 3.241 | 123.4634 | 86.0367 | -0.3067 | 123.468 | 3.241 | 86.0367 | 115.274 | 123.4634 | -123.8251 | -123.7885
5447.7344 | 123.8663 | -61.3541 | 62.114 | -0.11574 | 0.014315 | 0.0097818 | 0.0084744 | 0.057898 | -0.00011953 | 0.078622 | -58.1543 | 62.1094 | -61.6837 | -61.5189 | 54.1718 | 24.8932 | 8.3405 | 8.1436 | 62.1094 | -61.6791 | -0.32959 | -0.004578 | 3.1998 | -0.16479 | -7.9422 | -0.32501 | -0.004578 | 3.5294 | 69.6945 | 69.4977 | 115.5258 | 123.4634 | 3.1998 | 123.4634 | 86.2473 | -0.32501 | 123.4634 | 3.1998 | 86.2473 | 115.5258 | 123.4634 | -123.7976 | -123.793
5448.7188 | 123.8159 | -61.3953 | 62.0819 | 0.92186 | 0.014529 | 0.013413 | 0.015097 | 0.061103 | -0.0020421 | 0.078622 | -58.1039 | 62.1002 | -61.7203 | -61.5509 | 54.0985 | 24.7375 | 8.2626 | 8.0795 | 62.0819 | -61.6974 | -0.32501 | 0.018311 | 3.2913 | -0.15564 | -7.9834 | -0.30212 | 0 | 3.6163 | 69.6579 | 69.4748 | 115.4938 | 123.4955 | 3.2913 | 123.4772 | 86.1328 | -0.30212 | 123.4955 | 3.2913 | 86.1328 | 115.4938 | 123.4772 | -123.8022 | -123.7793
5449.7344 | 123.8022 | -61.377 | 62.1323 | -0.5201 | 0.01282 | 0.0078592 | 0.01232 | 0.057257 | -0.0014013 | 0.078408 | -58.1863 | 62.0865 | -61.6928 | -61.4822 | 54.158 | 24.7421 | 8.3542 | 8.1528 | 62.1185 | -61.6699 | -0.31586 | -0.045776 | 3.1906 | -0.10529 | -7.9742 | -0.29297 | -0.013733 | 3.5065 | 69.7311 | 69.5297 | 115.535 | 123.4634 | 3.1906 | 123.4955 | 86.1191 | -0.29297 | 123.4634 | 3.1906 | 86.1191 | 115.535 | 123.4955 | -123.8251 | -123.8022
5450.7188 | 123.793 | -61.3861 | 62.1094 | 0.18181 | 0.014315 | 0.012345 | 0.013601 | 0.059394 | -0.0020421 | 0.07969 | -58.1451 | 62.0636 | -61.7157 | -61.5326 | 54.0939 | 24.7559 | 8.2443 | 8.0475 | 62.0728 | -61.7065 | -0.32959 | -0.045776 | 3.241 | -0.14648 | -8.0154 | -0.32044 | -0.036621 | 3.5706 | 69.6304 | 69.4336 | 115.48 | 123.4497 | 3.241 | 123.4589 | 86.142 | -0.32044 | 123.4497 | 3.241 | 86.142 | 115.48 | 123.4589 | -123.8251 | -123.8159
5451.7188 | 123.8205 | -61.3861 | 62.1277 | 0.79216 | 0.013674 | 0.014695 | 0.012747 | 0.05918 | -0.0016149 | 0.077126 | -58.1085 | 62.0911 | -61.7111 | -61.5372 | 54.0985 | 24.7192 | 8.2214 | 8.0338 | 62.0453 | -61.702 | -0.32501 | -0.036622 | 3.2776 | -0.15106 | -8.0292 | -0.31586 | -0.082398 | 3.6026 | 69.6075 | 69.4199 | 115.4846 | 123.4772 | 3.2776 | 123.4314 | 86.1053 | -0.31586 | 123.4772 | 3.2776 | 86.1053 | 115.4846 | 123.4314 | -123.8388 | -123.8297
5452.7188 | 123.8022 | -61.3724 | 62.114 | 0.15129 | 0.014101 | 0.014695 | 0.013388 | 0.057257 | -0.0016149 | 0.078835 | -58.1268 | 62.0956 | -61.7157 | -61.5555 | 54.0802 | 24.7284 | 8.2169 | 8.0063 | 62.0819 | -61.6791 | -0.34332 | -0.018311 | 3.2455 | -0.18311 | -8.0338 | -0.3067 | -0.032044 | 3.5889 | 69.5892 | 69.3787 | 115.4526 | 123.468 | 3.2455 | 123.4543 | 86.1008 | -0.3067 | 123.468 | 3.2455 | 86.1008 | 115.4526 | 123.4543 | -123.8297 | -123.793
5453.7188 | 123.7518 | -61.4319 | 62.1094 | 0.2047 | 0.019228 | 0.016191 | 0.016592 | 0.058753 | 0.00030767 | 0.078195 | -58.168 | 62.1323 | -61.7615 | -61.5875 | 53.9841 | 24.6597 | 8.2764 | 7.901 | 62.1002 | -61.7432 | -0.32959 | 0.022888 | 3.2639 | -0.15564 | -8.1253 | -0.31128 | -0.009155 | 3.5934 | 69.7083 | 69.3329 | 115.416 | 123.5641 | 3.2639 | 123.5321 | 86.0916 | -0.31128 | 123.5641 | 3.2639 | 86.0916 | 115.416 | 123.5321 | -123.8708 | -123.8525
5454.7344 | 123.7701 | -61.3953 | 62.1277 | -0.25307 | 0.013674 | 0.013627 | 0.0097562 | 0.059607 | -0.0022559 | 0.078835 | -58.1863 | 62.0911 | -61.734 | -61.5509 | 54.0527 | 24.678 | 8.3038 | 8.0063 | 62.1048 | -61.6653 | -0.33875 | -0.036622 | 3.2089 | -0.15564 | -8.075 | -0.27008 | -0.022889 | 3.5477 | 69.6991 | 69.4016 | 115.448 | 123.4863 | 3.2089 | 123.5001 | 86.0733 | -0.27008 | 123.4863 | 3.2089 | 86.0733 | 115.448 | 123.5001 | -123.8617 | -123.793
5455.7188 | 123.88 | -61.4182 | 62.1094 | 0.12077 | 0.016878 | 0.014482 | 0.015738 | 0.059394 | -0.0014013 | 0.078622 | -58.0994 | 62.1094 | -61.7249 | -61.5463 | 54.0527 | 24.8062 | 8.1161 | 7.7728 | 62.059 | -61.7386 | -0.3067 | 0 | 3.3188 | -0.12817 | -8.0566 | -0.32043 | -0.050354 | 3.6255 | 69.5343 | 69.191 | 115.4709 | 123.5275 | 3.3188 | 123.4772 | 86.2244 | -0.32043 | 123.5275 | 3.3188 | 86.2244 | 115.4709 | 123.4772 | -123.8342 | -123.848
5456.7188 | 123.8251 | -61.3724 | 62.1002 | -0.14626 | 0.012606 | 0.012132 | 0.012747 | 0.060462 | -0.0024695 | 0.081826 | -58.0948 | 62.114 | -61.7294 | -61.5326 | 54.0161 | 24.7971 | 8.1894 | 8.0063 | 62.0636 | -61.6928 | -0.35706 | 0.013733 | 3.2776 | -0.16022 | -8.0841 | -0.32044 | -0.036621 | 3.6346 | 69.5618 | 69.3787 | 115.3885 | 123.4863 | 3.2776 | 123.436 | 86.1694 | -0.32044 | 123.4863 | 3.2776 | 86.1694 | 115.3885 | 123.436 | -123.8297 | -123.793
5457.7344 | 123.8113 | -61.377 | 62.1185 | -0.062332 | 0.015169 | 0.013841 | 0.0091152 | 0.060462 | -0.00076053 | 0.080117 | -58.136 | 62.1048 | -61.7065 | -61.5326 | 54.0527 | 24.733 | 8.2443 | 8.0246 | 62.114 | -61.6882 | -0.32959 | -0.013733 | 3.241 | -0.15564 | -8.0658 | -0.31128 | -0.004577 | 3.5706 | 69.6213 | 69.4016 | 115.4297 | 123.4818 | 3.241 | 123.4909 | 86.1099 | -0.31128 | 123.4818 | 3.241 | 86.1099 | 115.4297 | 123.4909 | -123.8251 | -123.8068
5458.7188 | 123.7564 | -61.4182 | 62.1277 | 0.23521 | 0.018374 | 0.014909 | 0.017447 | 0.059607 | 0.00052127 | 0.079476 | -58.1543 | 62.1597 | -61.7477 | -61.5921 | 53.9246 | 24.5911 | 8.2626 | 7.9239 | 62.114 | -61.734 | -0.32959 | 0.032043 | 3.2639 | -0.17395 | -8.2031 | -0.31586 | -0.013733 | 3.5934 | 69.6808 | 69.342 | 115.3427 | 123.5779 | 3.2639 | 123.5321 | 86.0092 | -0.31586 | 123.5779 | 3.2639 | 86.0092 | 115.3427 | 123.5321 | -123.8754 | -123.8617
5459.7344 | 123.8571 | -61.3495 | 62.1185 | -0.12337 | 0.015383 | 0.0085 | 0.0078336 | 0.057685 | -0.00076053 | 0.078835 | -58.0902 | 62.0819 | -61.7249 | -61.4822 | 54.0665 | 24.7879 | 8.2352 | 8.0841 | 62.1002 | -61.6608 | -0.37537 | -0.036621 | 3.2593 | -0.13275 | -8.0521 | -0.31128 | -0.01831 | 3.6346 | 69.5847 | 69.4336 | 115.416 | 123.4314 | 3.2593 | 123.4497 | 86.1374 | -0.31128 | 123.4314 | 3.2593 | 86.1374 | 115.416 | 123.4497 | -123.8434 | -123.7793
5460.7188 | 123.6786 | -61.4365 | 62.1506 | 0.18944 | 0.016024 | 0.014695 | 0.018728 | 0.060034 | -0.0024695 | 0.079904 | -58.1451 | 62.1826 | -61.7203 | -61.6333 | 53.9154 | 24.5911 | 8.4 | 7.8644 | 62.1506 | -61.7706 | -0.28381 | 0.032043 | 3.2913 | -0.19684 | -8.2352 | -0.33417 | 0 | 3.5751 | 69.8364 | 69.3008 | 115.3519 | 123.6191 | 3.2913 | 123.587 | 86.0275 | -0.33417 | 123.6191 | 3.2913 | 86.0275 | 115.3519 | 123.587 | -123.8708 | -123.9212
5461.7188 | 123.6649 | -61.4227 | 62.1277 | 0.13603 | 0.019442 | 0.017045 | 0.01531 | 0.061957 | 0.00073487 | 0.078835 | -58.1726 | 62.1872 | -61.7569 | -61.5967 | 54.0436 | 24.5499 | 8.3267 | 7.901 | 62.1552 | -61.7386 | -0.33417 | 0.059509 | 3.2501 | -0.17395 | -8.0841 | -0.31586 | 0.027465 | 3.5843 | 69.7494 | 69.3237 | 115.4663 | 123.6099 | 3.2501 | 123.5779 | 85.9726 | -0.31586 | 123.6099 | 3.2501 | 85.9726 | 115.4663 | 123.5779 | -123.8846 | -123.8663
5462.7188 | 123.8068 | -61.409 | 62.114 | 0.21233 | 0.016238 | 0.014695 | 0.015951 | 0.064734 | -0.00097413 | 0.079049 | -58.1085 | 62.1689 | -61.7523 | -61.5829 | 53.9795 | 24.646 | 8.2626 | 7.9605 | 62.114 | -61.7157 | -0.34332 | 0.054931 | 3.3005 | -0.17395 | -8.1345 | -0.3067 | 0 | 3.6438 | 69.6716 | 69.3695 | 115.3885 | 123.5779 | 3.3005 | 123.523 | 86.055 | -0.3067 | 123.5779 | 3.3005 | 86.055 | 115.3885 | 123.523 | -123.8663 | -123.8297
5463.7188 | 123.6923 | -61.4365 | 62.146 | 0.052109 | 0.016024 | 0.015336 | 0.01531 | 0.063239 | -0.00097413 | 0.077126 | -58.1223 | 62.2192 | -61.7386 | -61.647 | 53.9062 | 24.5773 | 8.3633 | 7.869 | 62.1414 | -61.7386 | -0.30212 | 0.073242 | 3.3142 | -0.21057 | -8.2397 | -0.30212 | -0.004578 | 3.6163 | 69.7998 | 69.3054 | 115.3427 | 123.6557 | 3.3142 | 123.5779 | 86.0138 | -0.30212 | 123.6557 | 3.3142 | 86.0138 | 115.3427 | 123.5779 | -123.8846 | -123.8846
5464.7188 | 123.674 | -61.4136 | 62.146 | 0.059738 | 0.01581 | 0.011277 | 0.01766 | 0.061957 | -0.0024695 | 0.080117 | -58.0811 | 62.1826 | -61.7294 | -61.6287 | 53.92 | 24.6231 | 8.3359 | 7.8598 | 62.1506 | -61.7294 | -0.31586 | 0.036621 | 3.3325 | -0.21515 | -8.226 | -0.31586 | 0.004578 | 3.6484 | 69.7494 | 69.2734 | 115.3336 | 123.5962 | 3.3325 | 123.5641 | 86.0367 | -0.31586 | 123.5962 | 3.3325 | 86.0367 | 115.3336 | 123.5641 | -123.8754 | -123.8754
5465.7188 | 123.6832 | -61.4365 | 62.1231 | -0.0089264 | 0.017733 | 0.016831 | 0.017019 | 0.065589 | -0.00097413 | 0.080972 | -58.1451 | 62.2101 | -61.7661 | -61.647 | 53.9062 | 24.646 | 8.3405 | 7.8186 | 62.1506 | -61.7294 | -0.32959 | 0.086975 | 3.2913 | -0.21057 | -8.2169 | -0.29297 | 0.027466 | 3.6209 | 69.7769 | 69.2551 | 115.3427 | 123.6465 | 3.2913 | 123.587 | 86.0825 | -0.29297 | 123.6465 | 3.2913 | 86.0825 | 115.3427 | 123.587 | -123.8892 | -123.8525
5466.7188 | 123.7335 | -61.4044 | 62.1368 | -0.039444 | 0.01816 | 0.01085 | 0.015524 | 0.063239 | -0.0024695 | 0.078195 | -58.049 | 62.1918 | -61.7203 | -61.5784 | 53.92 | 24.6826 | 8.3313 | 7.8827 | 62.178 | -61.734 | -0.31586 | 0.054931 | 3.3554 | -0.17395 | -8.2169 | -0.32959 | 0.041199 | 3.6713 | 69.7357 | 69.2871 | 115.3244 | 123.5962 | 3.3554 | 123.5825 | 86.087 | -0.32959 | 123.5962 | 3.3554 | 86.087 | 115.3244 | 123.5825 | -123.8571 | -123.8708
5467.7344 | 123.8297 | -61.409 | 62.1094 | 0.19707 | 0.016238 | 0.01085 | 0.01296 | 0.061957 | -0.00054693 | 0.084603 | -58.049 | 62.0911 | -61.7249 | -61.7294 | 53.7735 | 24.8566 | 8.2306 | 7.869 | 62.146 | -61.6699 | -0.31586 | -0.018311 | 3.36 | -0.32043 | -8.3359 | -0.26093 | 0.036621 | 3.6758 | 69.6396 | 69.278 | 115.1825 | 123.5001 | 3.36 | 123.555 | 86.2656 | -0.26093 | 123.5001 | 3.36 | 86.2656 | 115.1825 | 123.555 | -123.8342 | -123.7793
5468.7188 | 123.7289 | -61.4182 | 62.1277 | -0.054703 | 0.019442 | 0.014909 | 0.018301 | 0.061743 | -0.0018285 | 0.080544 | -58.0582 | 62.2055 | -61.7249 | -61.615 | 53.8239 | 24.6048 | 8.3542 | 7.8644 | 62.1552 | -61.7477 | -0.3067 | 0.077819 | 3.36 | -0.19684 | -8.3038 | -0.32959 | 0.027465 | 3.6667 | 69.7723 | 69.2825 | 115.242 | 123.6237 | 3.36 | 123.5733 | 86.0229 | -0.32959 | 123.6237 | 3.36 | 86.0229 | 115.242 | 123.5733 | -123.8525 | -123.8754
5469.7188 | 123.7106 | -61.409 | 62.1552 | -0.054703 | 0.015383 | 0.015977 | 0.014883 | 0.062812 | -0.0020421 | 0.079476 | -58.0399 | 62.2055 | -61.7477 | -61.5784 | 53.8879 | 24.6552 | 8.3313 | 7.8552 | 62.1735 | -61.734 | -0.33875 | 0.050354 | 3.3691 | -0.16937 | -8.2672 | -0.32501 | 0.018311 | 3.7079 | 69.7403 | 69.2642 | 115.2969 | 123.6145 | 3.3691 | 123.5825 | 86.0641 | -0.32501 | 123.6145 | 3.3691 | 86.0641 | 115.2969 | 123.5825 | -123.9029 | -123.8892
5470.7188 | 123.7289 | -61.4227 | 62.1552 | 0.0063326 | 0.018587 | 0.017686 | 0.016165 | 0.063239 | 0.00030767 | 0.080758 | -58.0353 | 62.2147 | -61.7249 | -61.5738 | 53.9246 | 24.7009 | 8.3221 | 7.8735 | 62.1414 | -61.7477 | -0.30213 | 0.05951 | 3.3875 | -0.15106 | -8.2306 | -0.32501 | -0.013733 | 3.6896 | 69.7449 | 69.2963 | 115.3473 | 123.6374 | 3.3875 | 123.5641 | 86.1237 | -0.32501 | 123.6374 | 3.3875 | 86.1237 | 115.3473 | 123.5641 | -123.88 | -123.9029
5471.7188 | 123.7427 | -61.3998 | 62.146 | -0.077591 | 0.017092 | 0.012773 | 0.017019 | 0.063239 | -0.0018285 | 0.080758 | -58.049 | 62.2238 | -61.7249 | -61.5875 | 53.5995 | 24.4675 | 8.4595 | 7.8094 | 62.1735 | -61.7065 | -0.32501 | 0.07782 | 3.3508 | -0.18768 | -8.5464 | -0.3067 | 0.027466 | 3.6758 | 69.8593 | 69.2093 | 114.9994 | 123.6237 | 3.3508 | 123.5733 | 85.8673 | -0.3067 | 123.6237 | 3.3508 | 85.8673 | 114.9994 | 123.5733 | -123.8708 | -123.8525
5472.7344 | 123.8251 | -61.3907 | 62.0865 | 0.18944 | 0.014742 | 0.012132 | 0.011251 | 0.06153 | -0.0018285 | 0.079476 | -58.0399 | 62.1323 | -61.7203 | -61.5738 | 53.8055 | 24.527 | 8.313 | 8.0841 | 62.0911 | -61.6699 | -0.32959 | 0.045776 | 3.3508 | -0.18311 | -8.2809 | -0.27924 | 0.004577 | 3.6804 | 69.7037 | 69.4748 | 115.1962 | 123.5229 | 3.3508 | 123.4818 | 85.9177 | -0.27924 | 123.5229 | 3.3508 | 85.9177 | 115.1962 | 123.4818 | -123.8068 | -123.7564
5473.7188 | 123.7381 | -61.377 | 62.1597 | -0.131 | 0.017947 | 0.014695 | 0.013601 | 0.06153 | -0.0016149 | 0.07969 | -58.0399 | 62.2467 | -61.734 | -61.5646 | 53.9108 | 24.7513 | 8.2489 | 7.8415 | 62.1872 | -61.7249 | -0.35706 | 0.086975 | 3.3371 | -0.18768 | -8.2489 | -0.3479 | 0.027466 | 3.6942 | 69.6259 | 69.2184 | 115.2878 | 123.6237 | 3.3371 | 123.5641 | 86.1282 | -0.3479 | 123.6237 | 3.3371 | 86.1282 | 115.2878 | 123.5641 | -123.8937 | -123.8846
5474.7188 | 123.7473 | -61.3907 | 62.178 | -0.23781 | 0.018801 | 0.011491 | 0.013601 | 0.061103 | 0.00052127 | 0.077981 | -58.0582 | 62.2238 | -61.7203 | -61.5875 | 53.8605 | 24.7284 | 8.2809 | 7.8049 | 62.2101 | -61.702 | -0.32959 | 0.045776 | 3.3325 | -0.19684 | -8.3176 | -0.31128 | 0.032043 | 3.6621 | 69.6716 | 69.1956 | 115.2512 | 123.6145 | 3.3325 | 123.6008 | 86.1191 | -0.31128 | 123.6145 | 3.3325 | 86.1191 | 115.2512 | 123.6008 | -123.8983 | -123.88
5475.7188 | 123.7564 | -61.4182 | 62.1643 | -0.17677 | 0.017092 | 0.014268 | 0.014669 | 0.062384 | -0.0011877 | 0.07734 | -58.0215 | 62.2101 | -61.7157 | -61.5646 | 53.8651 | 24.733 | 8.2581 | 7.8415 | 62.2055 | -61.7065 | -0.29755 | 0.045776 | 3.3966 | -0.14648 | -8.2993 | -0.28839 | 0.041198 | 3.6942 | 69.6762 | 69.2596 | 115.2832 | 123.6282 | 3.3966 | 123.6237 | 86.1511 | -0.28839 | 123.6282 | 3.3966 | 86.1511 | 115.2832 | 123.6237 | -123.88 | -123.8709
5476.7188 | 123.7335 | -61.409 | 62.1826 | -0.16914 | 0.019228 | 0.014695 | 0.01296 | 0.061743 | -0.00011953 | 0.078195 | -58.0353 | 62.1964 | -61.7249 | -61.5829 | 53.8559 | 24.7055 | 8.3084 | 7.869 | 62.2147 | -61.7111 | -0.31586 | 0.013733 | 3.3737 | -0.17395 | -8.3267 | -0.30212 | 0.032044 | 3.6896 | 69.7174 | 69.278 | 115.2649 | 123.6053 | 3.3737 | 123.6237 | 86.1145 | -0.30212 | 123.6053 | 3.3737 | 86.1145 | 115.2649 | 123.6237 | -123.9075 | -123.8937
5477.7344 | 123.6832 | -61.409 | 62.146 | 0.13603 | 0.016238 | 0.016831 | 0.01531 | 0.061316 | 0.00052127 | 0.07969 | -58.0627 | 62.1872 | -61.7477 | -61.6653 | 53.7552 | 24.5911 | 8.3038 | 7.7957 | 62.1689 | -61.7661 | -0.33875 | 0.041199 | 3.3463 | -0.25635 | -8.3908 | -0.35706 | 0.022888 | 3.685 | 69.7128 | 69.2047 | 115.1642 | 123.5962 | 3.3463 | 123.5779 | 86.0001 | -0.35706 | 123.5962 | 3.3463 | 86.0001 | 115.1642 | 123.5779 | -123.8937 | -123.912
5478.7188 | 123.7106 | -61.4273 | 62.1643 | -0.20729 | 0.017092 | 0.013413 | 0.014456 | 0.060462 | -0.00097413 | 0.079263 | -58.0627 | 62.2009 | -61.7386 | -61.615 | 53.8376 | 24.7192 | 8.3313 | 7.8461 | 62.2192 | -61.7294 | -0.31128 | 0.036621 | 3.3646 | -0.18768 | -8.3267 | -0.30212 | 0.054931 | 3.6758 | 69.7586 | 69.2734 | 115.2649 | 123.6282 | 3.3646 | 123.6465 | 86.1465 | -0.30212 | 123.6282 | 3.3646 | 86.1465 | 115.2649 | 123.6465 | -123.9029 | -123.8937
5479.7188 | 123.7289 | -61.4044 | 62.1735 | -0.1844 | 0.019015 | 0.010423 | 0.016165 | 0.061743 | -0.0020421 | 0.081185 | -58.049 | 62.1872 | -61.7157 | -61.5692 | 53.7827 | 24.614 | 8.3313 | 7.9056 | 62.1872 | -61.7157 | -0.31128 | 0.013733 | 3.3554 | -0.1648 | -8.3908 | -0.31128 | 0.013733 | 3.6667 | 69.7357 | 69.31 | 115.1871 | 123.5916 | 3.3554 | 123.5916 | 86.0184 | -0.31128 | 123.5916 | 3.3554 | 86.0184 | 115.1871 | 123.5916 | -123.8892 | -123.8892
5480.7188 | 123.7152 | -61.4319 | 62.178 | -0.2607 | 0.014529 | 0.012345 | 0.0097562 | 0.060889 | 0.0022303 | 0.079476 | -58.0536 | 62.1964 | -61.7477 | -61.6196 | 53.8055 | 24.6918 | 8.6884 | 7.6859 | 62.233 | -61.702 | -0.31586 | 0.01831 | 3.3783 | -0.18768 | -8.3725 | -0.27008 | 0.054931 | 3.6942 | 70.1202 | 69.1177 | 115.2374 | 123.6282 | 3.3783 | 123.6649 | 86.1237 | -0.27008 | 123.6282 | 3.3783 | 86.1237 | 115.2374 | 123.6649 | -123.9258 | -123.88
5481.7188 | 123.6832 | -61.4136 | 62.1826 | -0.46669 | 0.013674 | 0.013627 | 0.012747 | 0.060462 | -0.00097413 | 0.080544 | -58.0399 | 62.1689 | -61.7249 | -61.615 | 53.7872 | 24.6552 | 8.4137 | 7.9285 | 62.1735 | -61.7065 | -0.31128 | -0.013733 | 3.3737 | -0.20142 | -8.3954 | -0.29297 | -0.009155 | 3.685 | 69.8273 | 69.342 | 115.2008 | 123.5825 | 3.3737 | 123.587 | 86.0687 | -0.29297 | 123.5825 | 3.3737 | 86.0687 | 115.2008 | 123.587 | -123.9075 | -123.8892
5482.7188 | 123.7473 | -61.3998 | 62.1552 | 0.090256 | 0.018374 | 0.013413 | 0.017019 | 0.062598 | -0.0014013 | 0.077981 | -57.962 | 62.2101 | -61.7157 | -61.5784 | 53.7827 | 24.6826 | 8.1985 | 7.8369 | 62.1826 | -61.7203 | -0.31586 | 0.054932 | 3.4378 | -0.17853 | -8.3725 | -0.32043 | 0.027466 | 3.7537 | 69.5984 | 69.2368 | 115.1825 | 123.6099 | 3.4378 | 123.5825 | 86.0825 | -0.32043 | 123.6099 | 3.4378 | 86.0825 | 115.1825 | 123.5825 | -123.8708 | -123.8754
5483.7188 | 123.7152 | -61.3861 | 62.2421 | -0.20729 | 0.01581 | 0.010209 | 0.010397 | 0.058753 | -0.00076053 | 0.080331 | -58.049 | 62.1826 | -61.7477 | -61.6104 | 53.7598 | 24.6002 | 8.3359 | 7.8461 | 62.2284 | -61.702 | -0.36163 | -0.059509 | 3.3371 | -0.22431 | -8.4824 | -0.31586 | -0.013732 | 3.6987 | 69.722 | 69.2322 | 115.1459 | 123.5687 | 3.3371 | 123.6145 | 85.9863 | -0.31586 | 123.5687 | 3.3371 | 85.9863 | 115.1459 | 123.6145 | -123.9899 | -123.9441
5484.7188 | 123.7198 | -61.3998 | 62.1918 | 0.059738 | 0.015383 | 0.0085 | 0.011251 | 0.061743 | -0.0022559 | 0.080544 | -58.017 | 62.1643 | -61.7477 | -61.6013 | 53.7186 | 24.6414 | 8.3588 | 7.869 | 62.2147 | -61.7111 | -0.3479 | -0.027465 | 3.3829 | -0.20142 | -8.4732 | -0.31128 | 0.022889 | 3.7308 | 69.7586 | 69.2688 | 115.1184 | 123.5641 | 3.3829 | 123.6145 | 86.0413 | -0.31128 | 123.5641 | 3.3829 | 86.0413 | 115.1184 | 123.6145 | -123.9395 | -123.9029
5485.7188 | 123.6923 | -61.4044 | 62.1826 | -0.23781 | 0.016665 | 0.0082864 | 0.015524 | 0.061103 | -0.0020421 | 0.082467 | -58.1406 | 62.1872 | -61.7203 | -61.6562 | 53.7323 | 24.6506 | 8.3633 | 7.8827 | 62.1918 | -61.7386 | -0.31586 | 0.004578 | 3.2639 | -0.25177 | -8.4503 | -0.33417 | 0.009155 | 3.5797 | 69.7678 | 69.2871 | 115.1367 | 123.5916 | 3.2639 | 123.5962 | 86.055 | -0.33417 | 123.5916 | 3.2639 | 86.055 | 115.1367 | 123.5962 | -123.9029 | -123.9212
5486.7188 | 123.6374 | -61.3861 | 62.1506 | -0.23781 | 0.014529 | 0.011491 | 0.012747 | 0.058325 | -0.0024695 | 0.078622 | -58.0353 | 62.1689 | -61.7294 | -61.615 | 53.7231 | 24.6048 | 8.5007 | 8.1757 | 62.2513 | -61.6653 | -0.34332 | 0.01831 | 3.3508 | -0.22888 | -8.4274 | -0.27924 | 0.10071 | 3.6942 | 69.8868 | 69.5618 | 115.1093 | 123.555 | 3.3508 | 123.6374 | 85.9909 | -0.27924 | 123.555 | 3.3508 | 85.9909 | 115.1093 | 123.6374 | -123.88 | -123.8159
5487.7344 | 123.6923 | -61.4136 | 62.1826 | 0.03685 | 0.019228 | 0.012986 | 0.01766 | 0.061957 | -0.0018285 | 0.079049 | -57.9758 | 62.1918 | -61.7432 | -61.6241 | 53.7094 | 24.6094 | 8.4 | 7.9239 | 62.1964 | -61.7386 | -0.32959 | 0.009155 | 3.4378 | -0.21057 | -8.4732 | -0.32501 | 0.013733 | 3.7674 | 69.8135 | 69.3375 | 115.123 | 123.6053 | 3.4378 | 123.6099 | 86.0229 | -0.32501 | 123.6053 | 3.4378 | 86.0229 | 115.123 | 123.6099 | -123.9258 | -123.9212
5488.7188 | 123.7747 | -61.3815 | 62.1506 | -0.21492 | 0.013888 | 0.010209 | 0.010183 | 0.060462 | -0.0022559 | 0.080117 | -57.9483 | 62.1185 | -61.7065 | -61.5326 | 53.7781 | 24.7055 | 8.313 | 8.0658 | 62.1918 | -61.6745 | -0.32501 | -0.032044 | 3.4332 | -0.15106 | -8.3725 | -0.29297 | 0.041198 | 3.7582 | 69.6945 | 69.4473 | 115.1596 | 123.5001 | 3.4332 | 123.5733 | 86.087 | -0.29297 | 123.5001 | 3.4332 | 86.087 | 115.1596 | 123.5733 | -123.8571 | -123.8251
5489.7188 | 123.6969 | -61.4182 | 62.1826 | -0.22255 | 0.015383 | 0.013841 | 0.011251 | 0.05918 | -0.0022559 | 0.080758 | -57.9803 | 62.1597 | -61.7111 | -61.5738 | 53.7415 | 24.646 | 8.3679 | 7.9239 | 62.178 | -61.702 | -0.29297 | -0.022888 | 3.4378 | -0.15564 | -8.4412 | -0.28381 | -0.004577 | 3.7308 | 69.7861 | 69.342 | 115.1596 | 123.5779 | 3.4378 | 123.5962 | 86.0641 | -0.28381 | 123.5779 | 3.4378 | 86.0641 | 115.1596 | 123.5962 | -123.8937 | -123.8846
5490.7188 | 123.7106 | -61.3724 | 62.1918 | -0.28358 | 0.016665 | 0.0087138 | 0.011892 | 0.058753 | 0.00030767 | 0.079476 | -57.9849 | 62.1552 | -61.702 | -61.5646 | 53.7186 | 24.646 | 8.3725 | 7.9788 | 62.1918 | -61.6791 | -0.32959 | -0.036621 | 3.3875 | -0.19226 | -8.4732 | -0.3067 | 0 | 3.717 | 69.7449 | 69.3512 | 115.0909 | 123.5275 | 3.3875 | 123.5641 | 86.0184 | -0.3067 | 123.5275 | 3.3875 | 86.0184 | 115.0909 | 123.5641 | -123.8937 | -123.8708
5491.7188 | 123.7564 | -61.4136 | 62.178 | -0.28358 | 0.014315 | 0.011704 | 0.011038 | 0.058753 | -0.0028967 | 0.079049 | -57.9529 | 62.1323 | -61.6974 | -61.5601 | 53.7689 | 24.7192 | 8.3633 | 8.0017 | 62.178 | -61.702 | -0.28381 | -0.045777 | 3.4607 | -0.14649 | -8.4091 | -0.28839 | 0 | 3.7445 | 69.7769 | 69.4153 | 115.1825 | 123.5458 | 3.4607 | 123.5916 | 86.1328 | -0.28839 | 123.5458 | 3.4607 | 86.1328 | 115.1825 | 123.5916 | -123.8754 | -123.88
5492.7188 | 123.6877 | -61.4044 | 62.1872 | -0.2607 | 0.015597 | 0.01085 | 0.01531 | 0.057044 | -0.0014013 | 0.078622 | -58.0215 | 62.1597 | -61.7157 | -61.5829 | 53.714 | 24.678 | 8.4366 | 7.9697 | 62.2055 | -61.734 | -0.31128 | -0.027466 | 3.3829 | -0.17853 | -8.4732 | -0.32959 | 0.01831 | 3.6942 | 69.841 | 69.3741 | 115.1184 | 123.5641 | 3.3829 | 123.6099 | 86.0825 | -0.32959 | 123.5641 | 3.3829 | 86.0825 | 115.1184 | 123.6099 | -123.9029 | -123.9212
5493.7188 | 123.7198 | -61.3907 | 62.2101 | -0.2607 | 0.016451 | 0.011277 | 0.014883 | 0.058112 | -0.0016149 | 0.078408 | -57.9987 | 62.178 | -61.7111 | -61.6058 | 53.6865 | 24.6918 | 8.4503 | 7.9971 | 62.178 | -61.7111 | -0.32043 | -0.032043 | 3.392 | -0.21515 | -8.5236 | -0.32043 | -0.032043 | 3.7125 | 69.841 | 69.3878 | 115.0772 | 123.5687 | 3.392 | 123.5687 | 86.0825 | -0.32043 | 123.5687 | 3.392 | 86.0825 | 115.0772 | 123.5687 | -123.9212 | -123.9212
5494.7188 | 123.793 | -61.3724 | 62.1552 | -0.23018 | 0.015597 | 0.011491 | 0.013815 | 0.058539 | 0.00073487 | 0.078835 | -57.9254 | 62.1094 | -61.6882 | -61.5189 | 53.7598 | 24.7559 | 8.3771 | 8.0978 | 62.146 | -61.6699 | -0.31586 | -0.045776 | 3.447 | -0.14648 | -8.3954 | -0.29755 | -0.009155 | 3.7628 | 69.7494 | 69.4702 | 115.1321 | 123.4818 | 3.447 | 123.5184 | 86.1282 | -0.29755 | 123.4818 | 3.447 | 86.1282 | 115.1321 | 123.5184 | -123.8434 | -123.8251
5495.7188 | 123.8022 | -61.3586 | 62.1643 | -0.22255 | 0.016238 | 0.010423 | 0.012533 | 0.058112 | 9.4068e-05 | 0.078622 | -57.9117 | 62.1277 | -61.7111 | -61.5051 | 53.746 | 24.7101 | 8.3084 | 8.0795 | 62.1414 | -61.6928 | -0.35248 | -0.036621 | 3.447 | -0.14648 | -8.4183 | -0.33417 | -0.022889 | 3.7994 | 69.6671 | 69.4382 | 115.1047 | 123.4863 | 3.447 | 123.5001 | 86.0687 | -0.33417 | 123.4863 | 3.447 | 86.0687 | 115.1047 | 123.5001 | -123.8754 | -123.8571
5496.7188 | 123.7289 | -61.3861 | 62.1872 | -0.37514 | 0.016238 | 0.0087138 | 0.014456 | 0.057685 | -0.0016149 | 0.079904 | -57.9483 | 62.1506 | -61.7203 | -61.5738 | 53.6591 | 24.6506 | 8.4183 | 7.9651 | 62.1872 | -61.7065 | -0.33417 | -0.036621 | 3.4378 | -0.18768 | -8.5281 | -0.32044 | 0 | 3.772 | 69.8044 | 69.3512 | 115.0452 | 123.5367 | 3.4378 | 123.5733 | 86.0367 | -0.32044 | 123.5367 | 3.4378 | 86.0367 | 115.0452 | 123.5733 | -123.9075 | -123.8937
5497.9844 | 123.7152 | -61.409 | 62.1872 | -0.13863 | 0.017519 | 0.012773 | 0.015524 | 0.057471 | -0.0018285 | 0.075845 | -57.9391 | 62.1918 | -61.7065 | -61.5921 | 53.6041 | 24.5865 | 8.4274 | 7.9926 | 62.2055 | -61.734 | -0.29755 | 0.004577 | 3.4698 | -0.1831 | -8.5831 | -0.32501 | 0.01831 | 3.7674 | 69.8364 | 69.4016 | 115.0131 | 123.6008 | 3.4698 | 123.6145 | 85.9955 | -0.32501 | 123.6008 | 3.4698 | 85.9955 | 115.0131 | 123.6145 | -123.8937 | -123.9212
5499 | 123.7793 | -61.3724 | 62.1506 | 0.45647 | 0.016878 | 0.012132 | 0.0091152 | 0.060248 | 0.00030767 | 0.081826 | -57.962 | 62.1277 | -61.7432 | -61.5509 | 53.6774 | 24.6963 | 8.2809 | 8.0475 | 62.1277 | -61.7386 | -0.37079 | -0.022888 | 3.4103 | -0.17853 | -8.4732 | -0.36621 | -0.022888 | 3.7811 | 69.6533 | 69.4199 | 115.0497 | 123.5001 | 3.4103 | 123.5001 | 86.0687 | -0.36621 | 123.5001 | 3.4103 | 86.0687 | 115.0497 | 123.5001 | -123.8937 | -123.8892
5500.1562 | 123.7244 | -61.3632 | 62.1918 | -0.26833 | 0.016024 | 0.009141 | 0.013174 | 0.058753 | -0.00076053 | 0.080331 | -57.9025 | 62.1323 | -61.7065 | -61.5372 | 53.6682 | 24.6963 | 8.3908 | 8.0933 | 62.178 | -61.6928 | -0.34332 | -0.059509 | 3.4607 | -0.17395 | -8.5236 | -0.32959 | -0.013732 | 3.804 | 69.754 | 69.4565 | 115.0314 | 123.4955 | 3.4607 | 123.5413 | 86.0596 | -0.32959 | 123.4955 | 3.4607 | 86.0596 | 115.0314 | 123.5413 | -123.8983 | -123.8846
5501.0938 | 123.7152 | -61.3953 | 62.1552 | -0.039444 | 0.016024 | 0.013413 | 0.020651 | 0.060889 | -0.0016149 | 0.078195 | -57.8934 | 62.178 | -61.7249 | -61.5601 | 53.6224 | 24.6735 | 8.313 | 7.9605 | 62.1597 | -61.7523 | -0.32959 | 0.022889 | 3.5019 | -0.1648 | -8.5327 | -0.35706 | 0.004578 | 3.8315 | 69.7083 | 69.3558 | 115.0177 | 123.5733 | 3.5019 | 123.555 | 86.0687 | -0.35706 | 123.5733 | 3.5019 | 86.0687 | 115.0177 | 123.555 | -123.88 | -123.9075
5501.9688 | 123.7564 | -61.4365 | 62.1185 | 0.16655 | 0.020937 | 0.015336 | 0.01766 | 0.06153 | -0.0016149 | 0.081399 | -57.9666 | 62.1826 | -61.7386 | -61.6241 | 53.5583 | 24.6506 | 8.2306 | 7.8781 | 62.1552 | -61.734 | -0.30212 | 0.064087 | 3.4698 | -0.18768 | -8.5602 | -0.29755 | 0.036621 | 3.772 | 69.6671 | 69.3146 | 114.9948 | 123.6191 | 3.4698 | 123.5916 | 86.087 | -0.29755 | 123.6191 | 3.4698 | 86.087 | 114.9948 | 123.5916 | -123.8571 | -123.8525
5504.0156 | 123.7152 | -61.3998 | 62.1735 | -0.23781 | 0.017519 | 0.011918 | 0.013601 | 0.060889 | -0.0016149 | 0.078195 | -57.9529 | 62.1964 | -61.7157 | -61.5921 | 53.5858 | 24.5773 | 8.4137 | 7.988 | 62.1964 | -61.7249 | -0.31586 | 0.022888 | 3.447 | -0.19226 | -8.5876 | -0.32501 | 0.022888 | 3.7628 | 69.8135 | 69.3878 | 114.9857 | 123.5962 | 3.447 | 123.5962 | 85.9772 | -0.32501 | 123.5962 | 3.447 | 85.9772 | 114.9857 | 123.5962 | -123.8892 | -123.8983
5504.9219 | 123.7839 | -61.409 | 62.1323 | -0.77187 | 0.013247 | 0.0082864 | 0.0089016 | 0.05918 | -0.00033333 | 0.080758 | -58.0719 | 62.0865 | -61.7386 | -61.5738 | 53.5858 | 24.6872 | 8.2901 | 8.0566 | 62.1506 | -61.702 | -0.32959 | -0.045776 | 3.3371 | -0.16479 | -8.5464 | -0.29297 | 0.018311 | 3.6667 | 69.6991 | 69.4656 | 114.9948 | 123.4955 | 3.3371 | 123.5596 | 86.0962 | -0.29297 | 123.4955 | 3.3371 | 86.0962 | 114.9948 | 123.5596 | -123.8708 | -123.8342
5505.4844 | 123.6923 | -61.409 | 62.1826 | -0.1844 | 0.017092 | 0.0093546 | 0.014456 | 0.058753 | -0.0024695 | 0.07734 | -57.9483 | 62.1506 | -61.7203 | -61.4273 | 53.7735 | 24.5819 | 8.2993 | 8.0063 | 62.2147 | -61.6928 | -0.31128 | -0.032043 | 3.4607 | -0.01831 | -8.4091 | -0.28381 | 0.032044 | 3.772 | 69.7083 | 69.4153 | 115.1825 | 123.5596 | 3.4607 | 123.6237 | 85.9909 | -0.28381 | 123.5596 | 3.4607 | 85.9909 | 115.1825 | 123.6237 | -123.9029 | -123.8754
5506.4062 | 123.7839 | -61.3678 | 62.0956 | 0.052109 | 0.016665 | 0.0093546 | 0.0099698 | 0.058966 | 9.4068e-05 | 0.080331 | -57.9575 | 62.0682 | -61.7249 | -61.5784 | 53.5995 | 24.6368 | 8.2901 | 8.0658 | 62.1552 | -61.6653 | -0.35706 | -0.027466 | 3.4103 | -0.21057 | -8.4961 | -0.29755 | 0.059509 | 3.7674 | 69.6579 | 69.4336 | 114.9673 | 123.436 | 3.4103 | 123.5229 | 86.0046 | -0.29755 | 123.436 | 3.4103 | 86.0046 | 114.9673 | 123.5229 | -123.8205 | -123.761
5510.6094 | 123.7015 | -61.4365 | 62.1277 | 0.18944 | 0.01816 | 0.013413 | 0.019156 | 0.060462 | -0.00033333 | 0.080758 | -57.9163 | 62.1643 | -61.7203 | -61.6058 | 53.5034 | 24.5636 | 8.4412 | 8.0017 | 62.1597 | -61.7615 | -0.28381 | 0.036621 | 3.5202 | -0.16937 | -8.6243 | -0.32501 | 0.032043 | 3.804 | 69.8776 | 69.4382 | 114.9399 | 123.6008 | 3.5202 | 123.5962 | 86.0001 | -0.32501 | 123.6008 | 3.5202 | 86.0001 | 114.9399 | 123.5962 | -123.848 | -123.8892
5511.1406 | 123.7244 | -61.3998 | 62.1597 | -0.031814 | 0.017306 | 0.016618 | 0.019583 | 0.063239 | -0.0018285 | 0.08204 | -57.8522 | 62.1918 | -61.7249 | -61.5784 | 53.5034 | 24.5544 | 8.4869 | 8.0383 | 62.1552 | -61.734 | -0.32501 | 0.032043 | 3.5477 | -0.17853 | -8.6563 | -0.33417 | -0.004578 | 3.8727 | 69.8868 | 69.4382 | 114.9033 | 123.5916 | 3.5477 | 123.555 | 85.9543 | -0.33417 | 123.5916 | 3.5477 | 85.9543 | 114.9033 | 123.555 | -123.8846 | -123.8937
5511.7188 | 123.7518 | -61.3586 | 62.1643 | -0.20729 | 0.014956 | 0.0087138 | 0.010183 | 0.060248 | -0.0011877 | 0.079904 | -57.8751 | 62.1597 | -61.6974 | -61.5189 | 53.595 | 24.6826 | 8.5144 | 8.1848 | 62.1735 | -61.6379 | -0.33874 | -0.004578 | 3.4836 | -0.16022 | -8.5693 | -0.27923 | 0.009155 | 3.8223 | 69.873 | 69.5435 | 114.9536 | 123.5184 | 3.4836 | 123.5321 | 86.0413 | -0.27923 | 123.5184 | 3.4836 | 86.0413 | 114.9536 | 123.5321 | -123.8617 | -123.8022
5512.7188 | 123.8068 | -61.3312 | 62.1506 | -0.15388 | 0.017092 | 0.0095682 | 0.011892 | 0.059607 | -0.0024695 | 0.078408 | -57.8476 | 62.1231 | -61.702 | -61.5051 | 53.5721 | 24.6826 | 8.4457 | 8.1985 | 62.1506 | -61.6241 | -0.37079 | -0.027466 | 3.4836 | -0.17395 | -8.5785 | -0.29297 | 0 | 3.8544 | 69.7769 | 69.5297 | 114.9033 | 123.4543 | 3.4836 | 123.4818 | 86.0138 | -0.29297 | 123.4543 | 3.4836 | 86.0138 | 114.9033 | 123.4818 | -123.8525 | -123.7747
5513.7188 | 123.7015 | -61.3998 | 62.1872 | -0.23018 | 0.01581 | 0.007432 | 0.01531 | 0.057898 | -0.00054693 | 0.081185 | -57.8522 | 62.1277 | -61.7065 | -61.5509 | 53.5217 | 24.614 | 8.5556 | 8.1528 | 62.1689 | -61.6791 | -0.3067 | -0.059509 | 3.5477 | -0.15106 | -8.6655 | -0.27924 | -0.018311 | 3.8544 | 69.9554 | 69.5526 | 114.9216 | 123.5275 | 3.5477 | 123.5687 | 86.0138 | -0.27924 | 123.5275 | 3.5477 | 86.0138 | 114.9216 | 123.5687 | -123.8937 | -123.8663
5514.7188 | 123.7656 | -61.3632 | 62.1643 | -0.2607 | 0.014529 | 0.015122 | 0.01296 | 0.059607 | -0.00076053 | 0.078195 | -57.8293 | 62.1231 | -61.6928 | -61.5372 | 53.5263 | 24.6689 | 8.5144 | 8.1985 | 62.146 | -61.6653 | -0.32959 | -0.041199 | 3.5339 | -0.17395 | -8.638 | -0.30212 | -0.018311 | 3.8635 | 69.8776 | 69.5618 | 114.8895 | 123.4863 | 3.5339 | 123.5092 | 86.0321 | -0.30212 | 123.4863 | 3.5339 | 86.0321 | 114.8895 | 123.5092 | -123.8571 | -123.8297
5515.7188 | 123.8159 | -61.3724 | 62.1323 | -0.14626 | 0.016451 | 0.0097818 | 0.0084744 | 0.058753 | 0.00052127 | 0.080544 | -57.8064 | 62.1048 | -61.6928 | -61.5738 | 53.6499 | 24.7238 | 8.3405 | 8.3084 | 62.0819 | -61.647 | -0.32044 | -0.027466 | 3.566 | -0.20142 | -8.4824 | -0.27466 | -0.050354 | 3.8864 | 69.7128 | 69.6808 | 115.0223 | 123.4772 | 3.566 | 123.4543 | 86.0962 | -0.27466 | 123.4772 | 3.566 | 86.0962 | 115.0223 | 123.4543 | -123.8251 | -123.7793
5516.7188 | 123.8525 | -61.3586 | 62.1918 | -0.10811 | 0.014529 | 0.0087138 | 0.01232 | 0.058753 | -0.0039649 | 0.080117 | -57.8064 | 62.0773 | -61.6516 | -61.4914 | 53.5675 | 24.7238 | 8.3679 | 8.226 | 62.0956 | -61.6608 | -0.29297 | -0.11444 | 3.5522 | -0.13275 | -8.6243 | -0.30212 | -0.09613 | 3.8452 | 69.7266 | 69.5847 | 114.9261 | 123.436 | 3.5522 | 123.4543 | 86.0825 | -0.30212 | 123.436 | 3.5522 | 86.0825 | 114.9261 | 123.4543 | -123.8434 | -123.8525
5517.7188 | 123.7381 | -61.3907 | 62.1826 | -0.1844 | 0.018374 | 0.012345 | 0.019156 | 0.059607 | -0.00054693 | 0.080758 | -57.8339 | 62.2055 | -61.7157 | -61.5463 | 53.4668 | 24.6277 | 8.5236 | 8.1802 | 62.1643 | -61.7157 | -0.32501 | 0.022888 | 3.5568 | -0.15564 | -8.7158 | -0.32501 | -0.01831 | 3.8818 | 69.9142 | 69.5709 | 114.8575 | 123.5962 | 3.5568 | 123.555 | 86.0184 | -0.32501 | 123.5962 | 3.5568 | 86.0184 | 114.8575 | 123.555 | -123.8983 | -123.8983
5518.7188 | 123.8251 | -61.3541 | 62.146 | -0.19966 | 0.01346 | 0.012345 | 0.011679 | 0.062598 | -0.00011953 | 0.079904 | -57.7744 | 62.0865 | -61.7111 | -61.4273 | 53.5263 | 24.614 | 8.4641 | 8.3405 | 62.1231 | -61.6287 | -0.35706 | -0.059509 | 3.5797 | -0.073242 | -8.6197 | -0.27466 | -0.022888 | 3.9368 | 69.8181 | 69.6945 | 114.8804 | 123.4406 | 3.5797 | 123.4772 | 85.968 | -0.27466 | 123.4406 | 3.5797 | 85.968 | 114.8804 | 123.4772 | -123.8571 | -123.7747
5519.7188 | 123.7106 | -61.3449 | 62.2009 | -0.12337 | 0.014101 | 0.012345 | 0.0091152 | 0.059394 | 0.00030767 | 0.080544 | -57.7972 | 62.0911 | -61.7249 | -61.4731 | 53.54 | 24.7238 | 8.4045 | 8.2718 | 62.1414 | -61.6653 | -0.37994 | -0.10986 | 3.5477 | -0.12817 | -8.6609 | -0.32043 | -0.05951 | 3.9276 | 69.7495 | 69.6167 | 114.8849 | 123.436 | 3.5477 | 123.4863 | 86.0687 | -0.32043 | 123.436 | 3.5477 | 86.0687 | 114.8849 | 123.4863 | -123.9258 | -123.8663
5520.7188 | 123.8159 | -61.3495 | 62.146 | -1.367 | 0.015169 | 0.010636 | 0.014029 | 0.058112 | 0.00030767 | 0.080117 | -57.8705 | 62.0911 | -61.7111 | -61.4777 | 53.5263 | 24.7467 | 8.4183 | 8.2672 | 62.114 | -61.6425 | -0.36163 | -0.054932 | 3.479 | -0.12817 | -8.6197 | -0.29297 | -0.032043 | 3.8406 | 69.7678 | 69.6167 | 114.8758 | 123.4406 | 3.479 | 123.4634 | 86.0962 | -0.29297 | 123.4406 | 3.479 | 86.0962 | 114.8758 | 123.4634 | -123.8571 | -123.7885
5521.7344 | 123.7152 | -61.3815 | 62.1826 | 0.021591 | 0.019015 | 0.012559 | 0.020224 | 0.060248 | -0.0018285 | 0.080758 | -57.8064 | 62.1826 | -61.7111 | -61.5875 | 53.3752 | 24.614 | 8.5236 | 8.1345 | 62.1643 | -61.7432 | -0.32959 | 0 | 3.5751 | -0.20599 | -8.8074 | -0.36163 | -0.01831 | 3.9047 | 69.9051 | 69.516 | 114.7568 | 123.5641 | 3.5751 | 123.5458 | 85.9955 | -0.36163 | 123.5641 | 3.5751 | 85.9955 | 114.7568 | 123.5458 | -123.8937 | -123.9258
5522.7188 | 123.6694 | -61.4365 | 62.1826 | -0.19966 | 0.017947 | 0.011277 | 0.015524 | 0.05918 | -0.00011953 | 0.077126 | -57.8751 | 62.2055 | -61.7386 | -61.4914 | 53.6407 | 24.5773 | 8.4457 | 8.1436 | 62.1735 | -61.7065 | -0.30212 | 0.022888 | 3.5614 | -0.054932 | -8.5419 | -0.27008 | -0.009155 | 3.8635 | 69.8822 | 69.5801 | 115.0772 | 123.642 | 3.5614 | 123.6099 | 86.0138 | -0.27008 | 123.642 | 3.5614 | 86.0138 | 115.0772 | 123.6099 | -123.9212 | -123.8892
5523.7188 | 123.8113 | -61.3449 | 62.1368 | -0.131 | 0.014315 | 0.011064 | 0.010611 | 0.060248 | 0.00094847 | 0.07969 | -57.8064 | 62.0773 | -61.6974 | -61.496 | 53.5263 | 24.733 | 8.4045 | 8.2764 | 62.1552 | -61.647 | -0.35248 | -0.059509 | 3.5385 | -0.15106 | -8.6105 | -0.30212 | 0.01831 | 3.891 | 69.7495 | 69.6213 | 114.8712 | 123.4222 | 3.5385 | 123.5001 | 86.0779 | -0.30212 | 123.4222 | 3.5385 | 86.0779 | 114.8712 | 123.5001 | -123.8342 | -123.7839
5524.7188 | 123.8342 | -61.3724 | 62.1277 | -0.13863 | 0.013033 | 0.006791 | 0.0097562 | 0.058112 | -0.0028967 | 0.080758 | -57.8064 | 62.1002 | -61.6974 | -61.5097 | 53.4531 | 24.7192 | 8.3862 | 8.2672 | 62.1048 | -61.6837 | -0.32501 | -0.027466 | 3.566 | -0.13733 | -8.6746 | -0.31128 | -0.022889 | 3.891 | 69.7586 | 69.6396 | 114.8254 | 123.4726 | 3.566 | 123.4772 | 86.0916 | -0.31128 | 123.4726 | 3.566 | 86.0916 | 114.8254 | 123.4772 | -123.8251 | -123.8113
5525.7188 | 123.8113 | -61.3678 | 62.1323 | -0.13863 | 0.014529 | 0.011704 | 0.011465 | 0.057685 | -0.0020421 | 0.080117 | -57.811 | 62.0728 | -61.702 | -61.528 | 53.4576 | 24.7101 | 8.4686 | 8.2901 | 62.1002 | -61.6882 | -0.33417 | -0.059509 | 3.5568 | -0.16022 | -8.6746 | -0.32043 | -0.032043 | 3.891 | 69.8364 | 69.6579 | 114.8254 | 123.4406 | 3.5568 | 123.468 | 86.0779 | -0.32043 | 123.4406 | 3.5568 | 86.0779 | 114.8254 | 123.468 | -123.8342 | -123.8205
5526.7188 | 123.7793 | -61.3724 | 62.1689 | -0.20729 | 0.014956 | 0.016404 | 0.015524 | 0.057044 | 0.0013757 | 0.07969 | -57.7652 | 62.1323 | -61.6928 | -61.5234 | 53.4485 | 24.7192 | 8.5556 | 8.3038 | 62.1277 | -61.6608 | -0.32044 | -0.036621 | 3.6072 | -0.15106 | -8.7204 | -0.28839 | -0.041198 | 3.9276 | 69.928 | 69.6762 | 114.8209 | 123.5046 | 3.6072 | 123.5001 | 86.0916 | -0.28839 | 123.5046 | 3.6072 | 86.0916 | 114.8209 | 123.5001 | -123.8617 | -123.8297
5527.7188 | 123.7976 | -61.3403 | 62.1826 | -0.16914 | 0.013033 | 0.014482 | 0.010824 | 0.057685 | -0.00054693 | 0.079904 | -57.7469 | 62.1277 | -61.6837 | -61.5097 | 53.4348 | 24.6597 | 8.5144 | 8.2352 | 62.1185 | -61.6653 | -0.34332 | -0.054931 | 3.5934 | -0.16937 | -8.7479 | -0.32501 | -0.064087 | 3.9368 | 69.8547 | 69.5755 | 114.7751 | 123.468 | 3.5934 | 123.4589 | 86.0001 | -0.32501 | 123.468 | 3.5934 | 86.0001 | 114.7751 | 123.4589 | -123.8663 | -123.848
5528.7188 | 123.8022 | -61.3632 | 62.1552 | -0.031814 | 0.015597 | 0.01555 | 0.0097562 | 0.058539 | 9.4068e-05 | 0.080972 | -57.7927 | 62.0773 | -61.6928 | -61.5051 | 53.4164 | 24.7101 | 8.3954 | 8.2123 | 62.0956 | -61.6425 | -0.32959 | -0.077819 | 3.5706 | -0.14191 | -8.7387 | -0.27924 | -0.059509 | 3.9001 | 69.7586 | 69.5755 | 114.7797 | 123.4406 | 3.5706 | 123.4589 | 86.0733 | -0.27924 | 123.4406 | 3.5706 | 86.0733 | 114.7797 | 123.4589 | -123.848 | -123.7976
5529.7188 | 123.7701 | -61.3861 | 62.1323 | 0.052109 | 0.017519 | 0.013413 | 0.011679 | 0.057471 | -0.0014013 | 0.079904 | -57.605 | 62.114 | -61.6882 | -61.5463 | 53.3478 | 24.6689 | 8.432 | 8.1482 | 62.1231 | -61.6745 | -0.30212 | -0.01831 | 3.7811 | -0.16022 | -8.7845 | -0.28839 | -0.009155 | 4.0833 | 69.8181 | 69.5343 | 114.7339 | 123.5001 | 3.7811 | 123.5092 | 86.055 | -0.28839 | 123.5001 | 3.7811 | 86.055 | 114.7339 | 123.5092 | -123.8205 | -123.8068
5530.7188 | 123.8159 | -61.3724 | 62.1277 | -0.047073 | 0.014956 | 0.012132 | 0.012533 | 0.056617 | 0.0015893 | 0.080758 | -57.8018 | 62.0865 | -61.7111 | -61.5509 | 53.4256 | 24.6826 | 8.4091 | 8.1802 | 62.1185 | -61.6882 | -0.33875 | -0.041199 | 3.5706 | -0.17853 | -8.7021 | -0.31586 | -0.009156 | 3.9093 | 69.7815 | 69.5526 | 114.798 | 123.4589 | 3.5706 | 123.4909 | 86.055 | -0.31586 | 123.4589 | 3.5706 | 86.055 | 114.798 | 123.4909 | -123.8388 | -123.8159
5531.7188 | 123.6557 | -61.409 | 62.1964 | -0.20729 | 0.019015 | 0.014054 | 0.014669 | 0.058325 | -0.0011877 | 0.080758 | -57.7927 | 62.1826 | -61.7386 | -61.4502 | 53.5767 | 24.5956 | 8.4641 | 8.194 | 62.1735 | -61.7065 | -0.32959 | -0.013733 | 3.6163 | -0.041198 | -8.6197 | -0.29755 | -0.022888 | 3.9459 | 69.873 | 69.603 | 114.9857 | 123.5916 | 3.6163 | 123.5825 | 86.0046 | -0.29755 | 123.5916 | 3.6163 | 86.0046 | 114.9857 | 123.5825 | -123.9349 | -123.9029
5532.7188 | 123.8342 | -61.3449 | 62.1277 | -0.131 | 0.013888 | 0.0089274 | 0.012106 | 0.058753 | -0.0011877 | 0.080331 | -57.7423 | 62.0728 | -61.702 | -61.4777 | 53.4576 | 24.7467 | 8.4183 | 8.345 | 62.1323 | -61.6425 | -0.35706 | -0.054932 | 3.6026 | -0.13275 | -8.67 | -0.29755 | 0.004577 | 3.9597 | 69.7632 | 69.6899 | 114.8026 | 123.4177 | 3.6026 | 123.4772 | 86.0916 | -0.29755 | 123.4177 | 3.6026 | 86.0916 | 114.8026 | 123.4772 | -123.8297 | -123.7701
5533.7188 | 123.7839 | -61.3678 | 62.1597 | 0.090256 | 0.01346 | 0.016191 | 0.010824 | 0.056617 | 0.0020167 | 0.079476 | -57.7835 | 62.1094 | -61.7157 | -61.5601 | 53.3981 | 24.6963 | 8.4732 | 8.2764 | 62.1277 | -61.6562 | -0.3479 | -0.050354 | 3.5843 | -0.19226 | -8.7616 | -0.28839 | -0.032043 | 3.9322 | 69.841 | 69.6442 | 114.7659 | 123.4772 | 3.5843 | 123.4955 | 86.0641 | -0.28839 | 123.4772 | 3.5843 | 86.0641 | 114.7659 | 123.4955 | -123.8754 | -123.8159
5534.7188 | 123.793 | -61.3861 | 62.1185 | 0.18944 | 0.013247 | 0.011491 | 0.0095424 | 0.054908 | 0.00030767 | 0.080544 | -57.8064 | 62.0773 | -61.7157 | -61.5463 | 53.389 | 24.7467 | 8.4778 | 8.2489 | 62.1002 | -61.6745 | -0.32959 | -0.041198 | 3.5797 | -0.16022 | -8.7296 | -0.28839 | -0.01831 | 3.9093 | 69.8639 | 69.635 | 114.7751 | 123.4634 | 3.5797 | 123.4863 | 86.1328 | -0.28839 | 123.4634 | 3.5797 | 86.1328 | 114.7751 | 123.4863 | -123.8342 | -123.793
5535.7188 | 123.7518 | -61.3861 | 62.1277 | -0.0089264 | 0.017519 | 0.012986 | 0.013601 | 0.058112 | -0.00054693 | 0.081399 | -57.7881 | 62.0865 | -61.7294 | -61.528 | 53.3295 | 24.6872 | 8.4595 | 8.2397 | 62.0819 | -61.6882 | -0.34332 | -0.041199 | 3.598 | -0.14191 | -8.7982 | -0.30212 | -0.045777 | 3.9413 | 69.8456 | 69.6259 | 114.7156 | 123.4726 | 3.598 | 123.468 | 86.0733 | -0.30212 | 123.4726 | 3.598 | 86.0733 | 114.7156 | 123.468 | -123.8571 | -123.8159
5536.7188 | 123.7656 | -61.3724 | 62.1094 | 0.16655 | 0.014529 | 0.0093546 | 0.014029 | 0.060034 | 0.0011621 | 0.081826 | -57.7423 | 62.0682 | -61.7294 | -61.5555 | 53.3615 | 24.7833 | 8.4412 | 8.2626 | 62.0911 | -61.6791 | -0.35706 | -0.041199 | 3.6301 | -0.18311 | -8.7479 | -0.3067 | -0.018311 | 3.9871 | 69.8135 | 69.635 | 114.7339 | 123.4406 | 3.6301 | 123.4634 | 86.1557 | -0.3067 | 123.4406 | 3.6301 | 86.1557 | 114.7339 | 123.4634 | -123.8388 | -123.7885
5537.7188 | 123.8022 | -61.3678 | 62.1597 | -0.08522 | 0.016451 | 0.012345 | 0.011038 | 0.056189 | -0.00033333 | 0.079904 | -57.7606 | 62.0773 | -61.6928 | -61.5005 | 53.4027 | 24.8154 | 8.4412 | 8.3084 | 62.1048 | -61.647 | -0.32501 | -0.082397 | 3.6072 | -0.13275 | -8.757 | -0.27924 | -0.054932 | 3.9322 | 69.809 | 69.6762 | 114.7705 | 123.4451 | 3.6072 | 123.4726 | 86.1832 | -0.27924 | 123.4451 | 3.6072 | 86.1832 | 114.7705 | 123.4726 | -123.8525 | -123.8068
5538.7188 | 123.7564 | -61.3998 | 62.114 | 0.18181 | 0.017947 | 0.013841 | 0.014883 | 0.056617 | -0.00097413 | 0.080544 | -57.756 | 62.0728 | -61.7203 | -61.5692 | 53.3112 | 24.765 | 8.4595 | 8.2718 | 62.0911 | -61.6928 | -0.32043 | -0.041199 | 3.6438 | -0.16937 | -8.8028 | -0.29297 | -0.022889 | 3.9642 | 69.8593 | 69.6716 | 114.711 | 123.4726 | 3.6438 | 123.4909 | 86.1649 | -0.29297 | 123.4726 | 3.6438 | 86.1649 | 114.711 | 123.4909 | -123.8342 | -123.8068
5539.7188 | 123.761 | -61.3907 | 62.1185 | 0.11314 | 0.015169 | 0.015763 | 0.014242 | 0.057898 | -0.00054693 | 0.080331 | -57.7423 | 62.0773 | -61.7249 | -61.5417 | 53.2928 | 24.7604 | 8.432 | 8.2809 | 62.0956 | -61.6745 | -0.33417 | -0.041198 | 3.6484 | -0.15106 | -8.8257 | -0.28381 | -0.022888 | 3.9825 | 69.8227 | 69.6716 | 114.6835 | 123.468 | 3.6484 | 123.4863 | 86.1511 | -0.28381 | 123.468 | 3.6484 | 86.1511 | 114.6835 | 123.4863 | -123.8434 | -123.793
5540.7188 | 123.8068 | -61.3678 | 62.0865 | 0.17418 | 0.015597 | 0.012773 | 0.01531 | 0.061103 | -0.00011953 | 0.08204 | -57.6965 | 62.0819 | -61.7249 | -61.5189 | 53.3478 | 24.7742 | 8.432 | 8.2947 | 62.059 | -61.6974 | -0.35706 | -0.004578 | 3.6713 | -0.15106 | -8.7387 | -0.32959 | -0.027466 | 4.0283 | 69.7998 | 69.6625 | 114.7156 | 123.4497 | 3.6713 | 123.4268 | 86.142 | -0.32959 | 123.4497 | 3.6713 | 86.142 | 114.7156 | 123.4268 | -123.8113 | -123.7839
5541.7188 | 123.7518 | -61.3586 | 62.1002 | 0.13603 | 0.016665 | 0.015977 | 0.011892 | 0.058325 | 0.00052127 | 0.080117 | -57.7469 | 62.0728 | -61.7294 | -61.5646 | 53.27 | 24.678 | 8.5281 | 8.2993 | 62.0956 | -61.6837 | -0.37079 | -0.027466 | 3.6118 | -0.20599 | -8.8303 | -0.32501 | -0.004578 | 3.9825 | 69.8868 | 69.6579 | 114.6286 | 123.4314 | 3.6118 | 123.4543 | 86.0367 | -0.32501 | 123.4314 | 3.6118 | 86.0367 | 114.6286 | 123.4543 | -123.8297 | -123.7839
5542.7188 | 123.8525 | -61.3129 | 62.1597 | -0.21492 | 0.016238 | 0.011277 | 0.011251 | 0.058966 | -0.0033239 | 0.079263 | -57.6782 | 62.0682 | -61.6928 | -61.4639 | 53.3615 | 24.7421 | 8.5602 | 8.4549 | 62.1094 | -61.647 | -0.37994 | -0.091553 | 3.6346 | -0.15106 | -8.7982 | -0.33417 | -0.050354 | 4.0146 | 69.873 | 69.7678 | 114.6744 | 123.381 | 3.6346 | 123.4222 | 86.055 | -0.33417 | 123.381 | 3.6346 | 86.055 | 114.6744 | 123.4222 | -123.8525 | -123.8068
5543.7188 | 123.7976 | -61.3449 | 62.1185 | 0.17418 | 0.017306 | 0.011918 | 0.015738 | 0.05918 | 0.0020167 | 0.083108 | -57.6874 | 62.0819 | -61.702 | -61.4319 | 53.4851 | 24.7559 | 8.3954 | 8.4045 | 62.0865 | -61.6745 | -0.35706 | -0.036621 | 3.6575 | -0.086975 | -8.6334 | -0.32959 | -0.032043 | 4.0146 | 69.7403 | 69.7495 | 114.83 | 123.4268 | 3.6575 | 123.4314 | 86.1008 | -0.32959 | 123.4268 | 3.6575 | 86.1008 | 114.83 | 123.4314 | -123.8205 | -123.793
5544.7188 | 123.8022 | -61.3953 | 62.114 | 0.097885 | 0.016238 | 0.009141 | 0.015951 | 0.058325 | -0.00054693 | 0.080758 | -57.6828 | 62.0819 | -61.7249 | -61.5143 | 53.2654 | 24.6826 | 8.4595 | 8.3862 | 62.0865 | -61.6608 | -0.32959 | -0.032044 | 3.7125 | -0.11902 | -8.8486 | -0.2655 | -0.027466 | 4.0421 | 69.8547 | 69.7815 | 114.6606 | 123.4772 | 3.7125 | 123.4818 | 86.0779 | -0.2655 | 123.4772 | 3.7125 | 86.0779 | 114.6606 | 123.4818 | -123.8388 | -123.7747
5545.7188 | 123.8205 | -61.3678 | 62.0911 | -1.4204 | 0.015597 | 0.014695 | 0.015738 | 0.060034 | -0.0018285 | 0.080972 | -57.724 | 62.114 | -61.702 | -61.5372 | 53.27 | 24.6597 | 8.4183 | 8.3817 | 62.0682 | -61.7065 | -0.33417 | 0.022889 | 3.6438 | -0.16937 | -8.8211 | -0.33875 | -0.022888 | 3.978 | 69.7861 | 69.7495 | 114.6378 | 123.4818 | 3.6438 | 123.436 | 86.0275 | -0.33875 | 123.4818 | 3.6438 | 86.0275 | 114.6378 | 123.436 | -123.793 | -123.7976
5546.7188 | 123.8113 | -61.3724 | 62.114 | 0.19707 | 0.018587 | 0.016831 | 0.017233 | 0.061743 | 0.00052127 | 0.083322 | -57.6736 | 62.0911 | -61.7203 | -61.7294 | 53.2242 | 24.8154 | 8.4869 | 8.3771 | 62.0819 | -61.7065 | -0.3479 | -0.022889 | 3.6987 | -0.35706 | -8.8898 | -0.33417 | -0.032044 | 4.0466 | 69.8593 | 69.7494 | 114.5966 | 123.4634 | 3.6987 | 123.4543 | 86.1877 | -0.33417 | 123.4634 | 3.6987 | 86.1877 | 114.5966 | 123.4543 | -123.8342 | -123.8205
5547.7188 | 123.8205 | -61.3541 | 62.1506 | -0.0089264 | 0.01581 | 0.014482 | 0.0095424 | 0.055548 | -0.0018285 | 0.082467 | -57.7377 | 62.0819 | -61.7294 | -61.528 | 53.2745 | 24.614 | 8.5693 | 8.4412 | 62.1002 | -61.647 | -0.37537 | -0.068665 | 3.6163 | -0.17395 | -8.876 | -0.29297 | -0.050354 | 3.9917 | 69.9234 | 69.7952 | 114.6286 | 123.436 | 3.6163 | 123.4543 | 85.968 | -0.29297 | 123.436 | 3.6163 | 85.968 | 114.6286 | 123.4543 | -123.88 | -123.7976
5548.7188 | 123.7976 | -61.3724 | 62.1185 | 0.99815 | 0.017306 | 0.014482 | 0.015738 | 0.05918 | 0.00073487 | 0.082681 | -57.6233 | 62.0911 | -61.6928 | -61.5234 | 53.2471 | 24.6506 | 8.5007 | 8.4595 | 62.0544 | -61.7111 | -0.32044 | -0.027466 | 3.7491 | -0.15106 | -8.8715 | -0.33875 | -0.064087 | 4.0695 | 69.873 | 69.8318 | 114.6194 | 123.4634 | 3.7491 | 123.4268 | 86.0229 | -0.33875 | 123.4634 | 3.7491 | 86.0229 | 114.6194 | 123.4268 | -123.8113 | -123.8297
5549.7188 | 123.7793 | -61.3815 | 62.1002 | 0.2581 | 0.018587 | 0.015336 | 0.018301 | 0.060675 | -0.00076053 | 0.080544 | -57.7057 | 62.1185 | -61.7294 | -61.5555 | 53.2333 | 24.6506 | 8.5831 | 8.4091 | 62.0819 | -61.6928 | -0.3479 | 0.01831 | 3.6758 | -0.17395 | -8.8669 | -0.31128 | -0.018311 | 4.0237 | 69.9646 | 69.7906 | 114.6149 | 123.5001 | 3.6758 | 123.4634 | 86.0321 | -0.31128 | 123.5001 | 3.6758 | 86.0321 | 114.6149 | 123.4634 | -123.8297 | -123.793
5550.7188 | 123.7427 | -61.3724 | 62.0911 | 0.21996 | 0.016451 | 0.018327 | 0.019369 | 0.058966 | 9.4068e-05 | 0.079263 | -57.7148 | 62.1277 | -61.734 | -61.5692 | 53.183 | 24.614 | 8.551 | 8.3267 | 62.1185 | -61.6974 | -0.36163 | 0.036622 | 3.6575 | -0.19684 | -8.9081 | -0.32501 | 0.027466 | 4.0192 | 69.9234 | 69.6991 | 114.5554 | 123.5001 | 3.6575 | 123.4909 | 85.9863 | -0.32501 | 123.5001 | 3.6575 | 85.9863 | 114.5554 | 123.4909 | -123.8251 | -123.7885
5551.7188 | 123.8022 | -61.3541 | 62.1048 | 0.25047 | 0.02051 | 0.019608 | 0.017019 | 0.05918 | -0.0018285 | 0.080972 | -57.6691 | 62.114 | -61.7111 | -61.4914 | 53.2471 | 24.6872 | 8.4824 | 8.3405 | 62.0865 | -61.6791 | -0.35706 | 0.009156 | 3.685 | -0.13733 | -8.8577 | -0.32501 | -0.01831 | 4.0421 | 69.8364 | 69.6945 | 114.6011 | 123.468 | 3.685 | 123.4406 | 86.0413 | -0.32501 | 123.468 | 3.685 | 86.0413 | 114.6011 | 123.4406 | -123.8159 | -123.7839
5552.7188 | 123.7701 | -61.3586 | 62.1231 | 0.074997 | 0.016451 | 0.017259 | 0.011465 | 0.058753 | -0.0018285 | 0.082253 | -57.7286 | 62.0819 | -61.7157 | -61.5692 | 53.2242 | 24.646 | 8.5739 | 8.3496 | 62.114 | -61.6699 | -0.35706 | -0.041199 | 3.6301 | -0.21057 | -8.8989 | -0.31128 | -0.009155 | 3.9871 | 69.9326 | 69.7083 | 114.5828 | 123.4406 | 3.6301 | 123.4726 | 86.0046 | -0.31128 | 123.4406 | 3.6301 | 86.0046 | 114.5828 | 123.4726 | -123.8388 | -123.793
5553.7188 | 123.7976 | -61.3541 | 62.1094 | 0.2047 | 0.018801 | 0.015122 | 0.018942 | 0.060462 | 9.4068e-05 | 0.080972 | -57.6874 | 62.1506 | -61.7111 | -61.5646 | 53.1921 | 24.6552 | 8.5281 | 8.313 | 62.0819 | -61.7157 | -0.35706 | 0.041199 | 3.6667 | -0.21057 | -8.9172 | -0.36163 | -0.027466 | 4.0237 | 69.8822 | 69.6671 | 114.5462 | 123.5046 | 3.6667 | 123.436 | 86.0092 | -0.36163 | 123.5046 | 3.6667 | 86.0092 | 114.5462 | 123.436 | -123.8205 | -123.8251
5554.7188 | 123.7839 | -61.3998 | 62.1094 | 0.2047 | 0.022219 | 0.017259 | 0.019583 | 0.060675 | -0.00033333 | 0.080972 | -57.6736 | 62.1552 | -61.7249 | -61.5784 | 53.183 | 24.5728 | 8.606 | 8.2993 | 62.1185 | -61.7294 | -0.32501 | 0.045776 | 3.7262 | -0.17853 | -8.9264 | -0.32959 | 0.009155 | 4.0512 | 70.0058 | 69.6991 | 114.5828 | 123.555 | 3.7262 | 123.5184 | 85.9726 | -0.32959 | 123.555 | 3.7262 | 85.9726 | 114.5828 | 123.5184 | -123.8342 | -123.8388
5555.7188 | 123.7793 | -61.3632 | 62.1094 | 0.13603 | 0.019869 | 0.018113 | 0.017233 | 0.060889 | -0.00076053 | 0.080331 | -57.6279 | 62.1185 | -61.7157 | -61.5326 | 53.2379 | 24.6231 | 8.5236 | 8.3084 | 62.0819 | -61.6882 | -0.35248 | 0.009155 | 3.7354 | -0.16937 | -8.8715 | -0.32501 | -0.027466 | 4.0878 | 69.8868 | 69.6716 | 114.6011 | 123.4818 | 3.7354 | 123.4451 | 85.9863 | -0.32501 | 123.4818 | 3.7354 | 85.9863 | 114.6011 | 123.4451 | -123.8251 | -123.7976
5556.7188 | 123.7244 | -61.3998 | 62.114 | 0.17418 | 0.016878 | 0.013627 | 0.017019 | 0.062171 | 0.00073487 | 0.08204 | -57.7057 | 62.1735 | -61.7249 | -61.6104 | 53.1326 | 24.5682 | 8.6655 | 8.2718 | 62.1185 | -61.7157 | -0.32501 | 0.059509 | 3.6942 | -0.21057 | -8.9813 | -0.31586 | 0.004577 | 4.0192 | 70.0653 | 69.6716 | 114.5325 | 123.5733 | 3.6942 | 123.5184 | 85.968 | -0.31586 | 123.5733 | 3.6942 | 85.968 | 114.5325 | 123.5184 | -123.8388 | -123.8297
5557.7188 | 123.7152 | -61.3998 | 62.1094 | 0.18181 | 0.019442 | 0.012986 | 0.01766 | 0.063025 | -0.0011877 | 0.080544 | -57.7103 | 62.1689 | -61.6974 | -61.6196 | 53.1189 | 24.5453 | 8.67 | 8.2855 | 62.1414 | -61.7249 | -0.29755 | 0.059509 | 3.6896 | -0.21973 | -8.9905 | -0.32501 | 0.032043 | 3.9871 | 70.0699 | 69.6854 | 114.5187 | 123.5687 | 3.6896 | 123.5413 | 85.9451 | -0.32501 | 123.5687 | 3.6896 | 85.9451 | 114.5187 | 123.5413 | -123.8068 | -123.8342
5558.7188 | 123.7518 | -61.3907 | 62.1094 | 0.18181 | 0.017092 | 0.014482 | 0.017447 | 0.061957 | -0.00097413 | 0.081826 | -57.6782 | 62.1506 | -61.7294 | -61.5829 | 53.1464 | 24.6277 | 8.638 | 8.4045 | 62.1002 | -61.7249 | -0.33874 | 0.041199 | 3.7125 | -0.19226 | -8.963 | -0.33417 | -0.009155 | 4.0512 | 70.0287 | 69.7952 | 114.537 | 123.5413 | 3.7125 | 123.4909 | 86.0184 | -0.33417 | 123.5413 | 3.7125 | 86.0184 | 114.537 | 123.4909 | -123.8388 | -123.8342
5559.7188 | 123.7564 | -61.409 | 62.1185 | 0.19707 | 0.020296 | 0.020463 | 0.017019 | 0.062171 | 0.0020167 | 0.081399 | -57.6691 | 62.146 | -61.734 | -61.6058 | 53.1097 | 24.6094 | 8.6197 | 8.3176 | 62.1368 | -61.7432 | -0.32501 | 0.027466 | 3.7399 | -0.19684 | -9.0088 | -0.33417 | 0.018311 | 4.0649 | 70.0287 | 69.7266 | 114.5187 | 123.555 | 3.7399 | 123.5458 | 86.0184 | -0.33417 | 123.555 | 3.7399 | 86.0184 | 114.5187 | 123.5458 | -123.8525 | -123.8617
5560.7188 | 123.7747 | -61.4182 | 62.1231 | 0.15129 | 0.01816 | 0.015763 | 0.018087 | 0.06153 | -0.0022559 | 0.083535 | -57.6874 | 62.1643 | -61.734 | -61.6013 | 53.0914 | 24.5911 | 8.6334 | 8.2993 | 62.1231 | -61.7203 | -0.31586 | 0.041199 | 3.7308 | -0.1831 | -9.0317 | -0.30212 | 0 | 4.0466 | 70.0516 | 69.7174 | 114.5096 | 123.5825 | 3.7308 | 123.5413 | 86.0092 | -0.30212 | 123.5825 | 3.7308 | 86.0092 | 114.5096 | 123.5413 | -123.8571 | -123.8434
5561.7188 | 123.8159 | -61.3861 | 62.0819 | 0.2581 | 0.020083 | 0.016404 | 0.016165 | 0.062171 | -0.00097413 | 0.080331 | -57.6279 | 62.1323 | -61.734 | -61.5692 | 53.1876 | 24.6963 | 8.5464 | 8.3771 | 62.1094 | -61.702 | -0.3479 | 0.050354 | 3.7582 | -0.18311 | -8.8943 | -0.31586 | 0.027466 | 4.1061 | 69.9326 | 69.7632 | 114.5737 | 123.5184 | 3.7582 | 123.4955 | 86.0825 | -0.31586 | 123.5184 | 3.7582 | 86.0825 | 114.5737 | 123.4955 | -123.8159 | -123.7839
5562.7188 | 123.793 | -61.3678 | 62.146 | 0.28862 | 0.01581 | 0.014268 | 0.010824 | 0.059394 | 0.0020167 | 0.082467 | -57.6782 | 62.1094 | -61.7203 | -61.5784 | 53.1418 | 24.6963 | 8.6563 | 8.4274 | 62.1002 | -61.6791 | -0.35248 | -0.036621 | 3.6896 | -0.21057 | -9.0042 | -0.31128 | -0.045776 | 4.0421 | 70.0241 | 69.7952 | 114.5096 | 123.4772 | 3.6896 | 123.468 | 86.0641 | -0.31128 | 123.4772 | 3.6896 | 86.0641 | 114.5096 | 123.468 | -123.8663 | -123.8251
5563.7188 | 123.7061 | -61.3998 | 62.1506 | 0.15892 | 0.020083 | 0.015977 | 0.019796 | 0.060248 | -0.0016149 | 0.080544 | -57.6782 | 62.1735 | -61.7523 | -61.6287 | 53.0594 | 24.7192 | 8.7204 | 8.3359 | 62.1048 | -61.7477 | -0.35248 | 0.022888 | 3.7216 | -0.22888 | -9.0912 | -0.3479 | -0.045777 | 4.0741 | 70.1202 | 69.7357 | 114.4592 | 123.5733 | 3.7216 | 123.5046 | 86.1191 | -0.3479 | 123.5733 | 3.7216 | 86.1191 | 114.4592 | 123.5046 | -123.9029 | -123.8983
5564.7188 | 123.7152 | -61.4044 | 62.1185 | 0.58617 | 0.020083 | 0.015977 | 0.02001 | 0.059607 | 0.00052127 | 0.080331 | -57.6279 | 62.2009 | -61.734 | -61.6379 | 53.009 | 24.6185 | 8.7296 | 8.3679 | 62.146 | -61.7569 | -0.32959 | 0.082398 | 3.7766 | -0.23346 | -9.1095 | -0.35248 | 0.027466 | 4.1061 | 70.134 | 69.7723 | 114.4135 | 123.6053 | 3.7766 | 123.5504 | 86.0229 | -0.35248 | 123.6053 | 3.7766 | 86.0229 | 114.4135 | 123.5504 | -123.8525 | -123.8754
5565.7188 | 123.7198 | -61.3907 | 62.1552 | 0.14366 | 0.019656 | 0.016404 | 0.017874 | 0.063239 | -0.0014013 | 0.080544 | -57.6462 | 62.1735 | -61.7249 | -61.6058 | 53.0273 | 24.6185 | 8.6517 | 8.2764 | 62.1597 | -61.7294 | -0.33417 | 0.018311 | 3.7445 | -0.21515 | -9.1278 | -0.33874 | 0.004578 | 4.0787 | 70.0424 | 69.6671 | 114.418 | 123.5641 | 3.7445 | 123.5504 | 86.0092 | -0.33874 | 123.5641 | 3.7445 | 86.0092 | 114.418 | 123.5504 | -123.88 | -123.8846
5566.7188 | 123.7152 | -61.3953 | 62.1323 | 0.1284 | 0.023073 | 0.018327 | 0.018515 | 0.06153 | 0.00094847 | 0.082894 | -57.637 | 62.1826 | -61.7477 | -61.6196 | 53.0136 | 24.7101 | 8.6014 | 8.2306 | 62.1643 | -61.7477 | -0.35248 | 0.050354 | 3.7582 | -0.2243 | -9.1187 | -0.35248 | 0.032044 | 4.1107 | 69.9966 | 69.6259 | 114.4089 | 123.5779 | 3.7582 | 123.5596 | 86.1053 | -0.35248 | 123.5779 | 3.7582 | 86.1053 | 114.4089 | 123.5596 | -123.88 | -123.88
5567.7188 | 123.7747 | -61.4182 | 62.1185 | 0.15892 | 0.019656 | 0.012132 | 0.010397 | 0.060462 | -0.0028967 | 0.083322 | -57.6416 | 62.0911 | -61.7249 | -61.6104 | 53.0777 | 24.7559 | 8.606 | 8.3588 | 62.1368 | -61.6791 | -0.3067 | -0.027466 | 3.7766 | -0.19226 | -9.0408 | -0.26093 | 0.018311 | 4.0833 | 70.0241 | 69.7769 | 114.4958 | 123.5092 | 3.7766 | 123.555 | 86.174 | -0.26093 | 123.5092 | 3.7766 | 86.174 | 114.4958 | 123.555 | -123.8434 | -123.7976
5568.7188 | 123.7152 | -61.3998 | 62.1552 | 0.15129 | 0.020724 | 0.019822 | 0.017233 | 0.05918 | 0.00052127 | 0.083322 | -57.6279 | 62.1826 | -61.7111 | -61.615 | 52.9724 | 24.5773 | 8.6929 | 8.2535 | 62.1231 | -61.7706 | -0.31128 | 0.027466 | 3.772 | -0.21515 | -9.1827 | -0.37079 | -0.032043 | 4.0833 | 70.0928 | 69.6533 | 114.3723 | 123.5825 | 3.772 | 123.5229 | 85.9772 | -0.37079 | 123.5825 | 3.772 | 85.9772 | 114.3723 | 123.5229 | -123.8663 | -123.9258
5569.7188 | 123.7473 | -61.409 | 62.1277 | 0.18181 | 0.019442 | 0.015336 | 0.020865 | 0.062384 | -0.0020421 | 0.080758 | -57.6096 | 62.146 | -61.7249 | -61.5921 | 53.0182 | 24.6414 | 8.6243 | 8.3084 | 62.1414 | -61.7386 | -0.31586 | 0.01831 | 3.7994 | -0.1831 | -9.1095 | -0.32959 | 0.013732 | 4.1153 | 70.0333 | 69.7174 | 114.4272 | 123.555 | 3.7994 | 123.5504 | 86.0504 | -0.32959 | 123.555 | 3.7994 | 86.0504 | 114.4272 | 123.5504 | -123.8525 | -123.8663
5570.7188 | 123.7106 | -61.409 | 62.1323 | 4.0804 | 0.020724 | 0.015977 | 0.01766 | 0.061957 | -0.00011953 | 0.080972 | -57.5546 | 62.1552 | -61.7569 | -61.6333 | 52.9678 | 24.6689 | 8.6929 | 8.2901 | 62.1552 | -61.7386 | -0.3479 | 0.022888 | 3.8544 | -0.2243 | -9.1644 | -0.32959 | 0.022888 | 4.2023 | 70.1019 | 69.6991 | 114.3768 | 123.5641 | 3.8544 | 123.5641 | 86.0779 | -0.32959 | 123.5641 | 3.8544 | 86.0779 | 114.3768 | 123.5641 | -123.8892 | -123.8708
5571.7188 | 123.7152 | -61.409 | 62.146 | 0.11314 | 0.019656 | 0.016404 | 0.016378 | 0.065802 | 0.00094847 | 0.078835 | -57.6462 | 62.1826 | -61.7615 | -61.3541 | 53.1052 | 24.5316 | 8.7982 | 8.3908 | 62.2009 | -61.7203 | -0.35248 | 0.036621 | 3.7628 | 0.054932 | -9.0408 | -0.31128 | 0.054932 | 4.1153 | 70.2072 | 69.7998 | 114.5142 | 123.5916 | 3.7628 | 123.6099 | 85.9406 | -0.31128 | 123.5916 | 3.7628 | 85.9406 | 114.5142 | 123.6099 | -123.9075 | -123.8663
5572.7188 | 123.793 | -61.3678 | 62.1094 | 0.12077 | 0.017733 | 0.020036 | 0.010611 | 0.061743 | -0.0022559 | 0.082253 | -57.5684 | 62.0819 | -61.7203 | -61.5555 | 52.9999 | 24.7421 | 8.6105 | 8.4274 | 62.1048 | -61.6745 | -0.35248 | -0.027466 | 3.7994 | -0.18768 | -9.1095 | -0.3067 | -0.004578 | 4.1519 | 69.9783 | 69.7952 | 114.3677 | 123.4497 | 3.7994 | 123.4726 | 86.1099 | -0.3067 | 123.4497 | 3.7994 | 86.1099 | 114.3677 | 123.4726 | -123.8297 | -123.7839
5573.7188 | 123.6969 | -61.4182 | 62.146 | 0.34203 | 0.019656 | 0.017899 | 0.018515 | 0.060675 | -0.0014013 | 0.081613 | -57.605 | 62.2009 | -61.734 | -61.6287 | 52.8992 | 24.6552 | 8.7616 | 8.3267 | 62.1552 | -61.7386 | -0.31586 | 0.054932 | 3.8132 | -0.21057 | -9.2468 | -0.32043 | 0.009155 | 4.129 | 70.1797 | 69.7449 | 114.3173 | 123.6191 | 3.8132 | 123.5733 | 86.0733 | -0.32043 | 123.6191 | 3.8132 | 86.0733 | 114.3173 | 123.5733 | -123.88 | -123.8846
5574.7188 | 123.6969 | -61.4136 | 62.1277 | 0.9829 | 0.019228 | 0.020036 | 0.017447 | 0.064307 | 0.00052127 | 0.08204 | -57.5089 | 62.1918 | -61.7294 | -61.6241 | 52.8992 | 24.5911 | 8.812 | 8.3221 | 62.1506 | -61.7477 | -0.31586 | 0.064086 | 3.9047 | -0.21057 | -9.2285 | -0.33417 | 0.022888 | 4.2206 | 70.2255 | 69.7357 | 114.3127 | 123.6053 | 3.9047 | 123.5641 | 86.0046 | -0.33417 | 123.6053 | 3.9047 | 86.0046 | 114.3127 | 123.5641 | -123.8571 | -123.8754
5575.7188 | 123.6832 | -61.4319 | 62.1323 | 0.17418 | 0.020937 | 0.02324 | 0.015738 | 0.065375 | -0.0011877 | 0.08204 | -57.6553 | 62.178 | -61.7661 | -61.5646 | 52.8214 | 24.5499 | 8.8989 | 8.3725 | 62.1689 | -61.734 | -0.33417 | 0.045777 | 3.7766 | -0.13275 | -9.3109 | -0.30212 | 0.036621 | 4.1107 | 70.3308 | 69.8044 | 114.2532 | 123.6099 | 3.7766 | 123.6008 | 85.9818 | -0.30212 | 123.6099 | 3.7766 | 85.9818 | 114.2532 | 123.6008 | -123.8983 | -123.8663
5576.7188 | 123.7289 | -61.3953 | 62.1185 | 0.1284 | 0.020724 | 0.019395 | 0.015738 | 0.065589 | 0.0013757 | 0.082467 | -57.5958 | 62.1872 | -61.734 | -61.615 | 52.89 | 24.6094 | 8.8211 | 8.4549 | 62.1506 | -61.7111 | -0.33875 | 0.068665 | 3.7994 | -0.21973 | -9.2285 | -0.31586 | 0.032044 | 4.1382 | 70.2164 | 69.8502 | 114.2853 | 123.5825 | 3.7994 | 123.5458 | 86.0046 | -0.31586 | 123.5825 | 3.7994 | 86.0046 | 114.2853 | 123.5458 | -123.8525 | -123.8297
5577.7188 | 123.7106 | -61.4044 | 62.1323 | 0.11314 | 0.020083 | 0.015336 | 0.017447 | 0.063025 | -0.00011953 | 0.080544 | -57.6004 | 62.1643 | -61.7432 | -61.6241 | 52.858 | 24.559 | 8.8394 | 8.4 | 62.178 | -61.7386 | -0.33875 | 0.032044 | 3.804 | -0.21973 | -9.2743 | -0.33417 | 0.045777 | 4.1428 | 70.2438 | 69.8044 | 114.2624 | 123.5687 | 3.804 | 123.5825 | 85.9634 | -0.33417 | 123.5687 | 3.804 | 85.9634 | 114.2624 | 123.5825 | -123.8754 | -123.8708
5578.7188 | 123.6511 | -61.4502 | 62.1368 | 0.13603 | 0.019656 | 0.018113 | 0.017233 | 0.063452 | -0.00076053 | 0.081826 | -57.6141 | 62.2009 | -61.7294 | -61.6425 | 52.858 | 24.5773 | 8.8257 | 8.3405 | 62.1735 | -61.7523 | -0.27924 | 0.064087 | 3.8361 | -0.19226 | -9.2789 | -0.30212 | 0.036621 | 4.1153 | 70.2759 | 69.7906 | 114.3082 | 123.6511 | 3.8361 | 123.6237 | 86.0275 | -0.30212 | 123.6511 | 3.8361 | 86.0275 | 114.3082 | 123.6237 | -123.8663 | -123.8892
5579.7188 | 123.6969 | -61.441 | 62.1368 | 0.1284 | 0.019869 | 0.012986 | 0.013601 | 0.064093 | 0.00052127 | 0.080758 | -57.4951 | 62.1552 | -61.7661 | -61.5555 | 52.8397 | 24.5041 | 8.844 | 8.3862 | 62.2147 | -61.734 | -0.32501 | 0.01831 | 3.9459 | -0.11444 | -9.2972 | -0.29297 | 0.07782 | 4.2709 | 70.285 | 69.8273 | 114.2807 | 123.5962 | 3.9459 | 123.6557 | 85.9451 | -0.29297 | 123.5962 | 3.9459 | 85.9451 | 114.2807 | 123.6557 | -123.9029 | -123.8708
5580.7188 | 123.7015 | -61.4273 | 62.1414 | 0.1284 | 0.021792 | 0.016831 | 0.018301 | 0.064307 | -0.00076053 | 0.082253 | -57.5958 | 62.2101 | -61.7477 | -61.6379 | 52.8076 | 24.2798 | 8.8028 | 8.7387 | 62.1643 | -61.7523 | -0.32044 | 0.068665 | 3.8315 | -0.21057 | -9.3338 | -0.32501 | 0.022889 | 4.1519 | 70.2301 | 70.166 | 114.2349 | 123.6374 | 3.8315 | 123.5916 | 85.7071 | -0.32501 | 123.6374 | 3.8315 | 85.7071 | 114.2349 | 123.5916 | -123.8892 | -123.8937
5581.7188 | 123.6923 | -61.4182 | 62.1323 | 0.18944 | 0.020937 | 0.016618 | 0.014456 | 0.063452 | 0.00030767 | 0.084603 | -57.5958 | 62.2055 | -61.7615 | -61.6425 | 52.8305 | 24.5224 | 8.7936 | 8.3954 | 62.1735 | -61.7661 | -0.34332 | 0.073242 | 3.8223 | -0.2243 | -9.3018 | -0.3479 | 0.041199 | 4.1656 | 70.2118 | 69.8135 | 114.2487 | 123.6237 | 3.8223 | 123.5916 | 85.9406 | -0.3479 | 123.6237 | 3.8223 | 85.9406 | 114.2487 | 123.5916 | -123.8937 | -123.8983
5582.7188 | 123.7976 | -61.3861 | 62.0956 | 0.17418 | 0.01581 | 0.019822 | 0.014456 | 0.062812 | -0.0016149 | 0.082253 | -57.4997 | 62.1094 | -61.7203 | -61.5646 | 52.9358 | 24.5956 | 8.6563 | 8.4915 | 62.1002 | -61.6974 | -0.33417 | 0.013733 | 3.8864 | -0.17853 | -9.1599 | -0.31128 | 0.004578 | 4.2206 | 70.0424 | 69.8776 | 114.3219 | 123.4955 | 3.8864 | 123.4863 | 85.9818 | -0.31128 | 123.4955 | 3.8864 | 85.9818 | 114.3219 | 123.4863 | -123.8159 | -123.793
5583.7188 | 123.7106 | -61.3907 | 62.1597 | 0.13603 | 0.023073 | 0.019608 | 0.019583 | 0.060462 | 9.4068e-05 | 0.08204 | -57.9025 | 62.1552 | -61.7477 | -61.6745 | 52.771 | 24.2935 | 8.7341 | 8.2489 | 62.1643 | -61.7615 | -0.35706 | -0.004578 | 3.4882 | -0.28381 | -9.3887 | -0.37079 | 0.004578 | 3.8452 | 70.1248 | 69.6396 | 114.1617 | 123.5458 | 3.4882 | 123.555 | 85.6842 | -0.37079 | 123.5458 | 3.4882 | 85.6842 | 114.1617 | 123.555 | -123.9075 | -123.9212
5584.7188 | 123.6969 | -61.3861 | 62.1597 | 0.029221 | 0.020296 | 0.017472 | 0.019796 | 0.061316 | 0.00094847 | 0.082894 | -57.5272 | 62.2192 | -61.7477 | -61.615 | 52.7756 | 24.321 | 8.7936 | 8.3405 | 62.1872 | -61.7294 | -0.36163 | 0.059509 | 3.8589 | -0.22888 | -9.3842 | -0.34332 | 0.027466 | 4.2206 | 70.1797 | 69.7266 | 114.1617 | 123.6053 | 3.8589 | 123.5733 | 85.7071 | -0.34332 | 123.6053 | 3.8589 | 85.7071 | 114.1617 | 123.5733 | -123.9075 | -123.8892
5585.7188 | 123.6832 | -61.3953 | 62.1414 | 0.04448 | 0.02051 | 0.020463 | 0.019583 | 0.063666 | -0.0016149 | 0.081185 | -57.5134 | 62.2101 | -61.702 | -61.615 | 52.803 | 24.4583 | 8.8028 | 8.3954 | 62.2009 | -61.7432 | -0.3067 | 0.068665 | 3.8818 | -0.21973 | -9.3384 | -0.3479 | 0.05951 | 4.1885 | 70.1981 | 69.7906 | 114.1983 | 123.6053 | 3.8818 | 123.5962 | 85.8536 | -0.3479 | 123.6053 | 3.8818 | 85.8536 | 114.1983 | 123.5962 | -123.8434 | -123.8846
5586.7188 | 123.6832 | -61.4273 | 62.1506 | 0.12077 | 0.021364 | 0.011491 | 0.018087 | 0.063452 | -0.0018285 | 0.079476 | -57.5546 | 62.2009 | -61.702 | -61.6562 | 52.7527 | 24.4583 | 8.8028 | 8.2809 | 62.1872 | -61.7203 | -0.27466 | 0.050354 | 3.8727 | -0.22888 | -9.3979 | -0.29297 | 0.036621 | 4.1473 | 70.2301 | 69.7083 | 114.18 | 123.6282 | 3.8727 | 123.6145 | 85.8856 | -0.29297 | 123.6282 | 3.8727 | 85.8856 | 114.18 | 123.6145 | -123.8525 | -123.8708
5587.7188 | 123.8251 | -61.3541 | 62.0911 | -0.2607 | 0.018374 | 0.013413 | 0.011679 | 0.06388 | -0.00011953 | 0.084176 | -57.4997 | 62.1094 | -61.7111 | -61.5509 | 52.8488 | 24.4354 | 8.6151 | 8.4457 | 62.1094 | -61.6974 | -0.35706 | 0.018311 | 3.8544 | -0.19684 | -9.2422 | -0.34332 | 0.018311 | 4.2114 | 69.9692 | 69.7998 | 114.2029 | 123.4634 | 3.8544 | 123.4634 | 85.7895 | -0.34332 | 123.4634 | 3.8544 | 85.7895 | 114.2029 | 123.4634 | -123.8022 | -123.7885
5588.7188 | 123.674 | -61.3815 | 62.1643 | 0.021591 | 0.020296 | 0.015763 | 0.017874 | 0.061957 | -0.0014013 | 0.083749 | -57.4997 | 62.2101 | -61.7203 | -61.6379 | 52.7481 | 24.6231 | 8.7479 | 8.2718 | 62.1872 | -61.7432 | -0.33874 | 0.045776 | 3.8818 | -0.25635 | -9.4162 | -0.36163 | 0.022888 | 4.2206 | 70.1294 | 69.6533 | 114.1296 | 123.5916 | 3.8818 | 123.5687 | 86.0046 | -0.36163 | 123.5916 | 3.8818 | 86.0046 | 114.1296 | 123.5687 | -123.8846 | -123.9075
5589.7188 | 123.7198 | -61.4227 | 62.146 | 0.16655 | 0.020296 | 0.017045 | 0.016378 | 0.063666 | -0.0011877 | 0.081399 | -57.5409 | 62.2009 | -61.734 | -61.6287 | 52.7618 | 24.4583 | 8.7616 | 8.313 | 62.1689 | -61.7386 | -0.31128 | 0.054932 | 3.8818 | -0.20599 | -9.3842 | -0.31586 | 0.022888 | 4.1931 | 70.1843 | 69.7357 | 114.1846 | 123.6237 | 3.8818 | 123.5916 | 85.881 | -0.31586 | 123.6237 | 3.8818 | 85.881 | 114.1846 | 123.5916 | -123.88 | -123.8846
5590.7188 | 123.6603 | -61.4273 | 62.146 | 0.04448 | 0.017733 | 0.017045 | 0.018728 | 0.062171 | -0.00054693 | 0.082467 | -57.5134 | 62.2101 | -61.7294 | -61.6562 | 52.7344 | 24.408 | 8.8211 | 8.3313 | 62.2009 | -61.7386 | -0.30212 | 0.064087 | 3.9139 | -0.22888 | -9.4116 | -0.31128 | 0.054932 | 4.216 | 70.2484 | 69.7586 | 114.1617 | 123.6374 | 3.9139 | 123.6282 | 85.8353 | -0.31128 | 123.6374 | 3.9139 | 85.8353 | 114.1617 | 123.6282 | -123.8754 | -123.8846
5591.7188 | 123.7015 | -61.3998 | 62.1552 | -0.062332 | 0.020724 | 0.018113 | 0.016378 | 0.063239 | -0.00011953 | 0.08204 | -57.4631 | 62.2101 | -61.7294 | -61.5646 | 52.7664 | 24.5407 | 8.757 | 8.4 | 62.2147 | -61.7386 | -0.32959 | 0.054932 | 3.9368 | -0.16479 | -9.3887 | -0.33874 | 0.05951 | 4.2664 | 70.1569 | 69.7998 | 114.1663 | 123.6099 | 3.9368 | 123.6145 | 85.9406 | -0.33874 | 123.6099 | 3.9368 | 85.9406 | 114.1663 | 123.6145 | -123.8846 | -123.8937
5592.7188 | 123.6877 | -61.3998 | 62.1323 | 0.029221 | 0.021151 | 0.018113 | 0.018301 | 0.064307 | -0.0022559 | 0.082253 | -57.4631 | 62.2101 | -61.7386 | -61.6379 | 52.7664 | 24.4354 | 8.8074 | 8.3954 | 62.2284 | -61.7523 | -0.33874 | 0.07782 | 3.9368 | -0.23804 | -9.3658 | -0.35248 | 0.096131 | 4.2755 | 70.2072 | 69.7952 | 114.1663 | 123.6099 | 3.9368 | 123.6282 | 85.8353 | -0.35248 | 123.6099 | 3.9368 | 85.8353 | 114.1663 | 123.6282 | -123.8708 | -123.8846
5593.7188 | 123.6832 | -61.3861 | 62.146 | 0.013962 | 0.020296 | 0.014909 | 0.017874 | 0.063452 | 9.4068e-05 | 0.079904 | -57.4814 | 62.2192 | -61.7294 | -61.615 | 52.7252 | 24.4995 | 8.8348 | 8.4229 | 62.2055 | -61.7477 | -0.34332 | 0.073242 | 3.9047 | -0.22888 | -9.4208 | -0.36163 | 0.059509 | 4.248 | 70.2209 | 69.809 | 114.1113 | 123.6053 | 3.9047 | 123.5916 | 85.8856 | -0.36163 | 123.6053 | 3.9047 | 85.8856 | 114.1113 | 123.5916 | -123.8754 | -123.8937
5594.7188 | 123.6832 | -61.4044 | 62.1506 | -0.0089264 | 0.019228 | 0.015977 | 0.016592 | 0.065589 | -0.00054693 | 0.080972 | -57.4585 | 62.2238 | -61.7157 | -61.5967 | 52.7298 | 24.5499 | 8.812 | 8.4595 | 62.2101 | -61.7432 | -0.31128 | 0.073242 | 3.9459 | -0.19226 | -9.4208 | -0.33875 | 0.059509 | 4.2572 | 70.2164 | 69.8639 | 114.1342 | 123.6282 | 3.9459 | 123.6145 | 85.9543 | -0.33875 | 123.6282 | 3.9459 | 85.9543 | 114.1342 | 123.6145 | -123.8663 | -123.8937
5595.7188 | 123.6923 | -61.4136 | 62.146 | -0.039444 | 0.02051 | 0.017259 | 0.01766 | 0.063452 | 0.00030767 | 0.080972 | -57.4402 | 62.1964 | -61.7386 | -61.5829 | 52.7023 | 24.5636 | 8.876 | 8.4961 | 62.2055 | -61.7294 | -0.32501 | 0.050354 | 3.9734 | -0.16937 | -9.4437 | -0.31586 | 0.059509 | 4.2984 | 70.2896 | 69.9097 | 114.1159 | 123.6099 | 3.9734 | 123.6191 | 85.9772 | -0.31586 | 123.6099 | 3.9734 | 85.9772 | 114.1159 | 123.6191 | -123.8846 | -123.8754
5596.7188 | 123.7106 | -61.4136 | 62.1643 | -0.016556 | 0.019442 | 0.018327 | 0.019156 | 0.062384 | -0.00011953 | 0.08204 | -57.4722 | 62.2147 | -61.7386 | -61.6104 | 52.597 | 23.7305 | 8.8257 | 8.3359 | 62.2055 | -61.7111 | -0.32501 | 0.050354 | 3.9413 | -0.19684 | -9.5673 | -0.29755 | 0.041198 | 4.2664 | 70.2393 | 69.7494 | 114.0106 | 123.6282 | 3.9413 | 123.6191 | 85.144 | -0.29755 | 123.6282 | 3.9413 | 85.144 | 114.0106 | 123.6191 | -123.9029 | -123.8754
5597.7188 | 123.6603 | -61.3998 | 62.1552 | 0.11314 | 0.021578 | 0.018968 | 0.016165 | 0.065161 | 0.00052127 | 0.081826 | -57.4905 | 62.233 | -61.7477 | -61.6425 | 52.1393 | 23.6801 | 8.8348 | 8.3267 | 62.2055 | -61.7477 | -0.3479 | 0.07782 | 3.9093 | -0.24262 | -10.0159 | -0.3479 | 0.050354 | 4.2572 | 70.2347 | 69.7266 | 113.5391 | 123.6328 | 3.9093 | 123.6053 | 85.08 | -0.3479 | 123.6328 | 3.9093 | 85.08 | 113.5391 | 123.6053 | -123.9029 | -123.9029
5598.7188 | 123.7152 | -61.3724 | 62.146 | -0.08522 | 0.020937 | 0.016831 | 0.016806 | 0.06388 | 0.00030767 | 0.082681 | -57.3807 | 62.2009 | -61.6928 | -61.5555 | 52.6291 | 23.9273 | 8.8074 | 8.4274 | 62.2009 | -61.7111 | -0.32044 | 0.054932 | 3.9917 | -0.18311 | -9.5169 | -0.33875 | 0.054932 | 4.3121 | 70.1797 | 69.7998 | 114.0015 | 123.5733 | 3.9917 | 123.5733 | 85.2997 | -0.33875 | 123.5733 | 3.9917 | 85.2997 | 114.0015 | 123.5733 | -123.8388 | -123.8571
5599.7188 | 123.7473 | -61.3815 | 62.1414 | -0.039444 | 0.01816 | 0.016191 | 0.017233 | 0.063452 | -0.00054693 | 0.080972 | -57.4127 | 62.2192 | -61.7111 | -61.5875 | 52.652 | 24.1379 | 8.7845 | 8.3771 | 62.2101 | -61.7249 | -0.32959 | 0.07782 | 3.9688 | -0.20599 | -9.4894 | -0.34332 | 0.068665 | 4.2984 | 70.166 | 69.7586 | 114.0335 | 123.6008 | 3.9688 | 123.5916 | 85.5194 | -0.34332 | 123.6008 | 3.9688 | 85.5194 | 114.0335 | 123.5916 | -123.8525 | -123.8663
5600.7188 | 123.7335 | -61.3815 | 62.1689 | -0.08522 | 0.022433 | 0.014268 | 0.016592 | 0.065589 | -0.0024695 | 0.081399 | -57.4356 | 62.2101 | -61.7203 | -61.5875 | 52.6337 | 24.0738 | 8.8486 | 8.4595 | 62.178 | -61.7157 | -0.33874 | 0.041199 | 3.9459 | -0.20599 | -9.5352 | -0.33417 | 0.009156 | 4.2847 | 70.2301 | 69.841 | 114.0152 | 123.5916 | 3.9459 | 123.5596 | 85.4553 | -0.33417 | 123.5916 | 3.9459 | 85.4553 | 114.0152 | 123.5596 | -123.8892 | -123.8846
5601.7188 | 123.7289 | -61.3907 | 62.1689 | -0.23781 | 0.019869 | 0.018754 | 0.018301 | 0.063025 | -0.0014013 | 0.080331 | -57.399 | 62.2009 | -61.6882 | -61.5829 | 52.6062 | 24.0097 | 8.8852 | 8.4778 | 62.2009 | -61.734 | -0.29755 | 0.032044 | 3.9917 | -0.19226 | -9.5627 | -0.34332 | 0.032044 | 4.2892 | 70.2759 | 69.8685 | 113.9969 | 123.5916 | 3.9917 | 123.5916 | 85.4004 | -0.34332 | 123.5916 | 3.9917 | 85.4004 | 113.9969 | 123.5916 | -123.8571 | -123.9029
5602.7344 | 123.8022 | -61.3678 | 62.1597 | -0.16914 | 0.016238 | 0.01555 | 0.0071926 | 0.067084 | 0.0011621 | 0.083108 | -57.3807 | 62.1277 | -61.7203 | -61.4365 | 52.684 | 23.8998 | 8.7296 | 8.5831 | 62.1918 | -61.6425 | -0.35248 | -0.032043 | 3.9871 | -0.068664 | -9.4757 | -0.27466 | 0.032043 | 4.3396 | 70.0974 | 69.9509 | 114.0518 | 123.4955 | 3.9871 | 123.5596 | 85.2676 | -0.27466 | 123.4955 | 3.9871 | 85.2676 | 114.0518 | 123.5596 | -123.88 | -123.8022
5603.7188 | 123.6969 | -61.3861 | 62.1872 | -0.0012969 | 0.021151 | 0.019181 | 0.02001 | 0.06153 | -0.00054693 | 0.082681 | -57.3944 | 62.2238 | -61.7249 | -61.5875 | 52.5558 | 23.7991 | 8.8394 | 8.4595 | 62.2055 | -61.7477 | -0.33875 | 0.036621 | 3.9917 | -0.20142 | -9.6313 | -0.36163 | 0.01831 | 4.3304 | 70.2255 | 69.8456 | 113.942 | 123.6099 | 3.9917 | 123.5916 | 85.1852 | -0.36163 | 123.6099 | 3.9917 | 85.1852 | 113.942 | 123.5916 | -123.912 | -123.9349
5604.7188 | 123.7106 | -61.3724 | 62.1689 | -0.031814 | 0.019656 | 0.017259 | 0.017233 | 0.063666 | 0.0022303 | 0.082467 | -57.3669 | 62.2192 | -61.6837 | -61.5692 | 52.5696 | 23.9273 | 8.8623 | 8.5052 | 62.2101 | -61.7294 | -0.31128 | 0.050354 | 4.0054 | -0.19684 | -9.5993 | -0.35706 | 0.041199 | 4.3167 | 70.2347 | 69.8776 | 113.942 | 123.5916 | 4.0054 | 123.5825 | 85.2997 | -0.35706 | 123.5916 | 4.0054 | 85.2997 | 113.942 | 123.5825 | -123.8525 | -123.8983
5605.7188 | 123.7061 | -61.3907 | 62.1643 | -0.1844 | 0.019869 | 0.017472 | 0.018728 | 0.063239 | 0.00030767 | 0.083322 | -57.3761 | 62.2101 | -61.7157 | -61.5601 | 52.6016 | 24.0051 | 8.7891 | 8.4457 | 62.2009 | -61.7111 | -0.32501 | 0.045776 | 4.0146 | -0.16937 | -9.5627 | -0.32043 | 0.036621 | 4.3396 | 70.1797 | 69.8364 | 113.9923 | 123.6008 | 4.0146 | 123.5916 | 85.3958 | -0.32043 | 123.6008 | 4.0146 | 85.3958 | 113.9923 | 123.5916 | -123.88 | -123.8754
5606.7188 | 123.7289 | -61.3815 | 62.1689 | -0.15388 | 0.020296 | 0.015763 | 0.015738 | 0.060675 | -0.00097413 | 0.080331 | -57.3578 | 62.2238 | -61.6974 | -61.5509 | 52.597 | 23.9868 | 8.8531 | 8.5144 | 62.2101 | -61.7111 | -0.31586 | 0.054932 | 4.0237 | -0.16937 | -9.5718 | -0.32959 | 0.041199 | 4.3396 | 70.2347 | 69.8959 | 113.9786 | 123.6053 | 4.0237 | 123.5916 | 85.3683 | -0.32959 | 123.6053 | 4.0237 | 85.3683 | 113.9786 | 123.5916 | -123.8663 | -123.88
5607.7188 | 123.7473 | -61.3998 | 62.1277 | 0.15129 | 0.021151 | 0.019608 | 0.016592 | 0.064734 | 0.00073487 | 0.083322 | -57.4448 | 62.1964 | -61.7386 | -61.6241 | 52.5375 | 23.9502 | 8.7204 | 8.4183 | 62.1643 | -61.7157 | -0.33874 | 0.068664 | 3.9551 | -0.22431 | -9.5901 | -0.31586 | 0.036621 | 4.2938 | 70.1202 | 69.8181 | 113.9374 | 123.5962 | 3.9551 | 123.5641 | 85.35 | -0.31586 | 123.5962 | 3.9551 | 85.35 | 113.9374 | 123.5641 | -123.8663 | -123.8434
5608.7188 | 123.7289 | -61.4044 | 62.1552 | -0.024185 | 0.020937 | 0.014482 | 0.017233 | 0.063025 | 0.00052127 | 0.081399 | -57.3624 | 62.2055 | -61.7432 | -61.5784 | 52.5742 | 23.9868 | 8.8303 | 8.4549 | 62.1689 | -61.7294 | -0.33875 | 0.050354 | 4.0421 | -0.17395 | -9.581 | -0.32501 | 0.013733 | 4.3808 | 70.2347 | 69.8593 | 113.9786 | 123.6099 | 4.0421 | 123.5733 | 85.3912 | -0.32501 | 123.6099 | 4.0421 | 85.3912 | 113.9786 | 123.5733 | -123.8983 | -123.8846
5609.7188 | 123.7244 | -61.409 | 62.1735 | -0.08522 | 0.022005 | 0.016404 | 0.018728 | 0.065802 | -0.00033333 | 0.082894 | -57.3578 | 62.2421 | -61.7065 | -61.5646 | 52.5833 | 24.0967 | 8.8531 | 8.4961 | 62.2009 | -61.6928 | -0.29755 | 0.068664 | 4.0512 | -0.15564 | -9.5901 | -0.28381 | 0.027466 | 4.3488 | 70.2621 | 69.9051 | 113.9923 | 123.6511 | 4.0512 | 123.6099 | 85.5057 | -0.28381 | 123.6511 | 4.0512 | 85.5057 | 113.9923 | 123.6099 | -123.88 | -123.8663
5610.7188 | 123.7106 | -61.3998 | 62.146 | 0.21233 | 0.021792 | 0.014482 | 0.017233 | 0.064521 | 0.0022303 | 0.08204 | -57.3166 | 62.2147 | -61.7157 | -61.5509 | 52.6108 | 24.0784 | 8.8531 | 8.5052 | 62.2147 | -61.7203 | -0.31586 | 0.068665 | 4.0833 | -0.15106 | -9.5352 | -0.32043 | 0.068665 | 4.3991 | 70.253 | 69.9051 | 114.0106 | 123.6145 | 4.0833 | 123.6145 | 85.4782 | -0.32043 | 123.6145 | 4.0833 | 85.4782 | 114.0106 | 123.6145 | -123.8617 | -123.8663
5611.7188 | 123.7564 | -61.3678 | 62.1826 | -0.08522 | 0.020083 | 0.0132 | 0.017019 | 0.062384 | -0.0026831 | 0.082894 | -57.3624 | 62.2192 | -61.7203 | -61.5921 | 52.6154 | 24.1241 | 8.876 | 8.5464 | 62.2009 | -61.7065 | -0.35248 | 0.036621 | 4.0054 | -0.2243 | -9.5673 | -0.33875 | 0.018311 | 4.3579 | 70.2438 | 69.9142 | 113.9832 | 123.587 | 4.0054 | 123.5687 | 85.4919 | -0.33875 | 123.587 | 4.0054 | 85.4919 | 113.9832 | 123.5687 | -123.9029 | -123.8892
5612.7344 | 123.7473 | -61.3266 | 62.2101 | -0.16151 | 0.019442 | 0.0132 | 0.0082608 | 0.060248 | -0.0026831 | 0.084176 | -57.3441 | 62.0911 | -61.7065 | -61.4822 | 52.3773 | 24.1013 | 8.7616 | 8.6426 | 62.2238 | -61.6516 | -0.37994 | -0.11902 | 3.9825 | -0.15564 | -9.8328 | -0.32501 | 0.013733 | 4.3625 | 70.0882 | 69.9692 | 113.7039 | 123.4177 | 3.9825 | 123.5504 | 85.4279 | -0.32501 | 123.4177 | 3.9825 | 85.4279 | 113.7039 | 123.5504 | -123.9166 | -123.8617
5613.7188 | 123.7381 | -61.3632 | 62.178 | -0.16914 | 0.018374 | 0.014482 | 0.018087 | 0.059607 | -0.0014013 | 0.08439 | -57.3486 | 62.2101 | -61.702 | -61.5555 | 52.2629 | 24.028 | 8.8394 | 8.5144 | 62.2147 | -61.7157 | -0.33875 | 0.032043 | 4.0146 | -0.19226 | -9.9152 | -0.35248 | 0.036621 | 4.3533 | 70.2026 | 69.8776 | 113.6261 | 123.5733 | 4.0146 | 123.5779 | 85.3912 | -0.35248 | 123.5733 | 4.0146 | 85.3912 | 113.6261 | 123.5779 | -123.88 | -123.8937
5614.7188 | 123.7106 | -61.3815 | 62.1689 | -0.12337 | 0.021151 | 0.015977 | 0.019796 | 0.063666 | -0.0026831 | 0.081399 | -57.3441 | 62.2101 | -61.7065 | -61.5509 | 52.2858 | 24.0509 | 8.876 | 8.6014 | 62.2147 | -61.7157 | -0.32501 | 0.041199 | 4.0375 | -0.16937 | -9.8831 | -0.33417 | 0.045777 | 4.3625 | 70.2576 | 69.9829 | 113.6673 | 123.5916 | 4.0375 | 123.5962 | 85.4324 | -0.33417 | 123.5916 | 4.0375 | 85.4324 | 113.6673 | 123.5962 | -123.8754 | -123.8846
5615.7188 | 123.7473 | -61.3724 | 62.1964 | -0.13863 | 0.017519 | 0.016618 | 0.017233 | 0.062812 | 0.00073487 | 0.081185 | -57.3395 | 62.2147 | -61.7111 | -61.5372 | 52.2583 | 24.0646 | 8.876 | 8.6288 | 62.2284 | -61.6974 | -0.33875 | 0.018311 | 4.0329 | -0.1648 | -9.938 | -0.32501 | 0.032044 | 4.3716 | 70.2484 | 70.0012 | 113.6307 | 123.587 | 4.0329 | 123.6008 | 85.437 | -0.32501 | 123.587 | 4.0329 | 85.437 | 113.6307 | 123.6008 | -123.9075 | -123.8937
5616.7188 | 123.7152 | -61.3907 | 62.1689 | -0.17677 | 0.019015 | 0.019608 | 0.016378 | 0.060889 | 0.00052127 | 0.083108 | -57.3441 | 62.2284 | -61.702 | -61.5555 | 52.2354 | 24.0051 | 8.8898 | 8.606 | 62.2101 | -61.6791 | -0.31128 | 0.05951 | 4.0466 | -0.16479 | -9.9335 | -0.28839 | 0.041199 | 4.3579 | 70.2805 | 69.9966 | 113.6261 | 123.6191 | 4.0466 | 123.6008 | 85.3958 | -0.28839 | 123.6191 | 4.0466 | 85.3958 | 113.6261 | 123.6008 | -123.8708 | -123.848
5617.7188 | 123.7564 | -61.3998 | 62.1368 | 0.059738 | 0.018801 | 0.01854 | 0.0084744 | 0.061957 | 0.0018031 | 0.082253 | -57.3761 | 62.1643 | -61.6608 | -61.5372 | 52.2537 | 24.0005 | 8.7387 | 8.5373 | 62.1597 | -61.6974 | -0.26093 | 0.027466 | 4.0237 | -0.13733 | -9.8831 | -0.29755 | 0.022888 | 4.2847 | 70.1385 | 69.9371 | 113.6536 | 123.5641 | 4.0237 | 123.5596 | 85.4004 | -0.29755 | 123.5641 | 4.0237 | 85.4004 | 113.6536 | 123.5596 | -123.7976 | -123.8342
5618.7188 | 123.7335 | -61.3907 | 62.1689 | -0.13863 | 0.020083 | 0.01854 | 0.020865 | 0.061316 | -0.00054693 | 0.080758 | -57.3303 | 62.2009 | -61.7111 | -61.5463 | 52.2354 | 24.0509 | 8.8852 | 8.5693 | 62.1872 | -61.7203 | -0.32043 | 0.032044 | 4.0604 | -0.15564 | -9.9335 | -0.32959 | 0.018311 | 4.3808 | 70.2759 | 69.96 | 113.6261 | 123.5916 | 4.0604 | 123.5779 | 85.4416 | -0.32959 | 123.5916 | 4.0604 | 85.4416 | 113.6261 | 123.5779 | -123.88 | -123.8892
5619.7188 | 123.7198 | -61.409 | 62.1872 | -0.16151 | 0.019228 | 0.017259 | 0.016378 | 0.061743 | -0.0020421 | 0.081613 | -57.3715 | 62.2147 | -61.7157 | -61.5829 | 52.2583 | 24.1791 | 8.9264 | 8.4961 | 62.2238 | -61.702 | -0.3067 | 0.027466 | 4.0375 | -0.17395 | -9.9289 | -0.29297 | 0.036621 | 4.3442 | 70.3354 | 69.9051 | 113.6673 | 123.6237 | 4.0375 | 123.6328 | 85.5881 | -0.29297 | 123.6237 | 4.0375 | 85.5881 | 113.6673 | 123.6328 | -123.9029 | -123.8892
5620.7188 | 123.7198 | -61.3861 | 62.1735 | -0.1844 | 0.01816 | 0.017259 | 0.019156 | 0.063239 | -0.00054693 | 0.082467 | -57.3257 | 62.2421 | -61.702 | -61.5326 | 52.2858 | 24.147 | 8.8806 | 8.5785 | 62.1964 | -61.702 | -0.31586 | 0.068664 | 4.0604 | -0.14648 | -9.8877 | -0.31586 | 0.022888 | 4.3762 | 70.2667 | 69.9646 | 113.6719 | 123.6282 | 4.0604 | 123.5825 | 85.5331 | -0.31586 | 123.6282 | 4.0604 | 85.5331 | 113.6719 | 123.5825 | -123.8754 | -123.8754
5621.7188 | 123.7564 | -61.3998 | 62.1735 | -0.23781 | 0.019869 | 0.012773 | 0.017233 | 0.062384 | -0.00054693 | 0.082681 | -57.3303 | 62.2101 | -61.6882 | -61.5601 | 52.2949 | 24.2157 | 8.8348 | 8.5419 | 62.2192 | -61.7203 | -0.28839 | 0.036621 | 4.0695 | -0.16022 | -9.8785 | -0.32043 | 0.045776 | 4.3579 | 70.2347 | 69.9417 | 113.6948 | 123.6099 | 4.0695 | 123.6191 | 85.6155 | -0.32043 | 123.6099 | 4.0695 | 85.6155 | 113.6948 | 123.6191 | -123.8617 | -123.8937
5622.7188 | 123.6099 | -61.3632 | 62.1414 | -0.12337 | 0.023073 | 0.018113 | 0.017447 | 0.060675 | -0.00097413 | 0.082681 | -57.312 | 62.2147 | -61.702 | -61.5601 | 52.3361 | 24.2294 | 8.812 | 8.5785 | 62.2055 | -61.7249 | -0.33875 | 0.073243 | 4.0512 | -0.19684 | -9.8053 | -0.36163 | 0.064087 | 4.39 | 70.1752 | 69.9417 | 113.6993 | 123.5779 | 4.0512 | 123.5687 | 85.5927 | -0.36163 | 123.5779 | 4.0512 | 85.5927 | 113.6993 | 123.5687 | -123.8434 | -123.8663
5623.7188 | 123.7106 | -61.3815 | 62.1872 | -0.15388 | 0.018587 | 0.01085 | 0.017233 | 0.060889 | -0.00033333 | 0.081613 | -57.3486 | 62.2375 | -61.7294 | -61.5692 | 52.3224 | 24.147 | 8.9081 | 8.5968 | 62.2147 | -61.6974 | -0.3479 | 0.050354 | 4.0329 | -0.18768 | -9.8648 | -0.31586 | 0.027466 | 4.3808 | 70.2896 | 69.9783 | 113.7039 | 123.6191 | 4.0329 | 123.5962 | 85.5286 | -0.31586 | 123.6191 | 4.0329 | 85.5286 | 113.7039 | 123.5962 | -123.9166 | -123.8846
5624.7188 | 123.7518 | -61.3907 | 62.1689 | -0.17677 | 0.019015 | 0.016404 | 0.017447 | 0.060248 | -0.0018285 | 0.083749 | -57.2937 | 62.1964 | -61.702 | -61.5463 | 52.3453 | 24.4446 | 8.8715 | 8.5968 | 62.1918 | -61.702 | -0.31128 | 0.027466 | 4.097 | -0.15564 | -9.8236 | -0.31128 | 0.022888 | 4.4083 | 70.2621 | 69.9875 | 113.736 | 123.587 | 4.097 | 123.5825 | 85.8353 | -0.31128 | 123.587 | 4.097 | 85.8353 | 113.736 | 123.5825 | -123.8708 | -123.8708
5625.7188 | 123.7289 | -61.3724 | 62.1872 | -0.23018 | 0.021364 | 0.016191 | 0.016592 | 0.063025 | -0.00076053 | 0.082894 | -57.3532 | 62.2421 | -61.7249 | -61.5875 | 52.3178 | 24.2706 | 8.9447 | 8.6334 | 62.2467 | -61.7111 | -0.35248 | 0.054931 | 4.0192 | -0.21515 | -9.8694 | -0.33875 | 0.059509 | 4.3716 | 70.3171 | 70.0058 | 113.6902 | 123.6145 | 4.0192 | 123.6191 | 85.643 | -0.33875 | 123.6145 | 4.0192 | 85.643 | 113.6902 | 123.6191 | -123.912 | -123.8983
5626.7188 | 123.6832 | -61.377 | 62.2009 | -0.20729 | 0.020296 | 0.015763 | 0.013815 | 0.062384 | 0.00030767 | 0.084176 | -57.3441 | 62.2101 | -61.702 | -61.5875 | 52.2995 | 24.2889 | 8.9172 | 8.5831 | 62.2101 | -61.7249 | -0.32501 | 0.009155 | 4.0329 | -0.21057 | -9.9014 | -0.3479 | 0.009155 | 4.3579 | 70.2942 | 69.96 | 113.6765 | 123.587 | 4.0329 | 123.587 | 85.6659 | -0.3479 | 123.587 | 4.0329 | 85.6659 | 113.6765 | 123.587 | -123.9029 | -123.9258
5627.7188 | 123.6877 | -61.4044 | 62.1689 | 0.04448 | 0.019869 | 0.017899 | 0.018942 | 0.063025 | 0.0032983 | 0.082467 | -57.3349 | 62.1872 | -61.6974 | -61.615 | 52.2125 | 24.2569 | 8.8852 | 8.5419 | 62.1918 | -61.7294 | -0.29297 | 0.018311 | 4.0695 | -0.21057 | -9.9564 | -0.32501 | 0.022888 | 4.3625 | 70.2896 | 69.9463 | 113.6169 | 123.5916 | 4.0695 | 123.5962 | 85.6613 | -0.32501 | 123.5916 | 4.0695 | 85.6613 | 113.6169 | 123.5962 | -123.8663 | -123.8983
5628.7188 | 123.7289 | -61.3861 | 62.1872 | -0.131 | 0.021364 | 0.013841 | 0.016378 | 0.061316 | 0.00052127 | 0.081826 | -57.3395 | 62.2375 | -61.7249 | -61.5692 | 52.327 | 24.3073 | 8.9081 | 8.5876 | 62.2101 | -61.7249 | -0.33875 | 0.050354 | 4.0466 | -0.18311 | -9.8602 | -0.33875 | 0.022888 | 4.3854 | 70.2942 | 69.9738 | 113.7131 | 123.6237 | 4.0466 | 123.5962 | 85.6934 | -0.33875 | 123.6237 | 4.0466 | 85.6934 | 113.7131 | 123.5962 | -123.912 | -123.912
5629.7188 | 123.7015 | -61.3724 | 62.1872 | -0.14626 | 0.021364 | 0.018968 | 0.01531 | 0.062171 | 0.00030767 | 0.083962 | -57.3441 | 62.2375 | -61.6928 | -61.5784 | 52.2537 | 24.2065 | 8.9493 | 8.5739 | 62.2513 | -61.6791 | -0.32044 | 0.050354 | 4.0283 | -0.20599 | -9.9335 | -0.3067 | 0.064087 | 4.3488 | 70.3217 | 69.9463 | 113.6261 | 123.6099 | 4.0283 | 123.6237 | 85.5789 | -0.3067 | 123.6099 | 4.0283 | 85.5789 | 113.6261 | 123.6237 | -123.88 | -123.8663
5630.7188 | 123.6877 | -61.4182 | 62.1826 | -0.23781 | 0.022005 | 0.016191 | 0.015097 | 0.06388 | -0.00054693 | 0.083322 | -57.3441 | 62.2147 | -61.7157 | -61.5646 | 52.272 | 24.1882 | 8.9035 | 8.4915 | 62.2467 | -61.7111 | -0.29755 | 0.032044 | 4.0741 | -0.14648 | -9.9106 | -0.29297 | 0.064087 | 4.3716 | 70.3217 | 69.9097 | 113.6902 | 123.6328 | 4.0741 | 123.6649 | 85.6064 | -0.29297 | 123.6328 | 4.0741 | 85.6064 | 113.6902 | 123.6649 | -123.8983 | -123.8937
5631.7188 | 123.7244 | -61.3724 | 62.1964 | -0.24544 | 0.019869 | 0.014268 | 0.017447 | 0.063452 | -0.00011953 | 0.082467 | -57.28 | 62.2375 | -61.7111 | -61.5601 | 52.2903 | 24.2889 | 8.8943 | 8.5831 | 62.2192 | -61.6745 | -0.33875 | 0.041199 | 4.0924 | -0.18768 | -9.906 | -0.30213 | 0.022888 | 4.4312 | 70.2667 | 69.9554 | 113.6627 | 123.6099 | 4.0924 | 123.5916 | 85.6613 | -0.30213 | 123.6099 | 4.0924 | 85.6613 | 113.6627 | 123.5916 | -123.9075 | -123.8709
5632.7188 | 123.7015 | -61.4044 | 62.178 | 0.052109 | 0.022005 | 0.018113 | 0.018728 | 0.062384 | -0.00076053 | 0.08204 | -57.2937 | 62.2147 | -61.7386 | -61.615 | 52.2217 | 24.2706 | 8.876 | 8.4686 | 62.2192 | -61.6974 | -0.33417 | 0.036621 | 4.1107 | -0.21057 | -9.9564 | -0.29297 | 0.041198 | 4.4449 | 70.2805 | 69.873 | 113.6261 | 123.6191 | 4.1107 | 123.6237 | 85.675 | -0.29297 | 123.6191 | 4.1107 | 85.675 | 113.6261 | 123.6237 | -123.9166 | -123.8754
5633.7188 | 123.7015 | -61.3907 | 62.2009 | 0.92949 | 0.02051 | 0.019395 | 0.014883 | 0.059821 | -0.00011953 | 0.081399 | -57.4081 | 62.2375 | -61.7294 | -61.6058 | 52.2766 | 24.2981 | 8.9401 | 8.5464 | 62.1964 | -61.7386 | -0.33874 | 0.036621 | 3.9825 | -0.21515 | -9.9243 | -0.3479 | -0.004578 | 4.3213 | 70.3308 | 69.9371 | 113.6673 | 123.6282 | 3.9825 | 123.587 | 85.6888 | -0.3479 | 123.6282 | 3.9825 | 85.6888 | 113.6673 | 123.587 | -123.9304 | -123.9395
5634.7188 | 123.7289 | -61.377 | 62.1872 | -0.22255 | 0.020083 | 0.015336 | 0.016378 | 0.060889 | 0.00052127 | 0.082253 | -57.3303 | 62.2238 | -61.7203 | -61.5784 | 52.2217 | 24.2477 | 8.9584 | 8.5785 | 62.2101 | -61.7111 | -0.34332 | 0.036621 | 4.0466 | -0.20142 | -9.9655 | -0.33417 | 0.022888 | 4.39 | 70.3354 | 69.9554 | 113.5986 | 123.6008 | 4.0466 | 123.587 | 85.6247 | -0.33417 | 123.6008 | 4.0466 | 85.6247 | 113.5986 | 123.587 | -123.9075 | -123.8983
5635.7188 | 123.7061 | -61.3953 | 62.1826 | -0.21492 | 0.019442 | 0.015122 | 0.016806 | 0.060462 | -0.0011877 | 0.085031 | -57.2983 | 62.1964 | -61.702 | -61.5875 | 52.2354 | 24.2844 | 8.9859 | 8.5968 | 62.2055 | -61.6882 | -0.3067 | 0.013733 | 4.097 | -0.19226 | -9.9472 | -0.29297 | 0.022888 | 4.4037 | 70.3812 | 69.9921 | 113.6307 | 123.5916 | 4.097 | 123.6008 | 85.6796 | -0.29297 | 123.5916 | 4.097 | 85.6796 | 113.6307 | 123.6008 | -123.8846 | -123.8708
5636.7188 | 123.6877 | -61.3815 | 62.2009 | -0.16914 | 0.019869 | 0.014695 | 0.016378 | 0.061103 | -0.00033333 | 0.082894 | -57.3257 | 62.2147 | -61.702 | -61.5692 | 52.1896 | 24.2523 | 8.9676 | 8.5419 | 62.2009 | -61.6837 | -0.32043 | 0.013733 | 4.0558 | -0.18768 | -10.0113 | -0.30212 | 0 | 4.3762 | 70.3491 | 69.9234 | 113.5712 | 123.5962 | 4.0558 | 123.5825 | 85.6338 | -0.30212 | 123.5962 | 4.0558 | 85.6338 | 113.5712 | 123.5825 | -123.9029 | -123.8846
5637.7188 | 123.6694 | -61.4182 | 62.2009 | 0.059738 | 0.021792 | 0.019608 | 0.019583 | 0.06388 | 0.00094847 | 0.082467 | -57.28 | 62.2055 | -61.702 | -61.615 | 52.2034 | 24.2706 | 8.8989 | 8.519 | 62.1872 | -61.734 | -0.28381 | 0.004577 | 4.1382 | -0.19684 | -9.9976 | -0.31586 | -0.013733 | 4.422 | 70.3171 | 69.9371 | 113.6215 | 123.6237 | 4.1382 | 123.6053 | 85.6888 | -0.31586 | 123.6237 | 4.1382 | 85.6888 | 113.6215 | 123.6053 | -123.9029 | -123.9349
5638.7188 | 123.7244 | -61.3632 | 62.1872 | -0.20729 | 0.019015 | 0.0099954 | 0.016378 | 0.061103 | -0.0016149 | 0.082681 | -57.2754 | 62.2147 | -61.6928 | -61.5692 | 52.1988 | 24.2432 | 8.9447 | 8.5876 | 62.2375 | -61.6928 | -0.32959 | 0.027466 | 4.0878 | -0.20599 | -9.9884 | -0.32959 | 0.050354 | 4.4174 | 70.3079 | 69.9509 | 113.562 | 123.5779 | 4.0878 | 123.6008 | 85.6064 | -0.32959 | 123.5779 | 4.0878 | 85.6064 | 113.562 | 123.6008 | -123.88 | -123.88
5639.7188 | 123.6557 | -61.3953 | 62.1918 | -0.22255 | 0.019015 | 0.0097818 | 0.014669 | 0.06153 | 0.0028711 | 0.083108 | -57.3074 | 62.2055 | -61.6974 | -61.496 | 52.4277 | 24.2615 | 8.7891 | 8.6197 | 62.2192 | -61.6974 | -0.30212 | 0.013733 | 4.0878 | -0.10071 | -9.7641 | -0.30212 | 0.027466 | 4.39 | 70.1843 | 70.015 | 113.8229 | 123.6008 | 4.0878 | 123.6145 | 85.6567 | -0.30212 | 123.6008 | 4.0878 | 85.6567 | 113.8229 | 123.6145 | -123.8892 | -123.8892
5640.7188 | 123.6969 | -61.3861 | 62.178 | -0.23781 | 0.020083 | 0.010636 | 0.016592 | 0.062171 | -0.00033333 | 0.083108 | -57.2891 | 62.2238 | -61.7203 | -61.5829 | 52.2263 | 24.1882 | 9.05 | 8.6426 | 62.2375 | -61.6882 | -0.33417 | 0.045776 | 4.097 | -0.19684 | -9.9518 | -0.30212 | 0.059509 | 4.4312 | 70.4361 | 70.0287 | 113.6124 | 123.6099 | 4.097 | 123.6237 | 85.5743 | -0.30212 | 123.6099 | 4.097 | 85.5743 | 113.6124 | 123.6237 | -123.8983 | -123.8663
5641.7188 | 123.674 | -61.3724 | 62.178 | -0.50484 | 0.019015 | 0.014054 | 0.017019 | 0.059821 | -0.0016149 | 0.084176 | -57.3532 | 62.1918 | -61.7111 | -61.5738 | 52.1942 | 24.2157 | 9.0317 | 8.6334 | 62.2238 | -61.6928 | -0.33875 | 0.013732 | 4.0192 | -0.20142 | -9.9838 | -0.32044 | 0.045776 | 4.3579 | 70.4041 | 70.0058 | 113.5666 | 123.5641 | 4.0192 | 123.5962 | 85.5881 | -0.32044 | 123.5641 | 4.0192 | 85.5881 | 113.5666 | 123.5962 | -123.8892 | -123.8709
5642.7188 | 123.6649 | -61.3998 | 62.178 | 0.021591 | 0.023287 | 0.014482 | 0.019796 | 0.061103 | -0.0018285 | 0.082894 | -57.2296 | 62.1872 | -61.734 | -61.5921 | 52.2171 | 24.2432 | 8.9493 | 8.5922 | 62.1826 | -61.7249 | -0.33417 | 0.009155 | 4.1702 | -0.19226 | -9.9609 | -0.32501 | 0.004577 | 4.5044 | 70.3491 | 69.9921 | 113.6169 | 123.587 | 4.1702 | 123.5825 | 85.643 | -0.32501 | 123.587 | 4.1702 | 85.643 | 113.6169 | 123.5825 | -123.912 | -123.9029
5643.7188 | 123.6832 | -61.3815 | 62.2101 | -0.1844 | 0.018374 | 0.016191 | 0.013174 | 0.060034 | 0.00094847 | 0.083535 | -57.2754 | 62.2055 | -61.7065 | -61.5784 | 52.1667 | 24.234 | 8.9996 | 8.6334 | 62.233 | -61.6699 | -0.32501 | -0.004578 | 4.1061 | -0.19684 | -10.0433 | -0.28839 | 0.022888 | 4.4312 | 70.3812 | 70.015 | 113.5483 | 123.587 | 4.1061 | 123.6145 | 85.6155 | -0.28839 | 123.587 | 4.1061 | 85.6155 | 113.5483 | 123.6145 | -123.9166 | -123.88
5644.7188 | 123.674 | -61.377 | 62.2009 | -0.09285 | 0.01581 | 0.013841 | 0.017019 | 0.060248 | 0.0013757 | 0.082467 | -57.1747 | 62.1964 | -61.702 | -61.5738 | 52.1713 | 24.1699 | 9.05 | 8.6151 | 62.1918 | -61.6791 | -0.32501 | -0.004578 | 4.2023 | -0.19684 | -10.0296 | -0.30212 | -0.009156 | 4.5273 | 70.4269 | 69.9921 | 113.5483 | 123.5733 | 4.2023 | 123.5687 | 85.5469 | -0.30212 | 123.5733 | 4.2023 | 85.5469 | 113.5483 | 123.5687 | -123.9029 | -123.88
5645.7188 | 123.761 | -61.3403 | 62.2192 | -0.2607 | 0.019656 | 0.017686 | 0.014029 | 0.059607 | 0.00094847 | 0.08204 | -57.28 | 62.1964 | -61.6974 | -61.5784 | 52.1988 | 24.2752 | 9.0546 | 8.6472 | 62.2055 | -61.6928 | -0.35706 | -0.022888 | 4.0604 | -0.23804 | -10.0204 | -0.35248 | -0.013733 | 4.4174 | 70.3949 | 69.9875 | 113.5391 | 123.5367 | 4.0604 | 123.5458 | 85.6155 | -0.35248 | 123.5367 | 4.0604 | 85.6155 | 113.5391 | 123.5458 | -123.9166 | -123.912
5646.7188 | 123.7564 | -61.3678 | 62.1643 | -0.1844 | 0.016665 | 0.015977 | 0.011679 | 0.059394 | 0.00073487 | 0.084603 | -57.193 | 62.1643 | -61.6653 | -61.4914 | 52.2171 | 24.3073 | 8.9447 | 8.757 | 62.1689 | -61.6379 | -0.29755 | 0 | 4.1748 | -0.1236 | -9.9472 | -0.27008 | 0.004577 | 4.4724 | 70.3125 | 70.1248 | 113.5849 | 123.5321 | 4.1748 | 123.5367 | 85.675 | -0.27008 | 123.5321 | 4.1748 | 85.675 | 113.5849 | 123.5367 | -123.8297 | -123.8022
5647.7188 | 123.793 | -61.3449 | 62.1735 | -0.16914 | 0.017947 | 0.013627 | 0.01232 | 0.058753 | -0.00054693 | 0.082894 | -57.1976 | 62.0956 | -61.6837 | -61.496 | 52.2583 | 24.3851 | 8.9081 | 8.8074 | 62.1552 | -61.647 | -0.33875 | -0.07782 | 4.1473 | -0.15106 | -9.9152 | -0.30212 | -0.018311 | 4.4861 | 70.253 | 70.1523 | 113.6032 | 123.4406 | 4.1473 | 123.5001 | 85.73 | -0.30212 | 123.4406 | 4.1473 | 85.73 | 113.6032 | 123.5001 | -123.8571 | -123.8205
5648.7188 | 123.7885 | -61.3495 | 62.146 | -0.22255 | 0.019015 | 0.012773 | 0.014456 | 0.060034 | -0.00097413 | 0.081185 | -57.2113 | 62.1277 | -61.6745 | -61.4868 | 52.2491 | 24.3393 | 8.9401 | 8.7662 | 62.1735 | -61.6745 | -0.32501 | -0.01831 | 4.1382 | -0.13733 | -9.8968 | -0.32501 | 0.027466 | 4.4632 | 70.2896 | 70.1157 | 113.5986 | 123.4772 | 4.1382 | 123.5229 | 85.6888 | -0.32501 | 123.4772 | 4.1382 | 85.6888 | 113.5986 | 123.5229 | -123.8205 | -123.8205
5649.7188 | 123.7885 | -61.3403 | 62.1735 | -0.23018 | 0.017519 | 0.010636 | 0.013388 | 0.056189 | -0.0018285 | 0.083108 | -57.1838 | 62.114 | -61.6699 | -61.4914 | 52.2308 | 24.3027 | 8.9447 | 8.8486 | 62.1368 | -61.6516 | -0.32959 | -0.059509 | 4.1565 | -0.15106 | -9.9426 | -0.31128 | -0.036621 | 4.4861 | 70.285 | 70.1889 | 113.5712 | 123.4543 | 4.1565 | 123.4772 | 85.643 | -0.31128 | 123.4543 | 4.1565 | 85.643 | 113.5712 | 123.4772 | -123.8434 | -123.8251
5650.7188 | 123.8022 | -61.3403 | 62.1552 | -0.19203 | 0.016451 | 0.012986 | 0.014669 | 0.057471 | -0.00011953 | 0.083322 | -56.9183 | 62.178 | -61.6333 | -61.4914 | 52.2537 | 24.3851 | 8.8623 | 8.8486 | 62.1552 | -61.6516 | -0.29297 | 0.022889 | 4.422 | -0.15106 | -9.9014 | -0.31128 | 0 | 4.715 | 70.2026 | 70.1889 | 113.5941 | 123.5184 | 4.422 | 123.4955 | 85.7254 | -0.31128 | 123.5184 | 4.422 | 85.7254 | 113.5941 | 123.4955 | -123.7885 | -123.8068
5651.7188 | 123.8525 | -61.3495 | 62.1552 | -0.22255 | 0.016665 | 0.011918 | 0.013388 | 0.056403 | 0.00052127 | 0.083535 | -57.1701 | 62.0865 | -61.6791 | -61.4685 | 52.2583 | 24.4583 | 8.9035 | 8.8303 | 62.146 | -61.6425 | -0.32959 | -0.068664 | 4.1794 | -0.11902 | -9.8968 | -0.29297 | -0.009155 | 4.509 | 70.253 | 70.1797 | 113.6078 | 123.436 | 4.1794 | 123.4955 | 85.8078 | -0.29297 | 123.436 | 4.1794 | 85.8078 | 113.6078 | 123.4955 | -123.8342 | -123.7976
5652.7188 | 123.6832 | -61.3541 | 62.2147 | -0.23018 | 0.019869 | 0.011491 | 0.015738 | 0.058112 | 9.4068e-05 | 0.08204 | -57.225 | 62.178 | -61.6974 | -61.5692 | 52.0935 | 24.2798 | 9.0591 | 8.7341 | 62.2009 | -61.6974 | -0.34332 | -0.036621 | 4.129 | -0.21515 | -10.1212 | -0.34332 | -0.013733 | 4.4724 | 70.4132 | 70.0882 | 113.4476 | 123.5321 | 4.129 | 123.555 | 85.6338 | -0.34332 | 123.5321 | 4.129 | 85.6338 | 113.4476 | 123.555 | -123.912 | -123.912
5653.7188 | 123.8205 | -61.3678 | 62.1552 | -0.10811 | 0.015383 | 0.015336 | 0.013601 | 0.057898 | -0.00054693 | 0.08204 | -57.2113 | 62.0865 | -61.6882 | -61.4914 | 52.1942 | 24.3622 | 8.8852 | 8.8531 | 62.1414 | -61.6333 | -0.32043 | -0.068664 | 4.1565 | -0.1236 | -9.9609 | -0.2655 | -0.013733 | 4.4769 | 70.253 | 70.2209 | 113.562 | 123.4543 | 4.1565 | 123.5092 | 85.73 | -0.2655 | 123.4543 | 4.1565 | 85.73 | 113.562 | 123.5092 | -123.8434 | -123.7885
5654.7188 | 123.793 | -61.3449 | 62.1506 | -0.031814 | 0.018801 | 0.016831 | 0.014669 | 0.057257 | 0.00030767 | 0.082681 | -57.225 | 62.0865 | -61.7065 | -61.5051 | 52.1484 | 24.2569 | 8.9172 | 8.7845 | 62.1185 | -61.647 | -0.36163 | -0.064087 | 4.1199 | -0.16022 | -10.0021 | -0.30212 | -0.032044 | 4.4815 | 70.2621 | 70.1294 | 113.4933 | 123.4314 | 4.1199 | 123.4634 | 85.6018 | -0.30212 | 123.4314 | 4.1199 | 85.6018 | 113.4933 | 123.4634 | -123.8571 | -123.7976
5655.7188 | 123.8068 | -61.3358 | 62.1277 | -0.13863 | 0.017092 | 0.014268 | 0.01296 | 0.055762 | -0.00011953 | 0.082253 | -57.193 | 62.1002 | -61.702 | -61.4914 | 52.1851 | 24.3439 | 8.8715 | 8.757 | 62.1414 | -61.6379 | -0.36621 | -0.027466 | 4.1428 | -0.15564 | -9.9426 | -0.30212 | 0.013732 | 4.509 | 70.2072 | 70.0928 | 113.5208 | 123.436 | 4.1428 | 123.4772 | 85.6796 | -0.30212 | 123.436 | 4.1428 | 85.6796 | 113.5208 | 123.4772 | -123.8297 | -123.7656
5656.7188 | 123.8022 | -61.3449 | 62.1323 | -0.016556 | 0.016451 | 0.011704 | 0.012533 | 0.055335 | 0.0018031 | 0.083108 | -57.1976 | 62.0911 | -61.6791 | -61.5234 | 52.1942 | 24.3713 | 8.8715 | 8.7524 | 62.1048 | -61.6608 | -0.33417 | -0.041199 | 4.1473 | -0.17853 | -9.938 | -0.31586 | -0.027466 | 4.4815 | 70.2164 | 70.0974 | 113.5391 | 123.436 | 4.1473 | 123.4497 | 85.7162 | -0.31586 | 123.436 | 4.1473 | 85.7162 | 113.5391 | 123.4497 | -123.8113 | -123.793
5657.7188 | 123.7747 | -61.3403 | 62.1643 | -0.19203 | 0.016878 | 0.0095682 | 0.015524 | 0.057898 | -0.00011953 | 0.082894 | -57.1609 | 62.1277 | -61.6791 | -61.4731 | 52.1942 | 24.4125 | 8.9493 | 8.8165 | 62.1277 | -61.6333 | -0.33875 | -0.036621 | 4.1794 | -0.13275 | -9.9701 | -0.29297 | -0.036621 | 4.5181 | 70.2896 | 70.1569 | 113.5345 | 123.468 | 4.1794 | 123.468 | 85.7529 | -0.29297 | 123.468 | 4.1794 | 85.7529 | 113.5345 | 123.468 | -123.8434 | -123.7976
5658.7188 | 123.8251 | -61.3449 | 62.1597 | -0.024185 | 0.016451 | 0.011704 | 0.013601 | 0.057257 | 0.00094847 | 0.082681 | -57.2067 | 62.0773 | -61.6882 | -61.5051 | 52.1851 | 24.408 | 8.9218 | 8.7753 | 62.1323 | -61.6562 | -0.34332 | -0.082397 | 4.1382 | -0.16022 | -9.9747 | -0.31128 | -0.027466 | 4.4815 | 70.2667 | 70.1202 | 113.53 | 123.4222 | 4.1382 | 123.4772 | 85.7529 | -0.31128 | 123.4222 | 4.1382 | 85.7529 | 113.53 | 123.4772 | -123.848 | -123.8159
5659.7188 | 123.7976 | -61.3678 | 62.1552 | -0.0012969 | 0.015383 | 0.015336 | 0.013174 | 0.058539 | 0.00052127 | 0.08204 | -57.2159 | 62.0911 | -61.6928 | -61.5234 | 52.1805 | 24.4171 | 8.8394 | 8.7112 | 62.1506 | -61.6562 | -0.32501 | -0.064087 | 4.1519 | -0.15564 | -9.9747 | -0.28839 | -0.004577 | 4.4769 | 70.2072 | 70.079 | 113.5483 | 123.4589 | 4.1519 | 123.5184 | 85.7849 | -0.28839 | 123.4589 | 4.1519 | 85.7849 | 113.5483 | 123.5184 | -123.848 | -123.8113
5660.7188 | 123.7473 | -61.3495 | 62.1414 | 0.059738 | 0.016665 | 0.014054 | 0.014242 | 0.058539 | -0.00097413 | 0.083322 | -57.2067 | 62.0728 | -61.7065 | -61.5509 | 52.1713 | 24.4354 | 8.8211 | 8.7021 | 62.1048 | -61.6425 | -0.35706 | -0.068664 | 4.1428 | -0.20142 | -9.9701 | -0.29297 | -0.036621 | 4.4998 | 70.1706 | 70.0516 | 113.5208 | 123.4222 | 4.1428 | 123.4543 | 85.7849 | -0.29297 | 123.4222 | 4.1428 | 85.7849 | 113.5208 | 123.4543 | -123.848 | -123.7839
5661.7188 | 123.7839 | -61.3586 | 62.1231 | 0.082626 | 0.019015 | 0.016831 | 0.014669 | 0.057471 | 0.0026575 | 0.083322 | -57.1838 | 62.0728 | -61.7111 | -61.528 | 52.1713 | 24.3668 | 8.7891 | 8.6655 | 62.1185 | -61.6837 | -0.35248 | -0.050354 | 4.1748 | -0.16937 | -9.9518 | -0.32501 | -0.004578 | 4.5273 | 70.1477 | 70.0241 | 113.53 | 123.4314 | 4.1748 | 123.4772 | 85.7254 | -0.32501 | 123.4314 | 4.1748 | 85.7254 | 113.53 | 123.4772 | -123.8342 | -123.8068
5662.7188 | 123.7839 | -61.3037 | 62.2009 | -0.11574 | 0.017092 | 0.011064 | 0.013174 | 0.057685 | -0.00011953 | 0.08439 | -57.1426 | 62.0956 | -61.6699 | -61.4365 | 52.3041 | 24.5087 | 8.8303 | 8.7708 | 62.1323 | -61.647 | -0.36621 | -0.10529 | 4.1611 | -0.13275 | -9.8969 | -0.34332 | -0.068665 | 4.5273 | 70.134 | 70.0745 | 113.6078 | 123.3994 | 4.1611 | 123.436 | 85.8124 | -0.34332 | 123.3994 | 4.1611 | 85.8124 | 113.6078 | 123.436 | -123.8708 | -123.848
5663.7188 | 123.7335 | -61.3541 | 62.1277 | 0.11314 | 0.017306 | 0.014054 | 0.013388 | 0.05683 | 0.0013757 | 0.085031 | -57.1884 | 62.0819 | -61.7203 | -61.5326 | 52.1988 | 24.3851 | 8.8211 | 8.67 | 62.1094 | -61.6562 | -0.36621 | -0.045777 | 4.1656 | -0.17853 | -9.9289 | -0.30212 | -0.018311 | 4.5319 | 70.1752 | 70.0241 | 113.5529 | 123.436 | 4.1656 | 123.4634 | 85.7391 | -0.30212 | 123.436 | 4.1656 | 85.7391 | 113.5529 | 123.4634 | -123.848 | -123.7839
5664.7188 | 123.7427 | -61.3724 | 62.1277 | 0.15892 | 0.02051 | 0.014482 | 0.01296 | 0.058325 | -0.00011953 | 0.082681 | -57.1655 | 62.0819 | -61.6791 | -61.528 | 52.1255 | 24.3484 | 8.7662 | 8.6517 | 62.1323 | -61.6699 | -0.3067 | -0.045777 | 4.2068 | -0.15564 | -10.0021 | -0.29755 | 0.004577 | 4.5136 | 70.1385 | 70.0241 | 113.4979 | 123.4543 | 4.2068 | 123.5046 | 85.7208 | -0.29755 | 123.4543 | 4.2068 | 85.7208 | 113.4979 | 123.5046 | -123.8068 | -123.7976
5665.7188 | 123.7335 | -61.3358 | 62.1368 | 0.090256 | 0.018587 | 0.014695 | 0.015097 | 0.058753 | -0.00011953 | 0.080972 | -57.1838 | 62.0728 | -61.7065 | -61.5372 | 52.1118 | 24.3896 | 8.8715 | 8.6746 | 62.1002 | -61.6425 | -0.37079 | -0.064087 | 4.1519 | -0.20142 | -10.025 | -0.3067 | -0.036621 | 4.5227 | 70.2072 | 70.0104 | 113.4476 | 123.4085 | 4.1519 | 123.436 | 85.7254 | -0.3067 | 123.4085 | 4.1519 | 85.7254 | 113.4476 | 123.436 | -123.8434 | -123.7793
5666.7188 | 123.7381 | -61.3724 | 62.1231 | 0.059738 | 0.018801 | 0.019822 | 0.015097 | 0.059821 | 0.00094847 | 0.083749 | -57.1609 | 62.0682 | -61.6974 | -61.5417 | 52.0798 | 24.3439 | 8.7982 | 8.6792 | 62.0911 | -61.6516 | -0.32501 | -0.054932 | 4.2114 | -0.16937 | -10.0433 | -0.27924 | -0.032044 | 4.5364 | 70.1706 | 70.0516 | 113.4521 | 123.4406 | 4.2114 | 123.4634 | 85.7162 | -0.27924 | 123.4406 | 4.2114 | 85.7162 | 113.4521 | 123.4634 | -123.8205 | -123.7747
5667.7188 | 123.793 | -61.3449 | 62.1506 | -0.0012969 | 0.016878 | 0.017472 | 0.01296 | 0.058325 | 9.4068e-05 | 0.085885 | -57.193 | 62.1185 | -61.6882 | -61.5097 | 52.1027 | 24.4171 | 8.844 | 8.7021 | 62.1185 | -61.6699 | -0.34332 | -0.032044 | 4.1519 | -0.16479 | -10.0479 | -0.32501 | -0.032044 | 4.4952 | 70.1889 | 70.047 | 113.4476 | 123.4634 | 4.1519 | 123.4634 | 85.762 | -0.32501 | 123.4634 | 4.1519 | 85.762 | 113.4476 | 123.4634 | -123.8388 | -123.8205
5668.7188 | 123.7747 | -61.3495 | 62.1094 | 0.23521 | 0.018587 | 0.016191 | 0.018087 | 0.059394 | -0.00097413 | 0.083108 | -57.2708 | 62.0911 | -61.6928 | -61.5005 | 52.121 | 24.4629 | 8.7479 | 8.6655 | 62.0956 | -61.6699 | -0.34332 | -0.018311 | 4.0787 | -0.15106 | -9.9884 | -0.32043 | -0.013733 | 4.422 | 70.0974 | 70.015 | 113.4705 | 123.4406 | 4.0787 | 123.4451 | 85.8124 | -0.32043 | 123.4406 | 4.0787 | 85.8124 | 113.4705 | 123.4451 | -123.8022 | -123.7793
5669.7188 | 123.7885 | -61.3495 | 62.1185 | 0.15129 | 0.017733 | 0.017899 | 0.016592 | 0.059607 | -0.00076053 | 0.083322 | -57.106 | 62.0911 | -61.6974 | -61.496 | 52.1072 | 24.4308 | 8.7387 | 8.7112 | 62.1002 | -61.647 | -0.3479 | -0.027466 | 4.2435 | -0.14648 | -10.0113 | -0.29755 | -0.01831 | 4.5914 | 70.0882 | 70.0607 | 113.4567 | 123.4406 | 4.2435 | 123.4497 | 85.7803 | -0.29755 | 123.4406 | 4.2435 | 85.7803 | 113.4567 | 123.4497 | -123.8159 | -123.7656
5670.7188 | 123.8068 | -61.3541 | 62.1323 | 0.013962 | 0.022219 | 0.022172 | 0.017447 | 0.057898 | -0.00097413 | 0.084603 | -57.1198 | 62.0911 | -61.7111 | -61.4914 | 52.121 | 24.472 | 8.7479 | 8.757 | 62.0956 | -61.6653 | -0.35706 | -0.041199 | 4.2343 | -0.13733 | -10.0113 | -0.31128 | -0.036621 | 4.5914 | 70.1019 | 70.1111 | 113.475 | 123.4451 | 4.2343 | 123.4497 | 85.8261 | -0.31128 | 123.4451 | 4.2343 | 85.8261 | 113.475 | 123.4497 | -123.8434 | -123.7976
5671.7188 | 123.7976 | -61.3449 | 62.1048 | 1.6848 | 0.020937 | 0.016618 | 0.017019 | 0.059821 | 0.0041529 | 0.082253 | -57.0694 | 62.0956 | -61.6974 | -61.5051 | 52.1347 | 24.3988 | 8.7067 | 8.7616 | 62.0911 | -61.6699 | -0.35248 | -0.009155 | 4.2755 | -0.16022 | -9.9701 | -0.32501 | -0.013733 | 4.628 | 70.0516 | 70.1065 | 113.4796 | 123.4406 | 4.2755 | 123.436 | 85.7437 | -0.32501 | 123.4406 | 4.2755 | 85.7437 | 113.4796 | 123.436 | -123.8022 | -123.7747
5672.7188 | 123.7656 | -61.3632 | 62.1094 | 0.0063326 | 0.02051 | 0.016618 | 0.017874 | 0.057685 | -0.00033333 | 0.083108 | -57.2159 | 62.1231 | -61.702 | -61.5601 | 52.0889 | 24.3439 | 8.8394 | 8.7021 | 62.1002 | -61.6608 | -0.33875 | 0.013733 | 4.1473 | -0.19684 | -10.0204 | -0.29755 | -0.009155 | 4.4861 | 70.2026 | 70.0653 | 113.4521 | 123.4863 | 4.1473 | 123.4634 | 85.7071 | -0.29755 | 123.4863 | 4.1473 | 85.7071 | 113.4521 | 123.4634 | -123.8113 | -123.7701
5673.7188 | 123.7839 | -61.3541 | 62.114 | 0.11314 | 0.019228 | 0.02089 | 0.021078 | 0.059607 | -0.00054693 | 0.085031 | -57.0831 | 62.0956 | -61.6791 | -61.5189 | 52.066 | 24.3942 | 8.7479 | 8.725 | 62.0819 | -61.6745 | -0.32501 | -0.018311 | 4.2709 | -0.16479 | -10.0479 | -0.32044 | -0.032044 | 4.5959 | 70.1019 | 70.079 | 113.4201 | 123.4497 | 4.2709 | 123.436 | 85.7483 | -0.32044 | 123.4497 | 4.2709 | 85.7483 | 113.4201 | 123.436 | -123.793 | -123.7885
5674.7188 | 123.8251 | -61.3678 | 62.1002 | 0.24284 | 0.021151 | 0.015977 | 0.018301 | 0.060248 | -0.00097413 | 0.082894 | -57.106 | 62.1277 | -61.702 | -61.5005 | 52.0523 | 24.3484 | 8.7799 | 8.6929 | 62.0956 | -61.6745 | -0.33417 | 0.027466 | 4.2618 | -0.13275 | -10.0479 | -0.3067 | -0.004578 | 4.5959 | 70.1477 | 70.0607 | 113.4201 | 123.4955 | 4.2618 | 123.4634 | 85.7162 | -0.3067 | 123.4955 | 4.2618 | 85.7162 | 113.4201 | 123.4634 | -123.8022 | -123.7747
5675.7188 | 123.7793 | -61.3724 | 62.1277 | 0.22758 | 0.021792 | 0.016618 | 0.019796 | 0.059821 | -0.00097413 | 0.083535 | -57.1289 | 62.1506 | -61.7111 | -61.5326 | 51.9974 | 24.3942 | 8.7296 | 8.6609 | 62.0956 | -61.6562 | -0.33875 | 0.022888 | 4.2435 | -0.16022 | -10.1303 | -0.28381 | -0.032044 | 4.5822 | 70.1019 | 70.0333 | 113.3697 | 123.5229 | 4.2435 | 123.468 | 85.7666 | -0.28381 | 123.5229 | 4.2435 | 85.7666 | 113.3697 | 123.468 | -123.8388 | -123.7839
5676.7188 | 123.8205 | -61.3495 | 62.1002 | 0.22758 | 0.023501 | 0.021317 | 0.018728 | 0.060034 | -0.00054693 | 0.083322 | -57.0602 | 62.1185 | -61.7065 | -61.5005 | 51.9699 | 24.353 | 8.6746 | 8.6975 | 62.1002 | -61.6699 | -0.35706 | 0.01831 | 4.2892 | -0.15106 | -10.1303 | -0.32043 | 0 | 4.6463 | 70.0241 | 70.047 | 113.3194 | 123.468 | 4.2892 | 123.4497 | 85.7025 | -0.32043 | 123.468 | 4.2892 | 85.7025 | 113.3194 | 123.4497 | -123.8068 | -123.7701
5677.7188 | 123.7701 | -61.3495 | 62.1231 | 0.23521 | 0.020937 | 0.017045 | 0.019369 | 0.062598 | 0.00073487 | 0.083108 | -57.074 | 62.1323 | -61.6653 | -61.5143 | 51.9516 | 24.3118 | 8.725 | 8.7158 | 62.0865 | -61.6928 | -0.31586 | 0.009155 | 4.2755 | -0.16479 | -10.1715 | -0.34332 | -0.036621 | 4.5914 | 70.0745 | 70.0653 | 113.3011 | 123.4818 | 4.2755 | 123.436 | 85.6613 | -0.34332 | 123.4818 | 4.2755 | 85.6613 | 113.3011 | 123.436 | -123.7885 | -123.8159
5678.7188 | 123.7793 | -61.377 | 62.0911 | 0.21233 | 0.023714 | 0.017472 | 0.018087 | 0.061316 | 0.00094847 | 0.083322 | -57.1152 | 62.1506 | -61.6974 | -61.5463 | 51.915 | 24.2935 | 8.7845 | 8.7433 | 62.1185 | -61.702 | -0.32043 | 0.05951 | 4.2618 | -0.16937 | -10.1761 | -0.32501 | 0.027466 | 4.5822 | 70.1614 | 70.1202 | 113.2919 | 123.5275 | 4.2618 | 123.4955 | 85.6705 | -0.32501 | 123.5275 | 4.2618 | 85.6705 | 113.2919 | 123.4955 | -123.7885 | -123.793
5679.7188 | 123.8251 | -61.3586 | 62.0682 | 0.15129 | 0.023287 | 0.020036 | 0.018301 | 0.062171 | 0.00052127 | 0.08439 | -57.0602 | 62.1094 | -61.6928 | -61.5051 | 51.947 | 24.3256 | 8.7204 | 8.7021 | 62.0911 | -61.6425 | -0.33417 | 0.041199 | 4.2984 | -0.14648 | -10.1212 | -0.28381 | 0.022888 | 4.6326 | 70.079 | 70.0607 | 113.3057 | 123.468 | 4.2984 | 123.4497 | 85.6842 | -0.28381 | 123.468 | 4.2984 | 85.6842 | 113.3057 | 123.4497 | -123.761 | -123.7106
5680.7188 | 123.8159 | -61.3632 | 62.114 | 0.18181 | 0.022219 | 0.016404 | 0.018515 | 0.061103 | -0.00033333 | 0.084817 | -57.0877 | 62.1323 | -61.7157 | -61.5097 | 51.9424 | 24.3118 | 8.7158 | 8.7204 | 62.1048 | -61.6882 | -0.35248 | 0.01831 | 4.2755 | -0.14648 | -10.1715 | -0.32501 | -0.009156 | 4.628 | 70.079 | 70.0836 | 113.3057 | 123.4955 | 4.2755 | 123.468 | 85.675 | -0.32501 | 123.4955 | 4.2755 | 85.675 | 113.3057 | 123.468 | -123.8297 | -123.8022
5681.7188 | 123.6923 | -61.3815 | 62.1277 | 0.1284 | 0.022005 | 0.017045 | 0.020437 | 0.060462 | 0.00073487 | 0.085671 | -57.1289 | 62.1872 | -61.7294 | -61.6058 | 51.9104 | 24.2065 | 8.8577 | 8.5968 | 62.178 | -61.7111 | -0.3479 | 0.059509 | 4.2526 | -0.2243 | -10.2173 | -0.32959 | 0.050354 | 4.6005 | 70.2393 | 69.9783 | 113.2919 | 123.5687 | 4.2526 | 123.5596 | 85.5881 | -0.32959 | 123.5687 | 4.2526 | 85.5881 | 113.2919 | 123.5596 | -123.8571 | -123.8388
5682.7188 | 123.7564 | -61.3266 | 62.1185 | 0.067368 | 0.017947 | 0.012773 | 0.011038 | 0.060675 | -0.00033333 | 0.083749 | -57.1335 | 62.1002 | -61.7111 | -61.5692 | 51.9287 | 24.2706 | 8.7891 | 8.7067 | 62.1094 | -61.6608 | -0.38452 | -0.01831 | 4.1931 | -0.24262 | -10.1898 | -0.33417 | -0.009155 | 4.5776 | 70.1157 | 70.0333 | 113.2553 | 123.4268 | 4.1931 | 123.436 | 85.5972 | -0.33417 | 123.4268 | 4.1931 | 85.5972 | 113.2553 | 123.436 | -123.8297 | -123.7793
5683.7344 | 123.8022 | -61.3403 | 62.1506 | -0.069961 | 0.021151 | 0.015336 | 0.01232 | 0.058112 | -0.00097413 | 0.085244 | -57.0831 | 62.1094 | -61.6928 | -61.496 | 51.9791 | 24.2935 | 8.7662 | 8.7616 | 62.1323 | -61.6516 | -0.35248 | -0.041199 | 4.2572 | -0.15564 | -10.1715 | -0.31128 | -0.018311 | 4.6097 | 70.1065 | 70.1019 | 113.3194 | 123.4497 | 4.2572 | 123.4726 | 85.6338 | -0.31128 | 123.4497 | 4.2572 | 85.6338 | 113.3194 | 123.4726 | -123.8434 | -123.8022
5684.7188 | 123.7152 | -61.3953 | 62.1323 | 0.11314 | 0.022005 | 0.018754 | 0.02001 | 0.059607 | -0.0020421 | 0.08439 | -57.106 | 62.2009 | -61.702 | -61.5967 | 51.8509 | 24.2111 | 8.8531 | 8.5922 | 62.1323 | -61.7294 | -0.3067 | 0.068665 | 4.2892 | -0.20142 | -10.2814 | -0.33417 | 0 | 4.5959 | 70.2484 | 69.9875 | 113.2462 | 123.5962 | 4.2892 | 123.5275 | 85.6064 | -0.33417 | 123.5962 | 4.2892 | 85.6064 | 113.2462 | 123.5275 | -123.8342 | -123.8617
5685.7188 | 123.6923 | -61.4227 | 62.1597 | 0.37254 | 0.020724 | 0.019395 | 0.022146 | 0.060248 | -0.00076053 | 0.081826 | -57.1335 | 62.2192 | -61.7386 | -61.6058 | 51.8326 | 24.1699 | 8.9447 | 8.6334 | 62.1689 | -61.7294 | -0.31586 | 0.059509 | 4.2892 | -0.18311 | -10.3271 | -0.3067 | 0.009155 | 4.6051 | 70.3674 | 70.0562 | 113.2553 | 123.642 | 4.2892 | 123.5916 | 85.5927 | -0.3067 | 123.642 | 4.2892 | 85.5927 | 113.2553 | 123.5916 | -123.8983 | -123.8892
5686.7188 | 123.7289 | -61.3907 | 62.1048 | 0.18944 | 0.020296 | 0.020249 | 0.019583 | 0.063666 | -0.00033333 | 0.081613 | -57.1289 | 62.1872 | -61.734 | -61.5784 | 51.8234 | 24.2477 | 8.8348 | 8.6426 | 62.1323 | -61.7111 | -0.34332 | 0.082398 | 4.2618 | -0.18768 | -10.2814 | -0.32043 | 0.027466 | 4.6051 | 70.2255 | 70.0333 | 113.2141 | 123.5779 | 4.2618 | 123.5229 | 85.6384 | -0.32043 | 123.5779 | 4.2618 | 85.6384 | 113.2141 | 123.5229 | -123.8388 | -123.8159
5687.7188 | 123.7381 | -61.3907 | 62.1368 | 0.15129 | 0.020937 | 0.020677 | 0.022146 | 0.061316 | 0.0013757 | 0.085671 | -57.1152 | 62.1735 | -61.7294 | -61.5784 | 51.828 | 24.234 | 8.8303 | 8.6151 | 62.1735 | -61.7203 | -0.33874 | 0.036621 | 4.2755 | -0.18768 | -10.3088 | -0.32959 | 0.036621 | 4.6143 | 70.2209 | 70.0058 | 113.2187 | 123.5641 | 4.2755 | 123.5641 | 85.6247 | -0.32959 | 123.5641 | 4.2755 | 85.6247 | 113.2187 | 123.5641 | -123.8663 | -123.8571
5688.7344 | 123.7976 | -61.322 | 62.1506 | -0.031814 | 0.017947 | 0.015122 | 0.011892 | 0.059607 | 0.00030767 | 0.084817 | -57.1152 | 62.1094 | -61.702 | -61.5143 | 51.915 | 24.2798 | 8.8486 | 8.7936 | 62.1552 | -61.6425 | -0.37994 | -0.041199 | 4.2068 | -0.19226 | -10.2356 | -0.32044 | 0.004577 | 4.5868 | 70.1706 | 70.1157 | 113.237 | 123.4314 | 4.2068 | 123.4772 | 85.6018 | -0.32044 | 123.4314 | 4.2068 | 85.6018 | 113.237 | 123.4772 | -123.8525 | -123.793
5689.7188 | 123.6694 | -61.4044 | 62.1323 | 0.03685 | 0.021792 | 0.020463 | 0.020865 | 0.060675 | 0.00073487 | 0.083962 | -57.1198 | 62.1964 | -61.7432 | -61.6104 | 51.8143 | 24.2065 | 8.8806 | 8.6517 | 62.1597 | -61.7157 | -0.33875 | 0.064087 | 4.2847 | -0.20599 | -10.318 | -0.31128 | 0.027466 | 4.6234 | 70.285 | 70.0562 | 113.2187 | 123.6008 | 4.2847 | 123.5641 | 85.611 | -0.31128 | 123.6008 | 4.2847 | 85.611 | 113.2187 | 123.5641 | -123.8754 | -123.848
5690.7188 | 123.7106 | -61.4044 | 62.1368 | 0.18181 | 0.020937 | 0.017045 | 0.022787 | 0.061316 | 9.4068e-05 | 0.085885 | -57.0969 | 62.1826 | -61.7203 | -61.5784 | 51.7868 | 24.1928 | 8.8211 | 8.7112 | 62.1597 | -61.7203 | -0.31586 | 0.045776 | 4.3076 | -0.17395 | -10.35 | -0.31586 | 0.022888 | 4.6234 | 70.2255 | 70.1157 | 113.1912 | 123.587 | 4.3076 | 123.5641 | 85.5972 | -0.31586 | 123.587 | 4.3076 | 85.5972 | 113.1912 | 123.5641 | -123.8571 | -123.8571
5691.7188 | 123.7152 | -61.3815 | 62.1552 | 0.18181 | 0.022219 | 0.020677 | 0.018301 | 0.062598 | -0.00011953 | 0.085885 | -57.1014 | 62.1918 | -61.7294 | -61.6058 | 51.7593 | 24.1791 | 8.8852 | 8.6929 | 62.1552 | -61.7249 | -0.3479 | 0.036621 | 4.2801 | -0.2243 | -10.3958 | -0.34332 | 0 | 4.628 | 70.2667 | 70.0745 | 113.1409 | 123.5733 | 4.2801 | 123.5367 | 85.5606 | -0.34332 | 123.5733 | 4.2801 | 85.5606 | 113.1409 | 123.5367 | -123.8846 | -123.88
5692.7188 | 123.7747 | -61.3632 | 62.1094 | 0.097885 | 0.020083 | 0.018754 | 0.01232 | 0.060248 | -0.00011953 | 0.086526 | -57.0511 | 62.1048 | -61.6974 | -61.5372 | 51.8143 | 24.2477 | 8.8486 | 8.8486 | 62.1185 | -61.6653 | -0.33417 | -0.004578 | 4.3121 | -0.17395 | -10.2951 | -0.30212 | 0.009155 | 4.6463 | 70.2118 | 70.2118 | 113.1775 | 123.468 | 4.3121 | 123.4818 | 85.611 | -0.30212 | 123.468 | 4.3121 | 85.611 | 113.1775 | 123.4818 | -123.8068 | -123.7747
5693.7188 | 123.7976 | -61.3312 | 62.1872 | -0.16151 | 0.019228 | 0.016404 | 0.016378 | 0.057898 | 0.00073487 | 0.082894 | -57.0099 | 62.1597 | -61.6562 | -61.4914 | 51.8646 | 24.2798 | 8.9539 | 8.8165 | 62.146 | -61.6745 | -0.32501 | -0.027466 | 4.3213 | -0.16022 | -10.3226 | -0.34332 | -0.041199 | 4.6463 | 70.285 | 70.1477 | 113.1958 | 123.4909 | 4.3213 | 123.4772 | 85.611 | -0.34332 | 123.4909 | 4.3213 | 85.611 | 113.1958 | 123.4772 | -123.8434 | -123.8617
5694.7188 | 123.7289 | -61.3724 | 62.1231 | 0.18181 | 0.022219 | 0.016191 | 0.019369 | 0.060248 | 9.4068e-05 | 0.083535 | -57.0786 | 62.1735 | -61.7203 | -61.5875 | 51.828 | 24.234 | 8.8806 | 8.7204 | 62.1231 | -61.6974 | -0.3479 | 0.050354 | 4.2938 | -0.21515 | -10.2951 | -0.32501 | 0 | 4.6417 | 70.253 | 70.0928 | 113.2004 | 123.5458 | 4.2938 | 123.4955 | 85.6064 | -0.32501 | 123.5458 | 4.2938 | 85.6064 | 113.2004 | 123.4955 | -123.8434 | -123.8205
5695.7188 | 123.6923 | -61.3861 | 62.146 | 0.43358 | 0.021151 | 0.016191 | 0.019796 | 0.062384 | 0.00030767 | 0.083749 | -56.8314 | 62.1872 | -61.7294 | -61.5692 | 51.8326 | 24.2065 | 9.0134 | 8.6838 | 62.1643 | -61.7249 | -0.34332 | 0.041199 | 4.5547 | -0.18311 | -10.3134 | -0.33875 | 0.018311 | 4.8981 | 70.3995 | 70.0699 | 113.2187 | 123.5733 | 4.5547 | 123.5504 | 85.5927 | -0.33875 | 123.5733 | 4.5547 | 85.5927 | 113.2187 | 123.5504 | -123.8754 | -123.8708
5696.7188 | 123.7427 | -61.3815 | 62.146 | 0.14366 | 0.021792 | 0.015977 | 0.02001 | 0.063025 | -0.0014013 | 0.083962 | -57.0786 | 62.1918 | -61.734 | -61.6104 | 51.7822 | 24.1928 | 8.9218 | 8.6838 | 62.1506 | -61.7249 | -0.35248 | 0.045776 | 4.303 | -0.22888 | -10.3638 | -0.34332 | 0.004578 | 4.6555 | 70.3033 | 70.0653 | 113.1638 | 123.5733 | 4.303 | 123.5321 | 85.5743 | -0.34332 | 123.5733 | 4.303 | 85.5743 | 113.1638 | 123.5321 | -123.88 | -123.8708
5697.7188 | 123.8022 | -61.3403 | 62.0911 | 0.15892 | 0.020083 | 0.017686 | 0.014883 | 0.062384 | 0.00030767 | 0.084176 | -57.0007 | 62.1185 | -61.6882 | -61.5005 | 51.9424 | 24.3301 | 8.7891 | 8.8211 | 62.114 | -61.6516 | -0.3479 | 0.027466 | 4.3396 | -0.16022 | -10.1486 | -0.31128 | 0.022889 | 4.6875 | 70.1294 | 70.1614 | 113.2828 | 123.4589 | 4.3396 | 123.4543 | 85.6705 | -0.31128 | 123.4589 | 4.3396 | 85.6705 | 113.2828 | 123.4543 | -123.7793 | -123.7427
5698.7188 | 123.6969 | -61.3907 | 62.1552 | 0.17418 | 0.02286 | 0.016618 | 0.020865 | 0.062384 | -0.00011953 | 0.082681 | -57.0786 | 62.2055 | -61.734 | -61.6104 | 51.7776 | 24.1333 | 8.9218 | 8.6746 | 62.1506 | -61.7294 | -0.34332 | 0.050354 | 4.3121 | -0.21973 | -10.3775 | -0.33874 | -0.004577 | 4.6555 | 70.3125 | 70.0653 | 113.1683 | 123.5962 | 4.3121 | 123.5413 | 85.524 | -0.33874 | 123.5962 | 4.3121 | 85.524 | 113.1683 | 123.5413 | -123.8892 | -123.8846
5699.7188 | 123.7152 | -61.4044 | 62.1735 | -0.19966 | 0.021151 | 0.016618 | 0.017233 | 0.060675 | 9.4068e-05 | 0.085244 | -57.0969 | 62.2238 | -61.6974 | -61.6241 | 51.7639 | 24.0601 | 8.9493 | 8.6884 | 62.1689 | -61.7523 | -0.29297 | 0.050354 | 4.3076 | -0.21973 | -10.4095 | -0.3479 | -0.004578 | 4.6005 | 70.3537 | 70.0928 | 113.1683 | 123.6282 | 4.3076 | 123.5733 | 85.4645 | -0.3479 | 123.6282 | 4.3076 | 85.4645 | 113.1683 | 123.5733 | -123.8708 | -123.9258
5700.7188 | 123.8113 | -61.3495 | 62.1231 | 0.18181 | 0.019442 | 0.018327 | 0.017874 | 0.062171 | 0.00052127 | 0.085031 | -56.9916 | 62.1506 | -61.702 | -61.528 | 51.8463 | 24.2203 | 8.7296 | 8.7616 | 62.1597 | -61.6882 | -0.35248 | 0.027466 | 4.3579 | -0.17853 | -10.2768 | -0.33874 | 0.036621 | 4.7104 | 70.079 | 70.1111 | 113.1958 | 123.5001 | 4.3579 | 123.5092 | 85.5698 | -0.33874 | 123.5001 | 4.3579 | 85.5698 | 113.1958 | 123.5092 | -123.8251 | -123.8113
5701.7188 | 123.7839 | -61.3541 | 62.1231 | 0.17418 | 0.018801 | 0.012986 | 0.016165 | 0.061957 | 0.00030767 | 0.085244 | -57.0053 | 62.1643 | -61.7111 | -61.528 | 51.8738 | 24.1882 | 8.7845 | 8.7936 | 62.1643 | -61.6882 | -0.35706 | 0.041199 | 4.3488 | -0.17395 | -10.2493 | -0.33417 | 0.041199 | 4.7058 | 70.1385 | 70.1477 | 113.2278 | 123.5184 | 4.3488 | 123.5184 | 85.5423 | -0.33417 | 123.5184 | 4.3488 | 85.5423 | 113.2278 | 123.5184 | -123.8342 | -123.8113
5702.7344 | 123.8068 | -61.3403 | 62.1323 | -0.039444 | 0.018587 | 0.017045 | 0.011465 | 0.060462 | 0.00073487 | 0.084817 | -57.0374 | 62.1277 | -61.6974 | -61.5143 | 51.9058 | 24.1745 | 8.7982 | 8.8394 | 62.1689 | -61.6516 | -0.35706 | -0.004577 | 4.303 | -0.17395 | -10.2264 | -0.31128 | 0.036621 | 4.66 | 70.1385 | 70.1797 | 113.2462 | 123.468 | 4.303 | 123.5092 | 85.5148 | -0.31128 | 123.468 | 4.303 | 85.5148 | 113.2462 | 123.5092 | -123.8297 | -123.7839
5703.7188 | 123.6969 | -61.3953 | 62.1689 | 0.18181 | 0.020724 | 0.022599 | 0.02001 | 0.059607 | 0.00030767 | 0.085671 | -57.0602 | 62.2101 | -61.7294 | -61.6058 | 51.7868 | 24.1425 | 8.876 | 8.6334 | 62.1735 | -61.7523 | -0.33417 | 0.041199 | 4.335 | -0.21057 | -10.3821 | -0.35706 | 0.004578 | 4.6692 | 70.2713 | 70.0287 | 113.1821 | 123.6053 | 4.335 | 123.5687 | 85.5377 | -0.35706 | 123.6053 | 4.335 | 85.5377 | 113.1821 | 123.5687 | -123.8983 | -123.9212
5704.7188 | 123.7106 | -61.3998 | 62.1552 | 0.35728 | 0.022646 | 0.017045 | 0.021933 | 0.060462 | 0.0024439 | 0.08439 | -57.0419 | 62.2147 | -61.7111 | -61.6013 | 51.7593 | 24.0967 | 8.9355 | 8.6746 | 62.1735 | -61.7386 | -0.31128 | 0.05951 | 4.3579 | -0.20142 | -10.3958 | -0.33874 | 0.018311 | 4.6692 | 70.3354 | 70.0745 | 113.1592 | 123.6145 | 4.3579 | 123.5733 | 85.4965 | -0.33874 | 123.6145 | 4.3579 | 85.4965 | 113.1592 | 123.5733 | -123.8663 | -123.8937
5705.7188 | 123.7106 | -61.3953 | 62.1552 | 0.69298 | 0.021792 | 0.021531 | 0.020865 | 0.062171 | 0.0018031 | 0.085031 | -57.0236 | 62.2192 | -61.7432 | -61.6287 | 51.7822 | 24.0829 | 8.963 | 8.6838 | 62.1735 | -61.734 | -0.3479 | 0.064087 | 4.3716 | -0.23346 | -10.3729 | -0.33875 | 0.018311 | 4.7195 | 70.3583 | 70.079 | 113.1775 | 123.6145 | 4.3716 | 123.5687 | 85.4782 | -0.33875 | 123.6145 | 4.3716 | 85.4782 | 113.1775 | 123.5687 | -123.8983 | -123.8892
5706.7188 | 123.6557 | -61.3815 | 62.1506 | 0.14366 | 0.020937 | 0.017686 | 0.016592 | 0.065589 | 9.4068e-05 | 0.082894 | -56.8726 | 62.2147 | -61.7477 | -61.5189 | 51.8097 | 24.0829 | 8.9584 | 8.7387 | 62.2147 | -61.7111 | -0.36621 | 0.064087 | 4.509 | -0.13733 | -10.3409 | -0.32959 | 0.064087 | 4.8752 | 70.34 | 70.1202 | 113.1912 | 123.5962 | 4.509 | 123.5962 | 85.4645 | -0.32959 | 123.5962 | 4.509 | 85.4645 | 113.1912 | 123.5962 | -123.8983 | -123.8617
5707.7344 | 123.7656 | -61.3632 | 62.1323 | -0.062332 | 0.019228 | 0.016618 | 0.0095424 | 0.061316 | 0.0030847 | 0.083749 | -57.0374 | 62.1185 | -61.6974 | -61.5051 | 51.9058 | 24.2065 | 8.8715 | 8.8623 | 62.1323 | -61.6333 | -0.33417 | -0.013733 | 4.3259 | -0.14191 | -10.2264 | -0.27008 | 0 | 4.66 | 70.2347 | 70.2255 | 113.269 | 123.4818 | 4.3259 | 123.4955 | 85.5698 | -0.27008 | 123.4818 | 4.3259 | 85.5698 | 113.269 | 123.4955 | -123.8297 | -123.7656
5708.7188 | 123.7335 | -61.3953 | 62.1414 | 0.097885 | 0.024569 | 0.014695 | 0.021505 | 0.060462 | 0.00030767 | 0.084817 | -57.0511 | 62.2101 | -61.7111 | -61.5967 | 51.796 | 24.0601 | 8.8943 | 8.6334 | 62.1506 | -61.7294 | -0.31586 | 0.068665 | 4.3442 | -0.20142 | -10.3455 | -0.33417 | 0.009156 | 4.66 | 70.2896 | 70.0287 | 113.1912 | 123.6053 | 4.3442 | 123.5458 | 85.4553 | -0.33417 | 123.6053 | 4.3442 | 85.4553 | 113.1912 | 123.5458 | -123.8525 | -123.8708
5709.7188 | 123.6511 | -61.3815 | 62.1552 | 0.074997 | 0.022433 | 0.019608 | 0.020651 | 0.060248 | -0.00011953 | 0.086099 | -57.0236 | 62.2238 | -61.7065 | -61.6196 | 51.7319 | 24.0234 | 8.9813 | 8.6838 | 62.1689 | -61.7615 | -0.32501 | 0.068665 | 4.3579 | -0.23804 | -10.4233 | -0.37994 | 0.013733 | 4.6829 | 70.3629 | 70.0653 | 113.1134 | 123.6053 | 4.3579 | 123.5504 | 85.405 | -0.37994 | 123.6053 | 4.3579 | 85.405 | 113.1134 | 123.5504 | -123.8617 | -123.9166
5710.7188 | 123.6877 | -61.3953 | 62.178 | 0.16655 | 0.022646 | 0.016191 | 0.019796 | 0.06388 | 0.00030767 | 0.083535 | -57.0465 | 62.2101 | -61.7294 | -61.441 | 51.6632 | 24.0234 | 9.0683 | 8.5968 | 62.2009 | -61.7203 | -0.33417 | 0.032043 | 4.3488 | -0.045776 | -10.5148 | -0.32501 | 0.022888 | 4.6829 | 70.4636 | 69.9921 | 113.0585 | 123.6053 | 4.3488 | 123.5962 | 85.4187 | -0.32501 | 123.6053 | 4.3488 | 85.4187 | 113.0585 | 123.5962 | -123.9075 | -123.8983
5711.7188 | 123.6099 | -61.4182 | 62.146 | 0.074997 | 0.024782 | 0.019822 | 0.019796 | 0.063452 | 0.0011621 | 0.08439 | -57.0328 | 62.233 | -61.7203 | -61.6333 | 51.7273 | 24.0189 | 8.9035 | 8.6243 | 62.1918 | -61.7203 | -0.30212 | 0.086975 | 4.3854 | -0.21515 | -10.4187 | -0.30212 | 0.045776 | 4.6875 | 70.3217 | 70.0424 | 113.1454 | 123.6511 | 4.3854 | 123.6099 | 85.437 | -0.30212 | 123.6511 | 4.3854 | 85.437 | 113.1454 | 123.6099 | -123.8663 | -123.8663
5712.7188 | 123.8159 | -61.3541 | 62.1094 | 0.15892 | 0.019869 | 0.019822 | 0.014242 | 0.062598 | 0.0015893 | 0.083322 | -56.9687 | 62.114 | -61.6791 | -61.5234 | 51.8326 | 24.2157 | 8.7479 | 8.7845 | 62.1414 | -61.6882 | -0.32501 | 0.004578 | 4.3854 | -0.16937 | -10.2768 | -0.33417 | 0.032043 | 4.7104 | 70.1019 | 70.1385 | 113.1866 | 123.468 | 4.3854 | 123.4955 | 85.5698 | -0.33417 | 123.468 | 4.3854 | 85.5698 | 113.1866 | 123.4955 | -123.7885 | -123.7976
5713.7188 | 123.674 | -61.4044 | 62.1643 | 0.021591 | 0.023287 | 0.015336 | 0.021505 | 0.063452 | 0.00030767 | 0.084817 | -57.0145 | 62.2101 | -61.6837 | -61.615 | 51.7227 | 24.0875 | 8.9584 | 8.6197 | 62.2009 | -61.7249 | -0.27924 | 0.045776 | 4.39 | -0.21057 | -10.4416 | -0.32044 | 0.036621 | 4.6692 | 70.3629 | 70.0241 | 113.1271 | 123.6145 | 4.39 | 123.6053 | 85.4919 | -0.32044 | 123.6145 | 4.39 | 85.4919 | 113.1271 | 123.6053 | -123.848 | -123.8892
5714.7188 | 123.6877 | -61.377 | 62.1597 | 0.15892 | 0.022433 | 0.020249 | 0.02001 | 0.064093 | 0.0015893 | 0.088021 | -57.0374 | 62.2192 | -61.7065 | -61.94 | 51.4755 | 24.2752 | 9.0454 | 8.5648 | 62.1918 | -61.7294 | -0.32959 | 0.059509 | 4.3396 | -0.56305 | -10.6842 | -0.35248 | 0.032043 | 4.6692 | 70.4224 | 69.9417 | 112.8525 | 123.5962 | 4.3396 | 123.5687 | 85.6522 | -0.35248 | 123.5962 | 4.3396 | 85.6522 | 112.8525 | 123.5687 | -123.8663 | -123.8892
5715.7188 | 123.6282 | -61.4044 | 62.1597 | 0.059738 | 0.020296 | 0.021104 | 0.020437 | 0.063025 | 0.0013757 | 0.085031 | -57.0236 | 62.2238 | -61.7249 | -61.647 | 51.6678 | 23.9502 | 8.9539 | 8.6517 | 62.2192 | -61.7386 | -0.32044 | 0.064087 | 4.3808 | -0.24262 | -10.4919 | -0.33417 | 0.059509 | 4.7012 | 70.3583 | 70.0562 | 113.0722 | 123.6282 | 4.3808 | 123.6237 | 85.3546 | -0.33417 | 123.6282 | 4.3808 | 85.3546 | 113.0722 | 123.6237 | -123.8846 | -123.8983
5716.7188 | 123.6969 | -61.377 | 62.1552 | 0.021591 | 0.021578 | 0.017899 | 0.021078 | 0.063025 | -0.00097413 | 0.085031 | -56.9595 | 62.2375 | -61.702 | -61.5784 | 51.7639 | 24.1013 | 8.876 | 8.6655 | 62.2101 | -61.7249 | -0.32501 | 0.082398 | 4.4174 | -0.20142 | -10.3912 | -0.3479 | 0.054932 | 4.7424 | 70.253 | 70.0424 | 113.1409 | 123.6145 | 4.4174 | 123.587 | 85.4782 | -0.3479 | 123.6145 | 4.4174 | 85.4782 | 113.1409 | 123.587 | -123.8571 | -123.88
5717.7188 | 123.6877 | -61.4044 | 62.178 | 0.090256 | 0.023714 | 0.016618 | 0.019369 | 0.063452 | 0.0013757 | 0.083749 | -57.0007 | 62.2238 | -61.7203 | -61.615 | 51.6586 | 24.0601 | 8.8943 | 8.6151 | 62.2101 | -61.7203 | -0.31586 | 0.045776 | 4.4037 | -0.21057 | -10.5194 | -0.31586 | 0.032043 | 4.7195 | 70.2988 | 70.0195 | 113.063 | 123.6282 | 4.4037 | 123.6145 | 85.4645 | -0.31586 | 123.6282 | 4.4037 | 85.4645 | 113.063 | 123.6145 | -123.8983 | -123.8983
5718.7188 | 123.6557 | -61.3907 | 62.1597 | 0.067368 | 0.021792 | 0.019822 | 0.017447 | 0.064734 | 0.0011621 | 0.083322 | -56.9778 | 62.2101 | -61.6974 | -61.6058 | 51.7273 | 24.1196 | 8.9264 | 8.6655 | 62.2147 | -61.6974 | -0.3067 | 0.050354 | 4.4128 | -0.21515 | -10.4324 | -0.3067 | 0.054932 | 4.7195 | 70.3171 | 70.0562 | 113.118 | 123.6008 | 4.4128 | 123.6053 | 85.5103 | -0.3067 | 123.6008 | 4.4128 | 85.5103 | 113.118 | 123.6053 | -123.8571 | -123.8571
5719.7188 | 123.6649 | -61.3953 | 62.1414 | 0.021591 | 0.021792 | 0.014268 | 0.020437 | 0.063452 | -0.00054693 | 0.085458 | -56.9687 | 62.2284 | -61.7111 | -61.6013 | 51.6861 | 24.0692 | 8.9722 | 8.6746 | 62.2009 | -61.7157 | -0.31586 | 0.086976 | 4.4266 | -0.20599 | -10.4553 | -0.32043 | 0.05951 | 4.7424 | 70.3674 | 70.0699 | 113.0814 | 123.6237 | 4.4266 | 123.5962 | 85.4645 | -0.32043 | 123.6237 | 4.4266 | 85.4645 | 113.0814 | 123.5962 | -123.8525 | -123.8571
5720.7188 | 123.6969 | -61.3815 | 62.1643 | 0.0063326 | 0.021578 | 0.017686 | 0.018728 | 0.063452 | 9.4068e-05 | 0.085244 | -56.9687 | 62.2192 | -61.6837 | -61.6104 | 51.6541 | 24.0005 | 8.9539 | 8.6609 | 62.1964 | -61.7065 | -0.30212 | 0.054931 | 4.4128 | -0.22888 | -10.5103 | -0.32501 | 0.032043 | 4.715 | 70.3354 | 70.0424 | 113.0356 | 123.6008 | 4.4128 | 123.5779 | 85.3821 | -0.32501 | 123.6008 | 4.4128 | 85.3821 | 113.0356 | 123.5779 | -123.848 | -123.8709
5721.7188 | 123.7061 | -61.3998 | 62.0865 | 0.11314 | 0.019442 | 0.022172 | 0.018301 | 0.064948 | 9.4068e-05 | 0.086739 | -57.0053 | 62.2467 | -61.7249 | -61.6379 | 51.6449 | 23.8998 | 8.8806 | 8.638 | 62.2055 | -61.7294 | -0.32501 | 0.16022 | 4.3945 | -0.23804 | -10.4416 | -0.32959 | 0.11902 | 4.7195 | 70.2805 | 70.0378 | 113.0447 | 123.6465 | 4.3945 | 123.6053 | 85.2997 | -0.32959 | 123.6465 | 4.3945 | 85.2997 | 113.0447 | 123.6053 | -123.8113 | -123.8159
5722.7188 | 123.7152 | -61.3998 | 62.1552 | 0.10551 | 0.022646 | 0.018327 | 0.018515 | 0.062598 | 9.4068e-05 | 0.084176 | -57.0099 | 62.2055 | -61.7249 | -61.6196 | 51.6312 | 23.9548 | 8.8394 | 8.6792 | 62.1826 | -61.7294 | -0.32501 | 0.050354 | 4.39 | -0.21973 | -10.524 | -0.32959 | 0.027466 | 4.715 | 70.2393 | 70.079 | 113.031 | 123.6053 | 4.39 | 123.5825 | 85.3546 | -0.32959 | 123.6053 | 4.39 | 85.3546 | 113.031 | 123.5825 | -123.88 | -123.8846
5723.7188 | 123.6832 | -61.3953 | 62.1643 | 0.013962 | 0.022005 | 0.018754 | 0.019796 | 0.061743 | 0.00073487 | 0.085031 | -56.9366 | 62.2101 | -61.6837 | -61.5875 | 51.6312 | 23.9639 | 8.9081 | 8.7479 | 62.1918 | -61.7111 | -0.28839 | 0.045776 | 4.4586 | -0.19226 | -10.5331 | -0.31586 | 0.027465 | 4.747 | 70.3033 | 70.1431 | 113.0264 | 123.6053 | 4.4586 | 123.587 | 85.3592 | -0.31586 | 123.6053 | 4.4586 | 85.3592 | 113.0264 | 123.587 | -123.848 | -123.8754
5724.7188 | 123.6465 | -61.4044 | 62.1689 | 0.059738 | 0.021578 | 0.020036 | 0.018087 | 0.063666 | -0.00054693 | 0.087594 | -56.987 | 62.2421 | -61.7249 | -61.6379 | 51.6403 | 23.9456 | 8.9264 | 8.606 | 62.2009 | -61.7157 | -0.32044 | 0.073242 | 4.4174 | -0.23346 | -10.5286 | -0.31128 | 0.032044 | 4.7379 | 70.3308 | 70.0104 | 113.0447 | 123.6465 | 4.4174 | 123.6053 | 85.35 | -0.31128 | 123.6465 | 4.4174 | 85.35 | 113.0447 | 123.6053 | -123.8937 | -123.8846
5725.7188 | 123.6649 | -61.409 | 62.1735 | 0.029221 | 0.022005 | 0.020677 | 0.017874 | 0.065589 | -0.0020421 | 0.085244 | -56.9916 | 62.2513 | -61.7065 | -61.6425 | 51.6449 | 23.9319 | 8.8989 | 8.6014 | 62.2009 | -61.7157 | -0.29755 | 0.07782 | 4.4174 | -0.23346 | -10.5286 | -0.3067 | 0.027466 | 4.715 | 70.3079 | 70.0104 | 113.0539 | 123.6603 | 4.4174 | 123.6099 | 85.3409 | -0.3067 | 123.6603 | 4.4174 | 85.3409 | 113.0539 | 123.6099 | -123.88 | -123.8892
5726.7188 | 123.6465 | -61.3998 | 62.1643 | 0.10551 | 0.022646 | 0.017472 | 0.018515 | 0.064093 | 0.00052127 | 0.086526 | -56.9916 | 62.2284 | -61.7065 | -61.6379 | 51.5945 | 23.909 | 8.8898 | 8.6472 | 62.2101 | -61.7386 | -0.3067 | 0.064087 | 4.4083 | -0.23804 | -10.5698 | -0.33874 | 0.045776 | 4.715 | 70.2896 | 70.047 | 112.9944 | 123.6282 | 4.4083 | 123.6099 | 85.3088 | -0.33874 | 123.6282 | 4.4083 | 85.3088 | 112.9944 | 123.6099 | -123.8709 | -123.9029
5727.7188 | 123.793 | -61.3403 | 62.0911 | 0.16655 | 0.02286 | 0.020677 | 0.014456 | 0.063025 | 0.0024439 | 0.084176 | -56.9 | 62.146 | -61.702 | -61.5326 | 51.7502 | 24.0509 | 8.7067 | 8.7524 | 62.1552 | -61.6928 | -0.36163 | 0.054932 | 4.4403 | -0.19226 | -10.3409 | -0.35248 | 0.064087 | 4.8019 | 70.047 | 70.0928 | 113.0905 | 123.4863 | 4.4403 | 123.4955 | 85.3912 | -0.35248 | 123.4863 | 4.4403 | 85.3912 | 113.0905 | 123.4955 | -123.793 | -123.7839
5728.7188 | 123.6832 | -61.3998 | 62.1689 | -0.62691 | 0.022005 | 0.017259 | 0.018515 | 0.062171 | 0.00052127 | 0.083322 | -56.9778 | 62.2147 | -61.7386 | -61.6196 | 51.622 | 23.9914 | 8.8531 | 8.6288 | 62.2101 | -61.7432 | -0.33874 | 0.045777 | 4.422 | -0.21973 | -10.5469 | -0.34332 | 0.041199 | 4.7607 | 70.253 | 70.0287 | 113.0219 | 123.6145 | 4.422 | 123.6099 | 85.3912 | -0.34332 | 123.6145 | 4.422 | 85.3912 | 113.0219 | 123.6099 | -123.9075 | -123.912
5729.7188 | 123.6328 | -61.3953 | 62.1918 | 0.03685 | 0.024782 | 0.017899 | 0.021078 | 0.062598 | 0.0015893 | 0.084603 | -56.9641 | 62.2147 | -61.7065 | -61.6196 | 51.6037 | 23.9777 | 8.844 | 8.6288 | 62.233 | -61.734 | -0.31128 | 0.022889 | 4.4312 | -0.2243 | -10.5881 | -0.33875 | 0.041199 | 4.7424 | 70.2393 | 70.0241 | 112.999 | 123.6099 | 4.4312 | 123.6282 | 85.3729 | -0.33875 | 123.6099 | 4.4312 | 85.3729 | 112.999 | 123.6282 | -123.8983 | -123.9258
5730.7188 | 123.6557 | -61.3953 | 62.178 | 0.097885 | 0.02286 | 0.01854 | 0.018515 | 0.064093 | -0.0018285 | 0.085458 | -56.9504 | 62.2192 | -61.7294 | -61.6241 | 51.5579 | 23.9914 | 8.9127 | 8.6472 | 62.2147 | -61.7386 | -0.33417 | 0.041198 | 4.4449 | -0.22888 | -10.6201 | -0.34332 | 0.036621 | 4.7791 | 70.3079 | 70.0424 | 112.9532 | 123.6145 | 4.4449 | 123.6099 | 85.3867 | -0.34332 | 123.6145 | 4.4449 | 85.3867 | 112.9532 | 123.6099 | -123.9075 | -123.9166
5731.7188 | 123.6969 | -61.4044 | 62.1735 | 0.13603 | 0.025423 | 0.014054 | 0.017874 | 0.064521 | -0.00054693 | 0.082894 | -57.0969 | 62.1689 | -61.7523 | -61.5646 | 51.5213 | 23.9868 | 8.9127 | 8.6334 | 62.2192 | -61.7157 | -0.3479 | -0.004578 | 4.3076 | -0.16022 | -10.6522 | -0.31128 | 0.045776 | 4.6555 | 70.3171 | 70.0378 | 112.9257 | 123.5733 | 4.3076 | 123.6237 | 85.3912 | -0.31128 | 123.5733 | 4.3076 | 85.3912 | 112.9257 | 123.6237 | -123.9258 | -123.8892
5732.7188 | 123.8205 | -61.3541 | 62.1048 | 0.17418 | 0.019442 | 0.019822 | 0.012747 | 0.062598 | -0.00033333 | 0.087808 | -56.7673 | 62.1414 | -61.6379 | -61.5097 | 51.6632 | 24.115 | 8.6975 | 8.7662 | 62.146 | -61.6699 | -0.28381 | 0.036621 | 4.5868 | -0.15564 | -10.4416 | -0.31586 | 0.041199 | 4.8706 | 70.0516 | 70.1202 | 113.0173 | 123.4955 | 4.5868 | 123.5001 | 85.4691 | -0.31586 | 123.4955 | 4.5868 | 85.4691 | 113.0173 | 123.5001 | -123.7427 | -123.7747
5733.7188 | 123.6877 | -61.377 | 62.1597 | 0.18181 | 0.022646 | 0.018754 | 0.019156 | 0.061957 | 0.0028711 | 0.086312 | -56.9641 | 62.2055 | -61.702 | -61.9354 | 51.4023 | 24.2477 | 8.8715 | 8.606 | 62.2009 | -61.7386 | -0.32501 | 0.045776 | 4.4128 | -0.55847 | -10.7574 | -0.36163 | 0.041199 | 4.7379 | 70.2484 | 69.9829 | 112.7792 | 123.5825 | 4.4128 | 123.5779 | 85.6247 | -0.36163 | 123.5825 | 4.4128 | 85.6247 | 112.7792 | 123.5779 | -123.8617 | -123.8983
5734.7188 | 123.6923 | -61.3907 | 62.178 | 0.11314 | 0.023714 | 0.018327 | 0.022146 | 0.063452 | -0.00097413 | 0.086099 | -56.955 | 62.233 | -61.7065 | -61.6287 | 51.5167 | 24.0326 | 8.3588 | 8.4 | 62.114 | -61.7569 | -0.31586 | 0.054931 | 4.4357 | -0.23804 | -10.6613 | -0.36621 | -0.064087 | 4.7516 | 69.7495 | 69.7906 | 112.9074 | 123.6237 | 4.4357 | 123.5046 | 85.4233 | -0.36621 | 123.6237 | 4.4357 | 85.4233 | 112.9074 | 123.5046 | -123.8846 | -123.9349
5735.7188 | 123.7015 | -61.3953 | 62.146 | 0.22758 | 0.020724 | 0.018113 | 0.017019 | 0.062171 | -0.00011953 | 0.085244 | -56.955 | 62.2192 | -61.7157 | -61.6013 | 51.5717 | 23.9731 | 8.8531 | 8.6609 | 62.1918 | -61.702 | -0.32043 | 0.073242 | 4.4403 | -0.20599 | -10.5743 | -0.3067 | 0.045776 | 4.7607 | 70.2484 | 70.0562 | 112.9669 | 123.6145 | 4.4403 | 123.587 | 85.3683 | -0.3067 | 123.6145 | 4.4403 | 85.3683 | 112.9669 | 123.587 | -123.8617 | -123.848
5736.7188 | 123.6694 | -61.3998 | 62.1323 | 0.13603 | 0.023073 | 0.016831 | 0.019583 | 0.064093 | 0.00030767 | 0.085458 | -56.9366 | 62.2147 | -61.7294 | -61.6333 | 51.4526 | 23.8953 | 8.8715 | 8.6563 | 62.2238 | -61.7249 | -0.32959 | 0.082398 | 4.4632 | -0.23346 | -10.6796 | -0.32501 | 0.091553 | 4.7928 | 70.2713 | 70.0562 | 112.8525 | 123.6145 | 4.4632 | 123.6237 | 85.2951 | -0.32501 | 123.6145 | 4.4632 | 85.2951 | 112.8525 | 123.6237 | -123.8617 | -123.8571
5737.7188 | 123.7473 | -61.3678 | 62.1185 | 0.1284 | 0.019869 | 0.015336 | 0.018087 | 0.062598 | -0.00011953 | 0.085031 | -56.9229 | 62.1872 | -61.7157 | -61.5692 | 51.5305 | 23.9182 | 8.7616 | 8.6929 | 62.178 | -61.6837 | -0.3479 | 0.068665 | 4.4449 | -0.20142 | -10.5881 | -0.31586 | 0.05951 | 4.7928 | 70.1294 | 70.0607 | 112.8983 | 123.555 | 4.4449 | 123.5458 | 85.2859 | -0.31586 | 123.555 | 4.4449 | 85.2859 | 112.8983 | 123.5458 | -123.8342 | -123.8022
5738.7188 | 123.6832 | -61.377 | 62.1414 | -0.69557 | 0.023073 | 0.021104 | 0.021719 | 0.063239 | 0.0015893 | 0.086099 | -56.9366 | 62.2192 | -61.7065 | -61.6104 | 51.5305 | 23.909 | 8.8623 | 8.6334 | 62.1964 | -61.7432 | -0.32959 | 0.07782 | 4.4403 | -0.23346 | -10.611 | -0.36621 | 0.054932 | 4.7699 | 70.2393 | 70.0104 | 112.9074 | 123.5962 | 4.4403 | 123.5733 | 85.2859 | -0.36621 | 123.5962 | 4.4403 | 85.2859 | 112.9074 | 123.5733 | -123.848 | -123.8846
5739.7188 | 123.6969 | -61.3861 | 62.1506 | -2.1909 | 0.021364 | 0.019608 | 0.018942 | 0.060675 | 0.0028711 | 0.085244 | -57.0282 | 62.2192 | -61.7111 | -61.6379 | 51.4938 | 23.877 | 8.9172 | 8.6746 | 62.2101 | -61.7249 | -0.32501 | 0.068664 | 4.3579 | -0.25177 | -10.6567 | -0.33875 | 0.059509 | 4.6829 | 70.3033 | 70.0607 | 112.8799 | 123.6053 | 4.3579 | 123.5962 | 85.2631 | -0.33875 | 123.6053 | 4.3579 | 85.2631 | 112.8799 | 123.5962 | -123.8617 | -123.8754
5740.7188 | 123.6877 | -61.3953 | 62.146 | 0.18944 | 0.02521 | 0.019395 | 0.019156 | 0.062598 | 0.0022303 | 0.086526 | -57.1793 | 62.1918 | -61.7386 | -61.6562 | 51.5396 | 23.909 | 8.8715 | 8.6151 | 62.2192 | -61.7249 | -0.34332 | 0.045776 | 4.216 | -0.26093 | -10.6064 | -0.32959 | 0.073242 | 4.5593 | 70.2667 | 70.0104 | 112.9349 | 123.587 | 4.216 | 123.6145 | 85.3043 | -0.32959 | 123.587 | 4.216 | 85.3043 | 112.9349 | 123.6145 | -123.8846 | -123.8708
5741.7188 | 123.7152 | -61.3815 | 62.1414 | 0.15129 | 0.020724 | 0.019822 | 0.018301 | 0.060889 | -0.00033333 | 0.085031 | -56.9183 | 62.1964 | -61.7294 | -61.6058 | 51.5625 | 23.9822 | 8.812 | 8.6151 | 62.1826 | -61.7294 | -0.3479 | 0.054932 | 4.4632 | -0.2243 | -10.5789 | -0.3479 | 0.041199 | 4.8111 | 70.1935 | 69.9966 | 112.944 | 123.5779 | 4.4632 | 123.5641 | 85.3638 | -0.3479 | 123.5779 | 4.4632 | 85.3638 | 112.944 | 123.5641 | -123.8708 | -123.8708
5742.7188 | 123.7656 | -61.3266 | 62.114 | 0.10551 | 0.020296 | 0.015763 | 0.012106 | 0.062598 | 9.4068e-05 | 0.084176 | -56.8726 | 62.1094 | -61.7157 | -61.5509 | 51.5625 | 24.0189 | 8.7982 | 8.7845 | 62.146 | -61.6653 | -0.3891 | -0.004578 | 4.454 | -0.2243 | -10.5515 | -0.33874 | 0.032043 | 4.8431 | 70.1248 | 70.1111 | 112.8891 | 123.436 | 4.454 | 123.4726 | 85.3455 | -0.33874 | 123.436 | 4.454 | 85.3455 | 112.8891 | 123.4726 | -123.8297 | -123.7793
5743.7188 | 123.7244 | -61.3953 | 62.1964 | 0.12077 | 0.023073 | 0.021317 | 0.020437 | 0.060462 | 0.00030767 | 0.085244 | -56.9275 | 62.2009 | -61.702 | -61.6287 | 51.4709 | 23.9273 | 8.3862 | 8.3771 | 62.1231 | -61.7661 | -0.3067 | 0.004578 | 4.4678 | -0.23346 | -10.7254 | -0.37079 | -0.073242 | 4.7745 | 69.7815 | 69.7723 | 112.8662 | 123.5962 | 4.4678 | 123.5184 | 85.3226 | -0.37079 | 123.5962 | 4.4678 | 85.3226 | 112.8662 | 123.5184 | -123.8983 | -123.9624
5744.7188 | 123.642 | -61.3815 | 62.1735 | 0.052109 | 0.022433 | 0.021317 | 0.019583 | 0.063025 | -0.00076053 | 0.083962 | -56.9138 | 62.2192 | -61.7294 | -61.6425 | 51.4847 | 24.0005 | 8.9447 | 8.7021 | 62.1918 | -61.734 | -0.3479 | 0.045776 | 4.4678 | -0.26093 | -10.6888 | -0.35248 | 0.01831 | 4.8157 | 70.3262 | 70.0836 | 112.8662 | 123.6008 | 4.4678 | 123.5733 | 85.3821 | -0.35248 | 123.6008 | 4.4678 | 85.3821 | 112.8662 | 123.5733 | -123.9029 | -123.9075
5745.7188 | 123.6694 | -61.3724 | 62.1231 | 0.43358 | 0.024782 | 0.019181 | 0.019583 | 0.06388 | 0.00052127 | 0.08439 | -56.8588 | 62.2101 | -61.7065 | -61.615 | 51.4801 | 24.0189 | 8.8715 | 8.638 | 62.2009 | -61.7294 | -0.33417 | 0.086975 | 4.5135 | -0.24262 | -10.643 | -0.35706 | 0.07782 | 4.8477 | 70.2438 | 70.0104 | 112.8525 | 123.5825 | 4.5135 | 123.5733 | 85.3912 | -0.35706 | 123.5825 | 4.5135 | 85.3912 | 112.8525 | 123.5733 | -123.8297 | -123.8525
5746.7188 | 123.6832 | -61.4044 | 62.114 | 2.73 | 0.023073 | 0.01555 | 0.018301 | 0.064734 | 0.0011621 | 0.085671 | -56.6162 | 62.2147 | -61.7157 | -61.5784 | 51.5121 | 23.8998 | 8.8898 | 8.6472 | 62.1918 | -61.7477 | -0.31128 | 0.10071 | 4.7882 | -0.17395 | -10.6018 | -0.34332 | 0.077819 | 5.0995 | 70.2942 | 70.0516 | 112.9166 | 123.6191 | 4.7882 | 123.5962 | 85.3043 | -0.34332 | 123.6191 | 4.7882 | 85.3043 | 112.9166 | 123.5962 | -123.8297 | -123.8617
5747.7188 | 123.7885 | -61.3495 | 62.1277 | 0.57854 | 0.02051 | 0.019395 | 0.014029 | 0.062812 | 0.00094847 | 0.085031 | -56.694 | 62.1231 | -61.6882 | -61.5005 | 51.5854 | 24.0738 | 8.757 | 8.7936 | 62.1597 | -61.6882 | -0.33874 | -0.004578 | 4.6555 | -0.15106 | -10.5423 | -0.33874 | 0.032043 | 4.9942 | 70.1065 | 70.1431 | 112.9349 | 123.4726 | 4.6555 | 123.5092 | 85.4233 | -0.33874 | 123.4726 | 4.6555 | 85.4233 | 112.9349 | 123.5092 | -123.8159 | -123.8159
5748.7188 | 123.7015 | -61.3632 | 62.1323 | 0.15129 | 0.021364 | 0.018113 | 0.020437 | 0.062598 | -0.00076053 | 0.086312 | -56.8909 | 62.1964 | -61.7157 | -61.6058 | 51.4435 | 23.9273 | 8.9584 | 8.7021 | 62.1918 | -61.702 | -0.35248 | 0.064087 | 4.4724 | -0.24262 | -10.6888 | -0.33875 | 0.059509 | 4.8248 | 70.3217 | 70.0653 | 112.8067 | 123.5596 | 4.4724 | 123.555 | 85.2905 | -0.33875 | 123.5596 | 4.4724 | 85.2905 | 112.8067 | 123.555 | -123.848 | -123.8342
5749.7188 | 123.7198 | -61.3724 | 62.1414 | 0.021591 | 0.023928 | 0.01854 | 0.019583 | 0.062171 | 0.0013757 | 0.085244 | -56.9046 | 62.2055 | -61.6974 | -61.5921 | 51.4664 | 23.8907 | 8.9172 | 8.7067 | 62.2009 | -61.7249 | -0.32501 | 0.064087 | 4.4678 | -0.21973 | -10.675 | -0.35248 | 0.05951 | 4.7928 | 70.2896 | 70.079 | 112.8387 | 123.5779 | 4.4678 | 123.5733 | 85.2631 | -0.35248 | 123.5779 | 4.4678 | 85.2631 | 112.8387 | 123.5733 | -123.8388 | -123.8663
5750.7188 | 123.674 | -61.3861 | 62.1826 | 0.067368 | 0.025423 | 0.020677 | 0.020865 | 0.062598 | 0.0028711 | 0.085671 | -56.8817 | 62.2101 | -61.7157 | -61.615 | 51.4435 | 23.9273 | 8.9859 | 8.7112 | 62.2101 | -61.7477 | -0.32959 | 0.027466 | 4.5044 | -0.22888 | -10.7391 | -0.36163 | 0.027466 | 4.834 | 70.372 | 70.0974 | 112.8296 | 123.5962 | 4.5044 | 123.5962 | 85.3134 | -0.36163 | 123.5962 | 4.5044 | 85.3134 | 112.8296 | 123.5962 | -123.8983 | -123.9304
5751.7188 | 123.6465 | -61.377 | 62.2009 | 0.11314 | 0.024355 | 0.017259 | 0.021719 | 0.06388 | 0.0018031 | 0.083535 | -56.8726 | 62.2147 | -61.702 | -61.5967 | 51.4389 | 23.9182 | 8.9813 | 8.7296 | 62.2009 | -61.734 | -0.32501 | 0.013733 | 4.5044 | -0.21973 | -10.762 | -0.35706 | 0 | 4.8294 | 70.3583 | 70.1065 | 112.8159 | 123.5916 | 4.5044 | 123.5779 | 85.2951 | -0.35706 | 123.5916 | 4.5044 | 85.2951 | 112.8159 | 123.5779 | -123.9029 | -123.9349
5752.7188 | 123.7244 | -61.3724 | 62.146 | 0.074997 | 0.023714 | 0.020677 | 0.019156 | 0.06388 | 0.00094847 | 0.084817 | -56.8817 | 62.2009 | -61.7432 | -61.6058 | 51.4709 | 24.0189 | 8.8486 | 8.6884 | 62.1872 | -61.7157 | -0.37079 | 0.054932 | 4.4907 | -0.23346 | -10.675 | -0.34332 | 0.041199 | 4.8614 | 70.2209 | 70.0607 | 112.8433 | 123.5733 | 4.4907 | 123.5596 | 85.3912 | -0.34332 | 123.5733 | 4.4907 | 85.3912 | 112.8433 | 123.5596 | -123.8892 | -123.8617
5753.7188 | 123.6237 | -61.4136 | 62.1368 | 0.090256 | 0.021151 | 0.021104 | 0.02001 | 0.063452 | 0.0018031 | 0.084176 | -56.9 | 62.233 | -61.7386 | -61.6287 | 51.4572 | 24.0234 | 8.9493 | 8.6975 | 62.1735 | -61.7386 | -0.32501 | 0.09613 | 4.5135 | -0.21515 | -10.6796 | -0.32501 | 0.036621 | 4.8386 | 70.3629 | 70.1111 | 112.8708 | 123.6465 | 4.5135 | 123.587 | 85.437 | -0.32501 | 123.6465 | 4.5135 | 85.437 | 112.8708 | 123.587 | -123.8754 | -123.8754
5754.7188 | 123.642 | -61.4044 | 62.1414 | -0.0012969 | 0.023928 | 0.018754 | 0.020437 | 0.062812 | -0.00054693 | 0.085244 | -56.8954 | 62.2421 | -61.7111 | -61.6287 | 51.4343 | 23.9319 | 8.9355 | 8.6563 | 62.1872 | -61.7386 | -0.3067 | 0.10071 | 4.509 | -0.2243 | -10.7071 | -0.33417 | 0.045777 | 4.8157 | 70.34 | 70.0607 | 112.8387 | 123.6465 | 4.509 | 123.5916 | 85.3363 | -0.33417 | 123.6465 | 4.509 | 85.3363 | 112.8387 | 123.5916 | -123.8525 | -123.88
5755.7188 | 123.7015 | -61.3953 | 62.1597 | -0.67268 | 0.02286 | 0.021958 | 0.018728 | 0.063239 | -0.00033333 | 0.083962 | -56.868 | 62.2101 | -61.702 | -61.6241 | 51.4572 | 23.9685 | 8.9859 | 8.7433 | 62.2009 | -61.7386 | -0.3067 | 0.050354 | 4.5273 | -0.22888 | -10.7025 | -0.34332 | 0.041199 | 4.834 | 70.3812 | 70.1385 | 112.8525 | 123.6053 | 4.5273 | 123.5962 | 85.3638 | -0.34332 | 123.6053 | 4.5273 | 85.3638 | 112.8525 | 123.5962 | -123.8617 | -123.8983
5756.7188 | 123.674 | -61.3861 | 62.1597 | 0.090256 | 0.025851 | 0.023881 | 0.019796 | 0.062171 | 0.0020167 | 0.086099 | -57.1838 | 62.1414 | -61.7432 | -61.6562 | 51.4847 | 24.0326 | 8.9813 | 8.7296 | 62.2101 | -61.734 | -0.35706 | -0.018311 | 4.2023 | -0.27008 | -10.675 | -0.3479 | 0.050354 | 4.5593 | 70.3674 | 70.1157 | 112.8708 | 123.5275 | 4.2023 | 123.5962 | 85.4187 | -0.3479 | 123.5275 | 4.2023 | 85.4187 | 112.8708 | 123.5962 | -123.9029 | -123.8937
5757.7188 | 123.7061 | -61.3907 | 62.1185 | 0.1284 | 0.024996 | 0.018327 | 0.017233 | 0.064734 | 0.0015893 | 0.085031 | -56.868 | 62.2055 | -61.7249 | -61.5967 | 51.4847 | 24.0143 | 8.8806 | 8.7296 | 62.2055 | -61.7065 | -0.33417 | 0.086975 | 4.5227 | -0.20599 | -10.6339 | -0.31586 | 0.086975 | 4.8569 | 70.2713 | 70.1202 | 112.8754 | 123.5962 | 4.5227 | 123.5962 | 85.405 | -0.31586 | 123.5962 | 4.5227 | 85.405 | 112.8754 | 123.5962 | -123.8434 | -123.8251
5758.7188 | 123.6649 | -61.3724 | 62.1368 | 0.03685 | 0.021578 | 0.015122 | 0.020224 | 0.063452 | 0.0013757 | 0.08439 | -56.8542 | 62.2284 | -61.7065 | -61.5875 | 51.4526 | 24.028 | 8.9447 | 8.7204 | 62.1918 | -61.7294 | -0.33417 | 0.091553 | 4.5181 | -0.21515 | -10.6842 | -0.35706 | 0.054931 | 4.8523 | 70.3171 | 70.0928 | 112.825 | 123.6008 | 4.5181 | 123.5641 | 85.4004 | -0.35706 | 123.6008 | 4.5181 | 85.4004 | 112.825 | 123.5641 | -123.8434 | -123.8663
5759.7344 | 123.7564 | -61.3586 | 62.1368 | 0.12077 | 0.016878 | 0.013413 | 0.010397 | 0.062812 | 0.0015893 | 0.086312 | -56.8588 | 62.0911 | -61.7065 | -61.5692 | 51.5213 | 24.1287 | 8.8165 | 8.7708 | 62.1506 | -61.6516 | -0.3479 | -0.045777 | 4.4998 | -0.21057 | -10.6155 | -0.29297 | 0.013733 | 4.8477 | 70.1752 | 70.1294 | 112.8799 | 123.4497 | 4.4998 | 123.5092 | 85.4874 | -0.29297 | 123.4497 | 4.4998 | 85.4874 | 112.8799 | 123.5092 | -123.8434 | -123.7885
5760.7188 | 123.6694 | -61.3907 | 62.1735 | 0.10551 | 0.023073 | 0.021104 | 0.023214 | 0.060034 | 9.4068e-05 | 0.085885 | -56.8451 | 62.2009 | -61.6928 | -61.6241 | 51.3977 | 23.9685 | 8.9218 | 8.6792 | 62.1964 | -61.7569 | -0.30212 | 0.027466 | 4.5456 | -0.23346 | -10.7758 | -0.36621 | 0.022888 | 4.8477 | 70.3125 | 70.0699 | 112.7884 | 123.5916 | 4.5456 | 123.587 | 85.3592 | -0.36621 | 123.5916 | 4.5456 | 85.3592 | 112.7884 | 123.587 | -123.8663 | -123.9304
5761.7188 | 123.6465 | -61.3861 | 62.1552 | -0.054703 | 0.024355 | 0.020249 | 0.018301 | 0.060675 | 0.0020167 | 0.085458 | -56.9138 | 62.233 | -61.702 | -61.6196 | 51.3657 | 23.9319 | 8.9264 | 8.6929 | 62.1964 | -61.7203 | -0.31586 | 0.07782 | 4.4724 | -0.23346 | -10.7895 | -0.33417 | 0.041199 | 4.7882 | 70.3125 | 70.079 | 112.7518 | 123.6191 | 4.4724 | 123.5825 | 85.318 | -0.33417 | 123.6191 | 4.4724 | 85.318 | 112.7518 | 123.5825 | -123.8571 | -123.8754
5762.7188 | 123.7381 | -61.3495 | 62.1506 | 0.92186 | 0.021792 | 0.014054 | 0.011038 | 0.061957 | 0.00073487 | 0.085458 | -56.8222 | 62.1368 | -61.6974 | -61.5692 | 51.4435 | 24.0189 | 8.8806 | 8.8852 | 62.1643 | -61.6653 | -0.3479 | -0.013733 | 4.5273 | -0.21973 | -10.7071 | -0.31586 | 0.013733 | 4.8752 | 70.2301 | 70.2347 | 112.793 | 123.4863 | 4.5273 | 123.5138 | 85.3683 | -0.31586 | 123.4863 | 4.5273 | 85.3683 | 112.793 | 123.5138 | -123.848 | -123.8159
5763.7188 | 123.7061 | -61.3815 | 62.178 | 0.12077 | 0.023501 | 0.020463 | 0.024069 | 0.060248 | -0.00011953 | 0.089517 | -56.8588 | 62.2147 | -61.6882 | -61.8851 | 51.3474 | 24.2432 | 8.8806 | 8.6655 | 62.1826 | -61.734 | -0.3067 | 0.036621 | 4.5227 | -0.50354 | -10.8307 | -0.35248 | 0.004577 | 4.8294 | 70.2621 | 70.047 | 112.7289 | 123.5962 | 4.5227 | 123.5641 | 85.6247 | -0.35248 | 123.5962 | 4.5227 | 85.6247 | 112.7289 | 123.5641 | -123.8663 | -123.912
5764.7344 | 123.7701 | -61.3312 | 62.1277 | -1.5577 | 0.019656 | 0.017899 | 0.01232 | 0.06153 | -0.00033333 | 0.083108 | -57.0236 | 62.1277 | -61.6791 | -61.5509 | 51.5121 | 24.0921 | 8.876 | 8.812 | 62.1689 | -61.6562 | -0.3479 | 0 | 4.3076 | -0.21973 | -10.6155 | -0.32501 | 0.041198 | 4.6555 | 70.2072 | 70.1431 | 112.8433 | 123.4589 | 4.3076 | 123.5001 | 85.4233 | -0.32501 | 123.4589 | 4.3076 | 85.4233 | 112.8433 | 123.5001 | -123.8068 | -123.7839
5765.7188 | 123.6786 | -61.3815 | 62.1872 | 0.04448 | 0.023073 | 0.019608 | 0.023214 | 0.060889 | -0.00097413 | 0.083962 | -56.7993 | 62.2284 | -61.7111 | -61.5829 | 51.4618 | 23.996 | 8.9355 | 8.7433 | 62.1918 | -61.7157 | -0.32959 | 0.041199 | 4.5822 | -0.20142 | -10.7254 | -0.33417 | 0.004577 | 4.9118 | 70.3171 | 70.1248 | 112.8433 | 123.6099 | 4.5822 | 123.5733 | 85.3775 | -0.33417 | 123.6099 | 4.5822 | 85.3775 | 112.8433 | 123.5733 | -123.8983 | -123.9029
5766.7188 | 123.6832 | -61.3953 | 62.1689 | 0.11314 | 0.021578 | 0.020677 | 0.02236 | 0.063025 | 0.00052127 | 0.083108 | -56.8542 | 62.233 | -61.6974 | -61.6104 | 51.4069 | 23.9456 | 8.9264 | 8.6655 | 62.2192 | -61.7203 | -0.30212 | 0.064087 | 4.541 | -0.21515 | -10.762 | -0.32501 | 0.050354 | 4.8431 | 70.3217 | 70.0607 | 112.8021 | 123.6282 | 4.541 | 123.6145 | 85.3409 | -0.32501 | 123.6282 | 4.541 | 85.3409 | 112.8021 | 123.6145 | -123.8663 | -123.8892
5767.7188 | 123.7839 | -61.3312 | 62.1277 | 0.11314 | 0.020724 | 0.022599 | 0.017447 | 0.063025 | 0.00073487 | 0.084603 | -56.7902 | 62.1368 | -61.7065 | -61.5051 | 51.4664 | 24.0601 | 8.7296 | 8.7891 | 62.1414 | -61.6653 | -0.37537 | 0.009155 | 4.541 | -0.17395 | -10.6613 | -0.33417 | 0.013732 | 4.9164 | 70.0607 | 70.1202 | 112.7975 | 123.468 | 4.541 | 123.4726 | 85.3912 | -0.33417 | 123.468 | 4.541 | 85.3912 | 112.7975 | 123.4726 | -123.8342 | -123.793
5768.7188 | 123.6374 | -61.377 | 62.1689 | 0.059738 | 0.022219 | 0.020036 | 0.020651 | 0.061743 | -0.00011953 | 0.085031 | -56.8359 | 62.2375 | -61.6882 | -61.5921 | 51.416 | 23.9685 | 8.931 | 8.6838 | 62.178 | -61.7157 | -0.31128 | 0.068665 | 4.541 | -0.21515 | -10.7529 | -0.33875 | 0.009156 | 4.8523 | 70.3079 | 70.0607 | 112.793 | 123.6145 | 4.541 | 123.555 | 85.3455 | -0.33875 | 123.6145 | 4.541 | 85.3455 | 112.793 | 123.555 | -123.8571 | -123.8846
5769.7188 | 123.7518 | -61.3403 | 62.1506 | -1.1076 | 0.019015 | 0.016831 | 0.0097562 | 0.060675 | 0.00073487 | 0.08738 | -56.9687 | 62.1368 | -61.6745 | -61.5509 | 51.4526 | 24.0509 | 8.8211 | 8.8257 | 62.1643 | -61.6653 | -0.33417 | -0.013733 | 4.3716 | -0.21057 | -10.6979 | -0.32501 | 0.013733 | 4.7058 | 70.1614 | 70.166 | 112.793 | 123.4772 | 4.3716 | 123.5046 | 85.3912 | -0.32501 | 123.4772 | 4.3716 | 85.3912 | 112.793 | 123.5046 | -123.8251 | -123.8159
5770.7188 | 123.6923 | -61.3907 | 62.1826 | 0.14366 | 0.024569 | 0.016618 | 0.025351 | 0.062171 | -0.0026831 | 0.085885 | -56.8634 | 62.2284 | -61.7203 | -61.5189 | 51.2512 | 23.9639 | 8.9951 | 8.6563 | 62.2147 | -61.7203 | -0.32959 | 0.045777 | 4.5273 | -0.12817 | -10.9314 | -0.32959 | 0.032044 | 4.8569 | 70.3857 | 70.047 | 112.6419 | 123.6191 | 4.5273 | 123.6053 | 85.3546 | -0.32959 | 123.6191 | 4.5273 | 85.3546 | 112.6419 | 123.6053 | -123.9029 | -123.9029
5771.7188 | 123.6511 | -61.3861 | 62.178 | 0.074997 | 0.023287 | 0.022813 | 0.02236 | 0.060675 | -0.0022559 | 0.085244 | -56.7947 | 62.2192 | -61.7203 | -61.5967 | 51.4114 | 23.9227 | 8.9218 | 8.725 | 62.2055 | -61.7249 | -0.33417 | 0.041198 | 4.5914 | -0.21057 | -10.7666 | -0.33875 | 0.027465 | 4.9255 | 70.3079 | 70.1111 | 112.7975 | 123.6053 | 4.5914 | 123.5916 | 85.3088 | -0.33875 | 123.6053 | 4.5914 | 85.3088 | 112.7975 | 123.5916 | -123.8983 | -123.9029
5772.7344 | 123.7656 | -61.3266 | 62.0956 | 0.15129 | 0.022005 | 0.019395 | 0.013815 | 0.061103 | 0.0011621 | 0.085458 | -56.7947 | 62.1048 | -61.7065 | -61.5326 | 51.4664 | 24.1104 | 8.7616 | 8.8394 | 62.1323 | -61.6791 | -0.37994 | 0.009155 | 4.5319 | -0.20599 | -10.6293 | -0.35248 | 0.036621 | 4.9118 | 70.0882 | 70.166 | 112.793 | 123.4314 | 4.5319 | 123.4589 | 85.437 | -0.35248 | 123.4314 | 4.5319 | 85.437 | 112.793 | 123.4589 | -123.8022 | -123.7747
5773.7188 | 123.6465 | -61.3998 | 62.1826 | 0.10551 | 0.022005 | 0.018327 | 0.021078 | 0.060675 | -0.0018285 | 0.086312 | -56.8359 | 62.2147 | -61.6974 | -61.6058 | 51.3657 | 24.147 | 8.345 | 8.5327 | 62.1002 | -61.7981 | -0.29755 | 0.032044 | 4.5639 | -0.20599 | -10.817 | -0.39825 | -0.082397 | 4.8615 | 69.7449 | 69.9326 | 112.7655 | 123.6145 | 4.5639 | 123.5001 | 85.5469 | -0.39825 | 123.6145 | 4.5639 | 85.5469 | 112.7655 | 123.5001 | -123.88 | -123.9807
5774.7344 | 123.761 | -61.3449 | 62.1231 | 0.097885 | 0.019442 | 0.017472 | 0.011892 | 0.059394 | 9.4068e-05 | 0.086953 | -56.8314 | 62.0865 | -61.7111 | -61.5601 | 51.4297 | 24.0921 | 8.8394 | 8.8531 | 62.1735 | -61.6699 | -0.36621 | -0.036621 | 4.5136 | -0.21515 | -10.6934 | -0.32501 | 0.050354 | 4.8798 | 70.1843 | 70.1981 | 112.7747 | 123.4314 | 4.5136 | 123.5184 | 85.437 | -0.32501 | 123.4314 | 4.5136 | 85.437 | 112.7747 | 123.5184 | -123.8342 | -123.793
5775.7188 | 123.7518 | -61.3907 | 62.0956 | 0.013962 | 0.021792 | 0.019181 | 0.022787 | 0.063452 | 9.4068e-05 | 0.08738 | -56.8176 | 62.2284 | -61.7065 | -61.6241 | 51.4023 | 24.0509 | 8.963 | 8.7341 | 62.178 | -61.7386 | -0.31586 | 0.13275 | 4.5731 | -0.23346 | -10.6934 | -0.3479 | 0.082398 | 4.8889 | 70.3537 | 70.1248 | 112.793 | 123.6191 | 4.5731 | 123.5687 | 85.4416 | -0.3479 | 123.6191 | 4.5731 | 85.4416 | 112.793 | 123.5687 | -123.8022 | -123.8342
5776.7188 | 123.6832 | -61.3724 | 62.1552 | 0.3344 | 0.024355 | 0.019608 | 0.021292 | 0.062598 | 0.0035121 | 0.084817 | -56.813 | 62.1826 | -61.734 | -61.5967 | 51.4023 | 24.0051 | 8.8943 | 8.7204 | 62.1964 | -61.7294 | -0.36163 | 0.027466 | 4.5593 | -0.22431 | -10.7529 | -0.35706 | 0.041199 | 4.921 | 70.2667 | 70.0928 | 112.7747 | 123.555 | 4.5593 | 123.5687 | 85.3775 | -0.35706 | 123.555 | 4.5593 | 85.3775 | 112.7747 | 123.5687 | -123.8892 | -123.8846
5777.7344 | 123.7839 | -61.3266 | 62.1414 | -0.039444 | 0.018801 | 0.018327 | 0.011892 | 0.060675 | -0.00033333 | 0.085031 | -56.8085 | 62.114 | -61.7065 | -61.5097 | 51.4938 | 24.1333 | 8.8898 | 8.9035 | 62.1689 | -61.6333 | -0.37994 | -0.027465 | 4.5181 | -0.18311 | -10.6476 | -0.3067 | 0.027466 | 4.8981 | 70.2164 | 70.2301 | 112.8204 | 123.4406 | 4.5181 | 123.4955 | 85.4599 | -0.3067 | 123.4406 | 4.5181 | 85.4599 | 112.8204 | 123.4955 | -123.848 | -123.7747
5778.7188 | 123.6603 | -61.377 | 62.1826 | -0.016556 | 0.022646 | 0.022172 | 0.024496 | 0.059821 | 0.0043665 | 0.083322 | -56.7993 | 62.2147 | -61.6882 | -61.6013 | 51.3702 | 23.9731 | 8.9813 | 8.7799 | 62.1964 | -61.7249 | -0.31128 | 0.032044 | 4.5776 | -0.2243 | -10.8124 | -0.3479 | 0.013733 | 4.8889 | 70.3583 | 70.1569 | 112.7472 | 123.5916 | 4.5776 | 123.5733 | 85.35 | -0.3479 | 123.5916 | 4.5776 | 85.35 | 112.7472 | 123.5733 | -123.8708 | -123.9075
5779.7188 | 123.6694 | -61.4044 | 62.1689 | 0.03685 | 0.02286 | 0.020249 | 0.023214 | 0.060248 | -0.00011953 | 0.084817 | -56.7902 | 62.2147 | -61.7249 | -61.5829 | 51.4114 | 24.0326 | 8.963 | 8.7845 | 62.1964 | -61.7111 | -0.32044 | 0.045777 | 4.6143 | -0.17853 | -10.7574 | -0.3067 | 0.027466 | 4.9347 | 70.3674 | 70.1889 | 112.8159 | 123.6191 | 4.6143 | 123.6008 | 85.437 | -0.3067 | 123.6191 | 4.6143 | 85.437 | 112.8159 | 123.6008 | -123.8937 | -123.88
5780.7188 | 123.6603 | -61.3632 | 62.1552 | 0.097885 | 0.024355 | 0.017899 | 0.020437 | 0.062384 | 0.0022303 | 0.083749 | -56.8176 | 62.2513 | -61.7111 | -61.8118 | 51.741 | 24.234 | 8.8074 | 8.8348 | 62.1643 | -61.734 | -0.3479 | 0.096131 | 4.5456 | -0.44861 | -10.4141 | -0.37079 | 0.009156 | 4.8935 | 70.1706 | 70.1981 | 113.1042 | 123.6145 | 4.5456 | 123.5275 | 85.5972 | -0.37079 | 123.6145 | 4.5456 | 85.5972 | 113.1042 | 123.5275 | -123.8663 | -123.8892
5781.7188 | 123.6511 | -61.4044 | 62.1735 | 0.090256 | 0.022005 | 0.021531 | 0.018728 | 0.064307 | 9.4068e-05 | 0.085885 | -56.8085 | 62.2375 | -61.7111 | -61.6241 | 51.4069 | 23.9822 | 8.9767 | 8.7296 | 62.1964 | -61.7477 | -0.3067 | 0.064087 | 4.5959 | -0.21973 | -10.7666 | -0.34332 | 0.022888 | 4.9026 | 70.3812 | 70.134 | 112.8113 | 123.642 | 4.5959 | 123.6008 | 85.3867 | -0.34332 | 123.642 | 4.5959 | 85.3867 | 112.8113 | 123.6008 | -123.8846 | -123.9212
5782.7188 | 123.6786 | -61.3861 | 62.1643 | 0.090256 | 0.023073 | 0.020677 | 0.018087 | 0.062384 | 0.00052127 | 0.087594 | -56.8268 | 62.2238 | -61.734 | -61.6058 | 51.3474 | 24.0005 | 8.8943 | 8.7433 | 62.2055 | -61.7203 | -0.3479 | 0.059509 | 4.5593 | -0.21973 | -10.817 | -0.33417 | 0.041198 | 4.9072 | 70.2805 | 70.1294 | 112.7335 | 123.6099 | 4.5593 | 123.5916 | 85.3867 | -0.33417 | 123.6099 | 4.5593 | 85.3867 | 112.7335 | 123.5916 | -123.8983 | -123.8846
5783.7188 | 123.7106 | -61.3998 | 62.178 | -0.016556 | 0.023287 | 0.018968 | 0.019369 | 0.063452 | 0.00030767 | 0.085671 | -56.7444 | 62.2009 | -61.7157 | -61.5967 | 51.3336 | 23.9868 | 8.931 | 8.7616 | 62.1872 | -61.734 | -0.31586 | 0.022888 | 4.6555 | -0.19684 | -10.8444 | -0.33417 | 0.009155 | 4.9713 | 70.3308 | 70.1614 | 112.7335 | 123.6008 | 4.6555 | 123.587 | 85.3867 | -0.33417 | 123.6008 | 4.6555 | 85.3867 | 112.7335 | 123.587 | -123.8937 | -123.912
5784.7188 | 123.7015 | -61.3724 | 62.1552 | 0.11314 | 0.024996 | 0.019181 | 0.017019 | 0.065802 | -0.00076053 | 0.085458 | -56.7078 | 62.1918 | -61.7294 | -61.5234 | 51.3153 | 23.909 | 9.05 | 8.7936 | 62.2009 | -61.734 | -0.35706 | 0.036621 | 4.6646 | -0.15106 | -10.8398 | -0.36163 | 0.045777 | 5.0217 | 70.4224 | 70.166 | 112.6877 | 123.5641 | 4.6646 | 123.5733 | 85.2814 | -0.36163 | 123.5641 | 4.6646 | 85.2814 | 112.6877 | 123.5733 | -123.8846 | -123.8892
5785.7188 | 123.6649 | -61.3724 | 62.1643 | 0.04448 | 0.021364 | 0.017899 | 0.019796 | 0.062812 | 0.0011621 | 0.086953 | -56.7719 | 62.2421 | -61.6974 | -61.6013 | 51.297 | 23.9502 | 9.0179 | 8.8028 | 62.1872 | -61.7249 | -0.32501 | 0.077819 | 4.6005 | -0.22888 | -10.8673 | -0.35248 | 0.022888 | 4.9255 | 70.3903 | 70.1752 | 112.6694 | 123.6145 | 4.6005 | 123.5596 | 85.3226 | -0.35248 | 123.6145 | 4.6005 | 85.3226 | 112.6694 | 123.5596 | -123.8617 | -123.8892
5786.7188 | 123.6832 | -61.377 | 62.178 | -0.0012969 | 0.022433 | 0.023667 | 0.020865 | 0.06388 | 0.00030767 | 0.085671 | -56.7581 | 62.2009 | -61.7111 | -61.5921 | 51.3336 | 24.0646 | 9.0729 | 8.8623 | 62.178 | -61.7111 | -0.33417 | 0.022888 | 4.6188 | -0.21515 | -10.8444 | -0.33417 | 0 | 4.953 | 70.4498 | 70.2393 | 112.7106 | 123.5779 | 4.6188 | 123.555 | 85.4416 | -0.33417 | 123.5779 | 4.6188 | 85.4416 | 112.7106 | 123.555 | -123.8892 | -123.8892
5787.7188 | 123.7747 | -61.3495 | 62.1231 | 0.14366 | 0.021364 | 0.017045 | 0.015738 | 0.063239 | -0.00076053 | 0.086526 | -56.7307 | 62.114 | -61.6791 | -61.5372 | 51.4114 | 24.1379 | 8.9127 | 8.9355 | 62.1552 | -61.6379 | -0.32959 | -0.009155 | 4.6188 | -0.18768 | -10.7117 | -0.28839 | 0.032043 | 4.9484 | 70.2621 | 70.285 | 112.7609 | 123.4634 | 4.6188 | 123.5046 | 85.4874 | -0.28839 | 123.4634 | 4.6188 | 85.4874 | 112.7609 | 123.5046 | -123.8022 | -123.761
5788.7188 | 123.6694 | -61.3815 | 62.1552 | 0.021591 | 0.023287 | 0.02089 | 0.020865 | 0.061743 | 0.0020167 | 0.083108 | -56.7673 | 62.2284 | -61.7157 | -61.6241 | 51.3245 | 23.9914 | 9.0179 | 8.8211 | 62.178 | -61.7386 | -0.33417 | 0.073243 | 4.6143 | -0.24262 | -10.8307 | -0.35705 | 0.022889 | 4.9484 | 70.3995 | 70.2026 | 112.706 | 123.6099 | 4.6143 | 123.5596 | 85.3729 | -0.35705 | 123.6099 | 4.6143 | 85.3729 | 112.706 | 123.5596 | -123.8708 | -123.8937
5789.7188 | 123.674 | -61.3815 | 62.1826 | 0.059738 | 0.02286 | 0.018968 | 0.021933 | 0.06388 | 0.00073487 | 0.085031 | -56.7673 | 62.2101 | -61.7249 | -61.5829 | 51.3153 | 24.0005 | 8.9996 | 8.8257 | 62.2055 | -61.6974 | -0.34332 | 0.027466 | 4.6143 | -0.20142 | -10.8673 | -0.31586 | 0.022888 | 4.9576 | 70.3812 | 70.2072 | 112.6968 | 123.5916 | 4.6143 | 123.587 | 85.3821 | -0.31586 | 123.5916 | 4.6143 | 85.3821 | 112.6968 | 123.587 | -123.9075 | -123.88
5790.7188 | 123.6923 | -61.409 | 62.1048 | 0.12077 | 0.022646 | 0.021745 | 0.020651 | 0.061957 | 0.0018031 | 0.084817 | -56.7947 | 62.233 | -61.7249 | -61.6196 | 51.2604 | 24.0326 | 9.0546 | 8.8165 | 62.1826 | -61.7386 | -0.31586 | 0.12817 | 4.6143 | -0.21057 | -10.8444 | -0.32959 | 0.07782 | 4.9301 | 70.4636 | 70.2255 | 112.6694 | 123.642 | 4.6143 | 123.5916 | 85.4416 | -0.32959 | 123.642 | 4.6143 | 85.4416 | 112.6694 | 123.5916 | -123.8297 | -123.8434
5791.7188 | 123.6603 | -61.3907 | 62.1689 | 0.074997 | 0.020937 | 0.021531 | 0.018515 | 0.059607 | 0.0011621 | 0.086099 | -56.7856 | 62.2513 | -61.7294 | -61.6241 | 51.3153 | 24.0326 | 9.0088 | 8.7982 | 62.1735 | -61.7294 | -0.33874 | 0.082398 | 4.6051 | -0.23346 | -10.8536 | -0.33874 | 0.004578 | 4.9438 | 70.3995 | 70.1889 | 112.706 | 123.642 | 4.6051 | 123.5641 | 85.4233 | -0.33874 | 123.642 | 4.6051 | 85.4233 | 112.706 | 123.5641 | -123.8983 | -123.8983
5792.7344 | 123.7839 | -61.3174 | 62.1506 | 0.067368 | 0.018801 | 0.016404 | 0.011679 | 0.060034 | 0.0011621 | 0.085244 | -56.7398 | 62.1277 | -61.7157 | -61.5601 | 51.4114 | 24.1425 | 8.8257 | 8.8669 | 62.1277 | -61.6516 | -0.39825 | -0.022888 | 4.5776 | -0.24262 | -10.7391 | -0.33417 | -0.022888 | 4.9759 | 70.1431 | 70.1843 | 112.7289 | 123.4451 | 4.5776 | 123.4451 | 85.4599 | -0.33417 | 123.4451 | 4.5776 | 85.4599 | 112.7289 | 123.4451 | -123.8663 | -123.8022
5793.7188 | 123.6969 | -61.3449 | 62.1735 | -0.039444 | 0.024355 | 0.017045 | 0.021719 | 0.060248 | -0.0011877 | 0.085885 | -56.7215 | 62.2375 | -61.6882 | -61.5417 | 51.3565 | 24.0372 | 9.05 | 8.9264 | 62.178 | -61.7249 | -0.34332 | 0.064087 | 4.6234 | -0.19684 | -10.817 | -0.37994 | 0.004578 | 4.9667 | 70.3949 | 70.2713 | 112.7014 | 123.5825 | 4.6234 | 123.523 | 85.3821 | -0.37994 | 123.5825 | 4.6234 | 85.3821 | 112.7014 | 123.523 | -123.8617 | -123.8983
5794.7188 | 123.6969 | -61.3632 | 62.1735 | -0.016556 | 0.02286 | 0.023026 | 0.021719 | 0.060248 | 0.00030767 | 0.086526 | -56.7215 | 62.233 | -61.6562 | -61.5875 | 51.3016 | 24.0189 | 9.0363 | 8.8348 | 62.2238 | -61.7249 | -0.29297 | 0.059509 | 4.6417 | -0.2243 | -10.8719 | -0.36163 | 0.050354 | 4.9347 | 70.3995 | 70.1981 | 112.6648 | 123.5962 | 4.6417 | 123.587 | 85.3821 | -0.36163 | 123.5962 | 4.6417 | 85.3821 | 112.6648 | 123.587 | -123.8297 | -123.8983
5795.7188 | 123.7061 | -61.377 | 62.1597 | 0.021591 | 0.021792 | 0.019395 | 0.02001 | 0.06153 | 0.0011621 | 0.084817 | -56.7261 | 62.2284 | -61.6791 | -61.5875 | 51.3382 | 24.0784 | 8.9767 | 8.8577 | 62.2009 | -61.7065 | -0.30212 | 0.068665 | 4.6509 | -0.21057 | -10.8215 | -0.32959 | 0.041199 | 4.953 | 70.3537 | 70.2347 | 112.7151 | 123.6053 | 4.6509 | 123.5779 | 85.4553 | -0.32959 | 123.6053 | 4.6509 | 85.4553 | 112.7151 | 123.5779 | -123.8388 | -123.8663
5796.7188 | 123.6923 | -61.3678 | 62.1552 | -0.077591 | 0.021364 | 0.018327 | 0.020437 | 0.062171 | 0.0020167 | 0.085671 | -56.6986 | 62.233 | -61.6928 | -61.5646 | 51.3199 | 24.0921 | 8.9722 | 8.844 | 62.2147 | -61.702 | -0.32501 | 0.07782 | 4.6692 | -0.19684 | -10.8353 | -0.33417 | 0.05951 | 4.9942 | 70.34 | 70.2118 | 112.6877 | 123.6008 | 4.6692 | 123.5825 | 85.4599 | -0.33417 | 123.6008 | 4.6692 | 85.4599 | 112.6877 | 123.5825 | -123.848 | -123.8571
5797.7188 | 123.6649 | -61.4044 | 62.1918 | 0.0063326 | 0.023073 | 0.021317 | 0.018942 | 0.062171 | 9.4068e-05 | 0.083108 | -56.7307 | 62.2009 | -61.6745 | -61.6058 | 51.3245 | 24.0234 | 9.0271 | 8.8074 | 62.1964 | -61.6974 | -0.27008 | 0.009156 | 4.6738 | -0.20142 | -10.8673 | -0.29297 | 0.004578 | 4.9438 | 70.4315 | 70.2118 | 112.7289 | 123.6053 | 4.6738 | 123.6008 | 85.4279 | -0.29297 | 123.6053 | 4.6738 | 85.4279 | 112.7289 | 123.6008 | -123.8663 | -123.8892
5798.7188 | 123.6832 | -61.377 | 62.1552 | -0.016556 | 0.023501 | 0.017472 | 0.019583 | 0.062598 | -0.0014013 | 0.083749 | -56.7123 | 62.2192 | -61.7065 | -61.5829 | 51.3199 | 24.0189 | 9.0591 | 8.8257 | 62.1918 | -61.702 | -0.32959 | 0.064087 | 4.6646 | -0.20599 | -10.8353 | -0.32501 | 0.036621 | 4.9942 | 70.4361 | 70.2026 | 112.6968 | 123.5962 | 4.6646 | 123.5687 | 85.3958 | -0.32501 | 123.5962 | 4.6646 | 85.3958 | 112.6968 | 123.5687 | -123.8617 | -123.8571
5799.7188 | 123.7198 | -61.3815 | 62.1735 | -0.024185 | 0.023073 | 0.016191 | 0.018728 | 0.064521 | 0.00073487 | 0.085244 | -56.6666 | 62.2375 | -61.702 | -61.5372 | 51.3794 | 24.0692 | 8.9584 | 8.8989 | 62.2055 | -61.7249 | -0.32043 | 0.064087 | 4.715 | -0.15564 | -10.7941 | -0.34332 | 0.032043 | 5.0354 | 70.34 | 70.2805 | 112.7609 | 123.6191 | 4.715 | 123.587 | 85.4507 | -0.34332 | 123.6191 | 4.715 | 85.4507 | 112.7609 | 123.587 | -123.8754 | -123.8983
5800.7188 | 123.6877 | -61.3861 | 62.1689 | -0.047073 | 0.023501 | 0.018327 | 0.019156 | 0.063025 | -0.00097413 | 0.083962 | -56.6986 | 62.2192 | -61.6974 | -61.5738 | 51.3474 | 24.0921 | 9.0225 | 8.8577 | 62.2147 | -61.6974 | -0.31128 | 0.050354 | 4.6875 | -0.18768 | -10.8215 | -0.31128 | 0.045777 | 4.9988 | 70.4086 | 70.2438 | 112.7335 | 123.6053 | 4.6875 | 123.6008 | 85.4782 | -0.31128 | 123.6053 | 4.6875 | 85.4782 | 112.7335 | 123.6008 | -123.8663 | -123.8663
5801.7188 | 123.6923 | -61.3403 | 62.1643 | -0.0089264 | 0.024569 | 0.019822 | 0.019796 | 0.063239 | 0.0020167 | 0.085244 | -56.6849 | 62.2559 | -61.702 | -61.5738 | 51.3657 | 24.1287 | 8.9493 | 8.844 | 62.1918 | -61.7249 | -0.36163 | 0.091552 | 4.6555 | -0.23346 | -10.7986 | -0.38452 | 0.027465 | 5.0171 | 70.2896 | 70.1843 | 112.706 | 123.5962 | 4.6555 | 123.5321 | 85.4691 | -0.38452 | 123.5962 | 4.6555 | 85.4691 | 112.706 | 123.5321 | -123.8663 | -123.8892
5802.7188 | 123.7701 | -61.3495 | 62.114 | 0.21996 | 0.02286 | 0.017899 | 0.016592 | 0.06388 | 0.0024439 | 0.086312 | -56.6986 | 62.1826 | -61.7111 | -61.5326 | 51.3931 | 24.1608 | 8.8303 | 8.9218 | 62.1643 | -61.6791 | -0.36163 | 0.068664 | 4.6509 | -0.18311 | -10.7208 | -0.32959 | 0.050354 | 5.0125 | 70.1797 | 70.2713 | 112.7426 | 123.5321 | 4.6509 | 123.5138 | 85.5103 | -0.32959 | 123.5321 | 4.6509 | 85.5103 | 112.7426 | 123.5138 | -123.8251 | -123.793
5803.7188 | 123.6877 | -61.3586 | 62.1689 | 0.03685 | 0.022646 | 0.024095 | 0.017874 | 0.063239 | -0.00011953 | 0.085244 | -56.6528 | 62.2238 | -61.702 | -61.5463 | 51.3519 | 24.1104 | 8.9539 | 8.8989 | 62.1918 | -61.7065 | -0.34332 | 0.054932 | 4.7058 | -0.18768 | -10.817 | -0.3479 | 0.022888 | 5.0491 | 70.3125 | 70.2576 | 112.7106 | 123.5825 | 4.7058 | 123.5504 | 85.4691 | -0.3479 | 123.5825 | 4.7058 | 85.4691 | 112.7106 | 123.5504 | -123.8708 | -123.8754
5804.7188 | 123.6877 | -61.3632 | 62.1597 | -0.0012969 | 0.02286 | 0.019822 | 0.020224 | 0.065161 | -0.00011953 | 0.085885 | -56.6849 | 62.2284 | -61.6745 | -61.5829 | 51.3062 | 24.0509 | 9.0088 | 8.8898 | 62.2192 | -61.7065 | -0.31128 | 0.068665 | 4.6783 | -0.21973 | -10.8536 | -0.34332 | 0.059509 | 4.9896 | 70.372 | 70.253 | 112.6694 | 123.5916 | 4.6783 | 123.5825 | 85.4141 | -0.34332 | 123.5916 | 4.6783 | 85.4141 | 112.6694 | 123.5825 | -123.8342 | -123.8663
5805.7188 | 123.6969 | -61.3861 | 62.146 | -0.024185 | 0.02286 | 0.021531 | 0.019369 | 0.064307 | -0.00033333 | 0.085671 | -56.6803 | 62.2284 | -61.6837 | -61.5646 | 51.3245 | 24.0967 | 8.9584 | 8.8806 | 62.2101 | -61.6974 | -0.29755 | 0.082398 | 4.7058 | -0.17853 | -10.8215 | -0.31128 | 0.064087 | 5.0034 | 70.3445 | 70.2667 | 112.7106 | 123.6145 | 4.7058 | 123.5962 | 85.4828 | -0.31128 | 123.6145 | 4.7058 | 85.4828 | 112.7106 | 123.5962 | -123.8297 | -123.8434
5806.7188 | 123.7061 | -61.3632 | 62.1872 | -0.10811 | 0.021151 | 0.015763 | 0.01766 | 0.064521 | 0.00030767 | 0.086099 | -56.6574 | 62.233 | -61.6837 | -61.5372 | 51.3702 | 24.1425 | 8.6426 | 8.8852 | 62.2147 | -61.7249 | -0.32044 | 0.045776 | 4.7058 | -0.17395 | -10.817 | -0.36163 | 0.027466 | 5.0262 | 70.0058 | 70.2484 | 112.7335 | 123.5962 | 4.7058 | 123.5779 | 85.5057 | -0.36163 | 123.5962 | 4.7058 | 85.5057 | 112.7335 | 123.5779 | -123.8709 | -123.912
5807.7188 | 123.7885 | -61.3953 | 62.178 | 0.13603 | 0.023501 | 0.02089 | 0.018301 | 0.065375 | 0.0011621 | 0.085885 | -56.7535 | 62.2238 | -61.702 | -61.6287 | 51.3199 | 24.0417 | 9.0363 | 8.4 | 62.1643 | -61.7432 | -0.3067 | 0.045776 | 4.6417 | -0.23346 | -10.8582 | -0.3479 | -0.013733 | 4.9484 | 70.4315 | 69.7952 | 112.7151 | 123.6191 | 4.6417 | 123.5596 | 85.437 | -0.3479 | 123.6191 | 4.6417 | 85.437 | 112.7151 | 123.5596 | -123.88 | -123.9212
5808.7188 | 123.7289 | -61.3815 | 62.1643 | -0.47432 | 0.023287 | 0.021317 | 0.020224 | 0.061957 | -0.0020421 | 0.085244 | -56.6757 | 62.2284 | -61.6928 | -61.5509 | 51.3153 | 24.0967 | 9.0179 | 9.0134 | 62.2147 | -61.6882 | -0.31128 | 0.064087 | 4.7058 | -0.16937 | -10.849 | -0.3067 | 0.050354 | 5.0171 | 70.3995 | 70.3949 | 112.6968 | 123.6099 | 4.7058 | 123.5962 | 85.4782 | -0.3067 | 123.6099 | 4.7058 | 85.4782 | 112.6968 | 123.5962 | -123.8571 | -123.8525
5809.7188 | 123.7152 | -61.3632 | 62.178 | -0.024185 | 0.023073 | 0.014909 | 0.015097 | 0.064093 | -0.00011953 | 0.085671 | -56.662 | 62.233 | -61.7157 | -61.5097 | 51.3336 | 24.1425 | 9.0042 | 9.0271 | 62.2009 | -61.6882 | -0.35248 | 0.054931 | 4.7012 | -0.14648 | -10.8444 | -0.32501 | 0.022888 | 5.0537 | 70.3674 | 70.3903 | 112.6968 | 123.5962 | 4.7012 | 123.5641 | 85.5057 | -0.32501 | 123.5962 | 4.7012 | 85.5057 | 112.6968 | 123.5641 | -123.8937 | -123.8663
5810.7188 | 123.7061 | -61.3724 | 62.1689 | -0.09285 | 0.024782 | 0.020249 | 0.017874 | 0.061316 | 0.0022303 | 0.085244 | -56.6437 | 62.2284 | -61.7203 | -61.5372 | 51.4069 | 24.1333 | 8.7891 | 8.8669 | 62.1918 | -61.7111 | -0.3479 | 0.05951 | 4.7287 | -0.1648 | -10.762 | -0.33875 | 0.022888 | 5.0766 | 70.1614 | 70.2393 | 112.7792 | 123.6008 | 4.7287 | 123.5641 | 85.5057 | -0.33875 | 123.6008 | 4.7287 | 85.5057 | 112.7792 | 123.5641 | -123.8892 | -123.88
5811.7188 | 123.7061 | -61.3586 | 62.1918 | -0.062332 | 0.022646 | 0.019395 | 0.02001 | 0.063025 | 0.00030767 | 0.085671 | -56.6528 | 62.2284 | -61.7111 | -61.5417 | 51.3474 | 24.1196 | 8.9539 | 8.9951 | 62.2147 | -61.6837 | -0.35248 | 0.036622 | 4.7058 | -0.1831 | -10.8444 | -0.32501 | 0.022889 | 5.0583 | 70.3125 | 70.3537 | 112.706 | 123.587 | 4.7058 | 123.5733 | 85.4782 | -0.32501 | 123.587 | 4.7058 | 85.4782 | 112.706 | 123.5733 | -123.9029 | -123.8754
5812.7188 | 123.7701 | -61.3541 | 62.1277 | 0.44884 | 0.021364 | 0.017045 | 0.014029 | 0.061957 | 0.00094847 | 0.085671 | -56.6574 | 62.1597 | -61.6699 | -61.5372 | 51.3748 | 24.1196 | 8.8074 | 8.9676 | 62.1506 | -61.6608 | -0.31586 | 0.032043 | 4.6967 | -0.18311 | -10.7529 | -0.3067 | 0.022888 | 5.0125 | 70.1614 | 70.3217 | 112.7289 | 123.5138 | 4.6967 | 123.5046 | 85.4736 | -0.3067 | 123.5138 | 4.6967 | 85.4736 | 112.7289 | 123.5046 | -123.7976 | -123.7885
5813.7188 | 123.7198 | -61.377 | 62.2009 | -0.16914 | 0.020083 | 0.019181 | 0.017447 | 0.062384 | -0.00054693 | 0.084817 | -56.6483 | 62.233 | -61.6882 | -61.5189 | 51.3428 | 24.0784 | 9.0271 | 8.9767 | 62.2375 | -61.702 | -0.31128 | 0.032043 | 4.7287 | -0.14191 | -10.8582 | -0.32501 | 0.036621 | 5.04 | 70.4041 | 70.3537 | 112.7197 | 123.6099 | 4.7287 | 123.6145 | 85.4553 | -0.32501 | 123.6099 | 4.7287 | 85.4553 | 112.7197 | 123.6145 | -123.8892 | -123.9029
5814.7188 | 123.6923 | -61.3815 | 62.1735 | -0.12337 | 0.019228 | 0.017899 | 0.018515 | 0.064948 | 0.00052127 | 0.085244 | -56.6391 | 62.2284 | -61.6882 | -61.5417 | 51.3611 | 24.028 | 8.9493 | 8.963 | 62.2238 | -61.6928 | -0.3067 | 0.054932 | 4.7424 | -0.16022 | -10.8124 | -0.31128 | 0.050354 | 5.0491 | 70.3308 | 70.3445 | 112.7426 | 123.6099 | 4.7424 | 123.6053 | 85.4095 | -0.31128 | 123.6099 | 4.7424 | 85.4095 | 112.7426 | 123.6053 | -123.8617 | -123.8663
5815.7188 | 123.7106 | -61.3678 | 62.178 | -0.09285 | 0.023501 | 0.017686 | 0.022787 | 0.063239 | 0.00030767 | 0.085671 | -56.6391 | 62.2238 | -61.6928 | -61.5372 | 51.3519 | 24.0921 | 8.9539 | 8.9859 | 62.2284 | -61.6928 | -0.32501 | 0.045776 | 4.7287 | -0.16937 | -10.8261 | -0.32501 | 0.050354 | 5.0537 | 70.3217 | 70.3537 | 112.7197 | 123.5916 | 4.7287 | 123.5962 | 85.4599 | -0.32501 | 123.5916 | 4.7287 | 85.4599 | 112.7197 | 123.5962 | -123.8709 | -123.8709
5816.7188 | 123.7289 | -61.3541 | 62.1918 | -0.17677 | 0.023287 | 0.019822 | 0.019156 | 0.064093 | -0.00033333 | 0.085885 | -56.6345 | 62.2238 | -61.6837 | -61.5234 | 51.3794 | 23.9777 | 8.9905 | 9.0363 | 62.2284 | -61.6837 | -0.32959 | 0.032044 | 4.7195 | -0.16937 | -10.8124 | -0.32959 | 0.036622 | 5.0491 | 70.3445 | 70.3903 | 112.7335 | 123.5779 | 4.7195 | 123.5825 | 85.3317 | -0.32959 | 123.5779 | 4.7195 | 85.3317 | 112.7335 | 123.5825 | -123.8754 | -123.8754
5817.7188 | 123.6694 | -61.4136 | 62.1643 | -1.7561 | 0.024142 | 0.016831 | 0.020651 | 0.063025 | 0.0026575 | 0.085885 | -56.7764 | 62.2284 | -61.6837 | -61.6516 | 51.2924 | 23.9685 | 9.0088 | 8.9493 | 62.233 | -61.7432 | -0.27008 | 0.064087 | 4.6371 | -0.23804 | -10.8719 | -0.32959 | 0.068664 | 4.9072 | 70.4224 | 70.3629 | 112.706 | 123.642 | 4.6371 | 123.6465 | 85.3821 | -0.32959 | 123.642 | 4.6371 | 85.3821 | 112.706 | 123.6465 | -123.848 | -123.9075
5818.7188 | 123.7289 | -61.3632 | 62.178 | -0.031814 | 0.02286 | 0.019395 | 0.020651 | 0.06388 | 0.00030767 | 0.085671 | -56.6254 | 62.2284 | -61.6791 | -61.5372 | 51.3336 | 24.1516 | 8.67 | 8.9539 | 62.1872 | -61.702 | -0.31586 | 0.050354 | 4.7379 | -0.17395 | -10.8444 | -0.33875 | 0.009155 | 5.0537 | 70.0333 | 70.3171 | 112.6968 | 123.5916 | 4.7379 | 123.5504 | 85.5148 | -0.33875 | 123.5916 | 4.7379 | 85.5148 | 112.6968 | 123.5504 | -123.8571 | -123.88
5819.7188 | 123.6923 | -61.3358 | 62.1826 | -0.13863 | 0.021364 | 0.017472 | 0.017874 | 0.062812 | 0.0018031 | 0.086099 | -56.6574 | 62.2421 | -61.6928 | -61.5417 | 51.3245 | 24.0372 | 9.0042 | 8.9676 | 62.265 | -61.6974 | -0.35706 | 0.059509 | 4.6783 | -0.20599 | -10.8582 | -0.36163 | 0.082398 | 5.0354 | 70.34 | 70.3033 | 112.6602 | 123.5779 | 4.6783 | 123.6008 | 85.3729 | -0.36163 | 123.5779 | 4.6783 | 85.3729 | 112.6602 | 123.6008 | -123.8754 | -123.88
5820.7188 | 123.6877 | -61.3632 | 62.1918 | -0.1844 | 0.02051 | 0.019822 | 0.016806 | 0.063452 | 0.0011621 | 0.086312 | -56.6849 | 62.233 | -61.6791 | -61.5601 | 51.3107 | 24.0601 | 9.0363 | 8.9813 | 62.2513 | -61.6928 | -0.31586 | 0.041199 | 4.6783 | -0.19684 | -10.881 | -0.32959 | 0.05951 | 4.9942 | 70.3995 | 70.3445 | 112.6739 | 123.5962 | 4.6783 | 123.6145 | 85.4233 | -0.32959 | 123.5962 | 4.6783 | 85.4233 | 112.6739 | 123.6145 | -123.8708 | -123.8846
5821.7188 | 123.7152 | -61.3678 | 62.1964 | -0.16151 | 0.022646 | 0.01555 | 0.019583 | 0.061957 | 0.0011621 | 0.085244 | -56.6208 | 62.2101 | -61.6837 | -61.528 | 51.3199 | 24.0555 | 9.0134 | 9.0363 | 62.2192 | -61.6745 | -0.31586 | 0.013733 | 4.747 | -0.16022 | -10.8765 | -0.3067 | 0.022888 | 5.0629 | 70.3812 | 70.4041 | 112.6877 | 123.5779 | 4.747 | 123.587 | 85.4233 | -0.3067 | 123.5779 | 4.747 | 85.4233 | 112.6877 | 123.587 | -123.88 | -123.8709
5822.7188 | 123.7244 | -61.3861 | 62.1872 | 0.19707 | 0.023073 | 0.014909 | 0.024923 | 0.06388 | -0.0022559 | 0.086312 | -56.7169 | 62.2101 | -61.7065 | -61.4594 | 51.1459 | 23.9822 | 9.1919 | 8.9081 | 62.2467 | -61.7157 | -0.32044 | 0.022888 | 4.6692 | -0.073243 | -11.0413 | -0.32959 | 0.059509 | 4.9896 | 70.578 | 70.2942 | 112.532 | 123.5962 | 4.6692 | 123.6328 | 85.3683 | -0.32959 | 123.5962 | 4.6692 | 85.3683 | 112.532 | 123.6328 | -123.8937 | -123.9029
5823.7188 | 123.7061 | -61.3586 | 62.1872 | -0.1844 | 0.022005 | 0.020249 | 0.01766 | 0.060889 | -0.00054693 | 0.083962 | -56.6528 | 62.2147 | -61.6928 | -61.5417 | 51.2924 | 24.0738 | 9.1049 | 9.0225 | 62.2375 | -61.7065 | -0.33417 | 0.027466 | 4.7058 | -0.1831 | -10.8948 | -0.3479 | 0.050354 | 5.04 | 70.4636 | 70.3812 | 112.6511 | 123.5733 | 4.7058 | 123.5962 | 85.4324 | -0.3479 | 123.5733 | 4.7058 | 85.4324 | 112.6511 | 123.5962 | -123.88 | -123.8937
5824.7188 | 123.7335 | -61.3586 | 62.1689 | -0.077591 | 0.022219 | 0.016618 | 0.018301 | 0.062171 | 0.0013757 | 0.085885 | -56.5979 | 62.2238 | -61.6928 | -61.5189 | 51.2924 | 24.0784 | 9.0363 | 9.0408 | 62.2147 | -61.6653 | -0.33417 | 0.054932 | 4.7607 | -0.16022 | -10.8765 | -0.3067 | 0.045777 | 5.0949 | 70.3949 | 70.3995 | 112.6511 | 123.5825 | 4.7607 | 123.5733 | 85.437 | -0.3067 | 123.5825 | 4.7607 | 85.437 | 112.6511 | 123.5733 | -123.8617 | -123.8342
5825.7188 | 123.7015 | -61.3495 | 62.1643 | -0.21492 | 0.021578 | 0.015336 | 0.019156 | 0.063025 | -0.00033333 | 0.083749 | -56.6254 | 62.233 | -61.7111 | -61.5326 | 51.3062 | 24.1241 | 9.0637 | 9.0042 | 62.2238 | -61.6653 | -0.36163 | 0.068664 | 4.7241 | -0.18311 | -10.8582 | -0.31586 | 0.059509 | 5.0858 | 70.4132 | 70.3537 | 112.6556 | 123.5825 | 4.7241 | 123.5733 | 85.4736 | -0.31586 | 123.5825 | 4.7241 | 85.4736 | 112.6556 | 123.5733 | -123.8754 | -123.8297
5826.7188 | 123.6649 | -61.377 | 62.1964 | 0.013962 | 0.023928 | 0.015977 | 0.015951 | 0.05918 | 0.00073487 | 0.085244 | -56.6711 | 62.2559 | -61.6928 | -61.5784 | 51.2558 | 24.1196 | 9.0958 | 8.9676 | 62.265 | -61.6882 | -0.31586 | 0.059509 | 4.7058 | -0.20142 | -10.9406 | -0.31128 | 0.068665 | 5.0217 | 70.4727 | 70.3445 | 112.6328 | 123.6328 | 4.7058 | 123.642 | 85.4965 | -0.31128 | 123.6328 | 4.7058 | 85.4965 | 112.6328 | 123.642 | -123.8892 | -123.8846
5827.7188 | 123.7106 | -61.3815 | 62.2147 | -0.19203 | 0.022005 | 0.015336 | 0.018942 | 0.06388 | 0.00073487 | 0.084603 | -56.6528 | 62.2513 | -61.6791 | -61.5646 | 51.2604 | 24.1745 | 9.1003 | 9.0042 | 62.2284 | -61.6745 | -0.29755 | 0.036621 | 4.7287 | -0.1831 | -10.9543 | -0.29297 | 0.013733 | 5.0262 | 70.4819 | 70.3857 | 112.6419 | 123.6328 | 4.7287 | 123.6099 | 85.556 | -0.29297 | 123.6328 | 4.7287 | 85.556 | 112.6419 | 123.6099 | -123.8937 | -123.8892
5828.7188 | 123.7106 | -61.3907 | 62.2055 | -0.23018 | 0.022646 | 0.015122 | 0.019156 | 0.062384 | 0.00094847 | 0.086526 | -56.662 | 62.2147 | -61.6974 | -61.5692 | 51.297 | 24.1196 | 9.1187 | 9.0363 | 62.233 | -61.6837 | -0.3067 | 0.009156 | 4.7287 | -0.17853 | -10.9085 | -0.29297 | 0.027466 | 5.0354 | 70.5093 | 70.4269 | 112.6877 | 123.6053 | 4.7287 | 123.6237 | 85.5103 | -0.29297 | 123.6053 | 4.7287 | 85.5103 | 112.6877 | 123.6237 | -123.9029 | -123.8892
5829.7188 | 123.6877 | -61.3678 | 62.2055 | -0.16914 | 0.022433 | 0.015122 | 0.018087 | 0.060462 | 0.0018031 | 0.087167 | -56.6757 | 62.2009 | -61.6745 | -61.5692 | 51.3062 | 24.1516 | 9.0958 | 8.963 | 62.2421 | -61.6791 | -0.3067 | -0.004577 | 4.6921 | -0.20142 | -10.8994 | -0.31128 | 0.036621 | 4.9988 | 70.4636 | 70.3308 | 112.6739 | 123.5687 | 4.6921 | 123.6099 | 85.5194 | -0.31128 | 123.5687 | 4.6921 | 85.5194 | 112.6739 | 123.6099 | -123.88 | -123.8846
5830.7188 | 123.6832 | -61.3586 | 62.2055 | -1.0694 | 0.020937 | 0.019395 | 0.015524 | 0.062171 | 0.0028711 | 0.086953 | -56.7123 | 62.2055 | -61.7065 | -61.5692 | 51.2512 | 24.0509 | 9.0591 | 8.9676 | 62.265 | -61.647 | -0.3479 | 0 | 4.6463 | -0.21057 | -10.9543 | -0.28839 | 0.05951 | 4.9942 | 70.4178 | 70.3262 | 112.6099 | 123.5641 | 4.6463 | 123.6237 | 85.4095 | -0.28839 | 123.5641 | 4.6463 | 85.4095 | 112.6099 | 123.6237 | -123.912 | -123.8525
5831.7188 | 123.6832 | -61.3586 | 62.1918 | -0.19203 | 0.022646 | 0.014695 | 0.017447 | 0.060034 | -0.00097413 | 0.086739 | -56.6254 | 62.2238 | -61.6745 | -61.5417 | 51.21 | 24.0234 | 9.0546 | 9.0088 | 62.233 | -61.6974 | -0.31586 | 0.032044 | 4.7333 | -0.1831 | -10.9817 | -0.33874 | 0.041199 | 5.0491 | 70.4132 | 70.3674 | 112.5687 | 123.5825 | 4.7333 | 123.5916 | 85.3821 | -0.33874 | 123.5825 | 4.7333 | 85.3821 | 112.5687 | 123.5916 | -123.8663 | -123.8892
5832.7188 | 123.6877 | -61.3586 | 62.178 | -0.024185 | 0.021792 | 0.023026 | 0.021719 | 0.061957 | 0.00094847 | 0.086312 | -56.6208 | 62.2238 | -61.6974 | -61.5463 | 51.2604 | 24.0326 | 8.9996 | 8.9996 | 62.2192 | -61.6974 | -0.33874 | 0.045776 | 4.7379 | -0.18768 | -10.9177 | -0.33874 | 0.041198 | 5.0766 | 70.3583 | 70.3583 | 112.619 | 123.5825 | 4.7379 | 123.5779 | 85.3912 | -0.33874 | 123.5825 | 4.7379 | 85.3912 | 112.619 | 123.5779 | -123.8754 | -123.8754
5833.7188 | 123.6694 | -61.3815 | 62.1964 | -0.27596 | 0.02051 | 0.017899 | 0.016806 | 0.060462 | 0.0015893 | 0.085244 | -56.6483 | 62.1918 | -61.6928 | -61.5646 | 51.2329 | 24.0097 | 9.05 | 8.9905 | 62.2375 | -61.6745 | -0.31128 | -0.004578 | 4.7333 | -0.1831 | -10.9634 | -0.29297 | 0.041199 | 5.0446 | 70.4315 | 70.372 | 112.6144 | 123.5733 | 4.7333 | 123.6191 | 85.3912 | -0.29297 | 123.5733 | 4.7333 | 85.3912 | 112.6144 | 123.6191 | -123.8892 | -123.8709
5834.7188 | 123.674 | -61.3907 | 62.2055 | -0.28358 | 0.020937 | 0.017045 | 0.015738 | 0.06153 | -0.00033333 | 0.086099 | -56.6345 | 62.2101 | -61.6608 | -61.5234 | 51.2695 | 24.0326 | 9.0775 | 9.0042 | 62.2421 | -61.6608 | -0.27008 | 0.004578 | 4.7562 | -0.13275 | -10.936 | -0.27008 | 0.036621 | 5.0262 | 70.4681 | 70.3949 | 112.6602 | 123.6008 | 4.7562 | 123.6328 | 85.4233 | -0.27008 | 123.6008 | 4.7562 | 85.4233 | 112.6602 | 123.6328 | -123.8663 | -123.8663
5835.7188 | 123.6969 | -61.3541 | 62.2009 | -0.2607 | 0.022219 | 0.018754 | 0.017019 | 0.059821 | -0.0014013 | 0.086953 | -56.662 | 62.1964 | -61.6974 | -61.4777 | 51.0498 | 23.8998 | 9.2011 | 8.963 | 62.2147 | -61.6928 | -0.34332 | -0.004578 | 4.6921 | -0.1236 | -11.1511 | -0.33875 | 0.013733 | 5.0354 | 70.5551 | 70.3171 | 112.4039 | 123.5504 | 4.6921 | 123.5687 | 85.2539 | -0.33875 | 123.5504 | 4.6921 | 85.2539 | 112.4039 | 123.5687 | -123.8983 | -123.8937
5836.7188 | 123.6786 | -61.3541 | 62.2101 | -0.19966 | 0.022433 | 0.016191 | 0.017019 | 0.058539 | -0.00076053 | 0.087594 | -56.6574 | 62.2055 | -61.7386 | -61.5692 | 51.2375 | 24.0692 | 9.1599 | 9.0546 | 62.2238 | -61.6837 | -0.38452 | -0.004578 | 4.6967 | -0.21515 | -10.9726 | -0.32959 | 0.013733 | 5.0812 | 70.5139 | 70.4086 | 112.5916 | 123.5596 | 4.6967 | 123.5779 | 85.4233 | -0.32959 | 123.5596 | 4.6967 | 85.4233 | 112.5916 | 123.5779 | -123.9487 | -123.8937
5837.7188 | 123.7061 | -61.3724 | 62.1597 | -0.062332 | 0.021151 | 0.021104 | 0.023428 | 0.064093 | 0.0011621 | 0.085458 | -56.5842 | 62.2192 | -61.6745 | -61.5372 | 51.2283 | 24.0646 | 9.0912 | 9.0408 | 62.2238 | -61.6928 | -0.30213 | 0.059509 | 4.7882 | -0.1648 | -10.9314 | -0.32044 | 0.064087 | 5.0903 | 70.4636 | 70.4132 | 112.6007 | 123.5916 | 4.7882 | 123.5962 | 85.437 | -0.32044 | 123.5916 | 4.7882 | 85.437 | 112.6007 | 123.5962 | -123.8342 | -123.8525
5838.7188 | 123.6465 | -61.3815 | 62.2101 | -0.23781 | 0.022219 | 0.013627 | 0.018301 | 0.059394 | 0.00094847 | 0.085671 | -56.5704 | 62.2421 | -61.702 | -61.5921 | 51.2466 | 24.0738 | 9.0363 | 9.0134 | 62.2375 | -61.6882 | -0.32043 | 0.032043 | 4.8111 | -0.21057 | -10.9634 | -0.3067 | 0.027466 | 5.1315 | 70.4178 | 70.3949 | 112.6282 | 123.6237 | 4.8111 | 123.6191 | 85.4553 | -0.3067 | 123.6237 | 4.8111 | 85.4553 | 112.6282 | 123.6191 | -123.912 | -123.8983
5839.7188 | 123.6969 | -61.3632 | 62.1918 | -0.29121 | 0.019442 | 0.020249 | 0.017447 | 0.060462 | -0.0016149 | 0.085244 | -56.6666 | 62.1918 | -61.6837 | -61.5555 | 51.1047 | 24.1241 | 9.3613 | 8.8165 | 62.265 | -61.6287 | -0.32044 | 0 | 4.6967 | -0.19226 | -11.087 | -0.2655 | 0.073243 | 5.0171 | 70.7245 | 70.1797 | 112.468 | 123.555 | 4.6967 | 123.6282 | 85.4874 | -0.2655 | 123.555 | 4.6967 | 85.4874 | 112.468 | 123.6282 | -123.8754 | -123.8205
5840.7344 | 123.7015 | -61.3998 | 62.1597 | 0.16655 | 0.025423 | 0.019181 | 0.025137 | 0.061743 | -0.0014013 | 0.086526 | -56.6666 | 62.233 | -61.7386 | -61.5692 | 51.0956 | 24.0097 | 9.0134 | 8.8486 | 62.2009 | -61.7203 | -0.33874 | 0.073242 | 4.7333 | -0.16937 | -11.0641 | -0.32043 | 0.041199 | 5.072 | 70.4132 | 70.2484 | 112.4954 | 123.6328 | 4.7333 | 123.6008 | 85.4095 | -0.32043 | 123.6328 | 4.7333 | 85.4095 | 112.4954 | 123.6008 | -123.8983 | -123.88
5841.7188 | 123.7656 | -61.322 | 62.1735 | -0.19203 | 0.020083 | 0.016191 | 0.014456 | 0.057685 | -0.00011953 | 0.084817 | -56.5704 | 62.1368 | -61.6699 | -61.4914 | 51.2878 | 24.2249 | 8.9996 | 9.1187 | 62.1918 | -61.6516 | -0.3479 | -0.036621 | 4.7516 | -0.16937 | -10.8856 | -0.32959 | 0.01831 | 5.0995 | 70.3217 | 70.4407 | 112.6099 | 123.4589 | 4.7516 | 123.5138 | 85.5469 | -0.32959 | 123.4589 | 4.7516 | 85.5469 | 112.6099 | 123.5138 | -123.8434 | -123.8251
5842.7344 | 123.7061 | -61.3586 | 62.1597 | 1.6848 | 0.022646 | 0.018968 | 0.021933 | 0.061316 | 0.00030767 | 0.085031 | -56.4423 | 62.2009 | -61.7065 | -61.5143 | 51.2329 | 24.1287 | 9.0729 | 9.0454 | 62.1872 | -61.6791 | -0.3479 | 0.041199 | 4.9164 | -0.15564 | -10.9268 | -0.32043 | 0.027466 | 5.2643 | 70.4315 | 70.4041 | 112.5916 | 123.5596 | 4.9164 | 123.5458 | 85.4874 | -0.32043 | 123.5596 | 4.9164 | 85.4874 | 112.5916 | 123.5458 | -123.8663 | -123.8388
5843.7188 | 123.7381 | -61.3449 | 62.1918 | -0.2607 | 0.021151 | 0.0132 | 0.013388 | 0.059607 | -0.00011953 | 0.085031 | -56.5842 | 62.1323 | -61.6516 | -61.5143 | 51.2741 | 24.2249 | 9.0637 | 9.1187 | 62.2101 | -61.6379 | -0.3067 | -0.059509 | 4.7607 | -0.16937 | -10.9177 | -0.29297 | 0.018311 | 5.0674 | 70.4086 | 70.4636 | 112.619 | 123.4772 | 4.7607 | 123.555 | 85.5698 | -0.29297 | 123.4772 | 4.7607 | 85.5698 | 112.619 | 123.555 | -123.8434 | -123.8297
5844.7188 | 123.7518 | -61.3358 | 62.1597 | -0.2607 | 0.017092 | 0.013413 | 0.018087 | 0.059607 | -0.0020421 | 0.084817 | -56.575 | 62.1506 | -61.6653 | -61.4868 | 51.2833 | 24.1837 | 9.082 | 9.1873 | 62.1689 | -61.6241 | -0.32959 | -0.009155 | 4.7607 | -0.15106 | -10.8765 | -0.28839 | 0.009155 | 5.0903 | 70.4178 | 70.5231 | 112.619 | 123.4863 | 4.7607 | 123.5046 | 85.5194 | -0.28839 | 123.4863 | 4.7607 | 85.5194 | 112.619 | 123.5046 | -123.8251 | -123.7839
5845.7344 | 123.761 | -61.3586 | 62.1277 | 0.2047 | 0.02286 | 0.015336 | 0.022146 | 0.060675 | 0.0020167 | 0.086953 | -56.6071 | 62.1643 | -61.7065 | -61.5646 | 51.1917 | 24.1287 | 9.082 | 9.0729 | 62.1506 | -61.6882 | -0.3479 | 0.036621 | 4.7516 | -0.20599 | -10.936 | -0.32959 | 0.022888 | 5.0995 | 70.4407 | 70.4315 | 112.5504 | 123.523 | 4.7516 | 123.5092 | 85.4874 | -0.32959 | 123.523 | 4.7516 | 85.4874 | 112.5504 | 123.5092 | -123.8342 | -123.8159
5846.7188 | 123.7381 | -61.322 | 62.1689 | -0.2607 | 0.021792 | 0.013627 | 0.014456 | 0.058966 | 0.00052127 | 0.085458 | -56.5796 | 62.1597 | -61.6974 | -61.5051 | 51.2604 | 24.1287 | 9.082 | 9.169 | 62.2009 | -61.615 | -0.37537 | -0.009155 | 4.7424 | -0.18311 | -10.9085 | -0.29297 | 0.032044 | 5.1178 | 70.4041 | 70.491 | 112.5824 | 123.4818 | 4.7424 | 123.5229 | 85.4507 | -0.29297 | 123.4818 | 4.7424 | 85.4507 | 112.5824 | 123.5229 | -123.8663 | -123.7839
5847.7188 | 123.793 | -61.3037 | 62.146 | -0.20729 | 0.019656 | 0.011491 | 0.013388 | 0.057044 | 0.0037257 | 0.086739 | -56.2546 | 62.1735 | -61.6379 | -61.4639 | 51.3474 | 24.1928 | 8.8989 | 9.1919 | 62.1597 | -61.6104 | -0.33417 | 0.027466 | 5.0491 | -0.16022 | -10.7986 | -0.3067 | 0.013733 | 5.3833 | 70.2026 | 70.4956 | 112.6511 | 123.4772 | 5.0491 | 123.4634 | 85.4965 | -0.3067 | 123.4772 | 5.0491 | 85.4965 | 112.6511 | 123.4634 | -123.7839 | -123.7564
5848.7188 | 123.8113 | -61.3266 | 62.1552 | -0.17677 | 0.023714 | 0.017259 | 0.016378 | 0.058325 | 0.00030767 | 0.085458 | -56.5384 | 62.0956 | -61.647 | -61.441 | 51.2787 | 24.1608 | 9.5078 | 9.3155 | 62.1872 | -61.5738 | -0.32043 | -0.059509 | 4.7882 | -0.11444 | -10.8765 | -0.24719 | 0.032044 | 5.1086 | 70.8344 | 70.6421 | 112.6053 | 123.4222 | 4.7882 | 123.5138 | 85.4874 | -0.24719 | 123.4222 | 4.7882 | 85.4874 | 112.6053 | 123.5138 | -123.8022 | -123.7289
5849.7188 | 123.7839 | -61.3083 | 62.1735 | -0.3904 | 0.017092 | 0.017472 | 0.016806 | 0.058539 | -0.00054693 | 0.085458 | -56.5521 | 62.1094 | -61.6379 | -61.4594 | 51.2787 | 24.2432 | 8.9401 | 9.1507 | 62.1597 | -61.6104 | -0.32959 | -0.064087 | 4.7562 | -0.15106 | -10.8948 | -0.30212 | -0.013733 | 5.0858 | 70.2484 | 70.459 | 112.587 | 123.4177 | 4.7562 | 123.468 | 85.5515 | -0.30212 | 123.4177 | 4.7562 | 85.5515 | 112.587 | 123.468 | -123.8113 | -123.7839
5850.7344 | 123.6832 | -61.3586 | 62.1597 | -0.077591 | 0.025423 | 0.020036 | 0.02471 | 0.056617 | -0.0014013 | 0.08439 | -56.543 | 62.2284 | -61.6745 | -61.528 | 51.2146 | 24.0921 | 9.0363 | 9.0454 | 62.2055 | -61.6791 | -0.31586 | 0.068665 | 4.8157 | -0.16937 | -10.9451 | -0.32043 | 0.045776 | 5.1315 | 70.3949 | 70.4041 | 112.5732 | 123.587 | 4.8157 | 123.5641 | 85.4507 | -0.32043 | 123.587 | 4.8157 | 85.4507 | 112.5732 | 123.5641 | -123.8342 | -123.8388
5851.7188 | 123.7473 | -61.3083 | 62.1826 | -0.20729 | 0.021151 | 0.016191 | 0.017447 | 0.057685 | -0.00097413 | 0.086739 | -56.5475 | 62.1414 | -61.6562 | -61.4639 | 51.2512 | 24.1562 | 9.0088 | 9.1599 | 62.2009 | -61.6196 | -0.3479 | -0.041199 | 4.7607 | -0.15564 | -10.9314 | -0.31128 | 0.018311 | 5.1086 | 70.3171 | 70.4681 | 112.5595 | 123.4497 | 4.7607 | 123.5092 | 85.4645 | -0.31128 | 123.4497 | 4.7607 | 85.4645 | 112.5595 | 123.5092 | -123.8388 | -123.8022
5852.7344 | 123.7106 | -61.3678 | 62.1872 | -0.016556 | 0.024142 | 0.019608 | 0.023214 | 0.060889 | -0.0014013 | 0.086312 | -56.6757 | 62.1689 | -61.702 | -61.5051 | 51.2009 | 24.1058 | 9.0729 | 9.0958 | 62.1689 | -61.6791 | -0.33417 | -0.018311 | 4.6921 | -0.13733 | -10.9863 | -0.31128 | -0.018311 | 5.0262 | 70.4407 | 70.4636 | 112.5687 | 123.5367 | 4.6921 | 123.5367 | 85.4736 | -0.31128 | 123.5367 | 4.6921 | 85.4736 | 112.5687 | 123.5367 | -123.8892 | -123.8663
5853.7188 | 123.8022 | -61.3129 | 62.146 | -0.35225 | 0.020937 | 0.015977 | 0.015738 | 0.059821 | -0.00033333 | 0.086739 | -56.543 | 62.1185 | -61.6516 | -61.4639 | 51.2146 | 24.1745 | 8.9218 | 9.1782 | 62.1506 | -61.6241 | -0.33875 | -0.027466 | 4.7699 | -0.15106 | -10.9314 | -0.31128 | 0.004578 | 5.1086 | 70.2347 | 70.491 | 112.5275 | 123.4314 | 4.7699 | 123.4634 | 85.4874 | -0.31128 | 123.4314 | 4.7699 | 85.4874 | 112.5275 | 123.4634 | -123.7976 | -123.7701
5854.7188 | 123.8068 | -61.3037 | 62.1689 | -0.062332 | 0.019228 | 0.015977 | 0.015097 | 0.059394 | 0.0015893 | 0.086312 | -56.5659 | 62.0911 | -61.647 | -61.4685 | 51.2558 | 24.2569 | 8.9081 | 9.1827 | 62.1414 | -61.6287 | -0.34332 | -0.07782 | 4.7379 | -0.16479 | -10.9131 | -0.32501 | -0.027466 | 5.0812 | 70.2118 | 70.4865 | 112.5595 | 123.3948 | 4.7379 | 123.4451 | 85.5606 | -0.32501 | 123.3948 | 4.7379 | 85.5606 | 112.5595 | 123.4451 | -123.8159 | -123.7976
5855.7344 | 123.7061 | -61.3724 | 62.178 | -0.047073 | 0.022005 | 0.020249 | 0.024069 | 0.058325 | -0.0014013 | 0.085671 | -56.543 | 62.1414 | -61.6837 | -61.5234 | 51.1139 | 24.0921 | 9.0775 | 9.1003 | 62.1826 | -61.6562 | -0.31128 | -0.036622 | 4.8294 | -0.15106 | -11.0641 | -0.28381 | 0.004577 | 5.1407 | 70.4498 | 70.4727 | 112.4863 | 123.5138 | 4.8294 | 123.555 | 85.4645 | -0.28381 | 123.5138 | 4.8294 | 85.4645 | 112.4863 | 123.555 | -123.8617 | -123.8342
5856.7188 | 123.8068 | -61.3358 | 62.146 | -0.1844 | 0.018374 | 0.018327 | 0.017874 | 0.063452 | 0.00073487 | 0.085671 | -56.5247 | 62.1002 | -61.6653 | -61.3953 | 51.2375 | 24.1058 | 9.0042 | 9.2148 | 62.146 | -61.6104 | -0.32959 | -0.045776 | 4.8111 | -0.05951 | -10.9085 | -0.27466 | 0 | 5.1407 | 70.34 | 70.5505 | 112.5732 | 123.436 | 4.8111 | 123.4818 | 85.4416 | -0.27466 | 123.436 | 4.8111 | 85.4416 | 112.5732 | 123.4818 | -123.8113 | -123.7564
5857.7188 | 123.7656 | -61.3312 | 62.1735 | -0.1844 | 0.022005 | 0.012773 | 0.018087 | 0.058753 | 0.00052127 | 0.086739 | -56.5109 | 62.0956 | -61.6516 | -61.4502 | 51.2283 | 24.2249 | 8.9905 | 9.2011 | 62.1552 | -61.6287 | -0.32043 | -0.07782 | 4.8203 | -0.11902 | -10.9451 | -0.29755 | -0.018311 | 5.1407 | 70.3217 | 70.5322 | 112.5595 | 123.4268 | 4.8203 | 123.4863 | 85.556 | -0.29755 | 123.4268 | 4.8203 | 85.556 | 112.5595 | 123.4863 | -123.8251 | -123.8022
5858.7188 | 123.7244 | -61.2991 | 62.1506 | -0.10811 | 0.019442 | 0.016191 | 0.014883 | 0.054908 | 0.0013757 | 0.085458 | -56.5201 | 62.0865 | -61.6745 | -61.4502 | 51.297 | 24.2752 | 8.8943 | 9.3109 | 62.1552 | -61.615 | -0.37537 | -0.064087 | 4.7791 | -0.15106 | -10.8536 | -0.31586 | 0.004577 | 5.1544 | 70.1935 | 70.61 | 112.5961 | 123.3856 | 4.7791 | 123.4543 | 85.5743 | -0.31586 | 123.3856 | 4.7791 | 85.5743 | 112.5961 | 123.4543 | -123.8251 | -123.7656
5859.7188 | 123.7793 | -61.3083 | 62.1597 | -0.1844 | 0.023073 | 0.013627 | 0.015524 | 0.057257 | -0.0011877 | 0.084176 | -56.5063 | 62.1277 | -61.6653 | -61.4685 | 51.2558 | 24.1928 | 8.9218 | 9.1965 | 62.1506 | -61.6104 | -0.35705 | -0.032043 | 4.8019 | -0.16022 | -10.9039 | -0.30212 | -0.009155 | 5.159 | 70.2301 | 70.5048 | 112.5641 | 123.436 | 4.8019 | 123.4589 | 85.5011 | -0.30212 | 123.436 | 4.8019 | 85.5011 | 112.5641 | 123.4589 | -123.8251 | -123.7701
5860.7188 | 123.7656 | -61.3312 | 62.1872 | -0.25307 | 0.019442 | 0.019822 | 0.013174 | 0.054908 | -0.00097413 | 0.084817 | -56.5018 | 62.1277 | -61.6241 | -61.4685 | 51.2558 | 24.2523 | 8.8943 | 9.1919 | 62.1368 | -61.6379 | -0.29297 | -0.059509 | 4.8294 | -0.13733 | -10.9314 | -0.3067 | -0.050354 | 5.1224 | 70.2255 | 70.5231 | 112.587 | 123.4589 | 4.8294 | 123.468 | 85.5835 | -0.3067 | 123.4589 | 4.8294 | 85.5835 | 112.587 | 123.468 | -123.8113 | -123.8251
5861.7188 | 123.8068 | -61.3083 | 62.1689 | -0.077591 | 0.02051 | 0.015763 | 0.015524 | 0.057471 | -0.00076053 | 0.083962 | -56.5201 | 62.0956 | -61.647 | -61.441 | 51.265 | 24.2203 | 8.8806 | 9.2194 | 62.1506 | -61.5967 | -0.33874 | -0.073242 | 4.7882 | -0.13275 | -10.9039 | -0.28839 | -0.01831 | 5.127 | 70.1889 | 70.5276 | 112.5732 | 123.4039 | 4.7882 | 123.4589 | 85.5286 | -0.28839 | 123.4039 | 4.7882 | 85.5286 | 112.5732 | 123.4589 | -123.8159 | -123.7656
5862.7188 | 123.7518 | -61.3129 | 62.1826 | -0.1844 | 0.018587 | 0.016831 | 0.019156 | 0.057257 | 0.00094847 | 0.084176 | -56.5201 | 62.1323 | -61.6379 | -61.4731 | 51.2329 | 24.1745 | 8.9584 | 9.1644 | 62.1597 | -61.6608 | -0.32501 | -0.050354 | 4.7928 | -0.16022 | -10.9497 | -0.3479 | -0.022888 | 5.1178 | 70.2713 | 70.4773 | 112.5458 | 123.4451 | 4.7928 | 123.4726 | 85.4874 | -0.3479 | 123.4451 | 4.7928 | 85.4874 | 112.5458 | 123.4726 | -123.8205 | -123.8434
5863.7188 | 123.7976 | -61.3174 | 62.1552 | 2.6537 | 0.022219 | 0.013841 | 0.017019 | 0.056189 | 0.00094847 | 0.08439 | -56.4926 | 62.114 | -61.6974 | -61.4502 | 51.297 | 24.2203 | 8.8531 | 9.2194 | 62.1552 | -61.6013 | -0.37994 | -0.041198 | 4.8248 | -0.13275 | -10.8582 | -0.28381 | 0 | 5.2048 | 70.1706 | 70.5368 | 112.6144 | 123.4314 | 4.8248 | 123.4726 | 85.5377 | -0.28381 | 123.4314 | 4.8248 | 85.5377 | 112.6144 | 123.4726 | -123.8525 | -123.7564
5864.7188 | 123.7747 | -61.2991 | 62.1735 | -3.4879 | 0.020083 | 0.019395 | 0.017233 | 0.058325 | -0.0011877 | 0.086312 | -56.662 | 62.1231 | -61.6745 | -61.4685 | 51.2375 | 24.2203 | 8.8715 | 9.1827 | 62.1414 | -61.6104 | -0.37537 | -0.050354 | 4.6371 | -0.16937 | -10.936 | -0.31128 | -0.032044 | 5.0125 | 70.1706 | 70.4819 | 112.5366 | 123.4222 | 4.6371 | 123.4406 | 85.5194 | -0.31128 | 123.4222 | 4.6371 | 85.5194 | 112.5366 | 123.4406 | -123.848 | -123.7839
5865.7188 | 123.7839 | -61.322 | 62.1689 | -0.20729 | 0.019228 | 0.015977 | 0.015738 | 0.054267 | 0.0020167 | 0.085885 | -56.369 | 62.1643 | -61.6287 | -61.5097 | 51.3062 | 24.2889 | 8.8028 | 9.1827 | 62.1277 | -61.615 | -0.3067 | -0.004577 | 4.953 | -0.18768 | -10.8627 | -0.29297 | -0.041198 | 5.2597 | 70.1248 | 70.5048 | 112.6282 | 123.4863 | 4.953 | 123.4497 | 85.611 | -0.29297 | 123.4863 | 4.953 | 85.611 | 112.6282 | 123.4497 | -123.7976 | -123.7839
5866.7188 | 123.7427 | -61.3129 | 62.1689 | -0.19966 | 0.019656 | 0.01555 | 0.016378 | 0.057685 | -0.00097413 | 0.083535 | -56.5109 | 62.1277 | -61.6608 | -61.4456 | 51.2238 | 24.2157 | 8.9584 | 9.1324 | 62.1689 | -61.6013 | -0.3479 | -0.041198 | 4.8019 | -0.13275 | -10.9451 | -0.28839 | 0 | 5.1498 | 70.2713 | 70.4453 | 112.5366 | 123.4406 | 4.8019 | 123.4818 | 85.5286 | -0.28839 | 123.4406 | 4.8019 | 85.5286 | 112.5366 | 123.4818 | -123.8297 | -123.7701
5867.7188 | 123.7198 | -61.3632 | 62.2238 | -0.19203 | 0.023501 | 0.016831 | 0.023855 | 0.058966 | -0.00054693 | 0.085458 | -56.5659 | 62.233 | -61.6745 | -61.5097 | 51.1505 | 24.1058 | 9.0363 | 9.0225 | 62.2055 | -61.6653 | -0.31128 | 0.009155 | 4.7974 | -0.14648 | -11.0733 | -0.30212 | -0.018311 | 5.1086 | 70.3995 | 70.3857 | 112.5137 | 123.5962 | 4.7974 | 123.5687 | 85.4691 | -0.30212 | 123.5962 | 4.7974 | 85.4691 | 112.5137 | 123.5687 | -123.8983 | -123.8892
5868.7188 | 123.8251 | -61.3266 | 62.1597 | -0.21492 | 0.019228 | 0.019181 | 0.018515 | 0.062171 | 0.0028711 | 0.083962 | -56.4651 | 62.1048 | -61.6379 | -61.3953 | 51.1963 | 24.0601 | 8.8715 | 9.1507 | 62.1597 | -61.5829 | -0.31128 | -0.054932 | 4.8615 | -0.068665 | -10.9634 | -0.25635 | 0 | 5.1727 | 70.1981 | 70.4773 | 112.5229 | 123.4314 | 4.8615 | 123.4863 | 85.3867 | -0.25635 | 123.4314 | 4.8615 | 85.3867 | 112.5229 | 123.4863 | -123.7976 | -123.7427
5869.7188 | 123.793 | -61.3403 | 62.1277 | -0.17677 | 0.021151 | 0.016191 | 0.011038 | 0.057685 | 0.00094847 | 0.087808 | -56.4789 | 62.1048 | -61.6653 | -61.6013 | 51.3107 | 24.2294 | 8.6563 | 9.2011 | 62.1048 | -61.6058 | -0.32501 | -0.022889 | 4.8614 | -0.26093 | -10.817 | -0.2655 | -0.022889 | 5.1865 | 69.9966 | 70.5414 | 112.6511 | 123.4451 | 4.8614 | 123.4451 | 85.5698 | -0.2655 | 123.4451 | 4.8614 | 85.5698 | 112.6511 | 123.4451 | -123.793 | -123.7335
5870.7188 | 123.7701 | -61.3174 | 62.1872 | -0.20729 | 0.02286 | 0.019822 | 0.018301 | 0.056403 | 0.00094847 | 0.085885 | -56.4926 | 62.1231 | -61.6562 | -61.4548 | 51.2146 | 24.1287 | 8.9035 | 9.1232 | 62.1323 | -61.615 | -0.33874 | -0.064087 | 4.8248 | -0.13733 | -10.9726 | -0.29755 | -0.054932 | 5.1636 | 70.2209 | 70.4407 | 112.532 | 123.4406 | 4.8248 | 123.4497 | 85.4462 | -0.29755 | 123.4406 | 4.8248 | 85.4462 | 112.532 | 123.4497 | -123.8434 | -123.8022
5871.7188 | 123.7701 | -61.3083 | 62.178 | -0.12337 | 0.019656 | 0.023667 | 0.017874 | 0.058325 | -0.0024695 | 0.085671 | -56.488 | 62.1231 | -61.6745 | -61.4594 | 51.2009 | 24.115 | 8.9035 | 9.1278 | 62.1735 | -61.5875 | -0.36621 | -0.054932 | 4.8203 | -0.15106 | -10.9772 | -0.27923 | -0.004578 | 5.1865 | 70.2118 | 70.4361 | 112.5092 | 123.4314 | 4.8203 | 123.4818 | 85.4233 | -0.27923 | 123.4314 | 4.8203 | 85.4233 | 112.5092 | 123.4818 | -123.8525 | -123.7656
5872.7188 | 123.6923 | -61.3403 | 62.1872 | -0.10811 | 0.02521 | 0.018754 | 0.024496 | 0.061103 | -0.00097413 | 0.085885 | -56.4926 | 62.2375 | -61.6745 | -61.4822 | 51.1551 | 24.0784 | 8.9676 | 9.05 | 62.1826 | -61.6562 | -0.33417 | 0.050354 | 4.8477 | -0.14191 | -11.0321 | -0.31586 | -0.004578 | 5.1819 | 70.3079 | 70.3903 | 112.4954 | 123.5779 | 4.8477 | 123.5229 | 85.4187 | -0.31586 | 123.5779 | 4.8477 | 85.4187 | 112.4954 | 123.5229 | -123.8617 | -123.8434
5873.7188 | 123.6832 | -61.3449 | 62.2101 | -0.24544 | 0.021578 | 0.013841 | 0.017233 | 0.05918 | 0.00052127 | 0.085244 | -56.5247 | 62.178 | -61.6653 | -61.5051 | 51.1322 | 24.1058 | 9.0134 | 9.0546 | 62.2055 | -61.615 | -0.32043 | -0.032043 | 4.8203 | -0.16022 | -11.0779 | -0.27008 | -0.004578 | 5.1407 | 70.3583 | 70.3995 | 112.4771 | 123.523 | 4.8203 | 123.5504 | 85.4507 | -0.27008 | 123.523 | 4.8203 | 85.4507 | 112.4771 | 123.5504 | -123.8754 | -123.8251
5874.7188 | 123.6786 | -61.3449 | 62.2009 | -0.21492 | 0.021364 | 0.018754 | 0.020437 | 0.058325 | 0.0022303 | 0.086099 | -56.5659 | 62.1689 | -61.6653 | -61.496 | 50.9354 | 23.9914 | 9.1049 | 8.9676 | 62.2147 | -61.6928 | -0.32043 | -0.032044 | 4.7791 | -0.15106 | -11.2656 | -0.3479 | 0.013733 | 5.0995 | 70.4498 | 70.3125 | 112.2803 | 123.5138 | 4.7791 | 123.5596 | 85.3363 | -0.3479 | 123.5138 | 4.7791 | 85.3363 | 112.2803 | 123.5596 | -123.8663 | -123.8937
5875.7188 | 123.7701 | -61.2991 | 62.1689 | -0.23781 | 0.018587 | 0.015122 | 0.01766 | 0.060248 | 9.4068e-05 | 0.086953 | -56.488 | 62.146 | -61.647 | -61.4639 | 51.21 | 24.1974 | 8.9127 | 9.1187 | 62.1643 | -61.6241 | -0.3479 | -0.022888 | 4.8111 | -0.1648 | -10.9589 | -0.32501 | -0.004577 | 5.159 | 70.2118 | 70.4178 | 112.5092 | 123.4451 | 4.8111 | 123.4634 | 85.4965 | -0.32501 | 123.4451 | 4.8111 | 85.4965 | 112.5092 | 123.4634 | -123.8159 | -123.793
5876.7188 | 123.7793 | -61.3174 | 62.1643 | -0.19203 | 0.019442 | 0.014268 | 0.016592 | 0.059821 | -0.0011877 | 0.086312 | -56.4972 | 62.1414 | -61.647 | -61.4548 | 51.1826 | 24.1837 | 8.9127 | 9.1965 | 62.1597 | -61.6013 | -0.32959 | -0.022889 | 4.8203 | -0.13733 | -10.9818 | -0.28381 | -0.004578 | 5.1498 | 70.2301 | 70.5139 | 112.5 | 123.4589 | 4.8203 | 123.4772 | 85.5011 | -0.28381 | 123.4589 | 4.8203 | 85.5011 | 112.5 | 123.4772 | -123.8113 | -123.7656
5877.7188 | 123.7289 | -61.3449 | 62.178 | -0.15388 | 0.022433 | 0.02089 | 0.023214 | 0.056617 | -0.0014013 | 0.085671 | -56.488 | 62.2421 | -61.6745 | -61.4868 | 51.1551 | 24.1425 | 9.0408 | 9.1187 | 62.1597 | -61.6745 | -0.32959 | 0.064086 | 4.8569 | -0.14191 | -11.023 | -0.32959 | -0.018311 | 5.1865 | 70.3857 | 70.4636 | 112.5 | 123.587 | 4.8569 | 123.5046 | 85.4874 | -0.32959 | 123.587 | 4.8569 | 85.4874 | 112.5 | 123.5046 | -123.8525 | -123.8525
5878.7188 | 123.7518 | -61.3266 | 62.1826 | -0.25307 | 0.020296 | 0.017472 | 0.015738 | 0.058325 | 0.00094847 | 0.084603 | -56.4972 | 62.1414 | -61.6608 | -61.4731 | 51.1414 | 24.1379 | 9.1232 | 9.2377 | 62.1735 | -61.6379 | -0.33417 | -0.041199 | 4.8294 | -0.14648 | -11.0413 | -0.31128 | -0.009155 | 5.1636 | 70.4498 | 70.5643 | 112.468 | 123.468 | 4.8294 | 123.5001 | 85.4645 | -0.31128 | 123.468 | 4.8294 | 85.4645 | 112.468 | 123.5001 | -123.8434 | -123.8205
5879.7188 | 123.6649 | -61.3312 | 62.2513 | -0.2607 | 0.021578 | 0.020249 | 0.019369 | 0.05918 | -0.00033333 | 0.08738 | -56.5659 | 62.2055 | -61.6608 | -61.5509 | 51.0773 | 24.0234 | 9.2651 | 9.1278 | 62.2009 | -61.6516 | -0.32959 | -0.045777 | 4.7653 | -0.21973 | -11.174 | -0.32043 | -0.050354 | 5.0949 | 70.5963 | 70.459 | 112.4084 | 123.5367 | 4.7653 | 123.5321 | 85.3546 | -0.32043 | 123.5367 | 4.7653 | 85.3546 | 112.4084 | 123.5321 | -123.912 | -123.9029
5880.7188 | 123.6603 | -61.3403 | 62.2101 | -0.21492 | 0.023073 | 0.014268 | 0.017233 | 0.060034 | 0.00073487 | 0.085458 | -56.5475 | 62.1872 | -61.6699 | -61.5417 | 51.0818 | 24.0005 | 9.169 | 9.1141 | 62.2101 | -61.6562 | -0.32959 | -0.022888 | 4.7928 | -0.20142 | -11.1282 | -0.31586 | 0 | 5.1224 | 70.5093 | 70.4544 | 112.4222 | 123.5275 | 4.7928 | 123.5504 | 85.3409 | -0.31586 | 123.5275 | 4.7928 | 85.3409 | 112.4222 | 123.5504 | -123.88 | -123.8663
5881.7188 | 123.6603 | -61.3541 | 62.2192 | -0.28358 | 0.019656 | 0.012345 | 0.018087 | 0.057685 | 0.0013757 | 0.086739 | -56.5521 | 62.1872 | -61.6837 | -61.5692 | 51.1276 | 24.0921 | 9.1141 | 9.0866 | 62.2192 | -61.6425 | -0.32959 | -0.032043 | 4.8019 | -0.21515 | -11.0916 | -0.28839 | 0 | 5.1315 | 70.4681 | 70.4407 | 112.4817 | 123.5413 | 4.8019 | 123.5733 | 85.4462 | -0.28839 | 123.5413 | 4.8019 | 85.4462 | 112.4817 | 123.5733 | -123.9029 | -123.8617
5882.7188 | 123.7701 | -61.3174 | 62.1826 | -0.23018 | 0.022005 | 0.016404 | 0.016378 | 0.057471 | 0.00052127 | 0.084817 | -56.4835 | 62.1643 | -61.6516 | -61.4777 | 51.1688 | 24.1745 | 9.0546 | 9.2011 | 62.1689 | -61.6058 | -0.33417 | -0.01831 | 4.834 | -0.16022 | -11.0138 | -0.28839 | -0.013733 | 5.1682 | 70.372 | 70.5185 | 112.4863 | 123.4818 | 4.834 | 123.4863 | 85.4919 | -0.28839 | 123.4818 | 4.834 | 85.4919 | 112.4863 | 123.4863 | -123.8342 | -123.7885
5883.7188 | 123.674 | -61.3312 | 62.2101 | -0.24544 | 0.019869 | 0.017045 | 0.019369 | 0.059607 | 0.00052127 | 0.085885 | -56.5109 | 62.1689 | -61.6974 | -61.5463 | 51.0864 | 24.0189 | 9.1919 | 9.1278 | 62.2101 | -61.6516 | -0.36621 | -0.041199 | 4.8203 | -0.21515 | -11.1237 | -0.32043 | 0 | 5.1865 | 70.5231 | 70.459 | 112.4176 | 123.5001 | 4.8203 | 123.5413 | 85.35 | -0.32043 | 123.5001 | 4.8203 | 85.35 | 112.4176 | 123.5413 | -123.9075 | -123.8617
5884.7188 | 123.6694 | -61.3266 | 62.2009 | -0.25307 | 0.020724 | 0.020249 | 0.018301 | 0.05683 | 0.0022303 | 0.086953 | -56.5338 | 62.1872 | -61.6653 | -61.5417 | 51.0544 | 24.0189 | 9.2834 | 9.1278 | 62.1964 | -61.6608 | -0.33874 | -0.013733 | 4.7928 | -0.21515 | -11.1465 | -0.33417 | -0.004578 | 5.1315 | 70.61 | 70.4544 | 112.381 | 123.5138 | 4.7928 | 123.5229 | 85.3455 | -0.33417 | 123.5138 | 4.7928 | 85.3455 | 112.381 | 123.5229 | -123.8663 | -123.8617
5885.7188 | 123.7198 | -61.3358 | 62.2009 | -0.24544 | 0.019656 | 0.016618 | 0.019583 | 0.058539 | -0.0016149 | 0.086312 | -56.5155 | 62.1506 | -61.6608 | -61.5326 | 51.1093 | 24.0738 | 9.2377 | 9.1965 | 62.178 | -61.6287 | -0.32501 | -0.050354 | 4.8203 | -0.19684 | -11.0916 | -0.29297 | -0.022888 | 5.1453 | 70.5734 | 70.5322 | 112.4451 | 123.4863 | 4.8203 | 123.5138 | 85.4095 | -0.29297 | 123.4863 | 4.8203 | 85.4095 | 112.4451 | 123.5138 | -123.8617 | -123.8297
5886.7188 | 123.7061 | -61.3632 | 62.2421 | -0.29121 | 0.020724 | 0.017045 | 0.017447 | 0.057044 | -0.00054693 | 0.086526 | -56.5338 | 62.1964 | -61.6882 | -61.5417 | 51.0498 | 23.7442 | 9.3109 | 9.1644 | 62.2009 | -61.6516 | -0.32501 | -0.045776 | 4.8294 | -0.17853 | -11.1923 | -0.28839 | -0.041198 | 5.1544 | 70.6741 | 70.5276 | 112.413 | 123.5596 | 4.8294 | 123.5641 | 85.1074 | -0.28839 | 123.5596 | 4.8294 | 85.1074 | 112.413 | 123.5641 | -123.9304 | -123.8937
5887.7188 | 123.7152 | -61.3449 | 62.1414 | -0.069961 | 0.021578 | 0.017899 | 0.024496 | 0.062384 | -0.00054693 | 0.085244 | -56.488 | 62.2192 | -61.6837 | -61.4914 | 51.059 | 23.6847 | 9.2285 | 9.1919 | 62.1826 | -61.6791 | -0.33875 | 0.07782 | 4.8569 | -0.14648 | -11.0825 | -0.33417 | 0.041199 | 5.1956 | 70.5734 | 70.5368 | 112.4039 | 123.5641 | 4.8569 | 123.5275 | 85.0296 | -0.33417 | 123.5641 | 4.8569 | 85.0296 | 112.4039 | 123.5275 | -123.8251 | -123.8205
5888.7188 | 123.6832 | -61.3358 | 62.2192 | -0.26833 | 0.021364 | 0.022813 | 0.019583 | 0.061103 | -0.0014013 | 0.085244 | -56.5109 | 62.178 | -61.6516 | -61.5189 | 51.1002 | 23.7717 | 9.1141 | 9.1049 | 62.2055 | -61.647 | -0.31586 | -0.041198 | 4.8248 | -0.18311 | -11.1191 | -0.31128 | -0.013733 | 5.1407 | 70.4498 | 70.4407 | 112.4359 | 123.5138 | 4.8248 | 123.5413 | 85.1074 | -0.31128 | 123.5138 | 4.8248 | 85.1074 | 112.4359 | 123.5413 | -123.8708 | -123.8663
5889.7188 | 123.7747 | -61.3129 | 62.1506 | -0.17677 | 0.020083 | 0.01854 | 0.014669 | 0.059607 | 0.0028711 | 0.08738 | -56.456 | 62.1277 | -61.6425 | -61.4548 | 51.1368 | 23.8998 | 9.0317 | 9.2926 | 62.1735 | -61.6104 | -0.32959 | -0.022888 | 4.8569 | -0.14191 | -11.0138 | -0.29755 | 0.022888 | 5.1865 | 70.3445 | 70.6055 | 112.4496 | 123.4406 | 4.8569 | 123.4863 | 85.2127 | -0.29755 | 123.4406 | 4.8569 | 85.2127 | 112.4496 | 123.4863 | -123.793 | -123.761
5890.7188 | 123.7381 | -61.3403 | 62.1918 | -0.26833 | 0.019869 | 0.01555 | 0.01766 | 0.059607 | -0.00011953 | 0.085885 | -56.4743 | 62.1414 | -61.6608 | -61.4685 | 51.1093 | 23.8266 | 9.1324 | 9.2331 | 62.1689 | -61.6196 | -0.32044 | -0.050354 | 4.866 | -0.12817 | -11.0825 | -0.27924 | -0.022888 | 5.1865 | 70.4727 | 70.5734 | 112.4496 | 123.4818 | 4.866 | 123.5092 | 85.1669 | -0.27924 | 123.4818 | 4.866 | 85.1669 | 112.4496 | 123.5092 | -123.8525 | -123.8113
5891.7188 | 123.7427 | -61.322 | 62.1735 | -0.16151 | 0.020724 | 0.014054 | 0.017019 | 0.058539 | -0.0020421 | 0.085031 | -56.4606 | 62.1277 | -61.6379 | -61.4685 | 51.1551 | 23.9319 | 9.0271 | 9.2194 | 62.1643 | -61.5875 | -0.31586 | -0.045776 | 4.8614 | -0.14648 | -11.0184 | -0.2655 | -0.009155 | 5.1773 | 70.3491 | 70.5414 | 112.4771 | 123.4497 | 4.8614 | 123.4863 | 85.2539 | -0.2655 | 123.4497 | 4.8614 | 85.2539 | 112.4771 | 123.4863 | -123.8113 | -123.761
5892.7188 | 123.7701 | -61.3266 | 62.1735 | 0.15129 | 0.020296 | 0.017899 | 0.016806 | 0.057898 | -0.0022559 | 0.086739 | -56.4194 | 62.1185 | -61.6379 | -61.4502 | 51.1185 | 23.8449 | 8.9676 | 9.2514 | 62.1414 | -61.6196 | -0.31128 | -0.054932 | 4.9072 | -0.1236 | -11.055 | -0.29297 | -0.032044 | 5.2185 | 70.2942 | 70.578 | 112.4451 | 123.4451 | 4.9072 | 123.468 | 85.1715 | -0.29297 | 123.4451 | 4.9072 | 85.1715 | 112.4451 | 123.468 | -123.8113 | -123.793
5893.7188 | 123.761 | -61.2946 | 62.1689 | -0.19966 | 0.019656 | 0.016618 | 0.018515 | 0.056617 | -0.0011877 | 0.086739 | -56.4514 | 62.1414 | -61.6287 | -61.4777 | 51.0773 | 23.909 | 8.9951 | 9.2514 | 62.1735 | -61.6104 | -0.33417 | -0.027466 | 4.8431 | -0.1831 | -11.0916 | -0.31586 | 0.004578 | 5.1773 | 70.2896 | 70.546 | 112.3718 | 123.436 | 4.8431 | 123.468 | 85.2036 | -0.31586 | 123.436 | 4.8431 | 85.2036 | 112.3718 | 123.468 | -123.7976 | -123.7793
5894.7188 | 123.7885 | -61.3129 | 62.1826 | -0.21492 | 0.020724 | 0.016831 | 0.01766 | 0.057898 | 0.00052127 | 0.086099 | -56.4423 | 62.114 | -61.6379 | -61.4502 | 51.0681 | 23.909 | 8.9859 | 9.2011 | 62.1506 | -61.615 | -0.32501 | -0.068664 | 4.8706 | -0.13733 | -11.1145 | -0.30212 | -0.032043 | 5.1956 | 70.2988 | 70.5139 | 112.381 | 123.4268 | 4.8706 | 123.4634 | 85.2219 | -0.30212 | 123.4268 | 4.8706 | 85.2219 | 112.381 | 123.4634 | -123.8205 | -123.7976
5895.7188 | 123.8022 | -61.3129 | 62.1414 | -0.069961 | 0.021364 | 0.016831 | 0.015738 | 0.055976 | -0.0016149 | 0.085885 | -56.4651 | 62.1277 | -61.6562 | -61.4456 | 51.0773 | 24.0463 | 9.0271 | 9.2377 | 62.1323 | -61.5967 | -0.34332 | -0.013732 | 4.8477 | -0.13275 | -11.0641 | -0.28381 | -0.009155 | 5.191 | 70.34 | 70.5505 | 112.3901 | 123.4406 | 4.8477 | 123.4451 | 85.3592 | -0.28381 | 123.4406 | 4.8477 | 85.3592 | 112.3901 | 123.4451 | -123.7976 | -123.7381
5896.7188 | 123.793 | -61.322 | 62.1597 | -0.054703 | 0.019869 | 0.014054 | 0.01531 | 0.054908 | 0.0011621 | 0.086953 | -56.4743 | 62.0819 | -61.6699 | -61.4685 | 51.0544 | 23.8495 | 8.9401 | 9.2056 | 62.146 | -61.6013 | -0.3479 | -0.07782 | 4.8477 | -0.14648 | -11.1053 | -0.27924 | -0.013733 | 5.1956 | 70.2621 | 70.5276 | 112.3764 | 123.4039 | 4.8477 | 123.468 | 85.1715 | -0.27924 | 123.4039 | 4.8477 | 85.1715 | 112.3764 | 123.468 | -123.8297 | -123.761
5897.7188 | 123.6465 | -61.3312 | 62.2101 | -0.19966 | 0.022005 | 0.015763 | 0.020224 | 0.055976 | 0.00073487 | 0.084603 | -56.5018 | 62.1918 | -61.6562 | -61.5326 | 51.004 | 23.7762 | 9.1736 | 9.1003 | 62.1826 | -61.6699 | -0.32501 | -0.018311 | 4.8294 | -0.20142 | -11.2061 | -0.33875 | -0.027466 | 5.1544 | 70.5048 | 70.4315 | 112.3352 | 123.5229 | 4.8294 | 123.5138 | 85.1074 | -0.33875 | 123.5229 | 4.8294 | 85.1074 | 112.3352 | 123.5138 | -123.8663 | -123.88
5898.7188 | 123.7701 | -61.3174 | 62.1689 | -0.10048 | 0.021364 | 0.0132 | 0.014029 | 0.058325 | 0.0024439 | 0.086312 | -56.4606 | 62.1094 | -61.6333 | -61.4731 | 51.059 | 23.9365 | 8.9401 | 9.2468 | 62.146 | -61.5921 | -0.31586 | -0.059509 | 4.8569 | -0.15564 | -11.1099 | -0.27466 | -0.022888 | 5.1727 | 70.2576 | 70.5643 | 112.3764 | 123.4268 | 4.8569 | 123.4634 | 85.2539 | -0.27466 | 123.4268 | 4.8569 | 85.2539 | 112.3764 | 123.4634 | -123.8022 | -123.761
5899.7188 | 123.7793 | -61.3129 | 62.1552 | -0.039444 | 0.020296 | 0.014268 | 0.015097 | 0.057685 | 0.00052127 | 0.085885 | -56.5155 | 62.0911 | -61.6928 | -61.4685 | 51.0406 | 23.9227 | 9.05 | 9.256 | 62.1368 | -61.6287 | -0.37994 | -0.064087 | 4.7974 | -0.15564 | -11.1145 | -0.31586 | -0.01831 | 5.1773 | 70.3629 | 70.5688 | 112.3535 | 123.4039 | 4.7974 | 123.4497 | 85.2356 | -0.31586 | 123.4039 | 4.7974 | 85.2356 | 112.3535 | 123.4497 | -123.848 | -123.7839
5900.7188 | 123.8022 | -61.3037 | 62.1506 | -0.062332 | 0.019228 | 0.015336 | 0.016165 | 0.055762 | 0.00094847 | 0.08439 | -56.4651 | 62.1094 | -61.6562 | -61.4502 | 51.0361 | 23.8586 | 8.9676 | 9.2331 | 62.146 | -61.6196 | -0.35248 | -0.041199 | 4.8386 | -0.14648 | -11.1145 | -0.31586 | -0.004578 | 5.191 | 70.2713 | 70.5368 | 112.3398 | 123.4131 | 4.8386 | 123.4497 | 85.1624 | -0.31586 | 123.4131 | 4.8386 | 85.1624 | 112.3398 | 123.4497 | -123.8068 | -123.7701
5901.7188 | 123.793 | -61.3129 | 62.1414 | -0.062332 | 0.020083 | 0.015122 | 0.016592 | 0.058112 | 0.0011621 | 0.085458 | -56.4835 | 62.1002 | -61.6745 | -61.4548 | 50.9903 | 23.7946 | 9.0408 | 9.2377 | 62.1277 | -61.6058 | -0.36163 | -0.041198 | 4.8294 | -0.14191 | -11.1511 | -0.29297 | -0.013732 | 5.191 | 70.3537 | 70.5505 | 112.3032 | 123.4131 | 4.8294 | 123.4406 | 85.1074 | -0.29297 | 123.4131 | 4.8294 | 85.1074 | 112.3032 | 123.4406 | -123.8159 | -123.7473
5902.7344 | 123.7106 | -61.3678 | 62.2284 | -0.25307 | 0.02286 | 0.018968 | 0.021933 | 0.058325 | 0.00094847 | 0.082681 | -56.4743 | 62.2284 | -61.6699 | -61.4914 | 50.9811 | 23.7488 | 9.1232 | 9.1324 | 62.1735 | -61.6837 | -0.30212 | 0 | 4.8935 | -0.1236 | -11.2473 | -0.31586 | -0.054932 | 5.1956 | 70.491 | 70.5002 | 112.3489 | 123.5962 | 4.8935 | 123.5413 | 85.1166 | -0.31586 | 123.5962 | 4.8935 | 85.1166 | 112.3489 | 123.5413 | -123.8983 | -123.912
5903.7188 | 123.7518 | -61.3403 | 62.146 | 0.0063326 | 0.019869 | 0.015122 | 0.014883 | 0.057898 | 0.00094847 | 0.08439 | -56.5063 | 62.1185 | -61.6928 | -61.5051 | 50.9903 | 23.8632 | 8.9722 | 9.137 | 62.1323 | -61.6058 | -0.35248 | -0.027466 | 4.834 | -0.1648 | -11.1557 | -0.2655 | -0.013733 | 5.1865 | 70.3125 | 70.4773 | 112.3306 | 123.4589 | 4.834 | 123.4726 | 85.2036 | -0.2655 | 123.4589 | 4.834 | 85.2036 | 112.3306 | 123.4726 | -123.8388 | -123.7518
5904.7188 | 123.7427 | -61.3403 | 62.1506 | -0.024185 | 0.019442 | 0.012345 | 0.014669 | 0.058966 | 0.0026575 | 0.085458 | -56.4697 | 62.1414 | -61.6241 | -61.5234 | 51.0223 | 23.8129 | 8.963 | 9.1461 | 62.114 | -61.6287 | -0.28381 | -0.009156 | 4.8706 | -0.18311 | -11.1282 | -0.28839 | -0.036621 | 5.1544 | 70.3033 | 70.4864 | 112.3627 | 123.4818 | 4.8706 | 123.4543 | 85.1532 | -0.28839 | 123.4818 | 4.8706 | 85.1532 | 112.3627 | 123.4543 | -123.7747 | -123.7793
5905.7188 | 123.761 | -61.3037 | 62.1597 | 0.0063326 | 0.021578 | 0.015336 | 0.017447 | 0.05683 | 0.0015893 | 0.086312 | -56.5201 | 62.1048 | -61.6745 | -61.5143 | 50.9811 | 23.8266 | 9.0042 | 9.137 | 62.1323 | -61.6104 | -0.37079 | -0.054932 | 4.7836 | -0.21057 | -11.1786 | -0.3067 | -0.027466 | 5.1544 | 70.3079 | 70.4407 | 112.2849 | 123.4085 | 4.7836 | 123.436 | 85.1303 | -0.3067 | 123.4085 | 4.7836 | 85.1303 | 112.2849 | 123.436 | -123.8342 | -123.7701
5906.7188 | 123.7427 | -61.3541 | 62.1094 | 0.10551 | 0.023928 | 0.018327 | 0.014669 | 0.055335 | 0.0013757 | 0.086312 | -56.488 | 62.1277 | -61.6745 | -61.5051 | 50.9125 | 23.7488 | 8.9905 | 9.1187 | 62.1368 | -61.6653 | -0.32044 | 0.018311 | 4.866 | -0.15106 | -11.1969 | -0.31128 | 0.027466 | 5.1865 | 70.3445 | 70.4727 | 112.2665 | 123.4818 | 4.866 | 123.4909 | 85.1028 | -0.31128 | 123.4818 | 4.866 | 85.1028 | 112.2665 | 123.4909 | -123.7839 | -123.7747
5907.7188 | 123.7701 | -61.3266 | 62.1414 | -0.031814 | 0.019656 | 0.012773 | 0.01232 | 0.056617 | 0.0047937 | 0.084603 | -56.4972 | 62.1002 | -61.6562 | -61.5646 | 51.0132 | 23.7396 | 8.9767 | 9.0912 | 62.1231 | -61.5921 | -0.32959 | -0.041198 | 4.8294 | -0.23804 | -11.1282 | -0.2655 | -0.01831 | 5.159 | 70.3033 | 70.4178 | 112.3398 | 123.4268 | 4.8294 | 123.4497 | 85.0662 | -0.2655 | 123.4268 | 4.8294 | 85.0662 | 112.3398 | 123.4497 | -123.7976 | -123.7335
5908.7188 | 123.7427 | -61.3403 | 62.1368 | 0.090256 | 0.019656 | 0.017259 | 0.015097 | 0.056617 | 0.00030767 | 0.085031 | -56.4972 | 62.1185 | -61.6837 | -61.5051 | 50.9903 | 23.7991 | 8.9218 | 9.1095 | 62.114 | -61.6196 | -0.34332 | -0.018311 | 4.8431 | -0.1648 | -11.1465 | -0.27924 | -0.022888 | 5.1865 | 70.2621 | 70.4498 | 112.3306 | 123.4589 | 4.8431 | 123.4543 | 85.1395 | -0.27924 | 123.4589 | 4.8431 | 85.1395 | 112.3306 | 123.4543 | -123.8205 | -123.7564
5909.7188 | 123.7656 | -61.3449 | 62.1323 | 0.10551 | 0.020937 | 0.017259 | 0.019583 | 0.057044 | 0.0032983 | 0.086526 | -56.456 | 62.0865 | -61.6837 | -61.4777 | 50.9583 | 23.7534 | 8.9447 | 9.1827 | 62.0956 | -61.6241 | -0.33875 | -0.045776 | 4.8889 | -0.13275 | -11.174 | -0.27924 | -0.036621 | 5.2277 | 70.2896 | 70.5276 | 112.3032 | 123.4314 | 4.8889 | 123.4406 | 85.0983 | -0.27924 | 123.4314 | 4.8889 | 85.0983 | 112.3032 | 123.4406 | -123.8159 | -123.7564
5910.7188 | 123.7747 | -61.3312 | 62.1368 | 0.16655 | 0.02286 | 0.016404 | 0.02001 | 0.056403 | 0.0020167 | 0.086099 | -56.4514 | 62.1002 | -61.6653 | -61.4731 | 50.9445 | 23.8541 | 9.0042 | 9.2102 | 62.1048 | -61.6287 | -0.33417 | -0.036621 | 4.8798 | -0.14191 | -11.1923 | -0.29755 | -0.032044 | 5.2139 | 70.3354 | 70.5414 | 112.2757 | 123.4314 | 4.8798 | 123.436 | 85.1852 | -0.29755 | 123.4314 | 4.8798 | 85.1852 | 112.2757 | 123.436 | -123.8022 | -123.7656
5911.7188 | 123.7656 | -61.3403 | 62.1323 | 0.18181 | 0.022005 | 0.01854 | 0.017233 | 0.059821 | 0.00094847 | 0.085885 | -56.4789 | 62.1002 | -61.6882 | -61.4777 | 50.9491 | 23.7854 | 8.9127 | 9.1049 | 62.1094 | -61.6333 | -0.3479 | -0.032043 | 4.8614 | -0.13733 | -11.1832 | -0.29297 | -0.022888 | 5.2094 | 70.253 | 70.4453 | 112.2894 | 123.4406 | 4.8614 | 123.4497 | 85.1257 | -0.29297 | 123.4406 | 4.8614 | 85.1257 | 112.2894 | 123.4497 | -123.8205 | -123.7656
5912.7188 | 123.793 | -61.3129 | 62.1506 | -0.10811 | 0.021364 | 0.017899 | 0.015951 | 0.054908 | 0.00094847 | 0.084817 | -56.4285 | 62.114 | -61.6516 | -61.4319 | 51.0178 | 23.8541 | 9.0088 | 9.2514 | 62.1643 | -61.6333 | -0.33875 | -0.036621 | 4.8843 | -0.11902 | -11.1328 | -0.32044 | 0.013733 | 5.2231 | 70.3217 | 70.5643 | 112.3306 | 123.4268 | 4.8843 | 123.4772 | 85.1669 | -0.32044 | 123.4268 | 4.8843 | 85.1669 | 112.3306 | 123.4772 | -123.8022 | -123.7839
5913.7188 | 123.7656 | -61.322 | 62.1277 | 0.19707 | 0.020724 | 0.017686 | 0.019583 | 0.058539 | -0.00054693 | 0.086099 | -56.456 | 62.1185 | -61.6562 | -61.4731 | 50.9216 | 23.8129 | 8.8623 | 9.1049 | 62.0956 | -61.6608 | -0.33417 | -0.009156 | 4.866 | -0.15106 | -11.2061 | -0.33875 | -0.032044 | 5.2002 | 70.1843 | 70.4269 | 112.2437 | 123.4406 | 4.866 | 123.4177 | 85.1349 | -0.33875 | 123.4406 | 4.866 | 85.1349 | 112.2437 | 123.4177 | -123.7839 | -123.7885
5914.7188 | 123.7518 | -61.3449 | 62.1552 | 0.074997 | 0.018801 | 0.015122 | 0.016592 | 0.055976 | 0.0013757 | 0.087808 | -56.4743 | 62.1002 | -61.6699 | -61.5189 | 50.9125 | 23.7946 | 8.9081 | 9.1461 | 62.1185 | -61.6241 | -0.32501 | -0.054931 | 4.8706 | -0.17395 | -11.2427 | -0.27924 | -0.036621 | 5.1956 | 70.253 | 70.491 | 112.2574 | 123.4451 | 4.8706 | 123.4634 | 85.1395 | -0.27924 | 123.4451 | 4.8706 | 85.1395 | 112.2574 | 123.4634 | -123.8251 | -123.7793
5915.7188 | 123.7289 | -61.3358 | 62.1414 | 0.18944 | 0.022646 | 0.015763 | 0.018087 | 0.05918 | 0.0032983 | 0.085885 | -56.4789 | 62.0911 | -61.6837 | -61.4914 | 50.9399 | 23.822 | 8.8943 | 9.0958 | 62.1002 | -61.647 | -0.3479 | -0.050354 | 4.8569 | -0.15564 | -11.2015 | -0.31128 | -0.041198 | 5.2048 | 70.2301 | 70.4315 | 112.2757 | 123.4268 | 4.8569 | 123.436 | 85.1578 | -0.31128 | 123.4268 | 4.8569 | 85.1578 | 112.2757 | 123.436 | -123.8251 | -123.7885
5916.7188 | 123.7564 | -61.3358 | 62.1414 | 2.0586 | 0.022005 | 0.016191 | 0.018942 | 0.057044 | 0.00030767 | 0.088235 | -56.3187 | 62.1048 | -61.6791 | -61.4456 | 50.9949 | 23.9365 | 8.8989 | 9.1827 | 62.0956 | -61.6516 | -0.34332 | -0.036621 | 5.0171 | -0.10986 | -11.1465 | -0.31586 | -0.045776 | 5.3604 | 70.2347 | 70.5185 | 112.3306 | 123.4406 | 5.0171 | 123.4314 | 85.2722 | -0.31586 | 123.4406 | 5.0171 | 85.2722 | 112.3306 | 123.4314 | -123.8205 | -123.793
5917.7188 | 123.793 | -61.29 | 62.1368 | 0.17418 | 0.021364 | 0.020036 | 0.019583 | 0.062598 | 0.00030767 | 0.086312 | -56.4148 | 62.1231 | -61.6791 | -61.377 | 50.9125 | 23.7671 | 9.0729 | 9.1278 | 62.0956 | -61.6241 | -0.3891 | -0.013733 | 4.8752 | -0.086975 | -11.2244 | -0.33417 | -0.041199 | 5.2643 | 70.3629 | 70.4178 | 112.2025 | 123.4131 | 4.8752 | 123.3856 | 85.0571 | -0.33417 | 123.4131 | 4.8752 | 85.0571 | 112.2025 | 123.3856 | -123.8159 | -123.761
5918.7188 | 123.7793 | -61.3083 | 62.1185 | 0.15129 | 0.021792 | 0.02089 | 0.017447 | 0.058539 | -0.0014013 | 0.086099 | -56.4468 | 62.1231 | -61.6745 | -61.4914 | 50.9216 | 23.7534 | 8.876 | 9.137 | 62.1185 | -61.6562 | -0.36621 | 0.004578 | 4.8615 | -0.1831 | -11.1969 | -0.3479 | 0 | 5.2277 | 70.1843 | 70.4453 | 112.2299 | 123.4314 | 4.8615 | 123.4268 | 85.0616 | -0.3479 | 123.4314 | 4.8615 | 85.0616 | 112.2299 | 123.4268 | -123.793 | -123.7747
5919.7188 | 123.7518 | -61.3083 | 62.1323 | 0.15129 | 0.022005 | 0.017899 | 0.018515 | 0.058966 | 9.4068e-05 | 0.085031 | -56.4239 | 62.1048 | -61.6699 | -61.4914 | 50.9079 | 23.7305 | 8.9401 | 9.1736 | 62.1094 | -61.647 | -0.36163 | -0.027466 | 4.8843 | -0.1831 | -11.2244 | -0.33874 | -0.022888 | 5.246 | 70.2484 | 70.4819 | 112.2162 | 123.4131 | 4.8843 | 123.4177 | 85.0388 | -0.33874 | 123.4131 | 4.8843 | 85.0388 | 112.2162 | 123.4177 | -123.8022 | -123.7793
5920.7188 | 123.793 | -61.3129 | 62.146 | 0.16655 | 0.02286 | 0.019395 | 0.021292 | 0.060462 | 0.0030847 | 0.085458 | -56.4331 | 62.1094 | -61.6653 | -61.4868 | 50.9171 | 23.8083 | 8.9539 | 9.1827 | 62.1048 | -61.6379 | -0.35248 | -0.036621 | 4.8798 | -0.17395 | -11.2289 | -0.32501 | -0.041199 | 5.2322 | 70.2667 | 70.4956 | 112.2299 | 123.4222 | 4.8798 | 123.4177 | 85.1212 | -0.32501 | 123.4222 | 4.8798 | 85.1212 | 112.2299 | 123.4177 | -123.8113 | -123.7839
5921.7344 | 123.6969 | -61.322 | 62.1964 | -0.23018 | 0.022005 | 0.021531 | 0.020437 | 0.058539 | 0.00094847 | 0.085458 | -56.4606 | 62.178 | -61.6379 | -61.5005 | 50.8942 | 23.5977 | 9.1644 | 9.0775 | 62.1918 | -61.647 | -0.31586 | -0.01831 | 4.8614 | -0.17853 | -11.3022 | -0.32501 | -0.004578 | 5.1773 | 70.4865 | 70.3995 | 112.2162 | 123.5001 | 4.8614 | 123.5138 | 84.9197 | -0.32501 | 123.5001 | 4.8614 | 84.9197 | 112.2162 | 123.5138 | -123.8342 | -123.8434
5922.7188 | 123.7106 | -61.3129 | 62.1964 | -0.22255 | 0.021151 | 0.01555 | 0.018087 | 0.057685 | 0.0011621 | 0.087808 | -56.4514 | 62.1368 | -61.6608 | -61.4548 | 50.9537 | 23.7213 | 9.0179 | 9.1095 | 62.1689 | -61.5967 | -0.3479 | -0.059509 | 4.8614 | -0.14191 | -11.2427 | -0.28381 | -0.027466 | 5.2094 | 70.3308 | 70.4224 | 112.2665 | 123.4497 | 4.8614 | 123.4818 | 85.0342 | -0.28381 | 123.4497 | 4.8614 | 85.0342 | 112.2665 | 123.4818 | -123.8571 | -123.793
5923.7188 | 123.8159 | -61.3037 | 62.1277 | 0.92949 | 0.021151 | 0.015122 | 0.018942 | 0.060248 | 0.0015893 | 0.085671 | -56.3782 | 62.1277 | -61.6425 | -61.4731 | 50.9583 | 23.8083 | 8.8577 | 9.1095 | 62.0911 | -61.6241 | -0.33875 | 0 | 4.9255 | -0.16937 | -11.1694 | -0.32044 | -0.036622 | 5.2643 | 70.1614 | 70.4132 | 112.262 | 123.4314 | 4.9255 | 123.3948 | 85.112 | -0.32044 | 123.4314 | 4.9255 | 85.112 | 112.262 | 123.3948 | -123.7701 | -123.7518
5924.7188 | 123.7747 | -61.322 | 62.1048 | -1.3364 | 0.020296 | 0.022172 | 0.021933 | 0.060248 | -0.00033333 | 0.088662 | -56.3553 | 62.1185 | -61.6653 | -61.4685 | 50.8942 | 23.8403 | 8.8943 | 9.1415 | 62.1002 | -61.6287 | -0.34332 | 0.013733 | 4.9667 | -0.14648 | -11.2106 | -0.3067 | -0.004577 | 5.3101 | 70.2164 | 70.4636 | 112.2162 | 123.4406 | 4.9667 | 123.4222 | 85.1624 | -0.3067 | 123.4406 | 4.9667 | 85.1624 | 112.2162 | 123.4222 | -123.7701 | -123.7335
5925.7188 | 123.7473 | -61.3266 | 62.1368 | 0.15129 | 0.022646 | 0.013841 | 0.017019 | 0.058966 | -0.00033333 | 0.088662 | -56.4606 | 62.1185 | -61.6608 | -61.4914 | 50.9354 | 23.8815 | 8.9447 | 9.1232 | 62.1002 | -61.6425 | -0.33417 | -0.018311 | 4.866 | -0.16479 | -11.2015 | -0.31586 | -0.036621 | 5.2002 | 70.2713 | 70.4498 | 112.262 | 123.4451 | 4.866 | 123.4268 | 85.2081 | -0.31586 | 123.4451 | 4.866 | 85.2081 | 112.262 | 123.4268 | -123.7976 | -123.7793
5926.7344 | 123.6923 | -61.3907 | 62.2147 | -0.20729 | 0.021792 | 0.018754 | 0.021719 | 0.057471 | 9.4068e-05 | 0.087594 | -56.4743 | 62.233 | -61.6653 | -61.5326 | 50.8987 | 23.8037 | 9.0637 | 9.05 | 62.2009 | -61.6745 | -0.27466 | 0.01831 | 4.9164 | -0.14191 | -11.3159 | -0.28381 | -0.013733 | 5.191 | 70.4544 | 70.4407 | 112.2894 | 123.6237 | 4.9164 | 123.5916 | 85.1944 | -0.28381 | 123.6237 | 4.9164 | 85.1944 | 112.2894 | 123.5916 | -123.88 | -123.8892
5927.7344 | 123.761 | -61.29 | 62.178 | 0.61668 | 0.021151 | 0.01854 | 0.016806 | 0.056403 | 0.00030767 | 0.086953 | -56.4102 | 62.1277 | -61.6608 | -61.4319 | 50.9674 | 23.8495 | 8.9493 | 9.1919 | 62.1643 | -61.5784 | -0.37079 | -0.050354 | 4.8798 | -0.14191 | -11.2106 | -0.28839 | -0.013733 | 5.2505 | 70.2393 | 70.4819 | 112.2574 | 123.4177 | 4.8798 | 123.4543 | 85.1395 | -0.28839 | 123.4177 | 4.8798 | 85.1395 | 112.2574 | 123.4543 | -123.8388 | -123.7564
5928.7188 | 123.7518 | -61.3266 | 62.146 | 0.15892 | 0.020296 | 0.017045 | 0.016378 | 0.057898 | 0.0011621 | 0.086739 | -56.4697 | 62.1048 | -61.6379 | -61.5143 | 50.9125 | 23.7396 | 8.8211 | 9.0179 | 62.1231 | -61.6241 | -0.31128 | -0.041199 | 4.8569 | -0.18768 | -11.2335 | -0.29755 | -0.022888 | 5.1682 | 70.1477 | 70.3445 | 112.2391 | 123.4314 | 4.8569 | 123.4497 | 85.0662 | -0.29755 | 123.4314 | 4.8569 | 85.0662 | 112.2391 | 123.4497 | -123.7839 | -123.7701
5929.7188 | 123.7701 | -61.3266 | 62.1414 | 0.10551 | 0.022646 | 0.015122 | 0.017447 | 0.060034 | 0.0028711 | 0.085244 | -56.4606 | 62.1048 | -61.6608 | -61.5189 | 50.8347 | 23.7488 | 8.8074 | 9.0454 | 62.1231 | -61.6333 | -0.33417 | -0.036621 | 4.866 | -0.19226 | -11.3068 | -0.3067 | -0.01831 | 5.2002 | 70.134 | 70.372 | 112.1613 | 123.4314 | 4.866 | 123.4497 | 85.0754 | -0.3067 | 123.4314 | 4.866 | 85.0754 | 112.1613 | 123.4497 | -123.8022 | -123.7747
5930.7188 | 123.7656 | -61.3083 | 62.1368 | 0.19707 | 0.021578 | 0.018968 | 0.019583 | 0.058753 | 0.00073487 | 0.087167 | -56.4148 | 62.1094 | -61.6837 | -61.4777 | 50.885 | 23.7579 | 8.8348 | 9.1049 | 62.0956 | -61.647 | -0.37537 | -0.027466 | 4.8935 | -0.16937 | -11.2518 | -0.33874 | -0.041199 | 5.2689 | 70.1431 | 70.4132 | 112.1933 | 123.4177 | 4.8935 | 123.4039 | 85.0662 | -0.33874 | 123.4177 | 4.8935 | 85.0662 | 112.1933 | 123.4039 | -123.8205 | -123.7839
5931.7344 | 123.7793 | -61.3129 | 62.1643 | -0.19203 | 0.021792 | 0.018754 | 0.017233 | 0.058539 | 0.00052127 | 0.086099 | -56.3782 | 62.1277 | -61.6196 | -61.4136 | 50.8347 | 23.7167 | 8.9539 | 9.1187 | 62.1277 | -61.6287 | -0.3067 | -0.036621 | 4.9347 | -0.10071 | -11.3297 | -0.31586 | -0.036621 | 5.2414 | 70.2667 | 70.4315 | 112.1475 | 123.4406 | 4.9347 | 123.4406 | 85.0296 | -0.31586 | 123.4406 | 4.9347 | 85.0296 | 112.1475 | 123.4406 | -123.7839 | -123.793
5932.7188 | 123.7289 | -61.3129 | 62.1597 | 0.0063326 | 0.021578 | 0.01854 | 0.014029 | 0.056617 | 0.00030767 | 0.088448 | -56.4697 | 62.1277 | -61.6882 | -61.5143 | 50.8575 | 23.671 | 8.9081 | 9.3201 | 62.1689 | -61.5875 | -0.37537 | -0.032043 | 4.8431 | -0.20142 | -11.3022 | -0.27466 | 0.009155 | 5.2185 | 70.2209 | 70.6329 | 112.1704 | 123.4406 | 4.8431 | 123.4818 | 84.9838 | -0.27466 | 123.4406 | 4.8431 | 84.9838 | 112.1704 | 123.4818 | -123.848 | -123.7473
5933.7188 | 123.7427 | -61.3266 | 62.1689 | 0.04448 | 0.02286 | 0.016191 | 0.018728 | 0.058539 | 0.0013757 | 0.086739 | -56.4377 | 62.1231 | -61.6837 | -61.5005 | 50.8118 | 23.5519 | 8.8165 | 9.0546 | 62.1231 | -61.6379 | -0.35706 | -0.045776 | 4.8889 | -0.17395 | -11.3571 | -0.31128 | -0.045776 | 5.246 | 70.1431 | 70.3812 | 112.1384 | 123.4497 | 4.8889 | 123.4497 | 84.8785 | -0.31128 | 123.4497 | 4.8889 | 84.8785 | 112.1384 | 123.4497 | -123.8525 | -123.8068
5934.7188 | 123.7747 | -61.3449 | 62.1872 | 0.04448 | 0.022219 | 0.017899 | 0.01531 | 0.058539 | 9.4068e-05 | 0.086099 | -56.4377 | 62.114 | -61.6653 | -61.5097 | 50.8392 | 23.497 | 8.8806 | 9.0042 | 62.1597 | -61.6013 | -0.32043 | -0.073242 | 4.9072 | -0.16479 | -11.348 | -0.25635 | -0.027466 | 5.2277 | 70.2255 | 70.3491 | 112.1841 | 123.4589 | 4.9072 | 123.5046 | 84.8419 | -0.25635 | 123.4589 | 4.9072 | 84.8419 | 112.1841 | 123.5046 | -123.8525 | -123.7885
5935.7188 | 123.7244 | -61.3174 | 62.1597 | 0.082626 | 0.019015 | 0.015336 | 0.015951 | 0.057257 | 0.0032983 | 0.085458 | -56.456 | 62.1185 | -61.6791 | -61.5097 | 50.8255 | 23.5794 | 8.844 | 9.0363 | 62.1368 | -61.6333 | -0.36163 | -0.041199 | 4.8615 | -0.19226 | -11.3342 | -0.31586 | -0.022888 | 5.2231 | 70.1614 | 70.3537 | 112.1429 | 123.436 | 4.8615 | 123.4543 | 84.8969 | -0.31586 | 123.436 | 4.8615 | 84.8969 | 112.1429 | 123.4543 | -123.8388 | -123.793
5936.7344 | 123.6923 | -61.322 | 62.2147 | -0.16151 | 0.024569 | 0.018754 | 0.022574 | 0.059607 | -0.00054693 | 0.083962 | -56.4194 | 62.1826 | -61.6791 | -61.4639 | 50.8118 | 23.4787 | 9.0363 | 9.0134 | 62.1872 | -61.6333 | -0.35706 | -0.032044 | 4.9026 | -0.14191 | -11.4029 | -0.31128 | -0.027466 | 5.2597 | 70.3583 | 70.3354 | 112.1338 | 123.5046 | 4.9026 | 123.5092 | 84.8007 | -0.31128 | 123.5046 | 4.9026 | 84.8007 | 112.1338 | 123.5092 | -123.8937 | -123.848
5937.7344 | 123.6969 | -61.3083 | 62.2147 | -0.22255 | 0.021151 | 0.016191 | 0.018515 | 0.059821 | 0.0015893 | 0.086099 | -56.4285 | 62.1689 | -61.6287 | -61.4868 | 50.8255 | 23.4879 | 9.0958 | 9.0088 | 62.1964 | -61.6287 | -0.32043 | -0.045777 | 4.8798 | -0.17853 | -11.3892 | -0.32043 | -0.018311 | 5.2002 | 70.4041 | 70.3171 | 112.1338 | 123.4772 | 4.8798 | 123.5046 | 84.7961 | -0.32043 | 123.4772 | 4.8798 | 84.7961 | 112.1338 | 123.5046 | -123.8434 | -123.8434
5938.7188 | 123.7747 | -61.3129 | 62.146 | 0.16655 | 0.022005 | 0.015122 | 0.016165 | 0.059607 | 0.00094847 | 0.087808 | -56.4194 | 62.1048 | -61.6745 | -61.4731 | 50.8347 | 23.5931 | 8.8211 | 9.0225 | 62.1277 | -61.6196 | -0.36163 | -0.041199 | 4.8935 | -0.16022 | -11.3113 | -0.3067 | -0.01831 | 5.2551 | 70.134 | 70.3354 | 112.1475 | 123.4177 | 4.8935 | 123.4406 | 84.906 | -0.3067 | 123.4177 | 4.8935 | 84.906 | 112.1475 | 123.4406 | -123.8205 | -123.7656
5939.7188 | 123.7289 | -61.3266 | 62.1826 | 0.1284 | 0.021151 | 0.018327 | 0.015951 | 0.058539 | 0.0028711 | 0.087167 | -56.4468 | 62.1048 | -61.6653 | -61.5143 | 50.7751 | 23.5611 | 8.844 | 8.9813 | 62.1277 | -61.615 | -0.33874 | -0.07782 | 4.8798 | -0.18768 | -11.4075 | -0.28839 | -0.054931 | 5.2185 | 70.1706 | 70.3079 | 112.1017 | 123.4314 | 4.8798 | 123.4543 | 84.8877 | -0.28839 | 123.4314 | 4.8798 | 84.8877 | 112.1017 | 123.4543 | -123.848 | -123.7976
5940.7188 | 123.7289 | -61.3266 | 62.1368 | 0.03685 | 0.022646 | 0.015763 | 0.018728 | 0.058966 | 0.00094847 | 0.085885 | -56.4606 | 62.1048 | -61.6699 | -61.528 | 50.7477 | 23.5657 | 8.9035 | 8.9996 | 62.114 | -61.615 | -0.34332 | -0.032044 | 4.866 | -0.20142 | -11.3892 | -0.28839 | -0.022888 | 5.2094 | 70.2301 | 70.3262 | 112.0743 | 123.4314 | 4.866 | 123.4406 | 84.8923 | -0.28839 | 123.4314 | 4.866 | 84.8923 | 112.0743 | 123.4406 | -123.8068 | -123.7518
5941.7188 | 123.761 | -61.322 | 62.1323 | 0.03685 | 0.020937 | 0.015336 | 0.016806 | 0.060675 | 0.0015893 | 0.08738 | -56.4606 | 62.1094 | -61.6608 | -61.5005 | 50.7294 | 23.6481 | 8.9722 | 9.0271 | 62.1506 | -61.6196 | -0.33875 | -0.022888 | 4.8614 | -0.17853 | -11.4029 | -0.29755 | 0.018311 | 5.2002 | 70.2942 | 70.3491 | 112.0514 | 123.4314 | 4.8614 | 123.4726 | 84.9701 | -0.29755 | 123.4314 | 4.8614 | 84.9701 | 112.0514 | 123.4726 | -123.793 | -123.7518
5942.7188 | 123.7885 | -61.2808 | 62.1643 | -0.10048 | 0.020724 | 0.017259 | 0.016592 | 0.056189 | 0.0026575 | 0.08738 | -56.3965 | 62.1231 | -61.6562 | -61.441 | 50.8072 | 23.7625 | 8.9218 | 9.1507 | 62.1185 | -61.5875 | -0.37537 | -0.041199 | 4.8843 | -0.16022 | -11.3571 | -0.3067 | -0.045777 | 5.2597 | 70.2026 | 70.4315 | 112.088 | 123.4039 | 4.8843 | 123.3994 | 85.0433 | -0.3067 | 123.4039 | 4.8843 | 85.0433 | 112.088 | 123.3994 | -123.8205 | -123.7518
5943.7188 | 123.8022 | -61.3312 | 62.1872 | 0.059738 | 0.022646 | 0.01555 | 0.017874 | 0.057044 | 0.00030767 | 0.086312 | -56.4423 | 62.1185 | -61.6837 | -61.5051 | 50.6882 | 23.5336 | 8.844 | 9.0363 | 62.1323 | -61.6058 | -0.35248 | -0.068665 | 4.8889 | -0.17395 | -11.499 | -0.27466 | -0.054932 | 5.2414 | 70.1752 | 70.3674 | 112.0193 | 123.4497 | 4.8889 | 123.4634 | 84.8648 | -0.27466 | 123.4497 | 4.8889 | 84.8648 | 112.0193 | 123.4634 | -123.8709 | -123.793
5944.7188 | 123.7518 | -61.3312 | 62.1231 | 0.1284 | 0.019442 | 0.018327 | 0.020651 | 0.057471 | 0.0030847 | 0.084176 | -56.4102 | 62.1094 | -61.6653 | -61.4822 | 50.7111 | 23.6206 | 8.7753 | 9.0225 | 62.0819 | -61.647 | -0.33417 | -0.013733 | 4.921 | -0.15106 | -11.412 | -0.31586 | -0.041199 | 5.2551 | 70.1065 | 70.3537 | 112.0422 | 123.4406 | 4.921 | 123.4131 | 84.9518 | -0.31586 | 123.4406 | 4.921 | 84.9518 | 112.0422 | 123.4131 | -123.7885 | -123.7701
5945.7188 | 123.7518 | -61.3129 | 62.1368 | 0.13603 | 0.020083 | 0.016191 | 0.019583 | 0.058966 | 0.0018031 | 0.087808 | -56.4102 | 62.0911 | -61.6653 | -61.4731 | 50.766 | 23.6618 | 8.8989 | 9.0729 | 62.1048 | -61.6241 | -0.35248 | -0.045777 | 4.9026 | -0.16022 | -11.3708 | -0.31128 | -0.032044 | 5.2551 | 70.2118 | 70.3857 | 112.0789 | 123.4039 | 4.9026 | 123.4177 | 84.9747 | -0.31128 | 123.4039 | 4.9026 | 84.9747 | 112.0789 | 123.4177 | -123.8022 | -123.761
5946.7188 | 123.7244 | -61.3403 | 62.1368 | 0.11314 | 0.021792 | 0.016831 | 0.017447 | 0.056617 | 0.0015893 | 0.086312 | -56.4285 | 62.1002 | -61.6516 | -61.5097 | 50.7706 | 23.7808 | 8.8303 | 8.963 | 62.1414 | -61.647 | -0.31128 | -0.036621 | 4.9118 | -0.16937 | -11.3663 | -0.3067 | 0.004577 | 5.2231 | 70.1706 | 70.3033 | 112.1109 | 123.4406 | 4.9118 | 123.4818 | 85.1212 | -0.3067 | 123.4406 | 4.9118 | 85.1212 | 112.1109 | 123.4818 | -123.7885 | -123.7839
5947.7188 | 123.7793 | -61.3129 | 62.1506 | -0.10048 | 0.019656 | 0.01555 | 0.01531 | 0.058753 | 0.0015893 | 0.087167 | -56.3873 | 62.1094 | -61.6425 | -61.4319 | 50.8347 | 23.7305 | 8.8394 | 9.0408 | 62.1643 | -61.5784 | -0.32959 | -0.041199 | 4.9255 | -0.11902 | -11.3159 | -0.2655 | 0.013733 | 5.2551 | 70.1523 | 70.3537 | 112.1475 | 123.4222 | 4.9255 | 123.4772 | 85.0433 | -0.2655 | 123.4222 | 4.9255 | 85.0433 | 112.1475 | 123.4772 | -123.793 | -123.7289
5948.7188 | 123.7381 | -61.3495 | 62.1643 | 0.082626 | 0.021151 | 0.013841 | 0.018301 | 0.058325 | -0.00033333 | 0.084817 | -56.4514 | 62.0956 | -61.6791 | -61.5143 | 50.7477 | 23.5703 | 8.9584 | 9.0088 | 62.1643 | -61.6241 | -0.32959 | -0.068665 | 4.8981 | -0.16479 | -11.4166 | -0.27466 | 0 | 5.2277 | 70.3079 | 70.3583 | 112.0972 | 123.4451 | 4.8981 | 123.5138 | 84.9197 | -0.27466 | 123.4451 | 4.8981 | 84.9197 | 112.0972 | 123.5138 | -123.8434 | -123.7885
5949.7188 | 123.7564 | -61.3449 | 62.1552 | 0.03685 | 0.020937 | 0.015122 | 0.018301 | 0.054908 | 0.0032983 | 0.086312 | -56.4377 | 62.1048 | -61.702 | -61.5143 | 50.7523 | 23.616 | 8.9859 | 9.0179 | 62.114 | -61.6516 | -0.35706 | -0.050354 | 4.9072 | -0.16937 | -11.4029 | -0.3067 | -0.041198 | 5.2643 | 70.3308 | 70.3629 | 112.0972 | 123.4497 | 4.9072 | 123.4589 | 84.9609 | -0.3067 | 123.4497 | 4.9072 | 84.9609 | 112.0972 | 123.4589 | -123.8571 | -123.8068
5950.7188 | 123.7473 | -61.3266 | 62.1506 | 0.11314 | 0.02051 | 0.020677 | 0.016378 | 0.057898 | -0.00011953 | 0.085244 | -56.4331 | 62.1094 | -61.6882 | -61.4731 | 50.6973 | 23.5748 | 8.9447 | 9.0775 | 62.114 | -61.6287 | -0.36163 | -0.041199 | 4.8935 | -0.14648 | -11.4532 | -0.30212 | -0.036621 | 5.2551 | 70.2713 | 70.4041 | 112.0239 | 123.436 | 4.8935 | 123.4406 | 84.9014 | -0.30212 | 123.436 | 4.8935 | 84.9014 | 112.0239 | 123.4406 | -123.8388 | -123.7793
5951.7188 | 123.8068 | -61.3037 | 62.1094 | 0.15129 | 0.02286 | 0.025376 | 0.02001 | 0.058325 | 0.0024439 | 0.085244 | -56.4606 | 62.0911 | -61.7249 | -61.441 | 50.7339 | 23.8083 | 8.9493 | 8.9493 | 62.1002 | -61.6241 | -0.42114 | -0.018311 | 4.8431 | -0.13733 | -11.3754 | -0.32044 | -0.009155 | 5.2643 | 70.253 | 70.253 | 112.0377 | 123.3948 | 4.8431 | 123.4039 | 85.112 | -0.32044 | 123.3948 | 4.8431 | 85.112 | 112.0377 | 123.4039 | -123.8342 | -123.7335
5952.7188 | 123.7427 | -61.322 | 62.1506 | 0.0063326 | 0.020724 | 0.021531 | 0.016378 | 0.053839 | -0.0011877 | 0.089944 | -56.4377 | 62.1368 | -61.6699 | -61.5463 | 50.679 | 23.7213 | 8.9813 | 9.0042 | 62.1094 | -61.647 | -0.3479 | -0.013733 | 4.8843 | -0.22431 | -11.4716 | -0.32501 | -0.041199 | 5.2322 | 70.3033 | 70.3262 | 112.001 | 123.4589 | 4.8843 | 123.4314 | 85.0433 | -0.32501 | 123.4589 | 4.8843 | 85.0433 | 112.001 | 123.4314 | -123.8205 | -123.7976
5953.7188 | 123.793 | -61.3174 | 62.1323 | -0.11574 | 0.023501 | 0.018113 | 0.02001 | 0.058325 | 0.0015893 | 0.084176 | -56.4102 | 62.1048 | -61.6791 | -61.4639 | 50.7614 | 23.6755 | 8.9722 | 9.0775 | 62.114 | -61.6425 | -0.36163 | -0.027466 | 4.9072 | -0.14648 | -11.3708 | -0.32501 | -0.01831 | 5.2689 | 70.2896 | 70.3949 | 112.0789 | 123.4222 | 4.9072 | 123.4314 | 84.993 | -0.32501 | 123.4222 | 4.9072 | 84.993 | 112.0789 | 123.4314 | -123.8113 | -123.7747
5954.7188 | 123.7885 | -61.3083 | 62.1231 | 0.19707 | 0.023714 | 0.017686 | 0.025137 | 0.060462 | -0.00097413 | 0.084817 | -56.3873 | 62.1277 | -61.6516 | -61.3861 | 50.7523 | 23.8266 | 9.0042 | 8.9676 | 62.1094 | -61.6287 | -0.34332 | 0.004578 | 4.921 | -0.077819 | -11.3709 | -0.32043 | -0.013733 | 5.2643 | 70.3125 | 70.2759 | 112.0605 | 123.436 | 4.921 | 123.4177 | 85.1349 | -0.32043 | 123.436 | 4.921 | 85.1349 | 112.0605 | 123.4177 | -123.7747 | -123.7518
5955.7188 | 123.8022 | -61.322 | 62.1185 | 0.10551 | 0.019869 | 0.020249 | 0.019583 | 0.058753 | 0.0022303 | 0.084817 | -56.3919 | 62.1231 | -61.6745 | -61.4685 | 50.7935 | 23.8037 | 8.9447 | 8.9767 | 62.1002 | -61.6287 | -0.35248 | 0.004578 | 4.9301 | -0.14648 | -11.3251 | -0.3067 | -0.01831 | 5.2826 | 70.2667 | 70.2988 | 112.1155 | 123.4451 | 4.9301 | 123.4222 | 85.1257 | -0.3067 | 123.4451 | 4.9301 | 85.1257 | 112.1155 | 123.4222 | -123.793 | -123.7473
5956.7188 | 123.7701 | -61.3266 | 62.1185 | 0.18944 | 0.023073 | 0.022813 | 0.021505 | 0.05918 | -0.00033333 | 0.085885 | -56.4926 | 62.0911 | -61.6837 | -61.496 | 50.853 | 23.9319 | 8.9539 | 9.0454 | 62.1002 | -61.647 | -0.35706 | -0.027466 | 4.834 | -0.16937 | -11.2656 | -0.32043 | -0.01831 | 5.191 | 70.2805 | 70.372 | 112.1796 | 123.4177 | 4.834 | 123.4268 | 85.2585 | -0.32043 | 123.4177 | 4.834 | 85.2585 | 112.1796 | 123.4268 | -123.8022 | -123.7656
5957.7188 | 123.7473 | -61.3403 | 62.1323 | -0.054703 | 0.019656 | 0.017686 | 0.015524 | 0.057898 | -0.0031103 | 0.086526 | -56.4468 | 62.114 | -61.6608 | -61.3953 | 50.6653 | 23.7167 | 9.1461 | 8.9905 | 62.1414 | -61.6196 | -0.32044 | -0.01831 | 4.8935 | -0.054932 | -11.467 | -0.27924 | 0.009155 | 5.2139 | 70.4864 | 70.3308 | 112.0056 | 123.4543 | 4.8935 | 123.4818 | 85.0571 | -0.27924 | 123.4543 | 4.8935 | 85.0571 | 112.0056 | 123.4818 | -123.793 | -123.7518
5958.7188 | 123.6786 | -61.3724 | 62.146 | 0.16655 | 0.023073 | 0.02089 | 0.024496 | 0.058753 | 0.00052127 | 0.086526 | -56.4468 | 62.1826 | -61.6882 | -61.5417 | 50.7294 | 23.6893 | 9.1003 | 8.9493 | 62.1185 | -61.6745 | -0.31586 | 0.036621 | 4.9255 | -0.16937 | -11.4166 | -0.30213 | -0.027466 | 5.2414 | 70.4727 | 70.3217 | 112.1017 | 123.555 | 4.9255 | 123.4909 | 85.0616 | -0.30213 | 123.555 | 4.9255 | 85.0616 | 112.1017 | 123.4909 | -123.8342 | -123.8205
5959.7188 | 123.7015 | -61.3678 | 62.1506 | 0.15129 | 0.023928 | 0.017686 | 0.02236 | 0.060462 | -0.00011953 | 0.086312 | -56.4606 | 62.1964 | -61.6791 | -61.5738 | 50.7431 | 23.7625 | 9.1553 | 8.9264 | 62.1597 | -61.6837 | -0.31128 | 0.045776 | 4.9072 | -0.20599 | -11.4075 | -0.31586 | 0.009155 | 5.2185 | 70.5231 | 70.2942 | 112.1109 | 123.5641 | 4.9072 | 123.5275 | 85.1303 | -0.31586 | 123.5641 | 4.9072 | 85.1303 | 112.1109 | 123.5275 | -123.8297 | -123.8342
5960.7188 | 123.7885 | -61.3129 | 62.1185 | -0.3141 | 0.021151 | 0.020036 | 0.017233 | 0.061103 | 9.4068e-05 | 0.084817 | -56.4056 | 62.1414 | -61.6608 | -61.4777 | 50.8118 | 23.79 | 8.9905 | 9.0637 | 62.1185 | -61.6287 | -0.3479 | 0.022888 | 4.9072 | -0.16479 | -11.3068 | -0.31586 | 0 | 5.2551 | 70.3033 | 70.3766 | 112.1246 | 123.4543 | 4.9072 | 123.4314 | 85.1028 | -0.31586 | 123.4543 | 4.9072 | 85.1028 | 112.1246 | 123.4314 | -123.7793 | -123.7473
5961.7188 | 123.6694 | -61.3632 | 62.1506 | 0.18944 | 0.023714 | 0.020677 | 0.02236 | 0.061103 | 0.00030767 | 0.086739 | -56.4606 | 62.2101 | -61.6837 | -61.5509 | 50.7111 | 23.7305 | 9.1141 | 8.931 | 62.1597 | -61.6791 | -0.32044 | 0.059509 | 4.9026 | -0.18768 | -11.4395 | -0.31586 | 0.009155 | 5.2231 | 70.4773 | 70.2942 | 112.0743 | 123.5733 | 4.9026 | 123.5229 | 85.0937 | -0.31586 | 123.5733 | 4.9026 | 85.0937 | 112.0743 | 123.5229 | -123.8342 | -123.8297
5962.7188 | 123.7152 | -61.3495 | 62.1597 | 0.17418 | 0.023714 | 0.021104 | 0.021292 | 0.061957 | 0.0013757 | 0.08738 | -56.456 | 62.2009 | -61.702 | -61.5509 | 50.7568 | 23.822 | 9.0591 | 8.9584 | 62.1597 | -61.6837 | -0.35248 | 0.041199 | 4.8935 | -0.20142 | -11.4029 | -0.33417 | 0 | 5.246 | 70.4086 | 70.3079 | 112.1063 | 123.5504 | 4.8935 | 123.5092 | 85.1715 | -0.33417 | 123.5504 | 4.8935 | 85.1715 | 112.1063 | 123.5092 | -123.8617 | -123.8434
5963.7188 | 123.6786 | -61.3541 | 62.1552 | 0.11314 | 0.024569 | 0.018754 | 0.023428 | 0.063239 | -0.00011953 | 0.086526 | -56.4468 | 62.2192 | -61.6928 | -61.5509 | 50.7431 | 23.7991 | 9.0866 | 8.8394 | 62.1689 | -61.6882 | -0.33875 | 0.064087 | 4.9072 | -0.19684 | -11.412 | -0.33417 | 0.013733 | 5.246 | 70.4407 | 70.1935 | 112.0972 | 123.5733 | 4.9072 | 123.5229 | 85.1532 | -0.33417 | 123.5733 | 4.9072 | 85.1532 | 112.0972 | 123.5229 | -123.848 | -123.8434
5964.7188 | 123.6877 | -61.3724 | 62.1689 | 0.40306 | 0.024355 | 0.020036 | 0.023001 | 0.06388 | -0.00076053 | 0.088662 | -56.4239 | 62.2284 | -61.6791 | -61.5784 | 50.6927 | 23.7213 | 9.0179 | 8.844 | 62.1964 | -61.6837 | -0.3067 | 0.05951 | 4.9484 | -0.20599 | -11.4761 | -0.31128 | 0.027466 | 5.2551 | 70.3903 | 70.2164 | 112.0651 | 123.6008 | 4.9484 | 123.5687 | 85.0937 | -0.31128 | 123.6008 | 4.9484 | 85.0937 | 112.0651 | 123.5687 | -123.848 | -123.8525
5965.7188 | 123.7152 | -61.3449 | 62.1368 | 0.11314 | 0.024782 | 0.019395 | 0.019796 | 0.063666 | 0.00073487 | 0.086953 | -56.4377 | 62.2009 | -61.6882 | -61.5875 | 50.7065 | 23.8129 | 9.0317 | 8.8715 | 62.1689 | -61.6653 | -0.34332 | 0.064087 | 4.9072 | -0.24261 | -11.4304 | -0.32043 | 0.032043 | 5.2505 | 70.3766 | 70.2164 | 112.0514 | 123.5458 | 4.9072 | 123.5138 | 85.1578 | -0.32043 | 123.5458 | 4.9072 | 85.1578 | 112.0514 | 123.5138 | -123.8251 | -123.8022
5966.7188 | 123.6603 | -61.3541 | 62.1597 | 0.021591 | 0.026278 | 0.023026 | 0.023642 | 0.063025 | -0.00076053 | 0.086739 | -56.3873 | 62.2421 | -61.6974 | -61.5646 | 50.7568 | 23.7717 | 9.1049 | 8.8806 | 62.1918 | -61.6837 | -0.34332 | 0.082397 | 4.9667 | -0.21057 | -11.4029 | -0.32959 | 0.032043 | 5.3101 | 70.459 | 70.2347 | 112.1109 | 123.5962 | 4.9667 | 123.5458 | 85.1257 | -0.32959 | 123.5962 | 4.9667 | 85.1257 | 112.1109 | 123.5458 | -123.8571 | -123.8434
5967.7188 | 123.7839 | -61.3174 | 62.114 | 0.2581 | 0.02286 | 0.022172 | 0.019369 | 0.063025 | 0.0015893 | 0.088876 | -56.3644 | 62.1414 | -61.6653 | -61.5051 | 50.7751 | 23.9319 | 8.8486 | 8.9447 | 62.1506 | -61.6425 | -0.3479 | 0.027465 | 4.953 | -0.18768 | -11.3388 | -0.32501 | 0.036621 | 5.3009 | 70.166 | 70.2621 | 112.0926 | 123.4589 | 4.953 | 123.468 | 85.2493 | -0.32501 | 123.4589 | 4.953 | 85.2493 | 112.0926 | 123.468 | -123.7793 | -123.7564
5968.7188 | 123.6603 | -61.3541 | 62.1689 | 0.013962 | 0.025423 | 0.016831 | 0.023214 | 0.061103 | 0.00073487 | 0.087167 | -56.3965 | 62.2375 | -61.6562 | -61.5555 | 50.6882 | 23.7396 | 9.0958 | 8.8577 | 62.1826 | -61.7065 | -0.30212 | 0.068665 | 4.9576 | -0.20142 | -11.4807 | -0.35248 | 0.013733 | 5.2597 | 70.4498 | 70.2118 | 112.0422 | 123.5916 | 4.9576 | 123.5367 | 85.0937 | -0.35248 | 123.5916 | 4.9576 | 85.0937 | 112.0422 | 123.5367 | -123.8251 | -123.8754
5969.7188 | 123.6511 | -61.3586 | 62.1735 | 0.03685 | 0.02521 | 0.022386 | 0.022146 | 0.062598 | 0.00052127 | 0.088235 | -56.4468 | 62.2421 | -61.6974 | -61.5829 | 50.7019 | 23.9273 | 9.1187 | 8.8623 | 62.1964 | -61.6745 | -0.33874 | 0.068664 | 4.9118 | -0.2243 | -11.4716 | -0.31586 | 0.022888 | 5.2505 | 70.4773 | 70.2209 | 112.0605 | 123.6008 | 4.9118 | 123.555 | 85.2859 | -0.31586 | 123.6008 | 4.9118 | 85.2859 | 112.0605 | 123.555 | -123.8708 | -123.848
5970.7188 | 123.7289 | -61.3358 | 62.146 | 0.074997 | 0.021792 | 0.020036 | 0.012747 | 0.061957 | -0.00011953 | 0.086953 | -56.4468 | 62.114 | -61.6928 | -61.5509 | 50.766 | 23.9319 | 8.8943 | 8.9081 | 62.1368 | -61.6425 | -0.35706 | -0.032043 | 4.8889 | -0.21515 | -11.38 | -0.3067 | -0.009155 | 5.246 | 70.2301 | 70.2438 | 112.1017 | 123.4497 | 4.8889 | 123.4726 | 85.2676 | -0.3067 | 123.4497 | 4.8889 | 85.2676 | 112.1017 | 123.4726 | -123.8388 | -123.7885
5971.7188 | 123.642 | -61.3586 | 62.2009 | 0.029221 | 0.024142 | 0.019395 | 0.023001 | 0.060462 | 0.0026575 | 0.086739 | -56.3873 | 62.2421 | -61.6882 | -61.5692 | 50.6653 | 23.8586 | 9.0454 | 8.8852 | 62.2055 | -61.6928 | -0.32959 | 0.041198 | 4.9713 | -0.21057 | -11.5356 | -0.33417 | 0.004577 | 5.3009 | 70.4041 | 70.2438 | 112.0239 | 123.6008 | 4.9713 | 123.5641 | 85.2173 | -0.33417 | 123.6008 | 4.9713 | 85.2173 | 112.0239 | 123.5641 | -123.8892 | -123.8937
5972.7188 | 123.7244 | -61.3541 | 62.146 | 0.15892 | 0.024355 | 0.018113 | 0.02001 | 0.064734 | 0.0015893 | 0.087594 | -56.456 | 62.1872 | -61.6974 | -61.5601 | 50.6973 | 23.8541 | 8.9584 | 8.8577 | 62.1735 | -61.6699 | -0.34332 | 0.041199 | 4.8981 | -0.20599 | -11.4487 | -0.31586 | 0.027466 | 5.2414 | 70.3125 | 70.2118 | 112.0514 | 123.5413 | 4.8981 | 123.5275 | 85.2081 | -0.31586 | 123.5413 | 4.8981 | 85.2081 | 112.0514 | 123.5275 | -123.8434 | -123.8159
5973.7188 | 123.6923 | -61.3403 | 62.1826 | 0.0063326 | 0.023501 | 0.021531 | 0.021933 | 0.063239 | -0.0014013 | 0.085885 | -56.3828 | 62.2421 | -61.647 | -61.5326 | 50.7248 | 23.8953 | 9.0775 | 8.8852 | 62.1918 | -61.6791 | -0.3067 | 0.059509 | 4.9576 | -0.19226 | -11.4578 | -0.33875 | 0.009155 | 5.2643 | 70.4178 | 70.2255 | 112.0651 | 123.5825 | 4.9576 | 123.5321 | 85.2356 | -0.33875 | 123.5825 | 4.9576 | 85.2356 | 112.0651 | 123.5321 | -123.8297 | -123.8617
5974.7188 | 123.7015 | -61.3174 | 62.1597 | -0.80238 | 0.024355 | 0.021531 | 0.02236 | 0.06388 | -0.00054693 | 0.086739 | -56.369 | 62.2284 | -61.6837 | -61.5143 | 50.7065 | 23.8083 | 9.0408 | 8.931 | 62.2147 | -61.6562 | -0.36621 | 0.068665 | 4.9484 | -0.19684 | -11.4532 | -0.33874 | 0.054932 | 5.3146 | 70.3583 | 70.2484 | 112.0239 | 123.5458 | 4.9484 | 123.5321 | 85.1257 | -0.33874 | 123.5458 | 4.9484 | 85.1257 | 112.0239 | 123.5321 | -123.8434 | -123.8159
5975.7344 | 123.7701 | -61.29 | 62.1368 | 0.83794 | 0.020937 | 0.018754 | 0.015951 | 0.062171 | -0.00033333 | 0.088235 | -56.3324 | 62.146 | -61.6653 | -61.5051 | 50.8209 | 24.0234 | 8.7387 | 8.9035 | 62.1597 | -61.6333 | -0.37537 | 0.009155 | 4.9576 | -0.21515 | -11.3159 | -0.34332 | 0.022888 | 5.3329 | 70.0287 | 70.1935 | 112.1109 | 123.436 | 4.9576 | 123.4497 | 85.3134 | -0.34332 | 123.436 | 4.9576 | 85.3134 | 112.1109 | 123.4497 | -123.8022 | -123.7701
5976.7188 | 123.7244 | -61.3449 | 62.178 | -0.14626 | 0.023714 | 0.016404 | 0.021933 | 0.061957 | 0.00094847 | 0.088662 | -56.3507 | 62.233 | -61.6562 | -61.528 | 50.7065 | 23.7259 | 8.9172 | 8.8715 | 62.1689 | -61.6699 | -0.31128 | 0.054931 | 4.9942 | -0.18311 | -11.4716 | -0.32501 | -0.009156 | 5.3055 | 70.2621 | 70.2164 | 112.0514 | 123.5779 | 4.9942 | 123.5138 | 85.0708 | -0.32501 | 123.5779 | 4.9942 | 85.0708 | 112.0514 | 123.5138 | -123.8342 | -123.848
5977.7344 | 123.7701 | -61.322 | 62.1368 | 0.18944 | 0.020724 | 0.019181 | 0.018301 | 0.063452 | 9.4068e-05 | 0.086739 | -56.3782 | 62.1368 | -61.6974 | -61.5051 | 50.7339 | 23.8495 | 8.8257 | 8.9447 | 62.1506 | -61.6287 | -0.37537 | 0 | 4.9438 | -0.18311 | -11.4029 | -0.3067 | 0.013733 | 5.3192 | 70.1477 | 70.2667 | 112.056 | 123.4589 | 4.9438 | 123.4726 | 85.1715 | -0.3067 | 123.4589 | 4.9438 | 85.1715 | 112.056 | 123.4726 | -123.8342 | -123.7656
5978.7188 | 123.6969 | -61.3495 | 62.1643 | -0.08522 | 0.024142 | 0.020249 | 0.021292 | 0.063025 | 0.0015893 | 0.086953 | -56.3553 | 62.2467 | -61.6791 | -61.4914 | 50.7477 | 23.8449 | 8.8943 | 8.8806 | 62.1872 | -61.6745 | -0.32959 | 0.082397 | 4.9942 | -0.14191 | -11.4166 | -0.32501 | 0.022888 | 5.3238 | 70.2438 | 70.2301 | 112.0972 | 123.5962 | 4.9942 | 123.5367 | 85.1944 | -0.32501 | 123.5962 | 4.9942 | 85.1944 | 112.0972 | 123.5367 | -123.8434 | -123.8388
5979.7188 | 123.6786 | -61.3632 | 62.2147 | -0.24544 | 0.02521 | 0.019608 | 0.020224 | 0.063239 | 0.00094847 | 0.086953 | -56.4285 | 62.2604 | -61.6653 | -61.5463 | 50.6973 | 23.877 | 8.9722 | 8.844 | 62.2375 | -61.6745 | -0.30212 | 0.045776 | 4.9347 | -0.18311 | -11.5173 | -0.31128 | 0.022888 | 5.2368 | 70.3354 | 70.2072 | 112.0605 | 123.6237 | 4.9347 | 123.6008 | 85.2402 | -0.31128 | 123.6237 | 4.9347 | 85.2402 | 112.0605 | 123.6008 | -123.88 | -123.8892
5980.7344 | 123.7427 | -61.322 | 62.1597 | 1.372 | 0.021792 | 0.016191 | 0.012106 | 0.061743 | 0.0011621 | 0.087167 | -56.3919 | 62.1277 | -61.6653 | -61.5372 | 50.7156 | 23.941 | 8.844 | 8.8669 | 62.1643 | -61.6287 | -0.34332 | -0.032043 | 4.9301 | -0.21515 | -11.4441 | -0.3067 | 0.004578 | 5.2734 | 70.166 | 70.1889 | 112.0377 | 123.4497 | 4.9301 | 123.4863 | 85.2631 | -0.3067 | 123.4497 | 4.9301 | 85.2631 | 112.0377 | 123.4863 | -123.8251 | -123.7885
5981.7188 | 123.6877 | -61.3495 | 62.2101 | -0.19966 | 0.022646 | 0.018113 | 0.021719 | 0.05918 | 0.0020167 | 0.086312 | -56.3828 | 62.2421 | -61.6653 | -61.5463 | 50.6882 | 23.822 | 9.05 | 8.8211 | 62.2238 | -61.6928 | -0.31586 | 0.032043 | 4.9667 | -0.19684 | -11.5219 | -0.34332 | 0.013733 | 5.2826 | 70.3995 | 70.1706 | 112.0377 | 123.5916 | 4.9667 | 123.5733 | 85.1715 | -0.34332 | 123.5916 | 4.9667 | 85.1715 | 112.0377 | 123.5733 | -123.8754 | -123.9029
5982.7344 | 123.7244 | -61.3632 | 62.2101 | 0.1284 | 0.026278 | 0.019608 | 0.024282 | 0.061316 | 0.0030847 | 0.088448 | -56.4331 | 62.233 | -61.6882 | -61.5234 | 50.3128 | 23.4238 | 9.343 | 8.8715 | 62.2055 | -61.6882 | -0.32501 | 0.022888 | 4.9301 | -0.16022 | -11.8973 | -0.32501 | -0.004578 | 5.2551 | 70.7062 | 70.2347 | 111.676 | 123.5962 | 4.9301 | 123.5687 | 84.787 | -0.32501 | 123.5962 | 4.9301 | 84.787 | 111.676 | 123.5687 | -123.8983 | -123.8983
5983.7188 | 123.7015 | -61.3129 | 62.1735 | -0.20729 | 0.022433 | 0.019608 | 0.021078 | 0.063025 | 0.0011621 | 0.086739 | -56.3278 | 62.2559 | -61.6699 | -61.5005 | 50.7477 | 23.8495 | 8.8669 | 8.8257 | 62.2192 | -61.647 | -0.35706 | 0.082397 | 4.985 | -0.18768 | -11.4258 | -0.33417 | 0.045776 | 5.3421 | 70.1797 | 70.1385 | 112.0605 | 123.5687 | 4.985 | 123.5321 | 85.1624 | -0.33417 | 123.5687 | 4.985 | 85.1624 | 112.0605 | 123.5321 | -123.8434 | -123.8205
5984.7188 | 123.6649 | -61.3495 | 62.1735 | -0.016556 | 0.023501 | 0.018754 | 0.019796 | 0.062384 | 0.0015893 | 0.088021 | -56.3828 | 62.2192 | -61.6837 | -61.5463 | 50.7111 | 23.8129 | 8.9127 | 8.7616 | 62.2421 | -61.647 | -0.33417 | 0.045776 | 4.9667 | -0.19684 | -11.4624 | -0.29755 | 0.068664 | 5.3009 | 70.2621 | 70.1111 | 112.0605 | 123.5687 | 4.9667 | 123.5916 | 85.1624 | -0.29755 | 123.5687 | 4.9667 | 85.1624 | 112.0605 | 123.5916 | -123.8571 | -123.8205
5985.7344 | 123.7289 | -61.3083 | 62.1826 | -0.21492 | 0.018587 | 0.014909 | 0.01531 | 0.06153 | 9.4068e-05 | 0.086953 | -56.3553 | 62.1597 | -61.6516 | -61.4685 | 50.798 | 23.9868 | 8.812 | 8.8577 | 62.1735 | -61.6241 | -0.34332 | -0.022888 | 4.953 | -0.16022 | -11.3846 | -0.31586 | -0.009155 | 5.2963 | 70.1202 | 70.166 | 112.1063 | 123.468 | 4.953 | 123.4818 | 85.2951 | -0.31586 | 123.468 | 4.953 | 85.2951 | 112.1063 | 123.4818 | -123.8342 | -123.8068
5986.7188 | 123.6557 | -61.3449 | 62.2101 | -0.09285 | 0.021364 | 0.0132 | 0.017019 | 0.060034 | 0.00052127 | 0.088448 | -56.4011 | 62.2192 | -61.6562 | -61.5463 | 50.7523 | 23.9182 | 8.9401 | 8.7067 | 62.2421 | -61.6653 | -0.31128 | 0.009155 | 4.9438 | -0.20142 | -11.4578 | -0.32043 | 0.032043 | 5.2551 | 70.285 | 70.0516 | 112.0972 | 123.5641 | 4.9438 | 123.587 | 85.2631 | -0.32043 | 123.5641 | 4.9438 | 85.2631 | 112.0972 | 123.587 | -123.8663 | -123.8754
5987.7188 | 123.6832 | -61.3403 | 62.2238 | -0.131 | 0.022005 | 0.020249 | 0.022574 | 0.060675 | 0.00094847 | 0.088021 | -56.337 | 62.2421 | -61.6608 | -61.5051 | 50.7431 | 23.9319 | 8.7753 | 8.7067 | 62.2192 | -61.6562 | -0.32044 | 0.01831 | 5.0034 | -0.1648 | -11.4807 | -0.31586 | -0.004578 | 5.3238 | 70.1157 | 70.047 | 112.0834 | 123.5825 | 5.0034 | 123.5596 | 85.2722 | -0.31586 | 123.5825 | 5.0034 | 85.2722 | 112.0834 | 123.5596 | -123.8846 | -123.88
5988.7188 | 123.7976 | -61.3449 | 62.2055 | -0.13863 | 0.023287 | 0.02089 | 0.021292 | 0.060889 | -0.00054693 | 0.085885 | -56.3278 | 62.2559 | -61.6562 | -61.5097 | 50.7477 | 23.8495 | 8.812 | 8.638 | 62.1964 | -61.6791 | -0.31128 | 0.050354 | 5.0171 | -0.16479 | -11.4578 | -0.33417 | -0.009155 | 5.3284 | 70.1569 | 69.9829 | 112.0926 | 123.6008 | 5.0171 | 123.5413 | 85.1944 | -0.33417 | 123.6008 | 5.0171 | 85.1944 | 112.0926 | 123.5413 | -123.8617 | -123.8846
5989.7188 | 123.7015 | -61.3586 | 62.1964 | -0.15388 | 0.022646 | 0.023026 | 0.022146 | 0.063239 | -0.0014013 | 0.088021 | -56.3324 | 62.2513 | -61.6608 | -61.5051 | 50.7019 | 23.9044 | 8.8211 | 8.7204 | 62.2284 | -61.6562 | -0.30212 | 0.054932 | 5.0262 | -0.14648 | -11.4944 | -0.29755 | 0.032044 | 5.3284 | 70.1797 | 70.079 | 112.0605 | 123.6099 | 5.0262 | 123.587 | 85.2631 | -0.29755 | 123.6099 | 5.0262 | 85.2631 | 112.0605 | 123.587 | -123.8571 | -123.8525
5990.7344 | 123.6694 | -61.3541 | 62.2375 | -0.24544 | 0.023287 | 0.017259 | 0.01766 | 0.05918 | -0.00033333 | 0.08738 | -56.4194 | 62.2238 | -61.6608 | -61.6699 | 50.6058 | 24.0051 | 8.8394 | 8.6746 | 62.2421 | -61.6379 | -0.3067 | -0.013733 | 4.9347 | -0.31586 | -11.6318 | -0.28381 | 0.004577 | 5.2414 | 70.1935 | 70.0287 | 111.9598 | 123.5779 | 4.9347 | 123.5962 | 85.3592 | -0.28381 | 123.5779 | 4.9347 | 85.3592 | 111.9598 | 123.5962 | -123.8983 | -123.8754
5991.7188 | 123.7427 | -61.3129 | 62.1918 | -0.23018 | 0.020724 | 0.01854 | 0.013815 | 0.057044 | -0.00076053 | 0.087167 | -56.3416 | 62.1552 | -61.647 | -61.4456 | 50.7294 | 23.8907 | 8.7799 | 8.7891 | 62.1826 | -61.6196 | -0.33417 | -0.036621 | 4.9713 | -0.13275 | -11.4624 | -0.3067 | -0.009155 | 5.3055 | 70.0928 | 70.1019 | 112.0422 | 123.468 | 4.9713 | 123.4955 | 85.2036 | -0.3067 | 123.468 | 4.9713 | 85.2036 | 112.0422 | 123.4955 | -123.8388 | -123.8113
5992.7344 | 123.6786 | -61.3083 | 62.1964 | -0.10048 | 0.024569 | 0.026017 | 0.022574 | 0.061316 | 0.00073487 | 0.08738 | -56.3507 | 62.2192 | -61.6562 | -61.5234 | 50.6699 | 23.8129 | 8.812 | 8.725 | 62.2238 | -61.6333 | -0.3479 | 0.022888 | 4.9576 | -0.21515 | -11.5265 | -0.32501 | 0.027466 | 5.3055 | 70.1202 | 70.0333 | 111.9781 | 123.5275 | 4.9576 | 123.5321 | 85.1212 | -0.32501 | 123.5275 | 4.9576 | 85.1212 | 111.9781 | 123.5321 | -123.8525 | -123.8297
5993.7188 | 123.6877 | -61.3312 | 62.2009 | -0.23018 | 0.021792 | 0.017045 | 0.017447 | 0.061103 | 0.00073487 | 0.086099 | -56.3187 | 62.1918 | -61.6562 | -61.4868 | 50.6836 | 23.8815 | 8.844 | 8.7616 | 62.2101 | -61.6104 | -0.32501 | -0.009156 | 5.0125 | -0.15564 | -11.5173 | -0.27924 | 0.009155 | 5.3375 | 70.1752 | 70.0928 | 112.0148 | 123.5229 | 5.0125 | 123.5413 | 85.2127 | -0.27924 | 123.5229 | 5.0125 | 85.2127 | 112.0148 | 123.5413 | -123.8571 | -123.8113
5994.7188 | 123.6786 | -61.3312 | 62.2238 | -0.19966 | 0.021364 | 0.018113 | 0.01766 | 0.059821 | -0.0026831 | 0.086312 | -56.3782 | 62.2055 | -61.6562 | -61.5417 | 50.679 | 23.7854 | 8.8852 | 8.7158 | 62.2513 | -61.6516 | -0.32501 | -0.018311 | 4.953 | -0.21057 | -11.5448 | -0.32043 | 0.027466 | 5.278 | 70.2164 | 70.047 | 112.0102 | 123.5367 | 4.953 | 123.5825 | 85.1166 | -0.32043 | 123.5367 | 4.953 | 85.1166 | 112.0102 | 123.5825 | -123.88 | -123.8754
5995.7344 | 123.7885 | -61.2946 | 62.1689 | -0.19203 | 0.019228 | 0.012345 | 0.013601 | 0.058753 | 0.00073487 | 0.088235 | -56.0486 | 62.2009 | -61.615 | -61.4548 | 50.798 | 23.8632 | 8.7158 | 8.8898 | 62.1597 | -61.6013 | -0.32043 | 0.032044 | 5.246 | -0.16022 | -11.3708 | -0.3067 | -0.009155 | 5.5664 | 70.0104 | 70.1843 | 112.0926 | 123.4955 | 5.246 | 123.4543 | 85.1578 | -0.3067 | 123.4955 | 5.246 | 85.1578 | 112.0926 | 123.4543 | -123.7839 | -123.7701
5996.7344 | 123.7198 | -61.3174 | 62.1918 | -0.19203 | 0.023714 | 0.015977 | 0.021933 | 0.060675 | 0.00030767 | 0.084176 | -56.3232 | 62.2284 | -61.6379 | -61.4868 | 50.6195 | 23.8541 | 8.7936 | 8.7112 | 62.1918 | -61.6837 | -0.32043 | 0.036622 | 4.9942 | -0.16937 | -11.5723 | -0.36621 | 0 | 5.3146 | 70.1111 | 70.0287 | 111.937 | 123.5458 | 4.9942 | 123.5092 | 85.1715 | -0.36621 | 123.5458 | 4.9942 | 85.1715 | 111.937 | 123.5092 | -123.8297 | -123.8754
5997.7344 | 123.6237 | -61.3541 | 62.178 | -0.10811 | 0.024996 | 0.01854 | 0.025137 | 0.061103 | 0.0018031 | 0.085458 | -56.3049 | 62.233 | -61.6516 | -61.496 | 50.6516 | 23.7442 | 8.8211 | 8.6884 | 62.2147 | -61.6745 | -0.29755 | 0.054931 | 5.0491 | -0.14191 | -11.5265 | -0.32044 | 0.036621 | 5.3467 | 70.1752 | 70.0424 | 112.0056 | 123.587 | 5.0491 | 123.5687 | 85.0983 | -0.32044 | 123.587 | 5.0491 | 85.0983 | 112.0056 | 123.5687 | -123.8297 | -123.8525
5998.7188 | 123.7427 | -61.3174 | 62.1964 | -0.23781 | 0.020724 | 0.0132 | 0.015097 | 0.059607 | 0.00073487 | 0.085244 | -56.3324 | 62.1597 | -61.647 | -61.4594 | 50.6744 | 23.8358 | 8.6472 | 8.7662 | 62.2147 | -61.6013 | -0.32959 | -0.036621 | 4.985 | -0.14191 | -11.5219 | -0.28381 | 0.018311 | 5.3146 | 69.9646 | 70.0836 | 111.9919 | 123.4772 | 4.985 | 123.5321 | 85.1532 | -0.28381 | 123.4772 | 4.985 | 85.1532 | 111.9919 | 123.5321 | -123.8434 | -123.7976
5999.7188 | 123.7701 | -61.3083 | 62.146 | -0.10811 | 0.020937 | 0.018754 | 0.01296 | 0.058966 | 0.00073487 | 0.086526 | -56.3644 | 62.1185 | -61.6333 | -61.4594 | 50.7339 | 23.8586 | 8.6151 | 8.7524 | 62.1643 | -61.5921 | -0.32501 | -0.027466 | 4.9438 | -0.15106 | -11.412 | -0.28381 | 0.018311 | 5.2689 | 69.9234 | 70.0607 | 112.0422 | 123.4268 | 4.9438 | 123.4726 | 85.1669 | -0.28381 | 123.4268 | 4.9438 | 85.1669 | 112.0422 | 123.4726 | -123.7793 | -123.7381
6000.7344 | 123.793 | -61.29 | 62.1552 | -0.08522 | 0.020083 | 0.017472 | 0.016592 | 0.056617 | -0.00054693 | 0.086739 | -56.3507 | 62.1277 | -61.6333 | -61.441 | 50.7065 | 23.9044 | 8.5648 | 8.7433 | 62.1643 | -61.6196 | -0.34332 | -0.027465 | 4.9393 | -0.15106 | -11.4487 | -0.32959 | 0.009156 | 5.2826 | 69.8547 | 70.0333 | 111.9965 | 123.4177 | 4.9393 | 123.4543 | 85.1944 | -0.32959 | 123.4177 | 4.9393 | 85.1944 | 111.9965 | 123.4543 | -123.7885 | -123.7747
6001.7188 | 123.6969 | -61.3312 | 62.2238 | -0.2607 | 0.020724 | 0.014909 | 0.019796 | 0.056403 | -0.0018285 | 0.086312 | -56.3553 | 62.1689 | -61.647 | -61.4868 | 50.6607 | 23.7625 | 8.7936 | 8.7753 | 62.1872 | -61.6196 | -0.31586 | -0.054932 | 4.9759 | -0.15564 | -11.5631 | -0.28839 | -0.036621 | 5.2917 | 70.1248 | 70.1065 | 111.9919 | 123.5001 | 4.9759 | 123.5184 | 85.0937 | -0.28839 | 123.5001 | 4.9759 | 85.0937 | 111.9919 | 123.5184 | -123.8708 | -123.8434
6002.7344 | 123.6603 | -61.3586 | 62.1918 | 0.14366 | 0.022433 | 0.022813 | 0.025778 | 0.056403 | 0.00030767 | 0.088021 | -56.4194 | 62.1918 | -61.6837 | -61.5692 | 50.5737 | 23.7259 | 8.6288 | 8.5236 | 62.178 | -61.6608 | -0.32501 | 0 | 4.9393 | -0.21057 | -11.618 | -0.30212 | -0.013732 | 5.2643 | 69.9875 | 69.8822 | 111.9324 | 123.5504 | 4.9393 | 123.5367 | 85.0845 | -0.30212 | 123.5504 | 4.9393 | 85.0845 | 111.9324 | 123.5367 | -123.8754 | -123.8525
6003.7188 | 123.8022 | -61.2991 | 62.1689 | -0.2607 | 0.020724 | 0.017472 | 0.015097 | 0.060462 | 0.0013757 | 0.086526 | -56.3095 | 62.1323 | -61.6241 | -61.4136 | 50.7202 | 23.8953 | 8.6243 | 8.7936 | 62.1735 | -61.5921 | -0.32501 | -0.036621 | 4.9896 | -0.11444 | -11.4487 | -0.29297 | 0.004578 | 5.3146 | 69.9234 | 70.0928 | 112.0193 | 123.4314 | 4.9896 | 123.4726 | 85.1944 | -0.29297 | 123.4314 | 4.9896 | 85.1944 | 112.0193 | 123.4726 | -123.793 | -123.761
6004.7188 | 123.7106 | -61.3312 | 62.1964 | -0.12337 | 0.023928 | 0.018754 | 0.025564 | 0.059394 | -0.0022559 | 0.08439 | -56.3278 | 62.2284 | -61.6699 | -61.5005 | 50.5966 | 23.8998 | 8.638 | 8.6929 | 62.2284 | -61.647 | -0.33875 | 0.032044 | 5.0034 | -0.16937 | -11.5997 | -0.31586 | 0.032044 | 5.3421 | 69.9692 | 70.0241 | 111.9278 | 123.5596 | 5.0034 | 123.5596 | 85.231 | -0.31586 | 123.5596 | 5.0034 | 85.231 | 111.9278 | 123.5596 | -123.8663 | -123.8434
6005.7344 | 123.793 | -61.3083 | 62.1552 | -0.13863 | 0.022433 | 0.013841 | 0.014029 | 0.059821 | -0.00097413 | 0.08738 | -56.3507 | 62.1002 | -61.6562 | -61.441 | 50.6561 | 23.941 | 8.5739 | 8.7982 | 62.1826 | -61.615 | -0.3479 | -0.054931 | 4.9576 | -0.13275 | -11.499 | -0.3067 | 0.027466 | 5.3055 | 69.8822 | 70.1065 | 111.9644 | 123.4085 | 4.9576 | 123.4909 | 85.2493 | -0.3067 | 123.4085 | 4.9576 | 85.2493 | 111.9644 | 123.4909 | -123.8113 | -123.7701
6006.7188 | 123.7656 | -61.2991 | 62.1597 | -0.08522 | 0.02051 | 0.015763 | 0.013601 | 0.056189 | 0.0018031 | 0.086312 | -56.369 | 62.1277 | -61.6699 | -61.4456 | 50.6882 | 24.0509 | 8.606 | 8.7616 | 62.1735 | -61.6013 | -0.37079 | -0.032043 | 4.9301 | -0.14649 | -11.4716 | -0.30212 | 0.013733 | 5.3009 | 69.9051 | 70.0607 | 111.9873 | 123.4268 | 4.9301 | 123.4726 | 85.35 | -0.30212 | 123.4268 | 4.9301 | 85.35 | 111.9873 | 123.4726 | -123.8297 | -123.761
6007.7344 | 123.7976 | -61.322 | 62.146 | 0.17418 | 0.023287 | 0.023026 | 0.020224 | 0.05918 | 0.0039393 | 0.083535 | -56.3095 | 62.1094 | -61.647 | -61.4685 | 50.5554 | 23.1308 | 8.844 | 8.5419 | 62.1964 | -61.6241 | -0.32501 | -0.036621 | 5.0125 | -0.14648 | -11.5906 | -0.30213 | 0.050354 | 5.3375 | 70.166 | 69.8639 | 111.8774 | 123.4314 | 5.0125 | 123.5184 | 84.4528 | -0.30213 | 123.4314 | 5.0125 | 84.4528 | 111.8774 | 123.5184 | -123.793 | -123.7701
6008.7188 | 123.7244 | -61.322 | 62.1826 | -0.1844 | 0.021578 | 0.017899 | 0.018301 | 0.057898 | 0.0013757 | 0.085671 | -56.3141 | 62.1506 | -61.6196 | -61.3586 | 50.7294 | 23.9639 | 8.4641 | 8.7982 | 62.1826 | -61.6241 | -0.29755 | -0.032043 | 5.0079 | -0.036622 | -11.4532 | -0.30213 | 0 | 5.3055 | 69.7861 | 70.1202 | 112.0514 | 123.4726 | 5.0079 | 123.5046 | 85.2859 | -0.30213 | 123.4726 | 5.0079 | 85.2859 | 112.0514 | 123.5046 | -123.8022 | -123.8068
6009.7188 | 123.7335 | -61.29 | 62.1872 | -0.19203 | 0.019015 | 0.018327 | 0.017874 | 0.05683 | 0.00030767 | 0.088021 | -56.3232 | 62.1552 | -61.647 | -61.4365 | 50.6241 | 23.1537 | 8.5648 | 8.67 | 62.1735 | -61.5829 | -0.35706 | -0.032044 | 4.9667 | -0.14648 | -11.5631 | -0.29297 | -0.013733 | 5.3238 | 69.8547 | 69.96 | 111.9141 | 123.4451 | 4.9667 | 123.4634 | 84.4437 | -0.29297 | 123.4451 | 4.9667 | 84.4437 | 111.9141 | 123.4634 | -123.8342 | -123.7701
6010.7344 | 123.7106 | -61.3037 | 62.2284 | -0.077591 | 0.022433 | 0.018327 | 0.02471 | 0.058325 | -0.00076053 | 0.085244 | -56.2912 | 62.2421 | -61.6379 | -61.3632 | 50.7156 | 23.2269 | 8.6151 | 8.6655 | 62.2101 | -61.6287 | -0.33417 | 0.013732 | 5.0125 | -0.059509 | -11.5128 | -0.32501 | -0.018311 | 5.3467 | 69.9188 | 69.9692 | 112.0193 | 123.5458 | 5.0125 | 123.5138 | 84.5306 | -0.32501 | 123.5458 | 5.0125 | 84.5306 | 112.0193 | 123.5138 | -123.8663 | -123.8571
6011.7188 | 123.793 | -61.2946 | 62.178 | -0.12337 | 0.023501 | 0.02089 | 0.011679 | 0.060034 | 0.0041529 | 0.084176 | -56.3004 | 62.1323 | -61.6013 | -61.4639 | 50.7065 | 23.3047 | 8.4412 | 8.7936 | 62.1643 | -61.5692 | -0.3067 | -0.045777 | 4.9942 | -0.16937 | -11.4716 | -0.27466 | -0.013733 | 5.3009 | 69.7357 | 70.0882 | 112.001 | 123.4268 | 4.9942 | 123.4589 | 84.5993 | -0.27466 | 123.4268 | 4.9942 | 84.5993 | 112.001 | 123.4589 | -123.7793 | -123.7473
6012.7344 | 123.6328 | -61.3358 | 62.2238 | -0.0012969 | 0.023501 | 0.024308 | 0.024923 | 0.060248 | 0.00073487 | 0.084603 | -56.3461 | 62.2513 | -61.647 | -61.5372 | 50.4135 | 23.1674 | 8.5968 | 8.4961 | 62.2009 | -61.6791 | -0.31128 | 0.027466 | 4.9896 | -0.20142 | -11.8103 | -0.34332 | -0.022888 | 5.3009 | 69.9326 | 69.8318 | 111.7493 | 123.587 | 4.9896 | 123.5367 | 84.5032 | -0.34332 | 123.587 | 4.9896 | 84.5032 | 111.7493 | 123.5367 | -123.8708 | -123.9029
6013.7344 | 123.6328 | -61.3541 | 62.2101 | 0.021591 | 0.025423 | 0.020036 | 0.023642 | 0.062384 | -0.00054693 | 0.088021 | -56.3507 | 62.233 | -61.6791 | -61.5372 | 50.4639 | 23.0667 | 8.6929 | 8.5419 | 62.2375 | -61.6608 | -0.32501 | 0.022888 | 5.0034 | -0.18311 | -11.7462 | -0.3067 | 0.027466 | 5.3284 | 70.047 | 69.8959 | 111.8179 | 123.587 | 5.0034 | 123.5916 | 84.4208 | -0.3067 | 123.587 | 5.0034 | 84.4208 | 111.8179 | 123.5916 | -123.8892 | -123.8708
6014.7188 | 123.7473 | -61.3083 | 62.1826 | -0.0089264 | 0.020083 | 0.017045 | 0.013388 | 0.060034 | 0.0018031 | 0.087808 | -56.3553 | 62.1323 | -61.6562 | -61.4548 | 50.6012 | 23.2132 | 8.4686 | 8.6151 | 62.1964 | -61.5692 | -0.3479 | -0.050354 | 4.953 | -0.14648 | -11.5814 | -0.26093 | 0.013733 | 5.3009 | 69.7769 | 69.9234 | 111.9095 | 123.4406 | 4.953 | 123.5046 | 84.5215 | -0.26093 | 123.4406 | 4.953 | 84.5215 | 111.9095 | 123.5046 | -123.8388 | -123.7518
6015.7188 | 123.7839 | -61.3083 | 62.1597 | -0.10811 | 0.02286 | 0.012132 | 0.016165 | 0.057471 | -0.0014013 | 0.085031 | -56.3049 | 62.1414 | -61.6013 | -61.4319 | 50.647 | 23.172 | 8.4229 | 8.6288 | 62.1506 | -61.5555 | -0.29297 | -0.018311 | 5.0034 | -0.1236 | -11.5128 | -0.24719 | -0.009155 | 5.2963 | 69.7311 | 69.9371 | 111.9553 | 123.4497 | 5.0034 | 123.4589 | 84.4803 | -0.24719 | 123.4497 | 5.0034 | 84.4803 | 111.9553 | 123.4589 | -123.761 | -123.7152
6016.7344 | 123.674 | -61.3312 | 62.178 | 0.052109 | 0.022646 | 0.021317 | 0.02471 | 0.059607 | -0.0011877 | 0.08738 | -56.3187 | 62.233 | -61.6516 | -61.5234 | 50.4547 | 23.085 | 8.5052 | 8.4183 | 62.1964 | -61.6562 | -0.32043 | 0.054931 | 5.0125 | -0.19226 | -11.7233 | -0.32501 | 0.01831 | 5.3329 | 69.8364 | 69.7495 | 111.7859 | 123.5641 | 5.0125 | 123.5275 | 84.4162 | -0.32501 | 123.5641 | 5.0125 | 84.4162 | 111.7859 | 123.5275 | -123.8297 | -123.8342
6017.7344 | 123.6603 | -61.3586 | 62.1872 | 0.097885 | 0.023714 | 0.020249 | 0.023428 | 0.062598 | -0.00011953 | 0.083749 | -56.3644 | 62.2467 | -61.6791 | -61.5738 | 50.4044 | 23.0209 | 8.4503 | 8.3817 | 62.2009 | -61.6882 | -0.32043 | 0.059509 | 4.9942 | -0.21515 | -11.7828 | -0.32959 | 0.013733 | 5.3146 | 69.809 | 69.7403 | 111.763 | 123.6053 | 4.9942 | 123.5596 | 84.3796 | -0.32959 | 123.6053 | 4.9942 | 84.3796 | 111.763 | 123.5596 | -123.8663 | -123.8754
6018.7344 | 123.7015 | -61.2991 | 62.1872 | -0.15388 | 0.02521 | 0.021317 | 0.024923 | 0.061316 | 9.4068e-05 | 0.08738 | -56.2775 | 62.2742 | -61.6333 | -61.4685 | 50.4959 | 23.14 | 8.4183 | 8.3954 | 62.2147 | -61.6287 | -0.33417 | 0.086975 | 5.0217 | -0.16937 | -11.6913 | -0.32959 | 0.027466 | 5.3558 | 69.7174 | 69.6945 | 111.795 | 123.5733 | 5.0217 | 123.5138 | 84.4391 | -0.32959 | 123.5733 | 5.0217 | 84.4391 | 111.795 | 123.5138 | -123.8205 | -123.8159
6019.7188 | 123.7061 | -61.3266 | 62.2101 | -0.09285 | 0.022646 | 0.018968 | 0.02236 | 0.063239 | -0.0011877 | 0.087594 | -56.2775 | 62.2284 | -61.6608 | -61.4594 | 50.4776 | 23.1354 | 8.3542 | 8.3817 | 62.2421 | -61.6241 | -0.33417 | 0.018311 | 5.0491 | -0.13275 | -11.7325 | -0.29755 | 0.032043 | 5.3833 | 69.6808 | 69.7083 | 111.8042 | 123.555 | 5.0491 | 123.5687 | 84.462 | -0.29755 | 123.555 | 5.0491 | 84.462 | 111.8042 | 123.5687 | -123.8708 | -123.8342
6020.7188 | 123.761 | -61.29 | 62.2101 | -0.1844 | 0.020724 | 0.015336 | 0.011038 | 0.060248 | 9.4068e-05 | 0.086312 | -56.0486 | 62.2192 | -61.5784 | -61.4136 | 50.5554 | 23.1766 | 8.2901 | 8.4641 | 62.2192 | -61.5555 | -0.28839 | 0.009155 | 5.2414 | -0.1236 | -11.6547 | -0.2655 | 0.009155 | 5.5298 | 69.5801 | 69.754 | 111.8454 | 123.5092 | 5.2414 | 123.5092 | 84.4666 | -0.2655 | 123.5092 | 5.2414 | 84.4666 | 111.8454 | 123.5092 | -123.7885 | -123.7656
6021.7188 | 123.7976 | -61.2534 | 62.1826 | -0.10048 | 0.021151 | 0.016404 | 0.014883 | 0.057685 | -0.0011877 | 0.087594 | -56.25 | 62.1597 | -61.615 | -61.4136 | 50.5188 | 23.2727 | 8.1757 | 8.4091 | 62.1826 | -61.5646 | -0.36163 | -0.022888 | 5.0034 | -0.16022 | -11.6638 | -0.31128 | 0 | 5.365 | 69.429 | 69.6625 | 111.7722 | 123.4131 | 5.0034 | 123.436 | 84.5261 | -0.31128 | 123.4131 | 5.0034 | 84.5261 | 111.7722 | 123.436 | -123.7976 | -123.7473
6022.7188 | 123.6877 | -61.3174 | 62.2375 | -0.22255 | 0.023287 | 0.012986 | 0.019796 | 0.058753 | 0.00030767 | 0.08973 | -56.3507 | 62.2284 | -61.6241 | -61.5051 | 50.3586 | 23.0804 | 8.3908 | 8.2443 | 62.233 | -61.6241 | -0.3067 | -0.009155 | 4.9667 | -0.18768 | -11.879 | -0.3067 | -0.004578 | 5.2734 | 69.7083 | 69.5618 | 111.676 | 123.5458 | 4.9667 | 123.5504 | 84.3979 | -0.3067 | 123.5458 | 4.9667 | 84.3979 | 111.676 | 123.5504 | -123.8617 | -123.8617
6023.7188 | 123.7976 | -61.2808 | 62.2009 | -0.12337 | 0.018801 | 0.017472 | 0.015524 | 0.058966 | 0.00052127 | 0.085671 | -56.282 | 62.146 | -61.6196 | -61.3998 | 50.4272 | 23.204 | 8.1757 | 8.3954 | 62.178 | -61.5646 | -0.33875 | -0.054932 | 4.9988 | -0.11902 | -11.7737 | -0.28381 | -0.022888 | 5.3375 | 69.4565 | 69.6762 | 111.7081 | 123.4268 | 4.9988 | 123.4589 | 84.4849 | -0.28381 | 123.4268 | 4.9988 | 84.4849 | 111.7081 | 123.4589 | -123.8205 | -123.7656
6024.7188 | 123.7244 | -61.2671 | 62.2055 | -0.16914 | 0.020724 | 0.018968 | 0.019369 | 0.055976 | -0.00011953 | 0.086312 | -56.2958 | 62.146 | -61.6058 | -61.441 | 50.4227 | 23.1674 | 8.1985 | 8.2672 | 62.2101 | -61.5738 | -0.33874 | -0.059509 | 4.9713 | -0.17395 | -11.7828 | -0.3067 | 0.004578 | 5.3101 | 69.4656 | 69.5343 | 111.6898 | 123.4131 | 4.9713 | 123.4772 | 84.4345 | -0.3067 | 123.4131 | 4.9713 | 84.4345 | 111.6898 | 123.4772 | -123.8113 | -123.7793
6025.7188 | 123.6237 | -61.3083 | 62.2238 | -0.077591 | 0.024355 | 0.022813 | 0.025351 | 0.058539 | 0.00030767 | 0.087167 | -56.2729 | 62.2513 | -61.6333 | -61.4731 | 50.3265 | 23.1125 | 8.226 | 8.2352 | 62.2192 | -61.6241 | -0.32501 | 0.027466 | 5.0354 | -0.16479 | -11.8973 | -0.31586 | -0.004578 | 5.3604 | 69.5343 | 69.5435 | 111.6348 | 123.5596 | 5.0354 | 123.5275 | 84.4208 | -0.31586 | 123.5596 | 5.0354 | 84.4208 | 111.6348 | 123.5275 | -123.8571 | -123.848
6026.7188 | 123.7198 | -61.3037 | 62.2055 | -0.016556 | 0.023287 | 0.02324 | 0.022574 | 0.060889 | 0.00073487 | 0.085031 | -56.2592 | 62.2559 | -61.6287 | -61.4822 | 50.3311 | 22.9935 | 8.2123 | 8.1985 | 62.2559 | -61.5829 | -0.32501 | 0.050354 | 5.0446 | -0.17853 | -11.8744 | -0.27924 | 0.050354 | 5.3696 | 69.516 | 69.5023 | 111.6348 | 123.5596 | 5.0446 | 123.5596 | 84.2972 | -0.27924 | 123.5596 | 5.0446 | 84.2972 | 111.6348 | 123.5596 | -123.8342 | -123.7885
6027.7188 | 123.8068 | -61.2854 | 62.1689 | -0.08522 | 0.022219 | 0.013413 | 0.013601 | 0.059821 | 0.00052127 | 0.088876 | -56.2912 | 62.1597 | -61.6241 | -61.4365 | 50.4456 | 23.2407 | 8.0292 | 8.2489 | 62.2055 | -61.5829 | -0.33875 | -0.009155 | 4.9942 | -0.15106 | -11.7233 | -0.29755 | 0.036621 | 5.3329 | 69.3146 | 69.5343 | 111.731 | 123.4451 | 4.9942 | 123.4909 | 84.5261 | -0.29755 | 123.4451 | 4.9942 | 84.5261 | 111.731 | 123.4909 | -123.793 | -123.7518
6028.7344 | 123.6877 | -61.3174 | 62.2055 | -0.10811 | 0.024996 | 0.021317 | 0.023855 | 0.060248 | 9.4068e-05 | 0.086953 | -56.2271 | 62.233 | -61.6241 | -61.4731 | 50.2853 | 23.0621 | 8.1573 | 8.1299 | 62.2284 | -61.6058 | -0.3067 | 0.027466 | 5.0903 | -0.15564 | -11.9202 | -0.28839 | 0.022889 | 5.397 | 69.4748 | 69.4473 | 111.6028 | 123.5504 | 5.0903 | 123.5458 | 84.3796 | -0.28839 | 123.5504 | 5.0903 | 84.3796 | 111.6028 | 123.5458 | -123.8297 | -123.8113
6029.7188 | 123.7701 | -61.2625 | 62.1964 | -0.22255 | 0.018801 | 0.017045 | 0.019796 | 0.062384 | -0.0020421 | 0.085458 | -56.2271 | 62.1689 | -61.5692 | -61.3861 | 50.2579 | 23.1262 | 8.0429 | 8.1894 | 62.2238 | -61.5234 | -0.3067 | -0.027466 | 5.0354 | -0.1236 | -11.9385 | -0.26093 | 0.027466 | 5.3421 | 69.3054 | 69.4519 | 111.5204 | 123.4314 | 5.0354 | 123.4863 | 84.3887 | -0.26093 | 123.4314 | 5.0354 | 84.3887 | 111.5204 | 123.4863 | -123.7656 | -123.7198
6030.7188 | 123.7976 | -61.2579 | 62.2284 | -0.11574 | 0.019656 | 0.018113 | 0.015524 | 0.059607 | 0.00030767 | 0.08738 | -56.2408 | 62.178 | -61.5967 | -61.3998 | 50.322 | 23.0713 | 7.9102 | 8.1757 | 62.2055 | -61.5601 | -0.33874 | -0.050354 | 5.0171 | -0.14191 | -11.9064 | -0.30212 | -0.022889 | 5.3558 | 69.1681 | 69.4336 | 111.5799 | 123.436 | 5.0171 | 123.4634 | 84.3292 | -0.30212 | 123.436 | 5.0171 | 84.3292 | 111.5799 | 123.4634 | -123.8251 | -123.7885
6031.7344 | 123.6969 | -61.2854 | 62.2192 | 1.517 | 0.021792 | 0.019822 | 0.02471 | 0.05918 | 0.0018031 | 0.085458 | -56.2225 | 62.2467 | -61.6287 | -61.4594 | 50.2213 | 22.9935 | 7.9514 | 8.0154 | 62.2284 | -61.6196 | -0.34332 | 0.027466 | 5.0629 | -0.17395 | -11.998 | -0.33417 | 0.009156 | 5.4062 | 69.2368 | 69.3008 | 111.5067 | 123.5321 | 5.0629 | 123.5138 | 84.2789 | -0.33417 | 123.5321 | 5.0629 | 84.2789 | 111.5067 | 123.5138 | -123.848 | -123.8388
6032.7188 | 123.7747 | -61.2717 | 62.233 | -0.17677 | 0.020083 | 0.017686 | 0.016592 | 0.05683 | -0.0020421 | 0.089303 | -56.218 | 62.1643 | -61.5967 | -61.4136 | 50.2808 | 22.9614 | 7.901 | 8.1116 | 62.2055 | -61.5555 | -0.32501 | -0.068664 | 5.0537 | -0.14191 | -11.9522 | -0.28381 | -0.027466 | 5.3787 | 69.1727 | 69.3832 | 111.5524 | 123.436 | 5.0537 | 123.4772 | 84.2331 | -0.28381 | 123.436 | 5.0537 | 84.2331 | 111.5524 | 123.4772 | -123.8297 | -123.7885
6033.7188 | 123.7747 | -61.2625 | 62.2375 | -0.49721 | 0.022433 | 0.015763 | 0.018301 | 0.060889 | 0.0026575 | 0.085031 | -56.2271 | 62.1552 | -61.5875 | -61.3907 | 50.2991 | 23.0942 | 7.782 | 8.0063 | 62.233 | -61.5372 | -0.32501 | -0.082398 | 5.0354 | -0.12817 | -11.9385 | -0.27466 | -0.004578 | 5.3604 | 69.0445 | 69.2688 | 111.5616 | 123.4177 | 5.0354 | 123.4955 | 84.3567 | -0.27466 | 123.4177 | 5.0354 | 84.3567 | 111.5616 | 123.4955 | -123.8251 | -123.7747
6034.7344 | 123.6603 | -61.3083 | 62.2284 | 0.15129 | 0.023714 | 0.019395 | 0.024282 | 0.060889 | 0.0043665 | 0.090157 | -56.2775 | 62.2467 | -61.6425 | -61.7889 | 50.0977 | 23.1308 | 7.7591 | 7.7728 | 62.233 | -61.615 | -0.33417 | 0.01831 | 5.0308 | -0.48065 | -12.1307 | -0.3067 | 0.004577 | 5.365 | 69.0674 | 69.0811 | 111.4059 | 123.555 | 5.0308 | 123.5413 | 84.4391 | -0.3067 | 123.555 | 5.0308 | 84.4391 | 111.4059 | 123.5413 | -123.8709 | -123.8434
6035.7188 | 123.7473 | -61.2442 | 62.2009 | -0.031814 | 0.020937 | 0.019608 | 0.038809 | 0.060034 | 0.0011621 | 0.11323 | -56.2546 | 62.146 | -61.615 | -61.4365 | 50.148 | 22.9568 | 7.8278 | 8.0154 | 62.1964 | -61.5875 | -0.37079 | -0.054932 | 4.9896 | -0.19226 | -12.0529 | -0.34332 | -0.004578 | 5.3604 | 69.072 | 69.2596 | 111.3922 | 123.3902 | 4.9896 | 123.4406 | 84.2011 | -0.34332 | 123.3902 | 4.9896 | 84.2011 | 111.3922 | 123.4406 | -123.8159 | -123.7885
6036.7188 | 123.6923 | -61.2671 | 62.2604 | -0.23781 | 0.02286 | 0.021531 | 0.0324 | 0.057685 | 0.00073487 | 0.091012 | -56.2271 | 62.2238 | -61.6333 | -61.4319 | 50.148 | 22.7921 | 8.0154 | 7.9788 | 62.2559 | -61.5967 | -0.36621 | -0.036621 | 5.04 | -0.16479 | -12.1124 | -0.32959 | -0.004578 | 5.4062 | 69.2825 | 69.2459 | 111.4151 | 123.4909 | 5.04 | 123.5229 | 84.0591 | -0.32959 | 123.4909 | 5.04 | 84.0591 | 111.4151 | 123.5229 | -123.8937 | -123.8571
6037.7344 | 123.6969 | -61.2808 | 62.2375 | -0.024185 | 0.025851 | 0.01854 | 0.054831 | 0.062384 | 0.0013757 | 0.12476 | -56.1951 | 62.2696 | -61.6058 | -61.4594 | 50.0336 | 22.7417 | 7.8598 | 7.9147 | 62.2009 | -61.6196 | -0.32501 | 0.032043 | 5.0858 | -0.17853 | -12.204 | -0.33875 | -0.036621 | 5.4108 | 69.1406 | 69.1956 | 111.3144 | 123.5504 | 5.0858 | 123.4818 | 84.0225 | -0.33875 | 123.5504 | 5.0858 | 84.0225 | 111.3144 | 123.4818 | -123.8434 | -123.8571
6038.7188 | 123.7106 | -61.2305 | 62.2147 | 0.55565 | 0.019442 | 0.018968 | 0.033682 | 0.058325 | -0.00033333 | 0.099984 | -56.1356 | 62.1735 | -61.5646 | -61.3861 | 50.0931 | 22.9385 | 7.5714 | 7.7225 | 62.2192 | -61.5189 | -0.33417 | -0.041199 | 5.0949 | -0.15564 | -12.1216 | -0.28839 | 0.004577 | 5.4291 | 68.8019 | 68.9529 | 111.3235 | 123.4039 | 5.0949 | 123.4497 | 84.169 | -0.28839 | 123.4039 | 5.0949 | 84.169 | 111.3235 | 123.4497 | -123.7793 | -123.7335
6039.7188 | 118.0115 | -58.9462 | 58.3511 | -0.09285 | 0.022646 | 0.015336 | 6.9213 | -0.01217 | 0.032137 | 6.9985 | -54.3915 | 60.3561 | -62.2238 | 10.2859 | 39.7064 | 29.3015 | 19.78 | 14.1861 | 44.6823 | -45.3506 | -3.2776 | 2.005 | 4.5547 | 69.2322 | -18.6447 | 13.5956 | -13.6688 | 7.8323 | 78.7262 | 73.1323 | 98.6526 | 119.3024 | 4.5547 | 103.6285 | 88.2477 | 13.5956 | 119.3024 | 4.5547 | 88.2477 | 98.6526 | 103.6285 | -120.575 | -103.7018
6040.7344 | 123.3902 | -63.3499 | 59.9625 | -0.077591 | 0.02521 | 0.020677 | 0.0033474 | -0.0046932 | -0.0014013 | -0.010032 | -58.2733 | 59.9716 | -63.6337 | 57.9849 | 54.6112 | 55.7556 | 50.1572 | 37.6648 | 59.9487 | -63.6749 | -0.28381 | 0.009156 | 5.0766 | 121.3348 | -5.3513 | -0.32501 | -0.013733 | 5.3604 | 113.5071 | 101.0147 | 117.9611 | 123.3215 | 5.0766 | 123.2986 | 119.1055 | -0.32501 | 123.3215 | 5.0766 | 119.1055 | 117.9611 | 123.2986 | -123.5962 | -123.6374
6041.7188 | 123.5916 | -63.2858 | 59.9396 | -0.21492 | 0.022433 | 0.0132 | -0.0071202 | -0.0055478 | -0.0016149 | -0.0089636 | -58.2001 | 59.8938 | -63.652 | 58.1955 | 54.744 | 55.9387 | 50.0565 | 37.9852 | 59.967 | -63.5696 | -0.36621 | -0.045776 | 5.0858 | 121.4813 | -5.1956 | -0.28381 | 0.027466 | 5.452 | 113.3423 | 101.2711 | 118.0298 | 123.1796 | 5.0858 | 123.2529 | 119.2245 | -0.28381 | 123.1796 | 5.0858 | 119.2245 | 118.0298 | 123.2529 | -123.5916 | -123.5092
6042.7188 | 123.5596 | -63.3362 | 59.9579 | -0.031814 | 0.023073 | 0.011918 | -0.0028476 | -0.009393 | -0.00033333 | -0.0066138 | -58.287 | 59.9213 | -63.6795 | 58.1589 | 54.689 | 55.8609 | 50.0656 | 37.8296 | 59.9625 | -63.6429 | -0.34332 | -0.036621 | 5.0491 | 121.4951 | -5.2689 | -0.3067 | 0.004577 | 5.3925 | 113.4018 | 101.1658 | 118.0252 | 123.2574 | 5.0491 | 123.2986 | 119.1971 | -0.3067 | 123.2574 | 5.0491 | 119.1971 | 118.0252 | 123.2986 | -123.6374 | -123.6008
6043.7188 | 123.5962 | -63.3224 | 59.9808 | -0.20729 | 0.019869 | 0.02089 | 0.0014248 | -0.007684 | -0.0048193 | -0.0068274 | -58.3099 | 59.903 | -63.6475 | 58.1772 | 54.5975 | 55.8838 | 50.0748 | 37.9074 | 59.9579 | -63.6383 | -0.32501 | -0.07782 | 5.0125 | 121.4996 | -5.3833 | -0.31586 | -0.022888 | 5.3375 | 113.3972 | 101.2299 | 117.9199 | 123.2254 | 5.0125 | 123.2803 | 119.2062 | -0.31586 | 123.2254 | 5.0125 | 119.2062 | 117.9199 | 123.2803 | -123.6282 | -123.6191
6044.7188 | 123.6053 | -63.327 | 59.9991 | -0.17677 | 0.020296 | 0.016404 | 0.00057044 | -0.0098202 | -0.0050329 | -0.0066138 | -58.2047 | 59.935 | -63.6658 | 58.2001 | 54.6524 | 55.806 | 50.1297 | 37.9852 | 60.0082 | -63.6612 | -0.33875 | -0.064086 | 5.1224 | 121.5271 | -5.3467 | -0.33417 | 0.009156 | 5.4611 | 113.4567 | 101.3123 | 117.9794 | 123.262 | 5.1224 | 123.3353 | 119.133 | -0.33417 | 123.262 | 5.1224 | 119.133 | 117.9794 | 123.3353 | -123.6649 | -123.6603
6045.7188 | 123.5962 | -63.3316 | 59.9579 | 0.029221 | 0.021151 | 0.014909 | -0.0024204 | -0.0072568 | -0.0024695 | -0.0074682 | -58.287 | 59.9167 | -63.6978 | 58.1451 | 54.5837 | 55.7281 | 50.0748 | 37.9669 | 59.9533 | -63.6429 | -0.36621 | -0.041199 | 5.0446 | 121.4767 | -5.3741 | -0.31128 | -0.004578 | 5.4108 | 113.4064 | 101.2985 | 117.9153 | 123.2483 | 5.0446 | 123.2849 | 119.0598 | -0.31128 | 123.2483 | 5.0446 | 119.0598 | 117.9153 | 123.2849 | -123.6557 | -123.6008
6046.7344 | 123.5504 | -63.382 | 60.0082 | -0.22255 | 0.023073 | 0.021317 | 0.0022794 | -0.0089658 | -0.0022559 | -0.0085364 | -58.2047 | 60.0586 | -63.7161 | 58.1772 | 54.5197 | 55.6778 | 50.1801 | 38.0081 | 60.0266 | -63.7024 | -0.33417 | 0.050354 | 5.1773 | 121.5591 | -5.4886 | -0.32044 | 0.01831 | 5.5115 | 113.562 | 101.3901 | 117.9016 | 123.4406 | 5.1773 | 123.4085 | 119.0598 | -0.32044 | 123.4406 | 5.1773 | 119.0598 | 117.9016 | 123.4085 | -123.7244 | -123.7106
6047.7188 | 123.6374 | -63.3408 | 59.9716 | -0.069961 | 0.022219 | 0.013627 | -0.0017796 | -0.0072568 | -0.0016149 | -0.0051184 | -58.2642 | 59.9213 | -63.6978 | 58.1543 | 54.2816 | 55.5496 | 50.061 | 38.1042 | 60.0311 | -63.6383 | -0.35706 | -0.050354 | 5.0766 | 121.4951 | -5.69 | -0.29755 | 0.059509 | 5.4337 | 113.4018 | 101.445 | 117.6224 | 123.262 | 5.0766 | 123.3719 | 118.8904 | -0.29755 | 123.262 | 5.0766 | 118.8904 | 117.6224 | 123.3719 | -123.6694 | -123.6099
6048.7188 | 123.642 | -63.3224 | 59.9899 | -0.16151 | 0.020937 | 0.018113 | -0.0024204 | -0.011102 | -0.0011877 | -0.003623 | -58.2138 | 59.9258 | -63.6658 | 58.2001 | 54.4968 | 55.6458 | 50.0336 | 38.1729 | 59.9808 | -63.6475 | -0.34332 | -0.064087 | 5.1086 | 121.5225 | -5.4932 | -0.32501 | -0.009155 | 5.452 | 113.356 | 101.4954 | 117.8192 | 123.2483 | 5.1086 | 123.3032 | 118.9682 | -0.32501 | 123.2483 | 5.1086 | 118.9682 | 117.8192 | 123.3032 | -123.6557 | -123.6374
6049.7344 | 123.5413 | -63.382 | 60.0449 | -0.24544 | 0.023073 | 0.016191 | 0.00014304 | -0.0089658 | -0.00011953 | -0.0038366 | -58.2504 | 60.0128 | -63.6978 | 58.1131 | 54.4189 | 55.513 | 50.235 | 38.1363 | 60.0174 | -63.6795 | -0.31586 | -0.032044 | 5.1315 | 121.4951 | -5.6259 | -0.29755 | -0.027466 | 5.4474 | 113.6169 | 101.5182 | 117.8009 | 123.3948 | 5.1315 | 123.3994 | 118.895 | -0.29755 | 123.3948 | 5.1315 | 118.895 | 117.8009 | 123.3994 | -123.7427 | -123.7244
6050.7188 | 123.6877 | -63.3682 | 60.022 | -0.15388 | 0.019442 | 0.018968 | -0.001566 | -0.010034 | -0.0033239 | -0.0081092 | -58.1589 | 59.9533 | -63.6978 | 58.4061 | 54.2267 | 55.3894 | 50.1984 | 38.1821 | 59.9716 | -63.6749 | -0.32959 | -0.068665 | 5.2094 | 121.7743 | -5.7953 | -0.3067 | -0.050354 | 5.5389 | 113.5666 | 101.5503 | 117.5949 | 123.3215 | 5.2094 | 123.3398 | 118.7576 | -0.3067 | 123.3215 | 5.2094 | 118.7576 | 117.5949 | 123.3398 | -123.7198 | -123.6969
6051.7188 | 123.6328 | -63.3865 | 60.0266 | -0.054703 | 0.02286 | 0.015763 | -0.0028476 | -0.009393 | -0.0011877 | -0.0061866 | -58.2733 | 59.9487 | -63.7253 | 58.0994 | 54.3686 | 55.4947 | 50.0977 | 38.2599 | 59.9991 | -63.6795 | -0.33875 | -0.07782 | 5.1132 | 121.4859 | -5.658 | -0.29297 | -0.027466 | 5.452 | 113.4842 | 101.6464 | 117.7551 | 123.3353 | 5.1132 | 123.3856 | 118.8812 | -0.29297 | 123.3353 | 5.1132 | 118.8812 | 117.7551 | 123.3856 | -123.7518 | -123.7061
6052.7344 | 123.5687 | -63.414 | 60.0357 | -0.039444 | 0.023073 | 0.018113 | 0.0078336 | -0.0087522 | -0.0037511 | -0.0074682 | -58.1863 | 60.0723 | -63.7253 | 58.0627 | 54.277 | 55.394 | 50.1389 | 38.1958 | 60.0266 | -63.7573 | -0.31128 | 0.036621 | 5.2277 | 121.4767 | -5.7587 | -0.34332 | -0.009156 | 5.5389 | 113.5529 | 101.6098 | 117.691 | 123.4863 | 5.2277 | 123.4406 | 118.808 | -0.34332 | 123.4863 | 5.2277 | 118.808 | 117.691 | 123.4406 | -123.761 | -123.793
6053.7188 | 123.7198 | -63.327 | 59.9716 | -0.054703 | 0.021151 | 0.017045 | -0.002634 | -0.0070432 | -0.0031103 | -0.0049048 | -58.1818 | 59.9442 | -63.707 | 58.1406 | 54.3228 | 55.4855 | 50.0107 | 38.3606 | 59.9945 | -63.652 | -0.37994 | -0.027466 | 5.1453 | 121.4676 | -5.6488 | -0.32501 | 0.022888 | 5.5252 | 113.3377 | 101.6876 | 117.6498 | 123.2712 | 5.1453 | 123.3215 | 118.8126 | -0.32501 | 123.2712 | 5.1453 | 118.8126 | 117.6498 | 123.3215 | -123.6786 | -123.6237
6054.7188 | 123.6923 | -63.3362 | 59.9899 | -0.10811 | 0.019869 | 0.016191 | -0.0028476 | -0.0087522 | -0.0035375 | -0.0055456 | -58.2138 | 59.9487 | -63.7207 | 58.1223 | 54.2404 | 55.4077 | 49.9741 | 38.356 | 59.9854 | -63.6383 | -0.38452 | -0.041199 | 5.1224 | 121.4584 | -5.7495 | -0.30212 | -0.004577 | 5.5069 | 113.3102 | 101.6922 | 117.5766 | 123.2849 | 5.1224 | 123.3215 | 118.7439 | -0.30212 | 123.2849 | 5.1224 | 118.7439 | 117.5766 | 123.3215 | -123.7106 | -123.6282
6055.7188 | 123.6557 | -63.3728 | 60.0357 | -0.21492 | 0.022219 | 0.017259 | -7.0562e-05 | -0.011102 | -0.0018285 | -0.0081092 | -58.1635 | 59.9808 | -63.6978 | 58.1177 | 54.2908 | 55.3665 | 50.0107 | 38.3057 | 60.0128 | -63.6932 | -0.32501 | -0.054932 | 5.2094 | 121.4905 | -5.7449 | -0.32043 | -0.022889 | 5.5344 | 113.3835 | 101.6785 | 117.6636 | 123.3536 | 5.2094 | 123.3856 | 118.7393 | -0.32043 | 123.3536 | 5.2094 | 118.7393 | 117.6636 | 123.3856 | -123.7335 | -123.7289
6056.7188 | 123.7015 | -63.3545 | 59.9991 | -0.054703 | 0.021792 | 0.017259 | -0.004343 | -0.0098202 | -0.0028967 | -0.0055456 | -58.2047 | 59.9808 | -63.7115 | 58.0948 | 54.3228 | 55.3757 | 49.9466 | 38.3194 | 59.9808 | -63.6887 | -0.35706 | -0.01831 | 5.1498 | 121.4493 | -5.6763 | -0.33417 | -0.01831 | 5.5069 | 113.3011 | 101.6739 | 117.6773 | 123.3353 | 5.1498 | 123.3353 | 118.7302 | -0.33417 | 123.3353 | 5.1498 | 118.7302 | 117.6773 | 123.3353 | -123.7106 | -123.6877
6057.7344 | 123.6099 | -63.414 | 60.0494 | -0.08522 | 0.02521 | 0.015763 | 0.0050564 | -0.0087522 | -0.0031103 | -0.0064002 | -58.168 | 60.0632 | -63.7299 | 58.0582 | 54.245 | 55.2292 | 50.0427 | 38.2645 | 60.0082 | -63.7711 | -0.31586 | 0.013733 | 5.246 | 121.4722 | -5.8044 | -0.35706 | -0.041198 | 5.5618 | 113.4567 | 101.6785 | 117.659 | 123.4772 | 5.246 | 123.4222 | 118.6432 | -0.35706 | 123.4772 | 5.246 | 118.6432 | 117.659 | 123.4222 | -123.7793 | -123.8205
6058.7188 | 123.6694 | -63.3682 | 60.0311 | -0.069961 | 0.022005 | 0.017686 | -0.0049838 | -0.0074704 | -0.0031103 | -0.0068274 | -58.223 | 59.967 | -63.7573 | 58.0719 | 54.2725 | 55.2887 | 49.9924 | 38.3148 | 60.0266 | -63.6703 | -0.3891 | -0.064087 | 5.1453 | 121.4401 | -5.7587 | -0.30212 | -0.004578 | 5.5344 | 113.3606 | 101.683 | 117.6407 | 123.3353 | 5.1453 | 123.3948 | 118.6569 | -0.30212 | 123.3353 | 5.1453 | 118.6569 | 117.6407 | 123.3948 | -123.7885 | -123.7015
6059.7188 | 123.6877 | -63.3728 | 59.9945 | 0.013962 | 0.020937 | 0.017686 | -0.0028476 | -0.0078976 | -0.00054693 | -0.0051184 | -58.2184 | 59.9487 | -63.7436 | 58.0444 | 54.2313 | 55.2658 | 49.9878 | 38.4293 | 59.9625 | -63.6703 | -0.37079 | -0.045777 | 5.1544 | 121.4172 | -5.7632 | -0.29755 | -0.032044 | 5.5252 | 113.3606 | 101.8021 | 117.6041 | 123.3215 | 5.1544 | 123.3353 | 118.6386 | -0.29755 | 123.3215 | 5.1544 | 118.6386 | 117.6041 | 123.3353 | -123.7381 | -123.6649
6060.7188 | 123.7198 | -63.3682 | 60.0037 | -0.17677 | 0.022219 | 0.014695 | -0.00071136 | -0.0091794 | -0.0052465 | -0.0083228 | -58.1223 | 59.9579 | -63.7161 | 58.374 | 54.2725 | 54.9728 | 50.0153 | 38.5254 | 59.9762 | -63.6658 | -0.3479 | -0.045776 | 5.246 | 121.7422 | -5.7312 | -0.29755 | -0.027466 | 5.5939 | 113.3835 | 101.8936 | 117.6407 | 123.3261 | 5.246 | 123.3444 | 118.3411 | -0.29755 | 123.3261 | 5.246 | 118.3411 | 117.6407 | 123.3444 | -123.7198 | -123.6694
6061.7188 | 123.7015 | -63.3774 | 59.9991 | -0.09285 | 0.021151 | 0.0085 | -0.0030612 | -0.0089658 | -0.00033333 | -0.005332 | -58.1955 | 59.9808 | -63.7299 | 58.0444 | 54.213 | 55.2383 | 49.9512 | 38.5162 | 59.9762 | -63.6703 | -0.35248 | -0.01831 | 5.1819 | 121.4218 | -5.7861 | -0.29297 | -0.022888 | 5.5344 | 113.3286 | 101.8936 | 117.5903 | 123.3582 | 5.1819 | 123.3536 | 118.6157 | -0.29297 | 123.3582 | 5.1819 | 118.6157 | 117.5903 | 123.3536 | -123.7289 | -123.6694
6062.7344 | 123.6282 | -63.414 | 60.0311 | -0.047073 | 0.024142 | 0.017686 | 0.0056972 | -0.0078976 | -0.0016149 | -0.0074682 | -58.1451 | 60.0586 | -63.7344 | 58.0902 | 53.9474 | 54.9362 | 50.2716 | 38.4338 | 60.0357 | -63.7436 | -0.32044 | 0.027466 | 5.2689 | 121.5042 | -6.0837 | -0.32959 | 0.004578 | 5.5893 | 113.6856 | 101.8478 | 117.3614 | 123.4726 | 5.2689 | 123.4497 | 118.3502 | -0.32959 | 123.4726 | 5.2689 | 118.3502 | 117.3614 | 123.4497 | -123.7656 | -123.7747
6063.7188 | 123.6603 | -63.4094 | 59.9991 | -0.016556 | 0.018374 | 0.018327 | -0.0041294 | -0.0078976 | -0.00054693 | -0.010459 | -58.2275 | 59.935 | -63.739 | 58.1955 | 54.2679 | 54.9591 | 49.9191 | 38.4338 | 59.9945 | -63.6841 | -0.32959 | -0.064086 | 5.1819 | 121.6049 | -5.7312 | -0.27466 | -0.004577 | 5.5115 | 113.3286 | 101.8433 | 117.6773 | 123.3444 | 5.1819 | 123.4039 | 118.3685 | -0.27466 | 123.3444 | 5.1819 | 118.3685 | 117.6773 | 123.4039 | -123.7381 | -123.6832
6064.7188 | 123.6877 | -63.382 | 60.0128 | -0.16914 | 0.020937 | 0.019822 | -0.001566 | -0.010034 | -0.0022559 | -0.005973 | -58.1314 | 59.9533 | -63.707 | 58.049 | 54.1626 | 55.1193 | 50.3632 | 38.7817 | 60.0632 | -63.6429 | -0.32501 | -0.059509 | 5.2505 | 121.431 | -5.8502 | -0.26093 | 0.050354 | 5.5756 | 113.7451 | 102.1637 | 117.5446 | 123.3353 | 5.2505 | 123.4451 | 118.5013 | -0.26093 | 123.3353 | 5.2505 | 118.5013 | 117.5446 | 123.4451 | -123.7198 | -123.6557
6065.7344 | 123.674 | -63.4094 | 60.1318 | -0.22255 | 0.023501 | 0.017899 | 0.0020656 | -0.010247 | -0.00097413 | -0.0057592 | -58.1772 | 60.0632 | -63.7573 | 57.9163 | 53.9886 | 54.9088 | 49.9146 | 38.2599 | 60.0494 | -63.7161 | -0.3479 | -0.068665 | 5.2322 | 121.3257 | -6.1432 | -0.3067 | -0.082398 | 5.5801 | 113.324 | 101.6693 | 117.3981 | 123.4726 | 5.2322 | 123.4589 | 118.3182 | -0.3067 | 123.4726 | 5.2322 | 118.3182 | 117.3981 | 123.4589 | -123.8892 | -123.848
6066.7188 | 123.7152 | -63.3591 | 60.0449 | -0.20729 | 0.018801 | 0.017686 | -0.0034886 | -0.0078976 | -0.00054693 | -0.005973 | -57.7469 | 60.0494 | -63.6841 | 58.0261 | 54.039 | 54.9545 | 49.7131 | 38.3148 | 60.0266 | -63.6475 | -0.32501 | 0.004577 | 5.6122 | 121.3852 | -6.0059 | -0.28839 | -0.018311 | 5.9372 | 113.0722 | 101.6739 | 117.3981 | 123.4085 | 5.6122 | 123.3856 | 118.3136 | -0.28839 | 123.4085 | 5.6122 | 118.3136 | 117.3981 | 123.3856 | -123.7289 | -123.6923
6067.7188 | 123.5779 | -63.3362 | 60.022 | -0.14626 | 0.020724 | 0.017045 | -0.0028476 | -0.0096066 | -0.0048193 | -0.005973 | -58.0902 | 59.9442 | -63.7024 | 57.9529 | 54.0527 | 54.9637 | 49.5758 | 38.443 | 60.0357 | -63.6658 | -0.36621 | -0.07782 | 5.246 | 121.2891 | -5.9692 | -0.32959 | 0.013733 | 5.6122 | 112.912 | 101.7792 | 117.3889 | 123.2803 | 5.246 | 123.3719 | 118.2999 | -0.32959 | 123.2803 | 5.246 | 118.2999 | 117.3889 | 123.3719 | -123.7244 | -123.6877
6068.7188 | 123.6969 | -63.3728 | 60.0586 | -0.031814 | 0.021364 | 0.014695 | -0.0039158 | -0.011529 | -0.0011877 | -0.0055456 | -58.1131 | 59.9762 | -63.7344 | 57.9163 | 53.9841 | 54.9179 | 49.5575 | 38.0859 | 60.0128 | -63.6612 | -0.36163 | -0.082398 | 5.2597 | 121.2891 | -6.0745 | -0.28839 | -0.045777 | 5.6213 | 112.9303 | 101.4587 | 117.3569 | 123.349 | 5.2597 | 123.3856 | 118.2907 | -0.28839 | 123.349 | 5.2597 | 118.2907 | 117.3569 | 123.3856 | -123.793 | -123.7198
6069.7188 | 123.6603 | -63.3591 | 60.0311 | 0.11314 | 0.02286 | 0.017472 | -0.001566 | -0.010461 | -0.0037511 | -0.005973 | -58.0856 | 59.9945 | -63.7299 | 57.8339 | 53.92 | 54.8676 | 49.4522 | 37.9807 | 59.9991 | -63.6978 | -0.37079 | -0.036621 | 5.2734 | 121.1929 | -6.1111 | -0.33874 | -0.032044 | 5.6442 | 112.8113 | 101.3397 | 117.2791 | 123.3536 | 5.2734 | 123.3582 | 118.2266 | -0.33874 | 123.3536 | 5.2734 | 118.2266 | 117.2791 | 123.3582 | -123.761 | -123.7289
6070.7344 | 123.7335 | -63.3453 | 60.0311 | -0.11574 | 0.021792 | 0.015122 | -0.0022068 | -0.0087522 | -0.0020421 | -0.0068274 | -58.0261 | 60.0128 | -63.6978 | 57.9208 | 53.9886 | 54.9042 | 49.3515 | 38.0081 | 60.0128 | -63.6566 | -0.35248 | -0.018311 | 5.3192 | 121.2662 | -6.0425 | -0.31128 | -0.018311 | 5.6717 | 112.6968 | 101.3535 | 117.334 | 123.3582 | 5.3192 | 123.3582 | 118.2495 | -0.31128 | 123.3582 | 5.3192 | 118.2495 | 117.334 | 123.3582 | -123.7289 | -123.6877
6071.7188 | 123.7061 | -63.3865 | 60.0174 | 0.15129 | 0.021578 | 0.019181 | 0.00014304 | -0.010461 | -0.00033333 | -0.0051184 | -58.0124 | 59.9945 | -63.7207 | 57.8064 | 53.8879 | 54.7943 | 49.2096 | 37.8159 | 59.9991 | -63.6978 | -0.33417 | -0.022888 | 5.3741 | 121.1929 | -6.1295 | -0.31128 | -0.018311 | 5.7083 | 112.5961 | 101.2024 | 117.2745 | 123.381 | 5.3741 | 123.3856 | 118.1808 | -0.31128 | 123.381 | 5.3741 | 118.1808 | 117.2745 | 123.3856 | -123.7381 | -123.7152
6072.7344 | 123.7198 | -63.3453 | 60.0266 | -0.14626 | 0.022005 | 0.01854 | -0.0032748 | -0.0087522 | -0.0031103 | -0.0051184 | -57.9803 | 60.0174 | -63.6795 | 57.8384 | 54.0802 | 55.0964 | 49.0173 | 37.468 | 60.0449 | -63.6566 | -0.33417 | -0.009155 | 5.365 | 121.1838 | -5.9464 | -0.31128 | 0.018311 | 5.6992 | 112.3627 | 100.8133 | 117.4255 | 123.3627 | 5.365 | 123.3902 | 118.4418 | -0.31128 | 123.3627 | 5.365 | 118.4418 | 117.4255 | 123.3902 | -123.7061 | -123.6832
6073.7188 | 123.6694 | -63.3545 | 60.0723 | 0.13603 | 0.023501 | 0.020036 | -0.0024204 | -0.009393 | -0.0016149 | -0.0076818 | -58.0399 | 60.0082 | -63.7207 | 57.724 | 53.7918 | 54.6524 | 49.1043 | 37.5595 | 60.022 | -63.6795 | -0.36621 | -0.064087 | 5.3146 | 121.0785 | -6.2805 | -0.32501 | -0.050354 | 5.6808 | 112.4588 | 100.914 | 117.1463 | 123.3627 | 5.3146 | 123.3765 | 118.0069 | -0.32501 | 123.3627 | 5.3146 | 118.0069 | 117.1463 | 123.3765 | -123.793 | -123.7518
6074.7188 | 123.6969 | -63.3591 | 60.0357 | -0.039444 | 0.024569 | 0.018113 | -0.002634 | -0.010034 | -0.0028967 | -0.005973 | -58.0307 | 59.9991 | -63.7436 | 57.7148 | 53.8239 | 54.6799 | 48.967 | 37.5366 | 60.0266 | -63.6566 | -0.38452 | -0.036622 | 5.3284 | 121.0739 | -6.2119 | -0.29755 | -0.009156 | 5.7129 | 112.3261 | 100.8957 | 117.1829 | 123.3582 | 5.3284 | 123.3856 | 118.0389 | -0.29755 | 123.3582 | 5.3284 | 118.0389 | 117.1829 | 123.3856 | -123.7793 | -123.6923
6075.7188 | 123.7335 | -63.3636 | 60.0266 | 0.03685 | 0.022219 | 0.017686 | -0.0030612 | -0.010888 | -0.0028967 | -0.0049048 | -58.0444 | 59.9899 | -63.739 | 57.6553 | 53.7781 | 54.6158 | 48.8892 | 37.4634 | 60.0037 | -63.7024 | -0.37537 | -0.036621 | 5.3192 | 121.019 | -6.2485 | -0.33875 | -0.022888 | 5.6946 | 112.2528 | 100.827 | 117.1417 | 123.3536 | 5.3192 | 123.3673 | 117.9794 | -0.33875 | 123.3536 | 5.3192 | 117.9794 | 117.1417 | 123.3673 | -123.7656 | -123.7289
6076.7188 | 123.7015 | -63.3636 | 59.9945 | 0.11314 | 0.023073 | 0.019395 | -0.0017796 | -0.0083248 | 0.00052127 | -0.0051184 | -57.9849 | 59.9625 | -63.7482 | 57.5775 | 53.7094 | 54.4922 | 48.7427 | 37.4451 | 59.9808 | -63.7024 | -0.38452 | -0.032044 | 5.3787 | 120.9412 | -6.2851 | -0.33875 | -0.013733 | 5.7632 | 112.1063 | 100.8087 | 117.0731 | 123.3261 | 5.3787 | 123.3444 | 117.8558 | -0.33875 | 123.3261 | 5.3787 | 117.8558 | 117.0731 | 123.3444 | -123.7427 | -123.6969
6077.7188 | 123.6923 | -63.382 | 60.0403 | -0.0012969 | 0.023501 | 0.017472 | -0.0051974 | -0.0085386 | -0.00054693 | -0.0061866 | -57.9895 | 60.0128 | -63.7253 | 57.5363 | 53.6957 | 54.4281 | 48.8937 | 37.5183 | 60.0449 | -63.6658 | -0.34332 | -0.027466 | 5.3925 | 120.9183 | -6.3446 | -0.28381 | 0.004578 | 5.7358 | 112.2757 | 100.9003 | 117.0776 | 123.3948 | 5.3925 | 123.4268 | 117.8101 | -0.28381 | 123.3948 | 5.3925 | 117.8101 | 117.0776 | 123.4268 | -123.7656 | -123.7061
6078.7344 | 123.7015 | -63.3591 | 60.0449 | -0.19966 | 0.021151 | 0.023454 | -0.0011386 | -0.010034 | -0.0024695 | -0.0051184 | -57.9071 | 60.0174 | -63.7115 | 57.5363 | 53.6362 | 54.3411 | 48.7198 | 37.4725 | 60.0403 | -63.6795 | -0.35248 | -0.027466 | 5.452 | 120.8954 | -6.4087 | -0.32043 | -0.004578 | 5.8044 | 112.0789 | 100.8316 | 116.9952 | 123.3765 | 5.452 | 123.3994 | 117.7002 | -0.32043 | 123.3765 | 5.452 | 117.7002 | 116.9952 | 123.3994 | -123.7564 | -123.7244
6079.7188 | 123.6786 | -63.4232 | 59.9854 | 0.2047 | 0.026064 | 0.019822 | 0.0033474 | -0.0055478 | -0.0018285 | -0.0049048 | -57.9254 | 60.0174 | -63.7436 | 57.3944 | 53.5538 | 54.2313 | 48.4634 | 37.262 | 59.9899 | -63.7711 | -0.32043 | 0.032043 | 5.4977 | 120.8176 | -6.4316 | -0.3479 | 0.004577 | 5.8182 | 111.8866 | 100.6851 | 116.9769 | 123.4406 | 5.4977 | 123.4131 | 117.6544 | -0.3479 | 123.4406 | 5.4977 | 117.6544 | 116.9769 | 123.4131 | -123.7289 | -123.7564
6080.7344 | 123.5916 | -63.3911 | 60.0037 | -0.19966 | 0.022219 | 0.019181 | -0.0019932 | -0.0081112 | -0.0018285 | -0.0029822 | -57.8979 | 59.9625 | -63.7665 | 57.4402 | 53.6407 | 54.2221 | 48.5825 | 37.8845 | 60.0311 | -63.6795 | -0.37537 | -0.041199 | 5.4932 | 120.8313 | -6.3629 | -0.28839 | 0.027466 | 5.8685 | 111.9736 | 101.2756 | 117.0319 | 123.3536 | 5.4932 | 123.4222 | 117.6132 | -0.28839 | 123.3536 | 5.4932 | 117.6132 | 117.0319 | 123.4222 | -123.7701 | -123.6832
6081.7188 | 123.7244 | -63.4186 | 59.9899 | 0.24284 | 0.021364 | 0.023881 | 0.0033474 | -0.006616 | -0.0031103 | -0.0034094 | -57.8888 | 59.9487 | -63.7573 | 57.1701 | 53.3981 | 54.2404 | 48.4406 | 37.3627 | 59.9716 | -63.7253 | -0.33874 | -0.041199 | 5.5298 | 120.5887 | -6.5918 | -0.3067 | -0.01831 | 5.8685 | 111.8591 | 100.7812 | 116.8167 | 123.3673 | 5.5298 | 123.3902 | 117.659 | -0.3067 | 123.3673 | 5.5298 | 117.659 | 116.8167 | 123.3902 | -123.7473 | -123.7152
6082.7188 | 123.7198 | -63.414 | 59.9716 | -0.09285 | 0.024782 | 0.015977 | -0.0039158 | -0.0089658 | -0.00011953 | -0.0044776 | -57.8888 | 59.967 | -63.7665 | 57.3303 | 53.5675 | 54.1351 | 48.5046 | 37.6328 | 59.9808 | -63.7344 | -0.35248 | -0.004578 | 5.5252 | 120.7443 | -6.4041 | -0.32044 | 0.009155 | 5.8777 | 111.9186 | 101.0468 | 116.9815 | 123.381 | 5.5252 | 123.3948 | 117.5491 | -0.32044 | 123.381 | 5.5252 | 117.5491 | 116.9815 | 123.3948 | -123.7381 | -123.7061
6083.7344 | 123.7061 | -63.446 | 59.9854 | 0.10551 | 0.024782 | 0.019822 | -0.0011386 | -0.0091794 | -0.00076053 | -0.0057592 | -57.9117 | 59.9716 | -63.7939 | 57.1976 | 53.4439 | 53.9978 | 48.4268 | 37.5229 | 59.9716 | -63.7344 | -0.3479 | -0.013733 | 5.5344 | 120.6436 | -6.5414 | -0.28839 | -0.013733 | 5.8823 | 111.8729 | 100.9689 | 116.89 | 123.4177 | 5.5344 | 123.4177 | 117.4438 | -0.28839 | 123.4177 | 5.5344 | 117.4438 | 116.89 | 123.4177 | -123.7793 | -123.7198
6084.7188 | 123.674 | -63.4506 | 59.9167 | 0.17418 | 0.024569 | 0.020463 | 0.0033474 | -0.006616 | -0.0014013 | -0.0040502 | -57.8201 | 59.967 | -63.7665 | 57.1381 | 53.4164 | 53.8742 | 48.2758 | 37.5961 | 59.9304 | -63.7527 | -0.31586 | 0.050354 | 5.6305 | 120.5887 | -6.5002 | -0.30212 | 0.013733 | 5.9463 | 111.7264 | 101.0468 | 116.8671 | 123.4177 | 5.6305 | 123.381 | 117.3248 | -0.30212 | 123.4177 | 5.6305 | 117.3248 | 116.8671 | 123.381 | -123.6832 | -123.6694
6085.7188 | 123.7015 | -63.4506 | 59.9396 | -0.1844 | 0.024355 | 0.02324 | 0.00078404 | -0.0078976 | -0.0018285 | -0.0049048 | -57.8567 | 59.9442 | -63.7848 | 57.0786 | 53.334 | 53.7964 | 48.2758 | 37.6511 | 59.935 | -63.7802 | -0.33417 | 0.004578 | 5.5939 | 120.5292 | -6.6055 | -0.32959 | -0.004577 | 5.928 | 111.7264 | 101.1017 | 116.7847 | 123.3948 | 5.5939 | 123.3856 | 117.247 | -0.32959 | 123.3948 | 5.5939 | 117.247 | 116.7847 | 123.3856 | -123.7244 | -123.7198
6086.7188 | 123.674 | -63.501 | 59.9533 | 0.15129 | 0.029269 | 0.024949 | 0.00527 | -0.006616 | -0.00076053 | -0.0044776 | -57.8384 | 60.0082 | -63.8306 | 56.9733 | 53.2104 | 53.6133 | 48.3444 | 37.619 | 59.967 | -63.8306 | -0.32959 | 0.054932 | 5.6625 | 120.4742 | -6.7429 | -0.32959 | 0.013733 | 5.9921 | 111.8454 | 101.12 | 116.7114 | 123.5092 | 5.6625 | 123.468 | 117.1143 | -0.32959 | 123.5092 | 5.6625 | 117.1143 | 116.7114 | 123.468 | -123.7839 | -123.7839
6087.7188 | 123.7289 | -63.4964 | 59.8984 | 0.1284 | 0.024355 | 0.021958 | 0.004202 | -0.0053342 | -0.0024695 | -0.0061866 | -57.7835 | 59.9396 | -63.8306 | 56.9778 | 53.2791 | 53.5629 | 48.23 | 37.7609 | 59.9304 | -63.8168 | -0.33417 | 0.041199 | 5.7129 | 120.4742 | -6.6193 | -0.32043 | 0.032044 | 6.0471 | 111.7264 | 101.2573 | 116.7755 | 123.436 | 5.7129 | 123.4268 | 117.0593 | -0.32043 | 123.436 | 5.7129 | 117.0593 | 116.7755 | 123.4268 | -123.7289 | -123.7152
6088.7344 | 123.6923 | -63.4781 | 59.9625 | -0.24544 | 0.023714 | 0.019822 | -0.00092496 | -0.0074704 | -0.0031103 | -0.004264 | -57.7744 | 59.9304 | -63.826 | 56.8909 | 53.2196 | 53.5034 | 48.4177 | 38.0173 | 59.9716 | -63.7802 | -0.3479 | -0.032043 | 5.7037 | 120.369 | -6.7429 | -0.30212 | 0.009156 | 6.0516 | 111.8958 | 101.4954 | 116.6977 | 123.4085 | 5.7037 | 123.4497 | 116.9815 | -0.30212 | 123.4085 | 5.7037 | 116.9815 | 116.6977 | 123.4497 | -123.7885 | -123.7427
6089.7188 | 123.6374 | -63.6475 | 59.8206 | 0.18181 | 0.025851 | 0.024735 | 0.0037746 | -0.0046932 | -0.00054693 | -0.0038366 | -57.9666 | 59.8434 | -64.0182 | 54.1443 | 53.0685 | 52.9083 | 51.7593 | 49.8001 | 59.8389 | -64.0182 | -0.37079 | 0.022888 | 5.6808 | 117.7917 | -6.752 | -0.37079 | 0.01831 | 6.0516 | 115.4068 | 113.4476 | 116.716 | 123.4909 | 5.6808 | 123.4863 | 116.5558 | -0.37079 | 123.4909 | 5.6808 | 116.5558 | 116.716 | 123.4863 | -123.8388 | -123.8388
6090.7344 | 123.6877 | -63.8443 | 59.5734 | -0.0089264 | 0.024782 | 0.022172 | -0.0017796 | -0.0081112 | -0.00033333 | -0.0040502 | -58.1543 | 59.5871 | -64.1693 | 57.8659 | 53.064 | 53.8834 | 55.4443 | 57.4585 | 59.6146 | -64.1556 | -0.32501 | 0.013733 | 5.69 | 121.7102 | -6.5094 | -0.31128 | 0.041199 | 6.015 | 119.2886 | 121.3028 | 116.9083 | 123.4314 | 5.69 | 123.4589 | 117.7277 | -0.31128 | 123.4314 | 5.69 | 117.7277 | 116.9083 | 123.4589 | -123.7427 | -123.7289
6091.7188 | 123.6511 | -63.7527 | 59.7519 | 0.31151 | 0.028414 | 0.028367 | 0.0029202 | -0.0027706 | -0.0014013 | -0.0040502 | -57.962 | 59.7748 | -64.0503 | 53.5995 | 52.6749 | 52.2675 | 52.8122 | 53.4714 | 59.7382 | -64.0732 | -0.29755 | 0.022888 | 5.7907 | 117.3523 | -7.077 | -0.32043 | -0.013733 | 6.0883 | 116.5649 | 117.2241 | 116.4276 | 123.5275 | 5.7907 | 123.4909 | 116.0202 | -0.32043 | 123.5275 | 5.7907 | 116.0202 | 116.4276 | 123.4909 | -123.8022 | -123.8251
6092.7188 | 123.7335 | -63.6978 | 59.6878 | 0.21233 | 0.028628 | 0.022386 | 0.0031338 | -0.0027706 | 9.4068e-05 | -0.005332 | -57.8567 | 59.7336 | -64.0503 | 53.7781 | 52.8214 | 52.4139 | 52.7298 | 53.6499 | 59.7244 | -64.032 | -0.35248 | 0.045777 | 5.8411 | 117.4759 | -6.8665 | -0.33417 | 0.036621 | 6.1935 | 116.4276 | 117.3477 | 116.5192 | 123.4314 | 5.8411 | 123.4222 | 116.1118 | -0.33417 | 123.4314 | 5.8411 | 116.1118 | 116.5192 | 123.4222 | -123.7381 | -123.7198
6093.7344 | 123.7564 | -63.7894 | 59.6146 | -0.08522 | 0.024782 | 0.02559 | -0.00092496 | -0.007684 | -0.00097413 | -0.0012732 | -57.9163 | 59.5871 | -64.1464 | 56.0211 | 52.8763 | 53.0045 | 53.8605 | 55.3665 | 59.6237 | -64.0961 | -0.35705 | -0.027466 | 5.8731 | 119.8105 | -6.7383 | -0.3067 | 0.009155 | 6.2302 | 117.6498 | 119.1559 | 116.6656 | 123.3765 | 5.8731 | 123.4131 | 116.7938 | -0.3067 | 123.3765 | 5.8731 | 116.7938 | 116.6656 | 123.4131 | -123.761 | -123.7106
6094.7188 | 123.6465 | -63.7573 | 59.729 | 0.1284 | 0.0282 | 0.022172 | 0.0067654 | -0.0036252 | -0.0014013 | -0.0031958 | -57.843 | 59.761 | -64.0961 | 53.6133 | 52.5787 | 52.1072 | 52.7023 | 53.5309 | 59.6924 | -64.0869 | -0.33875 | 0.032043 | 5.9143 | 117.3706 | -7.1503 | -0.32959 | -0.036621 | 6.2531 | 116.4597 | 117.2882 | 116.3361 | 123.5184 | 5.9143 | 123.4497 | 115.8646 | -0.32959 | 123.5184 | 5.9143 | 115.8646 | 116.3361 | 123.4497 | -123.8251 | -123.8159
6095.7188 | 123.7198 | -63.9587 | 59.4635 | 0.059738 | 0.024355 | 0.017259 | 0.00014304 | -0.0098202 | -0.00076053 | -0.0027686 | -58.0353 | 59.4452 | -64.3158 | 59.2026 | 52.8397 | 53.9474 | 56.1676 | 59.1476 | 59.4681 | -64.2792 | -0.35706 | -0.018311 | 5.9235 | 123.1613 | -6.6238 | -0.32043 | 0.004578 | 6.2805 | 120.1263 | 123.1064 | 116.7984 | 123.4039 | 5.9235 | 123.4268 | 117.9062 | -0.32043 | 123.4039 | 5.9235 | 117.9062 | 116.7984 | 123.4268 | -123.7793 | -123.7427
6096.7188 | 123.761 | -63.9496 | 59.4635 | 0.17418 | 0.027132 | 0.029435 | 0.0071926 | -0.006616 | 0.0013757 | -0.0023414 | -57.9117 | 59.4681 | -64.2975 | 59.2072 | 52.7115 | 53.7552 | 55.9158 | 59.111 | 59.4406 | -64.27 | -0.3479 | 0.004578 | 6.0379 | 123.1567 | -6.752 | -0.32044 | -0.022888 | 6.3858 | 119.8654 | 123.0606 | 116.6611 | 123.4177 | 6.0379 | 123.3902 | 117.7048 | -0.32044 | 123.4177 | 6.0379 | 117.7048 | 116.6611 | 123.3902 | -123.761 | -123.7335
6097.7188 | 123.642 | -64.0686 | 59.436 | 0.18181 | 0.028841 | 0.022386 | 0.008688 | -0.0096066 | 0.00073487 | -0.0040502 | -58.0307 | 59.491 | -64.4073 | 59.5322 | 52.7527 | 53.6591 | 56.25 | 59.3628 | 59.4681 | -64.3936 | -0.33875 | 0.054932 | 6.0379 | 123.6008 | -6.6833 | -0.32501 | 0.032044 | 6.3766 | 120.3186 | 123.4314 | 116.8213 | 123.5596 | 6.0379 | 123.5367 | 117.7277 | -0.32501 | 123.5596 | 6.0379 | 117.7277 | 116.8213 | 123.5367 | -123.8434 | -123.8297
6098.7344 | 123.6786 | -64.032 | 59.436 | -0.08522 | 0.027773 | 0.02794 | 0.0089016 | -0.0055478 | -0.0033239 | -0.0034094 | -57.8979 | 59.491 | -64.3753 | 59.5276 | 52.5238 | 53.5309 | 56.3919 | 59.4818 | 59.4452 | -64.3936 | -0.34332 | 0.054932 | 6.134 | 123.5596 | -6.9122 | -0.36163 | 0.009155 | 6.4774 | 120.4239 | 123.5138 | 116.5558 | 123.5229 | 6.134 | 123.4772 | 117.5629 | -0.36163 | 123.5229 | 6.134 | 117.5629 | 116.5558 | 123.4772 | -123.8113 | -123.8297
6099.7188 | 123.6374 | -64.0732 | 59.436 | 0.17418 | 0.030978 | 0.024095 | 0.0095424 | -0.0064022 | -0.00097413 | -0.0027686 | -57.9071 | 59.5093 | -64.3662 | 59.491 | 52.3361 | 53.4302 | 56.282 | 59.3903 | 59.436 | -64.3936 | -0.29297 | 0.073242 | 6.1661 | 123.5641 | -7.0999 | -0.32043 | 0 | 6.459 | 120.3552 | 123.4634 | 116.4093 | 123.5825 | 6.1661 | 123.5092 | 117.5034 | -0.32043 | 123.5825 | 6.1661 | 117.5034 | 116.4093 | 123.5092 | -123.8022 | -123.8297
6100.7344 | 123.7381 | -62.3428 | 61.1206 | -0.016556 | 0.026064 | 0.02794 | 0.016378 | -0.0085386 | 0.060763 | 0.078622 | -56.1768 | 61.1206 | -62.6678 | 61.2808 | -61.6333 | 15.6555 | 54.8676 | 61.2396 | 61.1755 | -62.5671 | -0.32501 | 0 | 6.1661 | 123.6237 | -122.7539 | -0.2243 | 0.054932 | 6.4911 | 117.2104 | 123.5825 | 0.70953 | 123.4634 | 6.1661 | 123.5184 | 77.9984 | -0.2243 | 123.4634 | 6.1661 | 77.9984 | 0.70953 | 123.5184 | -123.7885 | -123.6877
6101.7188 | 123.7152 | -62.3428 | 61.1114 | 0.2047 | 0.030978 | 0.022172 | 0.026205 | -0.0072568 | 0.061831 | 0.079904 | -56.1035 | 61.1572 | -62.6816 | 61.2442 | -62.1002 | 15.4953 | 54.6799 | 61.1755 | 61.1069 | -62.6633 | -0.33875 | 0.045777 | 6.2393 | 123.587 | -123.2117 | -0.32043 | -0.004577 | 6.5781 | 117.0227 | 123.5184 | 0.24261 | 123.5001 | 6.2393 | 123.4497 | 77.8381 | -0.32043 | 123.5001 | 6.2393 | 77.8381 | 0.24261 | 123.4497 | -123.793 | -123.7747
6102.7188 | 123.6649 | -62.2833 | 61.1618 | 0.14366 | 0.024782 | 0.023454 | 0.018515 | -0.0085386 | 0.062258 | 0.080758 | -56.0165 | 61.1481 | -62.6038 | 61.2991 | -61.9492 | 15.5365 | 54.5883 | 61.2534 | 61.1572 | -62.5946 | -0.32044 | -0.013733 | 6.2668 | 123.5825 | -123.111 | -0.31128 | -0.004577 | 6.5872 | 116.8716 | 123.5367 | 0.33417 | 123.4314 | 6.2668 | 123.4406 | 77.8198 | -0.31128 | 123.4314 | 6.2668 | 77.8198 | 0.33417 | 123.4406 | -123.7656 | -123.7564
6103.7188 | 123.6694 | -62.2879 | 61.1984 | 0.013962 | 0.032473 | 0.024095 | 0.025991 | -0.0083248 | 0.060763 | 0.07734 | -55.8792 | 61.2671 | -62.6083 | 61.3174 | -61.9949 | 15.4816 | 54.5105 | 61.2076 | 61.1938 | -62.6358 | -0.32043 | 0.068665 | 6.4087 | 123.6053 | -123.1934 | -0.3479 | -0.004577 | 6.7291 | 116.7984 | 123.4955 | 0.29297 | 123.555 | 6.4087 | 123.4818 | 77.7695 | -0.3479 | 123.555 | 6.4087 | 77.7695 | 0.29297 | 123.4818 | -123.8068 | -123.8342
6104.7188 | 123.6237 | -62.3108 | 61.2076 | 0.22758 | 0.030764 | 0.024522 | 0.024282 | -0.0074704 | 0.062685 | 0.079904 | -55.8609 | 61.2579 | -62.5946 | 61.2762 | -62.0499 | 15.4587 | 54.2679 | 61.171 | 61.203 | -62.6358 | -0.28381 | 0.050354 | 6.4499 | 123.587 | -123.2574 | -0.32501 | -0.004578 | 6.7337 | 116.5787 | 123.4818 | 0.26093 | 123.5687 | 6.4499 | 123.5138 | 77.7695 | -0.32501 | 123.5687 | 6.4499 | 77.7695 | 0.26093 | 123.5138 | -123.8022 | -123.8434
6105.7188 | 123.6328 | -62.2925 | 61.1938 | 1.5093 | 0.029909 | 0.018968 | 0.025778 | -0.0057614 | 0.064181 | 0.080331 | -55.6 | 61.2213 | -62.6358 | 61.2762 | -61.9354 | 15.5182 | 54.1351 | 61.1755 | 61.1847 | -62.6175 | -0.34332 | 0.027465 | 6.6925 | 123.5687 | -123.1293 | -0.32501 | -0.009156 | 7.0358 | 116.4276 | 123.468 | 0.35705 | 123.5138 | 6.6925 | 123.4772 | 77.8107 | -0.32501 | 123.5138 | 6.6925 | 77.8107 | 0.35705 | 123.4772 | -123.8297 | -123.8113
6106.7188 | 123.6191 | -62.265 | 61.2442 | 0.13603 | 0.029269 | 0.027299 | 0.026632 | -0.004266 | 0.062685 | 0.081613 | -55.6824 | 61.2808 | -62.59 | 61.2717 | -62.0178 | 15.4358 | 53.9383 | 61.171 | 61.2442 | -62.5946 | -0.32501 | 0.036621 | 6.5826 | 123.5367 | -123.262 | -0.32959 | 0 | 6.9077 | 116.2033 | 123.436 | 0.24719 | 123.5458 | 6.5826 | 123.5092 | 77.7008 | -0.32959 | 123.5458 | 6.5826 | 77.7008 | 0.24719 | 123.5092 | -123.8342 | -123.8388
6107.7188 | 123.5733 | -62.2238 | 61.2762 | 0.17418 | 0.031618 | 0.024308 | 0.027914 | -0.0074704 | 0.062045 | 0.083322 | -55.6 | 61.3129 | -62.5717 | 61.3174 | -61.8622 | 15.3351 | 53.3661 | 61.4868 | 61.2396 | -62.5763 | -0.3479 | 0.036621 | 6.6238 | 123.5413 | -123.1384 | -0.35248 | -0.036621 | 6.9717 | 115.5899 | 123.7106 | 0.36163 | 123.5367 | 6.6238 | 123.4634 | 77.5589 | -0.35248 | 123.5367 | 6.6238 | 77.5589 | 0.36163 | 123.4634 | -123.848 | -123.8525
6108.7188 | 123.7061 | -62.178 | 61.235 | 0.53276 | 0.029696 | 0.025376 | 0.024282 | -0.0055478 | 0.065463 | 0.081399 | -55.4214 | 61.29 | -62.5351 | 61.4273 | -61.9583 | 15.564 | 53.3752 | 61.3678 | 61.2625 | -62.4985 | -0.35705 | 0.054932 | 6.7566 | 123.6053 | -123.1934 | -0.32043 | 0.027466 | 7.1136 | 115.5533 | 123.5458 | 0.21973 | 123.468 | 6.7566 | 123.4406 | 77.742 | -0.32043 | 123.468 | 6.7566 | 77.742 | 0.21973 | 123.4406 | -123.7701 | -123.7335
6109.7188 | 123.6374 | -62.1552 | 61.2991 | 0.18944 | 0.031832 | 0.024949 | 0.025564 | -0.0061886 | 0.062045 | 0.082894 | -55.3162 | 61.3541 | -62.4939 | 61.4136 | -62.0087 | 15.3122 | 53.334 | 61.3266 | 61.3266 | -62.5031 | -0.33875 | 0.054932 | 6.839 | 123.5687 | -123.3078 | -0.3479 | 0.027466 | 7.1777 | 115.4892 | 123.4818 | 0.14648 | 123.5092 | 6.839 | 123.4818 | 77.4673 | -0.3479 | 123.5092 | 6.839 | 77.4673 | 0.14648 | 123.4818 | -123.793 | -123.8022
6110.7344 | 123.7289 | -62.1277 | 61.2808 | 0.16655 | 0.027987 | 0.027726 | 0.024496 | -0.0061886 | 0.061617 | 0.084176 | -55.1697 | 61.2625 | -62.4619 | 61.4685 | -61.9995 | 15.3122 | 54.1946 | 61.377 | 61.2946 | -62.4481 | -0.33417 | -0.018311 | 6.958 | 123.5962 | -123.2803 | -0.32043 | 0.013733 | 7.2922 | 116.3223 | 123.5046 | 0.12817 | 123.3902 | 6.958 | 123.4222 | 77.4399 | -0.32043 | 123.3902 | 6.958 | 77.4399 | 0.12817 | 123.4222 | -123.7427 | -123.7289
6111.7188 | 123.6465 | -62.178 | 61.3037 | 0.021591 | 0.033541 | 0.027085 | 0.028555 | -0.0078976 | 0.062685 | 0.085671 | -55.1285 | 61.3541 | -62.5076 | 61.3678 | -62.1552 | 15.0238 | 60.8459 | 61.2808 | 61.3174 | -62.5351 | -0.32959 | 0.050354 | 7.0496 | 123.5458 | -123.4589 | -0.35705 | 0.013733 | 7.3792 | 123.024 | 123.4589 | 0.022889 | 123.5321 | 7.0496 | 123.4955 | 77.2018 | -0.35705 | 123.5321 | 7.0496 | 77.2018 | 0.022889 | 123.4955 | -123.8113 | -123.8388
6112.7344 | 123.7198 | -62.1597 | 61.2305 | 0.16655 | 0.0282 | 0.029862 | 0.024923 | -0.0061886 | 0.060336 | 0.084603 | -55.0003 | 61.2213 | -62.5076 | 61.4227 | -62.0636 | 14.7034 | 60.8963 | 61.3907 | 61.2625 | -62.4573 | -0.3479 | -0.009156 | 7.1594 | 123.5825 | -123.2941 | -0.29755 | 0.032043 | 7.5073 | 123.056 | 123.5504 | 0.09613 | 123.381 | 7.1594 | 123.4222 | 76.8631 | -0.29755 | 123.381 | 7.1594 | 76.8631 | 0.09613 | 123.4222 | -123.7381 | -123.6877
6113.7188 | 123.6191 | -62.1414 | 61.3312 | 0.013962 | 0.0329 | 0.031999 | 0.032827 | -0.0051206 | 0.062045 | 0.084603 | -54.8447 | 61.3907 | -62.4619 | 61.4227 | -62.114 | 14.1449 | 61.1526 | 61.3266 | 61.3495 | -62.4756 | -0.32043 | 0.059509 | 7.2968 | 123.5641 | -123.4451 | -0.33417 | 0.01831 | 7.6172 | 123.2941 | 123.468 | 0.027465 | 123.5321 | 7.2968 | 123.4909 | 76.2863 | -0.33417 | 123.5321 | 7.2968 | 76.2863 | 0.027465 | 123.4909 | -123.793 | -123.8068
6114.7188 | 123.6191 | -62.1323 | 61.3358 | 0.082626 | 0.034823 | 0.031144 | 0.031118 | -0.0046932 | 0.064394 | 0.084817 | -54.7165 | 61.4182 | -62.4802 | 61.4044 | -62.1094 | 13.765 | 61.203 | 61.3266 | 61.377 | -62.4573 | -0.3479 | 0.082398 | 7.4158 | 123.5367 | -123.4451 | -0.32501 | 0.041199 | 7.7637 | 123.3353 | 123.4589 | 0.022888 | 123.5504 | 7.4158 | 123.5092 | 75.8972 | -0.32501 | 123.5504 | 7.4158 | 75.8972 | 0.022888 | 123.5092 | -123.8159 | -123.793
6115.7188 | 123.674 | -62.0911 | 61.3037 | 0.10551 | 0.0329 | 0.026231 | 0.021719 | -0.0053342 | 0.063113 | 0.086953 | -54.6204 | 61.3312 | -62.439 | 61.4731 | -62.0224 | 13.4766 | 61.1023 | 61.4227 | 61.3358 | -62.4115 | -0.3479 | 0.027466 | 7.4707 | 123.5641 | -123.3261 | -0.32043 | 0.032043 | 7.8186 | 123.1934 | 123.5138 | 0.068664 | 123.4222 | 7.4707 | 123.4268 | 75.5676 | -0.32043 | 123.4222 | 7.4707 | 75.5676 | 0.068664 | 123.4268 | -123.7427 | -123.7152
6116.7188 | 123.6694 | -61.9629 | 61.4868 | 0.059738 | 0.033541 | 0.029862 | 0.034323 | -0.0064022 | 0.062899 | 0.089517 | -54.2358 | 61.5646 | -62.3108 | 61.5875 | -61.9446 | 12.5015 | 61.2854 | 61.5051 | 61.5051 | -62.2971 | -0.3479 | 0.07782 | 7.7271 | 123.5504 | -123.4314 | -0.33417 | 0.018311 | 8.075 | 123.2483 | 123.468 | 0.018311 | 123.5275 | 7.7271 | 123.468 | 74.4644 | -0.33417 | 123.5275 | 7.7271 | 74.4644 | 0.018311 | 123.468 | -123.7976 | -123.7839
6117.7188 | 123.6465 | -61.8256 | 61.6562 | 0.3344 | 0.034182 | 0.029435 | 0.029623 | -0.0061886 | 0.064608 | 0.088235 | -53.7598 | 61.734 | -62.1414 | 61.7477 | -61.7981 | 12.0666 | 61.4685 | 61.6608 | 61.702 | -62.1368 | -0.31586 | 0.07782 | 8.0658 | 123.5733 | -123.4543 | -0.31128 | 0.045776 | 8.3817 | 123.2941 | 123.4863 | 0.027466 | 123.5596 | 8.0658 | 123.5275 | 73.8922 | -0.31128 | 123.5596 | 8.0658 | 73.8922 | 0.027466 | 123.5275 | -123.7976 | -123.793
6118.7188 | 123.6282 | -61.7752 | 61.7203 | -0.0089264 | 0.041231 | 0.033067 | 0.037313 | -0.0036252 | 0.062258 | 0.087808 | -48.8022 | 61.8301 | -62.0407 | 61.9812 | -61.647 | 10.7117 | 61.4914 | 61.5417 | 61.734 | -62.1552 | -0.2655 | 0.10986 | 12.973 | 123.7564 | -123.3673 | -0.37994 | 0.013733 | 13.2385 | 123.2666 | 123.317 | 0.12817 | 123.6053 | 12.973 | 123.5092 | 72.4869 | -0.37994 | 123.6053 | 12.973 | 72.4869 | 0.12817 | 123.5092 | -123.761 | -123.8754
6119.7188 | 123.6374 | -58.0124 | 57.1472 | -0.0089264 | 1.1512 | 1.1398 | 0.083242 | -0.0023434 | 0.063967 | 0.13886 | 56.163 | 57.0282 | -64.151 | 54.5334 | -66.3254 | 64.7461 | 56.8405 | 57.106 | 57.0511 | -54.7165 | -6.1386 | -0.11902 | 114.1754 | 112.5458 | -123.4726 | 3.2959 | -0.096131 | 120.314 | 114.8529 | 115.1184 | -8.313 | 115.0406 | 114.1754 | 115.0635 | 122.7585 | 3.2959 | 115.0406 | 114.1754 | 122.7585 | -8.313 | 115.0635 | -121.2982 | -111.8637
6120.7344 | 123.6053 | -65.3412 | 57.962 | 0.074997 | 1.2288 | 1.2424 | 0.035605 | -0.0072568 | 0.063754 | 0.10169 | 57.1609 | 57.8522 | -65.6021 | 58.0994 | -65.3 | -65.506 | 57.7194 | 58.0627 | 57.9803 | -65.6342 | -0.26093 | -0.10986 | 122.5021 | 123.4406 | -123.262 | -0.29297 | 0.018311 | 122.7631 | 123.0606 | 123.4039 | 0.041199 | 123.1934 | 122.5021 | 123.3215 | -0.16479 | -0.29297 | 123.1934 | 122.5021 | -0.16479 | 0.041199 | 123.3215 | -123.5641 | -123.5962
6121.7188 | 123.4863 | -65.7578 | 57.5409 | -0.024185 | 1.7771 | 1.804 | 0.049917 | -0.0070432 | 0.06354 | 0.099343 | 56.7123 | 57.4539 | -65.9271 | 57.6187 | -65.712 | -65.9775 | 57.3395 | 57.5729 | 57.55 | -66.1102 | -0.16937 | -0.086976 | 122.4701 | 123.3765 | -123.2529 | -0.35248 | 0.009155 | 122.6395 | 123.0972 | 123.3307 | 0.045776 | 123.2117 | 122.4701 | 123.3078 | -0.21973 | -0.35248 | 123.2117 | 122.4701 | -0.21973 | 0.045776 | 123.3078 | -123.468 | -123.6511
6122.7188 | 123.5046 | -65.6799 | 57.605 | 0.31151 | 1.5624 | 1.5534 | 0.052694 | -0.0055478 | 0.062472 | 0.11494 | 57.2296 | 57.55 | -65.9134 | 57.6736 | -65.6113 | -65.8356 | 57.3761 | 57.6141 | 57.6187 | -66.0187 | -0.23346 | -0.054931 | 122.9095 | 123.3536 | -123.2162 | -0.33875 | 0.013733 | 123.143 | 123.056 | 123.2941 | 0.068665 | 123.23 | 122.9095 | 123.2986 | -0.15564 | -0.33875 | 123.23 | 122.9095 | -0.15564 | 0.068665 | 123.2986 | -123.5184 | -123.6237
6123.7188 | 123.436 | -66.0553 | 57.3166 | 0.03685 | 0.054476 | 0.047166 | 0.058249 | -0.0068296 | 0.06354 | 0.10981 | 57.2159 | 57.3578 | -66.3986 | 57.431 | -66.0141 | -66.2796 | 57.1793 | 57.2891 | 57.3944 | -66.3666 | -0.34332 | 0.041199 | 123.2712 | 123.4863 | -123.3307 | -0.31128 | 0.07782 | 123.6145 | 123.2346 | 123.3444 | 0.041199 | 123.4131 | 123.2712 | 123.4497 | -0.2243 | -0.31128 | 123.4131 | 123.2712 | -0.2243 | 0.041199 | 123.4497 | -123.7152 | -123.6832
6124.7188 | 123.5001 | -66.2659 | 57.1564 | 0.1284 | 0.054262 | 0.047807 | 0.047354 | -0.0053342 | 0.064394 | 0.10447 | 57.0145 | 57.1747 | -66.5909 | 57.1426 | -66.2704 | -66.5268 | 56.9229 | 57.0831 | 57.1747 | -66.5817 | -0.32501 | 0.018311 | 123.2803 | 123.4085 | -123.4268 | -0.31586 | 0.018311 | 123.6053 | 123.1888 | 123.349 | -0.004578 | 123.4406 | 123.2803 | 123.4406 | -0.26093 | -0.31586 | 123.4406 | 123.2803 | -0.26093 | -0.004578 | 123.4406 | -123.7473 | -123.7381
6125.7344 | 123.5733 | -66.4215 | 56.9092 | 1.1584 | 0.051913 | 0.044389 | 0.10781 | -0.0044796 | 0.063113 | 0.17133 | 56.9641 | 56.8726 | -66.7786 | 57.0648 | -66.3254 | -66.6046 | 56.6116 | 57.0236 | 56.9321 | -66.7236 | -0.35706 | -0.036621 | 123.3856 | 123.4863 | -123.2346 | -0.30212 | 0.022888 | 123.7427 | 123.0331 | 123.4451 | 0.096131 | 123.2941 | 123.3856 | 123.3536 | -0.1831 | -0.30212 | 123.2941 | 123.3856 | -0.1831 | 0.096131 | 123.3536 | -123.6877 | -123.6328
6126.7188 | 123.4909 | -66.7419 | 56.7032 | 0.013962 | 0.054262 | 0.04802 | 0.048636 | -0.0085386 | 0.063967 | 0.10618 | 56.6162 | 56.7535 | -67.0303 | 56.7307 | -66.7511 | -66.9846 | 56.6116 | 56.6528 | 56.7444 | -67.0258 | -0.28839 | 0.050354 | 123.3582 | 123.4726 | -123.4543 | -0.28381 | 0.041199 | 123.6465 | 123.3536 | 123.3948 | -0.009156 | 123.4955 | 123.3582 | 123.4863 | -0.24262 | -0.28381 | 123.4955 | 123.3582 | -0.24262 | -0.009156 | 123.4863 | -123.7335 | -123.7289
6127.7188 | 123.5321 | -66.6412 | 56.7581 | 0.067368 | 0.05704 | 0.052506 | 0.051626 | -0.0053342 | 0.063967 | 0.10746 | 56.694 | 56.8451 | -66.9571 | 56.7902 | -66.6733 | -66.925 | 56.7078 | 56.7307 | 56.8222 | -66.9891 | -0.31586 | 0.086975 | 123.3353 | 123.4314 | -123.4314 | -0.3479 | 0.064087 | 123.6511 | 123.349 | 123.3719 | -0.032044 | 123.4863 | 123.3353 | 123.4634 | -0.28381 | -0.3479 | 123.4863 | 123.3353 | -0.28381 | -0.032044 | 123.4634 | -123.7152 | -123.7473
6128.7188 | 123.5825 | -66.9067 | 56.4697 | 0.1284 | 0.055758 | 0.048448 | 0.050344 | -0.0051206 | 0.064181 | 0.10874 | 56.4743 | 56.5567 | -67.2043 | 56.5979 | -66.8701 | -67.1173 | 56.3553 | 56.5292 | 56.5338 | -67.2043 | -0.29755 | 0.086975 | 123.381 | 123.5046 | -123.3398 | -0.29755 | 0.064086 | 123.6786 | 123.262 | 123.436 | 0.036621 | 123.4634 | 123.381 | 123.4406 | -0.21057 | -0.29755 | 123.4634 | 123.381 | -0.21057 | 0.036621 | 123.4406 | -123.674 | -123.674
6129.7188 | 123.5321 | -67.5064 | 55.9067 | 0.1284 | 0.05469 | 0.050797 | 0.060171 | -0.0068296 | 0.062685 | 0.11259 | 55.8334 | 55.9845 | -67.8406 | 55.957 | -67.5156 | -67.7582 | 55.8426 | 55.8929 | 55.957 | -67.836 | -0.33417 | 0.07782 | 123.3398 | 123.4634 | -123.4222 | -0.32959 | 0.050354 | 123.674 | 123.349 | 123.3994 | -0.009155 | 123.4909 | 123.3398 | 123.4634 | -0.25177 | -0.32959 | 123.4909 | 123.3398 | -0.25177 | -0.009155 | 123.4634 | -123.7473 | -123.7427
6130.7344 | 123.5825 | -67.6254 | 55.7053 | 0.12077 | 0.052126 | 0.047593 | 0.049063 | -0.0083248 | 0.06354 | 0.11259 | 55.7098 | 55.7007 | -67.9962 | 55.8838 | -67.5476 | -67.8085 | 55.5359 | 55.8151 | 55.7327 | -67.9276 | -0.37079 | -0.004577 | 123.3353 | 123.5092 | -123.2529 | -0.30212 | 0.027466 | 123.7061 | 123.1613 | 123.4406 | 0.07782 | 123.3261 | 123.3353 | 123.3582 | -0.18311 | -0.30212 | 123.3261 | 123.3353 | -0.18311 | 0.07782 | 123.3582 | -123.7015 | -123.6328
6131.7188 | 123.5962 | -68.0557 | 55.3253 | -0.016556 | 0.058321 | 0.052506 | 0.054403 | -0.0085386 | 0.06119 | 0.11109 | 55.2658 | 55.3574 | -68.4402 | 55.4077 | -68.074 | -68.3441 | 55.2292 | 55.3619 | 55.3207 | -68.4402 | -0.38452 | 0.032044 | 123.3215 | 123.4634 | -123.3994 | -0.38452 | -0.004577 | 123.7061 | 123.2849 | 123.4177 | -0.018311 | 123.4131 | 123.3215 | 123.3765 | -0.28839 | -0.38452 | 123.4131 | 123.3215 | -0.28839 | -0.018311 | 123.3765 | -123.7656 | -123.7656
6132.7188 | 122.8821 | -68.7241 | 53.952 | 0.19707 | 0.054262 | 0.04802 | 0.067648 | -0.005975 | 0.060977 | 0.13459 | 53.9749 | 54.0207 | -69.0262 | 54.0161 | -67.7124 | -67.7994 | 53.7781 | 54.0619 | 53.9612 | -69.0262 | -0.30212 | 0.068665 | 122.699 | 122.7402 | -121.6644 | -0.30212 | 0.009156 | 123.0011 | 122.5021 | 122.7859 | 1.0117 | 122.7448 | 122.699 | 122.6852 | 0.92468 | -0.30212 | 122.7448 | 122.699 | 0.92468 | 1.0117 | 122.6852 | -122.9782 | -122.9782
6133.7188 | 123.23 | -69.5755 | 53.4668 | 0.12077 | 0.055971 | 0.044175 | 0.21248 | -0.0057614 | 0.064608 | 0.27345 | 53.4439 | 53.0777 | -70.1431 | 53.4164 | -69.1635 | -44.3939 | 53.3661 | 53.4851 | 53.4714 | -69.8868 | -0.56763 | -0.3891 | 123.0194 | 122.9919 | -122.6303 | -0.31128 | 0.004578 | 123.587 | 122.9416 | 123.0606 | 0.41199 | 122.6532 | 123.0194 | 123.0469 | 25.1816 | -0.31128 | 122.6532 | 123.0194 | 25.1816 | 0.41199 | 123.0469 | -123.6099 | -123.3536
6134.7188 | 123.1888 | -69.6304 | 53.4485 | 0.12077 | 0.059603 | 0.048875 | 0.16057 | -0.0053342 | 0.062472 | 0.21342 | 53.3752 | 53.5538 | -69.9692 | 53.2288 | -69.4839 | -68.4082 | 53.4164 | 53.4256 | 53.508 | -69.9738 | -0.33875 | 0.10529 | 123.0057 | 122.8592 | -122.9324 | -0.34332 | 0.05951 | 123.3444 | 123.0469 | 123.056 | 0.14648 | 123.1842 | 123.0057 | 123.1384 | 1.2222 | -0.34332 | 123.1842 | 123.0057 | 1.2222 | 0.14648 | 123.1384 | -123.4177 | -123.4222
6135.7188 | 123.5321 | -73.8556 | 49.3011 | 0.15129 | 0.056826 | 0.047807 | 0.1123 | -0.0057614 | -0.0014013 | 0.054055 | 49.3378 | 49.3195 | -74.1211 | 49.4293 | 46.994 | 47.5067 | 49.1272 | 49.4751 | 49.3286 | -74.0707 | -0.2655 | 0.018311 | 123.1934 | 123.2849 | -2.3071 | -0.21515 | 0.027466 | 123.4589 | 122.9828 | 123.3307 | 120.8496 | 123.175 | 123.1934 | 123.1842 | 121.3623 | -0.21515 | 123.175 | 123.1934 | 121.3623 | 120.8496 | 123.1842 | -123.4222 | -123.3719
6136.7188 | 123.3627 | -67.6117 | 55.513 | 0.15892 | 0.0017111 | -0.0075216 | 0.21334 | -0.0051206 | 0.0018031 | 0.22581 | 0.23804 | 0.35248 | -0.1831 | 55.513 | 37.468 | 52.1622 | 55.2933 | 55.6137 | 55.481 | -67.9276 | 67.4286 | -55.1605 | 67.8497 | 123.1247 | -18.045 | -0.31586 | -0.032043 | 0.42114 | 122.905 | 123.2254 | 105.0797 | 67.9642 | 67.8497 | 123.0927 | 119.7739 | -0.31586 | 67.9642 | 67.8497 | 119.7739 | 105.0797 | 123.0927 | -55.6961 | -123.4406
6137.7188 | 123.4772 | -68.1519 | 54.9866 | 0.10551 | 0.0014975 | -0.012008 | 0.033041 | -0.0072568 | -0.0037511 | 0.025002 | 0.20599 | 0.31128 | -0.23804 | 55.1422 | 53.9749 | 54.6616 | 54.8035 | 55.1147 | 54.9911 | -68.4402 | 67.9138 | -54.6753 | 68.3578 | 123.2941 | -1.0117 | -0.28839 | 0.004578 | 0.44403 | 122.9553 | 123.2666 | 122.1268 | 68.4631 | 68.3578 | 123.143 | 122.8134 | -0.28839 | 68.4631 | 68.3578 | 122.8134 | 122.1268 | 123.143 | -55.2246 | -123.4268
6138.7188 | 123.2162 | -68.1793 | 54.9042 | -0.65742 | 0.0032065 | -0.012435 | 0.026419 | -0.0061886 | -0.0033239 | 0.01603 | 0.16937 | 0.3891 | -0.21515 | 54.9728 | 51.091 | 54.0665 | 54.8721 | 54.9454 | 54.9454 | -68.4998 | 67.9642 | -54.5151 | 68.3487 | 123.1522 | -3.8132 | -0.32044 | 0.041199 | 0.38452 | 123.0515 | 123.1247 | 119.2703 | 68.5684 | 68.3487 | 123.1247 | 122.2458 | -0.32044 | 68.5684 | 68.3487 | 122.2458 | 119.2703 | 123.1247 | -55.1193 | -123.4039
6139.7188 | 123.7152 | -68.4677 | 54.6341 | 0.029221 | 0.0040609 | -0.010085 | 0.030691 | -0.0068296 | -0.0024695 | 0.023293 | 0.10986 | 0.34332 | -0.26093 | 54.6661 | 40.4984 | 54.1992 | 54.6295 | 54.6021 | 54.6844 | -66.8015 | 68.2068 | -54.2908 | 68.5776 | 123.1338 | -14.1357 | 1.6663 | 0.050354 | 0.37079 | 123.0972 | 123.0698 | 108.9661 | 68.811 | 68.5776 | 123.1522 | 122.6669 | 1.6663 | 68.811 | 68.5776 | 122.6669 | 108.9661 | 123.1522 | -54.895 | -121.4355
6140.7188 | 123.3353 | -66.655 | 56.4423 | 0.13603 | 0.0012839 | -0.004531 | 0.5013 | -0.0055478 | 0.05884 | 0.53428 | -0.027466 | 0.32959 | -0.27466 | 56.1035 | -63.5834 | 51.4801 | 56.2958 | 56.3873 | 56.4651 | -66.9342 | 66.3803 | -56.1127 | 66.6275 | 122.7585 | -120.0256 | -0.27924 | 0.022888 | 0.24719 | 122.9507 | 123.0423 | 3.0716 | 66.9846 | 66.6275 | 123.1201 | 118.1351 | -0.27924 | 66.9846 | 66.6275 | 118.1351 | 3.0716 | 123.1201 | -56.7169 | -123.3765
6141.7188 | 116.9174 | -60.6949 | 56.0623 | 0.15892 | 0.0051291 | -0.010512 | 6.9213 | -0.0046932 | 0.0090663 | 6.9985 | 0.11902 | 0.35248 | -0.27008 | 19.574 | 6.8802 | 14.74 | 19.8761 | 17.2943 | 35.6415 | -40.8417 | 60.4248 | -55.7098 | 60.8139 | 80.2689 | -49.1821 | 19.8532 | -20.4208 | 0.3891 | 80.571 | 77.9892 | 67.5751 | 61.0474 | 60.8139 | 96.3364 | 75.4349 | 19.8532 | 61.0474 | 60.8139 | 75.4349 | 67.5751 | 96.3364 | -56.3324 | -96.904
6142.7344 | 122.438 | -67.3508 | 54.9316 | 0.1284 | -0.0014933 | -0.010299 | 0.77111 | 0.0021426 | 0.0015893 | 0.77375 | 0.11444 | 0.32044 | -0.21515 | 43.84 | 42.2012 | 44.4992 | 43.6432 | 42.9794 | 54.8355 | -67.6804 | 67.1356 | -54.6112 | 67.4652 | 111.1908 | -12.7304 | -0.32959 | -0.096131 | 0.32959 | 110.994 | 110.3302 | 109.552 | 67.6712 | 67.4652 | 122.1863 | 111.85 | -0.32959 | 67.6712 | 67.4652 | 111.85 | 109.552 | 122.1863 | -55.1468 | -122.612
6143.7188 | 122.6028 | -67.8268 | 54.5975 | 0.090256 | 0.0019247 | -0.01158 | 1.137 | -0.0006344 | 0.0011621 | 1.1549 | 0.11902 | 0.37537 | -0.1831 | 44.1467 | 44.2429 | 44.8425 | 44.1879 | 43.0847 | 54.6204 | -67.9688 | 67.6437 | -54.2221 | 67.9459 | 111.9736 | -10.3546 | -0.14191 | 0.022888 | 0.30212 | 112.0148 | 110.9116 | 112.0697 | 68.2022 | 67.9459 | 122.4472 | 112.6694 | -0.14191 | 68.2022 | 67.9459 | 112.6694 | 112.0697 | 122.4472 | -54.7806 | -122.5662
6144.7188 | 115.5716 | -57.9071 | 57.5272 | 1.2194 | 0.0014975 | -0.010085 | 6.9213 | 0.0059878 | 0.0082117 | 6.9985 | 0.064087 | 0.32501 | -0.26093 | 2.9297 | 3.5706 | 3.2501 | 2.7969 | 2.1698 | 34.1629 | -34.9411 | 57.6462 | -57.2021 | 57.9712 | 60.8368 | -53.9566 | 22.966 | -23.3643 | 0.32501 | 60.704 | 60.0769 | 61.4777 | 58.2321 | 57.9712 | 92.07 | 61.1572 | 22.966 | 58.2321 | 57.9712 | 61.1572 | 61.4777 | 92.07 | -57.7881 | -92.4683
6145.7344 | 122.612 | -65.1352 | 57.0282 | 0.18181 | -0.00021146 | -0.01094 | 0.0080472 | 0.0091922 | 0.010134 | 0.027993 | 0.16022 | 0.3067 | -0.21515 | 29.0588 | 29.1321 | 29.2511 | 29.1046 | 29.5166 | 56.6025 | -65.8035 | 64.92 | -56.7215 | 65.2954 | 94.194 | -27.8961 | -0.66833 | -0.42572 | 0.37537 | 94.2398 | 94.6518 | 94.2673 | 65.4419 | 65.2954 | 121.7377 | 94.3863 | -0.66833 | 65.4419 | 65.2954 | 94.3863 | 94.2673 | 121.7377 | -57.2433 | -122.8317
6146.7188 | 122.5525 | -52.9266 | 69.4702 | 0.082626 | 0.0040609 | -0.011153 | 0.025991 | 0.051917 | 0.054568 | 0.13993 | 0.054932 | 0.30212 | -0.31128 | -37.6007 | -37.2894 | -37.6831 | -37.5778 | -37.5458 | 69.4839 | -53.2425 | 52.6154 | -69.1681 | 52.9816 | 15.3259 | -106.7596 | -0.31586 | 0.013733 | 0.36621 | 15.3488 | 15.3809 | 15.6372 | 53.2288 | 52.9816 | 122.4106 | 15.2435 | -0.31586 | 53.2288 | 52.9816 | 15.2435 | 15.6372 | 122.4106 | -69.7815 | -122.7127
6147.7188 | 122.5571 | -51.5625 | 70.871 | 0.10551 | 0.0019247 | -0.0081626 | 0.11165 | 0.056403 | 0.055636 | 0.23692 | 0.045776 | 0.30212 | -0.31586 | -42.7002 | -42.2104 | -42.7917 | -42.7094 | -42.6682 | 70.8481 | -51.8738 | 51.2466 | -70.5688 | 51.6083 | 8.8623 | -113.0814 | -0.31128 | -0.022889 | 0.36163 | 8.8531 | 8.8943 | 9.3521 | 51.8646 | 51.6083 | 122.4106 | 8.7708 | -0.31128 | 51.8646 | 51.6083 | 8.7708 | 9.3521 | 122.4106 | -71.1868 | -122.7448
6148.7188 | 122.4655 | -51.3336 | 71.0953 | 0.21233 | 0.0044881 | -0.0083762 | 0.10888 | 0.058112 | 0.057131 | 0.20359 | 0.050354 | 0.31586 | -0.3067 | -42.9337 | -42.2104 | -42.952 | -42.8879 | -42.8513 | 71.1182 | -51.6449 | 51.0269 | -70.7794 | 51.384 | 8.4 | -113.3057 | -0.31128 | 0.022888 | 0.35706 | 8.4457 | 8.4824 | 9.1232 | 51.6495 | 51.384 | 122.4518 | 8.3817 | -0.31128 | 51.6495 | 51.384 | 8.3817 | 9.1232 | 122.4518 | -71.402 | -122.7402
6149.7344 | 122.7219 | -50.7477 | 71.64 | -0.10811 | -0.0012797 | -0.012862 | 0.16677 | 0.056189 | 0.057345 | 0.30207 | -0.004578 | 0.31128 | -0.2243 | -43.7393 | -43.0115 | -43.602 | -43.7027 | -43.2129 | 71.6583 | -50.9903 | 50.5234 | -71.3287 | 50.7431 | 7.0084 | -114.6515 | -0.24261 | 0.01831 | 0.21973 | 7.045 | 7.5348 | 7.7362 | 51.059 | 50.7431 | 122.406 | 7.1457 | -0.24261 | 51.059 | 50.7431 | 7.1457 | 7.7362 | 122.406 | -71.8643 | -122.6303
6150.7344 | 122.6944 | -50.3082 | 72.1024 | -0.0012969 | -0.0029887 | -0.010085 | 0.56325 | 0.053626 | 0.057345 | 0.67634 | 0.054932 | 0.25635 | -0.26093 | -43.9133 | -43.3502 | -43.9682 | -44.0643 | -43.8171 | 72.0245 | -50.5829 | 50.0473 | -71.846 | 50.3632 | 6.395 | -115.4526 | -0.27466 | -0.07782 | 0.31586 | 6.2439 | 6.4911 | 6.958 | 50.5646 | 50.3632 | 122.3328 | 6.34 | -0.27466 | 50.5646 | 50.3632 | 6.34 | 6.958 | 122.3328 | -72.3633 | -122.6852
6151.7188 | 122.6532 | -49.6353 | 72.8394 | -0.062332 | 0.0021383 | -0.010726 | 0.10097 | 0.056617 | 0.062685 | 0.20017 | 0.12817 | 0.31586 | -0.25635 | -45.5566 | -44.9982 | -45.5109 | -45.5246 | -45.4422 | 72.8165 | -49.9649 | 49.379 | -72.5235 | 49.7635 | 4.0787 | -117.8375 | -0.32959 | -0.022888 | 0.38452 | 4.1107 | 4.1931 | 4.6371 | 49.9512 | 49.7635 | 122.4518 | 4.1245 | -0.32959 | 49.9512 | 49.7635 | 4.1245 | 4.6371 | 122.4518 | -73.0957 | -122.8043
6152.7188 | 122.7173 | -49.3011 | 73.2285 | 0.22758 | 0.0014975 | -0.013076 | 0.13473 | 0.060889 | 0.060977 | 0.25144 | 0.082397 | 0.31128 | -0.28381 | -45.5566 | -44.9203 | -45.5154 | -45.6161 | -45.3644 | 73.2147 | -49.5758 | 49.0173 | -72.9172 | 49.3835 | 3.7445 | -118.1488 | -0.27466 | -0.013733 | 0.36621 | 3.685 | 3.9368 | 4.3808 | 49.6124 | 49.3835 | 122.5159 | 3.7857 | -0.27466 | 49.6124 | 49.3835 | 3.7857 | 4.3808 | 122.5159 | -73.5123 | -122.8043
6153.7188 | 122.0764 | -50.5325 | 71.4203 | -0.08522 | 0.0047019 | -0.013503 | 0.055685 | 0.055548 | 0.05649 | 0.16428 | 0.15106 | 0.36621 | -0.23346 | -39.7202 | -39.7751 | -39.6973 | -39.1067 | -38.9832 | 71.5118 | -50.5005 | 50.2991 | -71.0541 | 50.6836 | 10.8124 | -111.1954 | 0.032044 | 0.091553 | 0.38452 | 11.4258 | 11.5494 | 10.7574 | 50.8987 | 50.6836 | 122.0444 | 10.8353 | 0.032044 | 50.8987 | 50.6836 | 10.8353 | 10.7574 | 122.0444 | -71.6537 | -121.9208
6154.7344 | 122.3648 | -49.2004 | 72.9309 | -0.016556 | 0.00042934 | -0.014144 | 0.018728 | 0.059607 | 0.060977 | 0.14954 | 0.086975 | 0.29755 | -0.23804 | -44.2291 | -44.458 | -44.3848 | -44.2841 | -43.927 | 72.9126 | -49.4934 | 48.9624 | -72.6334 | 49.2874 | 4.9713 | -117.3889 | -0.29297 | -0.01831 | 0.32501 | 4.9164 | 5.2734 | 4.7424 | 49.498 | 49.2874 | 122.113 | 4.8157 | -0.29297 | 49.498 | 49.2874 | 4.8157 | 4.7424 | 122.113 | -73.1689 | -122.4243
6155.7188 | 122.4609 | -49.2691 | 72.8989 | 0.18944 | 0.0029929 | -0.01094 | 0.28084 | 0.055121 | 0.060549 | 0.40119 | 0.091553 | 0.31586 | -0.27924 | -42.7185 | -43.3823 | -42.8879 | -42.7872 | -42.4667 | 72.9034 | -49.5758 | 48.9899 | -72.583 | 49.3607 | 6.5506 | -116.2811 | -0.3067 | 0.004577 | 0.37079 | 6.4819 | 6.8024 | 5.8868 | 49.585 | 49.3607 | 122.1725 | 6.3812 | -0.3067 | 49.585 | 49.3607 | 6.3812 | 5.8868 | 122.1725 | -73.1781 | -122.4747
6156.7188 | 122.2412 | -48.0881 | 74.1531 | 0.13603 | 0.0036337 | -0.0079488 | 0.14541 | 0.058539 | 0.061831 | 0.28391 | 0.013733 | 0.33875 | -0.27466 | -45.0851 | -45.401 | -45.3827 | -45.3964 | -45.4697 | 74.1806 | -48.381 | 47.8134 | -73.8144 | 48.1018 | 3.0029 | -119.5541 | -0.29297 | 0.027466 | 0.28839 | 2.6917 | 2.6184 | 2.6871 | 48.4268 | 48.1018 | 122.2687 | 2.7054 | -0.29297 | 48.4268 | 48.1018 | 2.7054 | 2.6871 | 122.2687 | -74.4278 | -122.5342
6157.7188 | 122.2229 | -74.1669 | 47.7219 | -0.19966 | 0.00042934 | -0.0098714 | 0.20244 | -0.0068296 | -0.0037511 | 0.17902 | 0.14191 | 0.29755 | -0.23804 | 47.0032 | 46.9116 | 46.9299 | 46.756 | 47.0169 | 47.7539 | -74.5148 | 73.9288 | -47.4243 | 74.3088 | 121.17 | -0.81024 | -0.3479 | 0.032043 | 0.37994 | 120.9229 | 121.1838 | 121.0785 | 74.4644 | 74.3088 | 121.9208 | 121.0968 | -0.3479 | 74.4644 | 74.3088 | 121.0968 | 121.0785 | 121.9208 | -47.9599 | -122.2366
6158.7188 | 122.4472 | -74.6109 | 47.4564 | 0.18944 | 0.0021383 | -0.0085898 | 0.026632 | -0.0061886 | -0.0037511 | 0.07264 | 0.19226 | 0.29755 | -0.20142 | 46.4813 | 46.3348 | 46.3943 | 46.1472 | 46.4813 | 47.4838 | -74.9222 | 74.4095 | -47.1588 | 74.8032 | 121.0922 | -1.1215 | -0.31128 | 0.027466 | 0.39368 | 120.7581 | 121.0922 | 120.9457 | 74.9084 | 74.8032 | 122.0947 | 121.0052 | -0.31128 | 74.9084 | 74.8032 | 121.0052 | 120.9457 | 122.0947 | -47.6578 | -122.3785
6159.7344 | 122.3511 | -74.6841 | 47.3831 | 0.18944 | 0.00042934 | -0.0081626 | 0.20266 | -0.0044796 | -0.0039649 | 0.21043 | 0.17395 | 0.30212 | -0.23346 | 46.2524 | 46.0739 | 46.1563 | 45.9045 | 46.2112 | 47.4197 | -74.9817 | 74.4507 | -47.081 | 74.8581 | 120.9366 | -1.3092 | -0.29755 | 0.036621 | 0.40741 | 120.5887 | 120.8954 | 120.7581 | 74.9863 | 74.8581 | 122.1039 | 120.8405 | -0.29755 | 74.9863 | 74.8581 | 120.8405 | 120.7581 | 122.1039 | -47.6166 | -122.3648
6160.7188 | 122.374 | -74.9222 | 47.2504 | -0.077591 | 0.0014975 | -0.012008 | 0.60811 | -0.0055478 | -0.0048193 | 0.60627 | 0.19226 | 0.35706 | -0.21057 | 44.5633 | 44.3207 | 44.3756 | 44.3344 | 44.4489 | 47.4197 | -73.7228 | 74.7116 | -46.8933 | 75.1144 | 119.4855 | -2.9297 | 1.1993 | 0.16937 | 0.40283 | 119.2566 | 119.371 | 119.2429 | 75.2792 | 75.1144 | 122.3419 | 119.2978 | 1.1993 | 75.2792 | 75.1144 | 119.2978 | 119.2429 | 122.3419 | -47.4609 | -120.9732
6161.7188 | 122.3785 | -71.1411 | 51.0956 | -0.12337 | 0.0032065 | -0.009017 | 0.66921 | 0.0004336 | -0.00054693 | 0.63746 | 0.16022 | 0.33875 | -0.22888 | 40.686 | 42.009 | 40.6998 | 40.4846 | 40.5167 | 51.0544 | -71.3882 | 70.9122 | -50.7568 | 71.3013 | 111.8271 | -9.0866 | -0.24719 | -0.041199 | 0.3891 | 111.6257 | 111.6577 | 113.15 | 71.4798 | 71.3013 | 122.1954 | 111.8408 | -0.24719 | 71.4798 | 71.3013 | 111.8408 | 113.15 | 122.1954 | -51.3245 | -122.4838
6162.7188 | 121.7377 | -78.4515 | 43.1763 | 0.013962 | 0.0023519 | -0.0083762 | 0.0031338 | -0.0036252 | -0.0041785 | -0.011954 | 0.11444 | 0.32501 | -0.26093 | 40.7272 | 40.567 | 40.6357 | 40.7135 | 40.7089 | 43.2312 | 8.4412 | 78.1906 | -42.8513 | 78.566 | 119.1788 | -2.6093 | 86.8927 | 0.054931 | 0.37537 | 119.165 | 119.1605 | 119.0186 | 78.7766 | 78.566 | 121.6827 | 119.0872 | 86.8927 | 78.7766 | 78.566 | 119.0872 | 119.0186 | 121.6827 | -43.4372 | -34.7351
6163.7188 | 122.0993 | -79.1702 | 42.7643 | -0.13863 | 0.0019247 | -0.0075216 | 0.0031338 | -0.004907 | -0.0024695 | -0.011527 | 0.15564 | 0.32959 | -0.27008 | 40.9561 | 40.7547 | 40.8279 | 40.8142 | 40.9195 | 42.8238 | 8.4503 | 78.9001 | -42.4347 | 79.3259 | 120.1263 | -2.0096 | 87.6205 | 0.05951 | 0.42572 | 119.9844 | 120.0897 | 119.9249 | 79.4998 | 79.3259 | 121.994 | 119.9982 | 87.6205 | 79.4998 | 79.3259 | 119.9982 | 119.9249 | 121.994 | -43.0344 | -34.314
6164.7188 | 122.1771 | -79.6188 | 42.3889 | -0.11574 | 0.0021383 | -0.012649 | 0.0039882 | -0.0040524 | -0.0052465 | -0.011527 | 0.16937 | 0.35706 | -0.21973 | 40.773 | 40.5899 | 40.6494 | 40.6311 | 40.7547 | 42.4255 | 8.4503 | 79.3991 | -42.0319 | 79.7882 | 120.3918 | -1.799 | 88.0692 | 0.036621 | 0.3891 | 120.2499 | 120.3735 | 120.2087 | 79.9759 | 79.7882 | 122.0444 | 120.2682 | 88.0692 | 79.9759 | 79.7882 | 120.2682 | 120.2087 | 122.0444 | -42.6086 | -33.9386
6165.7188 | 122.2229 | -80.1956 | 41.8854 | -0.0012969 | 0.0029929 | -0.0070944 | 0.0031338 | -0.0036252 | -0.0041785 | -0.010673 | 0.14191 | 0.33875 | -0.24261 | 40.0177 | 39.8117 | 39.8849 | 39.8392 | 39.8438 | 41.8579 | 8.4412 | 79.953 | -41.5466 | 80.3375 | 120.2133 | -2.0737 | 88.6368 | -0.027466 | 0.38452 | 120.0348 | 120.0394 | 120.0073 | 80.5344 | 80.3375 | 122.0535 | 120.0806 | 88.6368 | 80.5344 | 80.3375 | 120.0806 | 120.0073 | 122.0535 | -42.128 | -33.4442
6166.7188 | 122.2137 | -80.6946 | 41.3818 | 0.090256 | 0.0014975 | -0.015853 | 0.0039882 | -0.0027706 | -0.0052465 | -0.010886 | 0.14648 | 0.38452 | -0.20599 | 39.8804 | 39.6698 | 39.7614 | 39.8071 | 39.8346 | 41.4413 | 8.4412 | 80.4886 | -40.9973 | 80.8411 | 120.575 | -1.712 | 89.1357 | 0.059509 | 0.35248 | 120.5017 | 120.5292 | 120.3644 | 81.0791 | 80.8411 | 122.1359 | 120.4559 | 89.1357 | 81.0791 | 80.8411 | 120.4559 | 120.3644 | 122.1359 | -41.5878 | -32.9407
6167.7188 | 122.2916 | -81.1111 | 40.979 | 0.18181 | -0.00042506 | -0.0094442 | 0.0031338 | -0.0017026 | -0.0050329 | -0.0096044 | 0.054932 | 0.34332 | -0.21973 | 39.1525 | 38.9465 | 39.061 | 39.0244 | 39.1113 | 41.0385 | 8.4549 | 80.8914 | -40.6357 | 81.1661 | 120.2637 | -2.0325 | 89.566 | 0.059509 | 0.27466 | 120.1355 | 120.2225 | 120.0577 | 81.4545 | 81.1661 | 122.1497 | 120.1721 | 89.566 | 81.4545 | 81.1661 | 120.1721 | 120.0577 | 122.1497 | -41.1987 | -32.5241
6168.7188 | 122.2916 | -81.6101 | 40.4938 | -0.10811 | 0.0012839 | -0.0088034 | 0.001852 | -0.0017026 | -0.0043921 | -0.0096044 | 0.16022 | 0.35248 | -0.21973 | 38.356 | 38.1775 | 38.2645 | 38.2462 | 38.3377 | 40.5533 | 8.4503 | 81.3904 | -40.1413 | 81.7703 | 119.9661 | -2.3163 | 90.0604 | 0.05951 | 0.37994 | 119.8563 | 119.9478 | 119.7876 | 81.9626 | 81.7703 | 122.1634 | 119.8746 | 90.0604 | 81.9626 | 81.7703 | 119.8746 | 119.7876 | 122.1634 | -40.7135 | -32.0435
6169.7188 | 122.2961 | -82.2372 | 39.917 | -0.25307 | 2.138e-06 | -0.0088034 | 0.0031338 | -0.004907 | -0.0046057 | -0.010245 | 0.10529 | 0.36163 | -0.21973 | 37.5504 | 37.3993 | 37.468 | 37.5 | 37.5641 | 39.9719 | 8.4595 | 82.0175 | -39.5554 | 82.3425 | 119.7876 | -2.5177 | 90.6967 | 0.054932 | 0.32501 | 119.7372 | 119.8013 | 119.6365 | 82.5989 | 82.3425 | 122.2092 | 119.7052 | 90.6967 | 82.5989 | 82.3425 | 119.7052 | 119.6365 | 122.2092 | -40.1367 | -31.4575
6170.7188 | 122.2961 | -82.5577 | 39.5782 | -0.17677 | 0.0029929 | -0.009017 | 0.0027066 | -0.0036252 | -0.0026831 | -0.0091772 | 0.16937 | 0.39368 | -0.20142 | 36.9095 | 36.7447 | 36.8225 | 36.8454 | 36.8958 | 39.6378 | 8.4503 | 82.3563 | -39.1846 | 82.7271 | 119.4672 | -2.8336 | 91.008 | 0.059509 | 0.37079 | 119.4031 | 119.4534 | 119.3024 | 82.9514 | 82.7271 | 122.1954 | 119.3802 | 91.008 | 82.9514 | 82.7271 | 119.3802 | 119.3024 | 122.1954 | -39.7797 | -31.1279
6171.7188 | 122.319 | -82.5806 | 39.5966 | -0.22255 | 0.0012839 | -0.014785 | -0.00049776 | -0.0046932 | -0.0031103 | -0.00875 | 0.10986 | 0.35248 | -0.25177 | 36.4426 | 36.2732 | 36.3876 | 36.6577 | 36.3556 | 39.6881 | 8.4549 | 82.3288 | -39.2441 | 82.6904 | 119.0231 | -3.3234 | 91.0355 | 0.091552 | 0.36163 | 119.2383 | 118.9362 | 118.8538 | 82.933 | 82.6904 | 122.2687 | 118.9682 | 91.0355 | 82.933 | 82.6904 | 118.9682 | 118.8538 | 122.2687 | -39.8483 | -31.1417
6172.7188 | 122.3785 | -83.2855 | 38.8641 | 0.22758 | -0.00042506 | -0.0068808 | 0.002493 | -0.001489 | -0.0043921 | -0.0085364 | 0.13275 | 0.32959 | -0.22888 | 36.4105 | 36.2595 | 36.3373 | 36.2045 | 36.4197 | 38.9099 | 8.4641 | 83.0566 | -38.5345 | 83.4183 | 119.696 | -2.6047 | 91.7496 | 0.045776 | 0.36163 | 119.4901 | 119.7052 | 119.545 | 83.6151 | 83.4183 | 122.1954 | 119.6228 | 91.7496 | 83.6151 | 83.4183 | 119.6228 | 119.545 | 122.1954 | -39.093 | -30.4001
6173.7188 | 122.3373 | -83.3405 | 38.887 | -0.2607 | 2.138e-06 | -0.012649 | -0.001566 | -0.005975 | -0.0048193 | -0.0091772 | 0.082397 | 0.32501 | -0.2655 | 35.3668 | 35.2249 | 35.2753 | 35.3943 | 35.3851 | 38.9282 | 8.4595 | 83.075 | -38.562 | 83.4229 | 118.7073 | -3.6621 | 91.7999 | 0.041199 | 0.3479 | 118.7347 | 118.7256 | 118.5654 | 83.6655 | 83.4229 | 122.2687 | 118.6157 | 91.7999 | 83.6655 | 83.4229 | 118.6157 | 118.5654 | 122.2687 | -39.1525 | -30.4276
6174.7188 | 122.374 | -84.137 | 38.0768 | -0.10811 | 0.0010703 | -0.010512 | 0.0033474 | -0.0051206 | -0.0052465 | -0.010245 | 0.16479 | 0.33875 | -0.22888 | 35.0784 | 34.8587 | 34.964 | 34.9228 | 35.0143 | 38.0997 | 8.4549 | 83.9081 | -37.738 | 84.3018 | 119.2154 | -3.2181 | 92.5919 | 0.022888 | 0.39368 | 119.0598 | 119.1513 | 118.9957 | 84.4757 | 84.3018 | 122.2366 | 119.101 | 92.5919 | 84.4757 | 84.3018 | 119.101 | 118.9957 | 122.2366 | -38.3057 | -29.6219
6175.7188 | 122.3602 | -85.0525 | 37.1796 | -0.0012969 | 0.0029929 | -0.009017 | 0.0037746 | -0.0053342 | -0.0014013 | -0.0111 | 0.25177 | 0.34332 | -0.20142 | 34.8358 | 34.6436 | 34.7397 | 34.7488 | 34.8221 | 37.1841 | 8.4549 | 84.8511 | -36.8362 | 85.3043 | 119.8883 | -2.536 | 93.5074 | 0.004578 | 0.45319 | 119.8013 | 119.8746 | 119.696 | 85.3958 | 85.3043 | 122.2366 | 119.7922 | 93.5074 | 85.3958 | 85.3043 | 119.7922 | 119.696 | 122.2366 | -37.381 | -28.7247
6176.7188 | 122.3969 | -85.2676 | 36.9965 | -0.22255 | -0.0014933 | -0.012862 | 0.00078404 | -0.0051206 | -0.0041785 | -0.0098182 | 0.10529 | 0.37537 | -0.24261 | 34.4055 | 34.2682 | 34.3094 | 34.3826 | 34.4238 | 37.0285 | 8.4641 | 85.025 | -36.6211 | 85.3729 | 119.6732 | -2.7283 | 93.7317 | 0.032043 | 0.3479 | 119.6503 | 119.6915 | 119.5358 | 85.643 | 85.3729 | 122.2961 | 119.577 | 93.7317 | 85.643 | 85.3729 | 119.577 | 119.5358 | 122.2961 | -37.2391 | -28.5324
6177.7188 | 122.3557 | -85.6842 | 36.557 | 0.16655 | 0.0019247 | -0.010085 | 0.0044156 | -0.004266 | -0.0033239 | -0.0068274 | 0.091553 | 0.34332 | -0.24719 | 33.2886 | 33.1375 | 33.197 | 33.2565 | 33.2657 | 36.6165 | 8.4686 | 85.437 | -36.2137 | 85.7758 | 118.9728 | -3.4195 | 94.1528 | 0.059509 | 0.33874 | 118.9407 | 118.9499 | 118.8217 | 86.0275 | 85.7758 | 122.3007 | 118.8812 | 94.1528 | 86.0275 | 85.7758 | 118.8812 | 118.8217 | 122.3007 | -36.8042 | -28.0884
6178.7188 | 122.4106 | -87.5015 | 34.7305 | -0.14626 | 0.0010703 | -0.011367 | 0.0080472 | -0.0064022 | -0.0075963 | -0.0098182 | 0.14191 | 0.31586 | -0.24261 | 34.5383 | 34.3689 | 34.4513 | 34.4284 | 34.5428 | 34.7717 | 8.4641 | 87.2589 | -34.4147 | 87.6434 | 122.0398 | -0.36163 | 95.9656 | 0.041199 | 0.38452 | 121.9299 | 122.0444 | 121.8704 | 87.8174 | 87.6434 | 122.2733 | 121.9528 | 95.9656 | 87.8174 | 87.6434 | 121.9528 | 121.8704 | 122.2733 | -34.9731 | -26.2665
6179.7188 | 122.4701 | -87.9868 | 34.2453 | 0.37254 | 0.00085654 | -0.012008 | 0.00078404 | -0.0061886 | -0.0058875 | -0.0091772 | 0.15106 | 0.28839 | -0.21515 | 34.0439 | 33.902 | 33.9935 | 33.8974 | 34.0988 | 34.2773 | 8.4641 | 87.7716 | -33.9569 | 88.1378 | 122.0306 | -0.34332 | 96.4508 | 0.032044 | 0.36621 | 121.8842 | 122.0856 | 121.8887 | 88.2751 | 88.1378 | 122.2641 | 121.9803 | 96.4508 | 88.2751 | 88.1378 | 121.9803 | 121.8887 | 122.2641 | -34.4604 | -25.7812
6180.7344 | 122.4152 | -87.9272 | 34.3414 | -0.047073 | -0.00021146 | -0.009017 | 0.0071926 | -0.0040524 | -0.0058875 | -0.0083228 | 0.14648 | 0.32501 | -0.23346 | 32.4875 | 32.3318 | 32.4097 | 32.3822 | 32.5104 | 34.3552 | 8.4641 | 87.6938 | -34.0164 | 88.0737 | 120.4147 | -2.0096 | 96.3913 | 0.013733 | 0.37994 | 120.3094 | 120.4376 | 120.2591 | 88.2523 | 88.0737 | 122.2824 | 120.3369 | 96.3913 | 88.2523 | 88.0737 | 120.3369 | 120.2591 | 122.2824 | -34.5749 | -25.8774
6181.7188 | 122.3969 | -88.4537 | 33.8425 | -0.15388 | 0.00064294 | -0.012435 | 0.0016384 | -0.0091794 | -0.0058875 | -0.010673 | 0.082397 | 0.33875 | -0.23804 | 32.3547 | 32.2357 | 32.2815 | 32.3914 | 32.4097 | 33.8882 | 8.4641 | 88.2156 | -33.5037 | 88.5361 | 120.8084 | -1.6067 | 96.9177 | 0.045777 | 0.32043 | 120.845 | 120.8633 | 120.6894 | 88.7924 | 88.5361 | 122.3419 | 120.7352 | 96.9177 | 88.7924 | 88.5361 | 120.7352 | 120.6894 | 122.3419 | -34.0805 | -25.3784
6182.7188 | 122.525 | -88.7787 | 33.4167 | 0.17418 | -0.0010661 | -0.012008 | 0.0031338 | -0.0074704 | -0.0046057 | -0.010032 | 0.16937 | 0.27466 | -0.21515 | 32.0526 | 31.9702 | 32.2495 | 31.9473 | 32.222 | 33.4488 | 8.4732 | 88.5635 | -33.1421 | 88.9481 | 120.8313 | -1.4465 | 97.2519 | 0.032044 | 0.38452 | 120.726 | 121.0007 | 120.7489 | 89.0533 | 88.9481 | 122.2275 | 121.0281 | 97.2519 | 89.0533 | 88.9481 | 121.0281 | 120.7489 | 122.2275 | -33.6319 | -24.9435
6183.7188 | 122.4518 | -89.4608 | 32.8354 | -0.2607 | 0.0012839 | -0.011153 | 0.0037746 | -0.0085386 | -0.0056737 | -0.0096044 | 0.1236 | 0.32044 | -0.23804 | 31.398 | 31.2607 | 31.3065 | 31.3477 | 31.4255 | 32.8674 | 8.4732 | 89.2227 | -32.515 | 89.5844 | 120.8588 | -1.5747 | 97.934 | 0.032044 | 0.36163 | 120.8084 | 120.8862 | 120.7214 | 89.7812 | 89.5844 | 122.3282 | 120.7672 | 97.934 | 89.7812 | 89.5844 | 120.7672 | 120.7214 | 122.3282 | -33.0734 | -24.3622
6184.7188 | 122.4197 | -89.7583 | 32.5699 | -0.22255 | 0.00085654 | -0.01094 | 0.006979 | -0.0089658 | -0.0054601 | -0.012168 | 0.082397 | 0.33417 | -0.23804 | 31.2378 | 31.0089 | 30.8853 | 31.0776 | 31.1188 | 32.6065 | 8.4641 | 89.5203 | -32.2357 | 89.8407 | 120.9961 | -1.561 | 98.2224 | 0.036621 | 0.32043 | 120.8359 | 120.8771 | 120.7672 | 90.0925 | 89.8407 | 122.3648 | 120.6436 | 98.2224 | 90.0925 | 89.8407 | 120.6436 | 120.7672 | 122.3648 | -32.8079 | -24.1058
6185.7188 | 122.5067 | -90.3351 | 31.9427 | 0.03685 | -0.0025613 | -0.012435 | 0.0027066 | -0.0078976 | -0.0048193 | -0.010245 | 0.10529 | 0.29297 | -0.2243 | 30.5466 | 30.4138 | 30.4779 | 30.3543 | 30.6152 | 31.9794 | 8.4686 | 90.1108 | -31.6498 | 90.4404 | 120.8817 | -1.5289 | 98.8037 | 0.036621 | 0.32959 | 120.6894 | 120.9503 | 120.7489 | 90.6281 | 90.4404 | 122.3145 | 120.813 | 98.8037 | 90.6281 | 90.4404 | 120.813 | 120.7489 | 122.3145 | -32.1671 | -23.4741
6186.7188 | 122.4472 | -90.7562 | 31.5674 | 0.082626 | 0.00021574 | -0.013289 | 0.0099698 | -0.0072568 | -0.0052465 | -0.0093908 | 0.050354 | 0.36621 | -0.21973 | 29.9652 | 29.8462 | 29.8874 | 29.9423 | 29.9973 | 31.6132 | 8.4686 | 90.5365 | -31.2012 | 90.8066 | 120.7214 | -1.7212 | 99.2249 | 0.045776 | 0.27008 | 120.6985 | 120.7535 | 120.6024 | 91.1224 | 90.8066 | 122.3694 | 120.6436 | 99.2249 | 91.1224 | 90.8066 | 120.6436 | 120.6024 | 122.3694 | -31.7871 | -23.0988
6187.7188 | 122.4335 | -91.1545 | 31.1691 | -0.20729 | 0.0021383 | -0.01393 | 0.0067654 | -0.0068296 | -0.0048193 | -0.0096044 | 0.073242 | 0.32501 | -0.24719 | 29.5486 | 29.4113 | 29.4617 | 29.5624 | 29.5807 | 31.2241 | 8.4732 | 90.9073 | -30.8441 | 91.2277 | 120.7031 | -1.7578 | 99.6277 | 0.054932 | 0.32043 | 120.7169 | 120.7352 | 120.5658 | 91.4795 | 91.2277 | 122.3785 | 120.6162 | 99.6277 | 91.4795 | 91.2277 | 120.6162 | 120.5658 | 122.3785 | -31.4163 | -22.6959
6188.7188 | 122.5342 | -91.9098 | 30.4047 | 1.3949 | -0.0012797 | -0.015639 | 0.0046292 | -0.0068296 | -0.0048193 | -0.012168 | 0.21057 | 0.27924 | -0.23346 | 28.9764 | 28.8437 | 28.8895 | 28.7796 | 29.0405 | 30.4321 | 8.4824 | 91.6763 | -30.1254 | 92.1204 | 120.8862 | -1.561 | 100.3922 | 0.027466 | 0.44403 | 120.6894 | 120.9503 | 120.7535 | 92.189 | 92.1204 | 122.3419 | 120.7993 | 100.3922 | 92.189 | 92.1204 | 120.7993 | 120.7535 | 122.3419 | -30.6381 | -21.9223
6189.7188 | 122.5571 | -92.6102 | 29.6539 | -0.23018 | -0.0012797 | -0.015639 | 0.0054836 | -0.0085386 | -0.0043921 | -0.010886 | 0.16479 | 0.27924 | -0.23804 | 29.0817 | 28.7384 | 28.7201 | 28.8071 | 28.9902 | 29.6906 | 8.4778 | 92.3721 | -29.3747 | 92.775 | 121.6919 | -0.91553 | 101.088 | 0.036621 | 0.40283 | 121.4172 | 121.6003 | 121.3486 | 92.8894 | 92.775 | 122.3007 | 121.3303 | 101.088 | 92.8894 | 92.775 | 121.3303 | 121.3486 | 122.3007 | -29.892 | -21.1761
6190.7188 | 122.5204 | -93.5715 | 28.7384 | -0.27596 | -0.0014933 | -0.017776 | 0.0065518 | -0.0091794 | -0.0054601 | -0.0096044 | 0.15106 | 0.29297 | -0.21973 | 28.7476 | 28.5736 | 28.656 | 28.6057 | 28.7704 | 28.7842 | 8.4778 | 93.3517 | -28.4454 | 93.7225 | 122.319 | -0.1648 | 102.0493 | 0.045777 | 0.37079 | 122.1771 | 122.3419 | 122.1451 | 93.8644 | 93.7225 | 122.3557 | 122.2275 | 102.0493 | 93.8644 | 93.7225 | 122.2275 | 122.1451 | 122.3557 | -28.9581 | -20.2606
6191.7188 | 122.4747 | -94.2169 | 28.125 | -0.23781 | -0.0027751 | -0.016707 | 0.0089016 | -0.010247 | -0.0061011 | -0.011741 | 0.09613 | 0.30212 | -0.23346 | 28.0655 | 27.887 | 27.9556 | 28.038 | 28.093 | 28.1799 | 8.4778 | 93.9835 | -27.8229 | 94.313 | 122.2824 | -0.23804 | 102.6947 | 0.054932 | 0.32959 | 122.2549 | 122.3099 | 122.1039 | 94.519 | 94.313 | 122.3969 | 122.1725 | 102.6947 | 94.519 | 94.313 | 122.1725 | 122.1039 | 122.3969 | -28.3585 | -19.6472
6192.7188 | 122.4976 | -94.8532 | 27.4979 | -0.23018 | -0.0014933 | -0.011367 | 0.0067654 | -0.011316 | -0.0058875 | -0.0098182 | 0.1236 | 0.29755 | -0.21515 | 27.4612 | 27.3056 | 27.3605 | 27.3926 | 27.4796 | 27.5253 | 8.4824 | 94.6381 | -27.2003 | 94.9768 | 122.3145 | -0.19226 | 103.3356 | 0.027466 | 0.33875 | 122.2458 | 122.3328 | 122.1588 | 95.1508 | 94.9768 | 122.3785 | 122.2137 | 103.3356 | 95.1508 | 94.9768 | 122.2137 | 122.1588 | 122.3785 | -27.713 | -19.0155
6193.7188 | 122.6212 | -95.2881 | 26.9943 | -0.19203 | -0.0019205 | -0.01393 | 0.0050564 | -0.010888 | -0.0082373 | -0.010245 | 0.16937 | 0.28381 | -0.19226 | 27.095 | 26.9531 | 27.0264 | 26.7838 | 27.1683 | 27.0264 | 8.4732 | 95.0958 | -26.7105 | 95.4575 | 122.3831 | -0.041199 | 103.7613 | 0.032043 | 0.36163 | 122.0718 | 122.4564 | 122.2412 | 95.5719 | 95.4575 | 122.3145 | 122.3145 | 103.7613 | 95.5719 | 95.4575 | 122.3145 | 122.2412 | 122.3145 | -27.1866 | -18.5211
6194.7188 | 122.4838 | -95.9518 | 26.4313 | -0.19203 | 0.00042934 | -0.012435 | 0.0093288 | -0.010034 | -0.0063147 | -0.011313 | 0.07782 | 0.30212 | -0.23804 | 26.3763 | 26.2344 | 26.2894 | 26.3535 | 26.4175 | 26.4679 | 8.4732 | 95.7138 | -26.1291 | 96.0297 | 122.3282 | -0.19684 | 104.425 | 0.036622 | 0.31586 | 122.3053 | 122.3694 | 122.1863 | 96.254 | 96.0297 | 122.4197 | 122.2412 | 104.425 | 96.254 | 96.0297 | 122.2412 | 122.1863 | 122.4197 | -26.6693 | -17.9581
6195.7188 | 122.5113 | -96.46 | 25.946 | -0.26833 | 0.00021574 | -0.013503 | 0.010183 | -0.011316 | -0.0039649 | -0.0085364 | 0.13733 | 0.30212 | -0.24261 | 25.9094 | 25.7721 | 25.8224 | 25.8316 | 25.9552 | 25.9689 | 8.4778 | 96.2173 | -25.6439 | 96.5973 | 122.3694 | -0.17395 | 104.9377 | 0.022888 | 0.37994 | 122.2916 | 122.4152 | 122.2321 | 96.7621 | 96.5973 | 122.4289 | 122.2824 | 104.9377 | 96.7621 | 96.5973 | 122.2824 | 122.2321 | 122.4289 | -26.1887 | -17.4683
6196.7188 | 122.612 | -97.2794 | 25.0168 | -0.047073 | -0.0027751 | -0.010512 | 0.005911 | -0.011316 | -0.0046057 | -0.0098182 | 0.13275 | 0.28381 | -0.21973 | 25.0763 | 24.9527 | 25.0259 | 24.8199 | 25.1358 | 25.058 | 8.4824 | 97.0596 | -24.733 | 97.4121 | 122.3557 | -0.064087 | 105.7617 | 0.041198 | 0.35248 | 122.0993 | 122.4152 | 122.2321 | 97.5632 | 97.4121 | 122.3373 | 122.3053 | 105.7617 | 97.5632 | 97.4121 | 122.3053 | 122.2321 | 122.3373 | -25.2365 | -16.5344
6197.7188 | 122.5891 | -97.9797 | 24.3896 | -0.24544 | -0.0044839 | -0.012221 | 0.006979 | -0.010034 | -0.0061011 | -0.010886 | 0.15106 | 0.27924 | -0.22888 | 24.4217 | 24.2935 | 24.3393 | 24.2523 | 24.4812 | 24.4217 | 8.4732 | 97.7509 | -24.1104 | 98.1308 | 122.4014 | -0.09613 | 106.4529 | 0.032044 | 0.37994 | 122.2321 | 122.4609 | 122.2733 | 98.259 | 98.1308 | 122.4014 | 122.319 | 106.4529 | 98.259 | 98.1308 | 122.319 | 122.2733 | 122.4014 | -24.6185 | -15.9164
6198.7188 | 122.6395 | -98.4787 | 23.8815 | -0.10048 | -0.00085226 | -0.010299 | 0.006979 | -0.009393 | -0.0061011 | -0.011313 | 0.13275 | 0.28839 | -0.21515 | 23.9273 | 23.8174 | 23.877 | 23.6664 | 24.0189 | 23.8861 | 8.4869 | 98.2636 | -23.5931 | 98.6115 | 122.406 | -0.064087 | 106.9656 | 0.004577 | 0.3479 | 122.1451 | 122.4976 | 122.2961 | 98.7671 | 98.6115 | 122.3648 | 122.3557 | 106.9656 | 98.7671 | 98.6115 | 122.3557 | 122.2961 | 122.3648 | -24.0967 | -15.3946
6199.7188 | 122.6395 | -99.0417 | 23.3185 | -0.069961 | -0.0025613 | -0.014571 | 0.00527 | -0.010675 | -0.0050329 | -0.010245 | 0.14191 | 0.28381 | -0.22888 | 23.3871 | 23.259 | 23.3231 | 23.1308 | 23.4604 | 23.3414 | 8.4824 | 98.8129 | -23.0347 | 99.1837 | 122.4289 | -0.059509 | 107.5241 | 0.022889 | 0.37079 | 122.1725 | 122.5021 | 122.3007 | 99.3256 | 99.1837 | 122.3831 | 122.3648 | 107.5241 | 99.3256 | 99.1837 | 122.3648 | 122.3007 | 122.3831 | -23.5474 | -14.8361
6200.7188 | 122.5662 | -99.8566 | 22.554 | -0.24544 | -0.0010661 | -0.017348 | 0.008688 | -0.011956 | -0.0037511 | -0.0111 | 0.14648 | 0.28839 | -0.23346 | 22.5494 | 22.4258 | 22.467 | 22.4487 | 22.6089 | 22.5769 | 8.4824 | 99.6231 | -22.2656 | 100.0031 | 122.406 | -0.12817 | 108.3389 | 0.022888 | 0.37994 | 122.3053 | 122.4655 | 122.2824 | 100.145 | 100.0031 | 122.4335 | 122.3236 | 108.3389 | 100.145 | 100.0031 | 122.3236 | 122.2824 | 122.4335 | -22.7875 | -14.0717
6201.7188 | 122.6395 | -100.5615 | 21.8353 | -0.062332 | -0.0027751 | -0.013076 | 0.0074062 | -0.011529 | -0.0065283 | -0.011741 | 0.11444 | 0.28381 | -0.21515 | 21.8445 | 21.7438 | 21.8124 | 21.6248 | 21.9223 | 21.8445 | 8.4778 | 100.3464 | -21.5515 | 100.676 | 122.406 | -0.091553 | 109.0393 | 0.009155 | 0.32959 | 122.1863 | 122.4838 | 122.3053 | 100.8453 | 100.676 | 122.406 | 122.374 | 109.0393 | 100.8453 | 100.676 | 122.374 | 122.3053 | 122.406 | -22.0505 | -13.3575
6202.7188 | 122.644 | -101.0971 | 21.2997 | -0.069961 | -0.00085226 | -0.012221 | 0.0071926 | -0.011316 | -0.0043921 | -0.011954 | 0.10529 | 0.24261 | -0.26093 | 21.3318 | 21.2082 | 21.2723 | 21.0938 | 21.3776 | 21.3043 | 8.4824 | 100.8362 | -21.0571 | 101.2024 | 122.4289 | -0.091553 | 109.5795 | 0.004577 | 0.36621 | 122.1909 | 122.4747 | 122.3053 | 101.3397 | 101.2024 | 122.4014 | 122.3694 | 109.5795 | 101.3397 | 101.2024 | 122.3694 | 122.3053 | 122.4014 | -21.5607 | -12.8174
6203.7188 | 122.644 | -101.1749 | 21.2265 | 0.76927 | -0.0019205 | -0.012008 | 0.0056972 | -0.01217 | -0.0043921 | -0.012382 | 0.082397 | 0.22888 | -0.27008 | 21.2585 | 21.1121 | 21.199 | 21.0434 | 21.3272 | 21.2173 | 8.4778 | 100.9048 | -20.9976 | 101.2573 | 122.4335 | -0.11444 | 109.6527 | -0.009155 | 0.35248 | 122.2183 | 122.5021 | 122.287 | 101.4038 | 101.2573 | 122.3923 | 122.374 | 109.6527 | 101.4038 | 101.2573 | 122.374 | 122.287 | 122.3923 | -21.4966 | -12.7487
6204.7188 | 122.6669 | -101.6281 | 20.755 | -0.09285 | 0.00021574 | -0.015639 | 0.0061246 | -0.011102 | -0.0035375 | -0.011954 | 0.12817 | 0.27924 | -0.23804 | 20.8374 | 20.7184 | 20.7779 | 20.5902 | 20.9061 | 20.7687 | 8.4824 | 101.3901 | -20.4758 | 101.7563 | 122.4655 | -0.036621 | 110.1105 | 0.013733 | 0.36621 | 122.2183 | 122.5342 | 122.3465 | 101.9073 | 101.7563 | 122.3969 | 122.406 | 110.1105 | 101.9073 | 101.7563 | 122.406 | 122.3465 | 122.3969 | -20.993 | -12.2726
6205.7188 | 122.6761 | -101.889 | 20.4803 | -0.08522 | -0.00021146 | -0.015212 | 0.005911 | -0.010675 | -0.0050329 | -0.010673 | 0.10529 | 0.28381 | -0.2243 | 20.5765 | 20.4437 | 20.4895 | 20.2927 | 20.6314 | 20.5124 | 8.4869 | 101.6647 | -20.1965 | 101.9943 | 122.4655 | -0.036621 | 110.376 | 0.032043 | 0.32959 | 122.1817 | 122.5204 | 122.3328 | 102.1729 | 101.9943 | 122.4014 | 122.3785 | 110.376 | 102.1729 | 101.9943 | 122.3785 | 122.3328 | 122.4014 | -20.7047 | -11.9934
6206.7188 | 122.7127 | -102.562 | 19.7983 | -0.11574 | -0.0014933 | -0.012649 | 0.004202 | -0.011956 | -0.0031103 | -0.011527 | 0.14191 | 0.2655 | -0.21973 | 19.9493 | 19.7937 | 19.8441 | 19.6106 | 19.9951 | 19.8486 | 8.4824 | 102.3422 | -19.5328 | 102.7039 | 122.5113 | -0.004578 | 111.0443 | 0.050354 | 0.36163 | 122.1725 | 122.5571 | 122.3557 | 102.8275 | 102.7039 | 122.4106 | 122.406 | 111.0443 | 102.8275 | 102.7039 | 122.406 | 122.3557 | 122.4106 | -20.018 | -11.3159
6207.7188 | 122.731 | -103.0792 | 19.3588 | -0.24544 | -0.0021341 | -0.015212 | 0.006979 | -0.011743 | -0.0046057 | -0.010673 | 0.14648 | 0.26093 | -0.24261 | 19.4412 | 19.313 | 19.2581 | 19.4595 | 19.3497 | 19.3817 | 8.4869 | 102.8366 | -19.0979 | 103.2257 | 122.5204 | -0.045777 | 111.5662 | 0.022888 | 0.3891 | 122.5388 | 122.4289 | 122.3923 | 103.3401 | 103.2257 | 122.4609 | 122.3373 | 111.5662 | 103.3401 | 103.2257 | 122.3373 | 122.3923 | 122.4609 | -19.6014 | -10.8719
6208.7188 | 122.7402 | -103.4958 | 18.9194 | -0.23781 | -0.0021341 | -0.016921 | 0.0099698 | -0.012811 | -0.0065283 | -0.010673 | 0.14648 | 0.23346 | -0.23346 | 19.0109 | 18.8736 | 18.9423 | 18.7454 | 19.0704 | 18.9102 | 8.4915 | 103.2623 | -18.6859 | 103.6423 | 122.5067 | -0.045777 | 111.9873 | -0.009156 | 0.37994 | 122.2412 | 122.5662 | 122.3694 | 103.7292 | 103.6423 | 122.406 | 122.4381 | 111.9873 | 103.7292 | 103.6423 | 122.4381 | 122.3694 | 122.406 | -19.1528 | -10.4279
6209.7188 | 122.699 | -104.0771 | 18.3197 | -0.10048 | -0.0025613 | -0.012649 | 0.00527 | -0.010247 | -0.0043921 | -0.011741 | 0.13275 | 0.25635 | -0.21515 | 18.4204 | 18.2968 | 18.3609 | 18.1595 | 18.5074 | 18.3792 | 8.4824 | 103.862 | -18.0634 | 104.2099 | 122.4976 | -0.022888 | 112.5595 | 0.059509 | 0.3479 | 122.2366 | 122.5845 | 122.374 | 104.3335 | 104.2099 | 122.4564 | 122.438 | 112.5595 | 104.3335 | 104.2099 | 122.438 | 122.374 | 122.4564 | -18.5349 | -9.8373
6210.7344 | 122.5433 | -104.9423 | 17.5644 | -0.23781 | 0.0010703 | -0.011153 | 0.013174 | -0.010034 | -0.0037511 | -0.013022 | 0.059509 | 0.30212 | -0.28381 | 17.4728 | 17.3401 | 17.3813 | 17.4728 | 17.5873 | 17.5552 | 8.4778 | 104.6585 | -17.2623 | 105.0018 | 122.4152 | -0.2243 | 113.4201 | -0.009155 | 0.34332 | 122.4152 | 122.5296 | 122.2824 | 105.2444 | 105.0018 | 122.4976 | 122.3236 | 113.4201 | 105.2444 | 105.0018 | 122.3236 | 122.2824 | 122.4976 | -17.8482 | -9.0866
6211.7188 | 122.6944 | -105.5603 | 16.8686 | -0.3904 | -0.0027751 | -0.012008 | 0.0097562 | -0.0098202 | -0.0071691 | -0.010886 | 0.09613 | 0.22888 | -0.26093 | 16.9373 | 16.8091 | 16.8503 | 16.7038 | 17.0059 | 16.8915 | 8.4824 | 105.2994 | -16.6397 | 105.6564 | 122.4976 | -0.059509 | 114.0427 | 0.022888 | 0.35706 | 122.2641 | 122.5662 | 122.3694 | 105.7892 | 105.6564 | 122.4518 | 122.4106 | 114.0427 | 105.7892 | 105.6564 | 122.4106 | 122.3694 | 122.4518 | -17.1295 | -8.3862
6212.7188 | 122.7127 | -106.0684 | 16.3605 | -0.069961 | -0.00042506 | -0.01628 | 0.0091152 | -0.010247 | -0.0054601 | -0.011741 | 0.10529 | 0.25635 | -0.23804 | 16.4154 | 16.3055 | 16.3834 | 16.1819 | 16.5115 | 16.4017 | 8.4824 | 105.8304 | -16.1041 | 106.1737 | 122.4838 | -0.054932 | 114.5508 | 0.041198 | 0.34332 | 122.2504 | 122.58 | 122.374 | 106.3248 | 106.1737 | 122.4701 | 122.4518 | 114.5508 | 106.3248 | 106.1737 | 122.4518 | 122.374 | 122.4701 | -16.5985 | -7.8781
6213.7188 | 122.6944 | -106.6956 | 15.7562 | -0.08522 | -0.0010661 | -0.010512 | 0.0048428 | -0.0083248 | -0.0050329 | -0.010886 | 0.10986 | 0.25635 | -0.23346 | 15.7974 | 15.6738 | 15.7471 | 15.5502 | 15.8798 | 15.7608 | 8.4915 | 106.4621 | -15.4999 | 106.8054 | 122.493 | -0.082398 | 115.1871 | 0.004577 | 0.34332 | 122.2458 | 122.5754 | 122.3694 | 106.9519 | 106.8054 | 122.4564 | 122.4426 | 115.1871 | 106.9519 | 106.8054 | 122.4426 | 122.3694 | 122.4564 | -15.9897 | -7.2647
6214.7188 | 122.6898 | -107.016 | 15.4129 | -0.016556 | -0.0012797 | -0.017135 | 0.0082608 | -0.010034 | -0.0037511 | -0.014304 | 0.068665 | 0.24719 | -0.25177 | 15.4083 | 15.39 | 15.358 | 15.239 | 15.5502 | 15.4312 | 8.4869 | 106.7642 | -15.1657 | 107.0847 | 122.4243 | -0.022888 | 115.5029 | 0.01831 | 0.32044 | 122.2549 | 122.5662 | 122.406 | 107.2632 | 107.0847 | 122.4472 | 122.374 | 115.5029 | 107.2632 | 107.0847 | 122.374 | 122.406 | 122.4472 | -15.6647 | -6.926
6215.7188 | 122.7127 | -107.5195 | 14.9094 | -0.024185 | -0.0023477 | -0.0092306 | 0.0080472 | -0.010034 | -0.0028967 | -0.010245 | 0.082397 | 0.23804 | -0.25635 | 14.946 | 14.8361 | 14.8865 | 14.7125 | 15.0284 | 14.9506 | 8.4915 | 107.2632 | -14.6713 | 107.6019 | 122.4655 | -0.073242 | 116.011 | 0.041199 | 0.33875 | 122.2321 | 122.5479 | 122.3557 | 107.7576 | 107.6019 | 122.4701 | 122.406 | 116.011 | 107.7576 | 107.6019 | 122.406 | 122.3557 | 122.4701 | -15.1657 | -6.4178
6216.7188 | 122.7081 | -107.9773 | 14.4928 | -0.016556 | -0.0017069 | -0.012008 | 0.0071926 | -0.01217 | -0.0052465 | -0.010459 | 0.073242 | 0.24719 | -0.26093 | 14.4974 | 14.3829 | 14.4424 | 14.2868 | 14.5798 | 14.4836 | 8.4869 | 107.7164 | -14.2456 | 108.0505 | 122.4747 | -0.10986 | 116.4642 | -0.009155 | 0.33417 | 122.2641 | 122.5571 | 122.3602 | 108.2245 | 108.0505 | 122.4609 | 122.4197 | 116.4642 | 108.2245 | 108.0505 | 122.4197 | 122.3602 | 122.4609 | -14.7537 | -6.0059
6217.7188 | 122.7448 | -108.4122 | 14.0305 | -0.16151 | 0.0014975 | -0.011153 | 0.006979 | -0.011316 | -0.0052465 | -0.0093908 | 0.11902 | 0.24261 | -0.23346 | 14.0945 | 13.9893 | 14.0396 | 13.8382 | 14.1953 | 14.0762 | 8.4869 | 108.1787 | -13.7878 | 108.5312 | 122.5067 | -0.041199 | 116.8991 | 0.045776 | 0.35248 | 122.2504 | 122.6074 | 122.4014 | 108.6548 | 108.5312 | 122.4884 | 122.4518 | 116.8991 | 108.6548 | 108.5312 | 122.4518 | 122.4014 | 122.4884 | -14.2639 | -5.5435
6218.7188 | 122.7448 | -108.6777 | 13.765 | -0.10048 | 2.138e-06 | -0.014358 | 0.0097562 | -0.0098202 | -0.0065283 | -0.010459 | 0.11444 | 0.24261 | -0.25635 | 13.8199 | 13.7009 | 13.7604 | 13.5406 | 13.916 | 13.7833 | 8.4915 | 108.4213 | -13.5223 | 108.7921 | 122.4976 | -0.064087 | 117.1692 | 0.01831 | 0.37079 | 122.2183 | 122.5937 | 122.3785 | 108.9203 | 108.7921 | 122.4609 | 122.438 | 117.1692 | 108.9203 | 108.7921 | 122.438 | 122.3785 | 122.4609 | -14.0213 | -5.2734
6219.7188 | 122.7493 | -109.053 | 13.4171 | -0.12337 | -0.0017069 | -0.010726 | 0.0082608 | -0.0096066 | -0.0052465 | -0.0098182 | 0.11444 | 0.23804 | -0.25635 | 13.4537 | 13.3667 | 13.4171 | 13.1973 | 13.5727 | 13.4537 | 8.4915 | 108.7967 | -13.179 | 109.1675 | 122.5067 | -0.050354 | 117.5446 | 0.036621 | 0.37079 | 122.2504 | 122.6257 | 122.4197 | 109.2911 | 109.1675 | 122.5067 | 122.4701 | 117.5446 | 109.2911 | 109.1675 | 122.4701 | 122.4197 | 122.5067 | -13.6734 | -4.9255
6220.7188 | 122.7356 | -109.314 | 13.179 | 2.2265 | 0.00042934 | -0.017348 | 0.010397 | -0.011102 | -0.0061011 | -0.0111 | 0.19226 | 0.21057 | -0.29755 | 13.2248 | 13.1104 | 13.147 | 12.9776 | 13.3026 | 13.2019 | 8.4915 | 109.0164 | -12.9684 | 109.5062 | 122.5388 | -0.068664 | 117.8055 | 0.022888 | 0.48981 | 122.2916 | 122.6166 | 122.4243 | 109.5245 | 109.5062 | 122.5159 | 122.4609 | 117.8055 | 109.5245 | 109.5062 | 122.4609 | 122.4243 | 122.5159 | -13.4766 | -4.6875
6221.7188 | 122.7264 | -109.7534 | 12.7304 | 0.0063326 | -0.00085226 | -0.011794 | 0.0089016 | -0.009393 | -0.0046057 | -0.013877 | 0.059509 | 0.23346 | -0.26093 | 12.7075 | 12.6938 | 12.6572 | 12.5656 | 12.854 | 12.7625 | 8.4778 | 109.4925 | -12.4969 | 109.8129 | 122.4609 | -0.036621 | 118.2312 | 0.032043 | 0.32043 | 122.319 | 122.6074 | 122.4472 | 109.9869 | 109.8129 | 122.5159 | 122.4106 | 118.2312 | 109.9869 | 109.8129 | 122.4106 | 122.4472 | 122.5159 | -12.9913 | -4.2526
6222.7188 | 122.7402 | -110.0647 | 12.4374 | -0.016556 | 0.0010703 | -0.012862 | 0.0084744 | -0.0098202 | -0.0048193 | -0.012382 | 0.064087 | 0.23346 | -0.27466 | 12.442 | 12.3505 | 12.3871 | 12.2223 | 12.5427 | 12.4558 | 8.4686 | 109.79 | -12.204 | 110.1288 | 122.5067 | -0.086975 | 118.5333 | 0.018311 | 0.33875 | 122.287 | 122.6074 | 122.4152 | 110.2982 | 110.1288 | 122.5204 | 122.4518 | 118.5333 | 110.2982 | 110.1288 | 122.4518 | 122.4152 | 122.5204 | -12.7121 | -3.9688
6223.7188 | 122.7356 | -110.408 | 12.1078 | 0.052109 | -0.00042506 | -0.012221 | 0.0067654 | -0.0091794 | -0.0067419 | -0.010245 | 0.050354 | 0.21515 | -0.27466 | 12.0941 | 11.998 | 12.0346 | 11.8835 | 12.1994 | 12.117 | 8.4549 | 110.1334 | -11.8927 | 110.4584 | 122.5021 | -0.10986 | 118.8629 | 0.009155 | 0.32501 | 122.2916 | 122.6074 | 122.406 | 110.6232 | 110.4584 | 122.525 | 122.4426 | 118.8629 | 110.6232 | 110.4584 | 122.4426 | 122.406 | 122.525 | -12.3825 | -3.653
6224.7188 | 122.7356 | -110.6918 | 11.824 | 0.19707 | -0.00063866 | -0.015212 | 0.0074062 | -0.010034 | -0.0050329 | -0.011741 | 0.032043 | 0.1831 | -0.30212 | 11.8011 | 11.7004 | 11.7508 | 11.5997 | 11.8927 | 11.8469 | 8.4412 | 110.3897 | -11.6409 | 110.7239 | 122.493 | -0.1236 | 119.133 | 0.022888 | 0.33417 | 122.2916 | 122.5845 | 122.3923 | 110.8749 | 110.7239 | 122.5388 | 122.4426 | 119.133 | 110.8749 | 110.7239 | 122.4426 | 122.3923 | 122.5388 | -12.1262 | -3.3829
6225.7344 | 122.7219 | -111.0306 | 11.4532 | 0.17418 | 0.0012839 | -0.010512 | 0.01531 | -0.010461 | -0.0035375 | -0.012382 | 0.073242 | 0.26093 | -0.32501 | 11.4395 | 11.3068 | 11.3754 | 11.261 | 11.5128 | 11.5036 | 8.4137 | 110.7056 | -11.1923 | 111.1038 | 122.4701 | -0.14648 | 119.4443 | 0.050354 | 0.39825 | 122.2916 | 122.5433 | 122.3373 | 111.2915 | 111.1038 | 122.5342 | 122.406 | 119.4443 | 111.2915 | 111.1038 | 122.406 | 122.3373 | 122.5342 | -11.7783 | -3.0396
6226.7188 | 122.7768 | -111.264 | 11.2473 | -0.039444 | -0.0014933 | -0.01393 | 0.0082608 | -0.009393 | -0.0046057 | -0.0093908 | 0.064087 | 0.21515 | -0.27466 | 11.2885 | 11.1923 | 11.2427 | 11.0321 | 11.3892 | 11.2885 | 8.4045 | 110.9894 | -11.0321 | 111.3281 | 122.5525 | -0.054931 | 119.6686 | 0.041199 | 0.33875 | 122.2961 | 122.6532 | 122.4564 | 111.4792 | 111.3281 | 122.5525 | 122.5067 | 119.6686 | 111.4792 | 111.3281 | 122.5067 | 122.4564 | 122.5525 | -11.5219 | -2.8427
6227.7188 | 122.7676 | -111.5616 | 10.9543 | -0.047073 | -0.0019205 | -0.014358 | 0.010824 | -0.012384 | -0.0056737 | -0.011527 | 0.064087 | 0.22888 | -0.26093 | 10.9634 | 10.8765 | 10.9222 | 10.7437 | 11.0733 | 11.0001 | 8.3679 | 111.3007 | -10.7254 | 111.6257 | 122.525 | -0.07782 | 119.9295 | 0.045776 | 0.32501 | 122.3053 | 122.6349 | 122.438 | 111.7905 | 111.6257 | 122.5616 | 122.4838 | 119.9295 | 111.7905 | 111.6257 | 122.4838 | 122.438 | 122.5616 | -11.2152 | -2.5864
6228.7188 | 122.7402 | -111.8774 | 10.643 | -0.016556 | -0.0010661 | -0.016067 | 0.0080472 | -0.010461 | -0.0046057 | -0.011527 | 0.045776 | 0.21973 | -0.27466 | 10.6293 | 10.5286 | 10.5835 | 10.4645 | 10.7391 | 10.6705 | 8.3267 | 111.6028 | -10.4233 | 111.9232 | 122.5067 | -0.11444 | 120.2042 | 0.027466 | 0.32043 | 122.3419 | 122.6166 | 122.406 | 112.0972 | 111.9232 | 122.5479 | 122.4609 | 120.2042 | 112.0972 | 111.9232 | 122.4609 | 122.406 | 122.5479 | -10.9177 | -2.3163
6229.7188 | 122.7539 | -112.2437 | 10.3134 | 0.013962 | -0.0010661 | -0.01393 | 0.010183 | -0.010247 | -0.0058875 | -0.00875 | 0.013733 | 0.1831 | -0.33417 | 10.2676 | 10.1898 | 10.2127 | 10.0891 | 10.3912 | 10.3363 | 8.2809 | 111.9095 | -10.1303 | 112.2574 | 122.5113 | -0.1236 | 120.5246 | 0.022888 | 0.3479 | 122.3328 | 122.6349 | 122.4335 | 112.4268 | 112.2574 | 122.58 | 122.4564 | 120.5246 | 112.4268 | 112.2574 | 122.4564 | 122.4335 | 122.58 | -10.6476 | -2.0325
6230.7344 | 122.7036 | -112.4863 | 10.1257 | -0.16151 | 0.0010703 | -0.0094442 | 0.018728 | -0.010247 | -0.0035375 | -0.01345 | 0.07782 | 0.25635 | -0.31586 | 10.0433 | 9.9472 | 9.9884 | 9.9518 | 10.1395 | 10.1486 | 8.2214 | 112.1704 | -9.8694 | 112.5641 | 122.5296 | -0.17853 | 120.7077 | 0.022889 | 0.39368 | 122.438 | 122.6257 | 122.4335 | 112.7426 | 112.5641 | 122.6349 | 122.4747 | 120.7077 | 112.7426 | 112.5641 | 122.4747 | 122.4335 | 122.6349 | -10.4416 | -1.9043
6231.7188 | 122.7219 | -112.793 | 9.7778 | -0.047073 | -0.00021146 | -0.013717 | 0.0065518 | -0.010034 | -0.0056737 | -0.010459 | 0.032043 | 0.21057 | -0.28839 | 9.787 | 9.7092 | 9.7504 | 9.6176 | 9.9152 | 9.8785 | 8.1619 | 112.5046 | -9.5673 | 112.825 | 122.58 | -0.068665 | 120.9549 | 0.10071 | 0.32043 | 122.4106 | 122.7081 | 122.5021 | 113.0035 | 112.825 | 122.6715 | 122.5433 | 120.9549 | 113.0035 | 112.825 | 122.5433 | 122.5021 | 122.6715 | -10.0662 | -1.6159
6232.7188 | 122.7631 | -113.0081 | 9.5398 | 0.0063326 | -0.0023477 | -0.015212 | 0.008688 | -0.010675 | -0.0048193 | -0.011313 | 0.036621 | 0.20599 | -0.28839 | 9.494 | 9.4162 | 9.4711 | 9.3063 | 9.613 | 9.5627 | 8.0658 | 112.7197 | -9.3338 | 113.0447 | 122.5021 | -0.1236 | 121.0739 | 0.022888 | 0.32501 | 122.3145 | 122.6212 | 122.4243 | 113.2141 | 113.0447 | 122.5708 | 122.4792 | 121.0739 | 113.2141 | 113.0447 | 122.4792 | 122.4243 | 122.5708 | -9.8282 | -1.474
6233.7188 | 122.7676 | -113.2278 | 9.3338 | 0.0063326 | -0.0059793 | -0.012862 | 0.010183 | -0.0098202 | -0.0035375 | -0.010886 | 0.050354 | 0.18768 | -0.32959 | 9.2606 | 9.1782 | 9.2377 | 9.1003 | 9.3979 | 9.3475 | 7.9971 | 112.8983 | -9.1461 | 113.2782 | 122.4884 | -0.15564 | 121.225 | 0.013733 | 0.37994 | 122.3282 | 122.6257 | 122.406 | 113.4155 | 113.2782 | 122.5754 | 122.4655 | 121.225 | 113.4155 | 113.2782 | 122.4655 | 122.406 | 122.5754 | -9.6634 | -1.3367
6234.7188 | 122.7539 | -113.4796 | 9.0912 | 0.1284 | -0.00063866 | -0.011153 | 0.0099698 | -0.010034 | -0.0048193 | -0.012595 | 0.041199 | 0.20599 | -0.27466 | 9.0088 | 8.9035 | 8.963 | 8.8165 | 9.1232 | 9.0958 | 7.8827 | 113.205 | -8.8852 | 113.5208 | 122.4884 | -0.18768 | 121.3623 | 0.004577 | 0.31586 | 122.2961 | 122.6028 | 122.3831 | 113.6856 | 113.5208 | 122.5754 | 122.4426 | 121.3623 | 113.6856 | 113.5208 | 122.4426 | 122.3831 | 122.5754 | -9.3658 | -1.2085
6235.7344 | 122.7081 | -113.8275 | 8.8348 | 0.029221 | 0.0042745 | -0.019485 | 0.018301 | -0.0085386 | -0.0058875 | -0.011313 | 0.059509 | 0.22888 | -0.32044 | 8.6884 | 8.5831 | 8.6151 | 8.67 | 8.7662 | 8.8303 | 7.7271 | 113.5071 | -8.606 | 113.887 | 122.5159 | -0.25177 | 121.5546 | -0.004578 | 0.37994 | 122.4976 | 122.5937 | 122.4106 | 114.0564 | 113.887 | 122.6578 | 122.4426 | 121.5546 | 114.0564 | 113.887 | 122.4426 | 122.4106 | 122.6578 | -9.1553 | -1.1078
6236.7188 | 122.7722 | -113.9832 | 8.5785 | 0.03685 | -0.00021146 | -0.011367 | 0.0074062 | -0.0089658 | -0.0039649 | -0.010032 | 0.027466 | 0.20142 | -0.29297 | 8.4869 | 8.4274 | 8.4641 | 8.3405 | 8.6243 | 8.5922 | 7.608 | 113.6902 | -8.3771 | 114.0106 | 122.4701 | -0.15106 | 121.5912 | 0.013733 | 0.32043 | 122.3236 | 122.6074 | 122.4106 | 114.1846 | 114.0106 | 122.5754 | 122.4472 | 121.5912 | 114.1846 | 114.0106 | 122.4472 | 122.4106 | 122.5754 | -8.8715 | -0.97046
6237.7188 | 122.7859 | -114.1983 | 8.3862 | 0.074997 | 0.00021574 | -0.015853 | 0.012106 | -0.0096066 | -0.0054601 | -0.010459 | 0.027466 | 0.20599 | -0.27924 | 8.3084 | 8.2214 | 8.2901 | 8.1436 | 8.4274 | 8.4137 | 7.489 | 113.9191 | -8.1802 | 114.2258 | 122.5067 | -0.16479 | 121.6873 | 0.027466 | 0.3067 | 122.3419 | 122.6257 | 122.4197 | 114.4043 | 114.2258 | 122.612 | 122.4884 | 121.6873 | 114.4043 | 114.2258 | 122.4884 | 122.4197 | 122.612 | -8.6655 | -0.89722
6238.7188 | 122.7859 | -114.3127 | 8.2535 | 0.22758 | -0.0023477 | -0.012008 | 0.011251 | -0.010247 | -0.0061011 | -0.0074682 | 0.064087 | 0.19226 | -0.27466 | 8.1894 | 8.1207 | 8.1619 | 8.0154 | 8.313 | 8.2809 | 7.3975 | 114.0381 | -8.0612 | 114.3768 | 122.5021 | -0.13275 | 121.7102 | 0.027466 | 0.33875 | 122.3282 | 122.6257 | 122.4335 | 114.505 | 114.3768 | 122.5937 | 122.4747 | 121.7102 | 114.505 | 114.3768 | 122.4747 | 122.4335 | 122.5937 | -8.5281 | -0.85602
6239.7188 | 122.7768 | -114.5233 | 8.075 | 0.1284 | -0.0010661 | -0.012862 | 0.0099698 | -0.010034 | -0.0052465 | -0.010673 | 0.022888 | 0.20142 | -0.30212 | 7.9926 | 7.9147 | 7.9697 | 7.8415 | 8.1024 | 8.1161 | 7.2647 | 114.2212 | -7.8735 | 114.5462 | 122.5159 | -0.16022 | 121.788 | 0.041199 | 0.32501 | 122.3648 | 122.6257 | 122.438 | 114.7247 | 114.5462 | 122.6395 | 122.493 | 121.788 | 114.7247 | 114.5462 | 122.493 | 122.438 | 122.6395 | -8.3771 | -0.81024
6240.7188 | 122.7219 | -114.7614 | 7.9056 | -0.2607 | -0.0021341 | -0.0096578 | 0.013388 | -0.011316 | -0.0054601 | -0.010032 | 0.009155 | 0.2243 | -0.31586 | 7.7545 | 7.6767 | 7.7087 | 7.7774 | 7.8781 | 7.9193 | 7.0908 | 114.4455 | -7.6813 | 114.7705 | 122.5159 | -0.22888 | 121.8521 | 0.013733 | 0.32501 | 122.5388 | 122.6395 | 122.4381 | 114.9857 | 114.7705 | 122.6807 | 122.4701 | 121.8521 | 114.9857 | 114.7705 | 122.4701 | 122.4381 | 122.6807 | -8.2214 | -0.81482
6241.7188 | 122.8226 | -114.9033 | 7.6721 | 0.62431 | -0.00085226 | -0.0094442 | 0.014029 | -0.0091794 | -0.0037511 | -0.010032 | 0.11902 | 0.16022 | -0.29755 | 7.6401 | 7.5623 | 7.6172 | 7.3883 | 7.7637 | 7.7179 | 6.9534 | 114.6057 | -7.5119 | 115.0223 | 122.5433 | -0.10986 | 121.8567 | 0.045777 | 0.41656 | 122.2916 | 122.6669 | 122.4655 | 115.0635 | 115.0223 | 122.6212 | 122.5204 | 121.8567 | 115.0635 | 115.0223 | 122.5204 | 122.4655 | 122.6212 | -7.9697 | -0.71869
6242.7188 | 122.8226 | -115.1001 | 7.457 | 0.19707 | 0.0017111 | -0.016067 | 0.017233 | -0.0098202 | -0.0078101 | -0.010245 | 0.082397 | 0.18768 | -0.28381 | 7.4158 | 7.3059 | 7.4066 | 7.1365 | 7.5394 | 7.4615 | 6.7749 | 114.8163 | -7.2693 | 115.1825 | 122.5159 | -0.15106 | 121.875 | 0.004578 | 0.36621 | 122.2366 | 122.6395 | 122.406 | 115.2878 | 115.1825 | 122.5616 | 122.5067 | 121.875 | 115.2878 | 115.1825 | 122.5067 | 122.406 | 122.5616 | -7.7408 | -0.68207
6243.7188 | 122.7997 | -115.2283 | 7.3517 | 0.13603 | -0.0010661 | -0.0098714 | 0.011679 | -0.010888 | -0.0039649 | -0.007041 | 0.073242 | 0.17853 | -0.28381 | 7.2784 | 7.2189 | 7.283 | 7.0633 | 7.4066 | 7.3746 | 6.6788 | 114.9445 | -7.1732 | 115.3015 | 122.5067 | -0.13275 | 121.907 | 0.022888 | 0.35706 | 122.2916 | 122.6349 | 122.4472 | 115.4068 | 115.3015 | 122.6028 | 122.5113 | 121.907 | 115.4068 | 115.3015 | 122.5113 | 122.4472 | 122.6028 | -7.6355 | -0.67291
6244.7188 | 122.8271 | -115.4114 | 7.1915 | 0.23521 | -0.00085226 | -0.0077352 | 0.012747 | -0.0096066 | -0.0046057 | -0.011954 | 0.10071 | 0.18768 | -0.32044 | 7.1594 | 7.0724 | 7.132 | 6.9031 | 7.2968 | 7.2098 | 6.5506 | 115.0909 | -7.0038 | 115.5121 | 122.5708 | -0.11902 | 121.962 | 0.018311 | 0.42114 | 122.3145 | 122.7081 | 122.4838 | 115.5991 | 115.5121 | 122.6212 | 122.5433 | 121.962 | 115.5991 | 115.5121 | 122.5433 | 122.4838 | 122.6212 | -7.5119 | -0.64087
6245.7344 | 122.7631 | -115.5624 | 7.1045 | -0.29121 | -0.0010661 | -0.0096578 | 0.01232 | -0.0098202 | -0.0052465 | -0.010245 | 0.022888 | 0.2243 | -0.30212 | 6.9534 | 6.8802 | 6.9122 | 6.9672 | 7.0908 | 7.1594 | 6.4133 | 115.2603 | -6.8802 | 115.5853 | 122.5159 | -0.2243 | 121.9757 | 0.054932 | 0.32501 | 122.5296 | 122.6532 | 122.4426 | 115.7867 | 115.5853 | 122.7219 | 122.4747 | 121.9757 | 115.7867 | 115.5853 | 122.4747 | 122.4426 | 122.7219 | -7.4066 | -0.69122
6246.7188 | 122.8088 | -115.7135 | 6.8985 | 0.16655 | -0.0017069 | -0.014358 | 0.011251 | -0.0098202 | -0.0067419 | -0.010673 | 0.068665 | 0.1831 | -0.28839 | 6.8344 | 6.7566 | 6.8069 | 6.601 | 6.9626 | 6.9305 | 6.2576 | 115.4251 | -6.7154 | 115.7822 | 122.5479 | -0.14191 | 121.9711 | 0.032043 | 0.35706 | 122.3145 | 122.6761 | 122.4701 | 115.8966 | 115.7822 | 122.644 | 122.5204 | 121.9711 | 115.8966 | 115.7822 | 122.5204 | 122.4701 | 122.644 | -7.1869 | -0.64087
6247.7188 | 122.8363 | -115.8783 | 6.6971 | 0.1284 | 0.0014975 | -0.013717 | 0.010611 | -0.0083248 | -0.0039649 | -0.011954 | 0.082397 | 0.16479 | -0.3067 | 6.6513 | 6.5872 | 6.6422 | 6.3995 | 6.7841 | 6.7429 | 6.102 | 115.5716 | -6.5323 | 115.9607 | 122.5296 | -0.10986 | 121.9803 | 0.045776 | 0.3891 | 122.2778 | 122.6624 | 122.4655 | 116.0431 | 115.9607 | 122.6212 | 122.5204 | 121.9803 | 116.0431 | 115.9607 | 122.5204 | 122.4655 | 122.6212 | -7.0038 | -0.59509
6248.7188 | 122.8546 | -116.0156 | 6.5826 | 0.2047 | 0.0010703 | -0.0079488 | 0.016378 | -0.0081112 | -0.0048193 | -0.0083228 | 0.09613 | 0.17853 | -0.29755 | 6.5277 | 6.459 | 6.5277 | 6.2714 | 6.6513 | 6.6238 | 5.983 | 115.7181 | -6.4041 | 116.1118 | 122.5433 | -0.1236 | 121.9986 | 0.041198 | 0.39368 | 122.287 | 122.6669 | 122.4747 | 116.1942 | 116.1118 | 122.6395 | 122.5433 | 121.9986 | 116.1942 | 116.1118 | 122.5433 | 122.4747 | 122.6395 | -6.8802 | -0.59967
6249.7188 | 122.8546 | -116.153 | 6.4407 | 0.13603 | -0.00042506 | -0.010085 | 0.017019 | -0.0085386 | -0.0071691 | -0.010032 | 0.073242 | 0.1831 | -0.29297 | 6.3904 | 6.3217 | 6.3858 | 6.1523 | 6.5094 | 6.4636 | 5.8594 | 115.86 | -6.2576 | 116.2262 | 122.5433 | -0.11902 | 122.0123 | 0.022888 | 0.36621 | 122.3053 | 122.6624 | 122.4747 | 116.3361 | 116.2262 | 122.6166 | 122.5388 | 122.0123 | 116.3361 | 116.2262 | 122.5388 | 122.4747 | 122.6166 | -6.7337 | -0.58136
6250.7188 | 122.8226 | -116.2811 | 6.3721 | 0.021591 | -0.0012797 | -0.011367 | 0.0097562 | -0.011956 | -0.0039649 | -0.010459 | 0.009155 | 0.1831 | -0.31586 | 6.2485 | 6.221 | 6.2439 | 6.1066 | 6.4224 | 6.395 | 5.7632 | 115.9653 | -6.189 | 116.2903 | 122.5296 | -0.15106 | 122.0444 | 0.022888 | 0.32501 | 122.3877 | 122.7036 | 122.5021 | 116.4642 | 116.2903 | 122.6761 | 122.525 | 122.0444 | 116.4642 | 116.2903 | 122.525 | 122.5021 | 122.6761 | -6.6879 | -0.60882
6251.7188 | 122.8683 | -116.4047 | 6.2119 | 0.17418 | 0.00064294 | -0.0096578 | 0.016806 | -0.009393 | -0.0080237 | -0.010032 | 0.10529 | 0.17853 | -0.27466 | 6.1432 | 6.0608 | 6.1661 | 5.8823 | 6.2942 | 6.2393 | 5.6305 | 116.1301 | -6.0333 | 116.51 | 122.5479 | -0.15106 | 122.0352 | 0.027466 | 0.37994 | 122.287 | 122.699 | 122.4655 | 116.5833 | 116.51 | 122.644 | 122.5708 | 122.0352 | 116.5833 | 116.51 | 122.5708 | 122.4655 | 122.644 | -6.4865 | -0.58136
6252.7188 | 122.8317 | -116.4963 | 6.134 | 0.13603 | 0.0017111 | -0.011367 | 0.013815 | -0.0091794 | -0.0065283 | -0.010245 | 0.073242 | 0.18768 | -0.29755 | 6.0471 | 6.0104 | 6.0608 | 5.8365 | 6.189 | 6.1707 | 5.5573 | 116.1987 | -5.9463 | 116.5695 | 122.5433 | -0.1236 | 122.0535 | 0.036621 | 0.37079 | 122.3328 | 122.6852 | 122.5067 | 116.684 | 116.5695 | 122.6669 | 122.5571 | 122.0535 | 116.684 | 116.5695 | 122.5571 | 122.5067 | 122.6669 | -6.4316 | -0.57678
6253.7188 | 122.8271 | -116.6153 | 5.9921 | 0.19707 | -0.00063866 | -0.012221 | 0.01296 | -0.0098202 | -0.0052465 | -0.0093908 | 0.073242 | 0.16937 | -0.28839 | 5.9235 | 5.8685 | 5.9052 | 5.69 | 6.0471 | 6.0242 | 5.4291 | 116.3269 | -5.8228 | 116.6885 | 122.5388 | -0.1236 | 122.0444 | 0.032044 | 0.36163 | 122.3053 | 122.6624 | 122.4838 | 116.7847 | 116.6885 | 122.6395 | 122.5204 | 122.0444 | 116.7847 | 116.6885 | 122.5204 | 122.4838 | 122.6395 | -6.2805 | -0.56305
6254.7188 | 122.8455 | -116.7023 | 5.9326 | 0.15129 | 0.0017111 | -0.010512 | 0.014669 | -0.009393 | -0.0033239 | -0.0091772 | 0.073242 | 0.16937 | -0.30212 | 5.8594 | 5.8044 | 5.8502 | 5.6305 | 5.983 | 5.9738 | 5.3558 | 116.4001 | -5.7632 | 116.7755 | 122.5616 | -0.12817 | 122.0581 | 0.041199 | 0.37537 | 122.3328 | 122.6852 | 122.5067 | 116.8716 | 116.7755 | 122.6761 | 122.5525 | 122.0581 | 116.8716 | 116.7755 | 122.5525 | 122.5067 | 122.6761 | -6.2347 | -0.57678
6255.7344 | 122.8683 | -116.7847 | 5.864 | 0.13603 | -0.0017069 | -0.0098714 | 0.01296 | -0.011316 | -0.0058875 | -0.010032 | 0.073242 | 0.1831 | -0.29755 | 5.7953 | 5.722 | 5.7449 | 5.6122 | 5.9509 | 5.8868 | 5.2689 | 116.4871 | -5.6808 | 116.8579 | 122.58 | -0.14191 | 122.0535 | 0.022888 | 0.37079 | 122.3969 | 122.7356 | 122.5067 | 116.9678 | 116.8579 | 122.6715 | 122.5296 | 122.0535 | 116.9678 | 116.8579 | 122.5296 | 122.5067 | 122.6715 | -6.1615 | -0.59509
6256.7188 | 122.8912 | -116.9128 | 5.7495 | 0.17418 | 0.00021574 | -0.009017 | 0.017019 | -0.011102 | -0.0086645 | -0.010886 | 0.091553 | 0.17853 | -0.29297 | 5.6671 | 5.5893 | 5.6808 | 5.4153 | 5.8136 | 5.7678 | 5.191 | 116.6199 | -5.571 | 117.0044 | 122.58 | -0.16022 | 122.1039 | 0.01831 | 0.38452 | 122.3282 | 122.7264 | 122.5021 | 117.0914 | 117.0044 | 122.6807 | 122.5937 | 122.1039 | 117.0914 | 117.0044 | 122.5937 | 122.5021 | 122.6807 | -6.0425 | -0.55847
6257.7188 | 122.8317 | -116.9769 | 5.6992 | 0.13603 | 0.00021574 | -0.014571 | 0.015524 | -0.011102 | -0.0048193 | -0.0089636 | 0.059509 | 0.17853 | -0.29755 | 5.603 | 5.5206 | 5.5801 | 5.3833 | 5.7266 | 5.722 | 5.1178 | 116.6794 | -5.5206 | 117.0364 | 122.58 | -0.17853 | 122.0947 | 0.022888 | 0.35705 | 122.3602 | 122.7036 | 122.4976 | 117.1555 | 117.0364 | 122.699 | 122.5571 | 122.0947 | 117.1555 | 117.0364 | 122.5571 | 122.4976 | 122.699 | -5.9967 | -0.58136
6258.7188 | 122.8409 | -117.0319 | 5.6305 | 0.082626 | -0.00085226 | -0.011794 | 0.01296 | -0.011316 | -0.0052465 | -0.012382 | 0.064087 | 0.16479 | -0.32044 | 5.5435 | 5.4794 | 5.5252 | 5.3421 | 5.6808 | 5.6625 | 5.0812 | 116.7114 | -5.4657 | 117.0959 | 122.5754 | -0.15106 | 122.113 | 0.032044 | 0.38452 | 122.374 | 122.7127 | 122.5113 | 117.1967 | 117.0959 | 122.6944 | 122.5571 | 122.113 | 117.1967 | 117.0959 | 122.5571 | 122.5113 | 122.6944 | -5.9509 | -0.54932
6259.7188 | 122.8638 | -117.1188 | 5.5344 | 0.059738 | -0.00085226 | -0.012435 | 0.01232 | -0.0096066 | -0.0048193 | -0.010673 | 0.054932 | 0.17395 | -0.3067 | 5.452 | 5.3787 | 5.4611 | 5.2505 | 5.5984 | 5.571 | 4.9988 | 116.8121 | -5.3604 | 117.1738 | 122.5708 | -0.15564 | 122.1176 | 0.036621 | 0.36163 | 122.3694 | 122.7173 | 122.4976 | 117.2928 | 117.1738 | 122.6898 | 122.58 | 122.1176 | 117.2928 | 117.1738 | 122.58 | 122.4976 | 122.6898 | -5.8411 | -0.53558
6260.7188 | 122.8592 | -117.2195 | 5.4474 | -0.024185 | -0.0021341 | -0.012008 | 0.011892 | -0.011102 | -0.0061011 | -0.00875 | -0.004578 | 0.19226 | -0.29297 | 5.3421 | 5.2963 | 5.3284 | 5.2094 | 5.5069 | 5.5023 | 4.8935 | 116.9266 | -5.2551 | 117.215 | 122.5616 | -0.15106 | 122.113 | 0.054931 | 0.28839 | 122.4289 | 122.7264 | 122.5159 | 117.4118 | 117.215 | 122.7219 | 122.5479 | 122.113 | 117.4118 | 117.215 | 122.5479 | 122.5159 | 122.7219 | -5.7404 | -0.55389
6261.7188 | 122.8912 | -117.2928 | 5.4062 | -0.0012969 | 0.0012839 | -0.013076 | 0.011038 | -0.011743 | -0.0056737 | -0.0085364 | 0 | 0.18768 | -0.28381 | 5.2917 | 5.2139 | 5.2734 | 5.1498 | 5.4337 | 5.4291 | 4.8431 | 117.009 | -5.2185 | 117.2928 | 122.5845 | -0.19226 | 122.1359 | 0.022888 | 0.28381 | 122.4426 | 122.7264 | 122.5067 | 117.4805 | 117.2928 | 122.7219 | 122.5662 | 122.1359 | 117.4805 | 117.2928 | 122.5662 | 122.5067 | 122.7219 | -5.69 | -0.56305
6262.7188 | 122.8638 | -117.3798 | 5.3055 | 0.15129 | -0.00042506 | -0.010726 | 0.012747 | -0.011316 | -0.0039649 | -0.011741 | 0.036621 | 0.17395 | -0.29297 | 5.1727 | 5.1315 | 5.1819 | 5.0217 | 5.3329 | 5.3146 | 4.7516 | 117.0868 | -5.1315 | 117.4164 | 122.5525 | -0.17395 | 122.1313 | 0.009155 | 0.32959 | 122.4014 | 122.7127 | 122.5113 | 117.5537 | 117.4164 | 122.6944 | 122.5616 | 122.1313 | 117.5537 | 117.4164 | 122.5616 | 122.5113 | 122.6944 | -5.5985 | -0.55389
6263.7188 | 122.8867 | -117.4896 | 5.1956 | 0.15892 | -0.0014933 | -0.01393 | 0.01296 | -0.010034 | -0.0056737 | -0.0098182 | 0.027466 | 0.1831 | -0.29755 | 5.0949 | 5.0217 | 5.0766 | 4.9301 | 5.2231 | 5.2368 | 4.6463 | 117.1921 | -5.0125 | 117.5171 | 122.5845 | -0.17395 | 122.1359 | 0.041198 | 0.32501 | 122.4197 | 122.7127 | 122.5113 | 117.6727 | 117.5171 | 122.7264 | 122.5662 | 122.1359 | 117.6727 | 117.5171 | 122.5662 | 122.5113 | 122.7264 | -5.4932 | -0.54932
6264.7188 | 122.9507 | -117.6407 | 5.0858 | 0.052109 | -0.0014933 | -0.014144 | 0.010397 | -0.012384 | -0.0039649 | -0.011527 | 0 | 0.17395 | -0.30212 | 4.9942 | 4.953 | 4.9713 | 4.8569 | 5.1544 | 5.1361 | 4.5547 | 117.3386 | -4.9118 | 117.6407 | 122.6349 | -0.13275 | 122.1954 | 0.050354 | 0.30212 | 122.4976 | 122.7951 | 122.5937 | 117.8146 | 117.6407 | 122.7768 | 122.612 | 122.1954 | 117.8146 | 117.6407 | 122.612 | 122.5937 | 122.7768 | -5.3879 | -0.531
6265.7188 | 122.8683 | -117.6498 | 5.0537 | -0.23018 | -0.00085226 | -0.016921 | 0.01232 | -0.010675 | -0.0050329 | -0.012595 | 0.050354 | 0.19684 | -0.3067 | 4.9438 | 4.8752 | 4.8981 | 4.8431 | 5.0995 | 5.0903 | 4.4907 | 117.3431 | -4.8569 | 117.7002 | 122.5937 | -0.17853 | 122.1405 | 0.036621 | 0.35706 | 122.493 | 122.7493 | 122.525 | 117.8467 | 117.7002 | 122.7402 | 122.5479 | 122.1405 | 117.8467 | 117.7002 | 122.5479 | 122.525 | 122.7402 | -5.3604 | -0.56305
6266.7188 | 122.8683 | -117.6727 | 4.985 | -0.0089264 | -0.0021341 | -0.012649 | 0.013388 | -0.010247 | -0.0046057 | -0.011313 | 0.022888 | 0.1831 | -0.30212 | 4.9255 | 4.66 | 4.8248 | 4.5364 | 5.0262 | 5.0354 | 4.4724 | 117.3706 | -4.8019 | 117.6956 | 122.5983 | -0.32501 | 122.1451 | 0.050354 | 0.32501 | 122.2092 | 122.699 | 122.3328 | 117.8558 | 117.6956 | 122.7081 | 122.4976 | 122.1451 | 117.8558 | 117.6956 | 122.4976 | 122.3328 | 122.7081 | -5.2872 | -0.51269
6267.7188 | 122.9324 | -117.6865 | 4.9896 | -0.10048 | -0.00085226 | -0.010726 | 0.011251 | -0.010247 | -0.0067419 | -0.011741 | 0.027466 | 0.19684 | -0.31586 | 4.9164 | 4.8706 | 4.8843 | 4.6967 | 5.072 | 5.0262 | 4.4586 | 117.3706 | -4.7928 | 117.7139 | 122.6028 | -0.11902 | 122.1451 | 0.036621 | 0.34332 | 122.3831 | 122.7585 | 122.5571 | 117.8833 | 117.7139 | 122.7127 | 122.5708 | 122.1451 | 117.8833 | 117.7139 | 122.5708 | 122.5571 | 122.7127 | -5.3055 | -0.53101
6268.7188 | 122.9233 | -117.7643 | 4.9438 | -0.047073 | -0.0042703 | -0.011367 | 0.0097562 | -0.010461 | -0.0054601 | -0.011741 | 0.041199 | 0.16479 | -0.29297 | 4.8752 | 4.8065 | 4.834 | 4.6509 | 5.0125 | 4.9713 | 4.3991 | 117.4713 | -4.7791 | 117.8055 | 122.6395 | -0.13733 | 122.1634 | 0.027465 | 0.33417 | 122.4152 | 122.7768 | 122.5708 | 117.9291 | 117.8055 | 122.7356 | 122.5983 | 122.1634 | 117.9291 | 117.8055 | 122.5983 | 122.5708 | 122.7356 | -5.2368 | -0.54474
6269.7188 | 122.8821 | -117.8787 | 4.8019 | 0.082626 | -0.0010661 | -0.014785 | 0.011038 | -0.0085386 | -0.0039649 | -0.011741 | 0.009155 | 0.1831 | -0.31128 | 4.6326 | 4.6738 | 4.7012 | 4.541 | 4.8569 | 4.8203 | 4.2709 | 117.5674 | -4.6188 | 117.8879 | 122.5113 | -0.12817 | 122.1497 | 0.01831 | 0.32043 | 122.4197 | 122.7356 | 122.5525 | 118.0618 | 117.8879 | 122.699 | 122.58 | 122.1497 | 118.0618 | 117.8879 | 122.58 | 122.5525 | 122.699 | -5.1132 | -0.53101
6270.7344 | 122.8134 | -118.0161 | 4.7791 | -0.22255 | 0.0014975 | -0.012008 | 0.012747 | -0.011956 | -0.0046057 | -0.010245 | -0.032043 | 0.21515 | -0.33875 | 4.6005 | 4.541 | 4.5456 | 4.6509 | 4.7195 | 4.8248 | 4.1885 | 117.6773 | -4.5639 | 117.984 | 122.6166 | -0.23804 | 122.2046 | 0.045776 | 0.3067 | 122.6669 | 122.7356 | 122.5571 | 118.2312 | 117.984 | 122.8409 | 122.5616 | 122.2046 | 118.2312 | 117.984 | 122.5616 | 122.5571 | 122.8409 | -5.1178 | -0.59051
6271.7188 | 122.9233 | -117.9977 | 4.6967 | -0.069961 | -0.0027751 | -0.010726 | 0.010824 | -0.0089658 | -0.0065283 | -0.0093908 | 0.032043 | 0.19226 | -0.30212 | 4.6188 | 4.5731 | 4.5959 | 4.4266 | 4.7745 | 4.7424 | 4.1748 | 117.6956 | -4.5044 | 118.0298 | 122.6166 | -0.1236 | 122.1725 | 0.045777 | 0.33417 | 122.4243 | 122.7722 | 122.5708 | 118.19 | 118.0298 | 122.7402 | 122.5937 | 122.1725 | 118.19 | 118.0298 | 122.5937 | 122.5708 | 122.7402 | -4.9988 | -0.52185
6272.7188 | 122.9279 | -118.0389 | 4.7012 | -0.039444 | -0.0021341 | -0.010726 | 0.0093288 | -0.0096066 | -0.0056737 | -0.010245 | 0.022888 | 0.17395 | -0.31128 | 4.6005 | 4.5456 | 4.5685 | 4.4083 | 4.7562 | 4.7104 | 4.1336 | 117.7277 | -4.5273 | 118.0618 | 122.6395 | -0.15564 | 122.1725 | 0.009155 | 0.33417 | 122.4472 | 122.7951 | 122.5845 | 118.2129 | 118.0618 | 122.7493 | 122.6074 | 122.1725 | 118.2129 | 118.0618 | 122.6074 | 122.5845 | 122.7493 | -5.0125 | -0.56763
6273.7188 | 122.9645 | -118.1213 | 4.6051 | -0.17677 | -0.00042506 | -0.01393 | 0.010824 | -0.009393 | -0.0052465 | -0.010245 | 0.073242 | 0.16479 | -0.31128 | 4.541 | 4.4861 | 4.5319 | 4.2847 | 4.7104 | 4.6097 | 4.0695 | 117.8101 | -4.4403 | 118.1946 | 122.6624 | -0.11902 | 122.1909 | 0.004577 | 0.38452 | 122.406 | 122.8317 | 122.6074 | 118.2861 | 118.1946 | 122.731 | 122.6532 | 122.1909 | 118.2861 | 118.1946 | 122.6532 | 122.6074 | 122.731 | -4.9164 | -0.53558
6274.7188 | 122.9645 | -118.1763 | 4.5273 | -0.08522 | -0.0012797 | -0.014144 | 0.010611 | -0.010034 | -0.0046057 | -0.011527 | 0.064087 | 0.16022 | -0.29755 | 4.4815 | 4.4312 | 4.4632 | 4.2343 | 4.6417 | 4.5639 | 4.0146 | 117.8787 | -4.3671 | 118.2404 | 122.6578 | -0.096131 | 122.1909 | 0.036621 | 0.36163 | 122.4106 | 122.818 | 122.6074 | 118.3365 | 118.2404 | 122.7402 | 122.6395 | 122.1909 | 118.3365 | 118.2404 | 122.6395 | 122.6074 | 122.7402 | -4.8248 | -0.5127
6275.7188 | 122.8363 | -118.2587 | 4.5181 | -0.23018 | -0.00042506 | -0.011794 | 0.014883 | -0.011102 | -0.0026831 | -0.010673 | -0.018311 | 0.20142 | -0.34332 | 4.3259 | 4.2847 | 4.2801 | 4.3762 | 4.4678 | 4.6005 | 3.923 | 117.9153 | -4.3167 | 118.2404 | 122.5845 | -0.23346 | 122.1817 | 0.082398 | 0.32501 | 122.6349 | 122.7264 | 122.5433 | 118.4601 | 118.2404 | 122.8592 | 122.5388 | 122.1817 | 118.4601 | 118.2404 | 122.5388 | 122.5433 | 122.8592 | -4.8614 | -0.59509
6276.7188 | 122.9462 | -118.3273 | 4.4128 | -0.039444 | -0.0012797 | -0.012008 | 0.010611 | -0.010461 | -0.0054601 | -0.010245 | 0.009155 | 0.16479 | -0.32959 | 4.303 | 4.2755 | 4.2892 | 4.1519 | 4.4724 | 4.4449 | 3.8818 | 117.9977 | -4.248 | 118.3365 | 122.6303 | -0.13733 | 122.2092 | 0.032043 | 0.33875 | 122.4792 | 122.7997 | 122.6028 | 118.4921 | 118.3365 | 122.7722 | 122.6166 | 122.2092 | 118.4921 | 118.3365 | 122.6166 | 122.6028 | 122.7722 | -4.7424 | -0.53101
6277.7188 | 122.937 | -118.396 | 4.3533 | -0.039444 | -0.0027751 | -0.013076 | 0.011038 | -0.011316 | -0.0050329 | -0.012168 | 0.022888 | 0.16479 | -0.31586 | 4.2526 | 4.2114 | 4.2389 | 4.0741 | 4.4174 | 4.3991 | 3.8315 | 118.0801 | -4.1885 | 118.4189 | 122.6486 | -0.14191 | 122.2275 | 0.045776 | 0.33875 | 122.4701 | 122.8134 | 122.6074 | 118.5608 | 118.4189 | 122.7951 | 122.6349 | 122.2275 | 118.5608 | 118.4189 | 122.6349 | 122.6074 | 122.7951 | -4.6692 | -0.52185
6278.7188 | 122.9919 | -118.4647 | 4.2618 | -0.10048 | -0.0025613 | -0.01094 | 0.010824 | -0.010247 | -0.0039649 | -0.010459 | 0.059509 | 0.1831 | -0.29755 | 4.2114 | 4.1519 | 4.1885 | 3.9551 | 4.3533 | 4.2847 | 3.7491 | 118.1671 | -4.0787 | 118.5242 | 122.6761 | -0.10986 | 122.2137 | 0.022888 | 0.35705 | 122.4197 | 122.818 | 122.6166 | 118.6478 | 118.5242 | 122.7493 | 122.6532 | 122.2137 | 118.6478 | 118.5242 | 122.6532 | 122.6166 | 122.7493 | -4.5593 | -0.5127
6279.7188 | 122.9782 | -118.4875 | 4.2252 | -0.09285 | -0.00063866 | -0.014144 | 0.0091152 | -0.0087522 | -0.0048193 | -0.010245 | 0.07782 | 0.1831 | -0.30212 | 4.1885 | 4.1336 | 4.1565 | 3.9322 | 4.3488 | 4.2847 | 3.7216 | 118.1854 | -4.0421 | 118.5654 | 122.6761 | -0.091553 | 122.2092 | 0.059509 | 0.37994 | 122.4197 | 122.8363 | 122.6212 | 118.6707 | 118.5654 | 122.7722 | 122.644 | 122.2092 | 118.6707 | 118.5654 | 122.644 | 122.6212 | 122.7722 | -4.5273 | -0.50354
6280.7188 | 122.8271 | -118.5745 | 4.2435 | -0.22255 | 0.0012839 | -0.0085898 | 0.017019 | -0.010461 | -0.0035375 | -0.0093908 | 0 | 0.20599 | -0.36621 | 3.9505 | 3.9001 | 4.0146 | 4.0649 | 4.1336 | 4.303 | 3.6713 | 118.2083 | -4.0375 | 118.5745 | 122.525 | -0.34332 | 122.2458 | 0.05951 | 0.36621 | 122.6395 | 122.7081 | 122.4747 | 118.7805 | 118.5745 | 122.8775 | 122.5891 | 122.2458 | 118.7805 | 118.5745 | 122.5891 | 122.4747 | 122.8775 | -4.6097 | -0.5722
6281.7188 | 122.9507 | -118.5791 | 4.1473 | -0.1844 | -0.0021341 | -0.012435 | 0.0093288 | -0.0098202 | -0.0063147 | -0.010032 | 0.054932 | 0.16479 | -0.30212 | 4.1107 | 4.0695 | 4.0924 | 3.8727 | 4.2709 | 4.1931 | 3.6392 | 118.277 | -3.9825 | 118.634 | 122.6898 | -0.07782 | 122.2183 | 0.045776 | 0.35706 | 122.4518 | 122.85 | 122.6486 | 118.7439 | 118.634 | 122.7722 | 122.6715 | 122.2183 | 118.7439 | 118.634 | 122.6715 | 122.6486 | 122.7722 | -4.4495 | -0.50812
6282.7188 | 122.9553 | -118.5928 | 4.1428 | -0.19203 | -0.0019205 | -0.015853 | 0.011892 | -0.010461 | -0.0054601 | -0.010245 | 0.07782 | 0.16022 | -0.29755 | 4.0833 | 4.0421 | 4.0695 | 3.8498 | 4.2435 | 4.1794 | 3.6209 | 118.2953 | -3.9825 | 118.6707 | 122.6761 | -0.10071 | 122.2137 | 0.036621 | 0.37537 | 122.4426 | 122.8363 | 122.6349 | 118.7531 | 118.6707 | 122.7722 | 122.6624 | 122.2137 | 118.7531 | 118.6707 | 122.6624 | 122.6349 | 122.7722 | -4.4403 | -0.52185
6283.7188 | 122.9691 | -118.6157 | 4.1611 | -0.077591 | 0.0010703 | -0.016067 | 0.011038 | -0.0085386 | -0.0058875 | -0.0098182 | 0.050354 | 0.16937 | -0.31128 | 4.0878 | 4.0649 | 4.0649 | 3.8681 | 4.248 | 4.2023 | 3.6438 | 118.3044 | -3.9917 | 118.6661 | 122.7036 | -0.096131 | 122.2595 | 0.041199 | 0.36163 | 122.4838 | 122.8638 | 122.6807 | 118.7851 | 118.6661 | 122.818 | 122.6807 | 122.2595 | 118.7851 | 118.6661 | 122.6807 | 122.6807 | 122.818 | -4.4724 | -0.51727
6284.7188 | 122.9736 | -118.6111 | 4.1153 | -0.054703 | -0.0017069 | -0.014785 | 0.011679 | -0.011102 | -0.0054601 | -0.010032 | 0.032043 | 0.17395 | -0.31128 | 4.0375 | 4.0009 | 4.0283 | 3.8361 | 4.1977 | 4.1611 | 3.6118 | 118.2999 | -3.9413 | 118.6432 | 122.6486 | -0.11444 | 122.2229 | 0.045777 | 0.34332 | 122.4472 | 122.8088 | 122.612 | 118.7851 | 118.6432 | 122.7722 | 122.6395 | 122.2229 | 118.7851 | 118.6432 | 122.6395 | 122.612 | 122.7722 | -4.4266 | -0.50354
6285.7188 | 122.8455 | -118.7256 | 4.129 | -0.3141 | 0.0017111 | -0.0098714 | 0.014883 | -0.010461 | -0.0063147 | -0.0098182 | -0.022888 | 0.19226 | -0.3479 | 3.923 | 3.8773 | 3.8818 | 3.9871 | 4.0741 | 4.1794 | 3.5294 | 118.3777 | -3.9368 | 118.7027 | 122.6486 | -0.25177 | 122.2549 | 0.050354 | 0.32501 | 122.7127 | 122.7997 | 122.6028 | 118.9178 | 118.7027 | 122.905 | 122.6074 | 122.2549 | 118.9178 | 118.7027 | 122.6074 | 122.6028 | 122.905 | -4.4769 | -0.59967
6286.7188 | 122.9965 | -118.6752 | 4.0787 | -0.09285 | -0.0012797 | -0.015639 | 0.010611 | -0.0096066 | -0.0056737 | -0.0083228 | 0.064087 | 0.17395 | -0.29755 | 3.9917 | 3.9734 | 3.9917 | 3.772 | 4.184 | 4.1107 | 3.5431 | 118.3777 | -3.9047 | 118.7393 | 122.6669 | -0.10529 | 122.2183 | 0.032044 | 0.36163 | 122.4472 | 122.8592 | 122.6486 | 118.8492 | 118.7393 | 122.7859 | 122.6669 | 122.2183 | 118.8492 | 118.7393 | 122.6669 | 122.6486 | 122.7859 | -4.3762 | -0.53558
6287.7188 | 123.0103 | -118.7347 | 3.9963 | -0.23018 | -0.00085226 | -0.014998 | 0.011038 | -0.010675 | -0.0054601 | -0.012168 | 0.068665 | 0.15106 | -0.3067 | 3.9642 | 3.9276 | 3.9413 | 3.8681 | 3.7628 | 4.0695 | 3.511 | 118.428 | -3.8452 | 118.8034 | 122.699 | -0.068665 | 122.2458 | 0.073242 | 0.37537 | 122.6028 | 122.4976 | 122.6624 | 118.8858 | 118.8034 | 122.8043 | 122.6761 | 122.2458 | 118.8858 | 118.8034 | 122.6761 | 122.6624 | 122.8043 | -4.303 | -0.48523
6288.7188 | 122.9874 | -118.7622 | 3.9551 | -0.19203 | -0.0012797 | -0.010512 | 0.010183 | -0.011316 | -0.0056737 | -0.010886 | 0.073242 | 0.14648 | -0.28839 | 3.923 | 3.8727 | 3.8818 | 3.6987 | 4.097 | 4.0192 | 3.4744 | 118.4738 | -3.8086 | 118.8354 | 122.6852 | -0.082397 | 122.2366 | 0.064087 | 0.36163 | 122.4609 | 122.8592 | 122.6349 | 118.9087 | 118.8354 | 122.7814 | 122.644 | 122.2366 | 118.9087 | 118.8354 | 122.644 | 122.6349 | 122.7814 | -4.2435 | -0.48065
6289.7188 | 123.0057 | -118.8492 | 3.9322 | -0.15388 | -0.0032023 | -0.013717 | 0.013815 | -0.010461 | -0.0065283 | -0.011527 | 0.068665 | 0.15106 | -0.31586 | 3.8635 | 3.8269 | 3.8498 | 3.6438 | 4.0329 | 3.9459 | 3.4103 | 118.5333 | -3.7811 | 118.9178 | 122.7127 | -0.10529 | 122.2595 | 0.013733 | 0.38452 | 122.493 | 122.8821 | 122.6761 | 119.0002 | 118.9178 | 122.7951 | 122.699 | 122.2595 | 119.0002 | 118.9178 | 122.699 | 122.6761 | 122.7951 | -4.248 | -0.52185
6290.7188 | 122.905 | -118.8812 | 3.9276 | -0.23018 | -0.00021146 | -0.014571 | 0.012747 | -0.010461 | -0.0058875 | -0.010673 | 0.041199 | 0.17395 | -0.30212 | 3.772 | 3.7354 | 3.7628 | 3.7308 | 3.9368 | 3.9825 | 3.3691 | 118.5791 | -3.7537 | 118.9224 | 122.6532 | -0.19226 | 122.2504 | 0.054932 | 0.34332 | 122.612 | 122.818 | 122.6166 | 119.0552 | 118.9224 | 122.8638 | 122.644 | 122.2504 | 119.0552 | 118.9224 | 122.644 | 122.6166 | 122.8638 | -4.2297 | -0.55847
6291.7188 | 122.9874 | -118.9316 | 3.8544 | -0.016556 | -0.00042506 | -0.01158 | 0.010183 | -0.0098202 | -0.0063147 | -0.010032 | 0.009155 | 0.17395 | -0.31586 | 3.7308 | 3.6804 | 3.7216 | 3.5568 | 3.9001 | 3.8773 | 3.3234 | 118.6157 | -3.6804 | 118.9407 | 122.6624 | -0.17395 | 122.2549 | 0.022888 | 0.32501 | 122.4884 | 122.8317 | 122.612 | 119.1055 | 118.9407 | 122.8088 | 122.6532 | 122.2549 | 119.1055 | 118.9407 | 122.6532 | 122.612 | 122.8088 | -4.1702 | -0.53101
6292.7188 | 123.0103 | -118.9453 | 3.8177 | -0.09285 | -0.0010661 | -0.017348 | 0.0097562 | -0.012384 | -0.0058875 | -0.013022 | 0.054932 | 0.18768 | -0.28839 | 3.7308 | 3.7079 | 3.7262 | 3.5019 | 3.9001 | 3.8315 | 3.3005 | 118.6569 | -3.6301 | 119.0002 | 122.6761 | -0.10986 | 122.2458 | 0.013733 | 0.34332 | 122.4472 | 122.8455 | 122.6532 | 119.133 | 119.0002 | 122.7768 | 122.6715 | 122.2458 | 119.133 | 119.0002 | 122.6715 | 122.6532 | 122.7768 | -4.1061 | -0.51727
6293.7188 | 123.0331 | -119.0002 | 3.7628 | -0.08522 | -0.0029887 | -0.015853 | 0.010611 | -0.011102 | -0.0043921 | -0.010459 | 0.050354 | 0.16022 | -0.30212 | 3.6942 | 3.6484 | 3.6713 | 3.4607 | 3.8544 | 3.8086 | 3.2547 | 118.6981 | -3.6026 | 119.0506 | 122.6944 | -0.11444 | 122.2549 | 0.045777 | 0.35248 | 122.4609 | 122.8546 | 122.6486 | 119.1605 | 119.0506 | 122.8088 | 122.6715 | 122.2549 | 119.1605 | 119.0506 | 122.6715 | 122.6486 | 122.8088 | -4.0649 | -0.50812
6294.7188 | 123.0057 | -119.0643 | 3.6987 | -0.16151 | -0.0032023 | -0.018844 | 0.011465 | -0.011529 | -0.0061011 | -0.011527 | 0.068665 | 0.15106 | -0.30212 | 3.6255 | 3.5889 | 3.598 | 3.4103 | 3.7994 | 3.7308 | 3.1952 | 118.7622 | -3.5477 | 119.133 | 122.6898 | -0.10986 | 122.2595 | 0.032044 | 0.37079 | 122.4747 | 122.8638 | 122.6532 | 119.2154 | 119.133 | 122.7951 | 122.6624 | 122.2595 | 119.2154 | 119.133 | 122.6624 | 122.6532 | 122.7951 | -4.0009 | -0.50354
6295.7188 | 123.0469 | -119.0781 | 3.6713 | -0.23781 | -0.0021341 | -0.01628 | 0.011251 | -0.010461 | -0.0073827 | -0.0111 | 0.064087 | 0.16479 | -0.31128 | 3.6346 | 3.6026 | 3.6118 | 3.3737 | 3.804 | 3.7399 | 3.186 | 118.7668 | -3.5065 | 119.1422 | 122.7127 | -0.068665 | 122.2641 | 0.068664 | 0.37537 | 122.4518 | 122.8821 | 122.6807 | 119.2429 | 119.1422 | 122.818 | 122.6898 | 122.2641 | 119.2429 | 119.1422 | 122.6898 | 122.6807 | 122.818 | -3.9825 | -0.48523
6296.7344 | 122.905 | -119.1879 | 3.6575 | -0.039444 | 0.0019247 | -0.012008 | 0.020865 | -0.0085386 | -0.0056737 | -0.0111 | 0.054932 | 0.21515 | -0.32044 | 3.4882 | 3.4241 | 3.4561 | 3.4287 | 3.6118 | 3.717 | 3.1082 | 118.8675 | -3.4424 | 119.2429 | 122.6761 | -0.23346 | 122.2961 | 0.059509 | 0.37537 | 122.6166 | 122.7997 | 122.612 | 119.4031 | 119.2429 | 122.905 | 122.644 | 122.2961 | 119.4031 | 119.2429 | 122.644 | 122.612 | 122.905 | -3.978 | -0.54932
6297.7188 | 123.024 | -119.3069 | 3.5431 | 0.03685 | -0.0014933 | -0.018416 | 0.0065518 | -0.0098202 | -0.0065283 | -0.011741 | 0 | 0.15564 | -0.32501 | 3.4653 | 3.4287 | 3.4378 | 3.3142 | 3.6209 | 3.6484 | 3.0808 | 118.9819 | -3.3875 | 119.3069 | 122.7722 | -0.11444 | 122.3877 | 0.10528 | 0.32501 | 122.6212 | 122.9279 | 122.7356 | 119.4626 | 119.3069 | 122.9553 | 122.7448 | 122.3877 | 119.4626 | 119.3069 | 122.7448 | 122.7356 | 122.9553 | -3.8681 | -0.46234
6298.7188 | 123.0423 | -119.2154 | 3.5477 | -0.08522 | -0.0029887 | -0.015212 | 0.011251 | -0.0098202 | -0.0054601 | -0.0096044 | 0.045776 | 0.16937 | -0.3067 | 3.4607 | 3.4424 | 3.4744 | 3.2547 | 3.6667 | 3.5751 | 3.0487 | 118.9087 | -3.3783 | 119.2612 | 122.6761 | -0.10528 | 122.2641 | 0.027466 | 0.35248 | 122.4701 | 122.8821 | 122.6578 | 119.3848 | 119.2612 | 122.7905 | 122.6898 | 122.2641 | 119.3848 | 119.2612 | 122.6898 | 122.6578 | 122.7905 | -3.8544 | -0.49896
6299.7188 | 123.0286 | -119.2566 | 3.5431 | -0.077591 | -0.00042506 | -0.012221 | 0.011038 | -0.0087522 | -0.0056737 | -0.0091772 | 0.045776 | 0.14648 | -0.31586 | 3.447 | 3.4287 | 3.4287 | 3.2364 | 3.6072 | 3.5614 | 3.035 | 118.9407 | -3.3966 | 119.3024 | 122.7036 | -0.11444 | 122.2916 | 0.01831 | 0.36163 | 122.493 | 122.8638 | 122.6852 | 119.4031 | 119.3024 | 122.818 | 122.6852 | 122.2916 | 119.4031 | 119.3024 | 122.6852 | 122.6852 | 122.818 | -3.8589 | -0.50812
6300.7188 | 122.9507 | -119.3161 | 3.5614 | -0.17677 | 0.0010703 | -0.01094 | 0.013388 | -0.010034 | -0.0080237 | -0.011741 | -0.036621 | 0.18768 | -0.36163 | 3.3188 | 3.2684 | 3.2639 | 3.3646 | 3.4561 | 3.5843 | 2.9434 | 118.9545 | -3.3737 | 119.2795 | 122.6349 | -0.29297 | 122.2595 | 0.022889 | 0.32501 | 122.6807 | 122.7722 | 122.5845 | 119.5038 | 119.2795 | 122.9004 | 122.58 | 122.2595 | 119.5038 | 119.2795 | 122.58 | 122.5845 | 122.9004 | -3.923 | -0.61798
6301.7344 | 122.937 | -119.3481 | 3.4927 | -0.24544 | 2.138e-06 | -0.016067 | 0.021292 | -0.0087522 | -0.0058875 | -0.010886 | 0.032043 | 0.20142 | -0.35706 | 3.3554 | 3.2959 | 3.3096 | 3.3234 | 3.511 | 3.5614 | 2.9663 | 118.9911 | -3.2913 | 119.3802 | 122.7036 | -0.19684 | 122.3145 | 0.068664 | 0.3891 | 122.6715 | 122.8592 | 122.644 | 119.5496 | 119.3802 | 122.9095 | 122.6578 | 122.3145 | 119.5496 | 119.3802 | 122.6578 | 122.644 | 122.9095 | -3.8498 | -0.52643
6302.7188 | 123.0606 | -119.3756 | 3.4332 | -0.131 | -0.00042506 | -0.0083762 | 0.008688 | -0.0087522 | -0.0069555 | -0.0098182 | 0.050354 | 0.15564 | -0.32959 | 3.3554 | 3.3371 | 3.36 | 3.1265 | 3.5568 | 3.4744 | 2.9388 | 119.046 | -3.2776 | 119.426 | 122.731 | -0.096131 | 122.3145 | 0.041198 | 0.37994 | 122.5021 | 122.9324 | 122.7127 | 119.5312 | 119.426 | 122.85 | 122.7356 | 122.3145 | 119.5312 | 119.426 | 122.7356 | 122.7127 | 122.85 | -3.7628 | -0.49439
6303.7188 | 123.0377 | -119.4214 | 3.4012 | -0.19966 | -0.0029887 | -0.015639 | 0.010397 | -0.0096066 | -0.0058875 | -0.010032 | 0.054932 | 0.1831 | -0.30212 | 3.2959 | 3.2639 | 3.2959 | 3.0533 | 3.4882 | 3.4378 | 2.8793 | 119.1193 | -3.2181 | 119.4763 | 122.7173 | -0.13733 | 122.3007 | 0.036621 | 0.35706 | 122.4747 | 122.9095 | 122.6852 | 119.6045 | 119.4763 | 122.8592 | 122.7173 | 122.3007 | 119.6045 | 119.4763 | 122.7173 | 122.6852 | 122.8592 | -3.7033 | -0.52185
6304.7188 | 123.0194 | -119.4901 | 3.3188 | -0.0089264 | -0.0021341 | -0.015853 | 0.011251 | -0.0083248 | -0.0054601 | -0.010459 | 0.004578 | 0.16937 | -0.33417 | 3.2135 | 3.1769 | 3.1906 | 3.0441 | 3.3783 | 3.3829 | 2.8336 | 119.1559 | -3.1494 | 119.4946 | 122.7036 | -0.14191 | 122.3236 | 0.064087 | 0.33875 | 122.5342 | 122.8683 | 122.6669 | 119.6594 | 119.4946 | 122.8729 | 122.6807 | 122.3236 | 119.6594 | 119.4946 | 122.6807 | 122.6669 | 122.8729 | -3.653 | -0.48523
6305.7188 | 123.0011 | -119.5129 | 3.3051 | -0.16914 | -0.0010661 | -0.012008 | 0.013601 | -0.0096066 | -0.0067419 | -0.010245 | 0.041199 | 0.17395 | -0.32044 | 3.1952 | 3.1586 | 3.1723 | 3.0579 | 3.3463 | 3.36 | 2.774 | 119.1925 | -3.1311 | 119.5541 | 122.7081 | -0.14649 | 122.287 | 0.054931 | 0.36163 | 122.5708 | 122.8592 | 122.6715 | 119.6869 | 119.5541 | 122.8729 | 122.6852 | 122.287 | 119.6869 | 119.5541 | 122.6852 | 122.6715 | 122.8729 | -3.6255 | -0.53101
6306.7344 | 122.9599 | -119.6365 | 3.2959 | -0.21492 | 0.0034201 | -0.010512 | 0.017874 | -0.009393 | -0.0065283 | -0.011741 | 0 | 0.21057 | -0.35248 | 3.0487 | 3.0212 | 3.0304 | 3.0945 | 3.2181 | 3.3096 | 2.7008 | 119.2841 | -3.0853 | 119.6365 | 122.6852 | -0.27466 | 122.3373 | 0.013733 | 0.35248 | 122.731 | 122.8546 | 122.6578 | 119.8471 | 119.6365 | 122.9462 | 122.6669 | 122.3373 | 119.8471 | 119.6365 | 122.6669 | 122.6578 | 122.9462 | -3.6484 | -0.59509
6307.7188 | 123.0057 | -119.6045 | 3.2135 | 0.12077 | -0.0014933 | -0.016494 | 0.0097562 | -0.0078976 | -0.0078101 | -0.011527 | -0.004578 | 0.12817 | -0.35248 | 3.0579 | 3.0396 | 3.0624 | 2.9022 | 3.2227 | 3.2547 | 2.6962 | 119.252 | -3.0853 | 119.5999 | 122.6624 | -0.17395 | 122.3007 | 0.041199 | 0.3479 | 122.5067 | 122.8271 | 122.644 | 119.7327 | 119.5999 | 122.8592 | 122.6669 | 122.3007 | 119.7327 | 119.5999 | 122.6669 | 122.644 | 122.8592 | -3.566 | -0.51727
6308.7188 | 123.0698 | -119.6411 | 3.1815 | -0.17677 | -0.0014933 | -0.014998 | 0.01232 | -0.011102 | -0.0056737 | -0.010673 | 0.064087 | 0.15564 | -0.31586 | 3.0716 | 3.0533 | 3.0808 | 2.8702 | 3.273 | 3.2043 | 2.6733 | 119.3253 | -3.0258 | 119.7052 | 122.7127 | -0.12817 | 122.3145 | 0.022888 | 0.37994 | 122.5113 | 122.9141 | 122.6944 | 119.7968 | 119.7052 | 122.8455 | 122.7219 | 122.3145 | 119.7968 | 119.7052 | 122.7219 | 122.6944 | 122.8455 | -3.4973 | -0.50812
6309.7188 | 123.0652 | -119.6503 | 3.1769 | -0.19966 | -0.00063866 | -0.011153 | 0.012747 | -0.0096066 | -0.0061011 | -0.010032 | 0.054932 | 0.14191 | -0.31586 | 3.1036 | 3.0579 | 3.0853 | 2.8564 | 3.2593 | 3.2272 | 2.6688 | 119.3344 | -3.035 | 119.7052 | 122.7539 | -0.11902 | 122.319 | 0.050354 | 0.37079 | 122.5067 | 122.9095 | 122.7081 | 119.7922 | 119.7052 | 122.8775 | 122.7356 | 122.319 | 119.7922 | 119.7052 | 122.7356 | 122.7081 | 122.8775 | -3.4927 | -0.50812
6310.7188 | 122.9691 | -119.6915 | 3.186 | -0.131 | 0.0021383 | -0.0092306 | 0.021292 | -0.0083248 | -0.0063147 | -0.010245 | 0.050354 | 0.1831 | -0.34332 | 3.0258 | 2.9709 | 2.9709 | 2.9526 | 3.1631 | 3.2318 | 2.6321 | 119.3481 | -3.0029 | 119.7418 | 122.7173 | -0.21515 | 122.3236 | 0.045777 | 0.39368 | 122.644 | 122.8546 | 122.6624 | 119.8746 | 119.7418 | 122.9233 | 122.6624 | 122.3236 | 119.8746 | 119.7418 | 122.6624 | 122.6624 | 122.9233 | -3.5294 | -0.55389
6311.7188 | 122.9553 | -119.6823 | 3.1677 | -0.0012969 | -0.0010661 | -0.0075216 | 0.018301 | -0.0055478 | -0.0065283 | -0.010673 | 0.041199 | 0.22888 | -0.31128 | 2.9892 | 2.9572 | 2.9709 | 2.9526 | 3.1174 | 3.2227 | 2.6321 | 119.371 | -2.9388 | 119.7235 | 122.6715 | -0.21057 | 122.3145 | 0.054931 | 0.35248 | 122.6349 | 122.7997 | 122.6395 | 119.9112 | 119.7235 | 122.905 | 122.6532 | 122.3145 | 119.9112 | 119.7235 | 122.6532 | 122.6395 | 122.905 | -3.479 | -0.53558
6312.7188 | 123.0652 | -119.6823 | 3.1174 | -0.13863 | -0.00021146 | -0.015212 | 0.0089016 | -0.0098202 | -0.0084509 | -0.010886 | 0.022888 | 0.16022 | -0.3067 | 3.035 | 3.0121 | 3.0212 | 2.8107 | 3.2272 | 3.1586 | 2.623 | 119.3756 | -2.9572 | 119.7052 | 122.7173 | -0.10529 | 122.3053 | 0.041198 | 0.32959 | 122.493 | 122.9095 | 122.6944 | 119.8425 | 119.7052 | 122.8409 | 122.7036 | 122.3053 | 119.8425 | 119.7052 | 122.7036 | 122.6944 | 122.8409 | -3.4241 | -0.49438
6313.7188 | 123.0652 | -119.7418 | 3.0762 | -0.22255 | -0.0010661 | -0.014998 | 0.010824 | -0.0070432 | -0.0056737 | -0.0089636 | 0.041199 | 0.15106 | -0.29297 | 2.9938 | 2.9709 | 2.9938 | 2.7603 | 3.186 | 3.1219 | 2.5864 | 119.4489 | -2.9251 | 119.783 | 122.7356 | -0.10529 | 122.3282 | 0.045776 | 0.33417 | 122.5021 | 122.9279 | 122.7127 | 119.8929 | 119.783 | 122.8638 | 122.7356 | 122.3282 | 119.8929 | 119.783 | 122.7356 | 122.7127 | 122.8638 | -3.3691 | -0.48981
6314.7188 | 123.0881 | -119.7693 | 3.067 | -0.09285 | -0.0023477 | -0.013076 | 0.011892 | -0.010247 | -0.0052465 | -0.0098182 | 0.045776 | 0.16937 | -0.32044 | 2.9572 | 2.9297 | 2.9572 | 2.7283 | 3.1494 | 3.0899 | 2.5314 | 119.4489 | -2.8976 | 119.8151 | 122.7264 | -0.13733 | 122.3007 | 0.022888 | 0.36621 | 122.4976 | 122.9187 | 122.699 | 119.9387 | 119.8151 | 122.8592 | 122.7264 | 122.3007 | 119.9387 | 119.8151 | 122.7264 | 122.699 | 122.8592 | -3.3875 | -0.53558
6315.7344 | 122.9736 | -119.8746 | 3.0212 | -0.131 | 0.00064294 | -0.010085 | 0.019796 | -0.0061886 | -0.0052465 | -0.010886 | 0.054932 | 0.19226 | -0.3479 | 2.8656 | 2.8015 | 2.8244 | 2.8244 | 2.9938 | 3.0808 | 2.4902 | 119.5267 | -2.829 | 119.9295 | 122.7402 | -0.21973 | 122.3648 | 0.05951 | 0.40283 | 122.699 | 122.8683 | 122.6761 | 120.0668 | 119.9295 | 122.9553 | 122.699 | 122.3648 | 120.0668 | 119.9295 | 122.699 | 122.6761 | 122.9553 | -3.3691 | -0.53101
6316.7188 | 123.0515 | -119.8425 | 3.0029 | -0.19203 | 0.0012839 | -0.0098714 | 0.010824 | -0.0089658 | -0.0058875 | -0.0093908 | 0.054932 | 0.16022 | -0.32501 | 2.916 | 2.8931 | 2.8244 | 3.0624 | 3.1494 | 3.0441 | 2.4857 | 119.5175 | -2.8427 | 119.8975 | 122.7585 | -0.10986 | 122.3282 | 0.041198 | 0.37994 | 122.905 | 122.9919 | 122.7356 | 120.0027 | 119.8975 | 122.8867 | 122.6669 | 122.3282 | 120.0027 | 119.8975 | 122.6669 | 122.7356 | 122.8867 | -3.3279 | -0.51727
6317.7188 | 123.0606 | -119.8425 | 2.9984 | -0.09285 | -0.00021146 | -0.014358 | 0.0099698 | -0.010247 | -0.0075963 | -0.00875 | 0.041199 | 0.16022 | -0.32501 | 2.8931 | 2.8839 | 2.8839 | 2.6871 | 3.0762 | 3.0441 | 2.4994 | 119.5175 | -2.8381 | 119.8837 | 122.7356 | -0.11444 | 122.3419 | 0.045776 | 0.36621 | 122.5296 | 122.9187 | 122.7264 | 120.0027 | 119.8837 | 122.8867 | 122.7264 | 122.3419 | 120.0027 | 119.8837 | 122.7264 | 122.7264 | 122.8867 | -3.3234 | -0.49896
6318.7188 | 123.0652 | -119.838 | 3.0075 | -0.13863 | -0.0012797 | -0.014571 | 0.012747 | -0.009393 | -0.0071691 | -0.010032 | 0.022888 | 0.16022 | -0.30212 | 2.8885 | 2.8748 | 2.8885 | 2.71 | 3.0853 | 3.0487 | 2.504 | 119.5358 | -2.8473 | 119.8608 | 122.7264 | -0.13275 | 122.3419 | 0.041199 | 0.32501 | 122.5479 | 122.9233 | 122.7127 | 119.9982 | 119.8608 | 122.8867 | 122.7264 | 122.3419 | 119.9982 | 119.8608 | 122.7264 | 122.7127 | 122.8867 | -3.3096 | -0.50354
6319.7188 | 123.0789 | -119.9066 | 2.948 | -0.12337 | -0.0017069 | -0.01393 | 0.012106 | -0.012597 | -0.0061011 | -0.0085364 | 0.059509 | 0.15106 | -0.32501 | 2.8473 | 2.8244 | 2.8564 | 2.6596 | 3.0441 | 2.9984 | 2.4445 | 119.5816 | -2.7969 | 119.9661 | 122.7539 | -0.1236 | 122.3511 | 0.050354 | 0.38452 | 122.5662 | 122.9507 | 122.731 | 120.0577 | 119.9661 | 122.905 | 122.7631 | 122.3511 | 120.0577 | 119.9661 | 122.7631 | 122.731 | 122.905 | -3.273 | -0.50354
6320.7344 | 123.0011 | -119.9524 | 2.948 | -0.24544 | 0.00085654 | -0.013076 | 0.021505 | -0.0098202 | -0.0035375 | -0.012595 | 0.036621 | 0.20142 | -0.35706 | 2.774 | 2.7191 | 2.7237 | 2.7374 | 2.9388 | 3.0029 | 2.3987 | 119.5953 | -2.7466 | 119.989 | 122.7264 | -0.22888 | 122.3511 | 0.054932 | 0.39368 | 122.6898 | 122.8912 | 122.6715 | 120.1538 | 119.989 | 122.9553 | 122.6761 | 122.3511 | 120.1538 | 119.989 | 122.6761 | 122.6715 | 122.9553 | -3.3051 | -0.54932
6321.7188 | 123.0881 | -119.9753 | 2.8885 | -0.069961 | -0.0017069 | -0.014144 | 0.010824 | -0.010675 | -0.0041785 | -0.012168 | 0.022888 | 0.14191 | -0.29755 | 2.8061 | 2.7786 | 2.7924 | 2.5681 | 2.9938 | 2.9343 | 2.3941 | 119.6777 | -2.7466 | 119.9982 | 122.7814 | -0.10986 | 122.3694 | 0.045776 | 0.32043 | 122.5433 | 122.9691 | 122.7539 | 120.1172 | 119.9982 | 122.9095 | 122.7676 | 122.3694 | 120.1172 | 119.9982 | 122.7676 | 122.7539 | 122.9095 | -3.186 | -0.49438
6322.7188 | 123.1018 | -119.9341 | 2.8976 | -0.08522 | -0.0014933 | -0.013076 | 0.01296 | -0.0078976 | -0.0050329 | -0.0098182 | 0.045776 | 0.14648 | -0.31128 | 2.8107 | 2.7969 | 2.7786 | 2.5589 | 2.9938 | 2.9205 | 2.3987 | 119.6228 | -2.7512 | 119.9799 | 122.7448 | -0.10071 | 122.3328 | 0.022888 | 0.35705 | 122.493 | 122.9279 | 122.731 | 120.0806 | 119.9799 | 122.8546 | 122.7127 | 122.3328 | 120.0806 | 119.9799 | 122.7127 | 122.731 | 122.8546 | -3.2089 | -0.49896
6323.7188 | 123.0972 | -120.0165 | 2.8519 | -0.23781 | -0.00085226 | -0.011367 | 0.01296 | -0.010247 | -0.0065283 | -0.012168 | 0.045776 | 0.14191 | -0.31586 | 2.7649 | 2.7374 | 2.7512 | 2.6642 | 2.536 | 2.9022 | 2.33 | 119.7006 | -2.71 | 120.0623 | 122.7814 | -0.11444 | 122.3465 | 0.050354 | 0.36163 | 122.6807 | 122.5525 | 122.7539 | 120.1584 | 120.0623 | 122.9187 | 122.7676 | 122.3465 | 120.1584 | 120.0623 | 122.7676 | 122.7539 | 122.9187 | -3.1677 | -0.52185
6324.7188 | 123.0743 | -120.0165 | 2.8244 | -0.09285 | 0.00042934 | -0.011794 | 0.010611 | -0.010034 | -0.0078101 | -0.012168 | 0.032043 | 0.15106 | -0.3067 | 2.7512 | 2.71 | 2.7328 | 2.5406 | 2.916 | 2.8931 | 2.3392 | 119.7098 | -2.6733 | 120.0485 | 122.7676 | -0.11444 | 122.3557 | 0.068664 | 0.33874 | 122.5571 | 122.9324 | 122.7264 | 120.1675 | 120.0485 | 122.9095 | 122.7493 | 122.3557 | 120.1675 | 120.0485 | 122.7493 | 122.7264 | 122.9095 | -3.1311 | -0.48523
6325.7188 | 123.1018 | -120.0668 | 2.7878 | -0.20729 | 0.00021574 | -0.010299 | 0.011251 | -0.011743 | -0.0050329 | -0.010459 | 0.059509 | 0.16479 | -0.32959 | 2.7191 | 2.6917 | 2.71 | 2.4765 | 2.9022 | 2.8519 | 2.2934 | 119.7372 | -2.623 | 120.1263 | 122.7859 | -0.096131 | 122.3602 | 0.064087 | 0.3891 | 122.5433 | 122.9691 | 122.7585 | 120.2316 | 120.1263 | 122.9187 | 122.7768 | 122.3602 | 120.2316 | 120.1263 | 122.7768 | 122.7585 | 122.9187 | -3.1174 | -0.49438
6326.7188 | 123.0927 | -120.0989 | 2.7283 | -0.08522 | -0.0012797 | -0.010085 | 0.01232 | -0.010461 | -0.0069555 | -0.0111 | 0.050354 | 0.16022 | -0.31128 | 2.6733 | 2.6321 | 2.6413 | 2.4307 | 2.8381 | 2.7924 | 2.2614 | 119.7876 | -2.5681 | 120.1492 | 122.7722 | -0.09613 | 122.3602 | 0.064087 | 0.36163 | 122.5296 | 122.937 | 122.731 | 120.2591 | 120.1492 | 122.8912 | 122.7402 | 122.3602 | 120.2591 | 120.1492 | 122.7402 | 122.731 | 122.8912 | -3.0395 | -0.46692
6327.7188 | 123.0927 | -120.0485 | 2.8015 | -0.10048 | -0.0034159 | -0.0079488 | 0.012106 | -0.010675 | -0.0054601 | -0.0085364 | 0.054932 | 0.17395 | -0.31128 | 2.6825 | 2.6505 | 2.6779 | 2.4719 | 2.8748 | 2.8198 | 2.2888 | 119.7372 | -2.6276 | 120.1035 | 122.731 | -0.15106 | 122.3373 | 0.01831 | 0.36621 | 122.5204 | 122.9233 | 122.699 | 120.2225 | 120.1035 | 122.8683 | 122.7264 | 122.3373 | 120.2225 | 120.1035 | 122.7264 | 122.699 | 122.8683 | -3.1128 | -0.5127
6328.7188 | 123.0881 | -120.1584 | 2.7237 | -0.10811 | -0.00042506 | -0.01628 | 0.012106 | -0.0089658 | -0.0073827 | -0.010245 | 0.036621 | 0.15106 | -0.31128 | 2.5955 | 2.5635 | 2.5955 | 2.4078 | 2.7924 | 2.7695 | 2.2339 | 119.8471 | -2.5726 | 120.195 | 122.7539 | -0.16022 | 122.3923 | 0.045776 | 0.3479 | 122.5662 | 122.9507 | 122.7219 | 120.3094 | 120.195 | 122.9279 | 122.7539 | 122.3923 | 120.3094 | 120.195 | 122.7539 | 122.7219 | 122.9279 | -3.035 | -0.48981
6329.7188 | 123.1018 | -120.1859 | 2.6871 | -0.12337 | -0.00063866 | -0.014998 | 0.011251 | -0.011529 | -0.0061011 | -0.0096044 | 0.068665 | 0.16479 | -0.3067 | 2.623 | 2.5818 | 2.5955 | 2.3483 | 2.7924 | 2.7328 | 2.211 | 119.8791 | -2.5223 | 120.2545 | 122.8088 | -0.10529 | 122.3969 | 0.045776 | 0.37537 | 122.5342 | 122.9782 | 122.7676 | 120.3506 | 120.2545 | 122.9187 | 122.7814 | 122.3969 | 120.3506 | 120.2545 | 122.7814 | 122.7676 | 122.9187 | -2.9938 | -0.47607
6330.7188 | 123.0835 | -120.1996 | 2.6642 | -0.08522 | -0.0021341 | -0.0079488 | 0.0093288 | -0.012384 | -0.0026831 | -0.0096044 | 0.018311 | 0.13275 | -0.33875 | 2.5726 | 2.5635 | 2.536 | 2.3575 | 2.7695 | 2.7191 | 2.1652 | 119.8608 | -2.5314 | 120.2179 | 122.7722 | -0.10071 | 122.3648 | 0.054931 | 0.35706 | 122.5571 | 122.9691 | 122.7631 | 120.3323 | 120.2179 | 122.9187 | 122.7356 | 122.3648 | 120.3323 | 120.2179 | 122.7356 | 122.7631 | 122.9187 | -3.0029 | -0.49896

## Thermal Data
Fire Time | Norht 25 C | Cable 1 | Cable 2
-0.6521 | 25.0024 | 23.0484 | 23.2643
0.3479 | 25.0121 | 23.0322 | 23.2718
1.3479 | 25.0188 | 23.0316 | 23.2676
2.3479 | 25.1338 | 23.0373 | 23.2691
3.3479 | 25.8185 | 23.0335 | 23.2705
4.3635 | 27.3023 | 23.0422 | 23.2723
5.3479 | 29.5213 | 23.0375 | 23.2759
6.3479 | 32.3583 | 23.0414 | 23.2743
7.3479 | 35.7046 | 23.0349 | 23.2806
8.3479 | 39.4445 | 23.0523 | 23.3013
9.3479 | 43.5104 | 23.0415 | 23.3097
10.3479 | 47.8576 | 23.0575 | 23.3224
11.3479 | 52.4423 | 23.0501 | 23.3536
12.3479 | 57.266 | 23.0735 | 23.3781
13.3479 | 62.2587 | 23.0845 | 23.4208
14.3479 | 67.3388 | 23.0995 | 23.4732
15.3479 | 72.5636 | 23.126 | 23.5285
16.3479 | 77.9448 | 23.1464 | 23.5927
17.3479 | 83.4108 | 23.1794 | 23.6759
18.3479 | 88.9279 | 23.197 | 23.766
19.3479 | 94.5792 | 23.2563 | 23.8705
20.3479 | 100.2947 | 23.2881 | 23.9838
21.3479 | 106.0644 | 23.3558 | 24.1088
22.3479 | 111.872 | 23.3989 | 24.2424
23.3635 | 117.6928 | 23.4775 | 24.4037
24.3479 | 123.58 | 23.5339 | 24.5548
25.3479 | 129.4989 | 23.6155 | 24.7364
26.3479 | 135.4246 | 23.6963 | 24.9211
27.3479 | 141.3469 | 23.7899 | 25.1206
28.3635 | 147.258 | 23.8985 | 25.333
29.3479 | 153.199 | 24.0009 | 25.5584
30.3479 | 159.0882 | 24.128 | 25.8012
31.3635 | 165.015 | 24.2474 | 26.0614
32.3479 | 170.9395 | 24.3985 | 26.338
33.3479 | 176.8678 | 24.519 | 26.6375
34.3479 | 182.7576 | 24.6836 | 26.9587
35.3479 | 188.5599 | 24.8328 | 27.2833
36.3479 | 194.3489 | 25.0225 | 27.6319
37.3479 | 200.154 | 25.1889 | 27.9925
38.3479 | 205.9831 | 25.3873 | 28.3845
39.3635 | 211.8555 | 25.5983 | 28.7922
40.926 | 221.0125 | 25.9339 | 29.477
41.4885 | 224.2575 | 26.0725 | 29.7326
42.3479 | 229.0822 | 26.2725 | 30.1381
43.3479 | 234.7491 | 26.5467 | 30.6306
44.6292 | 242.0595 | 26.8872 | 31.2785
45.3635 | 246.3368 | 27.1066 | 31.6717
46.3479 | 252.0419 | 27.3802 | 32.2162
47.3479 | 257.7108 | 27.7016 | 32.788
48.3479 | 263.3616 | 28.0145 | 33.3911
49.3479 | 269.0241 | 28.3533 | 34.0111
50.3635 | 274.7031 | 28.6941 | 34.6573
51.3479 | 280.3038 | 29.0515 | 35.3186
52.3479 | 285.8498 | 29.4514 | 36.0084
53.3479 | 291.4254 | 29.8286 | 36.7433
54.3635 | 296.9145 | 30.2489 | 37.4876
55.3635 | 302.4787 | 30.6708 | 38.2653
56.3479 | 307.8742 | 31.1198 | 39.0561
57.3479 | 313.2831 | 31.5614 | 39.8726
58.3479 | 318.6369 | 32.052 | 40.7123
59.3635 | 323.9006 | 32.5239 | 41.5753
60.3479 | 329.0999 | 33.0297 | 42.4639
61.3479 | 334.3425 | 33.5524 | 43.3731
62.3479 | 339.8611 | 34.0773 | 44.311
63.3479 | 345.1527 | 34.6431 | 45.2688
64.3479 | 350.255 | 35.2107 | 46.2667
65.3479 | 355.5115 | 35.8126 | 47.2821
66.3479 | 360.6408 | 36.4163 | 48.3217
67.3479 | 365.6836 | 37.054 | 49.3884
68.3479 | 370.6701 | 37.6883 | 50.4686
69.3479 | 375.7052 | 38.3486 | 51.5854
70.3479 | 380.5856 | 39.0252 | 52.7334
71.3635 | 385.2122 | 39.7297 | 53.9114
72.3479 | 389.3877 | 40.4519 | 55.1392
73.3635 | 393.2819 | 41.1801 | 56.4212
74.3479 | 396.7757 | 41.9284 | 57.7268
75.3479 | 400.0038 | 42.6973 | 59.0647
76.3479 | 403.1504 | 43.4951 | 60.4256
77.3635 | 406.1281 | 44.2941 | 61.8147
78.3635 | 408.9538 | 45.1534 | 63.2211
79.3635 | 411.5784 | 46.018 | 64.641
80.3635 | 414.2297 | 46.901 | 66.0659
81.3635 | 416.6663 | 47.7849 | 67.4989
82.3479 | 418.9835 | 48.6924 | 68.9305
83.3635 | 421.0452 | 49.6127 | 70.3867
84.3479 | 422.9113 | 50.5452 | 71.8529
85.3635 | 424.5966 | 51.4808 | 73.3223
86.3479 | 425.923 | 52.4153 | 74.7941
87.3479 | 427.052 | 53.3755 | 76.2638
88.3479 | 428.1205 | 54.3096 | 77.7336
89.3479 | 428.7345 | 55.275 | 79.1862
90.3635 | 429.2085 | 56.2446 | 80.6437
91.3479 | 429.654 | 57.217 | 82.0886
92.3479 | 429.887 | 58.1543 | 83.4972
93.3635 | 430.0341 | 59.1296 | 84.9251
94.3635 | 430.2032 | 60.0728 | 86.3128
95.3635 | 430.2095 | 61.0223 | 87.6962
96.3635 | 430.2457 | 61.9682 | 89.0723
97.3479 | 430.3631 | 62.9045 | 90.426
98.3635 | 430.3729 | 63.8491 | 91.7647
99.3479 | 430.3866 | 64.7763 | 93.0977
100.3479 | 430.1693 | 65.7117 | 94.4041
101.3479 | 429.9148 | 66.62 | 95.6867
102.3479 | 429.6129 | 67.5472 | 96.9547
103.3479 | 429.6738 | 68.4242 | 98.2078
104.3479 | 429.7546 | 69.3222 | 99.4373
105.3635 | 429.8096 | 70.1859 | 100.6375
106.3479 | 429.813 | 71.0642 | 101.8136
107.3479 | 429.7848 | 71.9258 | 102.9731
108.3479 | 429.651 | 72.798 | 104.1104
109.3479 | 429.5687 | 73.6565 | 105.2253
110.3479 | 429.7088 | 74.5266 | 106.3296
111.3479 | 429.8281 | 75.3798 | 107.4449
112.3479 | 429.9513 | 76.2292 | 108.5335
113.3479 | 430.2661 | 77.0877 | 109.6034
114.3479 | 430.6132 | 77.9092 | 110.6729
115.3635 | 430.8164 | 78.7735 | 111.7521
116.3479 | 431.0372 | 79.5845 | 112.801
117.3479 | 431.0476 | 80.4131 | 113.8503
118.3635 | 431.2094 | 81.2335 | 114.8977
119.3635 | 431.1688 | 82.057 | 115.9518
120.3479 | 431.2061 | 82.8568 | 116.9941
121.3635 | 431.1816 | 83.6506 | 118.0375
122.3479 | 431.4148 | 84.4608 | 119.0805
123.3635 | 431.6589 | 85.2349 | 120.1098
124.3635 | 431.6992 | 86.0186 | 121.1297
125.3479 | 431.8187 | 86.783 | 122.1437
126.3635 | 432.0845 | 87.5845 | 123.1308
127.3479 | 432.1402 | 88.3392 | 124.1216
128.3635 | 432.1832 | 89.1164 | 125.0811
129.3479 | 432.2018 | 89.8746 | 126.0499
130.3479 | 432.3861 | 90.6521 | 126.988
131.3635 | 432.55 | 91.4181 | 127.9353
132.3479 | 432.6299 | 92.1826 | 128.8678
133.3635 | 432.5409 | 92.9504 | 129.7975
134.3479 | 432.3762 | 93.7252 | 130.7411
135.3635 | 432.2596 | 94.4736 | 131.6795
136.3479 | 432.2897 | 95.2088 | 132.5881
137.3635 | 432.2629 | 95.963 | 133.4999
138.3479 | 432.3657 | 96.6955 | 134.3938
139.3635 | 432.6082 | 97.4447 | 135.281
140.3479 | 432.7175 | 98.161 | 136.159
141.3635 | 432.9204 | 98.9129 | 137.03
142.3479 | 433.2588 | 99.6207 | 137.9035
143.3635 | 433.2508 | 100.3646 | 138.7617
144.3479 | 433.3491 | 101.0828 | 139.6091
145.3635 | 433.4945 | 101.8318 | 140.4651
146.3479 | 433.6216 | 102.5428 | 141.311
147.3479 | 433.5289 | 103.26 | 142.1517
148.3635 | 433.6161 | 103.9843 | 142.9773
149.3479 | 433.7049 | 104.6819 | 143.8098
150.3479 | 433.6969 | 105.384 | 144.6268
151.3635 | 433.9329 | 106.0739 | 145.4374
152.3479 | 434.0956 | 106.777 | 146.2408
153.3479 | 434.1929 | 107.452 | 147.0319
154.3479 | 434.1808 | 108.157 | 147.8056
155.3479 | 433.9874 | 108.8484 | 148.5777
156.3479 | 433.7955 | 109.5465 | 149.3493
157.3479 | 433.8928 | 110.2214 | 150.1219
158.3479 | 434.2114 | 110.8932 | 150.8851
159.3635 | 434.583 | 111.5637 | 151.6452
160.3479 | 434.542 | 112.2489 | 152.3968
161.3479 | 434.5607 | 112.9291 | 153.1441
162.3479 | 434.7805 | 113.588 | 153.8815
163.3479 | 435.0055 | 114.2448 | 154.6179
164.3479 | 434.9939 | 114.8875 | 155.3535
165.3479 | 435.0578 | 115.5319 | 156.0798
166.3479 | 434.9648 | 116.1646 | 156.7986
167.3479 | 435.0922 | 116.7939 | 157.5208
168.3479 | 435.1037 | 117.4012 | 158.2212
169.3479 | 435.0647 | 118.0246 | 158.9196
170.3635 | 434.8924 | 118.6329 | 159.6047
171.3479 | 434.8342 | 119.2288 | 160.2954
172.3479 | 434.814 | 119.839 | 160.9649
173.3479 | 434.8725 | 120.4163 | 161.6334
174.3479 | 434.9115 | 121.0059 | 162.2927
175.3635 | 434.8466 | 121.6098 | 162.9518
176.3479 | 434.6194 | 122.1696 | 163.5942
177.3479 | 434.3422 | 122.7407 | 164.2423
178.3635 | 434.2878 | 123.2936 | 164.8783
179.3479 | 434.1479 | 123.8238 | 165.5172
180.3635 | 434.0274 | 124.346 | 166.1614
181.3479 | 433.7508 | 124.8753 | 166.7944
182.3635 | 433.4819 | 125.4034 | 167.4315
183.3479 | 433.5824 | 125.9065 | 168.0693
184.3635 | 433.476 | 126.4126 | 168.7009
185.3479 | 433.4454 | 126.9237 | 169.3189
186.3635 | 433.2682 | 127.4034 | 169.9327
187.3479 | 433.2506 | 127.907 | 170.5339
188.3479 | 433.4316 | 128.3817 | 171.1216
189.3479 | 433.42 | 128.8759 | 171.7006
190.3479 | 433.4894 | 129.3425 | 172.293
191.3635 | 433.472 | 129.8251 | 172.8736
192.3479 | 433.2955 | 130.2851 | 173.447
193.3635 | 433.2757 | 130.7583 | 174.0069
194.3479 | 433.2746 | 131.2259 | 174.5652
195.3479 | 433.3804 | 131.6853 | 175.1002
196.3479 | 433.3596 | 132.1596 | 175.6387
197.3479 | 433.3511 | 132.6132 | 176.1758
198.3635 | 433.3408 | 133.1 | 176.7076
199.3479 | 433.3053 | 133.5705 | 177.2276
200.3479 | 433.1825 | 134.0623 | 177.7469
201.3479 | 433.0898 | 134.5364 | 178.2617
202.3479 | 433.1605 | 135.0266 | 178.7747
203.3635 | 433.2956 | 135.5208 | 179.305
204.3635 | 433.4152 | 136.0167 | 179.8387
205.3635 | 433.3992 | 136.5083 | 180.3723
206.3479 | 433.4487 | 137.0082 | 180.8853
207.3479 | 433.3823 | 137.5197 | 181.4224
208.3635 | 433.2852 | 137.9987 | 181.9383
209.3479 | 433.1572 | 138.5227 | 182.4719
210.3479 | 433.206 | 139.0154 | 182.9983
211.3635 | 433.1892 | 139.5369 | 183.5227
212.3479 | 433.2546 | 140.0264 | 184.0471
213.3635 | 433.0995 | 140.5437 | 184.5618
214.3479 | 433.0685 | 141.0533 | 185.0773
215.3479 | 433.0752 | 141.5718 | 185.5935
216.3479 | 432.9645 | 142.0634 | 186.1083
217.3635 | 432.9091 | 142.5949 | 186.6159
218.3479 | 432.8431 | 143.1038 | 187.1149
219.3479 | 432.8268 | 143.6207 | 187.6169
220.3479 | 432.5664 | 144.1328 | 188.0988
221.3479 | 432.5253 | 144.6579 | 188.5779
222.3479 | 432.4074 | 145.1774 | 189.0627
223.3635 | 432.4505 | 145.7015 | 189.5632
224.3479 | 432.57 | 146.226 | 190.053
225.3635 | 432.608 | 146.7491 | 190.5493
226.3635 | 432.7938 | 147.2901 | 191.0509
227.3479 | 432.796 | 147.8021 | 191.5344
228.3479 | 432.6985 | 148.3445 | 192.0295
229.3479 | 432.7467 | 148.8678 | 192.5062
230.3479 | 432.8881 | 149.4142 | 192.9834
231.3479 | 432.8755 | 149.944 | 193.4609
232.3479 | 432.9093 | 150.5033 | 193.9388
233.3635 | 432.9767 | 151.0487 | 194.4169
234.3635 | 433.084 | 151.5764 | 194.9059
235.3635 | 433.0671 | 152.136 | 195.4049
236.3479 | 433.1524 | 152.665 | 195.9043
237.3635 | 433.2845 | 153.2253 | 196.4161
238.3635 | 433.3533 | 153.7722 | 196.9303
239.3635 | 433.3198 | 154.319 | 197.4529
240.3635 | 433.3926 | 154.8703 | 197.9807
241.3635 | 433.4424 | 155.4227 | 198.51
242.3635 | 433.4712 | 155.9742 | 199.034
243.3635 | 433.3185 | 156.5172 | 199.5758
244.3635 | 433.2307 | 157.0852 | 200.0927
245.3635 | 433.1762 | 157.6195 | 200.6009
246.3635 | 433.1404 | 158.1866 | 201.1102
247.3635 | 433.2363 | 158.7347 | 201.63
248.3635 | 433.0666 | 159.2979 | 202.1508
249.3635 | 432.7731 | 159.8538 | 202.672
250.3635 | 432.5696 | 160.4393 | 203.1993
251.3635 | 432.4614 | 160.9988 | 203.7185
252.3479 | 432.3711 | 161.5614 | 204.2451
253.3635 | 432.3537 | 162.1343 | 204.7591
254.3635 | 432.1963 | 162.6869 | 205.2768
255.3635 | 432.044 | 163.2796 | 205.7887
256.3635 | 432.1577 | 163.829 | 206.2976
257.3635 | 432.2064 | 164.4086 | 206.7973
258.3479 | 432.1703 | 164.9637 | 207.3011
259.3479 | 432.25 | 165.5491 | 207.809
260.3635 | 432.026 | 166.0947 | 208.302
261.3635 | 432.0259 | 166.6715 | 208.7833
262.3635 | 432.0343 | 167.2305 | 209.2758
263.3635 | 432.1134 | 167.7932 | 209.7361
264.3479 | 432.1198 | 168.3503 | 210.2036
265.3635 | 432.0802 | 168.903 | 210.6704
266.3479 | 432.0432 | 169.4831 | 211.1333
267.3635 | 432.2265 | 170.0334 | 211.6067
268.3635 | 432.2229 | 170.604 | 212.0744
269.3635 | 432.2725 | 171.1463 | 212.5579
270.3635 | 432.127 | 171.7033 | 213.0282
271.3635 | 432.0829 | 172.2378 | 213.4971
272.3635 | 432.2842 | 172.8031 | 213.9656
273.3635 | 432.3255 | 173.3413 | 214.444
274.3635 | 432.3164 | 173.8977 | 214.927
275.3635 | 432.2581 | 174.4436 | 215.4164
276.3635 | 432.2129 | 174.9955 | 215.9106
277.3635 | 432.2071 | 175.5335 | 216.392
278.3635 | 432.3791 | 176.0995 | 216.8745
279.3479 | 432.4143 | 176.656 | 217.3659
280.3635 | 432.2226 | 177.1984 | 217.8446
281.3635 | 432.1923 | 177.7608 | 218.3204
282.3635 | 432.2266 | 178.3094 | 218.8084
283.3635 | 432.261 | 178.8732 | 219.2846
284.3635 | 432.3905 | 179.4174 | 219.7599
285.3635 | 432.2621 | 179.9748 | 220.2298
286.3635 | 432.1307 | 180.5124 | 220.6976
287.3635 | 432.0784 | 181.0447 | 221.1708
288.3635 | 431.891 | 181.5869 | 221.6482
289.3635 | 431.8128 | 182.1142 | 222.1177
290.3635 | 431.7131 | 182.6505 | 222.5998
291.3479 | 431.5961 | 183.1528 | 223.0791
292.3635 | 431.4799 | 183.7029 | 223.561
293.3635 | 431.3512 | 184.2037 | 224.0434
294.3635 | 431.3103 | 184.7325 | 224.5409
295.3635 | 431.4498 | 185.2358 | 225.0277
296.3635 | 431.5006 | 185.7749 | 225.5123
297.3479 | 431.4659 | 186.2689 | 226.0009
298.3635 | 431.4428 | 186.7723 | 226.5036
299.3635 | 431.4332 | 187.2959 | 226.9965
300.3479 | 431.3246 | 187.7819 | 227.4985
301.3635 | 431.2095 | 188.2977 | 227.9889
302.3635 | 431.1594 | 188.7876 | 228.4793
303.3635 | 431.1819 | 189.3076 | 228.9521
304.3635 | 431.1757 | 189.8037 | 229.4267
305.3635 | 431.2169 | 190.318 | 229.8879
306.3479 | 431.1067 | 190.8123 | 230.3408
307.3635 | 431.2603 | 191.317 | 230.799
308.3635 | 431.4297 | 191.8081 | 231.2542
309.3635 | 431.4056 | 192.3126 | 231.6961
310.3635 | 431.401 | 192.8256 | 232.1445
311.3635 | 431.4018 | 193.3126 | 232.5707
312.3635 | 431.4268 | 193.8229 | 232.9987
313.3635 | 431.4105 | 194.2912 | 233.422
314.3635 | 431.248 | 194.8041 | 233.8606
315.3635 | 431.3245 | 195.2838 | 234.2903
316.3635 | 431.4736 | 195.7842 | 234.7267
317.3635 | 431.5918 | 196.2687 | 235.1584
318.3635 | 431.7436 | 196.7612 | 235.6219
319.3635 | 431.8883 | 197.2491 | 236.0812
320.3635 | 432.041 | 197.7045 | 236.5504
321.3635 | 431.8791 | 198.2057 | 237.0155
322.3635 | 431.6451 | 198.668 | 237.488
323.3635 | 431.4317 | 199.1593 | 237.9589
324.3635 | 431.3522 | 199.6177 | 238.4391
325.3635 | 431.5932 | 200.0749 | 238.9088
326.3635 | 431.6818 | 200.5292 | 239.3733
327.3635 | 431.4832 | 200.9777 | 239.822
328.3635 | 431.5694 | 201.4409 | 240.2564
329.3635 | 431.6555 | 201.8992 | 240.699
330.3635 | 431.6077 | 202.3568 | 241.1265
331.3635 | 431.6406 | 202.795 | 241.5631
332.3635 | 431.6428 | 203.2672 | 241.9911
333.3479 | 431.8657 | 203.7236 | 242.4202
334.3635 | 432.0744 | 204.1892 | 242.8629
335.3635 | 432.1062 | 204.6445 | 243.2952
336.3635 | 431.9482 | 205.119 | 243.7346
337.3635 | 431.8732 | 205.5756 | 244.1759
338.3635 | 431.7601 | 206.034 | 244.6102
339.3635 | 431.6397 | 206.4996 | 245.0518
340.3635 | 431.6387 | 206.95 | 245.4913
341.3635 | 431.6543 | 207.4225 | 245.92
342.3635 | 431.5476 | 207.8645 | 246.3637
343.3635 | 431.3295 | 208.3454 | 246.7955
344.3635 | 431.1979 | 208.8017 | 247.2259
345.3635 | 431.2673 | 209.2794 | 247.6623
346.3635 | 431.2492 | 209.7226 | 248.0847
347.3635 | 431.2167 | 210.1745 | 248.5112
348.3635 | 431.3938 | 210.6339 | 248.9327
349.3635 | 431.3649 | 211.0712 | 249.3489
350.3635 | 431.5608 | 211.5149 | 249.7532
351.3635 | 431.62 | 211.9682 | 250.1506
352.3635 | 431.8359 | 212.3896 | 250.5537
353.3635 | 431.8851 | 212.8413 | 250.9412
354.3635 | 431.9569 | 213.2624 | 251.3428
355.3635 | 432.1083 | 213.7266 | 251.7562
356.3635 | 432.1246 | 214.1281 | 252.1422
357.3635 | 432.0834 | 214.5506 | 252.4822
358.3635 | 432.1575 | 214.9914 | 252.8508
359.3635 | 432.2334 | 215.3942 | 253.1622
360.3635 | 432.1091 | 215.8453 | 253.5218
361.3635 | 431.9509 | 216.2515 | 253.8623
362.3635 | 431.8661 | 216.6891 | 254.1951
363.3635 | 431.5876 | 217.1248 | 254.4911
364.3635 | 431.3412 | 217.5409 | 254.8275
365.3635 | 431.2437 | 217.9815 | 255.2108
366.3635 | 431.241 | 218.3825 | 255.4722
367.3635 | 431.1616 | 218.8517 | 255.769
368.3635 | 431.1099 | 219.2709 | 256.1602
369.3635 | 430.8349 | 219.6875 | 256.4653
370.3635 | 430.7661 | 220.1377 | 256.7657
371.3635 | 430.774 | 220.5446 | 257.1067
372.3635 | 430.7932 | 220.9807 | 257.4509
373.3635 | 430.7518 | 221.4137 | 257.7667
374.3635 | 430.646 | 221.828 | 258.0705
375.3635 | 430.6501 | 222.2755 | 258.3597
376.3635 | 430.637 | 222.6712 | 258.6447
377.3635 | 430.6214 | 223.1041 | 258.9439
378.3635 | 430.558 | 223.4978 | 259.2438
379.3635 | 430.4899 | 223.8832 | 259.559
380.3635 | 430.4457 | 224.3105 | 259.8508
381.3635 | 430.4857 | 224.6867 | 260.1416
382.3635 | 430.6267 | 225.1004 | 260.4685
383.3635 | 430.8526 | 225.4839 | 260.7756
384.3635 | 430.9009 | 225.886 | 261.0786
385.3635 | 430.8142 | 226.2806 | 261.3803
386.3479 | 430.812 | 226.6543 | 261.6599
387.3635 | 430.8471 | 227.0624 | 261.9516
388.3635 | 430.8257 | 227.43 | 262.1959
389.3635 | 430.856 | 227.8154 | 262.3416
390.3635 | 430.9355 | 228.2127 | 262.4813
391.3635 | 430.9472 | 228.5916 | 262.8064
392.3635 | 430.9043 | 229.0064 | 263.0827
393.3635 | 430.9149 | 229.3638 | 263.3201
394.3635 | 430.753 | 229.7705 | 263.4872
395.3635 | 430.5881 | 230.1645 | 263.6166
396.3635 | 430.5922 | 230.5442 | 263.9286
397.3635 | 430.6057 | 230.9579 | 264.1983
398.3635 | 430.631 | 231.3214 | 264.4384
399.3635 | 430.3949 | 231.7078 | 264.6748
400.3635 | 430.4548 | 232.1166 | 264.9062
401.3635 | 430.65 | 232.4824 | 265.1326
402.3635 | 430.9206 | 232.9032 | 265.3638
403.3635 | 430.9776 | 233.2879 | 265.5695
404.3635 | 430.9611 | 233.6853 | 265.774
405.4104 | 431.2616 | 234.0925 | 266.0054
406.3635 | 431.3712 | 234.4659 | 266.1967
407.3635 | 431.3768 | 234.8642 | 266.4865
408.3635 | 431.3835 | 235.2605 | 266.7068
409.3635 | 431.4855 | 235.6567 | 266.9379
410.3635 | 431.461 | 236.0546 | 267.179
411.3635 | 431.3587 | 236.4476 | 267.4034
412.3635 | 431.4039 | 236.84 | 267.6124
413.3635 | 431.402 | 237.2296 | 267.8512
414.3635 | 431.3974 | 237.6315 | 268.0766
415.3635 | 431.2916 | 238.03 | 268.3768
416.3635 | 431.238 | 238.4444 | 268.6127
417.3635 | 431.2436 | 238.8628 | 268.8509
418.3635 | 431.1289 | 239.2453 | 269.0925
419.3635 | 431.1327 | 239.6605 | 269.3191
420.3635 | 431.1712 | 240.0576 | 269.5445
421.3635 | 431.1444 | 240.4613 | 269.7539
422.3635 | 431.1101 | 240.8764 | 269.9585
423.3635 | 430.8933 | 241.2868 | 270.1586
424.3635 | 430.9687 | 241.7075 | 270.3416
425.3635 | 431.1747 | 242.0756 | 270.5151
426.3635 | 431.3132 | 242.5412 | 270.6828
427.3635 | 431.4835 | 242.9931 | 270.8353
428.3635 | 431.394 | 243.4133 | 270.9813
429.3635 | 431.2825 | 243.8888 | 271.121
430.3635 | 431.3822 | 244.3107 | 271.2693
431.3635 | 431.4237 | 244.7745 | 271.4334
432.3635 | 431.353 | 245.2429 | 271.5821
433.3635 | 431.2555 | 245.6898 | 271.7287
434.3635 | 431.2755 | 246.1732 | 271.8778
435.3635 | 431.197 | 246.6156 | 272.0186
436.3635 | 431.2591 | 247.1 | 272.1558
437.3635 | 431.4941 | 247.579 | 272.2891
438.3635 | 431.5726 | 248.0844 | 272.4147
439.3635 | 431.634 | 248.6041 | 272.5389
440.3635 | 431.7637 | 249.0616 | 272.6684
441.3635 | 431.776 | 249.5169 | 272.8083
442.3635 | 431.9015 | 249.9005 | 272.9466
443.3635 | 431.8392 | 250.2253 | 273.0918
444.3635 | 431.6049 | 250.3349 | 273.2224
445.3635 | 431.3474 | 249.9858 | 273.3537
446.3635 | 431.3787 | 249.7069 | 273.4727
447.3635 | 431.4128 | 249.4787 | 273.5995
448.3635 | 431.1676 | 251.1462 | 273.8035
449.3635 | 431.0022 | 251.7773 | 273.97
450.3635 | 431.041 | 252.2178 | 274.138
451.3635 | 430.9189 | 252.6338 | 274.3123
452.3635 | 430.7373 | 252.9869 | 274.4796
453.3635 | 430.6102 | 253.3454 | 274.6537
454.3635 | 430.5953 | 253.6748 | 274.8186
455.3635 | 430.5509 | 253.9959 | 274.9826
456.3635 | 430.4325 | 254.3479 | 275.0745
457.3635 | 430.445 | 254.6576 | 275.2026
458.3635 | 430.5579 | 255.0522 | 275.3351
459.3635 | 430.6228 | 255.4183 | 275.5629
460.3635 | 430.5948 | 255.7885 | 275.7367
461.3635 | 430.4002 | 256.1703 | 275.9126
462.3635 | 430.2802 | 256.5504 | 276.084
463.3635 | 430.1267 | 256.9298 | 276.2444
464.3635 | 430.0604 | 257.2891 | 276.3814
465.3635 | 429.9916 | 257.6619 | 276.5376
466.3635 | 429.9061 | 257.9904 | 276.6622
467.3635 | 429.8358 | 258.2081 | 276.797
468.3635 | 429.8655 | 258.4433 | 276.9319
469.3635 | 430.0879 | 258.7498 | 277.073
470.3635 | 430.2454 | 259.1023 | 277.2119
471.3635 | 430.4258 | 259.4755 | 277.3472
472.3479 | 430.4778 | 259.8151 | 277.486
473.3635 | 430.4285 | 260.1239 | 277.6345
474.3635 | 430.5211 | 260.4199 | 277.79
475.3635 | 430.5101 | 260.5943 | 277.9075
476.3635 | 430.562 | 260.775 | 277.9712
477.3635 | 430.576 | 260.423 | 278.0689
478.3635 | 430.4812 | 260.2272 | 278.1666
479.3635 | 430.5 | 260.1698 | 278.2107
480.3635 | 430.5712 | 260.1687 | 278.3003
481.3635 | 430.6943 | 260.165 | 278.4344
482.3635 | 430.7666 | 260.2306 | 278.565
483.3635 | 430.7189 | 260.2851 | 278.6973
484.3635 | 430.5885 | 260.3568 | 278.8349
485.3635 | 430.617 | 260.442 | 278.9874
486.3635 | 430.5271 | 260.5062 | 279.1417
487.3635 | 430.6104 | 260.6221 | 279.2912
488.3635 | 430.6313 | 260.7711 | 279.4472
489.3635 | 430.3411 | 260.9109 | 279.592
490.3635 | 430.4006 | 261.0937 | 279.7211
491.3635 | 430.4504 | 261.254 | 279.8654
492.3635 | 430.4361 | 261.4656 | 280.026
493.3635 | 430.5549 | 261.6675 | 280.2153
494.3635 | 430.5948 | 261.8816 | 280.3115
495.3635 | 430.4267 | 262.0857 | 280.4719
496.3635 | 430.2679 | 262.3001 | 280.5826
497.3635 | 430.4935 | 262.528 | 280.7113
498.3635 | 430.7209 | 262.7392 | 280.8642
499.3635 | 430.6331 | 262.9777 | 281.0103
500.3635 | 430.4724 | 263.1934 | 281.1429
501.3635 | 430.5899 | 263.4244 | 281.2092
502.3635 | 430.8248 | 263.6563 | 281.2616
503.3635 | 431.0197 | 263.8729 | 281.4536
504.3635 | 431.3575 | 264.1115 | 281.621
505.3635 | 431.3944 | 264.2881 | 281.7897
506.3635 | 431.2396 | 264.477 | 281.921
507.3635 | 431.0527 | 264.6462 | 282.1004
508.3635 | 431.1418 | 264.818 | 282.2925
509.3635 | 431.2367 | 264.9951 | 282.4723
510.3635 | 431.3211 | 265.16 | 282.6391
511.3635 | 431.2996 | 265.3536 | 282.7972
512.3635 | 431.2413 | 265.513 | 282.9797
513.3635 | 431.1469 | 265.6782 | 283.1963
514.3635 | 430.9986 | 265.8098 | 283.4348
515.3635 | 430.8875 | 265.9585 | 283.6491
516.3635 | 430.7251 | 266.1071 | 283.8575
517.3635 | 430.7028 | 266.244 | 284.0829
518.3635 | 430.6238 | 266.4189 | 284.2436
519.3479 | 430.5995 | 266.5558 | 284.4315
520.3479 | 430.6884 | 266.7412 | 284.6349
521.3635 | 430.63 | 266.8668 | 284.8071
522.3479 | 430.3428 | 266.9828 | 285.0039
523.3635 | 430.2697 | 267.131 | 285.1969
524.3635 | 430.2248 | 267.2289 | 285.3727
525.3635 | 430.1444 | 267.3734 | 285.5325
526.3635 | 429.9164 | 267.4987 | 285.7067
527.3635 | 429.9136 | 267.6427 | 285.8737
528.3635 | 430.0907 | 267.7854 | 286.0944
529.3635 | 430.2028 | 267.9351 | 286.2549
530.3635 | 430.3062 | 268.0814 | 286.4211
531.3635 | 430.3407 | 268.2172 | 286.6318
532.3635 | 430.292 | 268.3563 | 286.8319
533.3635 | 430.4975 | 268.5008 | 287.0328
534.3635 | 430.3079 | 268.6751 | 287.2131
535.3635 | 430.1216 | 268.8316 | 287.3851
536.3635 | 430.0147 | 268.9555 | 287.5053
537.3635 | 429.9543 | 269.0863 | 287.7239
538.3635 | 429.8188 | 269.1843 | 287.8985
539.3635 | 429.6459 | 269.3047 | 288.0546
540.3635 | 429.5479 | 269.4307 | 288.2464
541.3635 | 429.6186 | 269.5281 | 288.4381
542.3635 | 429.7236 | 269.6703 | 288.6624
543.3635 | 429.8004 | 269.7785 | 288.9146
544.3635 | 429.8974 | 269.9057 | 289.1048
545.3479 | 430.0776 | 270.0362 | 289.232
546.3635 | 430.0912 | 270.1499 | 289.3837
547.3635 | 430.1385 | 270.28 | 289.5833
548.3635 | 430.05 | 270.3899 | 289.7778
549.3635 | 430.115 | 270.5174 | 289.9775
550.3635 | 430.1819 | 270.6304 | 290.1839
551.3635 | 430.021 | 270.7678 | 290.3767
552.3635 | 430.0895 | 270.903 | 290.6157
553.3635 | 430.2033 | 271.0114 | 290.839
554.3635 | 430.189 | 271.1519 | 290.9987
555.3635 | 430.2264 | 271.2768 | 291.1857
556.3635 | 430.3994 | 271.4139 | 291.3838
557.3635 | 430.4694 | 271.546 | 291.6199
558.3635 | 430.3712 | 271.6712 | 291.8103
559.3635 | 430.3425 | 271.816 | 291.9199
560.3635 | 430.3912 | 271.9343 | 292.1148
561.3635 | 430.4484 | 272.097 | 292.3459
562.3635 | 430.5996 | 272.2408 | 292.5036
563.3635 | 430.7756 | 272.3755 | 292.6591
564.3635 | 430.9193 | 272.5247 | 292.8624
565.3635 | 430.9615 | 272.6543 | 293.0196
566.3635 | 430.991 | 272.8232 | 293.2088
567.3635 | 430.9391 | 272.9408 | 293.4066
568.3479 | 431.0356 | 273.0979 | 293.6382
569.3635 | 431.0176 | 273.2419 | 293.8115
570.3479 | 430.9641 | 273.3715 | 293.9537
571.3635 | 431.007 | 273.5157 | 294.1389
572.3635 | 430.8691 | 273.6381 | 294.3126
573.3635 | 430.8539 | 273.7853 | 294.4884
574.3635 | 430.8467 | 273.9288 | 294.7065
575.3635 | 430.6988 | 274.0674 | 294.9343
576.3479 | 430.5643 | 274.2219 | 295.1068
577.3635 | 430.36 | 274.3522 | 295.3108
578.3635 | 430.2454 | 274.508 | 295.4765
579.3635 | 430.1485 | 274.6395 | 295.6385
580.3635 | 430.2532 | 274.7901 | 295.8354
581.3635 | 430.4072 | 274.9497 | 296.0171
582.3635 | 430.2746 | 275.0768 | 296.6121
583.3635 | 430.2029 | 275.2411 | 296.9712
584.3635 | 430.1283 | 275.3739 | 297.2697
585.3635 | 430.0448 | 275.5222 | 297.6224
586.3635 | 430.0472 | 275.6913 | 297.891
587.3635 | 430.1468 | 275.8435 | 298.1879
588.3635 | 430.2056 | 275.9923 | 298.4491
589.3635 | 430.2876 | 276.1315 | 298.7246
590.3635 | 430.2311 | 276.2895 | 298.9851
591.3635 | 430.1217 | 276.4105 | 299.257
592.3635 | 430.2329 | 276.581 | 299.5113
593.3635 | 430.303 | 276.7308 | 299.7461
594.3635 | 430.4082 | 276.8647 | 299.9688
595.3635 | 430.7011 | 277.021 | 300.2358
596.3635 | 430.9416 | 277.1478 | 300.4941
597.3635 | 430.9185 | 277.2969 | 300.7301
598.3635 | 430.8625 | 277.4672 | 300.9834
599.3635 | 430.9199 | 277.5827 | 301.2052
600.3635 | 430.9374 | 277.747 | 301.4475
601.3635 | 430.8981 | 277.8839 | 301.6697
602.3635 | 430.9602 | 278.0384 | 301.8986
603.3635 | 430.9696 | 278.1864 | 302.1495
604.3635 | 430.8022 | 278.3177 | 302.3771
605.3635 | 430.534 | 278.4671 | 302.6358
606.3635 | 430.6133 | 278.6061 | 302.8552
607.3635 | 430.655 | 278.7722 | 303.0938
608.3635 | 430.5891 | 278.9077 | 303.3155
609.3635 | 430.5905 | 279.0621 | 303.5444
610.3635 | 430.7093 | 279.2088 | 303.7667
611.3635 | 430.7927 | 279.3425 | 303.9782
612.3635 | 430.6992 | 279.503 | 304.1902
613.3635 | 430.456 | 279.6367 | 304.3949
614.3635 | 430.1366 | 279.7969 | 304.5917
615.3635 | 429.9139 | 279.9379 | 304.7889
616.3635 | 429.9495 | 280.0779 | 305.0113
617.3635 | 429.9466 | 280.234 | 305.2047
618.3635 | 429.9279 | 280.3738 | 305.3913
619.3635 | 430.0037 | 280.5267 | 305.5707
620.3635 | 429.8914 | 280.6844 | 305.7434
621.3635 | 429.9642 | 280.8189 | 305.9189
622.3635 | 430.0968 | 280.9797 | 306.0869
623.3635 | 430.1036 | 281.1255 | 306.268
624.3635 | 430.1686 | 281.3002 | 306.4483
625.3635 | 430.3394 | 281.4258 | 306.6202
626.3635 | 430.2794 | 281.5707 | 306.8002
627.3635 | 430.0784 | 281.7419 | 306.9817
628.3635 | 429.9009 | 281.8674 | 307.1542
629.3635 | 429.8883 | 282.0429 | 307.3363
630.3479 | 429.9172 | 282.1832 | 307.5172
631.3635 | 429.7554 | 282.3289 | 307.6952
632.3635 | 429.6871 | 282.4704 | 307.8806
633.3635 | 429.8145 | 282.6003 | 308.067
634.3635 | 429.7357 | 282.7694 | 308.2446
635.3635 | 429.8015 | 282.9121 | 308.4133
636.3635 | 429.7698 | 283.0669 | 308.5898
637.3635 | 429.6628 | 283.2083 | 308.7388
638.3635 | 429.6597 | 283.3373 | 308.9112
639.3635 | 429.4181 | 283.4773 | 309.0662
640.3635 | 429.3402 | 283.6169 | 309.2295
641.3635 | 429.3716 | 283.7786 | 309.3993
642.3635 | 429.4662 | 283.9255 | 309.5463
643.3635 | 429.747 | 284.0662 | 309.6905
644.3635 | 430.0131 | 284.2231 | 309.8186
645.3635 | 430.1131 | 284.352 | 309.9598
646.3635 | 430.2705 | 284.5029 | 310.0906
647.3635 | 430.3321 | 284.6583 | 310.2171
648.3635 | 430.3914 | 284.8033 | 310.3695
649.3635 | 430.422 | 284.9727 | 310.5212
650.3635 | 430.533 | 285.1078 | 310.6584
651.3635 | 430.274 | 285.2768 | 310.8097
652.3635 | 430.1014 | 285.4283 | 310.9696
653.3635 | 430.1955 | 285.5745 | 311.1279
654.3635 | 430.2279 | 285.744 | 311.2775
655.3635 | 430.1565 | 285.859 | 311.4361
656.3635 | 430.3227 | 286.0468 | 311.5993
657.3635 | 430.0982 | 286.1865 | 311.7587
658.3635 | 429.9407 | 286.3406 | 311.9153
659.3635 | 429.8907 | 286.4947 | 312.0859
660.3635 | 429.8909 | 286.6346 | 312.2419
661.3479 | 429.8769 | 286.799 | 312.3991
662.3479 | 429.7238 | 286.9476 | 312.545
663.3479 | 429.6663 | 287.1081 | 312.687
664.3479 | 429.7816 | 287.269 | 312.8176
665.3479 | 429.8215 | 287.4146 | 312.9552
666.3479 | 429.9327 | 287.5859 | 313.0979
667.3479 | 430.057 | 287.7103 | 313.2297
668.3635 | 430.0545 | 287.8723 | 313.3665
669.3479 | 430.0868 | 288.0357 | 313.5039
670.3635 | 429.9061 | 288.1741 | 313.6509
671.3479 | 429.8386 | 288.3444 | 313.79
672.3635 | 429.8683 | 288.4869 | 313.922
673.3479 | 429.8852 | 288.6376 | 314.0603
674.3635 | 429.809 | 288.7943 | 314.1834
675.3479 | 429.9759 | 288.9452 | 314.3093
676.3635 | 429.9479 | 289.1137 | 314.4492
677.3479 | 429.9108 | 289.2416 | 314.5796
678.3635 | 430.0133 | 289.4198 | 314.7059
679.3479 | 429.9617 | 289.5449 | 314.8363
680.3479 | 430.0211 | 289.7227 | 314.9647
681.3479 | 430.1363 | 289.8686 | 315.1017
682.3479 | 430.1905 | 290.0247 | 315.2363
683.3635 | 430.1063 | 290.1945 | 315.3854
684.3479 | 429.9165 | 290.3559 | 315.5165
685.3479 | 430.1123 | 290.5368 | 315.6572
686.3479 | 430.2748 | 290.6774 | 315.7912
687.3479 | 430.3182 | 290.8276 | 315.9257
688.3479 | 430.4095 | 290.9797 | 316.0492
689.3479 | 430.4505 | 291.1108 | 316.1767
690.3479 | 430.4932 | 291.2705 | 316.3021
691.3479 | 430.5399 | 291.4118 | 316.4373
692.3479 | 430.5625 | 291.5719 | 316.5523
693.3635 | 430.4787 | 291.7128 | 316.6682
694.3479 | 430.3436 | 291.8653 | 316.8024
695.3635 | 430.3418 | 292.0212 | 316.921
696.3479 | 430.3781 | 292.1538 | 317.0623
697.3635 | 430.4166 | 292.319 | 317.1841
698.3479 | 430.3884 | 292.441 | 317.3033
699.3479 | 430.2512 | 292.5987 | 317.4243
700.3479 | 430.0899 | 292.7404 | 317.5443
701.3479 | 430.1544 | 292.8775 | 317.655
702.3635 | 430.1862 | 293.0474 | 317.7671
703.3479 | 430.1126 | 293.1808 | 317.8819
704.3479 | 429.9465 | 293.3405 | 317.9915
705.3479 | 429.9094 | 293.4862 | 318.1046
706.3479 | 429.9182 | 293.6339 | 318.2181
707.3479 | 429.9876 | 293.7854 | 318.3196
708.3479 | 429.9683 | 293.9377 | 318.4189
709.3635 | 430.0881 | 294.0876 | 318.5113
710.3635 | 430.2098 | 294.2681 | 318.6077
711.3635 | 430.1765 | 294.5246 | 318.7112
712.3479 | 430.049 | 294.7318 | 318.8131
713.3635 | 429.915 | 294.8998 | 318.9157
714.3479 | 429.9022 | 295.0875 | 319.0129
715.3635 | 429.8946 | 295.2221 | 319.1156
716.3479 | 429.9975 | 295.3744 | 319.2087
717.3635 | 430.0322 | 295.5091 | 319.3059
718.3479 | 430.0778 | 295.6475 | 319.3987
719.3635 | 430.062 | 295.7794 | 319.4914
720.3479 | 429.9949 | 295.8984 | 319.5733
721.3635 | 429.999 | 296.0306 | 319.6641
722.3479 | 429.9368 | 296.1564 | 319.747
723.3479 | 430.1286 | 296.277 | 319.8319
724.3479 | 430.3518 | 296.3979 | 319.9017
725.3479 | 430.6304 | 296.5286 | 319.9803
726.3479 | 430.6787 | 296.6643 | 320.0587
727.3479 | 430.6522 | 296.7834 | 320.1312
728.3479 | 430.7361 | 296.9343 | 320.2021
729.3479 | 430.8482 | 297.0671 | 320.2798
730.3479 | 430.7476 | 297.2042 | 320.3566
731.3635 | 430.4915 | 297.3476 | 320.441
732.3479 | 430.4493 | 297.4791 | 320.5097
733.3635 | 430.3135 | 297.6249 | 320.5924
734.3479 | 430.1546 | 297.7785 | 320.6791
735.3635 | 430.1484 | 297.9002 | 320.7638
736.3479 | 430.3071 | 298.0629 | 320.8381
737.3635 | 430.3776 | 298.1949 | 320.9203
738.3479 | 430.398 | 298.3664 | 320.997
739.3635 | 430.4534 | 298.5059 | 321.0833
740.3479 | 430.5442 | 298.6612 | 321.1647
741.3635 | 430.5393 | 298.8178 | 321.2628
742.3479 | 430.587 | 298.9507 | 321.3514
743.3635 | 430.5561 | 299.1218 | 321.4497
744.3479 | 430.3296 | 299.2518 | 321.5485
745.3635 | 430.2972 | 299.4156 | 321.6405
746.3479 | 430.446 | 299.5656 | 321.7469
747.3479 | 430.3745 | 299.6881 | 321.8563
748.3479 | 430.2789 | 299.8525 | 321.9631
749.3479 | 430.3935 | 299.9788 | 322.0811
750.3479 | 430.5728 | 300.13 | 322.1755
751.3479 | 430.8384 | 300.2552 | 322.2705
752.3635 | 431.1934 | 300.3951 | 322.3739
753.3479 | 431.4495 | 300.5265 | 322.4764
754.3479 | 431.6198 | 300.6562 | 322.6034
755.3479 | 431.8618 | 300.7884 | 322.725
756.3479 | 432.1159 | 300.884 | 322.8591
757.3479 | 432.3465 | 301.0141 | 323.0181
758.3635 | 432.4343 | 301.1458 | 323.1523
759.3479 | 432.3688 | 301.2699 | 323.3081
760.3479 | 432.5033 | 301.3753 | 323.4725
761.3635 | 432.5674 | 301.4913 | 323.6219
762.3479 | 432.4377 | 301.6392 | 323.806
763.3479 | 432.1763 | 301.7677 | 323.978
764.3635 | 432.0023 | 301.9303 | 324.1566
765.3635 | 431.7998 | 302.0843 | 324.3402
766.3479 | 431.7925 | 302.2234 | 324.5359
767.3479 | 431.6768 | 302.3444 | 324.7344
768.3479 | 431.3751 | 302.4777 | 324.9265
769.3479 | 431.1073 | 302.666 | 325.1277
770.3479 | 430.8597 | 302.8197 | 325.3309
771.3479 | 430.739 | 302.9599 | 325.5317
772.3479 | 430.4673 | 303.1461 | 325.7465
773.3479 | 430.319 | 303.3038 | 325.9505
774.3479 | 430.096 | 303.4996 | 326.1445
775.3479 | 430.0149 | 303.6722 | 326.3336
776.3479 | 429.9714 | 303.8476 | 326.53
777.3479 | 429.6781 | 304.0066 | 326.7311
778.3479 | 429.39 | 304.16 | 326.9236
779.3479 | 429.2465 | 304.3658 | 327.12
780.3479 | 429.2637 | 304.5599 | 327.3078
781.3479 | 429.4545 | 304.773 | 327.4843
782.3479 | 429.4941 | 304.9768 | 327.6589
783.3635 | 429.4065 | 305.1673 | 327.8617
784.3479 | 429.414 | 305.3571 | 328.0514
785.3635 | 429.44 | 305.5075 | 328.2477
786.3635 | 429.5592 | 305.7252 | 328.438
787.3479 | 429.5261 | 305.9372 | 328.6285
788.3479 | 429.4613 | 306.197 | 328.8234
789.3479 | 429.4938 | 306.4062 | 329.0154
790.3479 | 429.5431 | 306.6096 | 329.1702
791.3479 | 429.5342 | 306.8544 | 329.3298
792.3479 | 429.5118 | 307.0879 | 329.4822
793.3479 | 429.5486 | 307.2892 | 329.6449
794.3635 | 429.7202 | 307.5373 | 329.824
795.3635 | 429.7226 | 307.7475 | 329.9828
796.3479 | 429.843 | 307.9777 | 330.146
797.3479 | 429.784 | 308.232 | 330.3091
798.3479 | 429.7243 | 308.4632 | 330.4772
799.3635 | 429.6682 | 308.6438 | 330.6431
800.3479 | 429.596 | 308.8598 | 330.799
801.3479 | 429.6757 | 309.1009 | 330.9667
802.3479 | 429.7255 | 309.3093 | 331.1248
803.3479 | 429.7585 | 309.4933 | 331.2905
804.3479 | 429.7662 | 309.6788 | 331.4485
805.3479 | 429.7324 | 309.8842 | 331.6061
806.3479 | 429.6892 | 310.0672 | 331.767
807.3635 | 429.6736 | 310.2705 | 331.913
808.3479 | 429.7096 | 310.5361 | 332.0784
809.3635 | 429.5217 | 310.7024 | 332.2247
810.3479 | 429.4512 | 310.8661 | 332.3764
811.3635 | 429.3848 | 311.1265 | 332.5373
812.3635 | 429.2598 | 311.2944 | 332.6934
813.3479 | 429.1591 | 311.4791 | 332.8459
814.3479 | 429.0916 | 311.6631 | 333.0009
815.3635 | 429.0033 | 311.8458 | 333.1719
816.3479 | 429.0716 | 312.0852 | 333.3123
817.3479 | 429.0699 | 312.299 | 333.4743
818.3635 | 429.1772 | 312.4762 | 333.6224
819.3479 | 429.1321 | 312.647 | 333.7687
820.3479 | 429.1593 | 312.9257 | 333.9189
821.3479 | 429.0964 | 313.213 | 334.0762
822.3479 | 429.0775 | 313.3303 | 334.2537
823.3479 | 429.0363 | 313.574 | 334.4063
824.3479 | 428.7989 | 313.7867 | 334.5439
825.3479 | 428.6592 | 314.0196 | 334.6816
826.3479 | 428.7307 | 314.194 | 334.8372
827.3635 | 428.71 | 314.3217 | 334.9879
828.3479 | 428.6787 | 314.6227 | 335.1398
829.3479 | 428.5565 | 314.7737 | 335.2834
830.3479 | 428.4917 | 314.9326 | 335.4396
831.3479 | 428.4828 | 315.0809 | 335.5978
832.3479 | 428.3744 | 315.2738 | 335.7365
833.3479 | 428.4216 | 315.6518 | 335.8808
834.3479 | 428.4782 | 315.7843 | 336.0211
835.3479 | 428.4064 | 315.9804 | 336.1868
836.3635 | 428.4863 | 316.1521 | 336.3286
837.3479 | 428.6041 | 316.2302 | 336.4585
838.3635 | 428.6277 | 316.4091 | 336.5824
839.3479 | 428.5757 | 316.5003 | 336.7101
840.3635 | 428.5792 | 316.5595 | 336.8558
841.3635 | 428.6245 | 316.7339 | 336.9967
842.3635 | 428.6845 | 316.8169 | 337.1362
843.3635 | 428.6727 | 316.985 | 337.2659
844.3635 | 428.646 | 317.0885 | 337.3702
845.3479 | 428.6627 | 317.227 | 337.4942
846.3635 | 428.7484 | 317.3666 | 337.6082
847.3479 | 428.8741 | 317.483 | 337.726
848.3635 | 428.8669 | 317.6947 | 337.8345
849.3479 | 428.8619 | 317.858 | 337.9447
850.3635 | 428.8553 | 317.9789 | 338.0645
851.3479 | 428.9718 | 318.0797 | 338.1772
852.3479 | 429.0575 | 318.2303 | 338.2966
853.3479 | 429.204 | 318.3714 | 338.4243
854.3479 | 429.2153 | 318.5515 | 338.5597
855.3479 | 429.1969 | 318.6965 | 338.6875
856.3479 | 429.1712 | 318.8049 | 338.8112
857.3479 | 429.2329 | 318.9324 | 338.9353
858.3635 | 429.3343 | 319.1211 | 339.064
859.3479 | 429.4192 | 319.2243 | 339.1803
860.3479 | 429.5637 | 319.4041 | 339.3067
861.3479 | 429.5417 | 319.578 | 339.4333
862.3635 | 429.5476 | 319.7266 | 339.5405
863.3479 | 429.6168 | 319.8914 | 339.6602
864.3635 | 429.5988 | 320.0655 | 339.7765
865.3479 | 429.7715 | 320.2275 | 339.8872
866.3635 | 429.8339 | 320.3857 | 339.9925
867.3479 | 429.8545 | 320.6068 | 340.1015
868.3635 | 429.9514 | 320.7385 | 340.2166
869.3479 | 429.8533 | 320.8769 | 340.3569
870.3635 | 429.7946 | 321.088 | 340.4855
871.3635 | 429.7789 | 321.1928 | 340.6045
872.3479 | 429.7386 | 321.3201 | 340.7312
873.3479 | 429.8958 | 321.4609 | 340.8665
874.3479 | 429.954 | 321.5959 | 340.9891
875.3479 | 429.7623 | 321.7646 | 341.1207
876.3479 | 429.7084 | 321.8961 | 341.2468
877.3479 | 429.6882 | 322.0608 | 341.3715
878.3479 | 429.7429 | 322.2223 | 341.496
879.3479 | 429.6622 | 322.3393 | 341.6393
880.3479 | 429.5963 | 322.5643 | 341.778
881.3479 | 429.5373 | 322.6882 | 341.9255
882.3479 | 429.4204 | 322.8759 | 342.0536
883.3479 | 429.4287 | 322.968 | 342.1862
884.3635 | 429.4325 | 323.1269 | 342.3325
885.3479 | 429.3971 | 323.261 | 342.4683
886.3479 | 429.2127 | 323.3869 | 342.6168
887.3635 | 429.1421 | 323.56 | 342.7562
888.3479 | 429.1174 | 323.7302 | 342.8928
889.3479 | 428.9946 | 323.8833 | 343.0265
890.3479 | 429.0298 | 324.0167 | 343.1584
891.3479 | 428.8395 | 324.1834 | 343.2864
892.3635 | 428.7916 | 324.2779 | 343.4315
893.3635 | 428.8013 | 324.45 | 343.5677
894.3479 | 428.8325 | 324.5856 | 343.7229
895.3635 | 428.8712 | 324.7678 | 343.8703
896.3635 | 428.8527 | 324.8394 | 344.0214
897.3635 | 428.777 | 324.9922 | 344.1407
898.3635 | 428.8104 | 325.1043 | 344.2951
899.3635 | 428.9051 | 325.2578 | 344.4212
900.3635 | 428.8992 | 325.3847 | 344.5784
901.3635 | 428.8521 | 325.5501 | 344.705
902.3635 | 428.9372 | 325.7042 | 344.8262
903.3635 | 428.998 | 325.8481 | 344.9156
904.3635 | 429.0037 | 325.9595 | 345.0017
905.3635 | 428.9523 | 326.0788 | 345.1215
906.3635 | 428.8701 | 326.2645 | 345.2411
907.3635 | 428.8961 | 326.4122 | 345.347
908.3635 | 428.9829 | 326.541 | 345.446
909.3635 | 429.1454 | 326.6406 | 345.5499
910.3635 | 429.1533 | 326.7888 | 345.6555
911.3635 | 429.1346 | 326.9553 | 345.7433
912.3635 | 429.1298 | 327.0747 | 345.8511
913.3635 | 429.1295 | 327.1896 | 345.9448
914.3635 | 429.188 | 327.3948 | 346.0348
915.3479 | 429.2298 | 327.4996 | 346.1427
916.3635 | 429.2291 | 327.6353 | 346.2401
917.3479 | 429.4446 | 327.7763 | 346.3281
918.3635 | 429.5842 | 327.9225 | 346.4574
919.3635 | 429.6075 | 328.0461 | 346.5868
920.3635 | 429.531 | 328.1736 | 346.7062
921.3635 | 429.5048 | 328.3205 | 346.8281
922.3635 | 429.6075 | 328.4964 | 346.9587
923.3635 | 429.6656 | 328.6144 | 347.0929
924.3635 | 429.6303 | 328.7772 | 347.2061
925.3635 | 429.5869 | 328.9214 | 347.3172
926.3635 | 429.6534 | 329.0367 | 347.4341
927.3635 | 429.6718 | 329.1889 | 347.5459
928.3635 | 429.6037 | 329.3153 | 347.6448
929.3635 | 429.4926 | 329.4404 | 347.7661
930.3635 | 429.4508 | 329.5941 | 347.8699
931.3635 | 429.3894 | 329.7072 | 347.9858
932.3635 | 429.3915 | 329.8697 | 348.0966
933.3479 | 429.3764 | 329.9865 | 348.2063
934.3635 | 429.4212 | 330.1211 | 348.3061
935.3635 | 429.4605 | 330.2712 | 348.4194
936.3635 | 429.4423 | 330.4024 | 348.5365
937.3635 | 429.4466 | 330.5478 | 348.6471
938.3635 | 429.3689 | 330.7018 | 348.7585
939.3635 | 429.2855 | 330.8373 | 348.8739
940.3635 | 429.2826 | 331.0277 | 348.9886
941.3635 | 429.2463 | 331.1452 | 349.0955
942.3635 | 429.209 | 331.2467 | 349.2061
943.3635 | 429.1414 | 331.3629 | 349.3194
944.3635 | 429.0265 | 331.4824 | 349.4213
945.3635 | 428.9634 | 331.6564 | 349.5163
946.3635 | 428.8518 | 331.7675 | 349.6293
947.3635 | 428.7786 | 331.945 | 349.7396
948.3635 | 428.8271 | 332.1452 | 349.8396
949.3635 | 428.8975 | 332.2434 | 349.955
950.3635 | 428.854 | 332.3917 | 350.0499
951.3635 | 428.9053 | 332.5012 | 350.1553
952.3635 | 428.8752 | 332.6479 | 350.2617
953.3635 | 428.9659 | 332.777 | 350.3604
954.3635 | 428.9139 | 332.8906 | 350.463
955.3635 | 428.9453 | 333.0205 | 350.5655
956.3635 | 428.9356 | 333.1468 | 350.6582
957.3635 | 428.7967 | 333.2963 | 350.7595
958.3635 | 428.7972 | 333.409 | 350.8559
959.3635 | 428.7871 | 333.4958 | 350.9615
960.3635 | 428.7844 | 333.6477 | 351.0567
961.3635 | 428.7641 | 333.768 | 351.1537
962.3635 | 428.8186 | 333.883 | 351.2523
963.3635 | 428.9389 | 334.0194 | 351.3478
964.3635 | 428.9072 | 334.1507 | 351.4389
965.3635 | 428.7973 | 334.246 | 351.5362
966.3635 | 428.7069 | 334.3614 | 351.6252
967.3792 | 428.8106 | 334.4974 | 351.7011
968.4729 | 428.8702 | 334.6355 | 351.7925
969.3792 | 428.8585 | 334.7155 | 351.8857
970.3948 | 428.8162 | 334.805 | 351.9743
971.4885 | 428.9101 | 334.9233 | 352.0843
972.3635 | 428.9345 | 335.0365 | 352.1631
973.3635 | 429.0214 | 335.1403 | 352.2477
974.3635 | 428.9972 | 335.2478 | 352.3426
975.3635 | 429.0098 | 335.3446 | 352.4392
976.3635 | 429.0061 | 335.4413 | 352.5432
977.3635 | 429.0195 | 335.5631 | 352.646
978.3635 | 429.0694 | 335.6501 | 352.7505
979.3635 | 429.1029 | 335.767 | 352.8497
980.3635 | 429.1025 | 335.8841 | 352.9467
981.3635 | 429.1127 | 335.9726 | 353.0408
982.3635 | 429.2011 | 336.0578 | 353.139
983.3635 | 429.2148 | 336.1534 | 353.2371
984.3635 | 429.3272 | 336.27 | 353.3405
985.3635 | 429.3375 | 336.3681 | 353.4381
986.3635 | 429.3306 | 336.4719 | 353.5341
987.3635 | 429.3664 | 336.5782 | 353.6273
988.3635 | 429.4846 | 336.6803 | 353.7253
989.3635 | 429.3888 | 336.7671 | 353.8287
990.3635 | 429.2626 | 336.8966 | 353.9309
991.3635 | 429.1904 | 336.9877 | 354.0395
992.3635 | 429.2098 | 337.1064 | 354.1472
993.3635 | 429.1634 | 337.1996 | 354.2493
994.3635 | 429.1636 | 337.3113 | 354.3625
995.3635 | 429.1136 | 337.4215 | 354.4714
996.3635 | 429.1372 | 337.4886 | 354.5889
997.3635 | 429.1189 | 337.6067 | 354.6945
998.3635 | 429.0672 | 337.7115 | 354.7849
999.3635 | 429.052 | 337.8401 | 354.8861
1000.3635 | 429.1058 | 337.9333 | 354.9829
1001.3635 | 428.9733 | 338.0492 | 355.0843
1002.3635 | 428.9669 | 338.1183 | 355.1823
1003.3635 | 429.0433 | 338.2185 | 355.2723
1004.3635 | 429.129 | 338.3403 | 355.3935
1005.3635 | 429.1578 | 338.3922 | 355.4847
1006.3635 | 429.2067 | 338.5004 | 355.5734
1007.3635 | 429.2542 | 338.57 | 355.6661
1008.3635 | 429.2606 | 338.6275 | 355.7469
1009.3635 | 429.2314 | 338.7355 | 355.8285
1010.3635 | 429.1835 | 338.77 | 355.9059
1011.3635 | 429.2199 | 338.8493 | 356.0282
1012.3635 | 429.2614 | 338.9339 | 356.1201
1013.3635 | 429.2997 | 339.0254 | 356.2152
1014.3635 | 429.2749 | 339.1333 | 356.2783
1015.3635 | 429.298 | 339.212 | 356.3623
1016.3635 | 429.2993 | 339.3065 | 356.4568
1017.3635 | 429.1586 | 339.4012 | 356.5339
1018.3635 | 429.0561 | 339.4782 | 356.6169
1019.3635 | 429.0786 | 339.5817 | 356.7065
1020.3635 | 429.0058 | 339.6597 | 356.7959
1021.3635 | 429.0053 | 339.7185 | 356.8887
1022.3635 | 428.9764 | 339.7875 | 356.9657
1023.3635 | 428.8179 | 339.8753 | 357.0565
1024.3635 | 428.7878 | 339.9746 | 357.1371
1025.3635 | 428.8252 | 340.0517 | 357.2236
1026.3635 | 428.8838 | 340.1281 | 357.3321
1027.3635 | 428.8936 | 340.2023 | 357.4215
1028.3635 | 428.8952 | 340.2769 | 357.5126
1029.3635 | 428.9795 | 340.3422 | 357.6004
1030.3635 | 428.9825 | 340.4049 | 357.6719
1031.3479 | 429.029 | 340.5007 | 357.7583
1032.3635 | 429.153 | 340.5536 | 357.8361
1033.3635 | 429.121 | 340.6422 | 357.9134
1034.3635 | 429.1597 | 340.7439 | 357.9982
1035.3635 | 429.1626 | 340.8136 | 358.0789
1036.3635 | 429.1809 | 340.8996 | 358.1618
1037.3635 | 429.2683 | 340.9565 | 358.2405
1038.3479 | 429.1638 | 341.0451 | 358.3123
1039.3635 | 429.1803 | 341.1195 | 358.3932
1040.3635 | 429.276 | 341.2596 | 358.4592
1041.3635 | 429.2717 | 341.406 | 358.535
1042.3635 | 429.3559 | 341.4457 | 358.6044
1043.3635 | 429.4051 | 341.5343 | 358.6751
1044.3635 | 429.4503 | 341.646 | 358.7519
1045.3635 | 429.3712 | 341.7121 | 358.8272
1046.3635 | 429.2822 | 341.7763 | 358.9074
1047.3635 | 429.259 | 341.8618 | 358.9811
1048.3635 | 429.0861 | 341.9329 | 359.0595
1049.3635 | 428.9551 | 342.0145 | 359.1366
1050.3635 | 428.9222 | 342.091 | 359.2168
1051.3635 | 429.0179 | 342.1852 | 359.285
1052.3635 | 428.859 | 342.2344 | 359.3696
1053.3635 | 428.8625 | 342.3533 | 359.4448
1054.3635 | 428.7525 | 342.4153 | 359.5255
1055.3635 | 428.8543 | 342.5047 | 359.6206
1056.3635 | 428.7983 | 342.6317 | 359.7051
1057.3635 | 428.7852 | 342.6914 | 359.8037
1058.3635 | 428.8123 | 342.7619 | 359.8876
1059.3635 | 428.951 | 342.8604 | 359.9723
1060.3635 | 428.9688 | 342.9573 | 360.0533
1061.3479 | 428.8628 | 343.0035 | 360.1392
1062.3635 | 428.8962 | 343.062 | 360.2207
1063.3635 | 428.9779 | 343.1545 | 360.3032
1064.3635 | 429.1068 | 343.2049 | 360.3803
1065.3635 | 429.253 | 343.3261 | 360.4637
1066.3635 | 429.2312 | 343.4078 | 360.55
1067.3635 | 429.3178 | 343.4699 | 360.6379
1068.3635 | 429.3891 | 343.5514 | 360.7224
1069.3635 | 429.5073 | 343.6215 | 360.8128
1070.3635 | 429.6909 | 343.7077 | 360.9035
1071.3479 | 429.7067 | 343.7897 | 360.9788
1072.3635 | 429.5829 | 343.8467 | 361.0597
1073.3635 | 429.4764 | 343.9322 | 361.1407
1074.3635 | 429.4535 | 344.0218 | 361.2323
1075.3635 | 429.5825 | 344.1061 | 361.3088
1076.3635 | 429.5928 | 344.1655 | 361.393
1077.3635 | 429.4775 | 344.2499 | 361.4763
1078.3635 | 429.3118 | 344.3471 | 361.5524
1079.3635 | 429.3482 | 344.3961 | 361.6388
1080.3635 | 429.3854 | 344.4797 | 361.7178
1081.3479 | 429.3703 | 344.5319 | 361.7871
1082.3635 | 429.5549 | 344.6094 | 361.881
1083.3635 | 429.589 | 344.6836 | 361.961
1084.3635 | 429.5809 | 344.741 | 362.0453
1085.3635 | 429.6529 | 344.8343 | 362.1189
1086.3635 | 429.6958 | 344.9023 | 362.201
1087.3635 | 429.6757 | 344.9947 | 362.2897
1088.3635 | 429.7332 | 345.074 | 362.3634
1089.3635 | 429.7429 | 345.1466 | 362.4495
1090.3635 | 429.7353 | 345.2254 | 362.5325
1091.3635 | 429.6766 | 345.3087 | 362.6148
1092.3635 | 429.6624 | 345.3889 | 362.698
1093.3635 | 429.6351 | 345.4444 | 362.7861
1094.3635 | 429.5982 | 345.5401 | 362.8705
1095.3635 | 429.4895 | 345.6359 | 362.9533
1096.3479 | 429.2979 | 345.6857 | 363.0498
1097.3635 | 429.2295 | 345.7883 | 363.1465
1098.3635 | 429.251 | 345.8668 | 363.223
1099.3635 | 429.2634 | 345.9344 | 363.3127
1100.3635 | 429.3699 | 346.0278 | 363.4068
1101.3479 | 429.3259 | 346.0899 | 363.5017
1102.3635 | 429.2621 | 346.1792 | 363.5982
1103.3635 | 429.2831 | 346.2504 | 363.6841
1104.3479 | 429.307 | 346.3234 | 363.7746
1105.3635 | 429.2514 | 346.4003 | 363.8604
1106.3635 | 429.2566 | 346.4706 | 363.9374
1107.3635 | 429.2321 | 346.5507 | 364.0147
1108.3635 | 429.1848 | 346.6146 | 364.0947
1109.3635 | 429.2022 | 346.6987 | 364.1719
1110.3635 | 429.1291 | 346.7761 | 364.2372
1111.3635 | 429.0487 | 346.8459 | 364.3131
1112.3635 | 428.9876 | 346.9303 | 364.3837
1113.3635 | 428.9018 | 347.0008 | 364.4586
1114.3635 | 428.9698 | 347.0922 | 364.5321
1115.3635 | 428.955 | 347.1873 | 364.6042
1116.3479 | 428.9733 | 347.2398 | 364.6707
1117.3635 | 429.0719 | 347.3433 | 364.7335
1118.3635 | 429.1828 | 347.3996 | 364.7971
1119.3635 | 429.125 | 347.4917 | 364.8581
1120.3635 | 429.1604 | 347.5594 | 364.9247
1121.3635 | 429.1726 | 347.6356 | 364.996
1122.3635 | 429.0149 | 347.7317 | 365.0628
1123.3635 | 428.9826 | 347.771 | 365.1338
1124.3635 | 428.9328 | 347.8692 | 365.2004
1125.3635 | 428.8843 | 347.94 | 365.2681
1126.3635 | 428.8662 | 348.0202 | 365.3402
1127.3635 | 428.9058 | 348.1005 | 365.4052
1128.3635 | 428.9694 | 348.1715 | 365.4709
1129.3635 | 428.9485 | 348.2531 | 365.5373
1130.3635 | 428.98 | 348.3174 | 365.6092
1131.3479 | 429.0347 | 348.3934 | 365.6747
1132.3635 | 429.066 | 348.4714 | 365.7414
1133.3635 | 429.063 | 348.5386 | 365.8117
1134.3479 | 429.1462 | 348.6262 | 365.8839
1135.3635 | 429.1967 | 348.7025 | 365.951
1136.3635 | 429.1804 | 348.7873 | 366.0205
1137.3635 | 429.1909 | 348.8591 | 366.0785
1138.3635 | 429.1567 | 348.9456 | 366.1543
1139.3635 | 429.2547 | 349.0314 | 366.2247
1140.3635 | 429.2889 | 349.1059 | 366.2903
1141.3479 | 429.3716 | 349.205 | 366.3584
1142.3635 | 429.4935 | 349.2723 | 366.4264
1143.3635 | 429.651 | 349.3548 | 366.4823
1144.3635 | 429.6989 | 349.4468 | 366.5495
1145.3635 | 429.6323 | 349.5109 | 366.6162
1146.3635 | 429.6371 | 349.5988 | 366.6765
1147.3635 | 429.6602 | 349.6523 | 366.7377
1148.3635 | 429.6893 | 349.7511 | 366.7977
1149.3635 | 429.6931 | 349.8341 | 366.8585
1150.3635 | 429.6303 | 349.9068 | 366.9255
1151.3635 | 429.6715 | 350.0042 | 366.9839
1152.3479 | 429.6702 | 350.0763 | 367.0463
1153.3635 | 429.6712 | 350.1534 | 367.1109
1154.3635 | 429.683 | 350.2502 | 367.1721
1155.3635 | 429.6377 | 350.3266 | 367.2449
1156.3479 | 429.6029 | 350.4091 | 367.3052
1157.3635 | 429.5794 | 350.4881 | 367.3688
1158.3479 | 429.5995 | 350.5861 | 367.427
1159.3635 | 429.4718 | 350.6645 | 367.4886
1160.3635 | 429.3017 | 350.7518 | 367.5582
1161.3635 | 429.1543 | 350.8468 | 367.6147
1162.3635 | 429.1195 | 350.9263 | 367.6657
1163.3635 | 429.2086 | 351.0265 | 367.7247
1164.3635 | 429.2394 | 351.0995 | 367.7824
1165.3635 | 429.2447 | 351.1957 | 367.8381
1166.3635 | 429.2462 | 351.2757 | 367.8909
1167.3635 | 429.3221 | 351.3741 | 367.9548
1168.3635 | 429.3464 | 351.4882 | 368.0149
1169.3635 | 429.4203 | 351.5631 | 368.0721
1170.3635 | 429.4767 | 351.6532 | 368.1338
1171.3635 | 429.4016 | 351.7369 | 368.1974
1172.3635 | 429.3601 | 351.82 | 368.2576
1173.3635 | 429.2939 | 351.941 | 368.3234
1174.3635 | 429.3004 | 352.0183 | 368.38
1175.3635 | 429.3982 | 352.1141 | 368.4493
1176.3635 | 429.5133 | 352.2073 | 368.5039
1177.3479 | 429.4889 | 352.2819 | 368.5562
1178.3635 | 429.4195 | 352.3879 | 368.6044
1179.3635 | 429.381 | 352.4668 | 368.6645
1180.3635 | 429.2654 | 352.5703 | 368.7195
1181.3635 | 429.2509 | 352.6583 | 368.773
1182.3635 | 429.1817 | 352.7446 | 368.8314
1183.3635 | 429.2448 | 352.8327 | 368.8961
1184.3635 | 429.1391 | 352.9148 | 368.9527
1185.3635 | 428.9861 | 353.0006 | 369.0088
1186.3635 | 428.9665 | 353.087 | 369.0732
1187.3635 | 428.8959 | 353.1677 | 369.1273
1188.3635 | 428.9 | 353.2686 | 369.1756
1189.3635 | 428.9105 | 353.3337 | 369.2396
1190.3635 | 428.8751 | 353.4365 | 369.3007
1191.3479 | 428.8689 | 353.5061 | 369.3508
1192.3635 | 428.8798 | 353.5819 | 369.4122
1193.3635 | 428.8583 | 353.6806 | 369.4677
1194.3635 | 428.9227 | 353.735 | 369.5211
1195.3635 | 428.815 | 353.8322 | 369.5832
1196.3635 | 428.8987 | 353.9023 | 369.6347
1197.3635 | 428.9895 | 353.9932 | 369.7016
1198.3635 | 429.0907 | 354.0711 | 369.7589
1199.3635 | 429.0208 | 354.1303 | 369.8141
1200.3635 | 428.9334 | 354.2356 | 369.8767
1201.3479 | 428.9926 | 354.2857 | 369.9337
1202.3635 | 429.009 | 354.3728 | 369.9914
1203.3635 | 428.9804 | 354.4435 | 370.0576
1204.3635 | 429.1187 | 354.5116 | 370.1067
1205.3635 | 429.2539 | 354.6053 | 370.1601
1206.3479 | 429.1978 | 354.6708 | 370.2073
1207.3635 | 429.2149 | 354.7353 | 370.2594
1208.3635 | 429.1723 | 354.8248 | 370.3142
1209.3635 | 429.1725 | 354.8888 | 370.3658
1210.3635 | 429.1192 | 354.9712 | 370.4187
1211.3635 | 428.9831 | 355.0377 | 370.4702
1212.3635 | 428.8606 | 355.117 | 370.5245
1213.3635 | 428.8612 | 355.1961 | 370.5899
1214.3635 | 428.8723 | 355.262 | 370.6451
1215.3635 | 428.925 | 355.3426 | 370.6995
1216.3635 | 428.8428 | 355.4009 | 370.7441
1217.3635 | 428.7467 | 355.5001 | 370.7942
1218.3635 | 428.8181 | 355.5575 | 370.8495
1219.3635 | 428.9591 | 355.6224 | 370.9111
1220.3635 | 429.0327 | 355.7096 | 370.9681
1221.3479 | 429.0842 | 355.7681 | 371.0286
1222.3635 | 429.1564 | 355.8389 | 371.0872
1223.3635 | 429.264 | 355.9129 | 371.1436
1224.3635 | 429.1248 | 355.9715 | 371.1975
1225.3635 | 429.1499 | 356.0346 | 371.2561
1226.3635 | 429.1276 | 356.0955 | 371.3056
1227.3635 | 429.1454 | 356.1731 | 371.3496
1228.3635 | 429.1565 | 356.228 | 371.3969
1229.3635 | 429.2222 | 356.2835 | 371.4442
1230.3635 | 429.2669 | 356.3585 | 371.4931
1231.3635 | 429.2988 | 356.4059 | 371.5443
1232.3635 | 429.2465 | 356.4715 | 371.5748
1233.3635 | 429.3803 | 356.5318 | 371.6191
1234.3635 | 429.4034 | 356.5946 | 371.6657
1235.3635 | 429.3357 | 356.661 | 371.7083
1236.3635 | 429.4253 | 356.7017 | 371.763
1237.3635 | 429.4514 | 356.7635 | 371.8174
1238.3635 | 429.3751 | 356.8177 | 371.8566
1239.3635 | 429.3318 | 356.874 | 371.8985
1240.3635 | 429.2327 | 356.9266 | 371.946
1241.3479 | 429.1597 | 356.9837 | 371.9903
1242.3635 | 429.137 | 357.0413 | 372.0273
1243.3635 | 429.0967 | 357.0753 | 372.0783
1244.3635 | 429.042 | 357.1329 | 372.1137
1245.3635 | 429.0861 | 357.1797 | 372.1561
1246.3635 | 429.2037 | 357.2206 | 372.1991
1247.3635 | 429.204 | 357.2871 | 372.2327
1248.3635 | 429.2042 | 357.3217 | 372.2651
1249.3635 | 429.1771 | 357.3973 | 372.2924
1250.3635 | 429.1527 | 357.4362 | 372.3209
1251.3635 | 429.2361 | 357.4849 | 372.3543
1252.3635 | 429.1691 | 357.5367 | 372.3828
1253.3635 | 429.1679 | 357.58 | 372.4011
1254.3635 | 429.0961 | 357.6329 | 372.4352
1255.3635 | 428.9671 | 357.6788 | 372.4686
1256.3635 | 428.9108 | 357.7253 | 372.5011
1257.3635 | 428.9964 | 357.7674 | 372.5352
1258.3635 | 428.9384 | 357.7988 | 372.5708
1259.3635 | 428.932 | 357.8545 | 372.6094
1260.3635 | 428.9192 | 357.883 | 372.6476
1261.3635 | 428.9801 | 357.9316 | 372.6855
1262.3635 | 429.0255 | 357.9773 | 372.7211
1263.3635 | 429.166 | 358.014 | 372.7616
1264.3635 | 429.1628 | 358.0615 | 372.7958
1265.3635 | 429.1482 | 358.0931 | 372.8319
1266.3635 | 429.1254 | 358.1378 | 372.8695
1267.3635 | 429.1939 | 358.1741 | 372.9021
1268.3479 | 429.2613 | 358.2031 | 372.9362
1269.3635 | 429.2558 | 358.2605 | 372.9738
1270.3635 | 429.214 | 358.2726 | 373.0027
1271.3479 | 429.1496 | 358.3428 | 373.0364
1272.3635 | 429.131 | 358.3533 | 373.0582
1273.3479 | 429.2302 | 358.4033 | 373.0829
1274.3635 | 429.1855 | 358.4572 | 373.0995
1275.3479 | 429.1517 | 358.4759 | 373.1286
1276.3635 | 429.2129 | 358.5261 | 373.1599
1277.3479 | 429.3137 | 358.5381 | 373.1912
1278.3635 | 429.4474 | 358.5642 | 373.2261
1279.3479 | 429.5332 | 358.6061 | 373.2545
1280.3635 | 429.4655 | 358.6405 | 373.28
1281.3479 | 429.4278 | 358.6731 | 373.3136
1282.3635 | 429.3772 | 358.6886 | 373.3432
1283.3479 | 429.3964 | 358.7365 | 373.3722
1284.3635 | 429.3967 | 358.7463 | 373.3985
1285.3479 | 429.4416 | 358.7861 | 373.4244
1286.3635 | 429.427 | 358.8034 | 373.4539
1287.3635 | 429.4431 | 358.8252 | 373.4873
1288.3479 | 429.3717 | 358.8767 | 373.5243
1289.3479 | 429.3601 | 358.8917 | 373.5636
1290.3635 | 429.3075 | 358.923 | 373.6012
1291.3479 | 429.2581 | 358.947 | 373.6442
1292.3479 | 429.3522 | 358.965 | 373.6903
1293.3635 | 429.446 | 358.9917 | 373.7195
1294.3635 | 429.3908 | 359.01 | 373.7561
1295.3479 | 429.3309 | 359.0518 | 373.7955
1296.3635 | 429.2051 | 359.0536 | 373.823
1297.3479 | 429.237 | 359.1002 | 373.8672
1298.3635 | 429.2909 | 359.1234 | 373.9044
1299.3479 | 429.3653 | 359.1353 | 373.9401
1300.3635 | 429.3487 | 359.1649 | 373.974
1301.3635 | 429.2014 | 359.1861 | 374.0064
1302.3479 | 429.1983 | 359.2067 | 374.0343
1303.3635 | 429.1819 | 359.2381 | 374.064
1304.3635 | 429.2623 | 359.2452 | 374.0932
1305.3635 | 429.3057 | 359.2793 | 374.1242
1306.3635 | 429.2975 | 359.278 | 374.1572
1307.3479 | 429.3781 | 359.306 | 374.1794
1308.3479 | 429.4484 | 359.3387 | 374.2142
1309.3635 | 429.4871 | 359.3475 | 374.2382
1310.3635 | 429.5325 | 359.3674 | 374.2616
1311.3635 | 429.5047 | 359.3792 | 374.3022
1312.3479 | 429.4872 | 359.4097 | 374.3335
1313.3479 | 429.5645 | 359.4174 | 374.365
1314.3479 | 429.5363 | 359.4374 | 374.3952
1315.3479 | 429.5188 | 359.474 | 374.4261
1316.3635 | 429.4672 | 359.4699 | 374.4573
1317.3479 | 429.4561 | 359.5136 | 374.4763
1318.3479 | 429.4107 | 359.5297 | 374.5086
1319.3479 | 429.4993 | 359.5502 | 374.5353
1320.3479 | 429.5665 | 359.5871 | 374.5551
1321.3479 | 429.5721 | 359.5861 | 374.5822
1322.3479 | 429.5513 | 359.6373 | 374.6124
1323.3635 | 429.5803 | 359.6411 | 374.6389
1324.3479 | 429.6175 | 359.661 | 374.6626
1325.3479 | 429.614 | 359.6867 | 374.6883
1326.3479 | 429.6358 | 359.7077 | 374.7069
1327.3479 | 429.5782 | 359.7227 | 374.7258
1328.3479 | 429.6298 | 359.7311 | 374.7496
1329.3479 | 429.7158 | 359.7578 | 374.7681
1330.3479 | 429.6791 | 359.7791 | 374.7903
1331.3479 | 429.702 | 359.7744 | 374.8139
1332.3479 | 429.7282 | 359.8128 | 374.8371
1333.3479 | 429.8333 | 359.8245 | 374.865
1334.3479 | 429.7156 | 359.8466 | 374.8878
1335.3479 | 429.6669 | 359.8423 | 374.9178
1336.3479 | 429.6997 | 359.8674 | 374.9484
1337.3479 | 429.7044 | 359.8951 | 374.9732
1338.3479 | 429.6955 | 359.8883 | 374.9972
1339.3479 | 429.7408 | 359.9048 | 375.0286
1340.3479 | 429.773 | 359.9294 | 375.0439
1341.3479 | 429.8574 | 359.9449 | 375.068
1342.3479 | 429.8285 | 359.9679 | 375.093
1343.3479 | 429.7802 | 359.9696 | 375.1067
1344.3479 | 429.7434 | 359.999 | 375.1188
1345.3479 | 429.6597 | 360.0101 | 375.1312
1346.3635 | 429.6368 | 360.0297 | 375.1345
1347.3479 | 429.5805 | 360.0518 | 375.1468
1348.3479 | 429.5381 | 360.0603 | 375.1569
1349.3479 | 429.4851 | 360.0868 | 375.1672
1350.3479 | 429.5324 | 360.0872 | 375.1717
1351.3479 | 429.527 | 360.1037 | 375.1852
1352.3479 | 429.5614 | 360.1279 | 375.1924
1353.3479 | 429.5378 | 360.1425 | 375.1978
1354.3479 | 429.4009 | 360.1671 | 375.2097
1355.3479 | 429.2397 | 360.1794 | 375.2156
1356.3479 | 429.1667 | 360.2024 | 375.2224
1357.3479 | 429.301 | 360.2146 | 375.2344
1358.3635 | 429.2162 | 360.2419 | 375.2514
1359.3479 | 429.1254 | 360.2632 | 375.2575
1360.3479 | 429.0722 | 360.2821 | 375.268
1361.3479 | 429.1335 | 360.3125 | 375.2753
1362.3479 | 429.2367 | 360.3306 | 375.2832
1363.3479 | 429.2479 | 360.3472 | 375.305
1364.3635 | 429.2341 | 360.3679 | 375.3264
1365.3479 | 429.2931 | 360.3783 | 375.3372
1366.3479 | 429.3854 | 360.4141 | 375.3479
1367.3635 | 429.3507 | 360.423 | 375.3719
1368.3479 | 429.301 | 360.4465 | 375.3937
1369.3479 | 429.2285 | 360.476 | 375.4088
1370.3635 | 429.2103 | 360.4822 | 375.4243
1371.3479 | 429.135 | 360.5211 | 375.4459
1372.3479 | 429.0749 | 360.5156 | 375.4654
1373.3635 | 429.0601 | 360.5478 | 375.4835
1374.3479 | 429.1231 | 360.5789 | 375.5024
1375.3479 | 429.1072 | 360.5909 | 375.5242
1376.3635 | 429.0282 | 360.6206 | 375.543
1377.3479 | 429.0325 | 360.637 | 375.5634
1378.3635 | 429.077 | 360.6728 | 375.586
1379.3479 | 429.0359 | 360.6897 | 375.6037
1380.3479 | 429.0458 | 360.715 | 375.6218
1381.3479 | 429.0902 | 360.7504 | 375.6443
1382.3479 | 429.1223 | 360.7645 | 375.672
1383.3635 | 429.169 | 360.8104 | 375.6917
1384.3479 | 429.2165 | 360.8153 | 375.7116
1385.3635 | 429.3761 | 360.8498 | 375.7252
1386.3479 | 429.4061 | 360.8772 | 375.747
1387.3635 | 429.4539 | 360.898 | 375.7658
1388.3635 | 429.4381 | 360.92 | 375.7821
1389.3479 | 429.4007 | 360.9348 | 375.7928
1390.3635 | 429.5347 | 360.9589 | 375.8053
1391.3479 | 429.5999 | 360.9808 | 375.8237
1392.3479 | 429.6166 | 360.9825 | 375.8472
1393.3635 | 429.5107 | 361.0089 | 375.8577
1394.3635 | 429.3349 | 360.9997 | 375.8737
1395.3479 | 429.3634 | 361.0341 | 375.9007
1396.3479 | 429.3409 | 361.0405 | 375.9121
1397.3479 | 429.4115 | 361.0465 | 375.9263
1398.3479 | 429.346 | 361.0591 | 375.9415
1399.3635 | 429.237 | 361.0594 | 375.9488
1400.3635 | 429.299 | 361.0736 | 375.9632
1401.3479 | 429.3438 | 361.063 | 375.9797
1402.3479 | 429.3819 | 361.0776 | 375.9881
1403.3635 | 429.4231 | 361.0781 | 375.9882
1404.3479 | 429.5507 | 361.076 | 375.9977
1405.3635 | 429.6317 | 361.0852 | 375.9993
1406.3635 | 429.6762 | 361.0973 | 376.0051
1407.3635 | 429.6247 | 361.0938 | 376.0159
1408.3635 | 429.611 | 361.1251 | 376.0244
1409.3635 | 429.5456 | 361.1224 | 376.0249
1410.3635 | 429.5582 | 361.136 | 376.0298
1411.3479 | 429.6263 | 361.1359 | 376.023
1412.3635 | 429.7262 | 361.1519 | 376.0265
1413.3479 | 429.8314 | 361.1486 | 376.0207
1414.3635 | 429.8606 | 361.1582 | 376.0302
1415.3635 | 429.8255 | 361.1753 | 376.0203
1416.3479 | 429.7954 | 361.1631 | 376.0254
1417.3479 | 429.7663 | 361.1993 | 376.0232
1418.3479 | 429.72 | 361.2036 | 376.0213
1419.3479 | 429.7046 | 361.2086 | 376.0225
1420.3635 | 429.6669 | 361.2172 | 376.0311
1421.3635 | 429.6723 | 361.2249 | 376.0379
1422.3635 | 429.6386 | 361.2507 | 376.04
1423.3635 | 429.6994 | 361.2582 | 376.0441
1424.3635 | 429.759 | 361.2852 | 376.0574
1425.3635 | 429.7459 | 361.3112 | 376.0696
1426.3635 | 429.6253 | 361.3111 | 376.0837
1427.3479 | 429.6508 | 361.3332 | 376.0983
1428.3635 | 429.6362 | 361.3332 | 376.1092
1429.3479 | 429.5326 | 361.3656 | 376.1329
1430.3635 | 429.4005 | 361.385 | 376.1407
1431.3479 | 429.2892 | 361.3913 | 376.1635
1432.3635 | 429.2644 | 361.4309 | 376.1783
1433.3479 | 429.1329 | 361.4185 | 376.2018
1434.3635 | 429.1071 | 361.4472 | 376.2205
1435.3635 | 429.1407 | 361.4496 | 376.2376
1436.3479 | 429.1668 | 361.4593 | 376.2634
1437.3479 | 429.1384 | 361.4874 | 376.2741
1438.3479 | 429.1377 | 361.4722 | 376.2905
1439.3479 | 429.1844 | 361.5199 | 376.2976
1440.3479 | 429.1513 | 361.5161 | 376.3076
1441.3479 | 429.0628 | 361.5305 | 376.3183
1442.3479 | 429.1041 | 361.5635 | 376.3159
1443.3635 | 429.0261 | 361.5576 | 376.3252
1444.3479 | 429.0392 | 361.5892 | 376.3305
1445.3479 | 429.0368 | 361.5911 | 376.3355
1446.3479 | 429.0138 | 361.5952 | 376.3439
1447.3479 | 429.0785 | 361.6073 | 376.3464
1448.3479 | 429.0627 | 361.6051 | 376.3547
1449.3479 | 429.1746 | 361.622 | 376.3589
1450.3479 | 429.219 | 361.6234 | 376.3691
1451.3479 | 429.3173 | 361.6291 | 376.3691
1452.3479 | 429.3243 | 361.6332 | 376.384
1453.3479 | 429.2029 | 361.6442 | 376.3851
1454.3479 | 429.1158 | 361.6541 | 376.392
1455.3479 | 429.1602 | 361.6567 | 376.3987
1456.3479 | 429.2691 | 361.6797 | 376.3985
1457.3479 | 429.1666 | 361.6742 | 376.4025
1458.3479 | 429.1966 | 361.6809 | 376.4126
1459.3479 | 429.1384 | 361.7106 | 376.4162
1460.3635 | 429.1867 | 361.7096 | 376.4159
1461.3479 | 429.1793 | 361.74 | 376.4287
1462.3635 | 429.2277 | 361.743 | 376.4311
1463.3635 | 429.2457 | 361.7532 | 376.4328
1464.3635 | 429.2679 | 361.7802 | 376.4369
1465.3635 | 429.1929 | 361.7719 | 376.4367
1466.3635 | 429.3009 | 361.8039 | 376.4308
1467.3635 | 429.4375 | 361.8055 | 376.4261
1468.3635 | 429.517 | 361.822 | 376.4157
1469.3479 | 429.5825 | 361.8349 | 376.4146
1470.3479 | 429.566 | 361.8282 | 376.4136
1471.3635 | 429.657 | 361.8595 | 376.4051
1472.3479 | 429.6293 | 361.8543 | 376.3915
1473.3635 | 429.6205 | 361.8712 | 376.3875
1474.3479 | 429.5728 | 361.8779 | 376.3804
1475.3479 | 429.4821 | 361.8937 | 376.3805
1476.3479 | 429.5196 | 361.9046 | 376.3929
1477.3635 | 429.59 | 361.9068 | 376.3932
1478.3479 | 429.5715 | 361.9245 | 376.4054
1479.3635 | 429.6323 | 361.9152 | 376.4156
1480.3479 | 429.6333 | 361.9163 | 376.4298
1481.3635 | 429.6615 | 361.9526 | 376.4429
1482.3479 | 429.6107 | 361.9541 | 376.4572
1483.3479 | 429.5563 | 361.9714 | 376.4753
1484.3479 | 429.4396 | 361.9609 | 376.4927
1485.3479 | 429.4024 | 361.9784 | 376.5108
1486.3479 | 429.4857 | 361.9929 | 376.5387
1487.3479 | 429.4615 | 361.9937 | 376.5533
1488.3479 | 429.4554 | 362.005 | 376.5698
1489.3479 | 429.5339 | 362.0139 | 376.5883
1490.3479 | 429.5012 | 362.0397 | 376.6013
1491.3479 | 429.413 | 362.0444 | 376.6178
1492.3635 | 429.455 | 362.0514 | 376.6279
1493.3479 | 429.4655 | 362.088 | 376.6354
1494.3635 | 429.4127 | 362.091 | 376.6387
1495.3479 | 429.3604 | 362.1055 | 376.654
1496.3635 | 429.3796 | 362.1089 | 376.6631
1497.3479 | 429.434 | 362.1303 | 376.6763
1498.3479 | 429.4398 | 362.1484 | 376.6876
1499.3479 | 429.348 | 362.1469 | 376.7044
1500.3479 | 429.3944 | 362.1767 | 376.7206
1501.3479 | 429.3992 | 362.1786 | 376.7358
1502.3479 | 429.339 | 362.1857 | 376.7572
1503.3635 | 429.2749 | 362.192 | 376.7574
1504.3635 | 429.1179 | 362.182 | 376.7762
1505.3479 | 429.086 | 362.2086 | 376.7905
1506.3635 | 429.0593 | 362.212 | 376.8051
1507.3635 | 429.1842 | 362.2193 | 376.8112
1508.3479 | 429.2758 | 362.2309 | 376.8223
1509.3479 | 429.3785 | 362.2162 | 376.8258
1510.3635 | 429.4506 | 362.2572 | 376.8249
1511.3479 | 429.4431 | 362.2393 | 376.8265
1512.3479 | 429.4759 | 362.2586 | 376.8295
1513.3479 | 429.5253 | 362.2601 | 376.8295
1514.3479 | 429.4141 | 362.269 | 376.8379
1515.3479 | 429.4055 | 362.2755 | 376.838
1516.3479 | 429.3943 | 362.2788 | 376.8384
1517.3479 | 429.599 | 362.2881 | 376.8471
1518.3479 | 429.6165 | 362.3086 | 376.8405
1519.3479 | 429.7095 | 362.3038 | 376.8446
1520.3479 | 429.7512 | 362.3259 | 376.8515
1521.3479 | 429.6648 | 362.3201 | 376.8519
1522.3479 | 429.5926 | 362.3474 | 376.8537
1523.3635 | 429.4741 | 362.3648 | 376.8591
1524.3479 | 429.6162 | 362.3617 | 376.8673
1525.3479 | 429.5547 | 362.4017 | 376.8746
1526.3479 | 429.4489 | 362.4052 | 376.8835
1527.3479 | 429.521 | 362.4183 | 376.8932
1528.3479 | 429.5019 | 362.4223 | 376.8961
1529.3635 | 429.4293 | 362.4586 | 376.9085
1530.3635 | 429.3992 | 362.4818 | 376.9232
1531.3635 | 429.5164 | 362.4897 | 376.9315
1532.3635 | 429.6049 | 362.5148 | 376.943
1533.3635 | 429.6016 | 362.5078 | 376.9522
1534.3635 | 429.604 | 362.5396 | 376.9544
1535.3635 | 429.4886 | 362.5689 | 376.97
1536.3635 | 429.3139 | 362.5792 | 376.9747
1537.3635 | 429.31 | 362.6131 | 376.976
1538.3635 | 429.2297 | 362.6033 | 376.9803
1539.3635 | 429.2217 | 362.6387 | 376.9905
1540.3635 | 429.3094 | 362.6533 | 376.9905
1541.3635 | 429.3245 | 362.6441 | 376.9947
1542.3635 | 429.2323 | 362.6851 | 376.9964
1543.3635 | 429.187 | 362.6777 | 377.0006
1544.3635 | 429.2281 | 362.6834 | 376.9999
1545.3635 | 429.3138 | 362.6971 | 376.9986
1546.3635 | 429.3144 | 362.7157 | 377.0084
1547.3635 | 429.1702 | 362.7268 | 377.0124
1548.3635 | 429.0626 | 362.7244 | 377.0146
1549.3635 | 429.1235 | 362.7526 | 377.0096
1550.3635 | 429.0969 | 362.7479 | 377.0133
1551.3635 | 429.0183 | 362.7631 | 377.0097
1552.3635 | 428.9775 | 362.7735 | 377.007
1553.3635 | 428.9776 | 362.7857 | 377.007
1554.3635 | 429.0487 | 362.8156 | 377.0064
1555.3635 | 429.0153 | 362.8226 | 377.0044
1556.3635 | 429.0125 | 362.832 | 376.9988
1557.3635 | 429.0714 | 362.8545 | 377.0018
1558.3635 | 429.1291 | 362.8543 | 376.9968
1559.3635 | 429.1141 | 362.8812 | 376.9935
1560.3635 | 429.2779 | 362.8839 | 376.9953
1561.3635 | 429.3538 | 362.9076 | 376.9964
1562.3635 | 429.4799 | 362.9351 | 376.9894
1563.3635 | 429.4867 | 362.925 | 376.9946
1564.3635 | 429.3925 | 362.9537 | 376.9971
1565.3479 | 429.2683 | 362.9499 | 376.9919
1566.3635 | 429.4665 | 362.9646 | 376.9964
1567.3635 | 429.4176 | 362.9766 | 376.9939
1568.3635 | 429.2778 | 362.9759 | 377.0009
1569.3635 | 429.3954 | 362.9961 | 377.0014
1570.3635 | 429.4475 | 362.9937 | 377.0044
1571.3635 | 429.4172 | 363.0099 | 377.0042
1572.3635 | 429.4063 | 363.0201 | 377.0087
1573.3635 | 429.3309 | 363.025 | 377.0143
1574.3635 | 429.3893 | 363.0354 | 377.0087
1575.3635 | 429.4578 | 363.0344 | 377.0178
1576.3635 | 429.4831 | 363.0503 | 377.0253
1577.3479 | 429.3865 | 363.0508 | 377.0253
1578.3635 | 429.2829 | 363.0642 | 377.0307
1579.3635 | 429.3115 | 363.0904 | 377.038
1580.3479 | 429.3113 | 363.0828 | 377.042
1581.3635 | 429.3046 | 363.1002 | 377.0415
1582.3635 | 429.3153 | 363.1023 | 377.0422
1583.3479 | 429.3544 | 363.1084 | 377.0483
1584.3635 | 429.2424 | 363.1181 | 377.0455
1585.3635 | 429.1772 | 363.1199 | 377.0518
1586.3479 | 429.0728 | 363.142 | 377.0474
1587.3635 | 429.1671 | 363.1289 | 377.0459
1588.3635 | 429.1225 | 363.1486 | 377.0514
1589.3635 | 429.1408 | 363.1681 | 377.0532
1590.3635 | 429.2026 | 363.1538 | 377.0621
1591.3635 | 429.1525 | 363.1723 | 377.0709
1592.3479 | 429.2634 | 363.1735 | 377.0759
1593.3635 | 429.2335 | 363.1924 | 377.092
1594.3635 | 429.1711 | 363.1797 | 377.1032
1595.3479 | 429.1548 | 363.2173 | 377.1126
1596.3635 | 429.2581 | 363.2396 | 377.133
1597.3635 | 429.2887 | 363.2466 | 377.1443
1598.3479 | 429.3188 | 363.2553 | 377.1571
1599.3635 | 429.4449 | 363.2731 | 377.169
1600.3635 | 429.4421 | 363.2774 | 377.1793
1601.3479 | 429.3465 | 363.2999 | 377.1852
1602.3635 | 429.2992 | 363.2892 | 377.1949
1603.3635 | 429.366 | 363.3104 | 377.2051
1604.3635 | 429.3206 | 363.3314 | 377.2051
1605.3635 | 429.3562 | 363.3289 | 377.2201
1606.3479 | 429.4074 | 363.3592 | 377.2198
1607.3635 | 429.2898 | 363.3675 | 377.2239
1608.3635 | 429.2922 | 363.3662 | 377.2283
1609.3635 | 429.3812 | 363.4049 | 377.2379
1610.3635 | 429.4316 | 363.3944 | 377.2426
1611.3635 | 429.4156 | 363.4213 | 377.2523
1612.3479 | 429.3852 | 363.4326 | 377.2635
1613.3635 | 429.4133 | 363.438 | 377.2787
1614.3635 | 429.4109 | 363.4676 | 377.2893
1615.3479 | 429.3391 | 363.464 | 377.2998
1616.3635 | 429.3452 | 363.4977 | 377.3133
1617.3635 | 429.3675 | 363.4976 | 377.3243
1618.3479 | 429.4379 | 363.5166 | 377.3322
1619.3635 | 429.4237 | 363.5462 | 377.3417
1620.3635 | 429.3842 | 363.5611 | 377.3462
1621.3479 | 429.3572 | 363.5703 | 377.3617
1622.3635 | 429.4202 | 363.5879 | 377.3702
1623.3635 | 429.4058 | 363.6094 | 377.3735
1624.3635 | 429.3798 | 363.6343 | 377.3895
1625.3635 | 429.4201 | 363.6358 | 377.4049
1626.3635 | 429.5329 | 363.6627 | 377.4099
1627.3635 | 429.5428 | 363.6812 | 377.4248
1628.3479 | 429.4846 | 363.6853 | 377.4319
1629.3635 | 429.4579 | 363.7091 | 377.4434
1630.3635 | 429.5779 | 363.7307 | 377.4583
1631.3635 | 429.6291 | 363.7387 | 377.4547
1632.3635 | 429.6873 | 363.7607 | 377.4578
1633.3479 | 429.6756 | 363.7675 | 377.4658
1634.3635 | 429.6447 | 363.787 | 377.4701
1635.3635 | 429.752 | 363.7976 | 377.4739
1636.3635 | 429.7973 | 363.7991 | 377.4805
1637.3635 | 429.8095 | 363.8214 | 377.4863
1638.3635 | 429.7992 | 363.8194 | 377.4984
1639.3635 | 429.8129 | 363.8321 | 377.508
1640.3635 | 429.8952 | 363.84 | 377.5248
1641.3635 | 429.8835 | 363.8504 | 377.5279
1642.3479 | 429.8201 | 363.8754 | 377.5304
1643.3635 | 429.7768 | 363.8712 | 377.543
1644.3635 | 429.7205 | 363.8945 | 377.5492
1645.3635 | 429.6298 | 363.893 | 377.555
1646.3635 | 429.5256 | 363.9135 | 377.5639
1647.3635 | 429.3415 | 363.9346 | 377.5741
1648.3635 | 429.2259 | 363.9477 | 377.5817
1649.3635 | 429.2636 | 363.9579 | 377.5889
1650.3635 | 429.264 | 363.9735 | 377.6059
1651.3635 | 429.2201 | 363.9998 | 377.6069
1652.3635 | 429.2352 | 364.0189 | 377.6187
1653.3635 | 429.2968 | 364.0228 | 377.629
1654.3635 | 429.341 | 364.0455 | 377.6335
1655.3635 | 429.4104 | 364.0601 | 377.6422
1656.3635 | 429.3865 | 364.0647 | 377.6454
1657.3635 | 429.3334 | 364.0861 | 377.6428
1658.3635 | 429.4265 | 364.1032 | 377.646
1659.3635 | 429.4338 | 364.1243 | 377.6535
1660.3635 | 429.3795 | 364.1352 | 377.6603
1661.3635 | 429.4702 | 364.138 | 377.6698
1662.3635 | 429.4521 | 364.1571 | 377.6819
1663.3635 | 429.4496 | 364.1624 | 377.6815
1664.3635 | 429.4276 | 364.1821 | 377.6964
1665.3635 | 429.3947 | 364.191 | 377.7033
1666.3635 | 429.2873 | 364.1877 | 377.7158
1667.3635 | 429.2554 | 364.2001 | 377.7203
1668.3635 | 429.3005 | 364.1987 | 377.7256
1669.3635 | 429.4729 | 364.2314 | 377.7264
1670.3635 | 429.4952 | 364.2342 | 377.7303
1671.3635 | 429.4995 | 364.2414 | 377.744
1672.3635 | 429.4299 | 364.2757 | 377.7531
1673.3635 | 429.4356 | 364.2847 | 377.7593
1674.3635 | 429.3708 | 364.3055 | 377.7779
1675.3635 | 429.3382 | 364.3262 | 377.786
1676.3635 | 429.3774 | 364.3388 | 377.7897
1677.3635 | 429.3835 | 364.3679 | 377.8005
1678.3635 | 429.274 | 364.3891 | 377.8059
1679.3635 | 429.148 | 364.3994 | 377.8069
1680.3635 | 429.0948 | 364.4289 | 377.8156
1681.3635 | 429.1572 | 364.424 | 377.829
1682.3635 | 429.2334 | 364.4409 | 377.8305
1683.3635 | 429.2299 | 364.4348 | 377.8378
1684.3635 | 429.2291 | 364.458 | 377.846
1685.3635 | 429.2572 | 364.4619 | 377.8555
1686.3635 | 429.3088 | 364.4615 | 377.8687
1687.3635 | 429.2784 | 364.4691 | 377.8784
1688.3635 | 429.3494 | 364.461 | 377.8839
1689.3635 | 429.3707 | 364.479 | 377.903
1690.3635 | 429.3206 | 364.4844 | 377.9018
1691.3635 | 429.284 | 364.4727 | 377.9123
1692.3635 | 429.2913 | 364.4872 | 377.9259
1693.3635 | 429.3057 | 364.4784 | 377.9316
1694.3635 | 429.3156 | 364.4737 | 377.9339
1695.3635 | 429.3063 | 364.4747 | 377.9411
1696.3635 | 429.3336 | 364.4752 | 377.9479
1697.3635 | 429.323 | 364.4871 | 377.9455
1698.3635 | 429.3477 | 364.4892 | 377.9495
1699.3635 | 429.385 | 364.4986 | 377.9504
1700.3635 | 429.5957 | 364.4964 | 377.9512
1701.3635 | 429.6297 | 364.4936 | 377.9547
1702.3635 | 429.7522 | 364.5214 | 377.9554
1703.3635 | 429.8033 | 364.5113 | 377.964
1704.3635 | 429.8354 | 364.5266 | 377.9754
1705.3635 | 429.8176 | 364.5348 | 377.9832
1706.3635 | 429.7736 | 364.5267 | 377.9864
1707.3635 | 429.7628 | 364.5541 | 377.9906
1708.3635 | 429.6245 | 364.583 | 378.0061
1709.3635 | 429.5918 | 364.6316 | 378.0088
1710.3635 | 429.5301 | 364.6589 | 378.0136
1711.3635 | 429.4216 | 364.6922 | 378.0249
1712.3635 | 429.371 | 364.7232 | 378.0331
1713.3635 | 429.3575 | 364.7437 | 378.0381
1714.3635 | 429.3275 | 364.7718 | 378.0446
1715.3635 | 429.2864 | 364.7916 | 378.0524
1716.3635 | 429.2419 | 364.8191 | 378.0549
1717.3635 | 429.2254 | 364.8475 | 378.0601
1718.3635 | 429.207 | 364.8484 | 378.0639
1719.3635 | 429.1441 | 364.8813 | 378.0764
1720.3635 | 429.3112 | 364.8901 | 378.0793
1721.3635 | 429.3327 | 364.8886 | 378.0875
1722.3635 | 429.3943 | 364.927 | 378.096
1723.3635 | 429.3899 | 364.9188 | 378.1003
1724.3635 | 429.3279 | 364.9481 | 378.1048
1725.3635 | 429.2902 | 364.9474 | 378.1079
1726.3635 | 429.3188 | 364.963 | 378.1187
1727.3635 | 429.3909 | 364.966 | 378.1249
1728.3635 | 429.3535 | 364.9805 | 378.1246
1729.3635 | 429.276 | 364.9848 | 378.1312
1730.3635 | 429.3921 | 364.9923 | 378.1349
1731.3635 | 429.5385 | 365.0108 | 378.1508
1732.3635 | 429.6054 | 365.013 | 378.1539
1733.3635 | 429.5958 | 365.0196 | 378.1596
1734.3635 | 429.6204 | 365.0352 | 378.172
1735.3635 | 429.7268 | 365.0255 | 378.1888
1736.3635 | 429.7539 | 365.0477 | 378.2021
1737.3635 | 429.796 | 365.0566 | 378.2138
1738.3635 | 429.7631 | 365.0636 | 378.2181
1739.3635 | 429.8055 | 365.0662 | 378.2256
1740.3635 | 429.822 | 365.0748 | 378.2306
1741.3635 | 429.7452 | 365.0848 | 378.2385
1742.3635 | 429.5666 | 365.11 | 378.2342
1743.3635 | 429.4227 | 365.0944 | 378.2404
1744.3635 | 429.2096 | 365.1107 | 378.2496
1745.3635 | 429.1068 | 365.1046 | 378.2519
1746.3635 | 429.1306 | 365.1297 | 378.2509
1747.3635 | 429.0936 | 365.1439 | 378.2535
1748.3635 | 429.1673 | 365.1476 | 378.2556
1749.3635 | 429.2026 | 365.1698 | 378.2653
1750.3635 | 429.2289 | 365.1789 | 378.2574
1751.3635 | 429.2417 | 365.2031 | 378.269
1752.3635 | 429.2068 | 365.2013 | 378.2688
1753.3635 | 429.1338 | 365.2176 | 378.2665
1754.3635 | 429.0362 | 365.239 | 378.2697
1755.3635 | 429.0113 | 365.2412 | 378.2719
1756.3635 | 429.0981 | 365.2566 | 378.2765
1757.3635 | 429.083 | 365.2777 | 378.2859
1758.3635 | 429.0043 | 365.2805 | 378.2937
1759.3635 | 428.9456 | 365.306 | 378.2931
1760.3635 | 428.9708 | 365.3152 | 378.3089
1761.3635 | 428.93 | 365.3233 | 378.3246
1762.3635 | 428.8695 | 365.343 | 378.3359
1763.3635 | 428.9603 | 365.3553 | 378.3532
1764.3635 | 428.9884 | 365.3719 | 378.3685
1765.3635 | 428.9464 | 365.3641 | 378.3826
1766.3635 | 428.953 | 365.3903 | 378.3981
1767.3635 | 428.9484 | 365.3876 | 378.4145
1768.3635 | 428.8925 | 365.4079 | 378.4216
1769.3635 | 428.8731 | 365.4231 | 378.4293
1770.3635 | 428.9829 | 365.4284 | 378.4441
1771.3635 | 429.0699 | 365.4324 | 378.4562
1772.3635 | 429.1224 | 365.4519 | 378.466
1773.3635 | 429.1665 | 365.4557 | 378.4774
1774.3635 | 429.1782 | 365.4825 | 378.4772
1775.3635 | 429.2218 | 365.4737 | 378.4827
1776.3635 | 429.218 | 365.4876 | 378.488
1777.3635 | 429.1253 | 365.5027 | 378.491
1778.3635 | 429.0537 | 365.5107 | 378.4936
1779.3635 | 429.0176 | 365.5311 | 378.4977
1780.3635 | 429.1516 | 365.5398 | 378.5014
1781.3635 | 429.2374 | 365.5508 | 378.506
1782.3635 | 429.2292 | 365.564 | 378.5049
1783.3635 | 429.1846 | 365.5664 | 378.495
1784.3635 | 429.2224 | 365.5885 | 378.4862
1785.3635 | 429.2823 | 365.5951 | 378.4888
1786.3635 | 429.3984 | 365.6205 | 378.4876
1787.3635 | 429.4401 | 365.6266 | 378.4819
1788.3635 | 429.487 | 365.6438 | 378.4829
1789.3635 | 429.431 | 365.6569 | 378.4899
1790.3635 | 429.5545 | 365.6617 | 378.4851
1791.3635 | 429.5211 | 365.678 | 378.4871
1792.3635 | 429.464 | 365.7024 | 378.4866
1793.3635 | 429.4553 | 365.7051 | 378.4818
1794.3635 | 429.4482 | 365.7146 | 378.4854
1795.3635 | 429.3339 | 365.7261 | 378.4873
1796.3635 | 429.3166 | 365.7377 | 378.4799
1797.3635 | 429.316 | 365.7441 | 378.4799
1798.3479 | 429.3202 | 365.7425 | 378.4824
1799.3635 | 429.4235 | 365.7575 | 378.489
1800.3635 | 429.4953 | 365.7462 | 378.4919
1801.3635 | 429.5018 | 365.7662 | 378.5017
1802.3635 | 429.5138 | 365.7438 | 378.5023
1803.3479 | 429.5042 | 365.7573 | 378.5069
1804.3635 | 429.6563 | 365.7776 | 378.5144
1805.3635 | 429.7626 | 365.7596 | 378.5117
1806.3635 | 429.7796 | 365.7689 | 378.5231
1807.3635 | 429.8296 | 365.7633 | 378.5319
1808.3635 | 429.7523 | 365.7633 | 378.5348
1809.3635 | 429.6779 | 365.7863 | 378.5372
1810.3635 | 429.6178 | 365.7626 | 378.5475
1811.3635 | 429.5564 | 365.7866 | 378.5618
1812.3635 | 429.4655 | 365.7795 | 378.5601
1813.3635 | 429.4655 | 365.7859 | 378.5797
1814.3479 | 429.4697 | 365.7815 | 378.592
1815.3479 | 429.4829 | 365.7806 | 378.6189
1816.3479 | 429.4578 | 365.8091 | 378.6348
1817.3479 | 429.444 | 365.8031 | 378.6585
1818.3479 | 429.362 | 365.816 | 378.6739
1819.3479 | 429.3751 | 365.8142 | 378.6918
1820.3635 | 429.4052 | 365.8177 | 378.7075
1821.3635 | 429.3893 | 365.8332 | 378.7185
1822.3479 | 429.4811 | 365.8191 | 378.7282
1823.3479 | 429.4678 | 365.8427 | 378.7405
1824.3479 | 429.4924 | 365.8459 | 378.7491
1825.3479 | 429.6413 | 365.8434 | 378.76
1826.3479 | 429.7497 | 365.8601 | 378.7744
1827.3479 | 429.7637 | 365.8532 | 378.789
1828.3479 | 429.6899 | 365.8685 | 378.7936
1829.3479 | 429.6357 | 365.8768 | 378.8015
1830.3479 | 429.6621 | 365.8876 | 378.8105
1831.3479 | 429.7124 | 365.8781 | 378.8239
1832.3479 | 429.8291 | 365.8821 | 378.8374
1833.3479 | 429.8553 | 365.889 | 378.8515
1834.3479 | 429.8223 | 365.8965 | 378.8601
1835.3479 | 429.6986 | 365.9033 | 378.871
1836.3479 | 429.659 | 365.9189 | 378.8784
1837.3479 | 429.5967 | 365.9138 | 378.8869
1838.3479 | 429.6672 | 365.934 | 378.898
1839.3479 | 429.6423 | 365.9298 | 378.9027
1840.3479 | 429.6169 | 365.9394 | 378.9154
1841.3479 | 429.5155 | 365.939 | 378.9216
1842.3635 | 429.5808 | 365.9417 | 378.9282
1843.3479 | 429.5412 | 365.963 | 378.9303
1844.3635 | 429.6304 | 365.9473 | 378.9362
1845.3635 | 429.6269 | 365.9657 | 378.948
1846.3479 | 429.5186 | 365.974 | 378.9538
1847.3479 | 429.4392 | 365.9639 | 378.9655
1848.3635 | 429.4303 | 365.9995 | 378.9777
1849.3479 | 429.38 | 365.9861 | 378.9859
1850.3479 | 429.462 | 366.0077 | 379.0017
1851.3479 | 429.5218 | 366.0183 | 379.01
1852.3479 | 429.5473 | 366.0164 | 379.0292
1853.3479 | 429.5092 | 366.0384 | 379.0412
1854.3479 | 429.4803 | 366.0263 | 379.0525
1855.3479 | 429.4966 | 366.0455 | 379.0569
1856.3479 | 429.4402 | 366.0549 | 379.0681
1857.3479 | 429.4909 | 366.0626 | 379.0756
1858.3479 | 429.4205 | 366.0811 | 379.0813
1859.3479 | 429.4246 | 366.0712 | 379.0946
1860.3479 | 429.4043 | 366.0976 | 379.0967
1861.3479 | 429.4255 | 366.0924 | 379.0952
1862.3479 | 429.3324 | 366.1093 | 379.1093
1863.3479 | 429.2992 | 366.1259 | 379.1107
1864.3479 | 429.305 | 366.1204 | 379.1238
1865.3479 | 429.3175 | 366.1261 | 379.1238
1866.3479 | 429.3521 | 366.1413 | 379.1358
1867.3479 | 429.3544 | 366.1373 | 379.1408
1868.3479 | 429.301 | 366.1454 | 379.1596
1869.3635 | 429.324 | 366.1344 | 379.169
1870.3479 | 429.3219 | 366.1499 | 379.1809
1871.3479 | 429.3515 | 366.1509 | 379.19
1872.3479 | 429.3046 | 366.1639 | 379.1969
1873.3479 | 429.2665 | 366.1737 | 379.2058
1874.3479 | 429.2448 | 366.1667 | 379.213
1875.3635 | 429.2607 | 366.1825 | 379.2231
1876.3479 | 429.2589 | 366.1818 | 379.2159
1877.3479 | 429.3318 | 366.1849 | 379.2256
1878.3479 | 429.337 | 366.2077 | 379.2299
1879.3479 | 429.3805 | 366.1937 | 379.2419
1880.3479 | 429.2671 | 366.2096 | 379.2468
1881.3635 | 429.2432 | 366.2062 | 379.2471
1882.3479 | 429.2311 | 366.214 | 379.2505
1883.3479 | 429.1206 | 366.2248 | 379.2561
1884.3635 | 429.0592 | 366.2158 | 379.2569
1885.3479 | 429.1133 | 366.233 | 379.2641
1886.3479 | 429.1872 | 366.2394 | 379.2648
1887.3479 | 429.2086 | 366.2406 | 379.2759
1888.3479 | 429.2546 | 366.2475 | 379.2819
1889.3635 | 429.309 | 366.2469 | 379.2806
1890.3479 | 429.2452 | 366.2605 | 379.2868
1891.3635 | 429.2322 | 366.2544 | 379.291
1892.3479 | 429.38 | 366.2676 | 379.2986
1893.3635 | 429.4861 | 366.2717 | 379.2911
1894.3479 | 429.4499 | 366.27 | 379.2958
1895.3635 | 429.4424 | 366.2905 | 379.3049
1896.3479 | 429.3451 | 366.2908 | 379.3036
1897.3635 | 429.2811 | 366.3071 | 379.3034
1898.3479 | 429.2405 | 366.3353 | 379.3092
1899.3635 | 429.3279 | 366.3155 | 379.3013
1900.3479 | 429.3252 | 366.348 | 379.2986
1901.3479 | 429.2004 | 366.3424 | 379.2992
1902.3479 | 429.1746 | 366.3615 | 379.2991
1903.3635 | 429.2725 | 366.3711 | 379.2928
1904.3479 | 429.2814 | 366.3695 | 379.2965
1905.3479 | 429.2525 | 366.393 | 379.3002
1906.3479 | 429.3234 | 366.4029 | 379.3026
1907.3635 | 429.2193 | 366.4142 | 379.3198
1908.3479 | 429.1724 | 366.4268 | 379.3249
1909.3635 | 429.1528 | 366.4176 | 379.3316
1910.3479 | 429.1909 | 366.4545 | 379.3403
1911.3635 | 429.1595 | 366.4625 | 379.351
1912.3479 | 429.2672 | 366.4824 | 379.3607
1913.3635 | 429.3737 | 366.4777 | 379.3711
1914.3479 | 429.4837 | 366.4993 | 379.3855
1915.3635 | 429.4463 | 366.5066 | 379.4062
1916.3479 | 429.4111 | 366.5128 | 379.4164
1917.3479 | 429.4848 | 366.54 | 379.4279
1918.3479 | 429.467 | 366.5359 | 379.4405
1919.3479 | 429.3684 | 366.5353 | 379.4613
1920.3479 | 429.3659 | 366.5599 | 379.4699
1921.3479 | 429.2141 | 366.5591 | 379.481
1922.3479 | 429.1319 | 366.5857 | 379.4953
1923.3479 | 429.1614 | 366.5969 | 379.4994
1924.3479 | 429.125 | 366.5976 | 379.5011
1925.3635 | 429.011 | 366.6182 | 379.5084
1926.3479 | 429.0764 | 366.606 | 379.5106
1927.3635 | 429.0912 | 366.6403 | 379.5151
1928.3479 | 429.0115 | 366.6291 | 379.5184
1929.3635 | 429.0217 | 366.6414 | 379.5184
1930.3479 | 428.9483 | 366.6629 | 379.5248
1931.3635 | 428.9767 | 366.6486 | 379.5293
1932.3479 | 428.9681 | 366.6691 | 379.5171
1933.3635 | 429.1004 | 366.678 | 379.523
1934.3479 | 429.1237 | 366.6883 | 379.5319
1935.3479 | 429.159 | 366.7019 | 379.5412
1936.3479 | 429.2187 | 366.7012 | 379.5422
1937.3479 | 429.2974 | 366.7279 | 379.5488
1938.3479 | 429.2918 | 366.7263 | 379.5474
1939.3479 | 429.2816 | 366.7243 | 379.5543
1940.3479 | 429.2531 | 366.7423 | 379.551
1941.3479 | 429.244 | 366.7349 | 379.5524
1942.3479 | 429.1786 | 366.7478 | 379.5562
1943.3479 | 429.2595 | 366.7373 | 379.5632
1944.3479 | 429.1913 | 366.7534 | 379.5607
1945.3479 | 429.1053 | 366.774 | 379.5672
1946.3635 | 429.0872 | 366.7633 | 379.5712
1947.3479 | 429.0562 | 366.7821 | 379.563
1948.3635 | 428.8944 | 366.7802 | 379.5645
1949.3479 | 428.8033 | 366.7998 | 379.5542
1950.3635 | 428.9132 | 366.8091 | 379.5646
1951.3635 | 428.9156 | 366.8024 | 379.552
1952.3635 | 428.9032 | 366.821 | 379.5456
1953.3635 | 428.9087 | 366.8113 | 379.5496
1954.3635 | 428.8756 | 366.8458 | 379.5428
1955.3635 | 428.8829 | 366.8543 | 379.5426
1956.3635 | 428.8896 | 366.8614 | 379.5417
1957.3635 | 428.8181 | 366.87 | 379.5435
1958.3635 | 428.7644 | 366.8678 | 379.5393
1959.3635 | 428.8584 | 366.9061 | 379.5433
1960.3635 | 428.848 | 366.9091 | 379.5494
1961.3635 | 428.6695 | 366.9163 | 379.5476
1962.3635 | 428.5514 | 366.9368 | 379.5504
1963.3635 | 428.6046 | 366.9265 | 379.5462
1964.3635 | 428.7457 | 366.9397 | 379.5453
1965.3635 | 428.8517 | 366.9492 | 379.5466
1966.3635 | 428.9207 | 366.9517 | 379.55
1967.3635 | 428.9794 | 366.961 | 379.5523
1968.3635 | 429.0239 | 366.9689 | 379.5618
1969.3635 | 429.1233 | 366.9745 | 379.5547
1970.3635 | 429.1447 | 366.9646 | 379.5631
1971.3635 | 429.1993 | 366.962 | 379.5632
1972.3635 | 429.2394 | 366.9799 | 379.5705
1973.3635 | 429.2732 | 366.9683 | 379.5711
1974.3635 | 429.3199 | 366.9744 | 379.5743
1975.3635 | 429.365 | 366.9883 | 379.5759
1976.3635 | 429.2675 | 366.9702 | 379.5824
1977.3479 | 429.2932 | 366.9831 | 379.5844
1978.3635 | 429.2832 | 366.971 | 379.5815
1979.3635 | 429.2423 | 366.9582 | 379.5887
1980.3479 | 429.302 | 366.9633 | 379.5959
1981.3479 | 429.446 | 366.9564 | 379.596
1982.3479 | 429.4678 | 366.9686 | 379.5953
1983.3479 | 429.4516 | 366.9513 | 379.597
1984.3479 | 429.4764 | 366.9515 | 379.6061
1985.3479 | 429.6858 | 366.9526 | 379.6072
1986.3479 | 429.6442 | 366.9663 | 379.6127
1987.3635 | 429.6012 | 366.9817 | 379.6181
1988.3479 | 429.6276 | 366.9677 | 379.6302
1989.3479 | 429.6923 | 366.9888 | 379.6422
1990.3479 | 429.693 | 366.9888 | 379.6497
1991.3479 | 429.705 | 367.0022 | 379.6642
1992.3635 | 429.6545 | 367.022 | 379.6692
1993.3479 | 429.5752 | 367.0139 | 379.679
1994.3635 | 429.5371 | 367.0313 | 379.6885
1995.3479 | 429.5548 | 367.047 | 379.6882
1996.3635 | 429.4732 | 367.0351 | 379.6939
1997.3479 | 429.4433 | 367.0674 | 379.6925
1998.3635 | 429.3496 | 367.0703 | 379.7043
1999.3479 | 429.4639 | 367.086 | 379.7139
2000.3635 | 429.5206 | 367.0947 | 379.7177
2001.3479 | 429.4779 | 367.0959 | 379.723
2002.3635 | 429.4125 | 367.1117 | 379.7274
2003.3479 | 429.4457 | 367.1102 | 379.7282
2004.3479 | 429.4034 | 367.1313 | 379.7391
2005.3479 | 429.3542 | 367.1429 | 379.7436
2006.3479 | 429.1645 | 367.1444 | 379.7558
2007.3479 | 429.0444 | 367.1699 | 379.7581
2008.3479 | 428.9412 | 367.1669 | 379.7769
2009.3479 | 428.8343 | 367.1916 | 379.7875
2010.3635 | 428.8611 | 367.2065 | 379.8011
2011.3479 | 428.7753 | 367.2111 | 379.8099
2012.3479 | 428.7977 | 367.2385 | 379.8159
2013.3635 | 428.8405 | 367.2393 | 379.8211
2014.3479 | 428.8608 | 367.2667 | 379.8325
2015.3635 | 428.8689 | 367.2705 | 379.8373
2016.3635 | 428.8225 | 367.2815 | 379.8458
2017.3635 | 428.774 | 367.3106 | 379.8458
2018.3635 | 428.7773 | 367.2915 | 379.8555
2019.3635 | 428.8676 | 367.3419 | 379.8638
2020.3635 | 428.9873 | 367.3389 | 379.8665
2021.3635 | 429.0577 | 367.3698 | 379.8758
2022.3635 | 429.1161 | 367.3764 | 379.8822
2023.3635 | 429.1026 | 367.3779 | 379.8903
2024.3635 | 429.2261 | 367.3976 | 379.893
2025.3635 | 429.2702 | 367.3863 | 379.8951
2026.3635 | 429.2963 | 367.4072 | 379.8956
2027.3479 | 429.15 | 367.4154 | 379.9035
2028.3635 | 429.0189 | 367.418 | 379.9065
2029.3635 | 429.045 | 367.4369 | 379.9206
2030.3635 | 429.0757 | 367.4412 | 379.9281
2031.3635 | 429.0882 | 367.4532 | 379.9449
2032.3635 | 429.0544 | 367.4572 | 379.9615
2033.3635 | 428.947 | 367.4598 | 379.9764
2034.3635 | 428.898 | 367.4848 | 379.9902
2035.3635 | 428.8553 | 367.4823 | 379.9911
2036.3635 | 428.6913 | 367.4974 | 379.9937
2037.3635 | 428.7643 | 367.5103 | 380.0019
2038.3635 | 428.7982 | 367.5156 | 380.0072
2039.3635 | 428.7956 | 367.5387 | 380.0143
2040.3479 | 428.6821 | 367.5385 | 380.0205
2041.3635 | 428.6317 | 367.565 | 380.0274
2042.3635 | 428.6033 | 367.5594 | 380.0341
2043.3635 | 428.6529 | 367.5789 | 380.0406
2044.3635 | 428.7615 | 367.5887 | 380.0404
2045.3635 | 428.7384 | 367.5896 | 380.0477
2046.3479 | 428.7708 | 367.6108 | 380.0547
2047.3635 | 428.862 | 367.6031 | 380.0567
2048.3635 | 428.934 | 367.5986 | 380.0607
2049.3635 | 428.8603 | 367.6226 | 380.0628
2050.3635 | 428.8367 | 367.6141 | 380.067
2051.3635 | 428.8369 | 367.6248 | 380.0772
2052.3635 | 428.8451 | 367.6136 | 380.0707
2053.3479 | 428.9246 | 367.6155 | 380.0694
2054.3635 | 428.9554 | 367.6109 | 380.0683
2055.3635 | 429.073 | 367.6104 | 380.0644
2056.3635 | 429.0686 | 367.6254 | 380.0678
2057.3635 | 429.1626 | 367.5988 | 380.0796
2058.3635 | 429.1524 | 367.6171 | 380.091
2059.3635 | 429.1851 | 367.622 | 380.0979
2060.3635 | 429.2275 | 367.5993 | 380.1056
2061.3635 | 429.2386 | 367.6089 | 380.1198
2062.3635 | 429.1993 | 367.6042 | 380.1337
2063.3635 | 429.199 | 367.5913 | 380.1409
2064.3635 | 429.2089 | 367.5777 | 380.1566
2065.3635 | 429.2091 | 367.5948 | 380.1743
2066.3635 | 429.174 | 367.6039 | 380.1832
2067.3635 | 429.1807 | 367.5928 | 380.1866
2068.3635 | 429.1729 | 367.583 | 380.1882
2069.3635 | 429.2674 | 367.5958 | 380.1856
2070.3635 | 429.3862 | 367.5718 | 380.1885
2071.3635 | 429.3463 | 367.5993 | 380.1888
2072.3635 | 429.2675 | 367.587 | 380.185
2073.3635 | 429.2401 | 367.5874 | 380.1824
2074.3635 | 429.2205 | 367.5788 | 380.1777
2075.3635 | 429.227 | 367.5827 | 380.1689
2076.3635 | 429.247 | 367.5925 | 380.1734
2077.3635 | 429.266 | 367.5711 | 380.1752
2078.3635 | 429.2456 | 367.5814 | 380.1724
2079.3635 | 429.1654 | 367.581 | 380.1731
2080.3635 | 429.2084 | 367.5767 | 380.1835
2081.3635 | 429.2365 | 367.5912 | 380.1887
2082.3635 | 429.309 | 367.5612 | 380.1946
2083.3635 | 429.2906 | 367.5708 | 380.1965
2084.3635 | 429.3217 | 367.5695 | 380.2044
2085.3635 | 429.3517 | 367.5704 | 380.2198
2086.3635 | 429.2537 | 367.5757 | 380.2299
2087.3635 | 429.1463 | 367.5605 | 380.2507
2088.3635 | 429.1153 | 367.5628 | 380.2619
2089.3635 | 429.2127 | 367.5663 | 380.2785
2090.3635 | 429.3163 | 367.5617 | 380.2984
2091.3635 | 429.3587 | 367.5771 | 380.3147
2092.3479 | 429.3416 | 367.5593 | 380.3253
2093.3635 | 429.2747 | 367.5697 | 380.3449
2094.3635 | 429.1942 | 367.5754 | 380.3591
2095.3635 | 429.2566 | 367.5688 | 380.3776
2096.3635 | 429.2792 | 367.5671 | 380.3922
2097.3635 | 429.0851 | 367.5628 | 380.405
2098.3635 | 428.8728 | 367.5763 | 380.4188
2099.3635 | 428.9569 | 367.5712 | 380.4384
2100.3635 | 429.0783 | 367.557 | 380.4549
2101.3635 | 429.1023 | 367.5797 | 380.4671
2102.3635 | 429.0275 | 367.5685 | 380.4709
2103.3635 | 428.9341 | 367.5741 | 380.4858
2104.3479 | 428.8962 | 367.564 | 380.4877
2105.3635 | 428.8848 | 367.5741 | 380.487
2106.3635 | 429.0086 | 367.5775 | 380.4844
2107.3635 | 429.0018 | 367.5666 | 380.4821
2108.3635 | 428.9172 | 367.5927 | 380.4724
2109.3479 | 428.9602 | 367.5864 | 380.4671
2110.3635 | 429.0322 | 367.5973 | 380.4636
2111.3635 | 429.029 | 367.6124 | 380.4478
2112.3635 | 429.0326 | 367.5927 | 380.4443
2113.3635 | 429.1049 | 367.6015 | 380.4336
2114.3635 | 429.1459 | 367.5907 | 380.4255
2115.3635 | 429.2622 | 367.59 | 380.4133
2116.3635 | 429.253 | 367.6056 | 380.4069
2117.3635 | 429.3256 | 367.598 | 380.4043
2118.3635 | 429.3107 | 367.6039 | 380.3942
2119.3635 | 429.2725 | 367.5989 | 380.3954
2120.3635 | 429.3444 | 367.6013 | 380.4026
2121.3635 | 429.2309 | 367.5959 | 380.3976
2122.3635 | 429.1357 | 367.591 | 380.4002
2123.3635 | 429.2023 | 367.5988 | 380.413
2124.3635 | 429.2402 | 367.5909 | 380.4219
2125.3635 | 429.2391 | 367.5905 | 380.4269
2126.3635 | 429.2184 | 367.5979 | 380.4447
2127.3792 | 429.1727 | 367.5867 | 380.4485
2128.3635 | 429.1373 | 367.5981 | 380.4617
2129.3635 | 429.2077 | 367.583 | 380.4598
2130.3635 | 429.24 | 367.5864 | 380.4704
2131.3635 | 429.2552 | 367.5829 | 380.4686
2132.3635 | 429.2898 | 367.5843 | 380.4715
2133.3635 | 429.2327 | 367.5994 | 380.4796
2134.3635 | 429.1182 | 367.5664 | 380.4752
2135.3635 | 429.0357 | 367.5753 | 380.4691
2136.3635 | 428.9989 | 367.5713 | 380.4656
2137.3635 | 429.0119 | 367.5589 | 380.4609
2138.3635 | 429.0228 | 367.5539 | 380.4489
2139.3635 | 429.1244 | 367.551 | 380.4378
2140.3635 | 429.0299 | 367.5535 | 380.443
2141.3635 | 428.9805 | 367.5572 | 380.4433
2142.3635 | 429.0299 | 367.5504 | 380.4374
2143.3635 | 428.9746 | 367.5521 | 380.4266
2144.3635 | 429.0068 | 367.5391 | 380.4262
2145.3635 | 428.8592 | 367.5431 | 380.4159
2146.3635 | 428.8688 | 367.5324 | 380.411
2147.3635 | 429.0267 | 367.5158 | 380.4024
2148.3635 | 428.9984 | 367.5256 | 380.4036
2149.3635 | 428.9139 | 367.5085 | 380.4017
2150.3635 | 429.0251 | 367.5158 | 380.3995
2151.3635 | 429.0317 | 367.5033 | 380.4034
2152.3635 | 429.164 | 367.4982 | 380.4012
2153.3635 | 429.2841 | 367.4967 | 380.4121
2154.3635 | 429.327 | 367.4769 | 380.4103
2155.3635 | 429.3743 | 367.478 | 380.4195
2156.3635 | 429.3129 | 367.4715 | 380.4228
2157.3635 | 429.4144 | 367.476 | 380.4275
2158.3635 | 429.4677 | 367.4754 | 380.4308
2159.3635 | 429.5177 | 367.4536 | 380.4403
2160.3635 | 429.5575 | 367.4473 | 380.4354
2161.3635 | 429.498 | 367.4478 | 380.4293
2162.3635 | 429.4755 | 367.4547 | 380.4312
2163.3635 | 429.5643 | 367.4585 | 380.4298
2164.3635 | 429.5561 | 367.4539 | 380.4196
2165.3635 | 429.5874 | 367.4733 | 380.4187
2166.3635 | 429.5999 | 367.4622 | 380.414
2167.3635 | 429.5324 | 367.4718 | 380.415
2168.3635 | 429.3968 | 367.4761 | 380.4173
2169.3635 | 429.2951 | 367.4733 | 380.4155
2170.3635 | 429.2716 | 367.4982 | 380.4143
2171.3635 | 429.2353 | 367.4929 | 380.4163
2172.3635 | 429.15 | 367.5084 | 380.4218
2173.3635 | 429.1712 | 367.5098 | 380.4123
2174.3635 | 429.1583 | 367.5235 | 380.4223
2175.3635 | 429.1238 | 367.5198 | 380.4267
2176.3635 | 429.151 | 367.5334 | 380.4316
2177.3635 | 429.2019 | 367.5431 | 380.436
2178.3635 | 429.2286 | 367.5489 | 380.4441
2179.3635 | 429.262 | 367.5635 | 380.4458
2180.3635 | 429.3084 | 367.5731 | 380.4497
2181.3635 | 429.3111 | 367.5787 | 380.4548
2182.3635 | 429.3016 | 367.602 | 380.4599
2183.3635 | 429.2751 | 367.6043 | 380.4668
2184.3635 | 429.2403 | 367.6053 | 380.4725
2185.3635 | 429.17 | 367.6305 | 380.483
2186.3635 | 429.1899 | 367.6421 | 380.4807
2187.3635 | 429.0252 | 367.66 | 380.4875
2188.3635 | 428.8683 | 367.6582 | 380.4901
2189.3635 | 428.7548 | 367.678 | 380.5018
2190.3635 | 428.7315 | 367.6792 | 380.4985
2191.3635 | 428.8173 | 367.697 | 380.5083
2192.3635 | 428.8974 | 367.6993 | 380.5149
2193.3635 | 428.926 | 367.6965 | 380.5164
2194.3635 | 428.9444 | 367.7193 | 380.521
2195.3635 | 429.057 | 367.72 | 380.5228
2196.3635 | 428.9604 | 367.7121 | 380.519
2197.3635 | 428.8895 | 367.7176 | 380.5191
2198.3635 | 428.8584 | 367.7128 | 380.5104
2199.3635 | 428.8538 | 367.7287 | 380.5139
2200.3635 | 428.8418 | 367.7216 | 380.5033
2201.3635 | 428.8961 | 367.7311 | 380.487
2202.3635 | 428.924 | 367.7474 | 380.4838
2203.3635 | 428.9152 | 367.7425 | 380.4771
2204.3635 | 428.8719 | 367.7531 | 380.4731
2205.3635 | 428.9158 | 367.7424 | 380.4666
2206.3635 | 428.9544 | 367.7479 | 380.4687
2207.3635 | 429.0573 | 367.7484 | 380.4624
2208.3635 | 429.0722 | 367.7435 | 380.4588
2209.3635 | 429.1403 | 367.7493 | 380.4576
2210.3635 | 429.1986 | 367.7448 | 380.4595
2211.3635 | 429.1845 | 367.7583 | 380.4554
2212.3635 | 429.2404 | 367.7397 | 380.4559
2213.3635 | 429.234 | 367.7319 | 380.4556
2214.3635 | 429.2586 | 367.7533 | 380.462
2215.3635 | 429.3027 | 367.7365 | 380.4646
2216.3635 | 429.2741 | 367.7341 | 380.4662
2217.3635 | 429.2709 | 367.743 | 380.4696
2218.3635 | 429.2908 | 367.7274 | 380.4788
2219.3635 | 429.3122 | 367.7461 | 380.4839
2220.3635 | 429.3136 | 367.74 | 380.4943
2221.3635 | 429.3798 | 367.7491 | 380.502
2222.3635 | 429.3597 | 367.7453 | 380.5082
2223.3635 | 429.3271 | 367.7527 | 380.5144
2224.3635 | 429.2035 | 367.7546 | 380.5204
2225.3635 | 429.0394 | 367.7423 | 380.525
2226.3635 | 428.9933 | 367.758 | 380.5336
2227.3635 | 428.9407 | 367.7562 | 380.54
2228.3635 | 428.8624 | 367.7522 | 380.5395
2229.3635 | 428.7617 | 367.756 | 380.5422
2230.3635 | 428.7136 | 367.7428 | 380.5352
2231.3635 | 428.6183 | 367.7646 | 380.5408
2232.3635 | 428.5634 | 367.7637 | 380.5389
2233.3635 | 428.5712 | 367.7635 | 380.53
2234.3635 | 428.5472 | 367.7636 | 380.5292
2235.3635 | 428.637 | 367.7551 | 380.5295
2236.3635 | 428.5808 | 367.7647 | 380.5285
2237.3635 | 428.6485 | 367.7602 | 380.5281
2238.3635 | 428.6613 | 367.7602 | 380.5299
2239.3635 | 428.5624 | 367.7607 | 380.5191
2240.3635 | 428.4772 | 367.7461 | 380.5172
2241.3635 | 428.4931 | 367.7605 | 380.5164
2242.3635 | 428.5493 | 367.7457 | 380.5084
2243.3635 | 428.5368 | 367.7495 | 380.5093
2244.3635 | 428.5452 | 367.7523 | 380.5011
2245.3635 | 428.6746 | 367.7405 | 380.4903
2246.3635 | 428.8072 | 367.7469 | 380.486
2247.3635 | 428.8841 | 367.7395 | 380.4789
2248.3635 | 428.8678 | 367.7502 | 380.4725
2249.3635 | 429.0057 | 367.7425 | 380.4694
2250.3635 | 429.0853 | 367.7413 | 380.4707
2251.3635 | 429.0878 | 367.7494 | 380.4706
2252.3635 | 429.1602 | 367.7226 | 380.4622
2253.3635 | 429.3051 | 367.7301 | 380.4645
2254.3635 | 429.385 | 367.7256 | 380.4658
2255.3635 | 429.3857 | 367.7189 | 380.4658
2256.3635 | 429.3916 | 367.7219 | 380.4751
2257.3635 | 429.3845 | 367.709 | 380.4679
2258.3635 | 429.3696 | 367.706 | 380.4758
2259.3635 | 429.3637 | 367.6976 | 380.4728
2260.3635 | 429.4612 | 367.7074 | 380.4722
2261.3635 | 429.5082 | 367.705 | 380.4738
2262.3635 | 429.5146 | 367.6948 | 380.4703
2263.3635 | 429.5642 | 367.7007 | 380.4728
2264.3479 | 429.5602 | 367.6713 | 380.4697
2265.3635 | 429.5125 | 367.694 | 380.4703
2266.3479 | 429.3603 | 367.7082 | 380.4648
2267.3635 | 429.3434 | 367.7005 | 380.458
2268.3479 | 429.3434 | 367.7027 | 380.4591
2269.3479 | 429.3489 | 367.6987 | 380.4535
2270.3635 | 429.1309 | 367.7074 | 380.4547
2271.3479 | 429.12 | 367.7041 | 380.4479
2272.3635 | 429.0849 | 367.7162 | 380.4517
2273.3479 | 428.9421 | 367.7274 | 380.4539
2274.3479 | 428.904 | 367.7265 | 380.453
2275.3479 | 428.9934 | 367.742 | 380.4616
2276.3479 | 429.0848 | 367.7472 | 380.4714
2277.3635 | 429.1471 | 367.7606 | 380.4816
2278.3479 | 429.1451 | 367.758 | 380.4829
2279.3479 | 429.1465 | 367.7491 | 380.4911
2280.3479 | 429.0819 | 367.779 | 380.4836
2281.3479 | 429.2332 | 367.7796 | 380.4892
2282.3479 | 429.3127 | 367.7781 | 380.4881
2283.3635 | 429.3481 | 367.784 | 380.4902
2284.3479 | 429.3373 | 367.7875 | 380.4898
2285.3479 | 429.2462 | 367.8018 | 380.4952
2286.3479 | 429.246 | 367.7962 | 380.4976
2287.3479 | 429.2124 | 367.8038 | 380.5061
2288.3479 | 429.1853 | 367.817 | 380.5157
2289.3479 | 429.2036 | 367.8144 | 380.5237
2290.3479 | 429.1902 | 367.8355 | 380.5452
2291.3479 | 429.2347 | 367.8224 | 380.5528
2292.3479 | 429.2946 | 367.8442 | 380.5675
2293.3479 | 429.3601 | 367.85 | 380.5781
2294.3479 | 429.3507 | 367.8258 | 380.5956
2295.3479 | 429.2498 | 367.8395 | 380.5996
2296.3479 | 429.2641 | 367.8202 | 380.6101
2297.3479 | 429.2232 | 367.8258 | 380.628
2298.3635 | 429.2354 | 367.8324 | 380.633
2299.3479 | 429.159 | 367.8215 | 380.6394
2300.3479 | 429.252 | 367.8416 | 380.653
2301.3479 | 429.1997 | 367.8289 | 380.655
2302.3479 | 429.1929 | 367.8399 | 380.6591
2303.3479 | 429.2457 | 367.8235 | 380.6702
2304.3479 | 429.281 | 367.8293 | 380.6719
2305.3479 | 429.4089 | 367.8432 | 380.6839
2306.3479 | 429.3969 | 367.8323 | 380.6912
2307.3635 | 429.3573 | 367.8484 | 380.6946
2308.3479 | 429.4323 | 367.8426 | 380.7001
2309.3479 | 429.457 | 367.8563 | 380.7022
2310.3479 | 429.4714 | 367.8481 | 380.7076
2311.3479 | 429.5018 | 367.842 | 380.7057
2312.3479 | 429.6512 | 367.8609 | 380.7048
2313.3635 | 429.7253 | 367.851 | 380.7141
2314.3479 | 429.8385 | 367.8558 | 380.7099
2315.3479 | 429.9431 | 367.8482 | 380.708
2316.3479 | 429.9486 | 367.8442 | 380.7207
2317.3479 | 429.8645 | 367.8521 | 380.7205
2318.3479 | 429.8522 | 367.8372 | 380.7267
2319.3479 | 429.816 | 367.839 | 380.7317
2320.3479 | 429.7483 | 367.8365 | 380.7411
2321.3635 | 429.7292 | 367.822 | 380.7527
2322.3479 | 429.6658 | 367.8393 | 380.7578
2323.3479 | 429.6831 | 367.8189 | 380.7676
2324.3479 | 429.6392 | 367.8311 | 380.7718
2325.3479 | 429.5344 | 367.8245 | 380.7824
2326.3635 | 429.5778 | 367.8377 | 380.7845
2327.3635 | 429.7194 | 367.8344 | 380.778
2328.3479 | 429.7866 | 367.8203 | 380.7916
2329.3479 | 429.801 | 367.8523 | 380.793
2330.3479 | 429.8608 | 367.8486 | 380.7906
2331.3479 | 429.8506 | 367.8506 | 380.7992
2332.3479 | 429.8125 | 367.8523 | 380.8066
2333.3479 | 429.7054 | 367.8565 | 380.8049
2334.3479 | 429.7114 | 367.864 | 380.8128
2335.3479 | 429.7324 | 367.8608 | 380.8127
2336.3479 | 429.6887 | 367.8703 | 380.8085
2337.3635 | 429.7211 | 367.8684 | 380.8123
2338.3479 | 429.785 | 367.8697 | 380.8054
2339.3479 | 429.7973 | 367.8828 | 380.8037
2340.3479 | 429.8268 | 367.8861 | 380.8072
2341.3479 | 429.877 | 367.9082 | 380.8041
2342.3479 | 429.7547 | 367.8941 | 380.8109
2343.3479 | 429.7442 | 367.9173 | 380.81
2344.3479 | 429.7134 | 367.9259 | 380.8152
2345.3635 | 429.7156 | 367.9204 | 380.8179
2346.3479 | 429.7272 | 367.9459 | 380.8148
2347.3479 | 429.8154 | 367.9421 | 380.8194
2348.3479 | 429.8519 | 367.9421 | 380.8142
2349.3479 | 429.9233 | 367.9571 | 380.8176
2350.3479 | 429.9933 | 367.9475 | 380.8141
2351.3479 | 429.9535 | 367.9634 | 380.8191
2352.3479 | 429.8398 | 367.9728 | 380.8098
2353.3479 | 429.7959 | 367.9533 | 380.8145
2354.3479 | 429.7317 | 367.9791 | 380.8082
2355.3479 | 429.8006 | 367.9741 | 380.8144
2356.3479 | 429.7424 | 367.9885 | 380.8238
2357.3479 | 429.7007 | 367.9844 | 380.8158
2358.3479 | 429.7116 | 367.9979 | 380.8224
2359.3479 | 429.6941 | 367.9839 | 380.8266
2360.3479 | 429.5615 | 367.9993 | 380.8241
2361.3479 | 429.5861 | 368.0138 | 380.8252
2362.3479 | 429.6525 | 367.9719 | 380.8235
2363.3479 | 429.6891 | 368.0116 | 380.8209
2364.3479 | 429.6752 | 368.0029 | 380.8144
2365.3479 | 429.591 | 368.0069 | 380.8176
2366.3479 | 429.6216 | 368.0167 | 380.8114
2367.3635 | 429.5618 | 368.0122 | 380.8136
2368.3635 | 429.6477 | 368.0275 | 380.8105
2369.3479 | 429.6339 | 368.0272 | 380.8092
2370.3635 | 429.5947 | 368.0238 | 380.8139
2371.3635 | 429.6326 | 368.0409 | 380.8119
2372.3479 | 429.6871 | 368.0417 | 380.8204
2373.3479 | 429.6668 | 368.0581 | 380.8193
2374.3635 | 429.6633 | 368.0472 | 380.8252
2375.3479 | 429.7368 | 368.0625 | 380.8288
2376.3635 | 429.721 | 368.0601 | 380.839
2377.3479 | 429.7245 | 368.0661 | 380.8411
2378.3635 | 429.685 | 368.0733 | 380.8481
2379.3479 | 429.645 | 368.0667 | 380.8497
2380.3635 | 429.6188 | 368.0801 | 380.8526
2381.3479 | 429.6006 | 368.0784 | 380.8564
2382.3479 | 429.5269 | 368.0963 | 380.8624
2383.3479 | 429.4581 | 368.0975 | 380.868
2384.3479 | 429.4123 | 368.0895 | 380.8781
2385.3479 | 429.3549 | 368.1094 | 380.8733
2386.3479 | 429.3462 | 368.0902 | 380.8702
2387.3635 | 429.394 | 368.1128 | 380.8848
2388.3479 | 429.4154 | 368.1171 | 380.883
2389.3635 | 429.5236 | 368.1122 | 380.8806
2390.3479 | 429.5747 | 368.1352 | 380.88
2391.3635 | 429.5376 | 368.1242 | 380.8831
2392.3635 | 429.465 | 368.1491 | 380.883
2393.3635 | 429.4304 | 368.1465 | 380.8793
2394.3635 | 429.4353 | 368.1601 | 380.8737
2395.3479 | 429.4886 | 368.1733 | 380.8917
2396.3635 | 429.4847 | 368.1435 | 380.8908
2397.3635 | 429.341 | 368.1813 | 380.8956
2398.3635 | 429.348 | 368.1771 | 380.9041
2399.3635 | 429.3702 | 368.1722 | 380.921
2400.3479 | 429.3677 | 368.1948 | 380.9216
2401.3479 | 429.328 | 368.1948 | 380.9343
2402.3479 | 429.3073 | 368.2005 | 380.9336
2403.3479 | 429.3904 | 368.1993 | 380.9437
2404.3479 | 429.4383 | 368.205 | 380.9521
2405.3479 | 429.4952 | 368.2033 | 380.9598
2406.3479 | 429.4653 | 368.2035 | 380.9613
2407.3479 | 429.381 | 368.2094 | 380.9667
2408.3479 | 429.4682 | 368.1931 | 380.9711
2409.3479 | 429.5338 | 368.2048 | 380.9719
2410.3635 | 429.5311 | 368.2047 | 380.9852
2411.3479 | 429.5283 | 368.1904 | 380.982
2412.3479 | 429.5287 | 368.2031 | 380.9849
2413.3479 | 429.5831 | 368.1937 | 380.9901
2414.3635 | 429.6257 | 368.1987 | 380.9951
2415.3479 | 429.6963 | 368.206 | 380.9915
2416.3479 | 429.7092 | 368.2048 | 380.9896
2417.3479 | 429.725 | 368.1942 | 380.9935
2418.3479 | 429.8288 | 368.1829 | 380.987
2419.3479 | 429.8387 | 368.1981 | 380.982
2420.3479 | 429.8708 | 368.1811 | 380.9813
2421.3479 | 429.9111 | 368.1804 | 380.9761
2422.3479 | 429.8551 | 368.1594 | 380.9685
2423.3479 | 429.776 | 368.1669 | 380.961
2424.3635 | 429.7683 | 368.1797 | 380.953
2425.3479 | 429.7394 | 368.1642 | 380.9529
2426.3635 | 429.6878 | 368.1677 | 380.9458
2427.3635 | 429.6939 | 368.1748 | 380.9417
2428.3635 | 429.6705 | 368.1791 | 380.9417
2429.3479 | 429.5559 | 368.1873 | 380.9415
2430.3635 | 429.4469 | 368.1728 | 380.9463
2431.3479 | 429.5019 | 368.1873 | 380.9401
2432.3635 | 429.4805 | 368.1683 | 380.9486
2433.3479 | 429.4393 | 368.174 | 380.9495
2434.3635 | 429.5094 | 368.1981 | 380.95
2435.3479 | 429.5429 | 368.1843 | 380.9562
2436.3635 | 429.5113 | 368.1959 | 380.9632
2437.3479 | 429.4809 | 368.1772 | 380.9627
2438.3635 | 429.4475 | 368.1735 | 380.9717
2439.3479 | 429.4225 | 368.1785 | 380.9615
2440.3635 | 429.4147 | 368.1578 | 380.9629
2441.3479 | 429.5128 | 368.1646 | 380.9675
2442.3635 | 429.4951 | 368.1529 | 380.9565
2443.3479 | 429.528 | 368.1441 | 380.9539
2444.3635 | 429.6474 | 368.1463 | 380.9546
2445.3479 | 429.6283 | 368.132 | 380.9498
2446.3479 | 429.6834 | 368.1381 | 380.9445
2447.3479 | 429.677 | 368.1285 | 380.9578
2448.3635 | 429.5735 | 368.1136 | 380.955
2449.3635 | 429.4795 | 368.1258 | 380.9535
2450.3635 | 429.5046 | 368.1048 | 380.9503
2451.3479 | 429.5945 | 368.107 | 380.9579
2452.3479 | 429.5209 | 368.0907 | 380.9681
2453.3635 | 429.4674 | 368.0873 | 380.9779
2454.3635 | 429.4875 | 368.0935 | 380.9886
2455.3635 | 429.4292 | 368.0734 | 380.9919
2456.3635 | 429.3947 | 368.0828 | 381.0045
2457.3635 | 429.4203 | 368.0638 | 381.0182
2458.3635 | 429.3285 | 368.0607 | 381.0343
2459.3635 | 429.3243 | 368.0569 | 381.038
2460.3635 | 429.2945 | 368.0436 | 381.0492
2461.3635 | 429.2823 | 368.0549 | 381.0552
2462.3635 | 429.2965 | 368.0393 | 381.059
2463.3635 | 429.2587 | 368.0412 | 381.0678
2464.3635 | 429.2044 | 368.0422 | 381.0617
2465.3635 | 429.2439 | 368.0366 | 381.0682
2466.3635 | 429.2426 | 368.0451 | 381.0657
2467.3635 | 429.3146 | 368.0281 | 381.0675
2468.3635 | 429.4573 | 368.0375 | 381.0615
2469.3635 | 429.4539 | 368.0252 | 381.0591
2470.3635 | 429.5227 | 368.0231 | 381.0723
2471.3635 | 429.5365 | 368.0435 | 381.0753
2472.3635 | 429.5878 | 368.034 | 381.0924
2473.3635 | 429.5991 | 368.0389 | 381.0976
2474.3635 | 429.5207 | 368.0428 | 381.1019
2475.3635 | 429.4945 | 368.0441 | 381.1066
2476.3635 | 429.5434 | 368.043 | 381.1098
2477.3635 | 429.6088 | 368.0296 | 381.1186
2478.3635 | 429.6557 | 368.0515 | 381.1155
2479.3635 | 429.6249 | 368.0537 | 381.1135
2480.3635 | 429.6848 | 368.0528 | 381.1081
2481.3635 | 429.6414 | 368.0365 | 381.1095
2482.3635 | 429.567 | 368.0558 | 381.1072
2483.3635 | 429.5568 | 368.0735 | 381.1137
2484.3635 | 429.5045 | 368.0587 | 381.1085
2485.3635 | 429.4827 | 368.0706 | 381.1129
2486.3635 | 429.4305 | 368.0816 | 381.117
2487.3635 | 429.3252 | 368.0764 | 381.1102
2488.3635 | 429.3261 | 368.0963 | 381.1176
2489.3635 | 429.3561 | 368.0766 | 381.1143
2490.3635 | 429.2889 | 368.0801 | 381.1194
2491.3635 | 429.2036 | 368.0911 | 381.127
2492.3635 | 429.1962 | 368.0953 | 381.1296
2493.3635 | 429.1791 | 368.0949 | 381.1261
2494.3635 | 429.1975 | 368.0762 | 381.1336
2495.3635 | 429.2155 | 368.0955 | 381.1363
2496.3635 | 429.2043 | 368.0791 | 381.1386
2497.3635 | 429.2517 | 368.076 | 381.141
2498.3635 | 429.2588 | 368.0847 | 381.1433
2499.3635 | 429.2595 | 368.0457 | 381.1535
2500.3635 | 429.2227 | 368.0756 | 381.1564
2501.3635 | 429.2179 | 368.059 | 381.1557
2502.3635 | 429.2767 | 368.0462 | 381.1531
2503.3635 | 429.1211 | 368.0637 | 381.1609
2504.3635 | 429.0138 | 368.0464 | 381.1572
2505.3635 | 429.0948 | 368.054 | 381.1571
2506.3635 | 429.0386 | 368.0395 | 381.1577
2507.3635 | 429.1087 | 368.0471 | 381.1628
2508.3635 | 429.2625 | 368.0472 | 381.1593
2509.3635 | 429.2593 | 368.0378 | 381.1597
2510.3635 | 429.2862 | 368.047 | 381.1643
2511.3635 | 429.3211 | 368.0388 | 381.164
2512.3635 | 429.418 | 368.0459 | 381.1639
2513.3635 | 429.5423 | 368.0397 | 381.151
2514.3635 | 429.5641 | 368.0362 | 381.1606
2515.3635 | 429.5274 | 368.0519 | 381.1568
2516.3635 | 429.4876 | 368.0486 | 381.1585
2517.3635 | 429.5523 | 368.0523 | 381.159
2518.3635 | 429.7666 | 368.0559 | 381.159
2519.3635 | 429.8446 | 368.0558 | 381.1604
2520.3635 | 429.8484 | 368.0687 | 381.1654
2521.3635 | 429.8945 | 368.0564 | 381.1676
2522.3635 | 429.922 | 368.0768 | 381.1712
2523.3635 | 429.8771 | 368.0761 | 381.184
2524.3635 | 429.7348 | 368.067 | 381.1915
2525.3635 | 429.5747 | 368.0927 | 381.1936
2526.3635 | 429.5143 | 368.0731 | 381.2004
2527.3479 | 429.3371 | 368.078 | 381.2028
2528.3635 | 429.319 | 368.0743 | 381.2095
2529.3635 | 429.2785 | 368.065 | 381.2114
2530.3479 | 429.3495 | 368.0847 | 381.2199
2531.3635 | 429.3249 | 368.0792 | 381.2221
2532.3635 | 429.3923 | 368.0913 | 381.2276
2533.3479 | 429.4229 | 368.0809 | 381.22
2534.3635 | 429.4712 | 368.0891 | 381.2231
2535.3635 | 429.3611 | 368.0971 | 381.2339
2536.3479 | 429.3467 | 368.0979 | 381.2262
2537.3635 | 429.3234 | 368.111 | 381.2235
2538.3635 | 429.287 | 368.102 | 381.2271
2539.3635 | 429.2417 | 368.125 | 381.2265
2540.3635 | 429.1529 | 368.1316 | 381.2268
2541.3635 | 429.0617 | 368.1368 | 381.2261
2542.3479 | 429.0589 | 368.147 | 381.2213
2543.3635 | 429.053 | 368.1328 | 381.2089
2544.3635 | 429.0987 | 368.1517 | 381.2074
2545.3479 | 428.9737 | 368.1527 | 381.1908
2546.3635 | 428.925 | 368.1475 | 381.1866
2547.3635 | 428.9143 | 368.1699 | 381.1769
2548.3479 | 428.9812 | 368.1536 | 381.1722
2549.3635 | 429.0705 | 368.172 | 381.1567
2550.3635 | 429.0894 | 368.1873 | 381.1471
2551.3479 | 429.0357 | 368.1864 | 381.1335
2552.3635 | 429.1157 | 368.1859 | 381.1185
2553.3635 | 429.2279 | 368.1801 | 381.1127
2554.3479 | 429.2642 | 368.2062 | 381.0991
2555.3635 | 429.2767 | 368.1935 | 381.0925
2556.3635 | 429.247 | 368.2022 | 381.0747
2557.3479 | 429.2893 | 368.2018 | 381.0659
2558.3635 | 429.3373 | 368.1925 | 381.0474
2559.3635 | 429.4627 | 368.1903 | 381.037
2560.3479 | 429.4244 | 368.1845 | 381.0244
2561.3635 | 429.4723 | 368.185 | 381.0204
2562.3479 | 429.3799 | 368.1848 | 381.0145
2563.3635 | 429.4464 | 368.1911 | 381.0154
2564.3635 | 429.4849 | 368.189 | 381.0096
2565.3635 | 429.4073 | 368.1821 | 381.0034
2566.3479 | 429.4003 | 368.1886 | 381.021
2567.3635 | 429.3186 | 368.178 | 381.0179
2568.3479 | 429.395 | 368.1755 | 381.0304
2569.3635 | 429.441 | 368.18 | 381.0316
2570.3479 | 429.3992 | 368.166 | 381.0548
2571.3635 | 429.3689 | 368.1836 | 381.0734
2572.3635 | 429.2994 | 368.162 | 381.0824
2573.3635 | 429.1496 | 368.171 | 381.1052
2574.3635 | 429.2057 | 368.1694 | 381.1166
2575.3635 | 429.231 | 368.1691 | 381.1296
2576.3635 | 429.2658 | 368.1898 | 381.1419
2577.3635 | 429.1786 | 368.1751 | 381.1591
2578.3479 | 429.0644 | 368.1845 | 381.1642
2579.3635 | 428.9713 | 368.1938 | 381.1748
2580.3635 | 428.9759 | 368.1958 | 381.1835
2581.3635 | 429.0338 | 368.2023 | 381.1807
2582.3635 | 429.0382 | 368.2006 | 381.1909
2583.3635 | 429.0563 | 368.2085 | 381.1988
2584.3635 | 429.0151 | 368.2206 | 381.1991
2585.3635 | 428.9279 | 368.2198 | 381.1983
2586.3635 | 428.8348 | 368.224 | 381.1932
2587.3635 | 428.6856 | 368.217 | 381.1836
2588.3635 | 428.6332 | 368.2433 | 381.1851
2589.3635 | 428.7385 | 368.2378 | 381.187
2590.3635 | 428.8067 | 368.2588 | 381.1813
2591.3635 | 428.928 | 368.2569 | 381.1695
2592.3635 | 428.9164 | 368.2613 | 381.1649
2593.3635 | 429.0064 | 368.2779 | 381.1625
2594.3635 | 428.9836 | 368.2585 | 381.1583
2595.3635 | 428.8936 | 368.2831 | 381.16
2596.3635 | 428.8931 | 368.2636 | 381.1591
2597.3635 | 428.9824 | 368.2689 | 381.1583
2598.3635 | 428.9636 | 368.2808 | 381.1629
2599.3635 | 428.8963 | 368.2667 | 381.1678
2600.3635 | 428.9101 | 368.2795 | 381.1689
2601.3635 | 429.0429 | 368.2674 | 381.1731
2602.3635 | 429.0235 | 368.2719 | 381.1872
2603.3635 | 429.1209 | 368.2791 | 381.1821
2604.3479 | 429.109 | 368.2696 | 381.1805
2605.3635 | 429.1643 | 368.2697 | 381.1819
2606.3635 | 429.1652 | 368.2497 | 381.1826
2607.3635 | 429.1905 | 368.2566 | 381.185
2608.3635 | 429.0807 | 368.2377 | 381.1801
2609.3635 | 429.0729 | 368.2276 | 381.183
2610.3635 | 429.01 | 368.2369 | 381.1801
2611.3635 | 429.1269 | 368.2251 | 381.1805
2612.3635 | 429.3025 | 368.2283 | 381.1808
2613.3635 | 429.4166 | 368.2174 | 381.174
2614.3635 | 429.4179 | 368.2294 | 381.1742
2615.3635 | 429.4903 | 368.2073 | 381.1806
2616.3635 | 429.5492 | 368.2113 | 381.1792
2617.3635 | 429.5988 | 368.2107 | 381.1804
2618.3635 | 429.6874 | 368.1973 | 381.175
2619.3635 | 429.5575 | 368.2087 | 381.1787
2620.3635 | 429.4487 | 368.2069 | 381.1836
2621.3635 | 429.3085 | 368.2024 | 381.1819
2622.3635 | 429.3497 | 368.202 | 381.1855
2623.3479 | 429.3354 | 368.2068 | 381.1913
2624.3635 | 429.2488 | 368.208 | 381.2019
2625.3635 | 429.3067 | 368.1997 | 381.2125
2626.3635 | 429.3408 | 368.2234 | 381.2251
2627.3635 | 429.3272 | 368.1966 | 381.2337
2628.3635 | 429.4049 | 368.2141 | 381.2446
2629.3635 | 429.4088 | 368.2104 | 381.2488
2630.3635 | 429.4755 | 368.1958 | 381.2519
2631.3635 | 429.4367 | 368.2023 | 381.2602
2632.3635 | 429.4729 | 368.1854 | 381.2581
2633.3635 | 429.5586 | 368.2037 | 381.2557
2634.3635 | 429.4927 | 368.1685 | 381.2573
2635.3635 | 429.5877 | 368.1931 | 381.2658
2636.3635 | 429.6225 | 368.1849 | 381.2648
2637.3635 | 429.7312 | 368.1717 | 381.2645
2638.3635 | 429.7978 | 368.1834 | 381.2681
2639.3635 | 429.8985 | 368.1613 | 381.2626
2640.3635 | 429.9952 | 368.1789 | 381.2709
2641.3635 | 430.1201 | 368.1495 | 381.2773
2642.3635 | 430.1561 | 368.162 | 381.2735
2643.3635 | 430.0641 | 368.1467 | 381.2693
2644.3635 | 430.0018 | 368.1543 | 381.2767
2645.3635 | 429.9283 | 368.1594 | 381.2752
2646.3635 | 429.8406 | 368.1497 | 381.268
2647.3635 | 429.7625 | 368.1642 | 381.2639
2648.3635 | 429.7092 | 368.154 | 381.2607
2649.3635 | 429.6859 | 368.1603 | 381.2639
2650.3635 | 429.7052 | 368.1613 | 381.2628
2651.3635 | 429.6979 | 368.1633 | 381.2573
2652.3635 | 429.6589 | 368.1776 | 381.2636
2653.3635 | 429.6097 | 368.1796 | 381.264
2654.3635 | 429.4654 | 368.2136 | 381.2704
2655.3635 | 429.292 | 368.194 | 381.2705
2656.3635 | 429.2318 | 368.2174 | 381.2791
2657.3635 | 429.1605 | 368.2279 | 381.2791
2658.3635 | 429.1937 | 368.2314 | 381.2806
2659.3635 | 429.2481 | 368.2526 | 381.2866
2660.3635 | 429.2888 | 368.2331 | 381.2852
2661.3635 | 429.1562 | 368.2612 | 381.2864
2662.3635 | 429.1005 | 368.2536 | 381.2864
2663.3635 | 429.0907 | 368.2633 | 381.2803
2664.3635 | 429.0232 | 368.2722 | 381.2729
2665.3635 | 429.0039 | 368.2701 | 381.2762
2666.3635 | 429.1106 | 368.2836 | 381.2681
2667.3635 | 429.115 | 368.2717 | 381.2629
2668.3635 | 429.0724 | 368.3023 | 381.2535
2669.3479 | 428.9767 | 368.2893 | 381.2453
2670.3635 | 428.9794 | 368.3002 | 381.2491
2671.3479 | 428.8933 | 368.297 | 381.2305
2672.3635 | 428.9154 | 368.2981 | 381.2192
2673.3479 | 429.0206 | 368.3174 | 381.2178
2674.3635 | 429.0692 | 368.2903 | 381.207
2675.3479 | 428.9814 | 368.3046 | 381.203
2676.3635 | 428.9223 | 368.2936 | 381.1963
2677.3479 | 428.9208 | 368.3047 | 381.1904
2678.3479 | 428.9497 | 368.2954 | 381.1875
2679.3479 | 429.0202 | 368.2863 | 381.1872
2680.3479 | 428.9971 | 368.3026 | 381.1863
2681.3479 | 429.0674 | 368.2783 | 381.1885
2682.3479 | 429.1678 | 368.3075 | 381.1961
2683.3479 | 429.145 | 368.3003 | 381.1933
2684.3479 | 429.1437 | 368.2926 | 381.196
2685.3635 | 429.0855 | 368.3016 | 381.1947
2686.3479 | 429.0868 | 368.2943 | 381.2027
2687.3635 | 429.1673 | 368.2994 | 381.2073
2688.3479 | 429.1792 | 368.2864 | 381.2055
2689.3635 | 429.2086 | 368.2965 | 381.2072
2690.3479 | 429.2596 | 368.2902 | 381.2129
2691.3635 | 429.3029 | 368.2822 | 381.2065
2692.3479 | 429.3299 | 368.3032 | 381.2105
2693.3635 | 429.3846 | 368.2884 | 381.2136
2694.3479 | 429.3148 | 368.3118 | 381.2069
2695.3635 | 429.2707 | 368.2926 | 381.213
2696.3479 | 429.2807 | 368.3015 | 381.2035
2697.3635 | 429.2913 | 368.303 | 381.2087
2698.3635 | 429.295 | 368.3038 | 381.2038
2699.3479 | 429.3647 | 368.3081 | 381.192
2700.3635 | 429.3905 | 368.2944 | 381.1949
2701.3479 | 429.4234 | 368.318 | 381.1763
2702.3635 | 429.3935 | 368.3061 | 381.161
2703.3479 | 429.404 | 368.324 | 381.1444
2704.3635 | 429.4607 | 368.3169 | 381.1241
2705.3479 | 429.4069 | 368.3162 | 381.106
2706.3479 | 429.4173 | 368.3318 | 381.0844
2707.3479 | 429.4745 | 368.3332 | 381.0677
2708.3479 | 429.4576 | 368.3443 | 381.0547
2709.3479 | 429.4139 | 368.3277 | 381.0404
2710.3479 | 429.3065 | 368.3441 | 381.0391
2711.3479 | 429.2524 | 368.3443 | 381.0352
2712.3479 | 429.2263 | 368.3411 | 381.0365
2713.3635 | 429.2884 | 368.3489 | 381.0495
2714.3479 | 429.3965 | 368.3289 | 381.0527
2715.3635 | 429.4516 | 368.3476 | 381.0607
2716.3479 | 429.4423 | 368.3237 | 381.0709
2717.3635 | 429.3367 | 368.3351 | 381.085
2718.3635 | 429.2122 | 368.3217 | 381.0988
2719.3635 | 429.179 | 368.3133 | 381.1145
2720.3479 | 429.1163 | 368.3225 | 381.133
2721.3479 | 429.1165 | 368.3146 | 381.1485
2722.3635 | 429.1819 | 368.3172 | 381.168
2723.3479 | 429.2134 | 368.3031 | 381.1838
2724.3635 | 429.3097 | 368.3 | 381.1936
2725.3479 | 429.3196 | 368.3023 | 381.2045
2726.3479 | 429.3666 | 368.2748 | 381.2145
2727.3635 | 429.2543 | 368.2903 | 381.2159
2728.3479 | 429.233 | 368.265 | 381.2199
2729.3479 | 429.1765 | 368.273 | 381.2215
2730.3479 | 429.0864 | 368.259 | 381.2263
2731.3479 | 429.1796 | 368.24 | 381.2301
2732.3479 | 429.2207 | 368.2445 | 381.2413
2733.3479 | 429.3229 | 368.2178 | 381.2457
2734.3479 | 429.3833 | 368.2297 | 381.2544
2735.3479 | 429.3872 | 368.2077 | 381.2554
2736.3635 | 429.3676 | 368.2048 | 381.2625
2737.3635 | 429.3008 | 368.1858 | 381.2684
2738.3635 | 429.3441 | 368.1745 | 381.2646
2739.3479 | 429.4132 | 368.1739 | 381.2745
2740.3479 | 429.4062 | 368.1634 | 381.2783
2741.3479 | 429.3823 | 368.1633 | 381.2788
2742.3635 | 429.4548 | 368.1507 | 381.2858
2743.3479 | 429.4104 | 368.1518 | 381.2909
2744.3479 | 429.4157 | 368.138 | 381.2964
2745.3479 | 429.4372 | 368.1627 | 381.3005
2746.3479 | 429.4136 | 368.159 | 381.3022
2747.3635 | 429.3988 | 368.1572 | 381.3038
2748.3635 | 429.4049 | 368.166 | 381.2996
2749.3479 | 429.3544 | 368.1536 | 381.3016
2750.3479 | 429.3404 | 368.1849 | 381.3033
2751.3479 | 429.373 | 368.1721 | 381.3069
2752.3635 | 429.3913 | 368.1763 | 381.3142
2753.3479 | 429.4505 | 368.1878 | 381.3271
2754.3479 | 429.4799 | 368.1995 | 381.336
2755.3479 | 429.4777 | 368.207 | 381.3533
2756.3479 | 429.5452 | 368.1948 | 381.3553
2757.3635 | 429.504 | 368.2164 | 381.3768
2758.3635 | 429.4631 | 368.221 | 381.391
2759.3479 | 429.4863 | 368.2372 | 381.4013
2760.3635 | 429.4794 | 368.245 | 381.4182
2761.3479 | 429.5118 | 368.2428 | 381.4242
2762.3635 | 429.529 | 368.2737 | 381.4387
2763.3635 | 429.5166 | 368.2681 | 381.4476
2764.3479 | 429.4647 | 368.2941 | 381.4524
2765.3479 | 429.4269 | 368.2947 | 381.4508
2766.3635 | 429.4258 | 368.3172 | 381.4495
2767.3479 | 429.4053 | 368.3215 | 381.4497
2768.3635 | 429.4196 | 368.3352 | 381.4431
2769.3479 | 429.4025 | 368.3458 | 381.4402
2770.3479 | 429.3794 | 368.345 | 381.4384
2771.3479 | 429.4038 | 368.3674 | 381.4284
2772.3635 | 429.3945 | 368.352 | 381.4121
2773.3479 | 429.3921 | 368.3846 | 381.4047
2774.3479 | 429.4709 | 368.3798 | 381.4082
2775.3479 | 429.4506 | 368.3756 | 381.4005
2776.3479 | 429.4872 | 368.3938 | 381.3969
2777.3479 | 429.4963 | 368.3832 | 381.402
2778.3479 | 429.5796 | 368.4085 | 381.3992
2779.3479 | 429.6147 | 368.393 | 381.4007
2780.3479 | 429.5477 | 368.4002 | 381.4027
2781.3635 | 429.4748 | 368.3998 | 381.3997
2782.3635 | 429.4885 | 368.398 | 381.4116
2783.3479 | 429.4363 | 368.4176 | 381.4182
2784.3479 | 429.4411 | 368.3805 | 381.4202
2785.3479 | 429.4205 | 368.4018 | 381.4283
2786.3479 | 429.3816 | 368.3976 | 381.4287
2787.3479 | 429.3647 | 368.4143 | 381.4371
2788.3479 | 429.3761 | 368.4021 | 381.4386
2789.3479 | 429.3439 | 368.4018 | 381.433
2790.3479 | 429.2812 | 368.4154 | 381.4391
2791.3635 | 429.3927 | 368.3934 | 381.4258
2792.3635 | 429.359 | 368.4058 | 381.423
2793.3479 | 429.4679 | 368.3947 | 381.4126
2794.3479 | 429.4828 | 368.4045 | 381.4061
2795.3479 | 429.3885 | 368.4081 | 381.4033
2796.3479 | 429.425 | 368.3872 | 381.4004
2797.3635 | 429.414 | 368.4079 | 381.3929
2798.3635 | 429.3224 | 368.3935 | 381.3857
2799.3635 | 429.3371 | 368.4114 | 381.3812
2800.3635 | 429.3318 | 368.393 | 381.379
2801.3635 | 429.342 | 368.3922 | 381.3761
2802.3635 | 429.2268 | 368.3961 | 381.3755
2803.3635 | 429.1375 | 368.3831 | 381.3727
2804.3479 | 429.0843 | 368.3888 | 381.3647
2805.3635 | 429.0365 | 368.3564 | 381.3585
2806.3948 | 428.9715 | 368.3689 | 381.3521
2807.3635 | 428.9881 | 368.3512 | 381.349
2808.3635 | 429.0471 | 368.3354 | 381.3384
2809.3635 | 429.0645 | 368.3309 | 381.3305
2810.3635 | 429.1091 | 368.312 | 381.307
2811.3635 | 429.0929 | 368.3212 | 381.3011
2812.3635 | 429.0909 | 368.2834 | 381.2978
2813.3635 | 429.0311 | 368.2851 | 381.2916
2814.3635 | 429.0689 | 368.2752 | 381.2928
2815.3635 | 429.3002 | 368.2675 | 381.2826
2816.3635 | 429.468 | 368.271 | 381.2809
2817.3635 | 429.5546 | 368.25 | 381.2745
2818.3635 | 429.5519 | 368.2612 | 381.2761
2819.3479 | 429.5523 | 368.2485 | 381.2866
2820.3635 | 429.5076 | 368.2672 | 381.2849
2821.3635 | 429.4874 | 368.2623 | 381.2909
2822.3479 | 429.5702 | 368.2606 | 381.3057
2823.3635 | 429.5543 | 368.2618 | 381.3037
2824.3479 | 429.4025 | 368.2593 | 381.3078
2825.3635 | 429.3238 | 368.2807 | 381.3151
2826.3635 | 429.3571 | 368.2645 | 381.3209
2827.3635 | 429.191 | 368.2807 | 381.3201
2828.3479 | 429.1867 | 368.2789 | 381.3276
2829.3635 | 429.2172 | 368.2729 | 381.3341
2830.3635 | 429.3049 | 368.2935 | 381.3394
2831.3635 | 429.3718 | 368.2923 | 381.3446
2832.3635 | 429.2792 | 368.2985 | 381.3426
2833.3635 | 429.2424 | 368.2932 | 381.3459
2834.3479 | 429.27 | 368.3131 | 381.35
2835.3635 | 429.2171 | 368.318 | 381.3503
2836.3635 | 429.203 | 368.31 | 381.3573
2837.3479 | 429.2627 | 368.3266 | 381.353
2838.3635 | 429.2354 | 368.3223 | 381.3591
2839.3635 | 429.1788 | 368.3462 | 381.3628
2840.3635 | 429.1148 | 368.3405 | 381.373
2841.3635 | 429.0122 | 368.3522 | 381.3726
2842.3635 | 428.9465 | 368.3454 | 381.3727
2843.3479 | 428.9811 | 368.3459 | 381.3713
2844.3635 | 428.8778 | 368.3654 | 381.3688
2845.3479 | 428.8889 | 368.3604 | 381.3715
2846.3635 | 428.9202 | 368.3791 | 381.3737
2847.3635 | 428.9061 | 368.3675 | 381.3827
2848.3635 | 428.7959 | 368.3793 | 381.3807
2849.3635 | 428.8171 | 368.3872 | 381.3834
2850.3635 | 428.9639 | 368.3669 | 381.3916
2851.3635 | 429.0369 | 368.3972 | 381.3999
2852.3635 | 429.0606 | 368.3897 | 381.4039
2853.3635 | 429.0657 | 368.3947 | 381.4131
2854.3479 | 429.1632 | 368.3976 | 381.4214
2855.3635 | 429.1215 | 368.4096 | 381.4263
2856.3635 | 429.0756 | 368.4129 | 381.4301
2857.3635 | 429.1145 | 368.4178 | 381.4313
2858.3635 | 429.1154 | 368.4219 | 381.4316
2859.3635 | 429.0268 | 368.4237 | 381.4332
2860.3635 | 429.0965 | 368.4436 | 381.4247
2861.3635 | 429.1755 | 368.4392 | 381.4205
2862.3635 | 429.1607 | 368.4416 | 381.4159
2863.3635 | 429.1857 | 368.4576 | 381.403
2864.3635 | 429.1573 | 368.4489 | 381.4059
2865.3635 | 429.1748 | 368.4532 | 381.4023
2866.3635 | 429.1835 | 368.4556 | 381.4081
2867.3635 | 429.1817 | 368.4697 | 381.4075
2868.3635 | 429.1371 | 368.4722 | 381.4031
2869.3635 | 429.1985 | 368.4645 | 381.4134
2870.3635 | 429.1842 | 368.4639 | 381.4091
2871.3635 | 429.243 | 368.4625 | 381.4018
2872.3635 | 429.2294 | 368.4756 | 381.4016
2873.3635 | 429.2666 | 368.4735 | 381.387
2874.3635 | 429.2575 | 368.4679 | 381.3864
2875.3635 | 429.2401 | 368.4725 | 381.3781
2876.3635 | 429.276 | 368.4645 | 381.3732
2877.3479 | 429.1928 | 368.4861 | 381.3565
2878.3635 | 429.1441 | 368.4775 | 381.3616
2879.3479 | 429.1079 | 368.487 | 381.3576
2880.3635 | 429.1141 | 368.4698 | 381.3565
2881.3479 | 429.2113 | 368.4657 | 381.3565
2882.3635 | 429.2315 | 368.4685 | 381.365
2883.3479 | 429.1932 | 368.4641 | 381.3662
2884.3635 | 429.2122 | 368.4788 | 381.371
2885.3479 | 429.2342 | 368.4391 | 381.3746
2886.3635 | 429.233 | 368.4619 | 381.3761
2887.3635 | 429.3922 | 368.438 | 381.3797
2888.3479 | 429.4883 | 368.4271 | 381.3914
2889.3635 | 429.5792 | 368.4332 | 381.3936
2890.3479 | 429.5345 | 368.4055 | 381.3991
2891.3635 | 429.5128 | 368.4115 | 381.3971
2892.3479 | 429.5098 | 368.3855 | 381.4027
2893.3635 | 429.5294 | 368.3875 | 381.4147
2894.3479 | 429.5404 | 368.3657 | 381.4185
2895.3635 | 429.5191 | 368.3621 | 381.4247
2896.3479 | 429.6273 | 368.3619 | 381.4338
2897.3635 | 429.6658 | 368.3422 | 381.4377
2898.3479 | 429.7256 | 368.3536 | 381.4398
2899.3635 | 429.7828 | 368.3287 | 381.4442
2900.3479 | 429.7537 | 368.348 | 381.4381
2901.3635 | 429.6572 | 368.3329 | 381.435
2902.3479 | 429.6597 | 368.3378 | 381.4306
2903.3635 | 429.6434 | 368.342 | 381.4302
2904.3635 | 429.6321 | 368.322 | 381.4227
2905.3479 | 429.6225 | 368.34 | 381.423
2906.3635 | 429.5642 | 368.3165 | 381.4202
2907.3479 | 429.4627 | 368.3445 | 381.4177
2908.3635 | 429.4589 | 368.3221 | 381.4136
2909.3479 | 429.4305 | 368.3279 | 381.4185
2910.3635 | 429.3957 | 368.3299 | 381.4129
2911.3479 | 429.4312 | 368.3102 | 381.4019
2912.3635 | 429.4132 | 368.3286 | 381.3962
2913.3635 | 429.469 | 368.3097 | 381.3978
2914.3635 | 429.5641 | 368.3237 | 381.3923
2915.3479 | 429.5519 | 368.3138 | 381.3919
2916.3635 | 429.5683 | 368.3208 | 381.383
2917.3479 | 429.6212 | 368.3042 | 381.3898
2918.3635 | 429.5861 | 368.3067 | 381.3926
2919.3635 | 429.552 | 368.321 | 381.3927
2920.3635 | 429.604 | 368.2988 | 381.3921
2921.3635 | 429.5845 | 368.3147 | 381.3989
2922.3635 | 429.5962 | 368.2979 | 381.3919
2923.3635 | 429.5272 | 368.3179 | 381.4005
2924.3635 | 429.535 | 368.3091 | 381.3971
2925.3635 | 429.6385 | 368.304 | 381.4044
2926.3635 | 429.6439 | 368.3279 | 381.4046
2927.3635 | 429.7469 | 368.3064 | 381.4008
2928.3635 | 429.8142 | 368.3302 | 381.4035
2929.3635 | 429.7657 | 368.3264 | 381.3913
2930.3635 | 429.6828 | 368.3182 | 381.3843
2931.3635 | 429.6934 | 368.3262 | 381.3757
2932.3635 | 429.7897 | 368.3244 | 381.3676
2933.3635 | 429.8226 | 368.3247 | 381.3622
2934.3635 | 429.8781 | 368.3254 | 381.35
2935.3635 | 429.9026 | 368.3425 | 381.343
2936.3635 | 429.8502 | 368.3348 | 381.3342
2937.3635 | 429.7789 | 368.3268 | 381.3246
2938.3635 | 429.8304 | 368.3503 | 381.3091
2939.3635 | 429.7925 | 368.3285 | 381.3053
2940.3635 | 429.8207 | 368.3496 | 381.3019
2941.3635 | 429.9273 | 368.3555 | 381.2982
2942.3635 | 430.0076 | 368.3586 | 381.2943
2943.3635 | 429.8774 | 368.373 | 381.2876
2944.3635 | 429.7571 | 368.3692 | 381.2874
2945.3635 | 429.7285 | 368.3888 | 381.2862
2946.3635 | 429.7276 | 368.3708 | 381.3012
2947.3635 | 429.8396 | 368.398 | 381.3048
2948.3635 | 429.8264 | 368.3992 | 381.3104
2949.3635 | 429.9133 | 368.4005 | 381.3139
2950.3635 | 430.0507 | 368.4165 | 381.3215
2951.3635 | 430.0869 | 368.4154 | 381.3256
2952.3635 | 430.0963 | 368.4454 | 381.3345
2953.3635 | 430.0257 | 368.4389 | 381.34
2954.3635 | 430.0769 | 368.445 | 381.3528
2955.3635 | 430.0824 | 368.4677 | 381.3529
2956.3635 | 430.0361 | 368.4543 | 381.3626
2957.3635 | 430.0356 | 368.463 | 381.3736
2958.3635 | 430.0296 | 368.4729 | 381.3784
2959.3635 | 429.9223 | 368.4861 | 381.3828
2960.3635 | 429.9454 | 368.4887 | 381.3863
2961.3479 | 429.8929 | 368.4882 | 381.3897
2962.3635 | 429.709 | 368.4942 | 381.3963
2963.3635 | 429.6575 | 368.4934 | 381.4028
2964.3635 | 429.6783 | 368.5097 | 381.4158
2965.3635 | 429.6948 | 368.5097 | 381.4183
2966.3635 | 429.5832 | 368.5205 | 381.423
2967.3635 | 429.545 | 368.4995 | 381.4238
2968.3635 | 429.5926 | 368.5129 | 381.4293
2969.3635 | 429.7024 | 368.5104 | 381.4347
2970.3635 | 429.7044 | 368.4894 | 381.4418
2971.3635 | 429.5954 | 368.5051 | 381.4432
2972.3635 | 429.6711 | 368.4917 | 381.4427
2973.3635 | 429.7222 | 368.5063 | 381.4426
2974.3635 | 429.7043 | 368.4904 | 381.442
2975.3635 | 429.6405 | 368.4789 | 381.4443
2976.3635 | 429.6322 | 368.4935 | 381.4471
2977.3635 | 429.653 | 368.4838 | 381.4484
2978.3635 | 429.6931 | 368.4993 | 381.4558
2979.3635 | 429.675 | 368.4754 | 381.4512
2980.3635 | 429.6209 | 368.4769 | 381.4457
2981.3635 | 429.6241 | 368.4745 | 381.4533
2982.3635 | 429.5166 | 368.4742 | 381.4535
2983.3635 | 429.4592 | 368.4744 | 381.4604
2984.3635 | 429.472 | 368.4737 | 381.4658
2985.3635 | 429.4397 | 368.4775 | 381.4635
2986.3635 | 429.4803 | 368.4719 | 381.4672
2987.3635 | 429.3844 | 368.4743 | 381.4762
2988.3635 | 429.2712 | 368.469 | 381.4789
2989.3635 | 429.1624 | 368.4527 | 381.48
2990.3635 | 429.2179 | 368.4601 | 381.4872
2991.3635 | 429.2362 | 368.4446 | 381.4887
2992.3635 | 429.1668 | 368.4476 | 381.4921
2993.3635 | 429.2693 | 368.4376 | 381.4917
2994.3635 | 429.4085 | 368.4337 | 381.5002
2995.3635 | 429.4605 | 368.4316 | 381.4972
2996.3635 | 429.4842 | 368.4266 | 381.4965
2997.3635 | 429.4037 | 368.4221 | 381.4994
2998.3635 | 429.439 | 368.4084 | 381.5043
2999.3635 | 429.5713 | 368.4079 | 381.5042
3000.3635 | 429.639 | 368.4086 | 381.5108
3001.3635 | 429.598 | 368.4047 | 381.5189
3002.3635 | 429.5501 | 368.4075 | 381.5213
3003.3635 | 429.5859 | 368.3976 | 381.5275
3004.3635 | 429.4931 | 368.4047 | 381.5309
3005.3635 | 429.4228 | 368.4052 | 381.533
3006.3635 | 429.5153 | 368.4094 | 381.5397
3007.3635 | 429.4509 | 368.4078 | 381.5414
3008.3635 | 429.4271 | 368.4027 | 381.5294
3009.3635 | 429.3817 | 368.4074 | 381.532
3010.3635 | 429.3624 | 368.3999 | 381.5331
3011.3635 | 429.3956 | 368.4128 | 381.5308
3012.3635 | 429.4755 | 368.393 | 381.5217
3013.3635 | 429.4621 | 368.4054 | 381.518
3014.3635 | 429.3482 | 368.4024 | 381.5119
3015.3635 | 429.2731 | 368.393 | 381.5061
3016.3635 | 429.2844 | 368.3906 | 381.5062
3017.3635 | 429.3824 | 368.38 | 381.52
3018.3635 | 429.4626 | 368.3845 | 381.5212
3019.3635 | 429.4405 | 368.3671 | 381.5152
3020.3635 | 429.238 | 368.3653 | 381.521
3021.3635 | 429.155 | 368.364 | 381.5193
3022.3479 | 429.2209 | 368.3579 | 381.5161
3023.3635 | 429.3253 | 368.3702 | 381.5187
3024.3635 | 429.3123 | 368.347 | 381.5146
3025.3635 | 429.1996 | 368.369 | 381.5202
3026.3479 | 429.2684 | 368.3407 | 381.5099
3027.3635 | 429.2407 | 368.3463 | 381.5036
3028.3635 | 429.2216 | 368.332 | 381.5028
3029.3635 | 429.2561 | 368.325 | 381.4976
3030.3635 | 429.3196 | 368.3359 | 381.4898
3031.3635 | 429.3801 | 368.3192 | 381.4832
3032.3479 | 429.3878 | 368.3349 | 381.4774
3033.3635 | 429.4009 | 368.3047 | 381.478
3034.3635 | 429.3965 | 368.293 | 381.4667
3035.3635 | 429.3135 | 368.307 | 381.4748
3036.3635 | 429.4066 | 368.3004 | 381.4681
3037.3635 | 429.418 | 368.3107 | 381.4761
3038.3479 | 429.3519 | 368.297 | 381.471
3039.3635 | 429.3701 | 368.3073 | 381.4694
3040.3635 | 429.3766 | 368.2955 | 381.4593
3041.3635 | 429.3996 | 368.2934 | 381.4581
3042.3635 | 429.4339 | 368.2883 | 381.4541
3043.3635 | 429.4415 | 368.2913 | 381.4454
3044.3479 | 429.387 | 368.289 | 381.4512
3045.3635 | 429.3638 | 368.2841 | 381.4375
3046.3635 | 429.3549 | 368.287 | 381.4261
3047.3479 | 429.2512 | 368.2734 | 381.4195
3048.3635 | 429.2856 | 368.2814 | 381.4106
3049.3635 | 429.148 | 368.2862 | 381.4146
3050.3635 | 429.1771 | 368.2799 | 381.4038
3051.3479 | 429.1562 | 368.2798 | 381.396
3052.3635 | 429.1525 | 368.2654 | 381.4021
3053.3479 | 429.096 | 368.2897 | 381.403
3054.3635 | 429.1485 | 368.2716 | 381.4026
3055.3479 | 429.1122 | 368.2918 | 381.4073
3056.3635 | 429.0902 | 368.2943 | 381.4132
3057.3479 | 429.1888 | 368.2723 | 381.4196
3058.3635 | 429.037 | 368.2926 | 381.4192
3059.3479 | 429.0303 | 368.2857 | 381.4159
3060.3479 | 428.9511 | 368.2894 | 381.4177
3061.3479 | 428.9129 | 368.2821 | 381.42
3062.3479 | 428.9549 | 368.2861 | 381.4161
3063.3479 | 428.9653 | 368.2748 | 381.4135
3064.3479 | 429.0683 | 368.2732 | 381.4128
3065.3479 | 429.0159 | 368.2663 | 381.4121
3066.3479 | 429.0137 | 368.2734 | 381.4096
3067.3479 | 428.9607 | 368.2941 | 381.3992
3068.3479 | 429.1391 | 368.2822 | 381.3918
3069.3479 | 429.1843 | 368.2984 | 381.3978
3070.3479 | 429.0849 | 368.2951 | 381.3907
3071.3479 | 429.1178 | 368.2966 | 381.3958
3072.3479 | 429.0868 | 368.3021 | 381.3893
3073.3479 | 429.1319 | 368.2923 | 381.4023
3074.3479 | 429.1648 | 368.3098 | 381.3924
3075.3479 | 429.2001 | 368.2929 | 381.3951
3076.3479 | 429.1526 | 368.2999 | 381.3986
3077.3479 | 429.0548 | 368.2939 | 381.4004
3078.3479 | 429.0165 | 368.3042 | 381.3945
3079.3479 | 428.9908 | 368.2995 | 381.3949
3080.3479 | 429.0116 | 368.2927 | 381.3983
3081.3479 | 429.129 | 368.3061 | 381.4015
3082.3479 | 429.229 | 368.3069 | 381.4047
3083.3479 | 429.2653 | 368.3222 | 381.4105
3084.3479 | 429.3113 | 368.3393 | 381.4056
3085.3479 | 429.298 | 368.335 | 381.4054
3086.3635 | 429.3274 | 368.3507 | 381.4063
3087.3479 | 429.2918 | 368.3423 | 381.3999
3088.3479 | 429.23 | 368.3646 | 381.3918
3089.3635 | 429.2968 | 368.3539 | 381.392
3090.3479 | 429.2505 | 368.3537 | 381.3839
3091.3635 | 429.2794 | 368.3593 | 381.3773
3092.3479 | 429.3225 | 368.3613 | 381.3627
3093.3479 | 429.3365 | 368.3794 | 381.3572
3094.3479 | 429.3308 | 368.3694 | 381.3551
3095.3479 | 429.3324 | 368.3823 | 381.3458
3096.3479 | 429.2584 | 368.3778 | 381.3411
3097.3479 | 429.3214 | 368.3976 | 381.3432
3098.3635 | 429.3321 | 368.3818 | 381.3394
3099.3479 | 429.2507 | 368.3915 | 381.3324
3100.3479 | 429.2267 | 368.3979 | 381.3278
3101.3635 | 429.3159 | 368.3845 | 381.336
3102.3635 | 429.4068 | 368.4012 | 381.3255
3103.3479 | 429.3355 | 368.3911 | 381.3201
3104.3479 | 429.3972 | 368.3961 | 381.3308
3105.3479 | 429.3728 | 368.3884 | 381.3313
3106.3635 | 429.3719 | 368.3871 | 381.3368
3107.3635 | 429.4084 | 368.3753 | 381.3442
3108.3479 | 429.426 | 368.3769 | 381.3608
3109.3479 | 429.3641 | 368.3918 | 381.3623
3110.3479 | 429.3712 | 368.3663 | 381.3659
3111.3635 | 429.3802 | 368.3617 | 381.3844
3112.3479 | 429.3745 | 368.363 | 381.3974
3113.3479 | 429.3825 | 368.3513 | 381.4087
3114.3479 | 429.3211 | 368.3436 | 381.4301
3115.3479 | 429.2414 | 368.321 | 381.4422
3116.3479 | 429.2714 | 368.3505 | 381.4469
3117.3479 | 429.3152 | 368.3151 | 381.4564
3118.3479 | 429.3434 | 368.3384 | 381.4697
3119.3479 | 429.2647 | 368.3295 | 381.4672
3120.3479 | 429.2754 | 368.3037 | 381.4808
3121.3479 | 429.3936 | 368.3255 | 381.4816
3122.3479 | 429.3634 | 368.3089 | 381.4901
3123.3479 | 429.4105 | 368.3192 | 381.4927
3124.3479 | 429.4967 | 368.3073 | 381.4989
3125.3479 | 429.4685 | 368.299 | 381.5074
3126.3635 | 429.2462 | 368.2985 | 381.5133
3127.3479 | 429.176 | 368.2857 | 381.5193
3128.3479 | 429.1946 | 368.3046 | 381.5178
3129.3479 | 429.1437 | 368.2817 | 381.5176
3130.3635 | 429.0581 | 368.2888 | 381.5278
3131.3479 | 429.0267 | 368.2579 | 381.5219
3132.3635 | 429.0931 | 368.2704 | 381.5263
3133.3479 | 429.0761 | 368.2692 | 381.5298
3134.3635 | 428.9936 | 368.2602 | 381.5295
3135.3479 | 428.996 | 368.2671 | 381.5298
3136.3635 | 429.1176 | 368.2452 | 381.5317
3137.3479 | 429.0298 | 368.2526 | 381.528
3138.3635 | 428.9969 | 368.2337 | 381.5247
3139.3635 | 429.0374 | 368.2245 | 381.5217
3140.3479 | 429.0081 | 368.238 | 381.5243
3141.3479 | 428.9893 | 368.2151 | 381.5193
3142.3479 | 428.902 | 368.2321 | 381.5173
3143.3479 | 428.9094 | 368.2081 | 381.5225
3144.3479 | 428.9359 | 368.2212 | 381.5231
3145.3635 | 428.9324 | 368.2163 | 381.5303
3146.3479 | 428.9841 | 368.2026 | 381.5273
3147.3635 | 429.0364 | 368.2077 | 381.5346
3148.3479 | 429.1439 | 368.1873 | 381.5349
3149.3635 | 429.2726 | 368.2028 | 381.5277
3150.3479 | 429.3204 | 368.1805 | 381.5279
3151.3635 | 429.1779 | 368.1739 | 381.5308
3152.3479 | 429.1413 | 368.1714 | 381.5288
3153.3635 | 429.0566 | 368.1636 | 381.5291
3154.3479 | 429.1857 | 368.1715 | 381.5354
3155.3635 | 429.2681 | 368.1464 | 381.5272
3156.3479 | 429.2944 | 368.1661 | 381.5277
3157.3479 | 429.2109 | 368.145 | 381.5326
3158.3479 | 429.1891 | 368.1408 | 381.5304
3159.3479 | 429.2744 | 368.1393 | 381.5321
3160.3479 | 429.2858 | 368.1308 | 381.5336
3161.3479 | 429.4349 | 368.1544 | 381.5324
3162.3479 | 429.4673 | 368.1351 | 381.5335
3163.3479 | 429.3653 | 368.1519 | 381.5365
3164.3479 | 429.5007 | 368.1477 | 381.5323
3165.3479 | 429.5406 | 368.142 | 381.5354
3166.3635 | 429.5759 | 368.1602 | 381.5352
3167.3635 | 429.5842 | 368.1485 | 381.5335
3168.3479 | 429.5085 | 368.1747 | 381.5368
3169.3635 | 429.4679 | 368.1619 | 381.5363
3170.3479 | 429.5397 | 368.1835 | 381.5443
3171.3635 | 429.6248 | 368.1833 | 381.5422
3172.3479 | 429.592 | 368.1876 | 381.5413
3173.3635 | 429.6311 | 368.2132 | 381.5376
3174.3479 | 429.6453 | 368.2 | 381.543
3175.3635 | 429.712 | 368.2324 | 381.5436
3176.3479 | 429.7266 | 368.2144 | 381.542
3177.3635 | 429.6623 | 368.2504 | 381.5373
3178.3635 | 429.5848 | 368.2396 | 381.5359
3179.3635 | 429.5331 | 368.2635 | 381.5396
3180.3479 | 429.619 | 368.2817 | 381.5385
3181.3635 | 429.6739 | 368.2698 | 381.5501
3182.3479 | 429.7222 | 368.2843 | 381.5503
3183.3635 | 429.6981 | 368.2835 | 381.5611
3184.3479 | 429.6686 | 368.3082 | 381.5629
3185.3479 | 429.6566 | 368.2912 | 381.5663
3186.3479 | 429.61 | 368.2949 | 381.5726
3187.3479 | 429.6296 | 368.3171 | 381.5668
3188.3635 | 429.6413 | 368.2899 | 381.5557
3189.3635 | 429.7634 | 368.3247 | 381.5444
3190.3479 | 429.8749 | 368.315 | 381.5413
3191.3479 | 429.8502 | 368.3201 | 381.5273
3192.3479 | 429.9177 | 368.3218 | 381.5127
3193.3479 | 429.8773 | 368.3205 | 381.5091
3194.3479 | 429.7832 | 368.3304 | 381.5032
3195.3635 | 429.7537 | 368.3194 | 381.5019
3196.3479 | 429.734 | 368.3398 | 381.4954
3197.3635 | 429.6741 | 368.3357 | 381.4888
3198.3479 | 429.5919 | 368.3197 | 381.4883
3199.3635 | 429.5923 | 368.3377 | 381.4905
3200.3479 | 429.6847 | 368.3307 | 381.4894
3201.3479 | 429.7325 | 368.3437 | 381.4941
3202.3479 | 429.8412 | 368.3387 | 381.4988
3203.3635 | 429.7712 | 368.355 | 381.5026
3204.3635 | 429.7429 | 368.3374 | 381.5081
3205.3479 | 429.829 | 368.3434 | 381.5232
3206.3479 | 429.7741 | 368.3393 | 381.5148
3207.3479 | 429.7443 | 368.3473 | 381.5174
3208.3635 | 429.7816 | 368.3573 | 381.5181
3209.3635 | 429.8056 | 368.3532 | 381.5237
3210.3479 | 429.8112 | 368.3681 | 381.5311
3211.3635 | 429.8282 | 368.364 | 381.5258
3212.3479 | 429.7718 | 368.3744 | 381.5283
3213.3479 | 429.7961 | 368.3896 | 381.5254
3214.3479 | 429.8168 | 368.3785 | 381.5247
3215.3479 | 429.8824 | 368.4044 | 381.5297
3216.3479 | 429.9217 | 368.3965 | 381.5354
3217.3479 | 430.042 | 368.4069 | 381.5379
3218.3479 | 430.0518 | 368.4058 | 381.5472
3219.3479 | 429.9714 | 368.4108 | 381.5517
3220.3479 | 429.9099 | 368.4154 | 381.5575
3221.3479 | 429.8433 | 368.4076 | 381.5669
3222.3479 | 429.8306 | 368.4179 | 381.5633
3223.3479 | 429.8113 | 368.4313 | 381.5656
3224.3479 | 429.8205 | 368.4248 | 381.5702
3225.3635 | 429.8687 | 368.4307 | 381.566
3226.3635 | 429.8721 | 368.4135 | 381.5719
3227.3635 | 429.8434 | 368.4373 | 381.5753
3228.3635 | 429.976 | 368.4163 | 381.5821
3229.3635 | 430.0366 | 368.4167 | 381.5904
3230.3635 | 430.0255 | 368.4249 | 381.5954
3231.3635 | 430.0617 | 368.4181 | 381.5993
3232.3635 | 429.9709 | 368.4382 | 381.6021
3233.3635 | 429.9307 | 368.4291 | 381.6074
3234.3479 | 429.9486 | 368.4449 | 381.6145
3235.3635 | 429.9313 | 368.4296 | 381.6063
3236.3635 | 429.8218 | 368.4297 | 381.6182
3237.3635 | 429.8272 | 368.4465 | 381.6189
3238.3635 | 429.913 | 368.4332 | 381.6228
3239.3635 | 429.9463 | 368.4428 | 381.6236
3240.3635 | 429.8865 | 368.4283 | 381.6281
3241.3635 | 429.8529 | 368.4438 | 381.6304
3242.3635 | 429.8474 | 368.4384 | 381.6285
3243.3635 | 429.8821 | 368.4452 | 381.6289
3244.3635 | 429.9665 | 368.4355 | 381.6301
3245.3635 | 430.0019 | 368.438 | 381.6204
3246.3635 | 429.9394 | 368.4587 | 381.6131
3247.3635 | 429.8432 | 368.4244 | 381.6043
3248.3635 | 429.7712 | 368.4419 | 381.5914
3249.3635 | 429.8185 | 368.4266 | 381.5782
3250.3635 | 429.8353 | 368.4357 | 381.5688
3251.3635 | 429.7248 | 368.4383 | 381.5601
3252.3635 | 429.6572 | 368.4176 | 381.552
3253.3635 | 429.6638 | 368.4441 | 381.5467
3254.3635 | 429.5734 | 368.4344 | 381.544
3255.3635 | 429.6003 | 368.4351 | 381.5381
3256.3635 | 429.6347 | 368.4236 | 381.5339
3257.3635 | 429.6848 | 368.4258 | 381.5265
3258.3635 | 429.7865 | 368.4332 | 381.5265
3259.3635 | 429.7854 | 368.4277 | 381.5216
3260.3635 | 429.8005 | 368.4475 | 381.5208
3261.3635 | 429.7481 | 368.4432 | 381.5098
3262.3635 | 429.7107 | 368.4431 | 381.5051
3263.3635 | 429.7304 | 368.4529 | 381.4965
3264.3635 | 429.6908 | 368.4499 | 381.4967
3265.3635 | 429.7037 | 368.469 | 381.4994
3266.3635 | 429.6257 | 368.4577 | 381.4984
3267.3479 | 429.5581 | 368.4778 | 381.5085
3268.3635 | 429.5202 | 368.4735 | 381.5085
3269.3635 | 429.5594 | 368.4739 | 381.5206
3270.3635 | 429.6122 | 368.4933 | 381.5273
3271.3479 | 429.7331 | 368.4809 | 381.5339
3272.3635 | 429.8202 | 368.5038 | 381.5412
3273.3635 | 429.8801 | 368.4978 | 381.549
3274.3635 | 429.8053 | 368.5069 | 381.5647
3275.3635 | 429.7091 | 368.506 | 381.5769
3276.3635 | 429.6818 | 368.5134 | 381.5936
3277.3635 | 429.6264 | 368.5188 | 381.6015
3278.3635 | 429.5474 | 368.5128 | 381.6205
3279.3635 | 429.531 | 368.5508 | 381.6323
3280.3635 | 429.4157 | 368.5367 | 381.633
3281.3635 | 429.3072 | 368.5443 | 381.6408
3282.3635 | 429.2974 | 368.5464 | 381.6401
3283.3635 | 429.2548 | 368.5428 | 381.6397
3284.3635 | 429.2841 | 368.5594 | 381.6398
3285.3635 | 429.2935 | 368.54 | 381.6326
3286.3635 | 429.2372 | 368.5627 | 381.6361
3287.3635 | 429.1701 | 368.5474 | 381.6296
3288.3635 | 429.0946 | 368.5465 | 381.6305
3289.3635 | 429.1585 | 368.5547 | 381.631
3290.3635 | 429.0211 | 368.5378 | 381.6329
3291.3635 | 428.9114 | 368.5594 | 381.639
3292.3635 | 428.9709 | 368.5439 | 381.6451
3293.3635 | 429.0641 | 368.5565 | 381.6544
3294.3635 | 429.0278 | 368.5425 | 381.6587
3295.3635 | 429.0975 | 368.5531 | 381.6597
3296.3635 | 429.1112 | 368.5457 | 381.6694
3297.3635 | 429.1645 | 368.5504 | 381.6714
3298.3635 | 429.1924 | 368.5561 | 381.6754
3299.3635 | 429.236 | 368.5341 | 381.68
3300.3635 | 429.2266 | 368.5582 | 381.6832
3301.3635 | 429.2229 | 368.5453 | 381.6785
3302.3635 | 429.1896 | 368.5517 | 381.684
3303.3635 | 429.1717 | 368.5705 | 381.6892
3304.3635 | 429.2359 | 368.5502 | 381.694
3305.3635 | 429.2685 | 368.5758 | 381.6992
3306.3635 | 429.3238 | 368.5561 | 381.7068
3307.3479 | 429.2695 | 368.5983 | 381.7235
3308.3635 | 429.1791 | 368.6031 | 381.7292
3309.3635 | 429.2005 | 368.6147 | 381.7278
3310.3635 | 429.291 | 368.629 | 381.7384
3311.3635 | 429.1973 | 368.6105 | 381.7382
3312.3635 | 429.1237 | 368.6535 | 381.7392
3313.3635 | 429.033 | 368.6408 | 381.7421
3314.3635 | 428.9848 | 368.6624 | 381.7405
3315.3635 | 429.0136 | 368.6506 | 381.7376
3316.3635 | 428.975 | 368.6614 | 381.7339
3317.3635 | 429.0993 | 368.6598 | 381.7262
3318.3635 | 429.305 | 368.6452 | 381.7236
3319.3635 | 429.4035 | 368.6648 | 381.7171
3320.3635 | 429.4264 | 368.6623 | 381.7178
3321.3635 | 429.4851 | 368.6801 | 381.714
3322.3635 | 429.4853 | 368.6724 | 381.7167
3323.3635 | 429.5862 | 368.6715 | 381.7123
3324.3635 | 429.6373 | 368.6821 | 381.7178
3325.3635 | 429.6437 | 368.668 | 381.713
3326.3635 | 429.7727 | 368.6793 | 381.7111
3327.3635 | 429.8371 | 368.6626 | 381.7121
3328.3635 | 429.8851 | 368.6861 | 381.718
3329.3635 | 430.0023 | 368.672 | 381.7213
3330.3635 | 430.0234 | 368.6796 | 381.7167
3331.3635 | 429.9066 | 368.6836 | 381.7184
3332.3635 | 429.9427 | 368.6756 | 381.7095
3333.3635 | 430.0031 | 368.6857 | 381.699
3334.3635 | 429.9332 | 368.6824 | 381.6938
3335.3635 | 429.7988 | 368.7038 | 381.6925
3336.3635 | 429.5968 | 368.6924 | 381.6895
3337.3635 | 429.5814 | 368.7017 | 381.6885
3338.3635 | 429.6036 | 368.7097 | 381.6828
3339.3635 | 429.548 | 368.6942 | 381.6802
3340.3635 | 429.5586 | 368.6965 | 381.6839
3341.3635 | 429.612 | 368.6837 | 381.68
3342.3635 | 429.5246 | 368.7096 | 381.6732
3343.3635 | 429.461 | 368.6959 | 381.6797
3344.3635 | 429.4204 | 368.7065 | 381.6769
3345.3635 | 429.3549 | 368.701 | 381.677
3346.3635 | 429.3101 | 368.6936 | 381.6697
3347.3635 | 429.3661 | 368.7 | 381.6679
3348.3635 | 429.3101 | 368.6897 | 381.6642
3349.3635 | 429.2851 | 368.7097 | 381.6568
3350.3635 | 429.2314 | 368.6918 | 381.6532
3351.3635 | 429.2468 | 368.7117 | 381.6538
3352.3635 | 429.1644 | 368.6867 | 381.6462
3353.3635 | 429.1147 | 368.7008 | 381.6431
3354.3635 | 428.9908 | 368.7088 | 381.65
3355.3635 | 429.0051 | 368.7067 | 381.6499
3356.3635 | 428.8722 | 368.7203 | 381.6553
3357.3635 | 428.8265 | 368.7056 | 381.6695
3358.3635 | 428.8731 | 368.7214 | 381.6755
3359.3635 | 428.8453 | 368.7147 | 381.6765
3360.3635 | 428.9139 | 368.7185 | 381.6909
3361.3635 | 428.9909 | 368.725 | 381.699
3362.3635 | 429.0887 | 368.7101 | 381.6998
3363.3635 | 429.0159 | 368.7194 | 381.7123
3364.3635 | 428.9532 | 368.7032 | 381.7123
3365.3635 | 428.9434 | 368.7098 | 381.7185
3366.3635 | 428.9805 | 368.6956 | 381.7175
3367.3635 | 428.9925 | 368.6854 | 381.7105
3368.3635 | 429.0347 | 368.6835 | 381.6947
3369.3635 | 429.1369 | 368.6749 | 381.675
3370.3635 | 429.2677 | 368.6808 | 381.6653
3371.3635 | 429.2803 | 368.6637 | 381.639
3372.3635 | 429.2444 | 368.6682 | 381.6221
3373.3635 | 429.2119 | 368.6443 | 381.601
3374.3635 | 429.3408 | 368.6445 | 381.5848
3375.3635 | 429.4481 | 368.6248 | 381.565
3376.3635 | 429.5404 | 368.6191 | 381.5493
3377.3635 | 429.4836 | 368.6327 | 381.5321
3378.3635 | 429.507 | 368.6038 | 381.5147
3379.3635 | 429.4458 | 368.614 | 381.5095
3380.3635 | 429.3388 | 368.6059 | 381.4933
3381.3635 | 429.4201 | 368.602 | 381.4864
3382.3635 | 429.5109 | 368.6053 | 381.4694
3383.3635 | 429.6161 | 368.5845 | 381.4563
3384.3635 | 429.6333 | 368.6094 | 381.4571
3385.3635 | 429.6066 | 368.5833 | 381.456
3386.3635 | 429.6341 | 368.6113 | 381.4568
3387.3635 | 429.6622 | 368.5995 | 381.4498
3388.3635 | 429.6634 | 368.5889 | 381.451
3389.3635 | 429.6072 | 368.6003 | 381.4603
3390.3635 | 429.5695 | 368.6043 | 381.4593
3391.3635 | 429.4869 | 368.6175 | 381.4638
3392.3635 | 429.4933 | 368.621 | 381.4676
3393.3635 | 429.4722 | 368.631 | 381.4726
3394.3635 | 429.4541 | 368.6225 | 381.4672
3395.3635 | 429.4241 | 368.6366 | 381.4707
3396.3635 | 429.4656 | 368.6307 | 381.4682
3397.3635 | 429.4646 | 368.6219 | 381.4655
3398.3635 | 429.4564 | 368.6483 | 381.4731
3399.3635 | 429.3565 | 368.6298 | 381.4741
3400.3635 | 429.3656 | 368.6289 | 381.4772
3401.3635 | 429.3556 | 368.633 | 381.4662
3402.3635 | 429.3435 | 368.6252 | 381.4768
3403.3635 | 429.3873 | 368.6173 | 381.4784
3404.3635 | 429.4001 | 368.6118 | 381.4663
3405.3635 | 429.3241 | 368.6315 | 381.4695
3406.4104 | 429.2224 | 368.6214 | 381.4757
3407.3635 | 429.1848 | 368.6133 | 381.4762
3408.3635 | 429.207 | 368.5892 | 381.4742
3409.3635 | 429.1944 | 368.5962 | 381.4725
3410.3635 | 429.0609 | 368.5942 | 381.4705
3411.3635 | 428.964 | 368.5828 | 381.471
3412.3635 | 429.0871 | 368.5829 | 381.4753
3413.3635 | 429.1725 | 368.5674 | 381.4676
3414.3635 | 429.1923 | 368.5784 | 381.4738
3415.3635 | 429.2795 | 368.5524 | 381.4791
3416.3635 | 429.2448 | 368.5418 | 381.4866
3417.3635 | 429.2367 | 368.5404 | 381.4904
3418.3635 | 429.246 | 368.5257 | 381.4989
3419.3635 | 429.3048 | 368.523 | 381.5071
3420.3635 | 429.3799 | 368.5012 | 381.5119
3421.3635 | 429.4339 | 368.5015 | 381.5167
3422.3479 | 429.5269 | 368.4824 | 381.5178
3423.3635 | 429.3937 | 368.4852 | 381.5245
3424.3635 | 429.3391 | 368.4755 | 381.5272
3425.3635 | 429.3206 | 368.4694 | 381.532
3426.3635 | 429.2415 | 368.4763 | 381.5299
3427.3635 | 429.2978 | 368.4605 | 381.5265
3428.3635 | 429.3668 | 368.4764 | 381.5265
3429.3479 | 429.3241 | 368.4403 | 381.5297
3430.3635 | 429.3218 | 368.4693 | 381.5354
3431.3479 | 429.3356 | 368.452 | 381.5348
3432.3635 | 429.2949 | 368.4437 | 381.5415
3433.3479 | 429.367 | 368.462 | 381.5446
3434.3479 | 429.4762 | 368.447 | 381.55
3435.3479 | 429.4797 | 368.4507 | 381.5583
3436.3635 | 429.5334 | 368.4517 | 381.5624
3437.3479 | 429.5724 | 368.4618 | 381.5766
3438.3479 | 429.5759 | 368.4574 | 381.5814
3439.3479 | 429.6008 | 368.4763 | 381.5883
3440.3479 | 429.5792 | 368.4761 | 381.5867
3441.3479 | 429.4743 | 368.476 | 381.5969
3442.3635 | 429.4669 | 368.4889 | 381.6048
3443.3479 | 429.4145 | 368.4831 | 381.6207
3444.3479 | 429.4036 | 368.4895 | 381.6353
3445.3479 | 429.5418 | 368.4969 | 381.6442
3446.3479 | 429.5525 | 368.5022 | 381.659
3447.3479 | 429.6333 | 368.5175 | 381.6555
3448.3635 | 429.5866 | 368.5202 | 381.6582
3449.3479 | 429.536 | 368.5182 | 381.6557
3450.3479 | 429.4924 | 368.5262 | 381.6453
3451.3479 | 429.3989 | 368.5419 | 381.6447
3452.3635 | 429.4515 | 368.5208 | 381.6463
3453.3479 | 429.4893 | 368.5314 | 381.6397
3454.3635 | 429.5497 | 368.54 | 381.6392
3455.3479 | 429.5145 | 368.5391 | 381.6359
3456.3479 | 429.5512 | 368.5434 | 381.6365
3457.3479 | 429.5279 | 368.5294 | 381.6297
3458.3479 | 429.4673 | 368.5361 | 381.6304
3459.3479 | 429.4434 | 368.53 | 381.6255
3460.3479 | 429.4078 | 368.5282 | 381.6401
3461.3479 | 429.4451 | 368.5209 | 381.6435
3462.3635 | 429.4263 | 368.5111 | 381.648
3463.3479 | 429.3936 | 368.5229 | 381.6436
3464.3479 | 429.3638 | 368.493 | 381.6411
3465.3479 | 429.3523 | 368.4941 | 381.6478
3466.3635 | 429.4116 | 368.4714 | 381.6492
3467.3479 | 429.3684 | 368.4752 | 381.6428
3468.3479 | 429.4348 | 368.4619 | 381.6405
3469.3479 | 429.4373 | 368.4338 | 381.6327
3470.3479 | 429.4182 | 368.4397 | 381.6343
3471.3479 | 429.3819 | 368.4233 | 381.6367
3472.3479 | 429.4468 | 368.4191 | 381.6418
3473.3635 | 429.4172 | 368.3934 | 381.6472
3474.3479 | 429.401 | 368.3894 | 381.6539
3475.3479 | 429.4439 | 368.379 | 381.6621
3476.3479 | 429.3861 | 368.3727 | 381.6685
3477.3479 | 429.3739 | 368.3765 | 381.6703
3478.3635 | 429.4169 | 368.365 | 381.6828
3479.3479 | 429.4242 | 368.3629 | 381.6929
3480.3479 | 429.4298 | 368.3339 | 381.7021
3481.3479 | 429.4448 | 368.3347 | 381.7069
3482.3479 | 429.3993 | 368.3329 | 381.7157
3483.3479 | 429.3906 | 368.3176 | 381.7234
3484.3479 | 429.3391 | 368.3203 | 381.7359
3485.3479 | 429.31 | 368.3111 | 381.7482
3486.3479 | 429.3164 | 368.3181 | 381.7536
3487.3479 | 429.3112 | 368.2888 | 381.7647
3488.3479 | 429.3385 | 368.2912 | 381.7707
3489.3479 | 429.3084 | 368.2813 | 381.7756
3490.3479 | 429.2801 | 368.2662 | 381.784
3491.3479 | 429.3749 | 368.2773 | 381.7956
3492.3479 | 429.4404 | 368.258 | 381.8051
3493.3479 | 429.4019 | 368.2596 | 381.8069
3494.3479 | 429.3406 | 368.2435 | 381.8155
3495.3479 | 429.225 | 368.225 | 381.8105
3496.3479 | 429.2287 | 368.2324 | 381.8158
3497.3479 | 429.2001 | 368.2121 | 381.8238
3498.3479 | 429.2217 | 368.2257 | 381.8297
3499.3479 | 429.2169 | 368.2016 | 381.8154
3500.3479 | 429.2034 | 368.2059 | 381.8106
3501.3479 | 429.1898 | 368.1927 | 381.7918
3502.3479 | 429.1145 | 368.1858 | 381.7883
3503.3479 | 429.0888 | 368.1967 | 381.7713
3504.3479 | 429.1461 | 368.1606 | 381.768
3505.3479 | 429.1298 | 368.1705 | 381.7585
3506.3479 | 429.0337 | 368.1522 | 381.7453
3507.3479 | 428.9982 | 368.1412 | 381.74
3508.3635 | 428.9853 | 368.1383 | 381.7251
3509.3479 | 428.9663 | 368.1248 | 381.7123
3510.3479 | 429.0217 | 368.1367 | 381.7029
3511.3479 | 428.9555 | 368.1105 | 381.6912
3512.3479 | 428.8261 | 368.1024 | 381.6759
3513.3479 | 428.7297 | 368.1173 | 381.6624
3514.3479 | 428.7788 | 368.0868 | 381.6519
3515.3479 | 428.8851 | 368.1098 | 381.6275
3516.3479 | 429.0051 | 368.1061 | 381.6198
3517.3479 | 429.1336 | 368.1289 | 381.5976
3518.3479 | 429.0978 | 368.1045 | 381.5885
3519.3479 | 429.1323 | 368.1342 | 381.578
3520.3479 | 429.1425 | 368.1356 | 381.5649
3521.3479 | 429.1378 | 368.1331 | 381.5646
3522.3479 | 429.1806 | 368.1475 | 381.5515
3523.3479 | 429.1111 | 368.1458 | 381.5501
3524.3635 | 429.0738 | 368.1719 | 381.5444
3525.3479 | 429.1738 | 368.1665 | 381.5332
3526.3635 | 429.2718 | 368.1789 | 381.5285
3527.3479 | 429.3509 | 368.1921 | 381.5224
3528.3479 | 429.4244 | 368.1891 | 381.5131
3529.3479 | 429.3993 | 368.2191 | 381.5122
3530.3479 | 429.3407 | 368.2085 | 381.5116
3531.3635 | 429.4622 | 368.2284 | 381.5072
3532.3479 | 429.4988 | 368.229 | 381.5085
3533.3479 | 429.5621 | 368.2442 | 381.5105
3534.3479 | 429.6876 | 368.2538 | 381.5174
3535.3635 | 429.6777 | 368.2486 | 381.5186
3536.3479 | 429.6747 | 368.2675 | 381.5249
3537.3479 | 429.7443 | 368.2608 | 381.5255
3538.3635 | 429.7193 | 368.2861 | 381.5258
3539.3479 | 429.7338 | 368.2773 | 381.5324
3540.3479 | 429.7059 | 368.2866 | 381.5347
3541.3479 | 429.7768 | 368.3004 | 381.5385
3542.3479 | 429.8308 | 368.3011 | 381.5435
3543.3479 | 429.8159 | 368.3088 | 381.5514
3544.3479 | 429.6989 | 368.3092 | 381.5557
3545.3479 | 429.648 | 368.3372 | 381.5655
3546.3479 | 429.588 | 368.3266 | 381.5744
3547.3479 | 429.4778 | 368.3501 | 381.5902
3548.3479 | 429.4412 | 368.3273 | 381.5932
3549.3635 | 429.4672 | 368.3474 | 381.5995
3550.3635 | 429.4273 | 368.3325 | 381.6134
3551.3635 | 429.4066 | 368.3385 | 381.6224
3552.3479 | 429.4053 | 368.3444 | 381.6296
3553.3635 | 429.2723 | 368.3376 | 381.6411
3554.3479 | 429.2692 | 368.3444 | 381.6541
3555.3635 | 429.2743 | 368.3326 | 381.662
3556.3479 | 429.2807 | 368.3385 | 381.6704
3557.3635 | 429.2069 | 368.3331 | 381.6729
3558.3479 | 429.2511 | 368.3297 | 381.6741
3559.3635 | 429.2502 | 368.3317 | 381.6869
3560.3479 | 429.2639 | 368.3016 | 381.6829
3561.3635 | 429.3061 | 368.324 | 381.6899
3562.3479 | 429.2706 | 368.3194 | 381.6912
3563.3479 | 429.2914 | 368.3195 | 381.6904
3564.3635 | 429.2408 | 368.3132 | 381.6921
3565.3635 | 429.188 | 368.3021 | 381.6864
3566.3479 | 429.2871 | 368.3063 | 381.689
3567.3479 | 429.3662 | 368.2985 | 381.6796
3568.3635 | 429.4309 | 368.2958 | 381.674
3569.3479 | 429.4613 | 368.2903 | 381.6696
3570.3635 | 429.4268 | 368.2893 | 381.6713
3571.3635 | 429.4019 | 368.2813 | 381.6651
3572.3479 | 429.4738 | 368.264 | 381.6667
3573.3635 | 429.5577 | 368.2772 | 381.6616
3574.3479 | 429.5892 | 368.2612 | 381.6626
3575.3635 | 429.5868 | 368.2589 | 381.6623
3576.3479 | 429.5688 | 368.254 | 381.6497
3577.3635 | 429.5149 | 368.2604 | 381.6382
3578.3635 | 429.4872 | 368.2667 | 381.6397
3579.3635 | 429.4833 | 368.2552 | 381.6407
3580.3635 | 429.5103 | 368.2792 | 381.6441
3581.3635 | 429.5511 | 368.2669 | 381.647
3582.3635 | 429.6233 | 368.2753 | 381.6544
3583.3635 | 429.5722 | 368.2829 | 381.6614
3584.3635 | 429.5302 | 368.2772 | 381.6692
3585.3635 | 429.487 | 368.2889 | 381.6725
3586.3635 | 429.4837 | 368.2744 | 381.69
3587.3635 | 429.6077 | 368.3002 | 381.6902
3588.3635 | 429.703 | 368.2893 | 381.6965
3589.3635 | 429.6433 | 368.2901 | 381.7009
3590.3635 | 429.6156 | 368.2882 | 381.7165
3591.3635 | 429.6204 | 368.2878 | 381.7147
3592.3635 | 429.6511 | 368.302 | 381.7284
3593.3635 | 429.638 | 368.2964 | 381.7197
3594.3635 | 429.6457 | 368.3059 | 381.7228
3595.3635 | 429.5235 | 368.3047 | 381.7264
3596.3635 | 429.3879 | 368.3049 | 381.7264
3597.3635 | 429.407 | 368.302 | 381.7264
3598.3479 | 429.3858 | 368.3092 | 381.7261
3599.3635 | 429.4391 | 368.3337 | 381.715
3600.3635 | 429.5153 | 368.3087 | 381.7055
3601.3635 | 429.4641 | 368.3398 | 381.698
3602.3479 | 429.4137 | 368.3301 | 381.6975
3603.3635 | 429.4201 | 368.3582 | 381.6848
3604.3635 | 429.3528 | 368.353 | 381.6771
3605.3635 | 429.4044 | 368.3441 | 381.683
3606.3635 | 429.5088 | 368.3662 | 381.6761
3607.3635 | 429.5479 | 368.3456 | 381.6736
3608.3635 | 429.4878 | 368.349 | 381.6675
3609.3635 | 429.5112 | 368.3472 | 381.6793
3610.3635 | 429.5217 | 368.3475 | 381.6746
3611.3635 | 429.5201 | 368.3523 | 381.6714
3612.3635 | 429.422 | 368.3385 | 381.6751
3613.3635 | 429.4532 | 368.3446 | 381.6756
3614.3635 | 429.5187 | 368.3305 | 381.6778
3615.3635 | 429.5812 | 368.3453 | 381.6749
3616.3635 | 429.5256 | 368.3328 | 381.6792
3617.3635 | 429.5015 | 368.339 | 381.6822
3618.3635 | 429.4702 | 368.3445 | 381.6755
3619.3635 | 429.5137 | 368.3419 | 381.6833
3620.3635 | 429.4836 | 368.3555 | 381.681
3621.3635 | 429.4591 | 368.3455 | 381.6814
3622.3635 | 429.5456 | 368.3477 | 381.6741
3623.3635 | 429.5693 | 368.3625 | 381.6669
3624.3635 | 429.4755 | 368.3576 | 381.6545
3625.3635 | 429.3836 | 368.3775 | 381.6608
3626.3635 | 429.3968 | 368.3652 | 381.651
3627.3635 | 429.4173 | 368.3853 | 381.6453
3628.3635 | 429.357 | 368.3788 | 381.6445
3629.3635 | 429.3202 | 368.3959 | 381.6414
3630.3635 | 429.2017 | 368.3933 | 381.6383
3631.3635 | 429.183 | 368.3886 | 381.6426
3632.3635 | 429.1622 | 368.4057 | 381.6341
3633.3635 | 429.1695 | 368.3805 | 381.6338
3634.3479 | 429.189 | 368.4041 | 381.6262
3635.3479 | 429.2044 | 368.3907 | 381.6241
3636.3635 | 429.2527 | 368.3925 | 381.6279
3637.3479 | 429.3244 | 368.3964 | 381.6307
3638.3635 | 429.4409 | 368.3623 | 381.6272
3639.3635 | 429.475 | 368.377 | 381.6295
3640.3635 | 429.5747 | 368.3516 | 381.6365
3641.3635 | 429.619 | 368.3601 | 381.6307
3642.3479 | 429.6276 | 368.34 | 381.636
3643.3635 | 429.7582 | 368.3253 | 381.6436
3644.3635 | 429.788 | 368.3258 | 381.6529
3645.3635 | 429.7932 | 368.3158 | 381.6597
3646.3635 | 429.7526 | 368.3099 | 381.6604
3647.3635 | 429.7086 | 368.2854 | 381.6582
3648.3635 | 429.6966 | 368.2892 | 381.6626
3649.3635 | 429.5675 | 368.2792 | 381.6611
3650.3635 | 429.5765 | 368.2759 | 381.6668
3651.3635 | 429.7494 | 368.2753 | 381.6644
3652.3635 | 429.7862 | 368.2439 | 381.6671
3653.3635 | 429.7407 | 368.2606 | 381.6653
3654.3635 | 429.6421 | 368.237 | 381.6568
3655.3635 | 429.5765 | 368.247 | 381.6486
3656.3635 | 429.6234 | 368.2437 | 381.653
3657.3635 | 429.6605 | 368.2332 | 381.6384
3658.3635 | 429.7125 | 368.2456 | 381.6356
3659.3635 | 429.6622 | 368.2294 | 381.6197
3660.3635 | 429.6069 | 368.2422 | 381.6146
3661.3635 | 429.5685 | 368.2169 | 381.5975
3662.3635 | 429.48 | 368.2251 | 381.5876
3663.3635 | 429.4301 | 368.2244 | 381.581
3664.3635 | 429.4836 | 368.2233 | 381.5742
3665.3635 | 429.5198 | 368.2197 | 381.5604
3666.3635 | 429.4754 | 368.1957 | 381.5537
3667.3635 | 429.4778 | 368.2021 | 381.5496
3668.3635 | 429.3833 | 368.1793 | 381.547
3669.3635 | 429.2902 | 368.1872 | 381.5413
3670.3635 | 429.3773 | 368.1661 | 381.5237
3671.3635 | 429.4239 | 368.1718 | 381.5167
3672.3635 | 429.2782 | 368.1658 | 381.5007
3673.3635 | 429.1972 | 368.157 | 381.4908
3674.3635 | 429.2058 | 368.1658 | 381.4859
3675.3635 | 429.1331 | 368.1412 | 381.47
3676.3635 | 429.1576 | 368.1689 | 381.4671
3677.3635 | 429.0831 | 368.1354 | 381.4706
3678.3635 | 429.0309 | 368.1546 | 381.4734
3679.3635 | 429.086 | 368.1477 | 381.4752
3680.3635 | 429.2117 | 368.1499 | 381.4717
3681.3635 | 429.1519 | 368.153 | 381.4746
3682.3635 | 429.1731 | 368.1291 | 381.4664
3683.3635 | 429.0452 | 368.1463 | 381.4627
3684.3635 | 429.0538 | 368.138 | 381.454
3685.3635 | 429.1148 | 368.1513 | 381.4507
3686.3635 | 429.2064 | 368.1429 | 381.4421
3687.3635 | 429.3569 | 368.148 | 381.4233
3688.3479 | 429.356 | 368.1461 | 381.418
3689.3635 | 429.2744 | 368.1326 | 381.4125
3690.3635 | 429.2809 | 368.1552 | 381.3945
3691.3635 | 429.303 | 368.139 | 381.3996
3692.3635 | 429.2345 | 368.1501 | 381.393
3693.3635 | 429.1841 | 368.1535 | 381.3921
3694.3635 | 429.1205 | 368.1465 | 381.4012
3695.3635 | 429.2656 | 368.1541 | 381.3925
3696.3635 | 429.2349 | 368.1443 | 381.4001
3697.3635 | 429.2818 | 368.1729 | 381.3983
3698.3635 | 429.2857 | 368.1538 | 381.4098
3699.3635 | 429.355 | 368.1659 | 381.4106
3700.3635 | 429.2469 | 368.1634 | 381.4181
3701.3635 | 429.2265 | 368.1623 | 381.4231
3702.3635 | 429.3084 | 368.172 | 381.4239
3703.3635 | 429.3051 | 368.1627 | 381.4276
3704.3635 | 429.332 | 368.1712 | 381.436
3705.3635 | 429.1937 | 368.1515 | 381.4393
3706.3635 | 429.2528 | 368.1738 | 381.4373
3707.3635 | 429.2713 | 368.1681 | 381.4418
3708.3635 | 429.2467 | 368.1691 | 381.4483
3709.3635 | 429.2889 | 368.1857 | 381.4396
3710.3635 | 429.3943 | 368.1775 | 381.4498
3711.3635 | 429.4059 | 368.2025 | 381.4408
3712.3635 | 429.3885 | 368.1933 | 381.4425
3713.3635 | 429.5021 | 368.2076 | 381.4468
3714.3635 | 429.5963 | 368.1978 | 381.4477
3715.3635 | 429.5663 | 368.207 | 381.4545
3716.3635 | 429.5032 | 368.2129 | 381.4618
3717.3635 | 429.4492 | 368.1953 | 381.4635
3718.3635 | 429.4826 | 368.2214 | 381.4662
3719.3635 | 429.5662 | 368.2122 | 381.4761
3720.3635 | 429.6895 | 368.2161 | 381.4732
3721.3635 | 429.7315 | 368.2117 | 381.4833
3722.3635 | 429.823 | 368.2078 | 381.4948
3723.3635 | 429.7185 | 368.2017 | 381.5001
3724.3635 | 429.7189 | 368.1905 | 381.505
3725.3635 | 429.7043 | 368.2021 | 381.5136
3726.3635 | 429.7084 | 368.1798 | 381.5149
3727.3635 | 429.6827 | 368.1924 | 381.5141
3728.3635 | 429.7604 | 368.1806 | 381.5228
3729.3635 | 429.827 | 368.1674 | 381.5266
3730.3635 | 429.8697 | 368.1648 | 381.5303
3731.3635 | 429.9419 | 368.1548 | 381.524
3732.3635 | 429.9382 | 368.158 | 381.5199
3733.3635 | 429.9104 | 368.1387 | 381.5165
3734.3635 | 429.7593 | 368.1435 | 381.5149
3735.3635 | 429.6582 | 368.1399 | 381.5138
3736.3635 | 429.7651 | 368.1384 | 381.5087
3737.3635 | 429.864 | 368.14 | 381.503
3738.3635 | 429.7175 | 368.1339 | 381.4954
3739.3635 | 429.6222 | 368.1422 | 381.4903
3740.3635 | 429.5759 | 368.1253 | 381.4861
3741.3635 | 429.5328 | 368.15 | 381.4808
3742.3635 | 429.4245 | 368.1508 | 381.4691
3743.3635 | 429.387 | 368.1431 | 381.4513
3744.3635 | 429.3546 | 368.1576 | 381.4422
3745.3635 | 429.2746 | 368.141 | 381.4198
3746.3635 | 429.2538 | 368.1681 | 381.4142
3747.3635 | 429.2754 | 368.1674 | 381.4075
3748.3635 | 429.3001 | 368.1847 | 381.3979
3749.3635 | 429.3574 | 368.1778 | 381.395
3750.3635 | 429.3856 | 368.1804 | 381.3961
3751.3635 | 429.4093 | 368.1848 | 381.3923
3752.3635 | 429.4835 | 368.1789 | 381.3978
3753.3635 | 429.4625 | 368.2019 | 381.3957
3754.3635 | 429.4277 | 368.1924 | 381.4028
3755.3635 | 429.4415 | 368.1958 | 381.4031
3756.3635 | 429.3793 | 368.2026 | 381.4001
3757.3635 | 429.2114 | 368.1885 | 381.41
3758.3635 | 429.2077 | 368.1943 | 381.4009
3759.3635 | 429.2564 | 368.1813 | 381.4133
3760.3635 | 429.3579 | 368.1938 | 381.4043
3761.3635 | 429.3555 | 368.1829 | 381.4133
3762.3635 | 429.3094 | 368.1646 | 381.4179
3763.3635 | 429.2146 | 368.1959 | 381.4211
3764.3479 | 429.2619 | 368.1781 | 381.4148
3765.3635 | 429.1999 | 368.1882 | 381.422
3766.3635 | 429.0913 | 368.1725 | 381.4181
3767.3635 | 429.0799 | 368.1839 | 381.4198
3768.3635 | 429.0067 | 368.1833 | 381.418
3769.3635 | 428.9662 | 368.1641 | 381.4202
3770.3635 | 428.9922 | 368.1733 | 381.4275
3771.3635 | 429.044 | 368.1555 | 381.4299
3772.3635 | 429.0382 | 368.1618 | 381.4296
3773.3635 | 429.0428 | 368.135 | 381.4301
3774.3479 | 429.0448 | 368.1476 | 381.4275
3775.3635 | 429.0872 | 368.1464 | 381.4183
3776.3479 | 429.0668 | 368.138 | 381.4065
3777.3635 | 429.0118 | 368.1361 | 381.3938
3778.3635 | 428.9991 | 368.1176 | 381.3925
3779.3635 | 429.0138 | 368.1399 | 381.3831
3780.3635 | 429.1878 | 368.1088 | 381.374
3781.3479 | 429.3088 | 368.1214 | 381.3734
3782.3635 | 429.3385 | 368.1116 | 381.3664
3783.3479 | 429.3628 | 368.1117 | 381.3705
3784.3635 | 429.3452 | 368.1134 | 381.3657
3785.3479 | 429.3577 | 368.1011 | 381.3641
3786.3635 | 429.3864 | 368.1168 | 381.3643
3787.3479 | 429.4334 | 368.1086 | 381.3656
3788.3635 | 429.5235 | 368.122 | 381.3713
3789.3479 | 429.5872 | 368.1073 | 381.3691
3790.3635 | 429.5878 | 368.1107 | 381.3736
3791.3479 | 429.572 | 368.1081 | 381.3728
3792.3635 | 429.599 | 368.1044 | 381.364
3793.3479 | 429.537 | 368.1156 | 381.3556
3794.3635 | 429.6205 | 368.1033 | 381.3533
3795.3479 | 429.7047 | 368.1017 | 381.3411
3796.3635 | 429.782 | 368.0875 | 381.3337
3797.3479 | 429.7259 | 368.0755 | 381.326
3798.3635 | 429.7285 | 368.097 | 381.3131
3799.3479 | 429.6221 | 368.096 | 381.3132
3800.3479 | 429.6466 | 368.1021 | 381.3097
3801.3479 | 429.5725 | 368.096 | 381.3098
3802.3635 | 429.539 | 368.1088 | 381.3087
3803.3479 | 429.4901 | 368.1002 | 381.316
3804.3635 | 429.3969 | 368.119 | 381.3192
3805.3479 | 429.4465 | 368.1141 | 381.3187
3806.3635 | 429.4183 | 368.1295 | 381.3292
3807.3635 | 429.4677 | 368.1373 | 381.3367
3808.3479 | 429.5676 | 368.1242 | 381.3275
3809.3479 | 429.5369 | 368.1386 | 381.3308
3810.3635 | 429.4484 | 368.1248 | 381.3407
3811.3479 | 429.3708 | 368.1349 | 381.3396
3812.3479 | 429.3684 | 368.1349 | 381.3398
3813.3479 | 429.4283 | 368.1451 | 381.3504
3814.3479 | 429.4265 | 368.1435 | 381.3479
3815.3479 | 429.3224 | 368.1351 | 381.354
3816.3479 | 429.2996 | 368.1507 | 381.3657
3817.3635 | 429.3511 | 368.1344 | 381.3678
3818.3479 | 429.2957 | 368.1551 | 381.3668
3819.3479 | 429.3841 | 368.1464 | 381.3689
3820.3479 | 429.4028 | 368.1538 | 381.3786
3821.3479 | 429.4104 | 368.1474 | 381.3765
3822.3479 | 429.2897 | 368.1389 | 381.3812
3823.3479 | 429.2384 | 368.1413 | 381.3836
3824.3479 | 429.3073 | 368.1405 | 381.3893
3825.3479 | 429.3515 | 368.1489 | 381.3837
3826.3635 | 429.345 | 368.1338 | 381.3864
3827.3479 | 429.2635 | 368.1315 | 381.3944
3828.3479 | 429.2838 | 368.1301 | 381.4014
3829.3479 | 429.3584 | 368.1213 | 381.3944
3830.3635 | 429.4015 | 368.1252 | 381.3956
3831.3479 | 429.3115 | 368.1173 | 381.3995
3832.3635 | 429.1413 | 368.1346 | 381.3983
3833.3479 | 429.1338 | 368.1209 | 381.3951
3834.3479 | 429.2128 | 368.1213 | 381.3862
3835.3635 | 429.2835 | 368.1121 | 381.3831
3836.3479 | 429.3715 | 368.115 | 381.3809
3837.3635 | 429.306 | 368.1235 | 381.3746
3838.3635 | 429.2175 | 368.1035 | 381.3671
3839.3635 | 429.1339 | 368.1156 | 381.3584
3840.3635 | 429.1786 | 368.0882 | 381.3557
3841.3635 | 429.1844 | 368.1069 | 381.3578
3842.3635 | 429.1912 | 368.0869 | 381.3517
3843.3635 | 429.1595 | 368.0929 | 381.3411
3844.3635 | 429.1695 | 368.0919 | 381.3401
3845.3635 | 429.1731 | 368.0994 | 381.3383
3846.3635 | 429.191 | 368.1001 | 381.3298
3847.3635 | 429.1343 | 368.0835 | 381.3265
3848.3635 | 429.1546 | 368.0997 | 381.3237
3849.3479 | 429.1703 | 368.0836 | 381.3255
3850.3635 | 429.2457 | 368.0918 | 381.3287
3851.3479 | 429.2928 | 368.0772 | 381.332
3852.3635 | 429.3311 | 368.0885 | 381.3397
3853.3479 | 429.4312 | 368.0786 | 381.3457
3854.3479 | 429.5055 | 368.0696 | 381.3385
3855.3479 | 429.5624 | 368.0751 | 381.3426
3856.3479 | 429.6038 | 368.0541 | 381.3486
3857.3635 | 429.5543 | 368.077 | 381.3486
3858.3479 | 429.5512 | 368.068 | 381.3524
3859.3479 | 429.5126 | 368.0776 | 381.3554
3860.3479 | 429.6054 | 368.0701 | 381.3578
3861.3479 | 429.524 | 368.0615 | 381.3585
3862.3479 | 429.4093 | 368.08 | 381.3564
3863.3479 | 429.2958 | 368.0742 | 381.3558
3864.3479 | 429.3368 | 368.0852 | 381.3523
3865.3479 | 429.3827 | 368.0747 | 381.3442
3866.3479 | 429.3695 | 368.0888 | 381.3379
3867.3635 | 429.3388 | 368.0863 | 381.325
3868.3479 | 429.3798 | 368.0782 | 381.3199
3869.3479 | 429.338 | 368.1055 | 381.3009
3870.3479 | 429.3572 | 368.0889 | 381.2986
3871.3635 | 429.4143 | 368.1178 | 381.2957
3872.3479 | 429.3605 | 368.0906 | 381.281
3873.3479 | 429.3853 | 368.1095 | 381.2752
3874.3479 | 429.5411 | 368.1024 | 381.2674
3875.3479 | 429.6 | 368.1154 | 381.2684
3876.3635 | 429.5958 | 368.1034 | 381.2709
3877.3479 | 429.555 | 368.1056 | 381.2632
3878.3479 | 429.4156 | 368.1157 | 381.271
3879.3635 | 429.3435 | 368.1037 | 381.2721
3880.3479 | 429.2952 | 368.1217 | 381.2645
3881.3635 | 429.3227 | 368.1059 | 381.2734
3882.3635 | 429.3925 | 368.1214 | 381.2662
3883.3635 | 429.4524 | 368.1111 | 381.277
3884.3635 | 429.4636 | 368.1349 | 381.2684
3885.3479 | 429.3936 | 368.1391 | 381.2812
3886.3635 | 429.4166 | 368.1456 | 381.2885
3887.3635 | 429.4276 | 368.159 | 381.2965
3888.3479 | 429.4066 | 368.1647 | 381.3022
3889.3479 | 429.3756 | 368.1815 | 381.3171
3890.3635 | 429.3368 | 368.181 | 381.3293
3891.3479 | 429.2958 | 368.1961 | 381.341
3892.3479 | 429.4068 | 368.2002 | 381.3576
3893.3635 | 429.4502 | 368.2146 | 381.3638
3894.3479 | 429.4201 | 368.2419 | 381.3752
3895.3479 | 429.439 | 368.2196 | 381.3864
3896.3479 | 429.4195 | 368.2546 | 381.3894
3897.3479 | 429.4756 | 368.2451 | 381.4035
3898.3479 | 429.4835 | 368.2383 | 381.4131
3899.3479 | 429.5195 | 368.2388 | 381.4194
3900.3479 | 429.5826 | 368.2281 | 381.4241
3901.3479 | 429.7006 | 368.2391 | 381.4318
3902.3479 | 429.7184 | 368.2246 | 381.4361
3903.3479 | 429.6824 | 368.2284 | 381.4446
3904.3479 | 429.6726 | 368.2131 | 381.4428
3905.3479 | 429.6539 | 368.2201 | 381.4522
3906.3479 | 429.4987 | 368.223 | 381.4596
3907.3479 | 429.3997 | 368.1975 | 381.4659
3908.3479 | 429.3052 | 368.2178 | 381.4803
3909.3479 | 429.2745 | 368.2017 | 381.4915
3910.3479 | 429.3896 | 368.2024 | 381.4928
3911.3479 | 429.4641 | 368.1971 | 381.5002
3912.3479 | 429.4737 | 368.1924 | 381.5063
3913.3479 | 429.5339 | 368.2067 | 381.5037
3914.3479 | 429.604 | 368.1787 | 381.5108
3915.3479 | 429.5475 | 368.1932 | 381.5103
3916.3479 | 429.5179 | 368.1734 | 381.5022
3917.3479 | 429.5002 | 368.1708 | 381.4962
3918.3479 | 429.4909 | 368.1658 | 381.5018
3919.3479 | 429.4394 | 368.146 | 381.4907
3920.3479 | 429.4407 | 368.165 | 381.4911
3921.3479 | 429.4073 | 368.1518 | 381.4874
3922.3479 | 429.4162 | 368.1605 | 381.485
3923.3479 | 429.4205 | 368.1501 | 381.4803
3924.3479 | 429.3688 | 368.1583 | 381.4805
3925.3635 | 429.3572 | 368.1486 | 381.479
3926.3635 | 429.4348 | 368.152 | 381.4833
3927.3635 | 429.4496 | 368.1704 | 381.4779
3928.3635 | 429.4811 | 368.173 | 381.4761
3929.3635 | 429.4093 | 368.1845 | 381.4709
3930.3635 | 429.4255 | 368.1767 | 381.4737
3931.3479 | 429.4209 | 368.1889 | 381.4806
3932.3479 | 429.3569 | 368.1949 | 381.4779
3933.3479 | 429.2981 | 368.1844 | 381.4866
3934.3479 | 429.2676 | 368.1942 | 381.4833
3935.3635 | 429.3199 | 368.1813 | 381.4677
3936.3635 | 429.2818 | 368.2008 | 381.4742
3937.3479 | 429.3044 | 368.1969 | 381.4733
3938.3479 | 429.2899 | 368.1833 | 381.464
3939.3635 | 429.3674 | 368.1976 | 381.4613
3940.3635 | 429.4704 | 368.1905 | 381.4545
3941.3635 | 429.5437 | 368.2069 | 381.4544
3942.3479 | 429.59 | 368.1902 | 381.4529
3943.3635 | 429.606 | 368.2036 | 381.4468
3944.3635 | 429.7117 | 368.1979 | 381.4482
3945.3635 | 429.7184 | 368.1974 | 381.4479
3946.3635 | 429.6332 | 368.2113 | 381.4535
3947.3479 | 429.5829 | 368.2002 | 381.4534
3948.3479 | 429.7143 | 368.2075 | 381.4585
3949.3479 | 429.817 | 368.1991 | 381.4664
3950.3635 | 429.8593 | 368.2082 | 381.4619
3951.3635 | 429.8464 | 368.2014 | 381.4696
3952.3635 | 429.7949 | 368.2003 | 381.4642
3953.3479 | 429.7696 | 368.2105 | 381.4664
3954.3635 | 429.7246 | 368.1971 | 381.4701
3955.3635 | 429.7181 | 368.1969 | 381.4701
3956.3635 | 429.5997 | 368.2086 | 381.4732
3957.3479 | 429.4562 | 368.1982 | 381.4714
3958.3479 | 429.4287 | 368.2126 | 381.4767
3959.3635 | 429.5062 | 368.2002 | 381.4838
3960.3479 | 429.4769 | 368.2074 | 381.491
3961.3479 | 429.4278 | 368.2075 | 381.4911
3962.3635 | 429.3988 | 368.2062 | 381.4993
3963.3635 | 429.4537 | 368.2048 | 381.4981
3964.3479 | 429.4161 | 368.2083 | 381.501
3965.3635 | 429.4523 | 368.2271 | 381.4989
3966.3635 | 429.4892 | 368.2036 | 381.4935
3967.3635 | 429.4598 | 368.2198 | 381.4943
3968.3635 | 429.4763 | 368.2142 | 381.4932
3969.3635 | 429.4742 | 368.2095 | 381.5003
3970.3479 | 429.5715 | 368.2127 | 381.4992
3971.3635 | 429.5807 | 368.2109 | 381.496
3972.3635 | 429.6788 | 368.2078 | 381.5034
3973.3479 | 429.6744 | 368.1934 | 381.5072
3974.3635 | 429.626 | 368.1997 | 381.5039
3975.3635 | 429.4875 | 368.2001 | 381.5159
3976.3479 | 429.48 | 368.1937 | 381.5151
3977.3635 | 429.4854 | 368.1929 | 381.5153
3978.3635 | 429.5491 | 368.1748 | 381.5185
3979.3635 | 429.4951 | 368.1921 | 381.51
3980.3635 | 429.4294 | 368.1833 | 381.5132
3981.3635 | 429.4195 | 368.1879 | 381.5191
3982.3635 | 429.3779 | 368.1822 | 381.5171
3983.3635 | 429.3308 | 368.1765 | 381.5265
3984.3635 | 429.2932 | 368.1747 | 381.5293
3985.3635 | 429.2054 | 368.1708 | 381.5345
3986.3635 | 429.2633 | 368.1759 | 381.5398
3987.3635 | 429.2472 | 368.1707 | 381.5528
3988.3635 | 429.1353 | 368.1636 | 381.5543
3989.3635 | 429.1018 | 368.1666 | 381.5609
3990.3635 | 429.1328 | 368.1563 | 381.5671
3991.3635 | 429.179 | 368.1716 | 381.5765
3992.3635 | 429.1296 | 368.1551 | 381.5764
3993.3635 | 429.2212 | 368.1566 | 381.5862
3994.3635 | 429.2112 | 368.1527 | 381.5912
3995.3635 | 429.3004 | 368.1602 | 381.5883
3996.3635 | 429.3478 | 368.1584 | 381.5819
3997.3635 | 429.4082 | 368.1584 | 381.5878
3998.3635 | 429.4068 | 368.1712 | 381.5818
3999.3635 | 429.4106 | 368.1468 | 381.5799
4000.3635 | 429.3401 | 368.1743 | 381.5767
4001.3635 | 429.3174 | 368.1668 | 381.5713
4002.3479 | 429.2721 | 368.1502 | 381.5622
4003.3635 | 429.1284 | 368.1784 | 381.5588
4004.3635 | 429.1508 | 368.1586 | 381.5613
4005.3635 | 429.1728 | 368.1684 | 381.5627
4006.3948 | 429.1721 | 368.1639 | 381.5645
4007.3635 | 429.0572 | 368.1691 | 381.5582
4008.3635 | 429.0172 | 368.1769 | 381.5673
4009.3635 | 429.0718 | 368.1638 | 381.5694
4010.3635 | 429.0522 | 368.1729 | 381.5708
4011.3635 | 429.0362 | 368.1648 | 381.5833
4012.3635 | 429.0082 | 368.1673 | 381.5996
4013.3635 | 429.0741 | 368.1511 | 381.6111
4014.3635 | 429.1494 | 368.1628 | 381.6309
4015.3635 | 429.1535 | 368.1738 | 381.6444
4016.3635 | 429.1487 | 368.1482 | 381.6527
4017.3635 | 429.1586 | 368.1454 | 381.6578
4018.3635 | 429.157 | 368.1394 | 381.6745
4019.3635 | 429.0542 | 368.1544 | 381.672
4020.3635 | 429.1065 | 368.1468 | 381.6877
4021.3635 | 429.1373 | 368.1461 | 381.6995
4022.3635 | 429.178 | 368.1525 | 381.6912
4023.3635 | 429.2155 | 368.1405 | 381.6808
4024.3635 | 429.2878 | 368.1561 | 381.6733
4025.3635 | 429.3022 | 368.138 | 381.6676
4026.3635 | 429.3406 | 368.1508 | 381.6689
4027.3635 | 429.328 | 368.1512 | 381.6601
4028.3635 | 429.3601 | 368.1547 | 381.6651
4029.3635 | 429.4395 | 368.1685 | 381.6564
4030.3635 | 429.3889 | 368.1539 | 381.6586
4031.3635 | 429.3342 | 368.1684 | 381.6552
4032.3635 | 429.2628 | 368.1519 | 381.6598
4033.3635 | 429.2011 | 368.1732 | 381.654
4034.3635 | 429.1459 | 368.1691 | 381.6579
4035.3635 | 429.1098 | 368.1781 | 381.6624
4036.3635 | 429.2427 | 368.1926 | 381.6684
4037.3635 | 429.3264 | 368.1825 | 381.6771
4038.3635 | 429.2311 | 368.2002 | 381.6791
4039.3635 | 429.137 | 368.2166 | 381.6849
4040.3635 | 429.0169 | 368.2169 | 381.691
4041.3635 | 429.1252 | 368.2466 | 381.6943
4042.3635 | 429.1416 | 368.2377 | 381.691
4043.3635 | 429.1774 | 368.2591 | 381.697
4044.3635 | 429.0711 | 368.2526 | 381.6852
4045.3635 | 428.9723 | 368.2631 | 381.6833
4046.3635 | 428.973 | 368.2767 | 381.6909
4047.3635 | 429.0587 | 368.2761 | 381.6888
4048.3635 | 429.1142 | 368.29 | 381.6884
4049.3635 | 429.1348 | 368.293 | 381.6932
4050.3635 | 429.099 | 368.3114 | 381.6857
4051.3635 | 429.0265 | 368.3133 | 381.681
4052.3635 | 429.0064 | 368.3291 | 381.6741
4053.3635 | 428.9947 | 368.331 | 381.6504
4054.3635 | 429.0451 | 368.3276 | 381.6441
4055.3635 | 429.025 | 368.3532 | 381.632
4056.3635 | 429.1129 | 368.3554 | 381.627
4057.3635 | 429.1475 | 368.3655 | 381.6228
4058.3635 | 429.2824 | 368.3874 | 381.6174
4059.3635 | 429.245 | 368.3896 | 381.6151
4060.3635 | 429.3267 | 368.4044 | 381.6124
4061.3635 | 429.2332 | 368.419 | 381.6147
4062.3635 | 429.2192 | 368.4291 | 381.6128
4063.3635 | 429.1934 | 368.4431 | 381.6159
4064.3635 | 429.2286 | 368.4425 | 381.613
4065.3635 | 429.1899 | 368.4566 | 381.6063
4066.3635 | 429.1565 | 368.4743 | 381.6047
4067.3635 | 429.1174 | 368.4676 | 381.5964
4068.3635 | 429.04 | 368.4847 | 381.5938
4069.3635 | 429.0879 | 368.4924 | 381.5849
4070.3635 | 429.0746 | 368.5145 | 381.5773
4071.3635 | 429.0204 | 368.5203 | 381.5622
4072.3635 | 429.0639 | 368.5195 | 381.5512
4073.3635 | 428.9949 | 368.5202 | 381.5491
4074.3635 | 429.0438 | 368.5199 | 381.5376
4075.3635 | 429.0755 | 368.5162 | 381.5306
4076.3635 | NaN | NaN | NaN
4077.3635 | 403.5028 | 389.8432 | 391.1616
4078.3635 | 428.9841 | 368.5109 | 381.5222
4079.3635 | 429.0048 | 368.499 | 381.5275
4080.3635 | 429.0398 | 368.477 | 381.5169
4081.3635 | 429.0431 | 368.4775 | 381.5124
4082.3635 | 429.0578 | 368.4519 | 381.5156
4083.3635 | 429.0589 | 368.4571 | 381.5168
4084.3635 | 429.0042 | 368.4387 | 381.5186
4085.3635 | 429.0857 | 368.4407 | 381.5285
4086.3635 | 429.0548 | 368.4364 | 381.5339
4087.3635 | 429.0532 | 368.4209 | 381.5496
4088.3635 | 429.0883 | 368.4286 | 381.5533
4089.3635 | 429.101 | 368.4191 | 381.564
4090.3635 | 429.0985 | 368.4187 | 381.5707
4091.3635 | 429.1208 | 368.4072 | 381.5846
4092.3635 | 429.1453 | 368.4016 | 381.5953
4093.3635 | 429.2031 | 368.3932 | 381.6017
4094.3635 | 429.1766 | 368.3829 | 381.6095
4095.3635 | 429.2216 | 368.3734 | 381.6147
4096.3635 | 429.221 | 368.3647 | 381.6217
4097.3635 | 429.2914 | 368.3487 | 381.6237
4098.3635 | 429.4034 | 368.3386 | 381.6263
4099.3635 | 429.5164 | 368.3325 | 381.6304
4100.3635 | 429.5143 | 368.3142 | 381.6386
4101.3635 | 429.5718 | 368.3138 | 381.6518
4102.3635 | 429.5401 | 368.2838 | 381.6547
4103.3635 | 429.3981 | 368.2755 | 381.66
4104.3635 | 429.4955 | 368.269 | 381.6636
4105.3635 | 429.4964 | 368.251 | 381.6674
4106.3635 | 429.5067 | 368.2382 | 381.6682
4107.3635 | 429.5681 | 368.2285 | 381.6718
4108.3635 | 429.6154 | 368.231 | 381.6727
4109.3635 | 429.7067 | 368.2067 | 381.6729
4110.3635 | 429.7029 | 368.2101 | 381.6637
4111.3635 | 429.7102 | 368.2134 | 381.6566
4112.3635 | 429.7186 | 368.1979 | 381.646
4113.3635 | 429.7901 | 368.2109 | 381.6468
4114.3635 | 429.8094 | 368.2026 | 381.6494
4115.3635 | 429.783 | 368.1995 | 381.6395
4116.3635 | 429.7142 | 368.2077 | 381.6368
4117.3635 | 429.6578 | 368.2052 | 381.6363
4118.3635 | 429.5837 | 368.2071 | 381.6335
4119.3635 | 429.5482 | 368.2071 | 381.6285
4120.3635 | 429.6047 | 368.1976 | 381.6199
4121.3635 | 429.6543 | 368.211 | 381.6077
4122.3635 | 429.6009 | 368.1999 | 381.5968
4123.3635 | 429.6698 | 368.2037 | 381.5891
4124.3635 | 429.7653 | 368.2292 | 381.5715
4125.3635 | 429.6809 | 368.2165 | 381.5588
4126.3635 | 429.6122 | 368.2322 | 381.5568
4127.3635 | 429.5962 | 368.2366 | 381.5435
4128.3635 | 429.5452 | 368.2474 | 381.5332
4129.3635 | 429.4999 | 368.2469 | 381.5216
4130.3635 | 429.5269 | 368.2569 | 381.5187
4131.3635 | 429.4871 | 368.2669 | 381.5164
4132.3635 | 429.5353 | 368.2584 | 381.517
4133.3635 | 429.4409 | 368.2614 | 381.5202
4134.3635 | 429.5322 | 368.2755 | 381.5209
4135.3635 | 429.461 | 368.2689 | 381.5302
4136.3635 | 429.4421 | 368.2829 | 381.5371
4137.3635 | 429.4252 | 368.2724 | 381.5369
4138.3635 | 429.3924 | 368.2811 | 381.5389
4139.3635 | 429.4764 | 368.2824 | 381.5414
4140.3635 | 429.5255 | 368.2801 | 381.5472
4141.3479 | 429.4405 | 368.2813 | 381.5571
4142.3635 | 429.4811 | 368.2803 | 381.5613
4143.3479 | 429.4324 | 368.2859 | 381.5625
4144.3635 | 429.5266 | 368.2837 | 381.5741
4145.3635 | 429.4852 | 368.2958 | 381.5722
4146.3479 | 429.4471 | 368.2968 | 381.5676
4147.3479 | 429.4709 | 368.2921 | 381.5701
4148.3635 | 429.4518 | 368.304 | 381.5695
4149.3479 | 429.5397 | 368.3175 | 381.5678
4150.3635 | 429.5303 | 368.3055 | 381.5674
4151.3479 | 429.5046 | 368.3171 | 381.5754
4152.3635 | 429.5559 | 368.3145 | 381.5713
4153.3479 | 429.4106 | 368.3108 | 381.574
4154.3635 | 429.3763 | 368.3295 | 381.5711
4155.3635 | 429.4772 | 368.3255 | 381.5749
4156.3635 | 429.4666 | 368.3239 | 381.576
4157.3479 | 429.4074 | 368.3166 | 381.5685
4158.3479 | 429.3332 | 368.3309 | 381.5639
4159.3479 | 429.2905 | 368.3336 | 381.57
4160.3479 | 429.2494 | 368.3308 | 381.5645
4161.3479 | 429.2153 | 368.3282 | 381.5685
4162.3635 | 429.1928 | 368.3486 | 381.5678
4163.3635 | 429.1466 | 368.344 | 381.5662
4164.3479 | 429.1868 | 368.3447 | 381.5714
4165.3479 | 429.2192 | 368.3588 | 381.5773
4166.3479 | 429.2543 | 368.3593 | 381.5782
4167.3479 | 429.1681 | 368.3495 | 381.5787
4168.3479 | 429.2254 | 368.3704 | 381.5764
4169.3635 | 429.2396 | 368.3723 | 381.5669
4170.3479 | 429.2813 | 368.374 | 381.5635
4171.3479 | 429.3016 | 368.3805 | 381.5557
4172.3479 | 429.4231 | 368.3761 | 381.5488
4173.3479 | 429.4556 | 368.378 | 381.5434
4174.3479 | 429.5819 | 368.3799 | 381.5349
4175.3479 | 429.6472 | 368.3804 | 381.5329
4176.3479 | 429.6234 | 368.3843 | 381.537
4177.3479 | 429.558 | 368.3901 | 381.5295
4178.3479 | 429.4946 | 368.3809 | 381.5361
4179.3479 | 429.4941 | 368.3974 | 381.5252
4180.3635 | 429.5431 | 368.3938 | 381.5152
4181.3479 | 429.5258 | 368.3966 | 381.5201
4182.3479 | 429.5764 | 368.3874 | 381.5132
4183.3479 | 429.5761 | 368.3962 | 381.5172
4184.3479 | 429.5101 | 368.3887 | 381.5176
4185.3479 | 429.4476 | 368.3914 | 381.5135
4186.3635 | 429.4359 | 368.3894 | 381.5201
4187.3479 | 429.3402 | 368.375 | 381.5182
4188.3479 | 429.3668 | 368.3887 | 381.518
4189.3479 | 429.383 | 368.3896 | 381.5024
4190.3635 | 429.4274 | 368.3961 | 381.5008
4191.3479 | 429.3929 | 368.3837 | 381.4907
4192.3479 | 429.3953 | 368.3927 | 381.4998
4193.3479 | 429.439 | 368.3901 | 381.4939
4194.3635 | 429.5012 | 368.4033 | 381.4918
4195.3479 | 429.4148 | 368.3973 | 381.4924
4196.3479 | 429.4113 | 368.3968 | 381.492
4197.3479 | 429.535 | 368.3984 | 381.5008
4198.3479 | 429.4694 | 368.4034 | 381.5024
4199.3479 | 429.4373 | 368.395 | 381.5046
4200.3479 | 429.4837 | 368.4045 | 381.5034
4201.3635 | 429.4861 | 368.3895 | 381.4928
4202.3479 | 429.4849 | 368.3945 | 381.4876
4203.3479 | 429.3433 | 368.3968 | 381.4787
4204.3635 | 429.3764 | 368.3854 | 381.4824
4205.3479 | 429.3637 | 368.3949 | 381.4744
4206.3479 | 429.3291 | 368.3758 | 381.4771
4207.3479 | 429.3262 | 368.3899 | 381.4751
4208.3479 | 429.3123 | 368.4126 | 381.4692
4209.3479 | 429.2493 | 368.4106 | 381.4708
4210.3479 | 429.1857 | 368.399 | 381.4581
4211.3479 | 429.1518 | 368.4064 | 381.4573
4212.3479 | 429.1764 | 368.417 | 381.4641
4213.426 | 429.1433 | 368.4153 | 381.4578
4214.3479 | 429.161 | 368.4246 | 381.4665
4215.3479 | 429.176 | 368.4249 | 381.4742
4216.3479 | 429.1799 | 368.422 | 381.4822
4217.3479 | 429.2322 | 368.4215 | 381.4944
4218.3635 | 429.3825 | 368.417 | 381.5046
4219.3479 | 429.4705 | 368.4256 | 381.5132
4220.3635 | 429.5041 | 368.4257 | 381.5158
4221.3479 | 429.4281 | 368.4077 | 381.5205
4222.3635 | 429.4169 | 368.4048 | 381.5239
4223.3635 | 429.4272 | 368.4155 | 381.5356
4224.3635 | 429.4026 | 368.4138 | 381.5479
4225.3635 | 429.4422 | 368.4009 | 381.5606
4226.3479 | 429.5191 | 368.4027 | 381.5706
4227.3635 | 429.6216 | 368.397 | 381.5742
4228.3479 | 429.6009 | 368.3967 | 381.5823
4229.3635 | 429.72 | 368.3864 | 381.5779
4230.3479 | 429.7199 | 368.3817 | 381.5779
4231.3479 | 429.7438 | 368.3827 | 381.5806
4232.3479 | 429.7877 | 368.3682 | 381.5742
4233.3635 | 429.8638 | 368.3629 | 381.5809
4234.3479 | 429.8275 | 368.365 | 381.5726
4235.3635 | 429.8298 | 368.3412 | 381.5774
4236.3479 | 429.7858 | 368.3501 | 381.5745
4237.3635 | 429.7555 | 368.3486 | 381.5671
4238.3635 | 429.7714 | 368.3386 | 381.5694
4239.3479 | 429.8103 | 368.3338 | 381.5734
4240.3635 | 429.8255 | 368.3186 | 381.5746
4241.3479 | 429.702 | 368.3271 | 381.586
4242.3479 | 429.6537 | 368.3299 | 381.5941
4243.3479 | 429.7445 | 368.3245 | 381.6047
4244.3479 | 429.9815 | 368.3227 | 381.614
4245.3479 | 430.0771 | 368.3303 | 381.6234
4246.3479 | 430.045 | 368.329 | 381.6341
4247.3479 | 430.1128 | 368.3167 | 381.6359
4248.3479 | 430.0784 | 368.3235 | 381.6343
4249.3479 | 429.9737 | 368.3197 | 381.6303
4250.3635 | 429.8869 | 368.3132 | 381.6261
4251.3635 | 429.9154 | 368.3067 | 381.6291
4252.3635 | 429.9651 | 368.3126 | 381.6309
4253.3635 | 430.0333 | 368.3108 | 381.6325
4254.3635 | 430.0383 | 368.3116 | 381.6304
4255.3479 | 430.0462 | 368.3063 | 381.6266
4256.3635 | 429.9674 | 368.2981 | 381.6226
4257.3479 | 430.0718 | 368.281 | 381.628
4258.3635 | 430.2384 | 368.2909 | 381.6342
4259.3479 | 430.2871 | 368.2676 | 381.634
4260.3479 | 430.1276 | 368.2771 | 381.6331
4261.3479 | 429.9577 | 368.2628 | 381.6417
4262.3479 | 429.909 | 368.2525 | 381.648
4263.3479 | 429.9774 | 368.253 | 381.6462
4264.3635 | 430.0133 | 368.2375 | 381.6468
4265.3479 | 430.0605 | 368.2309 | 381.65
4266.3479 | 429.9454 | 368.2173 | 381.6636
4267.3479 | 429.9053 | 368.2247 | 381.6599
4268.3479 | 429.8039 | 368.2148 | 381.6609
4269.3479 | 429.7867 | 368.2037 | 381.6659
4270.3479 | 429.7457 | 368.1963 | 381.661
4271.3479 | 429.8085 | 368.1989 | 381.6629
4272.3479 | 429.7846 | 368.1809 | 381.6602
4273.3479 | 429.9493 | 368.178 | 381.6593
4274.3479 | 429.9212 | 368.1785 | 381.6457
4275.3479 | 429.8925 | 368.1735 | 381.6485
4276.3479 | 429.8296 | 368.1604 | 381.6374
4277.3479 | 429.8369 | 368.165 | 381.6311
4278.3635 | 429.725 | 368.1518 | 381.6254
4279.3479 | 429.6931 | 368.1593 | 381.622
4280.3635 | 429.6933 | 368.1528 | 381.6148
4281.3479 | 429.7178 | 368.1387 | 381.6089
4282.3635 | 429.7938 | 368.1375 | 381.6062
4283.3479 | 429.8134 | 368.1505 | 381.6085
4284.3635 | 429.8521 | 368.1416 | 381.6039
4285.3479 | 429.9221 | 368.1444 | 381.6026
4286.3479 | 429.9598 | 368.1336 | 381.6002
4287.3479 | 429.9464 | 368.1288 | 381.6006
4288.3635 | 429.9071 | 368.1334 | 381.6032
4289.3479 | 429.9681 | 368.146 | 381.5967
4290.3635 | 430.0361 | 368.1261 | 381.6014
4291.3479 | 430.0106 | 368.1364 | 381.6039
4292.3479 | 429.9905 | 368.1402 | 381.5994
4293.3479 | 430.1216 | 368.1442 | 381.5933
4294.3635 | 430.0409 | 368.15 | 381.5955
4295.3635 | 429.9789 | 368.1518 | 381.5985
4296.3635 | 430.0206 | 368.161 | 381.5934
4297.3635 | 430.0788 | 368.1531 | 381.6004
4298.3635 | 430.2158 | 368.1775 | 381.5815
4299.3635 | 430.1338 | 368.185 | 381.5756
4300.3635 | 430.0049 | 368.185 | 381.5597
4301.3635 | 429.7981 | 368.1973 | 381.5544
4302.3635 | 429.6983 | 368.2158 | 381.547
4303.3635 | 429.7106 | 368.2171 | 381.5376
4304.3635 | 429.7797 | 368.2235 | 381.5308
4305.3635 | 429.7512 | 368.2439 | 381.5204
4306.3635 | 429.6543 | 368.2497 | 381.5169
4307.3635 | 429.6788 | 368.2668 | 381.5093
4308.3635 | 429.7313 | 368.2629 | 381.5072
4309.3635 | 429.7401 | 368.2585 | 381.5067
4310.3635 | 429.6955 | 368.2713 | 381.5033
4311.3635 | 429.6202 | 368.2766 | 381.5002
4312.3635 | 429.6643 | 368.2719 | 381.498
4313.3635 | 429.6457 | 368.2757 | 381.5019
4314.3635 | 429.784 | 368.2641 | 381.4986
4315.3635 | 429.9074 | 368.258 | 381.4959
4316.3635 | 429.9535 | 368.272 | 381.489
4317.3635 | 430.0073 | 368.2655 | 381.4862
4318.3635 | 429.9569 | 368.265 | 381.4803
4319.3635 | 430.0043 | 368.2586 | 381.4784
4320.3635 | 430.0651 | 368.2637 | 381.4724
4321.3635 | 430.1638 | 368.2561 | 381.4807
4322.3635 | 430.2163 | 368.2442 | 381.4896
4323.3635 | 430.0855 | 368.2526 | 381.491
4324.3635 | 429.993 | 368.2619 | 381.4978
4325.3635 | 430.0522 | 368.2682 | 381.5077
4326.3635 | 430.1247 | 368.2512 | 381.5118
4327.3635 | 430.1419 | 368.2717 | 381.5208
4328.3635 | 430.0961 | 368.2598 | 381.5347
4329.3635 | 429.994 | 368.2807 | 381.5385
4330.3635 | 429.9777 | 368.2833 | 381.5525
4331.3635 | 430.0152 | 368.2778 | 381.561
4332.3635 | 429.9816 | 368.2938 | 381.57
4333.3635 | 429.9818 | 368.2896 | 381.5746
4334.3635 | 429.9126 | 368.2994 | 381.5862
4335.3635 | 429.8375 | 368.3153 | 381.5957
4336.3635 | 429.8686 | 368.3239 | 381.6095
4337.3635 | 429.956 | 368.3439 | 381.6173
4338.3635 | 430.0144 | 368.3416 | 381.6181
4339.3635 | 429.8984 | 368.3653 | 381.6203
4340.3635 | 429.8433 | 368.3842 | 381.6223
4341.3635 | 429.8303 | 368.3933 | 381.6199
4342.3635 | 429.6987 | 368.4109 | 381.632
4343.3635 | 429.6053 | 368.4315 | 381.6297
4344.3635 | 429.6309 | 368.4498 | 381.6312
4345.3635 | 429.7341 | 368.4604 | 381.6372
4346.3635 | 429.7537 | 368.4598 | 381.6425
4347.3635 | 429.7268 | 368.4634 | 381.6432
4348.3635 | 429.7 | 368.4867 | 381.6429
4349.3635 | 429.6603 | 368.4918 | 381.6481
4350.3635 | 429.597 | 368.4986 | 381.6493
4351.3635 | 429.5919 | 368.508 | 381.6587
4352.3635 | 429.6387 | 368.525 | 381.6582
4353.3635 | 429.6984 | 368.5342 | 381.6596
4354.3635 | 429.773 | 368.5394 | 381.6726
4355.3635 | 429.784 | 368.5398 | 381.6827
4356.3635 | 429.9171 | 368.5509 | 381.6821
4357.3635 | 429.8485 | 368.559 | 381.6861
4358.3635 | 429.903 | 368.5752 | 381.685
4359.3635 | 429.9681 | 368.588 | 381.6841
4360.3635 | 429.9654 | 368.602 | 381.6793
4361.3635 | 429.9263 | 368.6042 | 381.6725
4362.3635 | 429.9 | 368.6214 | 381.664
4363.3635 | 429.9382 | 368.638 | 381.6577
4364.3635 | 429.9095 | 368.6431 | 381.6539
4365.3635 | 429.7946 | 368.6569 | 381.6507
4366.3635 | 429.6165 | 368.6628 | 381.646
4367.3635 | 429.5027 | 368.6743 | 381.6432
4368.3479 | 429.5519 | 368.6869 | 381.6396
4369.3635 | 429.636 | 368.6826 | 381.6229
4370.3479 | 429.6489 | 368.6792 | 381.6063
4371.3635 | 429.6919 | 368.682 | 381.5978
4372.3479 | 429.8473 | 368.6865 | 381.5869
4373.3635 | 429.7853 | 368.6939 | 381.5781
4374.3635 | 429.7319 | 368.7035 | 381.5726
4375.3635 | 429.6577 | 368.7073 | 381.5669
4376.3479 | 429.6256 | 368.7106 | 381.5597
4377.3635 | 429.5719 | 368.7103 | 381.5605
4378.3635 | 429.5984 | 368.6994 | 381.5666
4379.3635 | 429.6459 | 368.702 | 381.5783
4380.3635 | 429.67 | 368.697 | 381.5772
4381.3635 | 429.6346 | 368.6907 | 381.5788
4382.3635 | 429.547 | 368.6919 | 381.5823
4383.3635 | 429.5785 | 368.6976 | 381.5893
4384.3635 | 429.6014 | 368.6876 | 381.5966
4385.3635 | 429.5018 | 368.67 | 381.5937
4386.3635 | 429.4086 | 368.6829 | 381.5946
4387.3635 | 429.4204 | 368.6781 | 381.5934
4388.3635 | 429.4816 | 368.6783 | 381.5959
4389.3635 | 429.444 | 368.6782 | 381.5929
4390.3635 | 429.4088 | 368.6761 | 381.5882
4391.3635 | 429.3527 | 368.6731 | 381.5891
4392.3635 | 429.3027 | 368.6645 | 381.5785
4393.3635 | 429.2313 | 368.6439 | 381.5698
4394.3479 | 429.2002 | 368.6499 | 381.5698
4395.3635 | 429.1488 | 368.6377 | 381.5738
4396.3635 | 429.1915 | 368.6326 | 381.5589
4397.3479 | 429.2936 | 368.6302 | 381.5545
4398.3635 | 429.2949 | 368.6079 | 381.5504
4399.3635 | 429.2855 | 368.6049 | 381.5478
4400.3635 | 429.3604 | 368.6076 | 381.5356
4401.3635 | 429.4525 | 368.5827 | 381.5222
4402.3635 | 429.4444 | 368.5812 | 381.5203
4403.3635 | 429.3141 | 368.5672 | 381.5149
4404.3635 | 429.3297 | 368.5695 | 381.5116
4405.3635 | 429.4256 | 368.562 | 381.5127
4406.3635 | 429.5373 | 368.5424 | 381.5053
4407.3635 | 429.5805 | 368.5454 | 381.5159
4408.3635 | 429.5557 | 368.5317 | 381.5091
4409.3635 | 429.5632 | 368.5176 | 381.5141
4410.3635 | 429.5689 | 368.5189 | 381.5143
4411.3479 | 429.5172 | 368.5082 | 381.5177
4412.3635 | 429.4279 | 368.4939 | 381.5234
4413.3635 | 429.4192 | 368.4929 | 381.5251
4414.3635 | 429.4033 | 368.4767 | 381.5329
4415.3635 | 429.4027 | 368.4725 | 381.5366
4416.3635 | 429.5137 | 368.457 | 381.5431
4417.3479 | 429.4784 | 368.4582 | 381.5399
4418.3635 | 429.5085 | 368.4546 | 381.5476
4419.3635 | 429.4997 | 368.4356 | 381.5463
4420.3479 | 429.4418 | 368.4442 | 381.5479
4421.3635 | 429.4216 | 368.4439 | 381.5471
4422.3635 | 429.4894 | 368.4502 | 381.5418
4423.3635 | 429.4058 | 368.438 | 381.5428
4424.3635 | 429.3545 | 368.4401 | 381.5365
4425.3635 | 429.5142 | 368.4473 | 381.5314
4426.3479 | 429.5659 | 368.4313 | 381.5257
4427.3635 | 429.5878 | 368.4318 | 381.5223
4428.3635 | 429.7468 | 368.4296 | 381.5147
4429.3635 | 429.8187 | 368.4388 | 381.5128
4430.3635 | 429.8278 | 368.4259 | 381.5176
4431.3635 | 429.8944 | 368.4197 | 381.5189
4432.3635 | 429.8656 | 368.411 | 381.52
4433.3635 | 429.8504 | 368.4138 | 381.5243
4434.3635 | 429.8642 | 368.4104 | 381.5177
4435.3635 | 429.8883 | 368.4055 | 381.5201
4436.3635 | 429.8294 | 368.393 | 381.5176
4437.3635 | 429.7837 | 368.3932 | 381.5219
4438.3635 | 429.6674 | 368.4025 | 381.528
4439.3635 | 429.6572 | 368.3933 | 381.5251
4440.3635 | 429.7919 | 368.3873 | 381.5141
4441.3635 | 429.8637 | 368.3809 | 381.5051
4442.3635 | 429.8389 | 368.3723 | 381.5047
4443.3635 | 429.7741 | 368.3655 | 381.5054
4444.3635 | 429.7215 | 368.3645 | 381.5048
4445.3635 | 429.7663 | 368.341 | 381.5054
4446.3635 | 429.7898 | 368.3621 | 381.5144
4447.3635 | 429.7436 | 368.3528 | 381.5185
4448.3635 | 429.8556 | 368.3509 | 381.5177
4449.3635 | 429.723 | 368.3535 | 381.516
4450.3635 | 429.7294 | 368.348 | 381.5171
4451.3635 | 429.8014 | 368.3376 | 381.5065
4452.3635 | 429.8827 | 368.3495 | 381.5077
4453.3635 | 429.9269 | 368.3414 | 381.5117
4454.3635 | 429.9017 | 368.3359 | 381.5037
4455.3635 | 429.9061 | 368.34 | 381.5089
4456.3635 | 429.9115 | 368.3366 | 381.4898
4457.3635 | 429.8056 | 368.331 | 381.4911
4458.3635 | 429.8033 | 368.3274 | 381.4735
4459.3635 | 429.8712 | 368.3208 | 381.4847
4460.3635 | 429.8996 | 368.3328 | 381.4854
4461.3635 | 429.8941 | 368.3346 | 381.4858
4462.3635 | 429.8044 | 368.337 | 381.497
4463.3635 | 429.7493 | 368.3417 | 381.5027
4464.3635 | 429.747 | 368.3375 | 381.5089
4465.3635 | 429.7274 | 368.3483 | 381.5093
4466.3635 | 429.7457 | 368.3577 | 381.527
4467.3635 | 429.6946 | 368.3564 | 381.5267
4468.3635 | 429.712 | 368.3801 | 381.5425
4469.3635 | 429.5683 | 368.3774 | 381.5523
4470.3635 | 429.5051 | 368.3828 | 381.5661
4471.3635 | 429.4211 | 368.3911 | 381.5681
4472.3635 | 429.4028 | 368.4076 | 381.5673
4473.3635 | 429.365 | 368.4109 | 381.5728
4474.3635 | 429.3945 | 368.4255 | 381.5693
4475.3479 | 429.409 | 368.4369 | 381.5562
4476.3635 | 429.4207 | 368.4384 | 381.5507
4477.3479 | 429.3581 | 368.4557 | 381.5569
4478.3635 | 429.2892 | 368.4675 | 381.5444
4479.3635 | 429.2244 | 368.4668 | 381.5434
4480.3479 | 429.1774 | 368.4836 | 381.5303
4481.3479 | 429.2141 | 368.4915 | 381.518
4482.3635 | 429.2448 | 368.4973 | 381.5086
4483.3479 | 429.2432 | 368.5034 | 381.5054
4484.3479 | 429.2148 | 368.5215 | 381.4926
4485.3635 | 429.2431 | 368.5335 | 381.482
4486.3479 | 429.2459 | 368.5415 | 381.4691
4487.3635 | 429.1636 | 368.5397 | 381.4693
4488.3479 | 429.1363 | 368.5607 | 381.4573
4489.3635 | 429.1613 | 368.5549 | 381.4555
4490.3479 | 429.23 | 368.5661 | 381.4377
4491.3635 | 429.22 | 368.581 | 381.4328
4492.3479 | 429.341 | 368.574 | 381.4243
4493.3635 | 429.3764 | 368.5889 | 381.4054
4494.3479 | 429.3476 | 368.602 | 381.399
4495.3635 | 429.254 | 368.6021 | 381.3965
4496.3479 | 429.3248 | 368.6168 | 381.4074
4497.3479 | 429.3835 | 368.614 | 381.4179
4498.3479 | 429.4543 | 368.6233 | 381.4306
4499.3635 | 429.5237 | 368.6332 | 381.4362
4500.3479 | 429.6168 | 368.6248 | 381.443
4501.3479 | 429.6829 | 368.6429 | 381.4361
4502.3479 | 429.7729 | 368.6411 | 381.441
4503.3479 | 429.7644 | 368.648 | 381.446
4504.3635 | 429.834 | 368.6613 | 381.4457
4505.3479 | 429.8909 | 368.6454 | 381.4509
4506.3479 | 429.9547 | 368.6493 | 381.4546
4507.3635 | 430.0295 | 368.6441 | 381.4419
4508.3479 | 430.1258 | 368.6597 | 381.4513
4509.3635 | 429.9745 | 368.6625 | 381.4591
4510.3479 | 429.9931 | 368.6654 | 381.4545
4511.3635 | 429.9598 | 368.6608 | 381.4516
4512.3479 | 429.9539 | 368.6725 | 381.446
4513.3635 | 429.9472 | 368.6558 | 381.4434
4514.3479 | 429.9703 | 368.6783 | 381.4434
4515.3635 | 429.8314 | 368.6789 | 381.446
4516.3479 | 429.7492 | 368.6761 | 381.4496
4517.3635 | 429.7801 | 368.6931 | 381.4539
4518.3635 | 429.7255 | 368.6986 | 381.4575
4519.3635 | 429.6652 | 368.7135 | 381.4722
4520.3479 | 429.7058 | 368.7109 | 381.4748
4521.3635 | 429.7667 | 368.7096 | 381.4921
4522.3479 | 429.8424 | 368.7259 | 381.5072
4523.3635 | 429.8832 | 368.7009 | 381.5061
4524.3479 | 429.9031 | 368.714 | 381.5092
4525.3479 | 429.8213 | 368.7241 | 381.5095
4526.3479 | 429.8416 | 368.7147 | 381.5168
4527.3479 | 429.8846 | 368.7246 | 381.5229
4528.3479 | 429.8075 | 368.7116 | 381.5135
4529.3635 | 429.673 | 368.7157 | 381.522
4530.3635 | 429.6294 | 368.718 | 381.5236
4531.3479 | 429.6961 | 368.706 | 381.5177
4532.3635 | 429.7265 | 368.717 | 381.5144
4533.3479 | 429.7519 | 368.7108 | 381.5139
4534.3635 | 429.6926 | 368.7043 | 381.5129
4535.3479 | 429.6764 | 368.7102 | 381.5087
4536.3635 | 429.6756 | 368.7043 | 381.5101
4537.3635 | 429.5933 | 368.7111 | 381.507
4538.3635 | 429.5909 | 368.7165 | 381.5055
4539.3635 | 429.5452 | 368.721 | 381.5134
4540.3479 | 429.5059 | 368.7181 | 381.5101
4541.3479 | 429.4637 | 368.7079 | 381.5105
4542.3479 | 429.3939 | 368.7145 | 381.5062
4543.3479 | 429.3531 | 368.7112 | 381.5023
4544.3479 | 429.2737 | 368.7061 | 381.5156
4545.3479 | 429.2689 | 368.6993 | 381.5147
4546.3479 | 429.3944 | 368.6955 | 381.5229
4547.3479 | 429.4614 | 368.6879 | 381.5359
4548.3479 | 429.4216 | 368.6835 | 381.5426
4549.3479 | 429.4736 | 368.6814 | 381.5519
4550.3479 | 429.5424 | 368.6768 | 381.5601
4551.3479 | 429.5818 | 368.6815 | 381.5601
4552.3479 | 429.5986 | 368.672 | 381.5554
4553.3479 | 429.674 | 368.6788 | 381.5513
4554.3479 | 429.7298 | 368.6627 | 381.5459
4555.3479 | 429.8028 | 368.6658 | 381.5392
4556.3479 | 429.8312 | 368.6467 | 381.5322
4557.3479 | 429.8917 | 368.6624 | 381.5316
4558.3479 | 429.8945 | 368.6703 | 381.5438
4559.3635 | 429.7676 | 368.6537 | 381.5584
4560.3479 | 429.549 | 368.6673 | 381.5722
4561.3635 | 429.5011 | 368.6672 | 381.5823
4562.3479 | 429.4969 | 368.6455 | 381.5917
4563.3635 | 429.4177 | 368.6634 | 381.5937
4564.3635 | 429.3943 | 368.6551 | 381.5956
4565.3635 | 429.391 | 368.6535 | 381.588
4566.3479 | 429.2617 | 368.6678 | 381.5881
4567.3479 | 429.2147 | 368.6475 | 381.5983
4568.3635 | 429.1954 | 368.6607 | 381.6013
4569.3635 | 429.1624 | 368.664 | 381.6041
4570.3479 | 429.1329 | 368.6507 | 381.6085
4571.3635 | 429.1178 | 368.6626 | 381.6147
4572.3635 | 429.1211 | 368.6377 | 381.6284
4573.3635 | 429.1971 | 368.6338 | 381.6337
4574.3479 | 429.1705 | 368.6297 | 381.6394
4575.3635 | 429.1978 | 368.6118 | 381.6508
4576.3479 | 429.2946 | 368.6091 | 381.6583
4577.3479 | 429.3816 | 368.6012 | 381.6577
4578.3635 | 429.4474 | 368.6008 | 381.6602
4579.3635 | 429.5622 | 368.5915 | 381.6514
4580.3479 | 429.6665 | 368.5631 | 381.6559
4581.3635 | 429.7295 | 368.57 | 381.6562
4582.3479 | 429.7863 | 368.5499 | 381.6559
4583.3479 | 429.8674 | 368.5429 | 381.6566
4584.3635 | 429.906 | 368.5493 | 381.6559
4585.3479 | 429.9485 | 368.517 | 381.6579
4586.3635 | 429.8424 | 368.5229 | 381.6547
4587.3479 | 429.7353 | 368.5299 | 381.6434
4588.3479 | 429.7465 | 368.5042 | 381.6345
4589.3635 | 429.7643 | 368.5207 | 381.6272
4590.3635 | 429.77 | 368.503 | 381.6158
4591.3635 | 429.8506 | 368.5112 | 381.5991
4592.3635 | 429.9527 | 368.5094 | 381.5935
4593.3479 | 429.9113 | 368.4872 | 381.5837
4594.3479 | 429.8997 | 368.4977 | 381.5725
4595.3635 | 429.8575 | 368.4747 | 381.5654
4596.3479 | 429.9153 | 368.4833 | 381.5613
4597.3635 | 429.8422 | 368.4944 | 381.5546
4598.3635 | 429.7612 | 368.4772 | 381.56
4599.3635 | 429.6847 | 368.4897 | 381.5713
4600.3635 | 429.7022 | 368.4855 | 381.5675
4601.3635 | 429.6171 | 368.4803 | 381.5644
4602.3635 | 429.6144 | 368.4923 | 381.5555
4603.3635 | 429.6446 | 368.4781 | 381.5667
4604.3635 | 429.555 | 368.4791 | 381.5671
4605.3635 | 429.4226 | 368.4776 | 381.5706
4606.3479 | 429.276 | 368.4796 | 381.563
4607.3635 | 429.2325 | 368.489 | 381.5704
4608.3479 | 429.1611 | 368.4739 | 381.5641
4609.3635 | 429.0525 | 368.4695 | 381.5622
4610.3635 | 429.0123 | 368.4704 | 381.552
4611.3635 | 429.0282 | 368.4625 | 381.5503
4612.3635 | 429.0447 | 368.4702 | 381.5443
4613.3635 | 429.1102 | 368.4587 | 381.5337
4614.3635 | 429.0619 | 368.4646 | 381.5358
4615.3635 | 429.0304 | 368.4549 | 381.5375
4616.3635 | 429.1572 | 368.4413 | 381.5341
4617.3635 | 429.1577 | 368.4434 | 381.5276
4618.3635 | 429.0122 | 368.4242 | 381.5219
4619.3635 | 428.9788 | 368.4398 | 381.5183
4620.3635 | 428.952 | 368.4356 | 381.515
4621.3479 | 429.0118 | 368.4226 | 381.5124
4622.3635 | 428.9867 | 368.4424 | 381.517
4623.3479 | 429.0975 | 368.4317 | 381.5105
4624.3635 | 429.1829 | 368.4458 | 381.5043
4625.3635 | 429.246 | 368.4502 | 381.4953
4626.3635 | 429.3263 | 368.4502 | 381.4842
4627.3635 | 429.3528 | 368.4674 | 381.4872
4628.3635 | 429.3974 | 368.4616 | 381.4811
4629.3635 | 429.4654 | 368.463 | 381.4802
4630.3635 | 429.4019 | 368.4799 | 381.4806
4631.3635 | 429.3743 | 368.4841 | 381.4802
4632.3635 | 429.3313 | 368.4979 | 381.4838
4633.3635 | 429.3447 | 368.5018 | 381.4907
4634.3635 | 429.4849 | 368.4942 | 381.4942
4635.3635 | 429.5966 | 368.5058 | 381.4818
4636.3635 | 429.5705 | 368.4912 | 381.4748
4637.3635 | 429.5227 | 368.4951 | 381.4731
4638.3635 | 429.4624 | 368.4878 | 381.4606
4639.3635 | 429.4886 | 368.4956 | 381.4539
4640.3635 | 429.4794 | 368.5043 | 381.4469
4641.3635 | 429.4378 | 368.4905 | 381.4563
4642.3635 | 429.4902 | 368.5046 | 381.456
4643.3635 | 429.4509 | 368.5061 | 381.4469
4644.3635 | 429.4894 | 368.5164 | 381.4526
4645.3635 | 429.4711 | 368.5357 | 381.4584
4646.3635 | 429.4381 | 368.5333 | 381.4618
4647.3635 | 429.3869 | 368.5462 | 381.4556
4648.3635 | 429.2927 | 368.5599 | 381.4548
4649.3635 | 429.2962 | 368.5702 | 381.4466
4650.3635 | 429.3368 | 368.5892 | 381.4463
4651.3635 | 429.5093 | 368.5825 | 381.4477
4652.3635 | 429.6411 | 368.5896 | 381.4586
4653.3635 | 429.5865 | 368.6012 | 381.4704
4654.3635 | 429.5691 | 368.597 | 381.4776
4655.3635 | 429.6116 | 368.61 | 381.481
4656.3635 | 429.631 | 368.5963 | 381.4791
4657.3635 | 429.7614 | 368.617 | 381.4862
4658.3635 | 429.8019 | 368.6179 | 381.4919
4659.3635 | 429.7767 | 368.6283 | 381.4928
4660.3635 | 429.7565 | 368.6401 | 381.4927
4661.3635 | 429.7855 | 368.6348 | 381.502
4662.3635 | 429.7376 | 368.6334 | 381.5004
4663.3635 | 429.8099 | 368.6378 | 381.5108
4664.3635 | 429.8884 | 368.6247 | 381.5111
4665.3635 | 429.9021 | 368.6434 | 381.5076
4666.3479 | 429.8387 | 368.6318 | 381.5221
4667.3635 | 429.8737 | 368.6398 | 381.5281
4668.3635 | 429.7684 | 368.6242 | 381.5271
4669.3635 | 429.7776 | 368.6148 | 381.5262
4670.3635 | 429.906 | 368.6174 | 381.5254
4671.3635 | 429.8678 | 368.6135 | 381.5244
4672.3635 | 429.8828 | 368.6112 | 381.5167
4673.3635 | 429.8964 | 368.6125 | 381.5164
4674.3635 | 429.8344 | 368.6142 | 381.5124
4675.3635 | 429.7663 | 368.6206 | 381.509
4676.3635 | 429.7557 | 368.6247 | 381.4998
4677.3635 | 429.7385 | 368.6296 | 381.5081
4678.3479 | 429.7011 | 368.6332 | 381.5092
4679.3635 | 429.5787 | 368.6159 | 381.5112
4680.3635 | 429.5007 | 368.624 | 381.5193
4681.3479 | 429.3886 | 368.6204 | 381.5265
4682.3635 | 429.3809 | 368.6279 | 381.5374
4683.3479 | 429.4095 | 368.6364 | 381.5487
4684.3635 | 429.4523 | 368.6345 | 381.5671
4685.3635 | 429.5451 | 368.6493 | 381.5846
4686.3479 | 429.4463 | 368.6479 | 381.5905
4687.3635 | 429.4214 | 368.6534 | 381.5948
4688.3479 | 429.4851 | 368.6539 | 381.6053
4689.3635 | 429.4476 | 368.6508 | 381.6058
4690.3479 | 429.5044 | 368.6522 | 381.6163
4691.3635 | 429.6113 | 368.6414 | 381.6126
4692.3479 | 429.6887 | 368.6621 | 381.6139
4693.3635 | 429.7275 | 368.6431 | 381.6154
4694.3635 | 429.6739 | 368.6549 | 381.6127
4695.3635 | 429.6642 | 368.6577 | 381.613
4696.3635 | 429.6659 | 368.658 | 381.6267
4697.3635 | 429.7271 | 368.6552 | 381.6356
4698.3635 | 429.7879 | 368.6463 | 381.6333
4699.3635 | 429.6948 | 368.6756 | 381.6429
4700.3635 | 429.67 | 368.6788 | 381.6546
4701.3635 | 429.6884 | 368.6833 | 381.6632
4702.3635 | 429.7468 | 368.6951 | 381.6675
4703.3635 | 429.7742 | 368.696 | 381.6682
4704.3635 | 429.7113 | 368.7094 | 381.6755
4705.3635 | 429.7498 | 368.6989 | 381.6593
4706.3635 | 429.6491 | 368.7033 | 381.6651
4707.3635 | 429.591 | 368.7231 | 381.6624
4708.3635 | 429.5974 | 368.7208 | 381.6675
4709.3635 | 429.4762 | 368.7407 | 381.6763
4710.3635 | 429.3934 | 368.7429 | 381.6808
4711.3635 | 429.3172 | 368.7469 | 381.6905
4712.3635 | 429.3045 | 368.7519 | 381.702
4713.3635 | 429.2793 | 368.7447 | 381.7089
4714.3635 | 429.2518 | 368.7763 | 381.7218
4715.3635 | 429.1574 | 368.7709 | 381.7237
4716.3635 | 429.0704 | 368.778 | 381.7296
4717.3635 | 429.087 | 368.7856 | 381.7441
4718.3635 | 429.0437 | 368.8023 | 381.739
4719.3635 | 429.072 | 368.7986 | 381.7368
4720.3635 | 429.1463 | 368.8068 | 381.7299
4721.3635 | 429.1334 | 368.828 | 381.7213
4722.3635 | 429.1298 | 368.8222 | 381.711
4723.3635 | 429.1311 | 368.8294 | 381.705
4724.3635 | 429.2016 | 368.8424 | 381.6915
4725.3635 | 429.2867 | 368.833 | 381.6819
4726.3635 | 429.4151 | 368.8351 | 381.6912
4727.3635 | 429.3933 | 368.8326 | 381.6838
4728.3635 | 429.3822 | 368.8313 | 381.6786
4729.3635 | 429.3394 | 368.8407 | 381.6735
4730.3635 | 429.2984 | 368.8248 | 381.661
4731.3635 | 429.2536 | 368.8316 | 381.6574
4732.3635 | 429.1677 | 368.835 | 381.6605
4733.3635 | 429.1199 | 368.8286 | 381.6494
4734.3635 | 429.0413 | 368.8339 | 381.6444
4735.3635 | 429.0345 | 368.8331 | 381.6378
4736.3635 | 429.0155 | 368.8302 | 381.6295
4737.3635 | 429.1702 | 368.8334 | 381.6338
4738.3635 | 429.2834 | 368.8382 | 381.6209
4739.3635 | 429.3204 | 368.8408 | 381.6106
4740.3635 | 429.3735 | 368.8516 | 381.6071
4741.3635 | 429.3337 | 368.8624 | 381.6026
4742.3635 | 429.3654 | 368.8445 | 381.5991
4743.3635 | 429.3543 | 368.851 | 381.589
4744.3635 | 429.3936 | 368.862 | 381.5783
4745.3635 | 429.3239 | 368.8551 | 381.5822
4746.3635 | 429.2728 | 368.8656 | 381.5823
4747.3635 | 429.1551 | 368.854 | 381.5843
4748.3635 | 429.1514 | 368.8576 | 381.5938
4749.3635 | 429.1917 | 368.8579 | 381.571
4750.3635 | 429.1127 | 368.8551 | 381.5837
4751.3635 | 429.1273 | 368.8648 | 381.584
4752.3635 | 429.0799 | 368.8595 | 381.5893
4753.3635 | 429.1259 | 368.8657 | 381.5972
4754.3635 | 429.1792 | 368.8693 | 381.5982
4755.3635 | 429.1964 | 368.8488 | 381.6046
4756.3635 | 429.1683 | 368.8521 | 381.6053
4757.3635 | 429.1907 | 368.8378 | 381.6098
4758.3635 | 429.1596 | 368.833 | 381.5955
4759.3635 | 429.1277 | 368.8284 | 381.5991
4760.3635 | 429.1143 | 368.8178 | 381.6034
4761.3635 | 429.2349 | 368.8096 | 381.5935
4762.3635 | 429.3439 | 368.7933 | 381.5893
4763.3635 | 429.3265 | 368.7991 | 381.5835
4764.3635 | 429.3484 | 368.7918 | 381.578
4765.3635 | 429.3785 | 368.7913 | 381.5542
4766.3635 | 429.3636 | 368.803 | 381.5467
4767.3635 | 429.4957 | 368.7833 | 381.5416
4768.3635 | 429.4779 | 368.7958 | 381.5428
4769.3479 | 429.3711 | 368.7902 | 381.5408
4770.3635 | 429.3522 | 368.7939 | 381.554
4771.3635 | 429.3722 | 368.8012 | 381.5609
4772.3635 | 429.4219 | 368.7849 | 381.5636
4773.3635 | 429.5052 | 368.7926 | 381.569
4774.3635 | 429.5963 | 368.788 | 381.5796
4775.3635 | 429.7552 | 368.7923 | 381.5948
4776.3635 | 429.7127 | 368.7926 | 381.5933
4777.3635 | 429.7815 | 368.778 | 381.6041
4778.3635 | 429.7917 | 368.7923 | 381.6073
4779.3635 | 429.7436 | 368.7779 | 381.6035
4780.3635 | 429.7327 | 368.7626 | 381.6101
4781.3635 | 429.7634 | 368.7746 | 381.6081
4782.3635 | 429.7475 | 368.7629 | 381.6217
4783.3635 | 429.7641 | 368.7616 | 381.626
4784.3635 | 429.7647 | 368.7505 | 381.6263
4785.3635 | 429.9145 | 368.7395 | 381.6291
4786.3948 | 429.9237 | 368.7304 | 381.6336
4787.3635 | 429.9103 | 368.7284 | 381.6368
4788.3635 | 429.9783 | 368.7307 | 381.6427
4789.3635 | 430.0162 | 368.7118 | 381.6445
4790.3635 | 430.0901 | 368.7096 | 381.6482
4791.3635 | 429.9942 | 368.7019 | 381.6511
4792.3635 | 429.938 | 368.6967 | 381.6513
4793.3635 | 429.8382 | 368.6876 | 381.6612
4794.3635 | 429.8508 | 368.665 | 381.6708
4795.3635 | 429.986 | 368.6717 | 381.667
4796.3635 | 429.998 | 368.6609 | 381.674
4797.3635 | 429.9499 | 368.6448 | 381.6896
4798.3635 | 430.0271 | 368.6427 | 381.6939
4799.3635 | 430.0554 | 368.636 | 381.6908
4800.3635 | 429.9709 | 368.6439 | 381.6968
4801.3635 | 429.9644 | 368.6414 | 381.6962
4802.3635 | 430.0676 | 368.6272 | 381.6943
4803.3635 | 430.0165 | 368.6263 | 381.6986
4804.3635 | 429.9511 | 368.6293 | 381.6959
4805.3635 | 429.8851 | 368.6143 | 381.6863
4806.3479 | 429.8826 | 368.6129 | 381.6916
4807.3479 | 429.9888 | 368.6054 | 381.6814
4808.3479 | 429.8424 | 368.6251 | 381.6856
4809.3479 | 429.7788 | 368.6096 | 381.6828
4810.3479 | 429.8378 | 368.6061 | 381.677
4811.3479 | 429.7958 | 368.5984 | 381.6741
4812.3479 | 429.7404 | 368.5976 | 381.6728
4813.3479 | 429.8249 | 368.606 | 381.6706
4814.3479 | 429.8257 | 368.5929 | 381.6711
4815.3479 | 429.7866 | 368.5839 | 381.6809
4816.3479 | 429.6333 | 368.5899 | 381.6786
4817.3479 | 429.538 | 368.5847 | 381.6774
4818.3479 | 429.4114 | 368.593 | 381.6893
4819.3479 | 429.4215 | 368.5838 | 381.684
4820.3479 | 429.4591 | 368.5753 | 381.6837
4821.3479 | 429.336 | 368.5968 | 381.6791
4822.3479 | 429.305 | 368.5844 | 381.6826
4823.3479 | 429.2121 | 368.5924 | 381.6837
4824.3479 | 429.2733 | 368.5678 | 381.685
4825.3479 | 429.2744 | 368.5848 | 381.6988
4826.3479 | 429.34 | 368.5791 | 381.7047
4827.3479 | 429.3747 | 368.5701 | 381.7122
4828.3479 | 429.415 | 368.5695 | 381.7126
4829.3479 | 429.5177 | 368.5565 | 381.7203
4830.3479 | 429.5445 | 368.5568 | 381.7284
4831.3479 | 429.5517 | 368.5403 | 381.7211
4832.3479 | 429.5681 | 368.5294 | 381.7095
4833.3479 | 429.5132 | 368.531 | 381.7091
4834.3479 | 429.663 | 368.5115 | 381.7059
4835.3479 | 429.7642 | 368.5174 | 381.7061
4836.3479 | 429.6768 | 368.5172 | 381.7061
4837.3479 | 429.655 | 368.4985 | 381.711
4838.3479 | 429.6886 | 368.5142 | 381.7057
4839.3479 | 429.7652 | 368.508 | 381.7026
4840.3479 | 429.8045 | 368.4919 | 381.701
4841.3479 | 429.8087 | 368.5017 | 381.7006
4842.3479 | 429.8185 | 368.502 | 381.6949
4843.3635 | 429.7999 | 368.5075 | 381.6939
4844.3479 | 429.6546 | 368.507 | 381.6842
4845.3479 | 429.5963 | 368.504 | 381.6721
4846.3479 | 429.5566 | 368.5224 | 381.6648
4847.3479 | 429.5164 | 368.5124 | 381.6626
4848.3479 | 429.4301 | 368.5007 | 381.6695
4849.3479 | 429.3708 | 368.5231 | 381.6651
4850.3479 | 429.2003 | 368.5089 | 381.6689
4851.3479 | 429.1939 | 368.5226 | 381.6635
4852.3479 | 429.1825 | 368.5185 | 381.6608
4853.3479 | 429.2043 | 368.5286 | 381.6613
4854.3479 | 429.1541 | 368.5309 | 381.6611
4855.3479 | 429.096 | 368.5258 | 381.646
4856.3479 | 429.1126 | 368.5408 | 381.6461
4857.3479 | 429.04 | 368.5414 | 381.639
4858.3635 | 429.0007 | 368.5343 | 381.641
4859.3479 | 428.9728 | 368.5416 | 381.6256
4860.3479 | 428.8417 | 368.5272 | 381.6069
4861.3635 | 428.9114 | 368.5423 | 381.6199
4862.3479 | 428.9471 | 368.5313 | 381.6205
4863.3479 | 428.9219 | 368.5363 | 381.6078
4864.3635 | 429.0972 | 368.5442 | 381.608
4865.3479 | 429.0901 | 368.5328 | 381.603
4866.3479 | 429.1315 | 368.5341 | 381.6034
4867.3479 | 429.1756 | 368.5302 | 381.6031
4868.3479 | 429.1183 | 368.5278 | 381.5948
4869.3479 | 429.1216 | 368.5272 | 381.6006
4870.3479 | 429.1567 | 368.5312 | 381.5979
4871.3479 | 429.0815 | 368.5291 | 381.602
4872.3479 | 429.1087 | 368.53 | 381.6034
4873.3479 | 429.1314 | 368.5263 | 381.6003
4874.3479 | 429.2476 | 368.5212 | 381.5912
4875.3635 | 429.2943 | 368.515 | 381.5945
4876.3635 | 429.322 | 368.5155 | 381.5934
4877.3479 | 429.3349 | 368.5188 | 381.5928
4878.3479 | 429.4067 | 368.5042 | 381.5941
4879.3479 | 429.4704 | 368.5088 | 381.5872
4880.3635 | 429.5417 | 368.5109 | 381.5884
4881.3479 | 429.5324 | 368.5004 | 381.5672
4882.3479 | 429.502 | 368.4987 | 381.57
4883.3479 | 429.5566 | 368.5098 | 381.573
4884.3479 | 429.5482 | 368.4946 | 381.5759
4885.3635 | 429.4334 | 368.5121 | 381.5721
4886.3635 | 429.4536 | 368.492 | 381.5697
4887.3479 | 429.4699 | 368.5006 | 381.5645
4888.3479 | 429.45 | 368.5064 | 381.5648
4889.3479 | 429.4224 | 368.501 | 381.561
4890.3479 | 429.4465 | 368.515 | 381.5489
4891.3479 | 429.4038 | 368.5266 | 381.5585
4892.3479 | 429.4262 | 368.5227 | 381.5505
4893.3479 | 429.3717 | 368.5328 | 381.554
4894.3479 | 429.3573 | 368.5391 | 381.5483
4895.3479 | 429.336 | 368.5384 | 381.5546
4896.3479 | 429.3441 | 368.5432 | 381.5479
4897.3479 | 429.3656 | 368.5534 | 381.5421
4898.3479 | 429.3362 | 368.5669 | 381.5341
4899.3479 | 429.2562 | 368.56 | 381.5274
4900.3479 | 429.2671 | 368.57 | 381.5304
4901.3479 | 429.2673 | 368.5695 | 381.5249
4902.3479 | 429.1695 | 368.5716 | 381.5223
4903.3479 | 429.1322 | 368.5661 | 381.5172
4904.3479 | 429.1644 | 368.5713 | 381.5217
4905.3479 | 429.1304 | 368.5676 | 381.5251
4906.3479 | 429.0718 | 368.5621 | 381.5273
4907.3479 | 429.1321 | 368.5558 | 381.523
4908.3479 | 429.2202 | 368.5543 | 381.5186
4909.3479 | 429.1831 | 368.5459 | 381.52
4910.3479 | 429.2355 | 368.5503 | 381.5127
4911.3479 | 429.3531 | 368.5384 | 381.5056
4912.3479 | 429.3652 | 368.5259 | 381.5022
4913.3479 | 429.3168 | 368.5126 | 381.4953
4914.3479 | 429.2365 | 368.5149 | 381.4917
4915.3479 | 429.3716 | 368.5169 | 381.4941
4916.3479 | 429.5283 | 368.5174 | 381.4824
4917.3479 | 429.5654 | 368.5058 | 381.4822
4918.3479 | 429.4669 | 368.5108 | 381.4811
4919.3635 | 429.4347 | 368.4977 | 381.4778
4920.3479 | 429.5033 | 368.5038 | 381.4945
4921.3479 | 429.5783 | 368.4797 | 381.4918
4922.3479 | 429.5648 | 368.4697 | 381.4861
4923.3479 | 429.5131 | 368.4696 | 381.4922
4924.3635 | 429.439 | 368.4659 | 381.487
4925.3479 | 429.414 | 368.4536 | 381.4888
4926.3479 | 429.4986 | 368.4439 | 381.4827
4927.3479 | 429.5219 | 368.4368 | 381.4656
4928.3479 | 429.5341 | 368.4211 | 381.4536
4929.3479 | 429.5459 | 368.4152 | 381.4285
4930.3479 | 429.5337 | 368.4201 | 381.4062
4931.3479 | 429.598 | 368.4215 | 381.3987
4932.3479 | 429.4871 | 368.4186 | 381.3945
4933.3479 | 429.4075 | 368.4143 | 381.4017
4934.3479 | 429.3958 | 368.4092 | 381.3889
4935.3479 | 429.4194 | 368.4025 | 381.406
4936.3479 | 429.5193 | 368.4082 | 381.413
4937.3479 | 429.5208 | 368.3996 | 381.407
4938.3479 | 429.5723 | 368.4026 | 381.4054
4939.3635 | 429.5072 | 368.3981 | 381.4234
4940.3479 | 429.4998 | 368.3917 | 381.423
4941.3635 | 429.5121 | 368.3965 | 381.4252
4942.3635 | 429.4614 | 368.3957 | 381.4296
4943.3635 | 429.4578 | 368.4065 | 381.4363
4944.3635 | 429.5287 | 368.4112 | 381.4346
4945.3635 | 429.445 | 368.3985 | 381.4353
4946.3635 | 429.3594 | 368.4095 | 381.4293
4947.3635 | 429.4025 | 368.423 | 381.429
4948.3635 | 429.3839 | 368.4185 | 381.4401
4949.3635 | 429.2778 | 368.4246 | 381.4444
4950.3479 | 429.296 | 368.4226 | 381.4447
4951.3635 | 429.3204 | 368.4252 | 381.4407
4952.3635 | 429.4494 | 368.4252 | 381.4428
4953.3635 | 429.5191 | 368.4391 | 381.443
4954.3635 | 429.5408 | 368.4448 | 381.4301
4955.3635 | 429.5599 | 368.4468 | 381.4394
4956.3635 | 429.5578 | 368.4364 | 381.446
4957.3635 | 429.6074 | 368.4455 | 381.4406
4958.3635 | 429.7238 | 368.4323 | 381.4344
4959.3635 | 429.775 | 368.45 | 381.4292
4960.3635 | 429.7711 | 368.4641 | 381.4226
4961.3635 | 429.8862 | 368.4526 | 381.4089
4962.3635 | 429.8583 | 368.4668 | 381.4068
4963.3635 | 429.8301 | 368.4626 | 381.3897
4964.3635 | 429.7723 | 368.4612 | 381.3907
4965.3635 | 429.7397 | 368.4781 | 381.3777
4966.3635 | 429.7547 | 368.4782 | 381.3732
4967.3635 | 429.7487 | 368.4843 | 381.3777
4968.3635 | 429.6477 | 368.5063 | 381.3759
4969.3635 | 429.6147 | 368.5022 | 381.3721
4970.3635 | 429.5996 | 368.5217 | 381.3655
4971.3635 | 429.5939 | 368.5417 | 381.3596
4972.3635 | 429.5247 | 368.554 | 381.3687
4973.3635 | 429.4488 | 368.558 | 381.3689
4974.3635 | 429.4802 | 368.5727 | 381.3636
4975.3635 | 429.4667 | 368.5857 | 381.3673
4976.3635 | 429.4474 | 368.6186 | 381.3665
4977.3635 | 429.5502 | 368.6255 | 381.3777
4978.3635 | 429.6728 | 368.6476 | 381.3729
4979.3635 | 429.6698 | 368.6498 | 381.377
4980.3635 | 429.5979 | 368.6703 | 381.3853
4981.3635 | 429.6375 | 368.6788 | 381.3867
4982.3635 | 429.6364 | 368.6965 | 381.3992
4983.3635 | 429.5631 | 368.6879 | 381.4058
4984.3635 | 429.5736 | 368.7082 | 381.4104
4985.3635 | 429.6038 | 368.7091 | 381.4161
4986.3635 | 429.5822 | 368.7115 | 381.3906
4987.3635 | 429.6652 | 368.7102 | 381.4027
4988.3635 | 429.7153 | 368.6983 | 381.4076
4989.3635 | 429.7526 | 368.7062 | 381.4019
4990.3635 | 429.7656 | 368.7033 | 381.4071
4991.3635 | 429.8098 | 368.6992 | 381.4171
4992.3635 | 429.8204 | 368.6987 | 381.4245
4993.3635 | 429.8712 | 368.6866 | 381.4177
4994.3635 | 429.8726 | 368.6804 | 381.402
4995.3635 | 429.8482 | 368.6862 | 381.4109
4996.3635 | 429.8217 | 368.6679 | 381.4187
4997.3635 | 429.7789 | 368.6765 | 381.4211
4998.3635 | 429.7289 | 368.6661 | 381.4235
4999.3635 | 429.6279 | 368.6561 | 381.4214
5000.3479 | 429.5877 | 368.639 | 381.4268
5001.3635 | 429.4967 | 368.6374 | 381.4431
5002.3635 | 429.3691 | 368.6347 | 381.4438
5003.3635 | 429.4463 | 368.6134 | 381.4387
5004.3635 | 429.4223 | 368.6059 | 381.4444
5005.3635 | 429.4378 | 368.5981 | 381.4512
5006.3635 | 429.3902 | 368.603 | 381.4521
5007.3635 | 429.4209 | 368.585 | 381.457
5008.3635 | 429.382 | 368.5967 | 381.4617
5009.3635 | 429.3591 | 368.5866 | 381.4692
5010.3635 | 429.337 | 368.5785 | 381.4659
5011.3635 | 429.3855 | 368.5872 | 381.4768
5012.3635 | 429.4535 | 368.5854 | 381.4536
5013.3635 | 429.4875 | 368.5743 | 381.4395
5014.3635 | 429.4788 | 368.5724 | 381.4326
5015.3635 | 429.4343 | 368.5619 | 381.4362
5016.3635 | 429.4776 | 368.5702 | 381.4454
5017.3635 | 429.4728 | 368.5732 | 381.4409
5018.3635 | 429.4201 | 368.5507 | 381.4368
5019.3635 | 429.3586 | 368.563 | 381.438
5020.3635 | 429.3203 | 368.55 | 381.4287
5021.3635 | 429.3839 | 368.5339 | 381.4343
5022.3635 | 429.3258 | 368.5429 | 381.4177
5023.3635 | 429.3181 | 368.5365 | 381.4115
5024.3635 | 429.3257 | 368.5258 | 381.4104
5025.3635 | 429.3832 | 368.5219 | 381.4158
5026.3635 | 429.3207 | 368.5194 | 381.4178
5027.3635 | 429.2859 | 368.5211 | 381.4088
5028.3635 | 429.3265 | 368.5177 | 381.4122
5029.3635 | 429.2977 | 368.5017 | 381.4115
5030.3635 | 429.28 | 368.5021 | 381.4176
5031.3635 | 429.325 | 368.4968 | 381.4195
5032.3635 | 429.4734 | 368.4826 | 381.4207
5033.3635 | 429.5378 | 368.4814 | 381.4166
5034.3635 | 429.5807 | 368.4886 | 381.4168
5035.3635 | 429.7075 | 368.4829 | 381.4093
5036.3635 | 429.7424 | 368.4819 | 381.4135
5037.3635 | 429.7272 | 368.4669 | 381.4001
5038.3635 | 429.771 | 368.4557 | 381.3937
5039.3635 | 429.7689 | 368.4781 | 381.3829
5040.3635 | 429.798 | 368.4941 | 381.385
5041.3635 | 429.7302 | 368.4819 | 381.3779
5042.3635 | 429.6256 | 368.5018 | 381.3814
5043.3635 | 429.568 | 368.5011 | 381.381
5044.3635 | 429.5453 | 368.5093 | 381.3882
5045.3635 | 429.5993 | 368.5221 | 381.3894
5046.3635 | 429.5769 | 368.5182 | 381.3849
5047.3635 | 429.5574 | 368.5257 | 381.3871
5048.3635 | 429.5252 | 368.5163 | 381.3963
5049.3635 | 429.5498 | 368.5226 | 381.4013
5050.3635 | 429.7059 | 368.5332 | 381.4105
5051.3635 | 429.6927 | 368.5223 | 381.4057
5052.3635 | 429.8176 | 368.5329 | 381.4274
5053.3635 | 429.8072 | 368.5294 | 381.4332
5054.3635 | 429.8618 | 368.5408 | 381.4421
5055.3635 | 429.7781 | 368.548 | 381.4425
5056.3635 | 429.7629 | 368.5153 | 381.4525
5057.3635 | 429.8336 | 368.5503 | 381.4518
5058.3635 | 429.8212 | 368.552 | 381.456
5059.3635 | 429.8394 | 368.5442 | 381.4473
5060.3635 | 429.8872 | 368.5504 | 381.451
5061.3635 | 429.8513 | 368.551 | 381.4561
5062.3635 | 429.8531 | 368.5713 | 381.4549
5063.3635 | 430.0184 | 368.5711 | 381.4528
5064.3635 | 430.0498 | 368.576 | 381.4564
5065.3635 | 430.0605 | 368.5995 | 381.4472
5066.3635 | 430.0912 | 368.5898 | 381.4429
5067.3635 | 430.2057 | 368.6074 | 381.4444
5068.3635 | 430.2112 | 368.5984 | 381.44
5069.3635 | 430.1779 | 368.6162 | 381.4353
5070.3635 | 430.0727 | 368.6388 | 381.432
5071.3635 | 429.9055 | 368.6552 | 381.443
5072.3635 | 429.8239 | 368.6584 | 381.4568
5073.3635 | 429.9046 | 368.6648 | 381.4653
5074.3635 | 429.9761 | 368.681 | 381.4672
5075.3635 | 429.9293 | 368.6828 | 381.4676
5076.3635 | 429.841 | 368.6954 | 381.4677
5077.3635 | 429.8532 | 368.7129 | 381.4813
5078.3635 | 429.8218 | 368.7226 | 381.4923
5079.3635 | 429.7111 | 368.7357 | 381.505
5080.3635 | 429.5893 | 368.7564 | 381.5132
5081.3635 | 429.5197 | 368.7609 | 381.5271
5082.3635 | 429.51 | 368.7882 | 381.5257
5083.3635 | 429.436 | 368.7946 | 381.5198
5084.3635 | 429.3754 | 368.799 | 381.5367
5085.3635 | 429.3877 | 368.806 | 381.5421
5086.3635 | 429.2586 | 368.8178 | 381.5502
5087.3635 | 429.1829 | 368.8434 | 381.552
5088.3635 | 429.1559 | 368.836 | 381.5496
5089.3635 | 429.2383 | 368.8397 | 381.548
5090.3635 | 429.3114 | 368.8433 | 381.5453
5091.3635 | 429.3487 | 368.8558 | 381.5288
5092.3635 | 429.3447 | 368.8458 | 381.522
5093.3479 | 429.2475 | 368.8377 | 381.5184
5094.3635 | 429.2961 | 368.8465 | 381.512
5095.3635 | 429.2365 | 368.8535 | 381.5104
5096.3635 | 429.2654 | 368.8581 | 381.5125
5097.3635 | 429.255 | 368.864 | 381.5087
5098.3635 | 429.3437 | 368.8611 | 381.5118
5099.3635 | 429.3703 | 368.8823 | 381.502
5100.3635 | 429.4079 | 368.8834 | 381.5063
5101.3635 | 429.3421 | 368.8967 | 381.5023
5102.3635 | 429.4077 | 368.8903 | 381.5032
5103.3635 | 429.523 | 368.9044 | 381.5155
5104.3635 | 429.597 | 368.9247 | 381.5225
5105.3635 | 429.5947 | 368.9083 | 381.5311
5106.3479 | 429.6361 | 368.9195 | 381.5371
5107.3479 | 429.763 | 368.9355 | 381.534
5108.3479 | 429.7715 | 368.9339 | 381.5401
5109.3479 | 429.6509 | 368.9513 | 381.5455
5110.3479 | 429.6361 | 368.9551 | 381.5427
5111.3479 | 429.6338 | 368.9778 | 381.5533
5112.3479 | 429.6272 | 368.9724 | 381.5597
5113.3635 | 429.5696 | 368.9898 | 381.5612
5114.3479 | 429.6188 | 368.9896 | 381.5581
5115.3948 | 429.613 | 368.9985 | 381.557
5116.3479 | 429.6277 | 368.9941 | 381.5678
5117.3479 | 429.7708 | 368.9815 | 381.5602
5118.3479 | 429.8703 | 368.9958 | 381.5649
5119.3479 | 429.8132 | 368.9841 | 381.5632
5120.3479 | 429.7106 | 368.9798 | 381.5541
5121.3479 | 429.6785 | 368.9811 | 381.5496
5122.3479 | 429.7162 | 368.9801 | 381.5375
5123.3479 | 429.638 | 368.9656 | 381.5233
5124.3479 | 429.5781 | 368.9726 | 381.5034
5125.3479 | 429.5888 | 368.9566 | 381.4948
5126.3479 | 429.5686 | 368.9532 | 381.4829
5127.3479 | 429.5963 | 368.9563 | 381.4741
5128.3479 | 429.6484 | 368.9589 | 381.4728
5129.3635 | 429.6544 | 368.9551 | 381.455
5130.3479 | 429.621 | 368.9461 | 381.4487
5131.3479 | 429.6929 | 368.9421 | 381.4508
5132.3479 | 429.7234 | 368.9324 | 381.455
5133.3479 | 429.8165 | 368.9259 | 381.4521
5134.3479 | 429.7564 | 368.9317 | 381.4391
5135.3479 | 429.748 | 368.9146 | 381.4356
5136.3479 | 429.7131 | 368.9236 | 381.4448
5137.3479 | 429.6646 | 368.9168 | 381.4541
5138.3479 | 429.5719 | 368.9057 | 381.468
5139.3479 | 429.6108 | 368.8977 | 381.4846
5140.3479 | 429.6566 | 368.9008 | 381.4746
5141.3479 | 429.5138 | 368.8952 | 381.4683
5142.3479 | 429.4963 | 368.8731 | 381.4485
5143.3479 | 429.5073 | 368.8868 | 381.4441
5144.3479 | 429.4438 | 368.8687 | 381.4474
5145.3479 | 429.5045 | 368.8715 | 381.4363
5146.3479 | 429.5969 | 368.8666 | 381.4244
5147.3479 | 429.6371 | 368.8422 | 381.4166
5148.3479 | 429.6303 | 368.8512 | 381.4179
5149.3479 | 429.7264 | 368.8269 | 381.4252
5150.3479 | 429.745 | 368.8283 | 381.4322
5151.3479 | 429.6981 | 368.8228 | 381.4428
5152.3479 | 429.6039 | 368.8017 | 381.4496
5153.3479 | 429.5746 | 368.7949 | 381.4539
5154.3479 | 429.6142 | 368.7862 | 381.4568
5155.3479 | 429.6204 | 368.7907 | 381.4574
5156.3479 | 429.5802 | 368.7654 | 381.4426
5157.3479 | 429.5729 | 368.7771 | 381.4214
5158.3635 | 429.6279 | 368.7736 | 381.3952
5159.3479 | 429.5984 | 368.7544 | 381.3768
5160.3479 | 429.5562 | 368.7739 | 381.3656
5161.3479 | 429.5767 | 368.7576 | 381.3374
5162.3479 | 429.515 | 368.7463 | 381.342
5163.3479 | 429.4965 | 368.7522 | 381.3433
5164.3635 | 429.4908 | 368.736 | 381.348
5165.3479 | 429.386 | 368.7528 | 381.3648
5166.3479 | 429.4724 | 368.7386 | 381.3728
5167.3479 | 429.4829 | 368.7378 | 381.34
5168.3635 | 429.3952 | 368.7272 | 381.3116
5169.3479 | 429.489 | 368.7275 | 381.3055
5170.3479 | 429.6186 | 368.7408 | 381.2977
5171.3479 | 429.676 | 368.7298 | 381.3005
5172.3479 | 429.616 | 368.7406 | 381.3007
5173.3479 | 429.5645 | 368.7149 | 381.3126
5174.3479 | 429.4908 | 368.7166 | 381.3248
5175.3479 | 429.62 | 368.7315 | 381.3372
5176.3479 | 429.7134 | 368.7163 | 381.3527
5177.3479 | 429.6068 | 368.7298 | 381.3624
5178.3635 | 429.4112 | 368.719 | 381.3671
5179.3479 | 429.353 | 368.7197 | 381.3562
5180.3479 | 429.2787 | 368.728 | 381.364
5181.3479 | 429.2965 | 368.7161 | 381.3737
5182.3479 | 429.333 | 368.7275 | 381.383
5183.3479 | 429.2694 | 368.715 | 381.3891
5184.3479 | 429.2229 | 368.729 | 381.4011
5185.3479 | 429.168 | 368.7171 | 381.4202
5186.3479 | 429.2239 | 368.7117 | 381.4171
5187.3479 | 429.1863 | 368.7106 | 381.4199
5188.3479 | 429.193 | 368.7089 | 381.4288
5189.3479 | 429.1353 | 368.7192 | 381.4366
5190.3479 | 429.0111 | 368.7069 | 381.4435
5191.3479 | 428.931 | 368.6978 | 381.4479
5192.3479 | 428.9886 | 368.7159 | 381.4531
5193.3479 | 429.0181 | 368.6923 | 381.4574
5194.3479 | 428.9422 | 368.7219 | 381.4692
5195.3479 | 428.9037 | 368.7055 | 381.4764
5196.3479 | 428.8611 | 368.6947 | 381.4822
5197.3479 | 428.8129 | 368.7125 | 381.4887
5198.3479 | 428.8586 | 368.6984 | 381.4825
5199.3479 | 428.9653 | 368.696 | 381.4787
5200.3479 | 429.0212 | 368.686 | 381.4816
5201.3479 | 428.9431 | 368.6849 | 381.4883
5202.3479 | 428.9719 | 368.6795 | 381.4936
5203.3479 | 429.0094 | 368.6545 | 381.5009
5204.3479 | 429.1246 | 368.6699 | 381.4889
5205.3479 | 429.2872 | 368.6606 | 381.4905
5206.3479 | 429.3069 | 368.6539 | 381.4759
5207.3479 | 429.2894 | 368.6568 | 381.4475
5208.3635 | 429.3464 | 368.642 | 381.4289
5209.3479 | 429.2983 | 368.6441 | 381.4008
5210.3479 | 429.2937 | 368.6398 | 381.3829
5211.3479 | 429.1058 | 368.6463 | 381.3673
5212.3479 | 429.0374 | 368.6452 | 381.365
5213.3479 | 429.1792 | 368.6429 | 381.3677
5214.3479 | 429.3251 | 368.6522 | 381.3649
5215.3479 | 429.3004 | 368.6438 | 381.3727
5216.3479 | 429.2393 | 368.6479 | 381.3745
5217.3479 | 429.0878 | 368.6503 | 381.3855
5218.3479 | 429.1198 | 368.6503 | 381.3916
5219.3479 | 429.1422 | 368.6585 | 381.393
5220.3479 | 429.2901 | 368.6755 | 381.3893
5221.3479 | 429.3994 | 368.6799 | 381.3892
5222.3479 | 429.2818 | 368.685 | 381.3873
5223.3479 | 429.2589 | 368.6815 | 381.3874
5224.3479 | 429.2209 | 368.6956 | 381.3834
5225.3479 | 429.1826 | 368.6936 | 381.3737
5226.3479 | 429.1687 | 368.6967 | 381.3708
5227.3479 | 429.2488 | 368.718 | 381.3586
5228.3479 | 429.2749 | 368.7129 | 381.3512
5229.3479 | 429.3074 | 368.7364 | 381.3477
5230.3635 | 429.3049 | 368.7338 | 381.3392
5231.3635 | 429.4001 | 368.7228 | 381.3361
5232.3479 | 429.3908 | 368.7126 | 381.3355
5233.3479 | 429.286 | 368.7253 | 381.3354
5234.3635 | 429.2616 | 368.7327 | 381.3367
5235.3635 | 429.3479 | 368.7191 | 381.3327
5236.3635 | 429.333 | 368.6971 | 381.3091
5237.3635 | 429.3004 | 368.6973 | 381.2928
5238.3635 | 429.2339 | 368.6984 | 381.2873
5239.3635 | 429.2027 | 368.6971 | 381.2885
5240.3635 | 429.1761 | 368.6967 | 381.2931
5241.3635 | 429.2205 | 368.6894 | 381.2815
5242.3635 | 429.2009 | 368.6936 | 381.2862
5243.3635 | 429.2348 | 368.6861 | 381.2889
5244.3635 | 429.2093 | 368.6872 | 381.2847
5245.3635 | 429.1212 | 368.6925 | 381.2819
5246.3635 | 429.1128 | 368.6796 | 381.2874
5247.3635 | 429.0633 | 368.691 | 381.2972
5248.3635 | 428.9918 | 368.7009 | 381.2886
5249.3635 | 429.0308 | 368.7088 | 381.293
5250.3635 | 429.0447 | 368.7024 | 381.2879
5251.3635 | 428.9796 | 368.7136 | 381.2966
5252.3635 | 428.8905 | 368.7145 | 381.3046
5253.3635 | 428.8659 | 368.7263 | 381.3081
5254.3635 | 428.8372 | 368.7203 | 381.3209
5255.3635 | 428.9073 | 368.7212 | 381.328
5256.3479 | 429.0268 | 368.7291 | 381.3164
5257.3635 | 428.9977 | 368.7351 | 381.3013
5258.3635 | 429.0885 | 368.7456 | 381.2891
5259.3635 | 429.0827 | 368.7377 | 381.2683
5260.3635 | 429.0544 | 368.7393 | 381.2593
5261.3635 | 429.0891 | 368.7257 | 381.2468
5262.3635 | 429.1689 | 368.7148 | 381.2276
5263.3479 | 429.1398 | 368.7204 | 381.2191
5264.3635 | 429.2353 | 368.7169 | 381.2013
5265.3635 | 429.3066 | 368.7217 | 381.1873
5266.3635 | 429.3555 | 368.7134 | 381.1858
5267.3635 | 429.3211 | 368.7013 | 381.1753
5268.3635 | 429.2917 | 368.7065 | 381.1639
5269.3635 | 429.3748 | 368.7051 | 381.1553
5270.3635 | 429.4118 | 368.7015 | 381.1512
5271.3635 | 429.2584 | 368.7043 | 381.1473
5272.3635 | 429.1627 | 368.6945 | 381.1436
5273.3635 | 429.2398 | 368.7005 | 381.1503
5274.3635 | 429.3371 | 368.6948 | 381.1556
5275.3635 | 429.3701 | 368.6857 | 381.1649
5276.3635 | 429.4384 | 368.6882 | 381.1666
5277.3635 | 429.5134 | 368.6695 | 381.166
5278.3635 | 429.5341 | 368.668 | 381.1701
5279.3635 | 429.6149 | 368.6632 | 381.1672
5280.3635 | 429.6558 | 368.664 | 381.1755
5281.3635 | 429.6804 | 368.6512 | 381.1819
5282.3635 | 429.5889 | 368.663 | 381.1937
5283.3635 | 429.5544 | 368.6442 | 381.206
5284.3479 | 429.6334 | 368.6387 | 381.2213
5285.3635 | 429.5737 | 368.6434 | 381.2173
5286.3635 | 429.7113 | 368.6485 | 381.2139
5287.3635 | 429.7098 | 368.6407 | 381.2249
5288.3635 | 429.7185 | 368.6288 | 381.2192
5289.3635 | 429.684 | 368.6395 | 381.2209
5290.3635 | 429.6391 | 368.6321 | 381.2257
5291.3635 | 429.5825 | 368.6047 | 381.2246
5292.3635 | 429.5727 | 368.6139 | 381.2268
5293.3635 | 429.5423 | 368.6124 | 381.2395
5294.3635 | 429.5808 | 368.6042 | 381.2449
5295.3635 | 429.6554 | 368.6039 | 381.2397
5296.3635 | 429.7053 | 368.5932 | 381.2457
5297.3635 | 429.6751 | 368.584 | 381.2584
5298.3635 | 429.6091 | 368.5696 | 381.2763
5299.3635 | 429.6587 | 368.5652 | 381.2797
5300.3635 | 429.5959 | 368.5525 | 381.2922
5301.3635 | 429.6527 | 368.5451 | 381.303
5302.3635 | 429.77 | 368.5409 | 381.3184
5303.3635 | 429.7709 | 368.5493 | 381.3189
5304.3635 | 429.6767 | 368.5338 | 381.3179
5305.3635 | 429.5872 | 368.5431 | 381.3134
5306.3635 | 429.4978 | 368.5428 | 381.3124
5307.3635 | 429.4917 | 368.5441 | 381.3137
5308.3635 | 429.487 | 368.5492 | 381.3027
5309.3635 | 429.5221 | 368.5448 | 381.2985
5310.3635 | 429.5141 | 368.5488 | 381.2866
5311.3635 | 429.5446 | 368.5501 | 381.2705
5312.3635 | 429.4926 | 368.5473 | 381.2677
5313.3635 | 429.5004 | 368.5615 | 381.2726
5314.3635 | 429.5414 | 368.5607 | 381.2765
5315.3635 | 429.4837 | 368.557 | 381.2758
5316.3635 | 429.4599 | 368.5666 | 381.2698
5317.3635 | 429.472 | 368.5641 | 381.257
5318.3635 | 429.4288 | 368.5728 | 381.2417
5319.3635 | 429.3929 | 368.5609 | 381.2421
5320.3635 | 429.4143 | 368.5651 | 381.2388
5321.3479 | 429.4362 | 368.5698 | 381.2451
5322.3635 | 429.4948 | 368.5562 | 381.2455
5323.3635 | 429.5377 | 368.5646 | 381.2364
5324.3635 | 429.6014 | 368.5638 | 381.2411
5325.3635 | 429.557 | 368.551 | 381.2436
5326.3635 | 429.5149 | 368.5505 | 381.2555
5327.3635 | 429.5281 | 368.5584 | 381.2682
5328.3635 | 429.5478 | 368.5513 | 381.2789
5329.3635 | 429.5203 | 368.5562 | 381.2931
5330.3635 | 429.4688 | 368.548 | 381.2978
5331.3635 | 429.3782 | 368.5421 | 381.3144
5332.3635 | 429.3991 | 368.53 | 381.3223
5333.3635 | 429.4825 | 368.5359 | 381.3253
5334.3635 | 429.459 | 368.5426 | 381.3177
5335.3635 | 429.5321 | 368.5367 | 381.3136
5336.3635 | 429.5452 | 368.5346 | 381.3192
5337.3635 | 429.4898 | 368.526 | 381.3251
5338.3635 | 429.5521 | 368.5237 | 381.3345
5339.3479 | 429.7215 | 368.5285 | 381.3393
5340.3635 | 429.7905 | 368.5022 | 381.3451
5341.3635 | 429.7884 | 368.519 | 381.3501
5342.3635 | 429.7424 | 368.5144 | 381.369
5343.3635 | 429.661 | 368.5123 | 381.3816
5344.3635 | 429.6876 | 368.5156 | 381.387
5345.3635 | 429.697 | 368.5059 | 381.3883
5346.3635 | 429.7618 | 368.5091 | 381.3953
5347.3635 | 429.8423 | 368.5166 | 381.39
5348.3635 | 429.878 | 368.5009 | 381.3957
5349.3635 | 430.0024 | 368.5175 | 381.3964
5350.3635 | 429.9573 | 368.5153 | 381.4103
5351.3635 | 429.9648 | 368.5169 | 381.4119
5352.3635 | 429.9473 | 368.5168 | 381.4199
5353.3635 | 429.8907 | 368.5069 | 381.4192
5354.3635 | 429.8266 | 368.4988 | 381.3727
5355.3635 | 429.8323 | 368.5065 | 381.3638
5356.3635 | 429.7609 | 368.5037 | 381.343
5357.3635 | 429.7024 | 368.4971 | 381.3377
5358.3635 | 429.6017 | 368.4921 | 381.3237
5359.3635 | 429.6291 | 368.4962 | 381.3303
5360.3635 | 429.5372 | 368.4989 | 381.3321
5361.3635 | 429.5574 | 368.4951 | 381.3453
5362.3635 | 429.4517 | 368.4912 | 381.3586
5363.3635 | 429.4148 | 368.4915 | 381.362
5364.3635 | 429.3519 | 368.4875 | 381.3415
5365.3635 | 429.3563 | 368.5002 | 381.3388
5366.3635 | 429.3056 | 368.4808 | 381.3217
5367.3635 | 429.3588 | 368.5 | 381.3381
5368.3635 | 429.4393 | 368.5013 | 381.3199
5369.3635 | 429.4818 | 368.4859 | 381.3207
5370.3635 | 429.419 | 368.4922 | 381.3118
5371.3635 | 429.4727 | 368.4764 | 381.3157
5372.3635 | 429.4951 | 368.4835 | 381.3153
5373.3635 | 429.53 | 368.487 | 381.3224
5374.3635 | 429.5062 | 368.4759 | 381.3261
5375.3635 | 429.6313 | 368.4654 | 381.3306
5376.3635 | 429.6753 | 368.4552 | 381.3326
5377.3635 | 429.7039 | 368.4534 | 381.3304
5378.3635 | 429.7655 | 368.4477 | 381.3437
5379.3635 | 429.829 | 368.4368 | 381.3576
5380.3635 | 429.8105 | 368.4242 | 381.369
5381.3635 | 429.9697 | 368.4257 | 381.3897
5382.3635 | 429.993 | 368.4241 | 381.3968
5383.3635 | 429.9347 | 368.4243 | 381.3974
5384.3635 | 429.8131 | 368.4255 | 381.3762
5385.3635 | 429.7642 | 368.424 | 381.3676
5386.3635 | 429.7714 | 368.4289 | 381.3668
5387.3635 | 429.8537 | 368.4268 | 381.3548
5388.3635 | 429.8584 | 368.4384 | 381.348
5389.3635 | 429.8477 | 368.4396 | 381.3529
5390.3479 | 429.8909 | 368.4526 | 381.3481
5391.3479 | 429.8611 | 368.4523 | 381.3304
5392.3479 | 429.7988 | 368.4627 | 381.3184
5393.3479 | 429.788 | 368.4758 | 381.3078
5394.3479 | 429.6964 | 368.4882 | 381.2806
5395.3635 | 429.531 | 368.4889 | 381.2568
5396.3479 | 429.5688 | 368.4894 | 381.2364
5397.3479 | 429.6543 | 368.4895 | 381.2268
5398.3479 | 429.7668 | 368.4962 | 381.2158
5399.3479 | 429.7457 | 368.4981 | 381.2175
5400.3635 | 429.7401 | 368.5021 | 381.1913
5401.3479 | 429.8799 | 368.5108 | 381.1839
5402.3479 | 430.5064 | 368.5105 | 381.1832
5403.3479 | 432.03 | 368.528 | 381.1805
5404.3479 | 434.2407 | 368.5232 | 381.1884
5405.3479 | 436.9401 | 368.5173 | 381.1847
5406.3479 | 440.0521 | 368.5434 | 381.1943
5407.3479 | 443.298 | 368.554 | 381.2197
5408.3479 | 446.7293 | 368.5666 | 381.2611
5409.3479 | 450.1437 | 368.5852 | 381.3142
5410.3479 | 453.2347 | 368.5986 | 381.3926
5411.3479 | 455.9427 | 368.6262 | 381.4852
5412.3479 | 458.2393 | 368.645 | 381.5873
5413.3479 | 460.0282 | 368.6797 | 381.7242
5414.3479 | 461.4075 | 368.7169 | 381.8955
5415.3479 | 462.4945 | 368.757 | 382.0668
5416.3479 | 463.3043 | 368.8271 | 382.2718
5417.3479 | 463.9856 | 368.9061 | 382.4601
5418.3635 | 464.3756 | 368.9817 | 382.6706
5419.3479 | 464.5081 | 369.0668 | 382.8983
5420.3479 | 464.4819 | 369.1717 | 383.136
5421.3479 | 464.4126 | 369.2729 | 383.376
5422.3479 | 464.0774 | 369.3986 | 383.6149
5423.3479 | 463.6369 | 369.5201 | 383.8583
5424.3479 | 463.3676 | 369.6446 | 384.1189
5425.3479 | 463.0515 | 369.7801 | 384.3367
5426.3479 | 462.5961 | 369.9188 | 384.5658
5427.3479 | 462.1567 | 370.052 | 384.7967
5428.3479 | 461.6221 | 370.2038 | 385.0333
5429.3479 | 461.1341 | 370.3472 | 385.2709
5430.3635 | 460.6872 | 370.4834 | 385.4895
5431.3479 | 460.194 | 370.6414 | 385.7164
5432.3479 | 459.5585 | 370.784 | 385.9305
5433.3479 | 459.099 | 370.948 | 386.1377
5434.3479 | 458.5783 | 371.0897 | 386.3332
5435.3479 | 457.9994 | 371.2411 | 386.5221
5436.3479 | 457.7177 | 371.404 | 386.7121
5437.3479 | 457.3351 | 371.5427 | 386.8992
5438.3479 | 457.0221 | 371.6944 | 386.9978
5439.3479 | 456.7875 | 371.8457 | 387.1807
5440.3479 | 456.4209 | 371.9988 | 387.3475
5441.3635 | 456.109 | 372.1406 | 387.5146
5442.3479 | 455.8846 | 372.2755 | 387.6738
5443.3479 | 455.5841 | 372.4165 | 387.8379
5444.3479 | 455.3328 | 372.5326 | 387.9788
5445.3479 | 455.1369 | 372.6612 | 388.1137
5446.3479 | 454.997 | 372.787 | 388.2508
5447.3479 | 454.738 | 372.9111 | 388.37
5448.3479 | 454.5706 | 373.0336 | 388.4853
5449.3479 | 454.5142 | 373.1385 | 388.576
5450.3635 | 454.3866 | 373.2667 | 388.6624
5451.3479 | 454.3626 | 373.3705 | 388.7114
5452.3479 | 454.2786 | 373.4736 | 388.7887
5453.3479 | 454.207 | 373.5957 | 388.8791
5454.3479 | 454.1445 | 373.6926 | 388.961
5455.3479 | 454.1927 | 373.7926 | 389.052
5456.3479 | 454.3143 | 373.8952 | 389.1266
5457.3479 | 454.3102 | 373.999 | 389.2002
5458.3479 | 454.191 | 374.1262 | 389.2744
5459.3479 | 454.1377 | 374.2103 | 389.3567
5460.3635 | 453.9982 | 374.3146 | 389.4389
5461.3479 | 453.8332 | 374.4084 | 389.5209
5462.3635 | 453.8282 | 374.5056 | 389.5893
5463.3479 | 453.9502 | 374.6069 | 389.6749
5464.3635 | 454.0912 | 374.6905 | 389.7612
5465.3635 | 454.1468 | 374.7885 | 389.775
5466.3479 | 454.2435 | 374.8744 | 389.8492
5467.3479 | 454.2396 | 374.9487 | 389.9357
5468.3635 | 454.218 | 375.0417 | 390.0394
5469.3479 | 454.2335 | 375.1274 | 390.1284
5470.3479 | 454.3469 | 375.2125 | 390.1834
5471.3479 | 454.4138 | 375.2932 | 390.2762
5472.3635 | 454.398 | 375.3654 | 390.3516
5473.3479 | 454.3502 | 375.458 | 390.4487
5474.3479 | 454.3344 | 375.5249 | 390.5637
5475.3635 | 454.3745 | 375.6109 | 390.6382
5476.3479 | 454.3078 | 375.695 | 390.7113
5477.3635 | 454.3593 | 375.7678 | 390.7803
5478.3479 | 454.3474 | 375.8524 | 390.8234
5479.3635 | 454.3505 | 375.9306 | 390.8893
5480.3635 | 454.219 | 376.0184 | 390.9644
5481.3635 | 454.2483 | 376.1036 | 391.0367
5482.3635 | 454.402 | 376.1767 | 391.1109
5483.3635 | 454.475 | 376.2629 | 391.1849
5484.3635 | 454.4681 | 376.3596 | 391.2587
5485.3635 | 454.3917 | 376.4451 | 391.3488
5486.3479 | 454.3776 | 376.5237 | 391.4128
5487.3635 | 454.3657 | 376.5849 | 391.4707
5488.3635 | 454.3982 | 376.6833 | 391.5491
5489.3635 | 454.4056 | 376.7594 | 391.6217
5490.3635 | 454.4025 | 376.8296 | 391.6883
5491.3635 | 454.3669 | 376.9075 | 391.764
5492.3635 | 454.4234 | 376.9824 | 391.7906
5493.3635 | 454.4226 | 377.0649 | 391.8358
5494.3635 | 454.3604 | 377.1388 | 391.8958
5495.3635 | 454.2308 | 377.2143 | 391.9636
5496.3635 | 454.3027 | 377.2865 | 392.0297
5497.3635 | 454.2297 | 377.3603 | 392.0908
5498.3635 | 454.1763 | 377.4491 | 392.1348
5499.3479 | 453.998 | 377.5206 | 392.1729
5500.3635 | 453.8586 | 377.6117 | 392.2142
5501.3635 | 453.7781 | 377.6916 | 392.258
5502.3635 | 453.7939 | 377.7726 | 392.3169
5503.3635 | 453.9259 | 377.8447 | 392.3612
5504.3635 | 453.9052 | 377.9255 | 392.3873
5505.3479 | 453.8943 | 377.9898 | 392.4356
5506.3635 | 453.8978 | 378.0755 | 392.4754
5507.3635 | 453.8935 | 378.1478 | 392.5345
5508.3635 | 453.8769 | 378.2259 | 392.5959
5509.3635 | 453.9522 | 378.295 | 392.6576
5510.3635 | 453.9621 | 378.3701 | 392.6929
5511.3635 | 453.9551 | 378.4687 | 392.7483
5512.3635 | 454.0146 | 378.5153 | 392.8034
5513.3635 | 453.865 | 378.6017 | 392.8647
5514.3635 | 453.9442 | 378.6625 | 392.9404
5515.3635 | 453.9674 | 378.7391 | 393.0125
5516.3635 | 453.9561 | 378.8086 | 393.0565
5517.3635 | 453.8795 | 378.8785 | 393.1075
5518.3635 | 453.8891 | 378.9543 | 393.1809
5519.3635 | 453.8251 | 379.0133 | 393.2174
5520.3635 | 453.8565 | 379.076 | 393.2732
5521.3635 | 453.9593 | 379.1446 | 393.3387
5522.3635 | 454.048 | 379.2119 | 393.3936
5523.3635 | 454.1061 | 379.2829 | 393.4181
5524.3635 | 454.1387 | 379.3493 | 393.435
5525.3635 | 454.1908 | 379.4034 | 393.5202
5526.3635 | 454.1445 | 379.4835 | 393.5945
5527.3635 | 454.1089 | 379.5343 | 393.6585
5528.3635 | 454.1597 | 379.6065 | 393.7213
5529.3635 | 454.1819 | 379.6471 | 393.7591
5530.3635 | 454.1519 | 379.7238 | 393.7886
5531.3635 | 454.1398 | 379.7834 | 393.8515
5532.3635 | 454.1611 | 379.8519 | 393.8991
5533.3635 | 454.178 | 379.9078 | 393.9551
5534.3635 | 454.1748 | 379.9609 | 394.0004
5535.3635 | 454.2313 | 380.0207 | 394.0507
5536.3635 | 454.2537 | 380.077 | 394.0556
5537.3635 | 454.2541 | 380.1315 | 394.1077
5538.3635 | 454.2115 | 380.2085 | 394.1551
5539.3635 | 454.2461 | 380.2497 | 394.1938
5540.3635 | 454.2375 | 380.3085 | 394.2321
5541.3635 | 454.2411 | 380.364 | 394.2822
5542.3635 | 454.2561 | 380.4153 | 394.3312
5543.3635 | 454.2861 | 380.4889 | 394.3981
5544.3635 | 454.3118 | 380.5485 | 394.4571
5545.3635 | 454.2316 | 380.6022 | 394.5044
5546.3635 | 454.1466 | 380.677 | 394.5525
5547.3635 | 454.201 | 380.725 | 394.5975
5548.3635 | 454.1676 | 380.7914 | 394.6438
5549.3635 | 454.0975 | 380.8435 | 394.6783
5550.3635 | 453.9645 | 380.9015 | 394.7302
5551.3635 | 453.9358 | 380.9766 | 394.7552
5552.3635 | 453.7933 | 381.0218 | 394.8125
5553.3635 | 453.7837 | 381.0748 | 394.8477
5554.3635 | 453.6612 | 381.1445 | 394.9115
5555.3635 | 453.7369 | 381.1944 | 394.9518
5556.3635 | 453.8544 | 381.27 | 394.993
5557.3635 | 453.9105 | 381.3196 | 395.0541
5558.3635 | 453.9095 | 381.3779 | 395.1061
5559.3635 | 453.9081 | 381.4349 | 395.1678
5560.3635 | 453.92 | 381.4948 | 395.2121
5561.3635 | 453.8999 | 381.5504 | 395.2523
5562.3635 | 453.865 | 381.6078 | 395.3037
5563.3635 | 453.9078 | 381.6632 | 395.3506
5564.3635 | 453.9849 | 381.7221 | 395.4008
5565.3635 | 454.0688 | 381.7547 | 395.4652
5566.3635 | 454.0279 | 381.8171 | 395.5096
5567.3635 | 454.0119 | 381.8671 | 395.5455
5568.3635 | 454.1389 | 381.907 | 395.5973
5569.3635 | 454.0956 | 381.9658 | 395.6463
5570.3635 | 454.0974 | 381.9985 | 395.6709
5571.3635 | 454.1421 | 382.0456 | 395.718
5572.3635 | 454.2332 | 382.0885 | 395.7298
5573.3635 | 454.3602 | 382.1285 | 395.7774
5574.3635 | 454.3917 | 382.1711 | 395.8265
5575.3635 | 454.319 | 382.2102 | 395.8607
5576.3635 | 454.26 | 382.257 | 395.9195
5577.3635 | 454.2875 | 382.3101 | 395.9632
5578.3635 | 454.2038 | 382.3403 | 395.993
5579.3635 | 454.1256 | 382.3915 | 396.0376
5580.3635 | 454.0658 | 382.4327 | 396.0813
5581.3635 | 454.08 | 382.4779 | 396.1178
5582.3635 | 454.0778 | 382.5382 | 396.1627
5583.3635 | 454.0464 | 382.5776 | 396.137
5584.3635 | 453.9354 | 382.6344 | 396.1844
5585.3635 | 453.9048 | 382.6656 | 396.2431
5586.3635 | 453.8661 | 382.7268 | 396.2775
5587.3635 | 453.9568 | 382.7708 | 396.3151
5588.3635 | 454.022 | 382.8112 | 396.38
5589.3635 | 454.0854 | 382.8751 | 396.4309
5590.3635 | 454.116 | 382.9136 | 396.51
5591.3635 | 454.1453 | 382.965 | 396.5896
5592.3635 | 454.1322 | 383.0179 | 396.6758
5593.3635 | 454.2202 | 383.0614 | 396.7543
5594.3635 | 454.2251 | 383.1201 | 396.8149
5595.3635 | 454.2294 | 383.1731 | 396.8325
5596.3635 | 454.2945 | 383.2167 | 396.8937
5597.3635 | 454.2819 | 383.2669 | 396.966
5598.3635 | 454.3375 | 383.3106 | 397.0132
5599.3635 | 454.3895 | 383.352 | 397.0816
5600.3635 | 454.4386 | 383.4243 | 397.1154
5601.3635 | 454.4849 | 383.4546 | 397.1689
5602.3635 | 454.5654 | 383.5223 | 397.2229
5603.3635 | 454.5503 | 383.562 | 397.2518
5604.3635 | 454.5089 | 383.6228 | 397.3058
5605.3635 | 454.4845 | 383.6805 | 397.376
5606.3635 | 454.4756 | 383.7263 | 397.4377
5607.3635 | 454.4462 | 383.7832 | 397.4703
5608.3635 | 454.3611 | 383.8351 | 397.524
5609.3635 | 454.3902 | 383.8826 | 397.5797
5610.3635 | 454.4801 | 383.9363 | 397.6129
5611.3635 | 454.4869 | 383.9801 | 397.6583
5612.3635 | 454.434 | 384.0342 | 397.691
5613.3635 | 454.3546 | 384.0771 | 397.7354
5614.3635 | 454.2404 | 384.1218 | 397.7771
5615.3635 | 454.1796 | 384.1793 | 397.8256
5616.3635 | 454.0417 | 384.211 | 397.8706
5617.3635 | 454.0729 | 384.259 | 397.9408
5618.3635 | 454.1299 | 384.317 | 397.9868
5619.3635 | 454.182 | 384.3496 | 398.0659
5620.3635 | 454.2364 | 384.4103 | 398.1147
5621.3635 | 454.1934 | 384.4513 | 398.1364
5622.3635 | 454.1741 | 384.509 | 398.154
5623.3635 | 454.1789 | 384.5516 | 398.2161
5624.3635 | 454.1658 | 384.5838 | 398.2284
5625.3635 | 454.2205 | 384.6542 | 398.2907
5626.3635 | 454.1188 | 384.6983 | 398.3515
5627.3635 | 454.0902 | 384.7489 | 398.3968
5628.3635 | 454.0456 | 384.7962 | 398.4451
5629.3635 | 454.0355 | 384.8473 | 398.4943
5630.3635 | 454.0675 | 384.9069 | 398.5544
5631.3635 | 453.9722 | 384.9563 | 398.6214
5632.3635 | 453.87 | 385.0004 | 398.6776
5633.3635 | 453.8332 | 385.0583 | 398.7279
5634.3635 | 453.8937 | 385.0946 | 398.7709
5635.3635 | 454.0677 | 385.1596 | 398.8075
5636.3635 | 454.1112 | 385.1984 | 398.8257
5637.3635 | 454.092 | 385.2535 | 398.8811
5638.3635 | 454.0145 | 385.3134 | 398.9359
5639.3635 | 454.0129 | 385.3496 | 398.9838
5640.3635 | 453.9012 | 385.3967 | 399.0125
5641.3635 | 453.8563 | 385.4377 | 399.0371
5642.3635 | 453.8326 | 385.4918 | 399.0798
5643.3635 | 453.7457 | 385.5428 | 399.1255
5644.3635 | 453.6867 | 385.5677 | 399.1689
5645.3635 | 453.6409 | 385.6277 | 399.1888
5646.3635 | 453.5669 | 385.6772 | 399.2115
5647.3635 | 453.6989 | 385.7165 | 399.2661
5648.3635 | 453.8865 | 385.7727 | 399.2851
5649.3635 | 454.0283 | 385.7932 | 399.2918
5650.3635 | 454.1641 | 385.8421 | 399.3342
5651.3635 | 454.2052 | 385.8781 | 399.3822
5652.3635 | 454.192 | 385.9198 | 399.4301
5653.3635 | 454.1215 | 385.9787 | 399.4789
5654.3635 | 454.0486 | 386.0187 | 399.5304
5655.3635 | 453.9199 | 386.0681 | 399.5743
5656.3635 | 453.8785 | 386.1127 | 399.5932
5657.3635 | 453.8359 | 386.1609 | 399.63
5658.3479 | 453.7992 | 386.2041 | 399.6555
5659.3479 | 453.9001 | 386.2408 | 399.6951
5660.3479 | 453.9389 | 386.2843 | 399.7453
5661.3479 | 453.9792 | 386.3362 | 399.7812
5662.3479 | 453.952 | 386.3528 | 399.8394
5663.3479 | 453.8757 | 386.4117 | 399.8806
5664.3479 | 453.8626 | 386.4539 | 399.9299
5665.3479 | 453.8689 | 386.4914 | 399.9345
5666.3479 | 453.8203 | 386.5394 | 399.9566
5667.3479 | 453.8525 | 386.5597 | 399.9923
5668.3479 | 453.9948 | 386.6114 | 400.0416
5669.3479 | 454.1098 | 386.6404 | 400.0471
5670.3479 | 454.2412 | 386.6802 | 400.1047
5671.3479 | 454.1018 | 386.7204 | 400.147
5672.3479 | 454.0736 | 386.749 | 400.1525
5673.3479 | 454.055 | 386.7938 | 400.1781
5674.3479 | 454.0465 | 386.8161 | 400.2362
5675.3479 | 454.0145 | 386.8493 | 400.2574
5676.3479 | 453.9866 | 386.8996 | 400.2714
5677.3479 | 453.9435 | 386.9092 | 400.3068
5678.3479 | 454.0305 | 386.9686 | 400.3778
5679.3479 | 454.1659 | 386.9928 | 400.4265
5680.3479 | 454.2885 | 387.0186 | 400.4659
5681.3479 | 454.3608 | 387.0627 | 400.5056
5682.3479 | 454.3075 | 387.0872 | 400.5472
5683.3479 | 454.3347 | 387.1332 | 400.58
5684.3479 | 454.3275 | 387.1717 | 400.6204
5685.3479 | 454.4579 | 387.207 | 400.6693
5686.3479 | 454.4783 | 387.2486 | 400.7071
5687.3479 | 454.3328 | 387.2776 | 400.7498
5688.3479 | 454.3454 | 387.338 | 400.7909
5689.3479 | 454.436 | 387.3786 | 400.833
5690.3479 | 454.4147 | 387.413 | 400.873
5691.3479 | 454.3732 | 387.4677 | 400.9226
5692.3479 | 454.3847 | 387.4986 | 400.9139
5693.3479 | 454.444 | 387.5465 | 400.916
5694.3479 | 454.3208 | 387.5845 | 400.9795
5695.3479 | 454.2796 | 387.6208 | 401.0367
5696.3479 | 454.2826 | 387.6684 | 401.0897
5697.3479 | 454.308 | 387.7215 | 401.1445
5698.3479 | 454.2849 | 387.7558 | 401.1929
5699.3479 | 454.2444 | 387.7891 | 401.2316
5700.3479 | 454.2823 | 387.8262 | 401.2639
5701.3479 | 454.3016 | 387.8766 | 401.3108
5702.3479 | 454.3003 | 387.8966 | 401.3267
5703.3479 | 454.4038 | 387.9359 | 401.3539
5704.3479 | 454.4613 | 387.9627 | 401.3956
5705.3479 | 454.4278 | 387.9928 | 401.4383
5706.3635 | 454.3476 | 388.0244 | 401.4653
5707.3479 | 454.3534 | 388.0618 | 401.4732
5708.3479 | 454.352 | 388.0682 | 401.5072
5709.3635 | 454.4135 | 388.1211 | 401.5439
5710.3635 | 454.4632 | 388.1372 | 401.5415
5711.3479 | 454.5135 | 388.1693 | 401.5923
5712.3479 | 454.432 | 388.1921 | 401.6286
5713.3479 | 454.3831 | 388.2245 | 401.6555
5714.3479 | 454.3329 | 388.2517 | 401.7021
5715.3479 | 454.2809 | 388.2774 | 401.7327
5716.3479 | 454.2773 | 388.3103 | 401.7665
5717.3479 | 454.3968 | 388.3364 | 401.7785
5718.3479 | 454.441 | 388.3712 | 401.8198
5719.3479 | 454.4982 | 388.4056 | 401.855
5720.3479 | 454.4528 | 388.4258 | 401.8943
5721.3479 | 454.3345 | 388.4694 | 401.909
5722.3479 | 454.4216 | 388.5002 | 401.9542
5723.3479 | 454.5136 | 388.5188 | 401.9935
5724.3479 | 454.5173 | 388.5573 | 402.0129
5725.3479 | 454.5091 | 388.5983 | 402.0123
5726.3479 | 454.5164 | 388.6374 | 402.0555
5727.3479 | 454.5821 | 388.6638 | 402.0862
5728.3479 | 454.6116 | 388.7112 | 402.1064
5729.3479 | 454.6758 | 388.755 | 402.1149
5730.3479 | 454.5672 | 388.7908 | 402.1629
5731.3479 | 454.456 | 388.8376 | 402.186
5732.3635 | 454.4459 | 388.8813 | 402.2066
5733.3479 | 454.344 | 388.9186 | 402.2305
5734.3479 | 454.3187 | 388.9628 | 402.2633
5735.3479 | 454.2044 | 389.0044 | 402.2861
5736.3479 | 454.1977 | 389.0353 | 402.3056
5737.3479 | 454.2026 | 389.078 | 402.3437
5738.3479 | 454.09 | 389.1165 | 402.3774
5739.3479 | 453.9582 | 389.16 | 402.4188
5740.3479 | 453.8798 | 389.1848 | 402.427
5741.3479 | 453.7828 | 389.2161 | 402.4365
5742.3479 | 453.7542 | 389.2636 | 402.4776
5743.3479 | 453.8376 | 389.2926 | 402.493
5744.3635 | 453.7616 | 389.33 | 402.5166
5745.3635 | 453.6378 | 389.3781 | 402.5583
5746.3479 | 453.541 | 389.4098 | 402.5849
5747.3479 | 453.4179 | 389.4432 | 402.5859
5748.3479 | 453.3026 | 389.4915 | 402.585
5749.3479 | 453.3845 | 389.5294 | 402.5949
5750.3479 | 453.3704 | 389.5734 | 402.6237
5751.3479 | 453.2362 | 389.6131 | 402.6511
5752.3635 | 453.2403 | 389.6541 | 402.6735
5753.3479 | 453.2893 | 389.6899 | 402.6822
5754.3479 | 453.1713 | 389.7351 | 402.6873
5755.3479 | 453.1784 | 389.7716 | 402.6921
5756.3479 | 453.1896 | 389.8123 | 402.695
5757.3479 | 453.2433 | 389.8339 | 402.6798
5758.3635 | 453.2245 | 389.8718 | 402.6798
5759.3479 | 453.2475 | 389.8882 | 402.7145
5760.3479 | 453.3077 | 389.909 | 402.7263
5761.3479 | 453.3516 | 389.9528 | 402.7539
5762.3479 | 453.3503 | 389.9762 | 402.7576
5763.3479 | 453.3796 | 389.995 | 402.7544
5764.3479 | 453.342 | 390.0344 | 402.757
5765.3479 | 453.4259 | 390.0705 | 402.7726
5766.3479 | 453.6443 | 390.0948 | 402.8071
5767.3479 | 453.7618 | 390.1173 | 402.8234
5768.3479 | 453.799 | 390.1357 | 402.8292
5769.3479 | 453.7961 | 390.1594 | 402.8239
5770.3479 | 453.7978 | 390.1857 | 402.8088
5771.3635 | 453.7308 | 390.2039 | 402.8121
5772.3479 | 453.792 | 390.2286 | 402.8143
5773.3635 | 453.8936 | 390.2469 | 402.8193
5774.3635 | 453.7421 | 390.2724 | 402.8314
5775.3635 | 453.6845 | 390.2935 | 402.8371
5776.3635 | 453.659 | 390.3198 | 402.8496
5777.3635 | 453.6614 | 390.3558 | 402.8552
5778.3635 | 453.6501 | 390.3555 | 402.8604
5779.3635 | 453.5746 | 390.3837 | 402.8931
5780.3635 | 453.4483 | 390.4203 | 402.8977
5781.3635 | 453.5674 | 390.4489 | 402.8955
5782.3635 | 453.5142 | 390.4789 | 402.8992
5783.3635 | 453.5982 | 390.5313 | 402.9256
5784.3635 | 453.5439 | 390.574 | 402.9276
5785.3635 | 453.5518 | 390.6051 | 402.8888
5786.3635 | 453.4807 | 390.6393 | 402.9048
5787.3635 | 453.6142 | 390.6791 | 402.9137
5788.3635 | 453.4848 | 390.7094 | 402.9294
5789.3635 | 453.4046 | 390.7418 | 402.929
5790.3479 | 453.3978 | 390.7806 | 402.9273
5791.3635 | 453.513 | 390.8065 | 402.9347
5792.3635 | 453.488 | 390.8548 | 402.944
5793.3635 | 453.4276 | 390.8894 | 402.9564
5794.3635 | 453.4976 | 390.9101 | 402.9597
5795.3635 | 453.5743 | 390.9528 | 402.9806
5796.3635 | 453.5239 | 390.973 | 402.977
5797.3635 | 453.5315 | 391.0061 | 402.9234
5798.3635 | 453.6769 | 391.0322 | 402.9061
5799.3635 | 453.7292 | 391.0557 | 402.9349
5800.3635 | 453.8083 | 391.0826 | 402.9444
5801.3635 | 453.8632 | 391.1032 | 402.9532
5802.3635 | 453.8331 | 391.1134 | 402.9778
5803.3635 | 453.8918 | 391.1297 | 403.0111
5804.3635 | 453.907 | 391.1473 | 403.0327
5805.3635 | 453.8165 | 391.1581 | 403.0573
5806.3635 | 453.844 | 391.1705 | 403.078
5807.3635 | 453.8583 | 391.1817 | 403.0962
5808.3635 | 453.7839 | 391.2093 | 403.1221
5809.3635 | 453.7865 | 391.2313 | 403.1389
5810.3635 | 453.97 | 391.2339 | 403.1521
5811.3635 | 454.0632 | 391.2718 | 403.1675
5812.3635 | 454.1276 | 391.2903 | 403.1865
5813.3635 | 454.1018 | 391.3035 | 403.217
5814.3635 | 454.1744 | 391.3176 | 403.2341
5815.3635 | 454.2397 | 391.3387 | 403.2531
5816.3635 | 454.1291 | 391.367 | 403.2244
5817.3635 | 453.9935 | 391.3734 | 403.201
5818.3635 | 453.8892 | 391.4023 | 403.2138
5819.3635 | 453.8984 | 391.4266 | 403.2534
5820.3635 | 453.982 | 391.4389 | 403.2939
5821.3635 | 453.9805 | 391.4581 | 403.2975
5822.3635 | 453.9855 | 391.4832 | 403.2982
5823.3635 | 453.9527 | 391.502 | 403.3232
5824.3635 | 454.0713 | 391.5075 | 403.3493
5825.3635 | 453.9952 | 391.5384 | 403.3476
5826.3635 | 453.9423 | 391.5545 | 403.3332
5827.3635 | 454.0217 | 391.5851 | 403.3626
5828.3635 | 454.094 | 391.6088 | 403.3696
5829.3635 | 454.1675 | 391.6172 | 403.3978
5830.3635 | 454.1169 | 391.6236 | 403.4198
5831.3635 | 454.1181 | 391.6579 | 403.4123
5832.3635 | 454.1413 | 391.6829 | 403.4239
5833.3635 | 454.2054 | 391.6936 | 403.4467
5834.3635 | 454.1825 | 391.7223 | 403.4662
5835.3635 | 454.1992 | 391.7513 | 403.4854
5836.3635 | 454.2168 | 391.7725 | 403.4954
5837.3635 | 454.2128 | 391.7974 | 403.5165
5838.3635 | 454.2072 | 391.8275 | 403.544
5839.3635 | 454.1917 | 391.8474 | 403.5698
5840.3635 | 454.078 | 391.8925 | 403.6035
5841.3635 | 454.0032 | 391.9085 | 403.6368
5842.3635 | 454.0981 | 391.935 | 403.6315
5843.3635 | 453.8935 | 391.9681 | 403.6402
5844.3635 | 453.8964 | 391.9807 | 403.6769
5845.3635 | 453.821 | 392.0145 | 403.7226
5846.3635 | 453.7893 | 392.0222 | 403.7562
5847.3635 | 453.7457 | 392.0527 | 403.7442
5848.3635 | 453.7436 | 392.0714 | 403.7611
5849.3635 | 453.8544 | 392.0948 | 403.7758
5850.3635 | 453.914 | 392.1136 | 403.8278
5851.3635 | 453.8346 | 392.119 | 403.8601
5852.3635 | 453.7505 | 392.1435 | 403.9087
5853.3635 | 453.8367 | 392.1703 | 403.9484
5854.3635 | 453.8603 | 392.1729 | 403.9714
5855.3635 | 453.9612 | 392.2063 | 403.9972
5856.3635 | 453.98 | 392.2167 | 404.0182
5857.3635 | 453.8502 | 392.2241 | 404.012
5858.3635 | 453.783 | 392.253 | 403.9735
5859.3635 | 453.8046 | 392.2565 | 404.0057
5860.3635 | 453.8348 | 392.2678 | 404.0332
5861.3635 | 453.899 | 392.2793 | 404.0682
5862.3635 | 453.9306 | 392.2908 | 404.0919
5863.3635 | 453.9644 | 392.3216 | 404.1134
5864.3635 | 454.0667 | 392.3272 | 404.0987
5865.3635 | 454.0706 | 392.3393 | 404.1362
5866.3635 | 454.0718 | 392.3624 | 404.1563
5867.3635 | 454.0098 | 392.3729 | 404.1853
5868.3635 | 453.98 | 392.3882 | 404.211
5869.3635 | 454.0174 | 392.4113 | 404.1796
5870.3635 | 453.8957 | 392.416 | 404.1984
5871.3635 | 453.8822 | 392.4465 | 404.1876
5872.3635 | 453.9624 | 392.4551 | 404.1599
5873.3635 | 453.9721 | 392.4762 | 404.2017
5874.3635 | 453.9646 | 392.4854 | 404.2315
5875.3635 | 453.9453 | 392.4985 | 404.24
5876.3635 | 454.1321 | 392.5325 | 404.2611
5877.3635 | 454.205 | 392.5339 | 404.2713
5878.3635 | 454.26 | 392.5492 | 404.2791
5879.3635 | 454.3396 | 392.5737 | 404.2855
5880.3635 | 454.2465 | 392.5922 | 404.2974
5881.3635 | 454.1631 | 392.6068 | 404.3066
5882.3635 | 454.1693 | 392.6204 | 404.3286
5883.3635 | 454.2787 | 392.6331 | 404.3091
5884.3635 | 454.443 | 392.66 | 404.285
5885.3635 | 454.5228 | 392.6871 | 404.289
5886.3635 | 454.5133 | 392.7034 | 404.2815
5887.3635 | 454.5181 | 392.7204 | 404.2877
5888.3635 | 454.5046 | 392.7447 | 404.3001
5889.3635 | 454.4447 | 392.7727 | 404.3179
5890.3635 | 454.4037 | 392.801 | 404.2943
5891.3635 | 454.4239 | 392.8377 | 404.253
5892.3635 | 454.4174 | 392.8538 | 404.2756
5893.3635 | 454.3535 | 392.8854 | 404.3053
5894.3635 | 454.2448 | 392.909 | 404.3298
5895.3635 | 454.2126 | 392.9367 | 404.357
5896.3635 | 454.126 | 392.9572 | 404.382
5897.3635 | 454.1053 | 392.9704 | 404.4062
5898.3635 | 454.1335 | 392.9935 | 404.4273
5899.3635 | 454.1417 | 393.0161 | 404.4514
5900.3635 | 454.0766 | 393.0298 | 404.4533
5901.3635 | 453.9822 | 393.0416 | 404.4604
5902.3635 | 454.0515 | 393.0692 | 404.4389
5903.3635 | 454.1369 | 393.0851 | 404.4191
5904.3635 | 454.2261 | 393.0986 | 404.4034
5905.3635 | 454.2274 | 393.1278 | 404.3924
5906.3635 | 454.1677 | 393.1565 | 404.4061
5907.3479 | 454.1618 | 393.1514 | 404.4148
5908.3635 | 454.2354 | 393.1943 | 404.4459
5909.3635 | 454.3141 | 393.2114 | 404.4887
5910.3635 | 454.3143 | 393.2461 | 404.5426
5911.3635 | 454.2258 | 393.2665 | 404.6013
5912.3635 | 454.1599 | 393.2835 | 404.6633
5913.3635 | 454.2309 | 393.3171 | 404.7377
5914.3635 | 454.2731 | 393.3362 | 404.8037
5915.3635 | 454.0946 | 393.3616 | 404.8771
5916.3635 | 453.9792 | 393.3881 | 404.9605
5917.3479 | 453.9185 | 393.4126 | 405.031
5918.3635 | 453.8837 | 393.4327 | 405.0843
5919.3479 | 453.7957 | 393.4585 | 405.1389
5920.3635 | 453.8982 | 393.4835 | 405.2201
5921.3479 | 454.0286 | 393.517 | 405.2939
5922.3635 | 454.0333 | 393.5345 | 405.3593
5923.3479 | 454.0343 | 393.5524 | 405.4163
5924.3635 | 454.0617 | 393.5812 | 405.447
5925.3635 | 454.1114 | 393.5874 | 405.4853
5926.3479 | 454.1115 | 393.5934 | 405.5256
5927.3479 | 454.0269 | 393.5979 | 405.5429
5928.3479 | 454.0324 | 393.6311 | 405.579
5929.3479 | 454.0859 | 393.646 | 405.6286
5930.3635 | 454.0937 | 393.665 | 405.6803
5931.3479 | 453.9727 | 393.6791 | 405.7202
5932.3479 | 453.9444 | 393.6752 | 405.777
5933.3635 | 453.9411 | 393.713 | 405.7883
5934.3635 | 453.8752 | 393.7184 | 405.8049
5935.3635 | 453.9477 | 393.7335 | 405.8314
5936.3635 | 454.0024 | 393.768 | 405.8514
5937.3635 | 453.9768 | 393.7748 | 405.8983
5938.3479 | 453.9531 | 393.7968 | 405.928
5939.3479 | 453.8782 | 393.807 | 405.9543
5940.3479 | 453.7486 | 393.8249 | 405.9713
5941.3479 | 453.6546 | 393.8439 | 405.9523
5942.3635 | 453.6561 | 393.8361 | 405.9092
5943.3479 | 453.6737 | 393.8622 | 405.9381
5944.3635 | 453.7015 | 393.8724 | 405.9217
5945.3635 | 453.6161 | 393.8814 | 405.9386
5946.3635 | 453.5373 | 393.8974 | 405.9518
5947.3635 | 453.6551 | 393.9017 | 405.9715
5948.3479 | 453.7679 | 393.9138 | 405.9788
5949.3479 | 453.8542 | 393.9045 | 405.9801
5950.3479 | 453.9527 | 393.9216 | 405.9723
5951.3792 | 454.0144 | 393.9232 | 405.9665
5952.3479 | 453.9886 | 393.9332 | 405.9578
5953.3479 | 453.9623 | 393.9187 | 405.9356
5954.3479 | 453.9759 | 393.9263 | 405.9375
5955.3479 | 454.0328 | 393.9083 | 405.8877
5956.3479 | 454.0892 | 393.9417 | 405.8762
5957.3479 | 454.1852 | 393.9295 | 405.8935
5958.3479 | 454.3432 | 393.9396 | 405.9192
5959.3479 | 454.3507 | 393.938 | 405.9256
5960.3479 | 454.1848 | 393.9354 | 405.9737
5961.3479 | 454.0951 | 393.9566 | 405.9922
5962.3479 | 454.165 | 393.9423 | 405.9777
5963.3479 | 454.1921 | 393.9553 | 405.9633
5964.3479 | 454.195 | 393.9671 | 405.9659
5965.3479 | 454.1643 | 393.9639 | 405.9714
5966.3479 | 454.114 | 393.9873 | 405.9709
5967.3479 | 454.0518 | 393.9943 | 405.9657
5968.3635 | 454.0145 | 394.0044 | 405.9606
5969.3479 | 454.0434 | 394.0222 | 405.9437
5970.3479 | 454.1203 | 394.024 | 405.9416
5971.3479 | 454.0923 | 394.0538 | 405.9591
5972.3479 | 454.0375 | 394.076 | 405.9434
5973.3479 | 454.0086 | 394.0707 | 405.8902
5974.3479 | 454.0776 | 394.0903 | 405.8608
5975.3479 | 454.0769 | 394.1001 | 405.8514
5976.3479 | 454.129 | 394.1219 | 405.8282
5977.3479 | 454.1302 | 394.1384 | 405.8705
5978.3479 | 454.0791 | 394.1408 | 405.8925
5979.3479 | 454.1464 | 394.1617 | 405.894
5980.3479 | 454.1774 | 394.1866 | 405.8765
5981.3635 | 454.1403 | 394.1873 | 405.9039
5982.3479 | 454.2243 | 394.2085 | 405.9409
5983.3479 | 454.2628 | 394.2343 | 405.9682
5984.3479 | 454.3108 | 394.2605 | 405.9715
5985.3635 | 454.3615 | 394.2587 | 405.9636
5986.3479 | 454.4579 | 394.2696 | 405.9576
5987.3479 | 454.5154 | 394.305 | 405.9749
5988.3479 | 454.5308 | 394.3209 | 405.9616
5989.3479 | 454.6636 | 394.3205 | 405.9354
5990.3479 | 454.6381 | 394.3725 | 405.909
5991.3635 | 454.6705 | 394.3839 | 405.8976
5992.3479 | 454.6999 | 394.406 | 405.8919
5993.3479 | 454.6875 | 394.4257 | 405.8633
5994.3479 | 454.5588 | 394.4425 | 405.8838
5995.3479 | 454.4248 | 394.492 | 405.8951
5996.3479 | 454.4903 | 394.5019 | 405.8623
5997.3479 | 454.5109 | 394.5234 | 405.8504
5998.3479 | 454.402 | 394.5659 | 405.8609
5999.3479 | 454.3648 | 394.5917 | 405.8825
6000.3479 | 454.291 | 394.6383 | 405.8915
6001.3479 | 454.2655 | 394.6494 | 405.908
6002.3479 | 454.5443 | 394.6858 | 405.9112
6003.3479 | 455.6746 | 394.7068 | 405.9057
6004.3635 | 457.6227 | 394.7459 | 405.8874
6005.3635 | 460.1176 | 394.7694 | 405.9052
6006.3479 | 462.9963 | 394.7864 | 405.8921
6007.3479 | 466.1978 | 394.8061 | 405.8924
6008.3635 | 469.5629 | 394.8249 | 405.875
6009.3479 | 472.863 | 394.8568 | 405.9752
6010.3479 | 475.9826 | 394.8776 | 406.0374
6011.3479 | 478.9186 | 394.9121 | 406.0915
6012.3479 | 481.4073 | 394.9476 | 406.1772
6013.3479 | 483.4093 | 395.0001 | 406.2913
6014.3479 | 485.0676 | 395.0485 | 406.4227
6015.3479 | 486.4055 | 395.1207 | 406.4882
6016.3479 | 487.332 | 395.1921 | 406.6254
6017.3479 | 487.8929 | 395.2666 | 406.7815
6018.3479 | 488.1406 | 395.3739 | 406.94
6019.3479 | 488.2435 | 395.4804 | 407.1154
6020.3479 | 488.2275 | 395.5831 | 407.3475
6021.3479 | 488.2127 | 395.7218 | 407.5494
6022.3479 | 488.0922 | 395.8427 | 407.7489
6023.3479 | 487.82 | 395.9803 | 407.9374
6024.3479 | 487.4249 | 396.1359 | 408.1259
6025.3479 | 487.0651 | 396.2607 | 408.3322
6026.3479 | 486.6466 | 396.4321 | 408.5339
6027.3635 | 486.2981 | 396.5843 | 408.7195
6028.3635 | 485.8557 | 396.7458 | 408.9678
6029.3635 | 485.5156 | 396.9197 | 409.1594
6030.3635 | 485.0396 | 397.081 | 409.3574
6031.3635 | 484.4947 | 397.254 | 409.5197
6032.3635 | 484.0566 | 397.414 | 409.6914
6033.3635 | 483.4754 | 397.599 | 409.8399
6034.3635 | 483.0144 | 397.7618 | 409.9846
6035.3635 | 482.6814 | 397.9373 | 410.2015
6036.3635 | 482.3349 | 398.1158 | 410.3779
6037.3635 | 481.9801 | 398.2658 | 410.4953
6038.3635 | 481.5563 | 398.4443 | 410.696
6039.3635 | 481.0762 | 398.6033 | 410.7996
6040.3635 | 480.8138 | 398.7539 | 410.8376
6041.3635 | 480.6745 | 398.9146 | 410.9861
6042.3635 | 480.4508 | 399.0653 | 411.1262
6043.3635 | 480.3174 | 399.2309 | 411.2748
6044.3635 | 480.137 | 399.3743 | 411.4362
6045.3635 | 479.8837 | 399.5354 | 411.5979
6046.3635 | 479.6098 | 399.672 | 411.8229
6047.3635 | 479.4488 | 399.8056 | 411.9871
6048.3635 | 479.372 | 399.9557 | 412.2612
6049.3635 | 479.2146 | 400.1015 | 412.4694
6050.3635 | 479.1687 | 400.2338 | 412.6659
6051.3635 | 479.1092 | 400.3757 | 412.9098
6052.3635 | 479.1108 | 400.5068 | 413.1928
6053.3635 | 479.0448 | 400.636 | 413.5572
6054.3635 | 478.9788 | 400.7875 | 413.9025
6055.3635 | 479.0527 | 400.9173 | 414.2136
6056.3635 | 479.0159 | 401.0512 | 414.5474
6057.3635 | 478.9141 | 401.1766 | 414.9426
6058.3635 | 478.8741 | 401.3146 | 415.3576
6059.3635 | 478.8699 | 401.448 | 415.7799
6060.3635 | 478.8292 | 401.5797 | 416.2139
6061.3635 | 478.8249 | 401.709 | 416.7219
6062.3635 | 478.8158 | 401.8384 | 417.3237
6063.3635 | 478.7448 | 401.9716 | 417.9615
6064.3635 | 478.624 | 402.0936 | 418.5137
6065.3635 | 478.6694 | 402.2457 | 419.405
6066.3635 | 478.6361 | 402.3765 | 420.0865
6067.3635 | 478.7619 | 402.4868 | 421.1922
6068.3635 | 478.9157 | 402.6512 | 422.7271
6069.3635 | 479.3229 | 402.7695 | 424.2795
6070.3635 | 479.4937 | 402.9081 | 425.3731
6071.3635 | 479.6525 | 403.1037 | 426.6698
6072.3635 | 479.7952 | 403.2849 | 427.9418
6073.3635 | 479.9439 | 403.4182 | 429.1506
6074.3635 | 479.9983 | 403.7279 | 430.9288
6075.3635 | 480.1581 | 404.0213 | 432.4824
6076.3635 | 480.261 | 404.5016 | 434.7136
6077.3635 | 480.2623 | 404.9433 | 435.8891
6078.3635 | 480.328 | 405.5088 | 437.4056
6079.3635 | 480.242 | 406.385 | 439.2054
6080.3635 | 480.2121 | 407.2311 | 441.2872
6081.3635 | 480.1682 | 408.2418 | 443.3683
6082.3635 | 480.1306 | 409.3507 | 445.6891
6083.3635 | 480.0199 | 410.4476 | 447.8854
6084.3635 | 479.9149 | 411.6064 | 450.2745
6085.3635 | 479.8503 | 413.2772 | 452.9251
6086.3635 | 479.8487 | 414.5961 | 455.5442
6087.3635 | 479.918 | 416.1439 | 457.8524
6088.3635 | 479.8926 | 417.7717 | 460.6403
6089.3635 | 479.8763 | 419.4744 | 463.5513
6090.3635 | 479.9276 | 421.194 | 466.0257
6091.3635 | 479.9226 | 423.2176 | 468.7453
6092.3635 | 479.9042 | 424.9228 | 470.823
6093.3635 | 479.7389 | 427.2277 | 473.5299
6094.3635 | 479.7168 | 429.3612 | 475.8928
6095.3635 | 479.7365 | 431.7899 | 478.198
6096.3635 | 479.6934 | 434.2236 | 480.9337
6097.3635 | 479.6433 | 436.9891 | 483.3723
6098.3635 | 479.5734 | 439.1573 | 485.8788
6099.3635 | 479.4183 | 441.8884 | 488.5757
6100.3635 | 479.4442 | 443.9693 | 490.5371
6101.3635 | 479.394 | 446.0988 | 492.5518
6102.3635 | 479.3485 | 448.4584 | 494.4801
6103.3635 | 479.2775 | 451.3436 | 496.0707
6104.3635 | 479.2714 | 453.2932 | 497.6571
6105.3635 | 479.229 | 456.0274 | 499.0475
6106.3635 | 479.1611 | 458.963 | 500.71
6107.3635 | 479.0113 | 461.4803 | 502.2073
6108.3635 | 478.8988 | 463.7365 | 503.6797
6109.3635 | 478.8321 | 465.6831 | 505.0924
6110.3635 | 478.9358 | 469.1301 | 506.0968
6111.3635 | 478.8674 | 471.3287 | 507.6114
6112.3635 | 478.7014 | 473.2509 | 508.7227
6113.3635 | 478.5928 | 475.5354 | 510.0257
6114.3635 | 478.5122 | 477.407 | 511.2989
6115.3635 | 478.3251 | 479.4685 | 513.0349
6116.3635 | 478.275 | 481.4114 | 514.243
6117.3635 | 478.176 | 483.098 | 515.4639
6118.3635 | 478.0691 | 485.3752 | 516.6366
6119.3635 | 477.9358 | 487.5061 | 519.0532
6120.3635 | 477.871 | 489.3976 | 520.4115
6121.3635 | 477.7644 | 490.7275 | 521.7994
6122.3635 | 477.6899 | 492.8242 | 522.8279
6123.3635 | 477.7526 | 494.7632 | 524.235
6124.3635 | 477.8343 | 496.6809 | 525.728
6125.3635 | 477.7409 | 498.5434 | 526.8301
6126.3635 | 477.6125 | 500.4637 | 528.8796
6127.3635 | 477.4749 | 502.5044 | 529.952
6128.3635 | 477.3887 | 504.0653 | 531.409
6129.3635 | 477.326 | 505.3484 | 532.5568
6130.3635 | 477.1782 | 507.6559 | 533.8493
6131.3635 | 477.1111 | 509.0468 | 534.9028
6132.3635 | 477.152 | 510.5441 | 536.5697
6133.3635 | 477.0759 | 511.5937 | 537.2953
6134.3635 | 477.1573 | 513.4 | 539.1796
6135.3635 | 477.0382 | 514.6669 | 541.0488
6136.3635 | 476.936 | 516.0786 | 542.6903
6137.3635 | 476.7638 | 516.1641 | 544.0492
6138.3635 | 476.5826 | 516.8378 | 545.2255
6139.3635 | 476.5685 | 518.9423 | 546.5334
6140.3635 | 476.5652 | 519.9795 | 547.8571
6141.3635 | 476.4356 | 521.2559 | 548.4438
6142.3635 | 476.4375 | 522.8668 | 550.1143
6143.3635 | 476.5596 | 523.4236 | 549.537
6144.3635 | 476.5083 | 525.9127 | 551.1336
6145.3635 | 476.4048 | 528.0041 | 553.2267
6146.3635 | 476.2224 | 527.6729 | 553.0693
6147.3635 | 476.0864 | 528.6593 | 555.4725
6148.3635 | 475.9111 | 528.7006 | 555.9841
6149.3635 | 475.7082 | 530.4108 | 556.9486
6150.3635 | 475.5769 | 530.9823 | 557.1597
6151.3635 | 475.3373 | 532.5689 | 557.6784
6152.3635 | 475.2032 | 534.1582 | 559.5397
6153.3635 | 475.0599 | 534.7871 | 561.1968
6154.3635 | 474.9868 | 535.6135 | 561.2747
6155.3635 | 474.784 | 536.4292 | 563.1374
6156.3635 | 474.6269 | 536.6663 | 564.857
6157.3635 | 474.3806 | 537.3357 | 567.5108
6158.3635 | 474.1977 | 537.6731 | 569.0878
6159.3635 | 473.875 | 537.6126 | 569.5484
6160.3635 | 473.646 | 539.752 | 572.3655
6161.3635 | 473.425 | 539.8898 | 574.1775
6162.3635 | 473.1957 | 541.2965 | 576.4432
6163.3635 | 473.3421 | 542.4477 | 580.9391
6164.3479 | 473.2808 | 542.7574 | 583.5373
6165.3635 | 473.0238 | 542.8674 | 585.2262
6166.3479 | 472.7414 | 543.4956 | 587.5324
6167.3479 | 472.498 | 544.569 | 589.9424
6168.3479 | 472.2948 | 545.552 | 593.1986
6169.3479 | 472.0504 | 546.1706 | 596.7195
6170.3479 | 471.8205 | 546.9134 | 599.5085
6171.3479 | 471.5591 | 547.3445 | 602.2091
6172.3635 | 471.3889 | 548.1978 | 604.4345
6173.3479 | 471.0977 | 548.7255 | 605.7614
6174.3479 | 470.8715 | 549.805 | 608.3454
6175.3479 | 470.7768 | 550.8145 | 610.784
6176.3479 | 470.6644 | 551.2822 | 612.82
6177.3479 | 470.6146 | 552.5493 | 614.5052
6178.3479 | 470.5341 | 551.9507 | 616.5365
6179.3479 | 470.3959 | 553.0006 | 618.7181
6180.3479 | 470.311 | 552.992 | 620.0034
6181.3479 | 470.277 | 553.1294 | 621.3537
6182.3479 | 470.2512 | 554.0926 | 623.7202
6183.3479 | 470.2582 | 553.139 | 624.0074
6184.3479 | 470.3206 | 553.8137 | 623.6816
6185.3479 | 470.2535 | 552.1847 | 624.1223
6186.3479 | 470.2475 | 551.5937 | 624.3707
6187.3479 | 470.2905 | 549.9654 | 624.477
6188.3479 | 470.2391 | 549.1713 | 624.7422
6189.3479 | 470.0841 | 549.6122 | 624.9755
6190.3479 | 470.0059 | 549.2457 | 625.3876
6191.3479 | 469.9086 | 549.9051 | 625.5799
6192.3479 | 469.8773 | 550.6626 | 626.4918
6193.3479 | 469.7988 | 550.9591 | 627.578
6194.3479 | 469.8289 | 551.2461 | 628.0909
6195.3479 | 469.8961 | 551.29 | 628.5109
6196.3479 | 469.746 | 551.5746 | 629.3241
6197.3479 | 469.7034 | 552.1378 | 630.1611
6198.3479 | 469.6886 | 552.002 | 630.643
6199.3479 | 469.74 | 551.2738 | 631.7979
6200.3479 | 469.8875 | 551.4695 | 633.5656
6201.3479 | 469.9001 | 551.5349 | 634.0775
6202.3479 | 469.9497 | 550.8938 | 634.4194
6203.3479 | 470.0904 | 550.4515 | 634.3063
6204.3479 | 470.1733 | 550.2826 | 634.5854
6205.3479 | 470.2436 | 549.8989 | 634.79
6206.3479 | 470.3771 | 550.2603 | 635.0963
6207.3479 | 470.4763 | 550.4217 | 635.3249
6208.3479 | 470.5092 | 550.5547 | 635.9789
6209.3479 | 470.5229 | 550.8725 | 637.0955
6210.3479 | 470.5283 | 549.829 | 637.882
6211.3479 | 470.6127 | 548.0087 | 638.6726
6212.3479 | 470.6916 | 547.8948 | 640.1469
6213.3479 | 470.763 | 548.1573 | 641.1536
6214.3479 | 470.8959 | 549.7272 | 641.6501
6215.3479 | 470.9323 | 548.2716 | 642.2172
6216.3479 | 470.9648 | 547.7439 | 642.2922
6217.3479 | 471.0197 | 547.0796 | 641.9369
6218.3479 | 471.0701 | 546.1451 | 641.8186
6219.3479 | 471.2405 | 546.3714 | 641.8972
6220.3479 | 471.4081 | 546.9923 | 642.1589
6221.3479 | 471.4939 | 547.2675 | 642.2601
6222.3479 | 471.6211 | 546.9014 | 642.6747
6223.3479 | 471.7499 | 547.5238 | 642.8243
6224.3479 | 471.9477 | 548.118 | 642.5539
6225.3479 | 472.0487 | 548.682 | 642.6346
6226.3479 | 472.1381 | 549.59 | 642.2522
6227.3479 | 472.2077 | 549.9364 | 642.2624
6228.3479 | 472.2749 | 550.6411 | 641.9158
6229.3479 | 472.4282 | 551.8929 | 641.4955
6230.3479 | 472.584 | 552.4387 | 641.5718
6231.3479 | 472.7618 | 552.8452 | 641.0045
6232.3479 | 472.8509 | 553.5865 | 640.8254
6233.3479 | 472.8909 | 553.979 | 640.4093
6234.3479 | 472.8621 | 554.4433 | 639.7077
6235.3479 | 472.8949 | 554.9104 | 639.0318
6236.3479 | 472.9923 | 555.43 | 638.4876
6237.3479 | 473.026 | 556.0258 | 637.6406
6238.3635 | 472.9982 | 557.1253 | 637.1152
6239.3635 | 473.0847 | 557.8491 | 635.8278
6240.3479 | 473.1746 | 558.6154 | 634.7988
6241.3479 | 473.2022 | 559.5314 | 633.5649
6242.3635 | 473.2717 | 560.061 | 631.9409
6243.3479 | 473.3556 | 560.9737 | 630.7304
6244.3479 | 473.342 | 561.9115 | 629.1955
6245.3479 | 473.3726 | 563.0528 | 627.4012
6246.3479 | 473.4787 | 564.1295 | 625.9325
6247.3479 | 473.5644 | 565.0649 | 624.8947
6248.3479 | 473.5392 | 566.2367 | 623.6324
6249.3635 | 473.5205 | 567.2297 | 621.6845
6250.3479 | 473.6293 | 568.3486 | 620.8984
6251.3479 | 473.8053 | 569.3537 | 619.8956
6252.3479 | 473.9244 | 570.4745 | 619.5976
6253.3479 | 473.9545 | 571.7104 | 619.7092
6254.3479 | 474.1482 | 572.8397 | 619.649
6255.3479 | 474.2999 | 573.9445 | 619.6066
6256.3479 | 474.3612 | 575.1272 | 619.8595
6257.3635 | 474.4717 | 576.3683 | 620.0244
6258.3479 | 474.5882 | 577.6601 | 620.4853
6259.3479 | 474.6337 | 578.8617 | 620.7942
6260.3635 | 474.6542 | 580.0175 | 621.1008
6261.3479 | 474.7216 | 581.2029 | 621.4185
6262.3635 | 474.856 | 582.2645 | 621.5795
6263.3635 | 474.8953 | 583.3605 | 621.7371
6264.3635 | 474.9545 | 584.3518 | 621.9762
6265.3635 | 475.0106 | 585.3767 | 622.182
6266.3635 | 475.1126 | 586.1599 | 622.4325
6267.3635 | 475.1145 | 586.9486 | 622.5788
6268.3635 | 475.1525 | 587.7006 | 622.8849
6269.3635 | 475.2412 | 588.4179 | 622.9795
6270.3635 | 475.3279 | 589.3625 | 623.9057
6271.3635 | 475.4291 | 590.1839 | 624.1989
6272.3635 | 475.4335 | 591.064 | 624.4673
6273.3635 | 475.4465 | 591.8725 | 624.5904
6274.3635 | 475.4445 | 592.8614 | 624.9652
6275.3635 | 475.4731 | 593.7587 | 625.2068
6276.3635 | 475.386 | 594.8362 | 625.5399
6277.3635 | 475.4232 | 595.8101 | 625.6844
6278.3635 | 475.4851 | 596.9343 | 626.1044
6279.3635 | 475.5082 | 597.9163 | 626.2089
6280.3635 | 475.4978 | 599.0197 | 626.4896
6281.3635 | 475.503 | 600.1211 | 626.8113
6282.3635 | 475.5021 | 601.17 | 627.0216
6283.3635 | 475.4918 | 602.2651 | 627.3481
6284.3635 | 475.4935 | 603.3621 | 627.6107
6285.3635 | 475.4292 | 604.4437 | 627.8802
6286.3635 | 475.4242 | 605.5092 | 628.0727
6287.3635 | 475.3395 | 606.6985 | 628.408
6288.3635 | 475.2571 | 607.7698 | 628.6091
6289.3635 | 475.2258 | 608.8286 | 628.868
6290.3635 | 475.2488 | 609.9006 | 629.0916
6291.3635 | 475.2647 | 610.9494 | 629.4896
6292.3635 | 475.2245 | 611.8478 | 629.6836
6293.3635 | 475.2579 | 612.6954 | 629.8883
6294.3635 | 475.2104 | 613.7208 | 630.3832
6295.3635 | 475.239 | 614.5979 | 630.6986
6296.3635 | 475.3085 | 615.3964 | 630.9036
6297.3635 | 475.2522 | 616.123 | 631.0616
6298.3635 | 475.1629 | 616.9283 | 631.4162
6299.3635 | 475.0738 | 617.8048 | 631.6822
6300.3635 | 475.0675 | 618.6497 | 632.029
6301.3635 | 475.1295 | 619.5044 | 632.3928
6302.3635 | 475.1256 | 620.1663 | 632.6096
6303.3635 | 475.1036 | 621.0356 | 633.1019
6304.3635 | 475.0587 | 621.7276 | 633.2513
6305.3635 | 475.0796 | 622.4653 | 633.5779
6306.3635 | 475.183 | 623.1835 | 633.8087
6307.3635 | 475.1908 | 623.8966 | 634.1019
6308.3635 | 475.3392 | 624.563 | 634.4078
6309.3635 | 475.3441 | 625.1853 | 634.5733
6310.3635 | 475.3311 | 625.8967 | 634.9845
6311.3635 | 475.3182 | 626.5619 | 635.3607
6312.3635 | 475.3057 | 627.263 | 635.7485
6313.3635 | 475.4121 | 627.8034 | 635.9154
6314.3635 | 475.4875 | 628.4573 | 636.1959
6315.3635 | 475.6039 | 629.0516 | 636.4447
6316.3635 | 475.7841 | 629.6925 | 636.7439
6317.3635 | 475.7997 | 630.3451 | 636.9641
6318.3635 | 475.8408 | 631.0443 | 637.2838
6319.3635 | 475.898 | 631.6149 | 637.4456
6320.3635 | 475.9161 | 632.0389 | 637.5879
6321.3635 | 475.9308 | 632.5762 | 637.8708
6322.3635 | 475.9977 | 633.1727 | 638.2235
6323.3635 | 476.0023 | 633.6981 | 638.5224
6324.3635 | 476.0666 | 634.1533 | 638.7034
6325.3635 | 476.1137 | 634.817 | 639.0885
6326.3635 | 476.1497 | 635.361 | 639.4118
6327.3635 | 476.118 | 635.9414 | 639.7912
6328.3635 | 476.0802 | 636.7379 | 640.3905
6329.3635 | 476.1334 | 637.2863 | 640.8285
6330.3635 | 476.1575 | 637.8744 | 641.218
6331.3635 | 476.1963 | 638.5924 | 641.6773
6332.3635 | 476.2128 | 639.1215 | 641.9143
6333.3635 | 476.0535 | 639.5805 | 642.0369
6334.3635 | 475.8508 | 640.0967 | 642.1886
6335.3635 | 475.6291 | 640.5707 | 642.3333
6336.3635 | 475.364 | 640.9682 | 642.4162
6337.3635 | 475.0417 | 641.426 | 642.5933
6338.3635 | 474.6054 | 641.9182 | 642.8148
6339.3635 | 474.1793 | 642.246 | 642.7947
6340.3635 | 473.6696 | 642.8102 | 643.0537
6341.3635 | 473.2133 | 643.0927 | 643.2199
6342.3635 | 472.7471 | 643.5037 | 643.4601
6343.3635 | 472.1955 | 643.9559 | 643.8261
6344.3635 | 471.6785 | 644.2984 | 644.0292
6345.3635 | 471.072 | 644.8036 | 644.2902
6346.3635 | 470.5103 | 645.3074 | 644.612
6347.3635 | 469.9818 | 645.8779 | 645.0226
6348.3635 | 469.4275 | 646.2968 | 645.236
6349.3635 | 468.8708 | 646.5553 | 645.3664
6350.3635 | 468.3972 | 647.2546 | 645.9053
6351.3635 | 467.7972 | 647.5388 | 645.9825
6352.3635 | 467.1819 | 647.7622 | 646.0728
6353.3635 | 466.6067 | 647.9904 | 646.3006
6354.3635 | 465.9719 | 648.2347 | 646.473
6355.3635 | 465.316 | 648.5444 | 646.7089
6356.3635 | 464.6446 | 648.8208 | 646.9864
6357.3635 | 464.0254 | 649.0899 | 647.1665
6358.3635 | 463.4502 | 649.448 | 647.4458
6359.3635 | 462.8216 | 649.7113 | 647.5644
6360.3635 | 462.2795 | 649.9901 | 647.7303
6361.3635 | 461.5842 | 650.2084 | 647.8121
6362.3635 | 460.9925 | 650.4276 | 647.996
6363.3635 | 460.4492 | 650.6923 | 648.1564
6364.3635 | 459.9435 | 650.8351 | 648.1709
6365.3635 | 459.3672 | 651.1177 | 648.3108
6366.3635 | 458.7409 | 651.2611 | 648.3163
6367.3635 | 458.0855 | 651.4941 | 648.3696
6368.3635 | 457.4539 | 651.7225 | 648.534
6369.3635 | 456.7554 | 652.0206 | 648.6762
6370.3635 | 456.1379 | 652.446 | 649.0322
6371.3635 | 455.4904 | 652.7799 | 649.3183
6372.3635 | 454.8533 | 653.0817 | 649.557
6373.3635 | 454.2828 | 653.426 | 649.7731
6374.3635 | 453.6595 | 653.6433 | 649.848
6375.3635 | 453.0572 | 654.0036 | 650.0649
6376.3635 | 452.4231 | 654.3197 | 650.2398
6377.3635 | 451.7747 | 654.7329 | 650.5704
6378.3635 | 451.1614 | 655.0903 | 650.9183
6379.3635 | 450.6535 | 655.3265 | 651.1327
6380.3635 | 450.0899 | 655.7269 | 651.5219
6381.3635 | 449.4932 | 655.9673 | 651.6803
6382.3635 | 448.8511 | 656.1885 | 651.8737
6383.3635 | 448.1924 | 656.5087 | 652.1853
6384.3635 | 447.5704 | 656.8066 | 652.5332
6385.3635 | 446.973 | 657.1865 | 652.8791
6386.3635 | 446.4967 | 657.7333 | 653.3046
6387.3635 | 445.995 | 658.4907 | 653.8835
6388.3635 | 445.4147 | 658.8477 | 654.1799
6389.3635 | 444.7413 | 659.255 | 654.4282
6390.3635 | 444.1084 | 659.7588 | 654.8693
6391.3635 | 443.4406 | 659.9695 | 655.0214
6392.3635 | 442.7967 | 660.3763 | 655.3278
6393.3635 | 442.2127 | 660.7924 | 655.6166
6394.3635 | 441.698 | 661.1609 | 655.824
6395.3635 | 441.1113 | 661.7208 | 656.2165
6396.3635 | 440.515 | 662.0168 | 656.3886
6397.3635 | 439.968 | 662.1 | 656.3597
6398.3635 | 439.4904 | 662.4749 | 656.6278
6399.3635 | 438.9939 | 662.956 | 657.0296
6400.3635 | 438.3454 | 663.4465 | 657.4824
6401.3635 | 437.69 | 663.8958 | 657.8273
6402.3635 | 437.0481 | 664.2289 | 658.1194
6403.3635 | 436.3959 | 664.6217 | 658.3823
6404.3635 | 435.7025 | 665.194 | 658.8085
6405.3635 | 435.0224 | 665.6681 | 659.1947
6406.3635 | 434.4846 | 666.1899 | 659.5744
6407.3635 | 433.8951 | 666.5114 | 659.8045
6408.3635 | 433.3604 | 666.8591 | 660.0566
6409.3479 | 432.8107 | 667.3434 | 660.4683
6410.3479 | 432.1894 | 668.0871 | 661.0653
6411.3479 | 431.5292 | 668.5238 | 661.5255
6412.3479 | 430.8976 | 668.9694 | 661.9489
6413.3479 | 430.2734 | 669.2972 | 662.3461
6414.3479 | 429.5867 | 669.6359 | 662.786
6415.3479 | 428.9674 | 670.1403 | 663.3294
6416.3479 | 428.3155 | 670.6095 | 663.8393
6417.3479 | 427.6789 | 671.0865 | 664.301
6418.3479 | 427.0537 | 671.6012 | 664.6534
6419.3479 | 426.4422 | 672.0339 | 664.8625
6420.3479 | 425.8328 | 672.4572 | 665.2022
6421.3635 | 425.2671 | 672.7635 | 665.5141
6422.3479 | 424.7156 | 673.0749 | 665.7991
6423.3479 | 424.1312 | 673.4713 | 666.1269
6424.3479 | 423.5944 | 673.7044 | 666.2854
6425.3479 | 422.9314 | 674.0616 | 666.513
6426.3479 | 422.3187 | 674.3716 | 666.7748
6427.3479 | 421.7146 | 674.7529 | 667.0701
6428.3479 | 421.201 | 675.1106 | 667.367
6429.3479 | 420.6149 | 675.3109 | 667.4984
6430.3479 | 419.9832 | 675.7334 | 667.825
6431.3479 | 419.4735 | 676.0527 | 668.1093
6432.3479 | 418.9356 | 676.3224 | 668.3634
6433.3479 | 418.3681 | 676.5919 | 668.5316
6434.3479 | 417.7858 | 676.9279 | 668.768
6435.3479 | 417.1203 | 677.2027 | 668.9989
6436.3479 | 416.5017 | 677.4721 | 669.155
6437.3479 | 415.9441 | 677.7388 | 669.3078
6438.3479 | 415.3731 | 678.0364 | 669.5484
6439.3479 | 414.7619 | 678.316 | 669.744
6440.3479 | 414.1546 | 678.6156 | 670.072
6441.3479 | 413.5538 | 678.8685 | 670.3558
6442.3479 | 412.9251 | 679.1293 | 670.6545
6443.3479 | 412.4286 | 679.4928 | 670.9976
6444.3479 | 411.7479 | 679.6913 | 671.2427
6445.3479 | 411.1438 | 679.9107 | 671.5829
6446.3479 | 410.5725 | 680.0505 | 671.8446
6447.3479 | 409.995 | 680.2923 | 672.1605
6448.3479 | 409.4794 | 680.4359 | 672.3457
6449.3479 | 408.8636 | 680.5112 | 672.4676
6450.3479 | 408.2045 | 680.6003 | 672.5342
6451.3635 | 407.5293 | 680.724 | 672.5813
6452.3479 | 406.9073 | 680.8258 | 672.5401
6453.3479 | 406.3751 | 680.9498 | 672.4731
6454.3479 | 405.876 | 681.1846 | 672.5482
6455.3479 | 405.3834 | 681.4687 | 672.7585
6456.3479 | 404.8527 | 681.5094 | 672.7227
6457.3479 | 404.2817 | 681.7419 | 672.896
6458.3479 | 403.7333 | 681.8928 | 672.9749
6459.3479 | 403.1936 | 681.9075 | 672.9517
6460.3479 | 402.6194 | 682.0219 | 673.0003
6461.3479 | 402.0556 | 682.0965 | 673.0312
6462.3479 | 401.4588 | 682.2603 | 673.1759
6463.3479 | 400.8439 | 682.5271 | 673.4328
6464.3479 | 400.267 | 682.6223 | 673.5274
6465.3479 | 399.696 | 682.8274 | 673.7018
6466.3479 | 399.2073 | 683.0441 | 673.8848
6467.3479 | 398.6463 | 683.2716 | 674.0524
6468.3635 | 398.089 | 683.402 | 674.0908
6469.3479 | 397.5186 | 683.5543 | 674.1778
6470.3479 | 396.9406 | 683.7777 | 674.336
6471.3479 | 396.4361 | 684.0768 | 674.5755
6472.3635 | 396.0086 | 684.1785 | 674.6052
6473.3479 | 395.3957 | 684.3556 | 674.745
6474.3479 | 394.8469 | 684.4889 | 674.8428
6475.3479 | 394.3012 | 684.7463 | 675.0317
6476.3479 | 393.8417 | 684.8964 | 675.1217
6477.3479 | 393.3839 | 684.8435 | 675.0442
6478.3479 | 392.8298 | 684.8799 | 675.0395
6479.3479 | 392.2508 | 684.9156 | 674.9743
6480.3479 | 391.6784 | 684.8865 | 674.9396
6481.3635 | 391.0631 | 684.967 | 675.0262
6482.3635 | 390.5193 | 685.1173 | 675.1958
6483.3635 | 389.9454 | 685.2343 | 675.3208
6484.3479 | 389.4168 | 685.5171 | 675.5625
6485.3479 | 388.8271 | 685.6772 | 675.759
6486.3479 | 388.3448 | 685.8602 | 675.9417
6487.3635 | 387.8485 | 685.9257 | 676.0289
6488.3479 | 387.2784 | 686.0514 | 676.1768
6489.3479 | 386.7381 | 686.2435 | 676.4042
6490.3479 | 386.2875 | 686.4408 | 676.6227
6491.3479 | 385.7817 | 686.5597 | 676.769
6492.3479 | 385.1959 | 686.738 | 677.0112
6493.3479 | 384.6874 | 686.9003 | 677.1755
6494.3479 | 384.2038 | 686.9595 | 677.2974
6495.3479 | 383.6082 | 687.0611 | 677.5123
6496.3479 | 383.0738 | 687.2135 | 677.7025
6497.3479 | 382.6369 | 687.3379 | 677.8886
6498.3479 | 382.0852 | 687.4698 | 677.9712
6499.3479 | 381.5559 | 687.5534 | 677.9263
6500.3479 | 381.0647 | 687.7173 | 677.9417
6501.3479 | 380.5913 | 687.872 | 677.9378
6502.3479 | 380.1179 | 688.0795 | 678.0789
6503.3479 | 379.5848 | 688.1846 | 678.1056
6504.3479 | 379.0696 | 688.3703 | 678.1835
6505.3635 | 378.6023 | 688.5394 | 678.2638
6506.3479 | 378.0531 | 688.7127 | 678.3501
6507.3479 | 377.4912 | 688.7644 | 678.3396
6508.3635 | 376.973 | 688.7906 | 678.4079
6509.3479 | 376.4955 | 688.8939 | 678.5263
6510.3479 | 375.9518 | 688.9976 | 678.6481
6511.3635 | 375.4423 | 688.8958 | 678.5654
6512.3479 | 374.9779 | 688.7882 | 678.5382
6513.3479 | 374.4502 | 688.7409 | 678.6048
6514.3635 | 373.878 | 688.6271 | 678.6251
6515.3635 | 373.3095 | 688.7829 | 678.7466
6516.3635 | 372.9105 | 688.8506 | 678.8192
6517.3635 | 372.383 | 688.7567 | 678.8174
6518.3635 | 371.9396 | 688.8304 | 678.8312
6519.3635 | 371.4355 | 688.8762 | 678.8674
6520.3635 | 370.9714 | 688.8711 | 678.9812
6521.3635 | 370.4408 | 688.8455 | 678.9722
6522.3635 | 369.9416 | 688.8246 | 678.903
6523.3635 | 369.4363 | 688.8029 | 678.8587
6524.3635 | 368.8821 | 688.7831 | 678.8298
6525.3635 | 368.319 | 688.7645 | 678.8498
6526.3635 | 367.744 | 688.8056 | 678.9884
6527.3635 | 367.2476 | 688.9371 | 679.1456
6528.3635 | 366.8085 | 688.9161 | 679.1463
6529.3635 | 366.3425 | 688.7881 | 679.0589
6530.3635 | 365.8145 | 688.7777 | 679.0656
6531.3635 | 365.269 | 688.7641 | 679.1108
6532.3635 | 364.761 | 688.773 | 679.172
6533.3635 | 364.1892 | 688.7364 | 679.1516
6534.3479 | 363.6677 | 688.7281 | 679.1383
6535.3635 | 363.2503 | 688.7313 | 679.1035
6536.3635 | 362.8617 | 688.643 | 679.0059
6537.3635 | 362.3921 | 688.6304 | 678.9686
6538.3635 | 361.9018 | 688.6395 | 678.9609
6539.3635 | 361.3994 | 688.6323 | 678.9828
6540.3635 | 360.8758 | 688.6657 | 678.9776
6541.3635 | 360.3738 | 688.6615 | 678.9944
6542.3635 | 359.8806 | 688.6664 | 679.0715
6543.3635 | 359.4147 | 688.614 | 679.0843
6544.3635 | 358.98 | 688.5195 | 679.0272
6545.3635 | 358.5373 | 688.4737 | 678.998
6546.3635 | 358.0422 | 688.3836 | 679.0251
6547.3635 | 357.5231 | 688.2699 | 678.9839
6548.3635 | 356.9783 | 688.1442 | 678.9225
6549.3635 | 356.5403 | 688.0049 | 678.7747
6550.3635 | 356.0584 | 687.9328 | 678.7162
6551.3635 | 355.5546 | 687.891 | 678.7354
6552.3635 | 355.0915 | 687.9036 | 678.6981
6553.3635 | 354.617 | 687.7696 | 678.6764
6554.3635 | 354.2485 | 687.6665 | 678.6682
6555.3635 | 353.8357 | 687.6842 | 678.5535
6556.3635 | 353.3661 | 687.6049 | 678.3595
6557.3635 | 352.8672 | 687.3964 | 678.3006
6558.3635 | 352.4034 | 687.331 | 678.4074
6559.3635 | 351.8635 | 687.2568 | 678.4127
6560.3635 | 351.3775 | 687.2753 | 678.3872
6561.3635 | 350.9059 | 687.2942 | 678.3492
6562.3635 | 350.423 | 687.2619 | 678.3506
6563.3635 | 349.93 | 687.2595 | 678.3166
6564.3635 | 349.4831 | 687.1587 | 678.3304
6565.3635 | 348.9881 | 687.0669 | 678.33
6566.3635 | 348.53 | 687.0365 | 678.4065
6567.3635 | 348.0576 | 686.9857 | 678.3569
6568.3635 | 347.5838 | 686.9589 | 678.3612
6569.3635 | 347.1281 | 686.9121 | 678.4147
6570.3635 | 346.6919 | 686.9368 | 678.4874
6571.3635 | 346.2578 | 686.8736 | 678.3735
6572.3635 | 345.7913 | 686.8175 | 678.2961
6573.3635 | 345.3186 | 686.7574 | 678.1901
6574.3635 | 344.8523 | 686.7245 | 678.0874
6575.3635 | 344.4777 | 686.7142 | 677.956
6576.3635 | 344.0465 | 686.7125 | 677.8665
6577.3635 | 343.6126 | 686.7752 | 677.8033
6578.3635 | 343.1667 | 686.7953 | 677.7569
6579.3635 | 342.742 | 686.7486 | 677.7186
6580.3635 | 342.2537 | 686.7387 | 677.7067
6581.3635 | 341.7758 | 686.6814 | 677.6757
6582.3635 | 341.317 | 686.6379 | 677.6299
6583.3635 | 340.8916 | 686.5454 | 677.572
6584.3635 | 340.4721 | 686.4156 | 677.4307
6585.3635 | 340.015 | 686.3584 | 677.425
6586.3635 | 339.5564 | 686.2522 | 677.3797
6587.3635 | 339.078 | 686.1934 | 677.404
6588.3635 | 338.6148 | 686.0649 | 677.3043
6589.3635 | 338.1759 | 686.0602 | 677.1953
6590.3635 | 337.7272 | 686.0424 | 677.1914
6591.3635 | 337.2547 | 686.0295 | 677.1195
6592.3635 | 336.8659 | 686.002 | 677.0728
6593.3635 | 336.4058 | 685.9218 | 676.9857
6594.3635 | 335.9658 | 685.8597 | 676.9246
6595.3635 | 335.537 | 685.7798 | 676.8582
6596.3635 | 335.1731 | 685.7425 | 676.8381
6597.3635 | 334.7754 | 685.5825 | 676.778
6598.3635 | 334.2645 | 685.4814 | 676.6931
6599.3635 | 333.8401 | 685.3949 | 676.5485
6600.3635 | 333.3671 | 685.3695 | 676.4634
6601.3635 | 332.9397 | 685.2938 | 676.4392
6602.3635 | 332.4861 | 685.2322 | 676.4297
6603.3635 | 332.0724 | 685.107 | 676.3181
6604.3635 | 331.5687 | 685.0168 | 676.2156
6605.3635 | 331.158 | 685.0114 | 676.0733
6606.3635 | 330.7547 | 684.8988 | 675.9354
6607.3635 | 330.3489 | 684.8532 | 675.8951
6608.3635 | 329.8832 | 684.8343 | 675.8396
6609.3635 | 329.5038 | 684.7894 | 675.6988
6610.3635 | 329.0609 | 684.7471 | 675.5471
6611.3635 | 328.6077 | 684.71 | 675.4887
6612.3635 | 328.18 | 684.7296 | 675.4806
6613.3635 | 327.7295 | 684.7786 | 675.595
6614.3635 | 327.3107 | 684.788 | 675.651
6615.3635 | 326.8901 | 684.7265 | 675.6213
6616.3635 | 326.4844 | 684.6118 | 675.5051
6617.3635 | 326.0652 | 684.4817 | 675.3347
6618.3635 | 325.6692 | 684.4161 | 675.2057
6619.3635 | 325.274 | 684.3171 | 675.0863
6620.3635 | 324.8796 | 684.2287 | 675.0882
6621.3635 | 324.5226 | 684.1832 | 675.1257
6622.3635 | 324.1843 | 684.1018 | 675.0715
6623.3635 | 323.7746 | 683.9386 | 674.9318
6624.3635 | 323.3373 | 683.8815 | 674.8581
6625.3635 | 322.879 | 683.8009 | 674.6878
6626.3635 | 322.4114 | 683.6919 | 674.441
6627.3635 | 322.0032 | 683.6328 | 674.2637
6628.3635 | 321.6382 | 683.5487 | 674.2023
6629.3635 | 321.2569 | 683.3876 | 674.112
6630.3635 | 320.8622 | 683.2519 | 674.0622
6631.3635 | 320.4798 | 683.1928 | 674.0265
6632.3635 | 320.0663 | 683.1111 | 674.0054
6633.3635 | 319.6335 | 683.0022 | 673.9076
6634.3635 | 319.1058 | 682.8478 | 673.7863
6635.3635 | 318.7214 | 682.7404 | 673.6517
6636.3635 | 318.2908 | 682.609 | 673.4566
6637.3635 | 317.8955 | 682.557 | 673.3956
6638.3635 | 317.497 | 682.4802 | 673.3091
6639.3635 | 317.0795 | 682.403 | 673.2155
6640.3635 | 316.7297 | 682.2653 | 673.1331
6641.3635 | 316.3836 | 682.1141 | 673.0428
6642.3635 | 316.0555 | 681.9828 | 672.9242
6643.3635 | 315.6575 | 681.899 | 672.839
6644.3635 | 315.2475 | 681.753 | 672.7281
6645.3635 | 314.8393 | 681.6003 | 672.6137
6646.3635 | 314.4471 | 681.4953 | 672.4676
6647.3635 | 314.0483 | 681.4005 | 672.288
6648.3635 | 313.6297 | 681.2377 | 672.1728
6649.3479 | 313.1572 | 681.0574 | 672.1065
6650.3635 | 312.7574 | 680.9339 | 672.0797
6651.3479 | 312.4385 | 680.8578 | 671.9437
6652.3479 | 312.0526 | 680.8046 | 671.8377
6653.3479 | 311.6733 | 680.6561 | 671.7627
6654.3479 | 311.2196 | 680.5119 | 671.652
6655.3479 | 310.797 | 680.3762 | 671.5503
6656.3479 | 310.4212 | 680.2279 | 671.479
6657.3479 | 310.0408 | 680.158 | 671.4739
6658.3479 | 309.6932 | 680.1091 | 671.5155
6659.3479 | 309.3861 | 680.0679 | 671.4835
6660.3479 | 309.0601 | 679.9717 | 671.4015
6661.3479 | 308.6547 | 679.9102 | 671.2653
6662.3479 | 308.2203 | 679.8763 | 671.213
6663.3479 | 307.8747 | 679.8104 | 671.1532
6664.3479 | 307.4952 | 679.6473 | 671.0389
6665.3479 | 307.1671 | 679.5711 | 670.9197
6666.3479 | 306.7592 | 679.5121 | 670.7792
6667.3479 | 306.3383 | 679.4168 | 670.706
6668.3479 | 305.942 | 679.3145 | 670.5891
6669.3479 | 305.5609 | 679.2236 | 670.4238
6670.3479 | 305.0938 | 679.1198 | 670.2696
6671.3479 | 304.6988 | 678.969 | 670.0724
6672.3479 | 304.3719 | 678.8217 | 669.8796
6673.3479 | 304.0072 | 678.7046 | 669.6596
6674.3479 | 303.5997 | 678.5572 | 669.5234
6675.3479 | 303.1937 | 678.4437 | 669.4379
6676.3479 | 302.8558 | 678.3464 | 669.3323
6677.3479 | 302.5049 | 678.3072 | 669.189
6678.3479 | 302.1486 | 678.1353 | 669.0097
6679.3479 | 301.7819 | 677.93 | 668.9091
6680.3479 | 301.4159 | 677.7993 | 668.9074
6681.3479 | 301.0879 | 677.7083 | 668.9062
6682.3479 | 300.7492 | 677.6251 | 668.7797
6683.3479 | 300.3613 | 677.4514 | 668.6869
6684.3479 | 299.958 | 677.2961 | 668.5925
6685.3479 | 299.5892 | 677.1357 | 668.5086
6686.3479 | 299.2013 | 677.0504 | 668.4225
6687.3479 | 298.8638 | 676.8845 | 668.3309
6688.3479 | 298.5007 | 676.7274 | 668.177
6689.3479 | 298.1207 | 676.653 | 668.0592
6690.3479 | 297.7877 | 676.5408 | 668.0035
6691.3479 | 297.4576 | 676.4525 | 667.9357
6692.3479 | 297.1439 | 676.3433 | 667.8489
6693.3479 | 296.8401 | 676.3007 | 667.8081
6694.3479 | 296.4794 | 676.1868 | 667.667
6695.3479 | 296.0865 | 676.0051 | 667.587
6696.3479 | 295.718 | 675.8523 | 667.5105
6697.3479 | 295.3582 | 675.6165 | 667.4382
6698.3479 | 295.019 | 675.4064 | 667.4199
6699.3479 | 294.6437 | 675.1926 | 667.4002
6700.3479 | 294.2808 | 675.0463 | 667.3622
6701.3479 | 293.9679 | 674.9066 | 667.203
6702.3479 | 293.628 | 674.807 | 666.9718
6703.3635 | 293.2768 | 674.7609 | 666.7725
6704.3479 | 292.9266 | 674.6603 | 666.6394
6705.3479 | 292.5147 | 674.5438 | 666.5935
6706.3479 | 292.1337 | 674.4156 | 666.5062
6707.3479 | 291.7974 | 674.3371 | 666.4205
6708.3479 | 291.4347 | 674.1721 | 666.3558
6709.3479 | 291.0908 | 673.9946 | 666.2376
6710.3479 | 290.7363 | 673.8531 | 666.1015
6711.3479 | 290.3737 | 673.7128 | 665.9688
6712.3479 | 290.0242 | 673.5806 | 665.7938
6713.3479 | 289.7183 | 673.4072 | 665.6541
6714.3479 | 289.3771 | 673.1742 | 665.6724
6715.3635 | 288.9899 | 673.0568 | 665.594
6716.3635 | 288.6527 | 672.8902 | 665.5367
6717.3479 | 288.2918 | 672.7976 | 665.4836
6718.3479 | 287.9359 | 672.6768 | 665.3892
6719.3635 | 287.5966 | 672.6294 | 665.2758
6720.3635 | 287.253 | 672.5731 | 665.191
6721.3635 | 286.9512 | 672.41 | 665.0143
6722.3479 | 286.5541 | 672.2035 | 664.8533
6723.3479 | 286.2753 | 672.0351 | 664.6457
6724.3479 | 286.0039 | 671.8663 | 664.5552
6725.3635 | 285.6988 | 671.6638 | 664.5534
6726.3635 | 285.4043 | 671.4205 | 664.5245
6727.3479 | 285.0286 | 671.1672 | 664.4522
6728.3479 | 284.6422 | 670.9951 | 664.3642
6729.3479 | 284.2786 | 670.8102 | 664.2718
6730.3479 | 283.952 | 670.5611 | 664.096
6731.3479 | 283.6068 | 670.3533 | 663.907
6732.3479 | 283.3137 | 670.2785 | 663.7562
6733.3479 | 282.9861 | 670.2608 | 663.5859
6734.3479 | 282.63 | 670.0018 | 663.5427
6735.3479 | 282.3185 | 669.7772 | 663.4897
6736.3635 | 281.9844 | 669.6196 | 663.3023
6737.3479 | 281.6991 | 669.4668 | 663.2257
6738.3479 | 281.3781 | 669.3813 | 663.091
6739.3479 | 281.0304 | 669.1271 | 662.8931
6740.3479 | 280.7119 | 668.9163 | 662.7006
6741.3479 | 280.3521 | 668.8116 | 662.6175
6742.3479 | 279.9683 | 668.7317 | 662.4615
6743.3479 | 279.6321 | 668.5745 | 662.306
6744.3479 | 279.2806 | 668.3714 | 662.2044
6745.3635 | 278.9812 | 668.0863 | 662.1794
6746.3479 | 278.6823 | 667.8854 | 662.1586
6747.3479 | 278.4139 | 667.6485 | 661.9759
6748.3479 | 278.137 | 667.3721 | 661.735
6749.3479 | 277.8206 | 667.1322 | 661.429
6750.3479 | 277.5061 | 666.9944 | 661.2151
6751.3479 | 277.1673 | 666.9019 | 661.0287
6752.3635 | 276.817 | 666.709 | 660.7681
6753.3635 | 276.5045 | 666.564 | 660.4718
6754.3635 | 276.2224 | 666.4485 | 660.227
6755.3635 | 275.9426 | 666.3437 | 660.0552
6756.3635 | 275.6277 | 666.1688 | 660.0702
6757.3635 | 275.3054 | 666.0739 | 660.0398
6758.3635 | 274.9735 | 665.9233 | 659.9694
6759.3635 | 274.6079 | 665.8246 | 659.9098
6760.3635 | 274.2546 | 665.6856 | 659.8897
6761.3635 | 273.9326 | 665.5033 | 659.8859
6762.3635 | 273.6135 | 665.3614 | 659.8795
6763.3635 | 273.3591 | 665.207 | 659.8048
6764.3635 | 273.0378 | 665.0189 | 659.7216
6765.3635 | 272.739 | 664.8371 | 659.6044
6766.3635 | 272.4392 | 664.639 | 659.4514
6767.3635 | 272.086 | 664.4835 | 659.2366
6768.3635 | 271.6895 | 664.3393 | 659.0279
6769.3635 | 271.3241 | 664.0837 | 658.9105
6770.3635 | 271.0138 | 663.9425 | 658.7589
6771.3635 | 270.7137 | 663.8161 | 658.7338
6772.3635 | 270.4324 | 663.597 | 658.5831
6773.3635 | 270.1319 | 663.4011 | 658.4941
6774.3635 | 269.8225 | 663.112 | 658.2913
6775.3635 | 269.5121 | 662.8865 | 658.1328
6776.3635 | 269.2084 | 662.631 | 657.9686
6777.3635 | 268.9021 | 662.4638 | 657.6824
6778.3635 | 268.6073 | 662.3284 | 657.4108
6779.3635 | 268.3284 | 662.0465 | 657.1794
6780.3635 | 268.0462 | 661.7873 | 656.9424
6781.3635 | 267.7429 | 661.5389 | 656.6746
6782.3635 | 267.4033 | 661.3854 | 656.5214
6783.3635 | 267.0842 | 661.1693 | 656.3708
6784.3635 | 266.7977 | 660.8708 | 656.3151
6785.3635 | 266.5366 | 660.5499 | 656.1097
6786.3635 | 266.2986 | 660.268 | 655.9703
6787.3635 | 266.0045 | 660.0123 | 655.7846
6788.3635 | 265.699 | 659.7333 | 655.6067
6789.3635 | 265.3803 | 659.4585 | 655.389
6790.3635 | 265.0886 | 659.1605 | 655.2025
6791.3635 | 264.8321 | 658.9533 | 655.133
6792.3635 | 264.5658 | 658.7947 | 655.0217
6793.3635 | 264.265 | 658.5276 | 654.9163
6794.3635 | 263.9418 | 658.2892 | 654.7964
6795.3635 | 263.6083 | 658.0347 | 654.6396
6796.3635 | 263.3127 | 657.8715 | 654.3915
6797.3635 | 263.0536 | 657.7256 | 654.0625
6798.3635 | 262.7723 | 657.4675 | 653.7499
6799.3635 | 262.4534 | 657.115 | 653.5431
6800.3635 | 262.1772 | 656.8174 | 653.3621
6801.3635 | 261.9371 | 656.5289 | 653.0807
6802.3635 | 261.619 | 656.222 | 652.8131
6803.3635 | 261.2487 | 655.9377 | 652.4546
6804.3635 | 260.9202 | 655.7259 | 652.1397
6805.3635 | 260.6007 | 655.5505 | 651.8158
6806.3635 | 260.2875 | 655.3773 | 651.5187
6807.3635 | 259.9367 | 655.1509 | 651.3916
6808.3635 | 259.6089 | 654.7979 | 651.1047
6809.3635 | 259.3174 | 654.51 | 650.8366
6810.3635 | 259.0749 | 654.2232 | 650.6201
6811.3635 | 258.8006 | 653.9679 | 650.3462
6812.3635 | 258.5072 | 653.6502 | 650.0453
6813.3635 | 258.1971 | 653.4049 | 649.755
6814.3635 | 257.8962 | 653.1508 | 649.4974
6815.3635 | 257.6155 | 652.9274 | 649.2736
6816.3635 | 257.3375 | 652.6027 | 648.9261
6817.3635 | 257.102 | 652.3893 | 648.6843
6818.3635 | 256.8903 | 652.1117 | 648.3958
6819.3635 | 256.611 | 651.7549 | 648.078
6820.3635 | 256.3392 | 651.4702 | 647.7203
6821.3635 | 256.0834 | 651.159 | 647.3495
6822.3635 | 255.8005 | 651.0524 | 646.9474
6823.3635 | 255.54 | 650.7684 | 646.5842
6824.3635 | 255.2848 | 650.4714 | 646.261
6825.3635 | 255.0361 | 650.0923 | 645.8218
6826.3635 | 254.7341 | 649.7854 | 645.4461
6827.3635 | 254.4511 | 649.5696 | 645.1014
6828.3635 | 254.1749 | 649.2414 | 644.721
6829.3635 | 253.9036 | 648.9382 | 644.3948
6830.3635 | 253.6074 | 648.5539 | 643.9445
6831.3635 | 253.2894 | 648.3253 | 643.4869
6832.3635 | 252.9999 | 648.036 | 643.0465
6833.3635 | 252.7051 | 647.7486 | 642.6199
6834.3635 | 252.4381 | 647.4507 | 642.2898
6835.3635 | 252.1172 | 647.2011 | 641.9215
6836.3635 | 251.8571 | 646.9743 | 641.5531
6837.3635 | 251.5698 | 646.6472 | 641.1462
6838.3635 | 251.2628 | 646.3303 | 640.7093
6839.3635 | 250.9806 | 645.9824 | 640.3027
6840.3635 | 250.7066 | 645.643 | 639.9014
6841.3635 | 250.3681 | 645.2672 | 639.5343
6842.3635 | 250.0608 | 644.979 | 639.1788
6843.3635 | 249.8129 | 644.6176 | 638.837
6844.3635 | 249.555 | 644.1908 | 638.4489
6845.3635 | 249.3083 | 643.9264 | 638.0441
6846.3635 | 249.0767 | 643.5669 | 637.6723
6847.3635 | 248.8075 | 643.1577 | 637.2228
6848.3635 | 248.5439 | 642.6794 | 636.7329
6849.3635 | 248.2515 | 642.2662 | 636.2853
6850.3635 | 247.9982 | 641.9098 | 635.9267
6851.3635 | 247.728 | 641.5861 | 635.5321
6852.3635 | 247.4237 | 641.1205 | 635.1007
6853.3635 | 247.1226 | 640.7978 | 634.6667
6854.3635 | 246.8689 | 640.4689 | 634.2656
6855.3635 | 246.6014 | 640.0894 | 633.8589
6856.3635 | 246.356 | 639.7009 | 633.5137
6857.3635 | 246.1176 | 639.3217 | 633.118
6858.3635 | 245.8039 | 638.874 | 632.6094
6859.3635 | 245.5282 | 638.5316 | 632.0736
6860.3635 | 245.2842 | 638.0789 | 631.6262
6861.3635 | 245.0222 | 637.6942 | 631.1957
6862.3635 | 244.7557 | 637.3299 | 630.7734
6863.3635 | 244.4461 | 636.9703 | 630.3763
6864.3635 | 244.1808 | 636.5514 | 629.9271
6865.3635 | 243.9399 | 636.2373 | 629.4159
6866.3635 | 243.6771 | 635.8309 | 628.9387
6867.3635 | 243.3965 | 635.5109 | 628.4727
6868.3635 | 243.0942 | 635.0658 | 628.0391
6869.3635 | 242.87 | 634.6948 | 627.4963
6870.3635 | 242.6644 | 634.3034 | 627.0425
6871.3635 | 242.4053 | 633.9755 | 626.5029
6872.3635 | 242.1645 | 633.5528 | 626.1012
6873.3635 | 241.921 | 633.1284 | 625.6813
6874.3635 | 241.6225 | 632.7211 | 625.2681
6875.3635 | 241.38 | 632.1245 | 624.9005
6876.3635 | 241.1721 | 631.681 | 624.4055
6877.3635 | 240.9594 | 631.2917 | 623.9374
6878.3635 | 240.7215 | 630.8482 | 623.4792
6879.3635 | 240.4981 | 630.5074 | 622.8499
6880.3635 | 240.2827 | 630.0154 | 622.3579
6881.3635 | 240.0032 | 629.4417 | 621.9257
6882.3635 | 239.7532 | 629.0135 | 621.401
6883.3635 | 239.4635 | 628.4804 | 620.8227
6884.3479 | 239.223 | 628.1278 | 620.1427
6885.3479 | 238.9869 | 627.6566 | 619.6497
6886.3479 | 238.7337 | 627.2289 | 619.145
6887.3479 | 238.4513 | 626.765 | 618.5631
6888.3479 | 238.1624 | 626.2634 | 617.9719
6889.3479 | 237.8755 | 625.9272 | 617.206
6890.3479 | 237.6667 | 625.1719 | 616.7581
6891.3479 | 237.362 | 624.5969 | 616.2056
6892.3479 | 237.1009 | 624.0029 | 615.6367
6893.3479 | 236.8622 | 623.476 | 615.1244
6894.3479 | 236.6149 | 622.8835 | 614.6322
6895.3479 | 236.391 | 621.9338 | 614.5306
6896.3635 | 236.1318 | 621.3624 | 613.9904
6897.3479 | 235.8826 | 620.7609 | 613.4644
6898.3479 | 235.6033 | 620.1925 | 612.8996
6899.3479 | 235.391 | 619.6445 | 612.3457
6900.3479 | 235.1484 | 619.0367 | 611.7424
6901.3635 | 234.945 | 618.5209 | 611.181
6902.3479 | 234.7324 | 617.9819 | 610.6277
6903.3479 | 234.4623 | 617.4951 | 610.0473
6904.3635 | 234.2206 | 616.9126 | 609.5303
6905.3479 | 233.9666 | 616.4408 | 608.8696
6906.3479 | 233.7527 | 615.9253 | 608.2651
6907.3479 | 233.4986 | 615.3842 | 607.6366
6908.3479 | 233.2375 | 614.7459 | 607.0819
6909.3479 | 232.9827 | 614.2095 | 606.5261
6910.3479 | 232.7143 | 613.6155 | 605.9456
6911.3635 | 232.4961 | 613.0038 | 605.3646
6912.3479 | 232.2487 | 612.4078 | 604.7698
6913.3479 | 232.0123 | 611.8372 | 604.1778
6914.3479 | 231.7458 | 611.2793 | 603.5988
6915.3479 | 231.4929 | 610.7508 | 602.9613
6916.3479 | 231.258 | 610.1614 | 602.3492
6917.3479 | 230.9914 | 609.647 | 601.6304
6918.3479 | 230.7437 | 609.005 | 600.9731
6919.3479 | 230.5384 | 608.4334 | 600.3149
6920.3479 | 230.3351 | 607.7271 | 599.817
6921.3479 | 230.1231 | 607.1803 | 599.1257
6922.3635 | 229.9159 | 606.5705 | 598.4558
6923.3479 | 229.6708 | 605.8644 | 597.8935
6924.3479 | 229.3994 | 605.2522 | 597.22
6925.3635 | 229.1555 | 604.62 | 596.5991
6926.3479 | 228.9073 | 604.0796 | 595.9476
6927.3479 | 228.6677 | 603.7707 | 595.0138
6928.3479 | 228.3974 | 602.8087 | 594.7929
6929.3479 | 228.1394 | 602.1838 | 594.2223
6930.3479 | 227.9093 | 601.9519 | 593.14
6931.3479 | 227.6532 | 601.3242 | 592.4107
6932.3479 | 227.4238 | 600.7054 | 591.6747
6933.3479 | 227.1538 | 600.2752 | 590.7522
6934.3479 | 226.9097 | 599.513 | 590.2274
6935.3479 | 226.6709 | 598.9874 | 589.4722
6936.3479 | 226.47 | 598.2764 | 588.9844
6937.3479 | 226.2354 | 597.5861 | 588.3724
6938.3479 | 226.0443 | 597.0719 | 587.6743
6939.3479 | 225.8012 | 596.4366 | 587.0013
6940.3479 | 225.5393 | 595.8693 | 586.2937
6941.3479 | 225.3211 | 595.2743 | 585.6164
6942.3479 | 225.1082 | 594.704 | 584.8856
6943.3479 | 224.925 | 594.1385 | 584.1694
6944.3479 | 224.6607 | 593.4884 | 583.4591
6945.3635 | 224.4405 | 592.6914 | 582.8637
6946.3479 | 224.2664 | 592.0706 | 582.1609
6947.3479 | 224.0682 | 591.6854 | 581.2145
6948.3479 | 223.8667 | 590.9073 | 580.7042
6949.3635 | 223.6912 | 590.2781 | 580.0302
6950.3479 | 223.3836 | 589.6519 | 579.2975
6951.3479 | 223.1741 | 588.8312 | 578.7969
6952.3479 | 222.9911 | 588.1573 | 578.1909
6953.3479 | 222.7489 | 587.4855 | 577.5388
6954.3479 | 222.5178 | 586.9412 | 576.8008
6955.3479 | 222.2397 | 586.2992 | 576.1074
6956.3479 | 221.9959 | 585.6788 | 575.3401
6957.3479 | 221.8381 | 585.0456 | 574.6516
6958.3479 | 221.677 | 584.3978 | 573.9516
6959.3479 | 221.4508 | 583.7197 | 573.2617
6960.3635 | 221.1735 | 583.0418 | 572.5472
6961.3635 | 220.9292 | 582.3557 | 571.8421
6962.3479 | 220.7384 | 581.7174 | 571.1665
6963.3479 | 220.5236 | 581.7224 | 569.742
6964.3635 | 220.2967 | 580.9289 | 569.2283
6965.3479 | 220.0333 | 580.3063 | 568.5986
6966.3479 | 219.7834 | 578.9665 | 568.6697
6967.3479 | 219.582 | 578.9059 | 567.3384
6968.3479 | 219.3965 | 578.3755 | 566.4971
6969.3635 | 219.1945 | 577.6982 | 565.8043
6970.3635 | 218.9675 | 576.938 | 565.1339
6971.3479 | 218.73 | 576.2391 | 564.4328
6972.3479 | 218.5363 | 575.5568 | 563.71
6973.3479 | 218.3148 | 574.8067 | 563.0633
6974.3479 | 218.0944 | 574.1467 | 562.2974
6975.3479 | 217.8612 | 573.4433 | 561.5495
6976.3479 | 217.5572 | 572.7827 | 560.7881
6977.3479 | 217.3618 | 572.074 | 560.0558
6978.3479 | 217.1178 | 571.3857 | 559.3383
6979.3479 | 216.8954 | 570.7494 | 558.5327
6980.3479 | 216.6192 | 570.0677 | 557.8105
6981.3479 | 216.4013 | 569.3178 | 557.1164
6982.3479 | 216.2292 | 568.6172 | 556.3793
6983.3479 | 215.9718 | 567.9021 | 555.6164
6984.3479 | 215.7559 | 567.1781 | 554.8995
6985.3635 | 215.5005 | 566.4826 | 554.1754
6986.3635 | 215.3303 | 565.7569 | 553.4482
6987.3635 | 215.0898 | 565.0543 | 552.709
6988.3635 | 214.8659 | 564.3633 | 551.9659
6989.3635 | 214.6556 | 563.6535 | 551.1788
6990.3635 | 214.471 | 562.9299 | 550.4003
6991.3635 | 214.2464 | 562.2063 | 549.6483
6992.3635 | 214.0178 | 561.5744 | 548.8781
6993.3635 | 213.7932 | 560.8813 | 548.1197
6994.3635 | 213.5625 | 560.1887 | 547.3713
6995.3635 | 213.3646 | 559.5648 | 546.5595
6996.3635 | 213.1931 | 558.9016 | 545.7941
6997.3635 | 212.9944 | 558.2193 | 545.0439
6998.3635 | 212.8396 | 557.5037 | 544.3056
6999.3635 | 212.6429 | 556.8238 | 543.5348
7000.3635 | 212.4324 | 556.108 | 542.7401